{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["Contents","Cover","1. F-Factor summary","2. Individual fire start info","3. Systems and Audit"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":2,"defined_names":97,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Contents","index":0,"n_rows":19,"n_cols":6,"rows_kept":19,"cut":false,"hidden":false,"merged":[[8,2,9,3],[2,1,2,10],[4,1,4,10]]}
[" "]
[]
[null,"Electricity Distribution Network Service Provider\nF-factor Reporting Template"]
[]
[null,"Table of contents"]
[]
[]
[null,null,"Cover sheet",null,null,"2. Fire start report"]
[]
[]
[]
[null,null,"1. F-factor summary",null,null,"3. Systems and Audit"]
[]
[]
[]
[]
[]
[]
[null,null,{"$f":"\"NOTE: This spreadsheet includes IRU targets up to and including FY\"&'1. F-Factor summary'!J9","v":"NOTE: This spreadsheet includes IRU targets up to and including FY2022/23"}]

{"sheet":"Cover","index":1,"n_rows":49,"n_cols":7,"rows_kept":49,"cut":false,"hidden":false,"merged":[[10,1,11,8],[13,1,13,8],[48,2,48,6],[42,2,42,3],[42,4,42,7],[46,2,46,6],[47,2,47,6],[38,2,38,3],[38,4,38,7],[41,2,41,3],[41,4,41,7],[37,2,37,3],[37,4,37,7],[32,3,32,8],[30,3,30,8],[15,1,15,8],[26,3,26,8],[28,3,28,8],[26,1,26,2],[31,3,31,5],[14,1,14,8],[16,1,16,8],[17,1,17,8],[21,1,21,8],[19,1,19,8]]}
[]
[]
[]
[]
[]
[]
[]
[null,"Distribution Network Service Provider"]
[null,"Fire start report"]
[]
[null,"This template is to be used by a DNSP to provide a fire start report to the AER in accordance with section 5 of the F-factor Order in Council.  "]
[]
[]
[null,"Colour coding of input sheets:"]
[null,"Dark blue = AER headings"]
[null,"Grey = AER instructions"]
[null,"Yellow = Input cells"]
[null,"Light orange = Automatically-generated cells"]
[]
[null,"Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so."]
[null,"The cells and structure of the spreadsheet is locked to prevent inadvertent interference with the automated settings."]
[null,"All dollar amounts are to be unrounded, and in nominal terms."]
[]
[]
[]
[]
[null,"DNSP:",null,"United Energy"]
[]
[null,"DNSP - trading name:",null,"United Energy Distribution Pty Ltd"]
[]
[null,"DNSP - Australian business number: ",null,"70 064 651 029"]
[]
[null,"Reporting year:",null,"2022/23"]
[]
[]
[]
[]
[null,"Business address","Address",null,"43 - 45 Centreway"]
[null,null,"Suburb",null,"Mt Waverley"]
[null,null,null,"State","Victoria","Postcode",3149]
[]
[null,"Postal address","Address",null,"P.O Box 449"]
[null,null,"Suburb",null,"Mt Waverley"]
[null,null,null,"State","Victoria","Postcode",3149]
[]
[]
[null,"Contact name/s"]
[null,"Contact phone/s"]
[null,"Contact email address/s"]

{"sheet":"1. F-Factor summary","index":2,"n_rows":14,"n_cols":15,"rows_kept":14,"cut":false,"hidden":false,"merged":[[5,1,5,2],[3,6,3,8],[4,6,4,8],[5,6,5,8],[11,2,11,3],[12,2,12,3],[13,2,13,3],[6,2,6,3],[7,2,7,3],[8,2,8,3],[9,2,9,3],[10,2,10,3]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"United Energy"},"IRU target:",{"$f":"IF(SUM(K2:O2)=0,\"\",SUM(K2:O2))","v":13.9},null,null,null,null,null,null,"AusNet Services","CitiPower","Jemena","Powercor","United Energy"]
[null,"F-factor data reporting","IRU amount:",{"$f":"IF(SUM('2. Individual fire start info'!S38:S2000)=0,\"\",SUM('2. Individual fire start info'!S38:S2000))","v":10.065600000000005},null,null,null,null,null,"current",{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>K1),\"\",LOOKUP($B3,$J3:$J100,K3:K100))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>L1),\"\",LOOKUP($B3,$J3:$J100,L3:L100))","v":""},"","",13.9]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2022/23"},"Revenue adjustment:",{"$f":"IF(OR(D1=\"\",D2=\"\"),\"\",15000*(D1-D2))","v":57515.999999999927},null,null,null,null,null,"2016/17",247.7,3.4,9.6999999999999993,468,22.3]
[null,null,null,null,null,null,null,null,null,"2017/18",247.7,3.4,9.6999999999999993,468,22.3]
[null,"Table 2: Summary of total fire starts by F factor Order definition",null,null,null,null,null,null,null,"2018/19",247.7,3.4,9.6999999999999993,468,22.3]
[null,"This is a summary of data in worksheet \"2. Fire Start Report\"",null,null,null,null,null,null,null,"2019/20",221.1,3.4,9.6999999999999993,412.8,22.3]
[null,"Kind of Fire Start by definition of fire start under clause 5 of F-factor Order","Total fires by cause",null,null,null,null,null,null,"2020/21",177.5,1.3,4.2,277.60000000000002,18.7]
[null,"Started in or originated from a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B8)","v":70},null,null,null,null,null,null,"2021/22",164.3,1.9,3.7,235.2,19]
[null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B9)","v":13},null,null,null,null,null,null,"2022/23",149.69999999999999,1.5,2.7,188,13.9]
[null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B10)","v":6}]
[null,"Started by lightning striking a distribution system or a part of a distribution system ",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B11)","v":1}]
[null,"Started by any other thing forming part of or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B12)","v":4}]
[null,"Otherwise started by a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B13)","v":0}]
[null,"Total",{"$f":"SUM(C8:C13)","v":94}]

{"sheet":"2. Individual fire start info","index":3,"n_rows":237,"n_cols":25,"rows_kept":237,"cut":false,"hidden":false,"merged":[[25,1,25,18],[27,1,27,20],[26,1,26,21],[35,19,35,21],[33,1,33,4],[35,2,35,10],[28,1,28,18],[29,1,29,18],[35,11,35,13],[35,14,35,17],[13,1,13,11],[22,1,22,21],[24,1,24,21],[14,1,14,20],[15,1,15,18],[16,1,16,18],[18,1,18,18],[21,1,21,18],[19,1,19,18],[23,1,23,18],[20,1,20,18],[17,1,17,18],[3,22,3,24],[4,22,4,24],[5,22,5,24],[7,1,7,21],[11,1,11,2],[9,1,9,21]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"United Energy"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2022/23"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"\"Enter into this worksheet fire start data, from any IT system, which have been recorded by \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\". Note that fire starts must be in accordance with the definition of a fire start in the Order In Council.\"","v":"Enter into this worksheet fire start data, from any IT system, which have been recorded by United Energy. Note that fire starts must be in accordance with the definition of a fire start in the Order In Council."}]
[]
[null,"\"Fire\" should be interpreted using its common meaning and can be defined as a process in which substances combine chemically with oxygen from the air and typically give out bright light, heat and smoke. A fire should be recorded where there is evidence of smoking, charring, scorching, burning or any other evidence that a fire had occurred.  "]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"United Energy must provide:"}]
[]
[null,"Table 3 - Individual Fire Starts"]
[null,"   (1) Date - dd/mm/yyyy"]
[null,"   (2) Time - if known, the 24-hour time of the fire start hh:mm"]
[null,"   (3) Latitude and longitude of the fire start as decimal coordinates"]
[null,"   (4) Address of the property on which the incident occurred or closest to the incident"]
[null,"   (5) Asset number for the asset nearest the fire start"]
[null,{"$f":"\"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the \"&B1&\" network\"","v":"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the United Energy network"}]
[null,"   (7) Voltage on the line in which the fire start occurred (note: this may not be the nearest polyphase overhead line)"]
[null,"   (8) Network categorisation - CBD, Urban, Rural Long or Rural Short"]
[null,"   (9) Asset type of primary asset causing fire in accordance with OSIRIS asset categories"]
[null,"   (10) Where the asset involved in the fire is a transformer or an overhead or underground line, provide the phase, or phases, of the line or transformer"]
[null,"   (11) Kind of fire start in accordance with categories specified in Clause 5 of the F-factor Order-In-Council [Note: For the 2022-2023 period, the AER and ESV will accept either the initiating event or the cause.]"]
[null,"   (12) Identify the location of the fire start in accordance with the categories specified in Clause 11(b) of the F-factor Order-In-Council"]
[null,"   (13) Provide the BOM fire danger rating applicable at the time of the fire start (data is available on the EM-COP website) [Note: The fire danger rating applies from the time it was issued; ratings do no apply retrospectively. The rating from the previous day carries into the current day until the rating is changed. If no fire danger rating is issued for the day, a rating of \"No forecast\" applies for the whole day.]"]
[null,{"$f":"\"   (14) \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\"'s record number for the incident\"","v":"   (14) United Energy's record number for the incident"}]
[null,"   (15) ESV's OSIRIS reference number for the incident"]
[null,"   (16) Free text description of the fault containing relevant comments from field reports "]
[]
[]
[]
[null,"Table 2: Individual Fire Starts"]
[]
[null,"Number","Fire starts",null,null,null,null,null,null,null,null,"Fire Type",null,null,"Risk Factors",null,null,null,"IRU \namount","Additional information"]
[null,null,"Date 1","Time 2","Latitude 3","Longitude 3","Address of incident 4","ID of \nnearest \nasset 5","ID of nearest \npolyphase \nline 6","Voltage of line in which \nfire start \noccurred 7","Network categorisation 8","Type of primary asset \ninvolved in fire start 9","Phase(s) of \nline or \ntransformer 10","Kind of fire start as per Clause 5\nof F-factor Order-In-Council 11","Location \narea 12","Location\nmultiplier","Fire \ndanger \nrating 13","Danger multiplier","Product of multipliers","DNSP record number 14","OSIRIS \n(ESV) reference \nnumber 15","Fault \ndescription 16"]
[{"$f":"COUNTA(C38:O38,Q38,T38:V38)","v":17},1,"2022-07-25","05:54:33",-37.983538844999998,145.18405806999999,"311 Chandler Rd, Keysborough VIC 3173, Australia",620237,"NP11","22kV AC","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O38=\"\",\"\",IF(O38=\"LBRA only\",0.2,IF(O38=\"HBRA only\",1,IF(O38=\"within electric line construction area\",19.8,IF(O38=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"No forecast",{"$f":"IF(Q38=\"\",\"\",IF(C38>=DATE(2022,9,1),IF(Q38=\"No forecast\",0.05,IF(Q38=\"Moderate\",0.334,IF(Q38=\"High\",0.678,IF(Q38=\"Extreme\",2.272,4.754)))),0.05))","v":0.05},{"$f":"IF(OR(P38=\"\",R38=\"\"),\"\",IF(AND(O38=\"within electric line construction area\",Q38=\"No forecast\"),1,P38*R38))","v":1.0000000000000002E-2},1637504,"20220728UTD_01","UE received a report from a customer seeing a transformer outside his house on fire. On attendance, the UE fault crew found the HV lead to a pole mounted Capacitor had burnt out. The capacitor was isolated from supply",null,null,"Overhead conductors"]
[17,2,"2022-08-04","05:39:57",-37.934731507999999,145.04745165,"454 South Rd, Moorabbin VIC 3189, Australia",1816987,"MR 15","11kV AC","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",{"$f":"IF(Q39=\"\",\"\",IF(C39>=DATE(2022,9,1),IF(Q39=\"No forecast\",0.05,IF(Q39=\"Moderate\",0.334,IF(Q39=\"High\",0.678,IF(Q39=\"Extreme\",2.272,4.754)))),0.05))","v":0.05},1.0000000000000002E-2,1640485,"20220905UTD_01","FRV reported fire on a pole fire coinciding with HV protection operation. On arrival a crew discovered a white phase HV dropper connection on a cap bank had failed and what looked like potential fire damage at HV fuse units.  Cap Bank isolated until repairs completed",null,null," - overhead conductor (bare; aluminium core steel reinforced)"]
[17,3,"2022-08-06","08:17:00",-38.071374734999999,145.12281055,"8 Mascot Ave, Bonbeach VIC 3196, Australia",3305205,"CRM13","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1641054,"20220905UTD_02","Crew investigated reports of pole damage and arrived on site to discover a 3 phase Fused Mains Box on the pole had likely caught fire and damaged several service connection to the box. Supply was isolated box replaced and connections fixed, supply restored.",null,null," - overhead conductor (bare; all aluminium conductor)"]
[17,4,"2022-08-15","08:21:00",-38.390308253000001,144.79264391000001,"1 Marcia Ave, Rye VIC 3941, Australia",1305681,"STO21","22kV AC","Rural"," - dropper / bridge","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.05,0.05,1643075,"20220816UTD_02","In response to a fault and reports of a loud noise, the attending UE fault crew found the dropper to a HV transformer bushing has failed and resulted in a fire to assets.  The supply to section supplying the pole transformer was isolated and repairs/replacement of the transformer was instigated.",null,null," - overhead conductor (bare; copper)"]
[17,5,"2022-08-16","07:44:49",-38.139763438000003,145.12046348999999,"4 Beach St, Frankston VIC 3199, Australia",3309169,"FTN14","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1643379,"20220817UTD_01","In response to a call of a pole fire, the attending fault crew found a LV Fused Switch Disconnector (Krone Box) had failed and caught fire. There was also debris from the failed FSD at the base of the pole. The supply to the FSD was isolated and the FSD replaced. ",null,null," - overhead conductor (bare; steel)"]
[17,6,"2022-08-21","15:11:00",-37.866194944999997,145.03791594,"54 Wheatland Rd, Malvern VIC 3144, Australia",9866617,"CFD16","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1644801,"20220822UTD_01","In response to a call for no supply, the attending fault crew found a LV Fused Switch Disconnector (Krone Box) had failed and caught fire. The supply to the FSD was isolated and the FSD replaced. ",null,null," - overhead conductor (ABC)"]
[17,7,"2022-08-22","15:51:35",-37.913244689000003,144.99597115,"21 Black St, Brighton VIC 3186, Australia",1803328,"NB 31","11kV AC","Urban"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1645113,"20220823UTD_01","UE received a report of a tree on fire, and in contact with powerlines. On attendance, the fault crew found the fronds from a private tree was growing into the OH HV lines and had caught fire. The attending fault crew cut the offending branch away from the OH HV lines.",null,null," - overhead conductor (covered uninsulated)"]
[17,8,"2022-08-24","19:40:34",-37.803170080999998,145.11761523000001,"600 Elgar Rd, Box Hill North VIC 3129, Australia",7001738,"DC 05","Low voltage AC (<1kV)","Urban"," - lamps (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1645777,"20220825UTD_01","UE received a report from the fire authority that a street light had caught fire. On arrival a 250HP Sodium head showed significant fire damage. The attending fault crew disconnected and removed the failed street light which was subsequently replaced",null,null," - overhead conductor (insulated)"]
[17,9,"2022-09-05","09:14:00",-38.362171576000001,144.77999126,"5 St Johns Wood Rd, Blairgowrie VIC 3942, Australia",1302640,"STO23","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1647931,"20220906UTD_01","In response to a call from the fire authority of a pole sparking, the attending UE fault crew found an 3 phase LV FMB had caught fire.  The supply to the pole was isolated and works to replace the damaged equipment were instigated",null,null,"Service lines"]
[17,10,"2022-09-08","23:11:32",-37.976917571999998,145.06718518,"25 Nepean Hwy, Mentone VIC 3194, Australia",1812700,"M 31","11kV AC","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1649072,"20220909UTD_01","In response to a feeder reclose event and a customer reporting pole on fire, it was found that a manual gas switch had failed and flashed over between bushings. The section of HV was isolated and the gas switch was replaced under access permit conditions.",null,null," - overhead service conductor (residential)"]
[17,11,"2022-09-15","18:38:00",-38.332580776999997,145.12704337,"467 Stumpy Gully Rd, Balnarring VIC 3926, Australia",1106146,"HGS22","Low voltage AC (<1kV)","Rural"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.05,0.05,1650524,"20220919UTD_01","On report of a fire on a pole, the attending UE fault crew found a pole mounted FOLCB had failed and caught fire.  The damaged FOLCB was replaced.",null,null," - overhead service conductor (commercial / industrial)"]
[17,12,"2022-09-16","19:47:18",-38.383827138999997,145.02198426999999,"122 Shoreham Rd, Red Hill VIC 3937, Australia",1307982,"DMA15","22kV AC","Rural"," - transformer (pole mounted)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"No forecast",0.05,0.05,1650816,"20220926UTD_02","On report of a fire on a pole, the attending UE fault crew found a possum had caused a fault/flashover and likely caught fire resulting in operation of a HV fuse on a transformer. The possum was removed from site and the fuse replaced",null,null," - overhead service conductor (subdivision / construction)"]
[17,13,"2022-09-17","18:28:00",-38.058649279999997,145.12421014,"40A Broadway, Bonbeach VIC 3196, Australia",3306136,"CRM15","Low voltage AC (<1kV)","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1650923,"20220926UTD_01","On report of a pole on fire, the attending UE fault crew found an LV Cu/Al connector had failed. The connector was replaced",null,null," - overhead service conductor (other)"]
[17,14,"2022-09-18","16:43:00",-38.375003956,144.83016380999999,"37A Hygeia St, Rye VIC 3941, Australia",1300992,"STO23","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1651008,"20220919UTD_04","On attendance to a report of a fire on a pole, the UE fault crew found a LV FMB on the pole had failed and caught fire.  The FMB was replaced.",null,null," - underground service cable (residential)"]
[17,15,"2022-09-21","02:16:33",-38.377474415999998,144.92556377,"380 Waterfall Gully Rd, Rosebud VIC 3939, Australia",1311322,"RBD24","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1651517,"20220926UTD_06","In response to a call of a fire on a pole, the attending UE fault crew found a pole mounted FMB had failed and caught fire. The failed FMB was replaced",null,null," - underground service cable (commercial / industrial)"]
[17,16,"2022-09-23","02:02:31",-38.401419828999998,144.95253679999999,"4A Browns Rd, Main Ridge VIC 3928, Australia",1308729,"RBD12","22kV AC","Rural"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.05,0.05,1651855,"20220926UTD_07","In response to an ACR reclose event, the patrolling UE crew found a  HV BA fuse had candled. The failed HV BA fuse was replaced",null,null," - underground service cable (subdivision / construction)"]
[17,17,"2022-09-24","15:17:03",-38.379036677999999,145.04472414,"45 Thomas Rd, Red Hill South VIC 3937, Australia",1308466,"DMA15","Low voltage AC (<1kV)","Rural"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.05,{"$f":"IF(OR(P54=\"\",R54=\"\"),\"\",IF(AND(O54=\"within electric line construction area\",Q54=\"No forecast\"),1,P54*R54))","v":0.05},1651978,"20220926UTD_04","On report of a supply outage, the attending UE fault crew found a single phase pole mounted FMB had failed and caught fire. The FMB was replaced",null,null," - underground service cable (other)"]
[17,18,"2022-09-25","10:47:00",-37.982314832999997,145.22318267,"14 Sunnyside Ave, Dandenong VIC 3175, Australia",625977,"LD7","Low voltage AC (<1kV)","Urban"," - transformer (pole mounted)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1652055,"20220926UTD_03","UE received reports of high volts on customer installations. On attendance, the UE fault crew found the distribution pole transformer neutral had failed and caused LV injection into properties supplied from this transformer.  The fault caused a fire at a customers swirtchboard.",null,null,"Underground cables"]
[17,19,"2022-10-05","09:02:17",-37.892488274000002,145.23200342000001,"8 Barry Ct, Scoresby VIC 3179, Australia",619620,"BRA21","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1654566,"20221007UTD_02","In response to call from fire authority, attending crews found a private palm tree had grown into the HV lines and had caught fire. The section of line was de-energised and the palm tree cut back from the OH HV conductors. ",null,null," - underground cable"]
[17,20,"2022-10-05","09:45:00",-38.381266773,144.88866480999999,"208 Boneo Rd, Rosebud VIC 3939, Australia",1315779,"RBD-STO #1","66kV AC","Rural"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1654601,"20221007UTD_01","In response to sub-transmission protection operation, patrolling fault crews found a branch from a pine tree located outside regulatory clearances had broken and fallen onto the bare OH lines and had caught fire. The sections of lines were de-energised and the branch removed.",null,null," - underground communications cable"]
[17,21,"2022-10-06","08:42:47",-38.099297548999999,145.15966261,"78S Frankston Gardens Dr, Carrum Downs VIC 3201, Australia",9653144,"CRM34","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1654848,"20221007UTD_03","In response to a call from the fire authority, the attending UE fault crew found a LV Fused Switch Disconnector (krone box) had failed on one phase and caught fire. The burnt out krone box was replaced.",null,null,"Poles"]
[17,22,"2022-10-06","18:52:42",-38.378659048999999,144.79615537000001,"45 Hogan Dr, Rye VIC 3941, Australia",1303407,"STO21","Low voltage AC (<1kV)","Rural"," - underground service cable (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1655035,"20221010UTD_01","A UE installed service fuse holder for a property with an Underground supply was found burnt out. The fuse holder was replaced.",null,null," - pole (concrete)"]
[17,23,"2022-10-14","22:54:45",-37.837837665999999,145.12223191000001,"18 Linden St, Box Hill South VIC 3128, Australia",7038697,"BH 31","Low voltage AC (<1kV)","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1656451,"20221017UTD_02","A branch from customer tree brought down an LV cond to the ground alive, this conductor also contacted an Optus cable which caused melted particles to fall on a car parked underneath which caused the bonnet protector to ignite briefly damaging the car. Car owner notified & LV repaired ",null,null," - pole (steel)"]
[17,24,"2022-10-15","12:50:02",-37.901142014000001,144.99430998,"3 Orchard St, Brighton VIC 3186, Australia",2307796,"NB 34","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1656521,"20221017UTD_01","A single phase transformer LV Fused Switch Disconnector (Krone switch) failed at the connection with transformer lead and caught fire. The attending fault crew replaced the single phase FSD",null,null," - pole (wood)"]
[17,25,"2022-10-22","21:16:21",-37.989313590999998,145.08946441000001,"38 Clare St, Parkdale VIC 3195, Australia",1808661,"M  13","11kV AC","Urban"," - pole (wood)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1658398,"20221024UTD_01","On report from fire authority of a pole fire, the attending crew found a pole had burnt at the kingbolt near the HV cross-arm.  The section of HV circuit was isolated and repairs instigated.",null,null,"Crossarms"]
[17,26,"2022-10-27","10:27:23",-37.920165914999998,145.15007890000001,"9 Anzed Ct, Mulgrave VIC 3170, Australia",9674781,"SV 23","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1659570,"20221028UTD_01","On receiving a report of a box on a pole on fire, the attending UE fault crew found a LV Fused Switch Disconnector (Krone switch) failed at the connection with transformer lead and caught fire.  The attending fault crew replaced the FSD",null,null," - crossarm (wood)"]
[17,27,"2022-10-27","18:12:57",-37.766696736999997,145.07976579999999,"15 Ilma Ct, Bulleen VIC 3105, Australia",9910864,"WD 36","Low voltage AC (<1kV)","Urban"," - services pit","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1659719,"20221031UTD_01","A customer called advising of flames from a pit which burnt a nearby bush. The attending UE fault crew isolated the supply to the pit and instigated repairs to the UG cable.",null,null," - crossarm (steel)"]
[17,28,"2022-11-02","14:11:14",-38.001221661999999,145.24923378,"20 Doveton Ave, Eumemmerring VIC 3177, Australia",616421,"DN22","22kV AC","Urban"," - fuse (powder filled)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1660772,"20221103UTD_01","In response to supply issues, the UE fault crew found a HV PF fuse had candled. The damaged fuse was replaced.",null,null," - crossarm (other)"]
[17,29,"2022-11-04","14:10:00",-37.966154516000003,145.05561890000001,"326-330 Charman Rd, Cheltenham VIC 3192, Australia",1822809,"M 32","Low voltage AC (<1kV)","Urban"," - connector / termination","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1661324,"20221107UTD_01","In response to a customer report of a pole fire, the attending UE fault crew found a insulating piercing connector had failed and likely caught fire during the failure process. The faulty insulating piercing connector was replaced",null,null,"Overhead assets"]
[17,30,"2022-11-07","10:49:00",-38.161589593000002,145.16680389999999,"1 Mornington Peninsula Fwy, Langwarrin VIC 3910, Australia",8816015,"FTS-FTN 66kV","66kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"No forecast",0.05,0.05,1661690,"20221108UTD_02","It appears a crow/raven caused a flash between the Blue phase and earth on the 66kV pole and dropped to the ground and started a ground fire. The feeder CB reclosed and held. Assets at the pole were inspected for any damage.",null,null," - capacity balancing units"]
[17,31,"2022-11-08","23:30:47",-38.374685970999998,144.88301609999999,"16 Curlew Dr, Capel Sound VIC 3940, Australia",1311872,"RBD11","22kV AC","Urban"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1662214,"20221109UTD_01","In response to a call stating there was a fire, the attending UE fault crew found a HV fuse on a cable head pole had candled. The section of HV circuit was isolated and repairs instigated.",null,null," - connector / termination"]
[17,32,"2022-11-17","13:40:00",-37.824173619,145.17396794999999,"2 Caversham Ct, Nunawading VIC 3131, Australia",7048447,"NW 21","Low voltage AC (<1kV)","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1664533,"20221121UTD_01","A tree fell onto LV mains, breaking the pole and LV conductors. The upstream protection did not operate, with the conductor alive until crews arrived. The live conductors also were in contact with a parked car and caused burning to a small section on car body. LV was isolated and repairs instigated. ",null,null," - dropper / bridge"]
[17,33,"2022-11-22","08:56:08",-38.175665883000001,145.13926615,"233 Frankston - Flinders Rd, Frankston South VIC 3199, Australia",3320971,"FSH12","22kV AC","Rural"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1665953,"20221124UTD_01","In high winds, a customer tree failed at the root system and fell onto HV lines in the street and caught fire.   The section of line was isolated and attending fault crews removed the branch",null,null," - guy wire"]
[17,34,"2022-11-26","19:08:20",-38.023109310000002,145.14257176999999,"50 Pillars Rd, Bangholme VIC 3175, Australia",3307461,"CRM35","22kV AC","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1667097,"20221128UTD_03","The top connection of a HV fuse unit failed and caused a small grass fire at the base of the pole. The attending fault crew replaced the failed fuse unit.",null,null," - insulator tie wires / connections"]
[17,35,"2022-11-26","19:50:02",-38.299976115,145.19095064999999,"115 Marine Parade, Hastings VIC 3915, Australia",1108619,"HGS32","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1667108,"20221128UTD_02","In response to a feeder protection operation and on receiving a call of a branch on fire, attending fault crews found a branch had blown onto HV conductors and caught fire. The line was isolated and the branch was removed from the lines.",null,null," - insulators"]
[17,36,"2022-11-27","15:49:28",-37.968743044999997,145.24098855,"29 Regnans Ave, Endeavour Hills VIC 3802, Australia",8830116,"DN 13","Low voltage AC (<1kV)","Urban"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1667216,"20221128UTD_01","An LV pillar caught fire and burnt surrounding grassed area. Supply to the pillar was isolated and repairs instigated.",null,null," - tower"]
[17,37,"2022-12-03","13:30:40",-38.351757294000002,144.743593,"33 James St, Sorrento VIC 3943, Australia",1306488,"STO13","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.05,0.05,1668674,"20221205UTD_01","In response to a call of a pole on fire, the attending UE fault crew found a pole mounted 3 phase FMB had failed and caught fire and scorched approximately 1sqm of the grass under the pole. The failed FMB was replaced",null,null," - traction lines"]
[17,38,"2022-12-04","14:04:00",-38.075297601999999,145.1514382,"10 Robinson Rd, Carrum Downs VIC 3201, Australia",3316122,"CRM14","Low voltage AC (<1kV)","Rural"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,{"$f":"IF(OR(P75=\"\",R75=\"\"),\"\",IF(AND(O75=\"within electric line construction area\",Q75=\"No forecast\"),1,P75*R75))","v":0.33400000000000002},1668768,"20221205UTD_03","On attendance for a loss of supply, the UE fault crew found a pole mounted Fused Switch Disconnector (Krone Box) had failed and caught fire, with some minor burning on the grass at the base of the pole. The damaged FSD was replaced",null,null,"Underground assets"]
[{"$f":"COUNTA(C76:O76,Q76,T76:V76)","v":17},39,"2022-12-04","17:46:00",-37.988021797999998,145.08507195999999,"44 Evan St, Parkdale VIC 3195, Australia",1807738,"M  13","Low voltage AC (<1kV)","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O76=\"\",\"\",IF(O76=\"LBRA only\",0.2,IF(O76=\"HBRA only\",1,IF(O76=\"within electric line construction area\",19.8,IF(O76=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"Moderate",0.33400000000000002,6.6800000000000012E-2,1668787,"20221205UTD_04","An LV copper to aluminium bridge connector failed with molten material falling to the ground and burnt the grass at the base of the pole. The fault crew replaced the damaged bridge connector and conductor.",null,null," - LV pillar"]
[17,40,"2022-12-05","09:33:00",-37.775432403000003,145.07676171,"175 Bulleen Rd, Bulleen VIC 3105, Australia",7057126,"WD36","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1668930,"20221206UTD_01","In response to customer report that a tree branch had briefly caught on fire after falling onto power lines, the attending UE fault crew found a branch had fallen from a nearby tree onto the HV conductors and did show signs of burning. The branch was removed, supply restored",null,null," - services pit"]
[17,41,"2022-12-06","00:32:52",-37.982748512000001,145.07699557999999,"Thrift Park Shopping Centre/Lower Dandenong Rd, Mentone VIC 3194, Australia",1822650,"M  33","11kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1669148,"20221209UTD_03","During a period of weather change where there was misty rain, UE crews attended to a pole fire at the kingbolt holding the centre phase HV fuse holder bracket.  Emergency switching was performed to isolated the faulty section, and repairs were instigated to the pole",null,null,"Transformers"]
[17,42,"2022-12-08","00:07:00",-37.800709408000003,145.18373437,"150 Mitcham Rd, Donvale VIC 3111, Australia",7068008,"NW 13","22kV AC","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1669683,"20221209UTD_04","In response to a call of a pole fire, the attending UE fault crew found the connection of the lead to a HV fuse unit had burnt out. Emergency switching was undertaken to isolate the faulty section, and repairs instigated to the lead and connect to the HV fuse unit",null,null," - transformer (pole mounted)"]
[17,43,"2022-12-27","18:55:00",-38.331928214000001,144.97674623,"1A Palm Grove, Dromana VIC 3936, Australia",1311525,"DMA21","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1673121,"20230106UTD_01","On attendance for a loss of supply, the UE fault crew found a pole mounted Fused Switch Disconnector (Krone Box) had failed and caught fire. The damaged FSD was replaced",null,null," - transformer (kiosk mounted)"]
[17,44,"2022-12-27","20:38:00",-38.336205292000002,144.98163253999999,"14 Lugano Ave, Dromana VIC 3936, Australia",1317650,"DMA13","Low voltage AC (<1kV)","Rural"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1672967,"20230106UTD_02","LV Conductor has failed adjacent to a copper/aluminium \"D\" connection from one pole and still connected to the other. resting in a tree, can't be touched yet but could fall completely. there was a fire on the ground, but it's been put out now.",null,null," - transformer (ground outdoor mounted)"]
[17,45,"2022-12-27","21:51:27",-37.957015149999997,145.00822790000001,"161 State Route 33, Sandringham VIC 3191, Australia",1817437,"SR 11","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1673107,"20230106UTD_03","In response to a call of a pole on fire, the attending UE fault crew found a pole mounted 3 phase FMB had failed. ",null,null," - transformer (indoor chamber mounted)"]
[17,46,"2022-12-29","01:17:55",-37.993934113000002,145.16920074000001,"Stanley Rd/Cheltenham Rd, Keysborough VIC 3173, Australia",638926,"KBH34","Low voltage AC (<1kV)","Urban"," - lamps (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1673272,"20230106UTD_04","Attending to report of a pole one fire a crew discovered that a 150w HP Sodium streetlight head had caught fire. The crew replaced the streetlight head and re wired streetlight bracket. ",null,null," - transformer (any other type)"]
[17,47,"2022-12-31","15:49:55",-37.967651834999998,145.15400407000001,"41 Olympic Ave, Springvale South VIC 3172, Australia",632187,"NP 23","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1673524,"20230106UTD_05","During a period of weather change where there was misty rain, UE crews attended to a pole burnt through between the 2 HV Xarm (Brown fog type insulators).  Pole was replaced",null,null," - measurement transformer (current transformer)"]
[17,48,"2023-01-04","17:57:47",-38.143465589000002,145.16231604000001,"Gretana Cres reserve, Gretana Cres, Frankston VIC 3199, Australia",3319081,"LWN24","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1674128,"20230130UTD_01","During light rain drizzly conditions, a crossarm fire occurred at the strap bolt on the HV cross-arm. The section of line was isolated and the damaged cross-arm replaced. ",null,null," - measurement transformer (voltage transformer)"]
[17,49,"2023-01-05","00:57:47",-37.993619633000002,145.22212754,"19A Wedge St, Dandenong VIC 3175, Australia",628547,"DN 06","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1674156,"20230130UTD_03","During light rain drizzly conditions, a pole fire occurred at the king bolt with the HV cross-arm. The section of line was isolated and the damaged cross-arm replaced.",null,null," - measurement transformer (capacitive voltage transformer)"]
[17,50,"2023-01-08","19:39:39",-37.889350555999997,145.10760311999999,"554 State Route 47, Chadstone VIC 3148, Australia",2325296,"OAK21","11kV AC","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1674569,"20230131UTD_06","An initial fault on an ug cable seems to have caused a seco.ndary fault at a HV tee off bridge where repairs were required. No obvious fire on the UE asset however small scorch marks s below indicated likely molten metal ignited grass. Connection repaired under A/P supply restored.",null,null,"Fuses and switchgear"]
[17,51,"2023-01-11","10:44:38",-38.412784137000003,144.88705898000001,"582 Boneo Rd, Boneo VIC 3939, Australia",1312478,"RBD21","22kV AC","Rural"," - dropper / bridge","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1675176,"20230130UTD_04","UE received a report from the fire authority that a bird had shorted across conductors and caused a small grass fire at the base of the pole. On attendance, the UE fault crew found a bird had shorted across the terminals of  a gas switch and fell to the ground. Switch was replaced",null,null," - fuse (boric acid)"]
[17,52,"2023-01-11","12:42:50",-38.389365108,145.09086354999999,"1 Merricks Rd, Merricks VIC 3916, Australia",1108488,"MTN32","22kV AC","Rural"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1675214,"20230131UTD_05","Local CFA reported a car into a pole which caused a failure of the HV conductors.  The resulting contact with the grass underneath resulted in several small spot fires. Conductors restrung - supply restored.",null,null," - fuse (EDO fuse)"]
[17,53,"2023-01-11","21:31:35",-38.477855247000001,145.00694591999999,"12 Vale St, Flinders VIC 3929, Australia",8831557,"RBD21","Low voltage AC (<1kV)","Rural"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1675323,"20230131UTD_07","In response to a call from CFA of a pole on fire, the attending UE fault crew found a pole mounted 3 phase FMB had failed. The resulting debris scorched several sections of grass underneath. FOLCB replaced - supply restored",null,null," - fuse (Fault Tamer)"]
[17,54,"2023-01-17","11:10:37",-37.896430488999997,144.98985726999999,"394 State Route 33, Brighton VIC 3186, Australia",2307957,"EW 14","Low voltage AC (<1kV)","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,1676471,"20230131UTD_08","Emergency services reported a truck has hit optus causing it to flick up into the LV mains and the resultant flash over caused the conductor to fail. . Conductors restrung - supply restored.",null,null," - fuse (powder filled)"]
[17,55,"2023-01-17","18:59:00",-38.285770192999998,145.00132690999999,"2 Spencer St, Mount Martha VIC 3934, Australia",1314542,"DMA14","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,1676636,"20230202UTD_01","CFA advised of a grass fire underneath a pole.  On arrival the crew discovered this was likely caused by a loose connection dropping molten metal from the load side U-bolt on red phase LV fused isolator. Replaced Isolator and damaged cable - supply restored.",null,null," - fuse (any other type)"]
[17,56,"2023-01-17","20:00:05",-38.078567935000002,145.13691929999999,"8 Palm Beach Dr, Patterson Lakes VIC 3197, Australia",8817946,"CRM23","22kV AC","Urban"," - transformer (ground outdoor mounted)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,1676653,"20230202UTD_02","UE crew responded to customer reports of an explosion and fire. On arrival a Kiosk type substation was well alight with FRV crews on site dousing the flames.  The cause of the ignition is believed to be a lightning strike however this is still under investigation.",null,null," - circuit breaker"]
[17,57,"2023-01-17","20:01:30",-37.948661027,145.01401332,"21 Hobson St, Sandringham VIC 3191, Australia",1818417,"SR 20","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,1676655,"20230202UTD_03","FRV advised that a council tree branch had brought down a service line and there was a small fire. On arrival the crew disconnected fire damaged service and customer FMB. Crew issued a customer defect on FMB and replaced service.",null,null," - switch (disconnector/isolator)"]
[17,58,"2023-01-23","10:37:03",-37.969391528000003,145.01197589,"248 State Route 33, Black Rock VIC 3193, Australia",1817496,"BR 13","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1678003,"20230202UTD_04","FRV notified UE of flames emanating from a box on the pole.  On arrival the crew replaced a fire damaged 3 phase FMB.  FMB replaced supply restored  ",null,null," - switch (earth)"]
[17,59,"2023-01-23","18:42:06",-38.038774064000002,145.21076241,"Colemans Rd/Frankston-Dandenong Rd, Dandenong South VIC 3175, Australia",3470119,"DVY12","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1678121,"20230202UTD_05","FRV reported a car had struck a pole and wires hit the ground igniting a grass fire.  On arrival the crew confirmed HV conductors on deck.  Conductors repaired - supply restored",null,null," - switch (FuseSaver)"]
[17,60,"2023-01-24","21:25:00",-37.880282905999998,144.97968900000001,"42 Shelley St, Elwood VIC 3184, Australia",2306154,"EW 12","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1678441,"20230202UTD_07","On attendance for FRV reported pole fire, the UE fault crew found a pole mounted Fused Switch Disconnector (Krone Box) had failed and caught fire. The Krone box was replaced. Supply restored",null,null," - switch (any other type)"]
[17,61,"2023-01-25","18:41:00",-38.171261786999999,145.13825245000001,"190 Frankston - Flinders Rd, Frankston South VIC 3199, Australia",3311124,"FSH13","Low voltage AC (<1kV)","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1678692,"20230202UTD_08","Customer reports sparks from pole ignited grass which she extinguished. On arrival the crew discovered a white phase transformer lead had failed at the CU/Al connection. Crew replaced lead and CU/AL clamp.",null,null,"SCADA, network control and protection systems"]
[17,62,"2023-01-26","08:32:25",-38.192412159,145.11491437999999,"68-70 Mather Rd, Mount Eliza VIC 3930, Australia",3311089,"FSH33","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1678821,"20230202UTD_09","Customer advised sparks from pole.  On arrival crew discovers a small ground fire emanated from molten metal falling from a failed isolator connection.  The isolator was replaced.",null,null," - audio frequency load controller (AFLC)"]
[17,63,"2023-01-28","14:30:16",-38.093035215999997,145.17828718999999,"1 Luscombe Ave, Carrum Downs VIC 3201, Australia",3317115,"CRM14","22kV AC","Rural"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,1679102,"20230202UTD_10","FRV reported lines down.  On arrival the crew discovered there had been a significant flashover with 2 x flexes burnt off (blue & white phases) and all 3 boric acid fuse units damaged (broken porcelain sheds) causing a grass fire at the base of pole. All damaged equipment replaced.",null,null," - arc suppresion coil"]
[17,64,"2023-02-01","14:02:42",-37.950068094999999,145.04762253999999,"1 Sandford St, Highett VIC 3190, Australia",1815650,"SR 15","22kV AC","Urban"," - fuse (powder filled)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1679934,"20230203UTD_01","Attending a report of low volts, a UE crew discovered a candling powdered filled S/Stn fuse.  The fuse was replaced supply restored.",null,null," - automatic circuit recloser (ACR)"]
[17,65,"2023-02-02","09:43:14",-37.903618835000003,145.16316039,"580 Springvale Rd, Wheelers Hill VIC 3150, Australia",607923,"MGE34","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,1680166,"20230209UTD_01","Crew attended a report of powerlines on fire. On attendance the crew discovered a small branch had fallen onto the HV conductors and the damage to branch indicated it had caught on fire at some point. Slight flash marks also on HV conductors. Crew removed branch from conductors.",null,null," - communications linear assets"]
[17,66,"2023-02-06","13:52:00",-38.374646925999997,145.05140255000001,"101 Stanleys Rd, Red Hill South VIC 3937, Australia",1318468,"DMA15","22kV AC","Rural"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",{"$f":"IF(Q103=\"\",\"\",IF(C103>=DATE(2022,9,1),IF(Q103=\"No forecast\",0.05,IF(Q103=\"Moderate\",0.334,IF(Q103=\"High\",0.678,IF(Q103=\"Extreme\",2.272,4.754)))),0.05))","v":0.33400000000000002},0.33400000000000002,1681160,"20230302UTD_03","Crew were called to an outage and on arrival discovered that a 6Amp B/A fuse had candled. The fuse was replaced and supply restored.",null,null," - communications network assets"]
[17,67,"2023-02-06","20:37:08",-38.113548174999998,145.14298836,"11 Apsley Pl, Seaford VIC 3198, Australia",3309300,"FTN12","Low voltage AC (<1kV)","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1681232,"20230309UTD_03","A customer reported witnessing a flame on the wiring on pole. On arrival the crew discovered a failed copper to aluminium connected which was the likely source of the flame.  The crew replace the lead and connection.",null,null," - communications site infrastructure"]
[17,68,"2023-02-06","22:56:11",-37.968598739000001,145.12719915,"27 McClure Rd, Dingley Village VIC 3172, Australia",607519,"SS 23","22kV AC","Urban"," - surge diverter","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1681247,"20230309UTD_04","Customer advised of a loud bang and a small fire on a pole.  On arrival crew discovered that the surge arrestors were blackened and had blown leads possibly confirming a small flame was evident at some point.  The surge arresters were cut clear and programmed for replacement.",null,null," - field devices"]
[17,69,"2023-02-12","09:09:33",-38.325042138999997,144.71455628999999,"9 Leyden Ave, Portsea VIC 3944, Australia",1307294,"STO13","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1682848,"20230309UTD_05","Crew were called to customer reports of a sparking and smoking from the pole top. On arrival the discovered a burnt out grey twisted service and a burn mark on the pole from a likely small fire.  The service was replaced.",null,null," - local network wiring assets"]
[17,70,"2023-02-16","17:24:00",-38.168671822,145.18795585000001,"188 Warrandyte Rd, Langwarrin VIC 3910, Australia",3310336,"FSH21","Low voltage AC (<1kV)","Rural"," - overhead conductor (bare; aluminium core steel reinforced)","single phase","Started in or originated from a distribution system","HBRA only",1,"High",0.67800000000000005,{"$f":"IF(OR(P107=\"\",R107=\"\"),\"\",IF(AND(O107=\"within electric line construction area\",Q107=\"No forecast\"),1,P107*R107))","v":0.67800000000000005},1684431,"20230309UTD_07","Possible LV conductor failure at bridge caused molten metal to fall to the base of the pole causing a small area of grass to singe. The bridge and conductor was repaired and supply restored.",null,null," - master station assets"]
[17,71,"2023-02-17","00:20:26",-38.373300579999999,144.82756938,"19 Bimble St, Rye VIC 3941, Australia",1301778,"STO23","Low voltage AC (<1kV)","Urban"," - lamps (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,1684475,"20230309UTD_01","A UE crew were called by the fire authority to a pole in the middle of the roundabout where a 150W Sodium street light head has caught on fire. Street Light was replaced",null,null," - neutral earthing resistor"]
[17,72,"2023-02-17","12:16:38",-38.391765810000003,144.79952936000001,"61 Heyfield Rd, Rye VIC 3941, Australia",1305571,"STO21","Low voltage AC (<1kV)","Rural"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"Extreme",2.2719999999999998,2.2719999999999998,1685069,"20230307UTD_01","On attendance for abnormal voltage detected a UE fault crew found a 3-phase pole mounted FMB had failed and dropped melted plastic on the ground which started a small grass fire caught fire. The FBB box was replaced. Supply restored.",null,null," - oil-filled circuit recloser (OCR)"]
[17,73,"2023-02-17","15:30:51",-37.828442991999999,145.1609819,"Gardiner's Creek Headwaters, Lake Rd, Blackburn VIC 3130, Australia",7032995,"NW 21","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Extreme",2.2719999999999998,0.45439999999999997,1684787,"20230228UTD_01","Crew arrived to a report of tree on conductor had started a fire. On arrival a council  tree in Gardiners Creek reserve had shed a limb onto HV conductors starting a small 10sqm ground fire.  Conductors repaired supply restored.",null,null," - rapid earth fault current limiter (REFCL)"]
[17,74,"2023-02-20","05:33:23",-37.819060903,145.16586129000001,"8 Burleigh Ct, Nunawading VIC 3131, Australia",7036611,"NW 32","Low voltage AC (<1kV)","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1685272,"20230302UTD_01","Crew were called to an incident where a garbage truck lifted a large skip type bin into above lv overhead conductors. Bin and contents in bin caught fire. FRV in attendance and fire extinguished upon arrival. Overhead conductors on the neutral and blue phases are damaged and have been sleeved out with new conductor. ",null,null," - surge diverter"]
[17,75,"2023-02-25","11:26:56",-37.789934422000002,145.10831107000001,"12 Ruda St, Doncaster VIC 3108, Australia",7055339,"WD 14","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.67800000000000005,0.13560000000000003,1686930,"20230309UTD_02","FRV reported a possible grassfire possibly caused by UE assets. On arrival the crew replaced burnt out white phase isolator and 185mm lead at a substation from overheated connection. Isolator was replaced.",null,null," - voltage regulator"]
[17,76,"2023-02-28","16:33:25",-37.978554975000002,145.14762171000001,"1 Paterson Rd, Springvale South VIC 3172, Australia",631760,"NP 12","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1687943,"20230302UTD_02","Crew were called by FRV to a HV crossarm fire. On arrival they discovered leakage from the road side HV grey fog insulator had caused the end of the crossarm to catch on fire and eventually fail.  Crossarm was replaced under A/P and supply restored.",null,null,"Public lighting"]
[17,77,"2023-03-24","00:46:02",-37.814858579999999,145.19229200000001,"13 Edward St, Mitcham VIC 3132, Australia",7040036,"RWT23","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1694135,"20230501UTD_01","UE received a report of FRV enroute to a believed pole and possibly a tree fire. On arrival the crew discovered a possum on conc pole caused wrap on to fail and conductor landed in a tree. Although no real evidence of fire there was likely some flame at one point due to the initial reports. Conductor repaired supply restored",null,null," - brackets (major road)"]
[17,78,"2023-03-26","12:47:00",-37.996713919999998,145.07371911000001,"10 Monaco St, Parkdale VIC 3195, Australia",1808834,"M  35","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1694606,"20230404UTD_07","A UE crew attended a report of a fire at the top of a pole. On arrival the crew discovered that a 3-phase FMB had failed and caught fire. The FMB was replaced supply restored",null,null," - brackets (minor road)"]
[17,79,"2023-03-27","03:26:43",-37.884809687000001,145.14594768000001,"380 Blackburn Rd, Glen Waverley VIC 3150, Australia",604079,"GW 08","22kV AC","Urban"," - surge diverter","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1694654,"20230501UTD_02","Crew were called to reports of a pole fire. On arrival they discovered a possum have bridged surge arrestor and conc pole. Although no real evidence of fire there was likely some flame at one point due to the initial reports. The surge arrestors were cut clear and are programmed for removal.",null,null," - lamps (major road)"]
[17,80,"2023-03-27","09:19:19",-37.982687706999997,145.07348590000001,"Unit 7/224 Nepean Hwy, Parkdale VIC 3195, Australia",1809106,"M  25","11kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1694726,"20230404UTD_04","FRV reported to UE a pole on fire, on arrival the crew discovered a frond from a customer's Palm tree had contacted the HV and briefly ignited. The Palm fronds were cut clear by a G@B crew.",null,null," - lamps (minor road)"]
[17,81,"2023-03-27","19:45:03",-38.021979842999997,145.22125731,"50-56 Nissan Dr, Dandenong South VIC 3175, Australia",9579967,"DVY32","22kV AC","Urban"," - underground cable","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1694898,"20230404UTD_06","A member of the public notified FRV of a pole fire who then notified UE. On arrival the UE crew discovered that a surge divertor lead had caught fire between the surge arrestor leads and the earth screen on HV UG cable on a Cable Head Pole (CHP). UE underground crew notified and rectified joint the next day.",null,null," - luminaires (major road)"]
[17,82,"2023-03-27","21:15:59",-38.187631562999997,145.22398713999999,"50 Mount Grandview Rd, Pearcedale VIC 3912, Australia",3300660,"FSH32","Low voltage AC (<1kV)","Rural"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1694919,"20230404UTD_03","A member of the public called the fire brigade to report a pole fire.  Although on there was no active fire on arrival the crew discovered a 3-phase Fused mains Box (FMB) was melted therefore there was a possibly of flames at one point. The FMB was replaced.",null,null," - luminaires (minor road)"]
[17,83,"2023-03-29","12:05:00",-37.777326688000002,145.16772675000001,"1 Dobell Pl, Doncaster East VIC 3109, Australia",7064589,"DC 10","Low voltage AC (<1kV)","Urban"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1695464,"20230404UTD_02","A UE crew were called to a pillar reported to be smoking.  On arrival the crew discovered the pillar was alight and extinguished with their fire extinguisher. A small amount of adjacent grass was singed. The crew arranged an underground crew to replace the pillar",null,null," - poles / columns (major road)"]
[17,84,"2023-03-29","20:03:51",-38.258645352999999,145.03505541999999,"14 Norman Rd, Mount Martha VIC 3934, Australia",9755974,"MTN24","22kV AC","Rural"," - capacity balancing units","three phase","Started in or originated from a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1695579,"20230404UTD_05","Found vacume switch at \"cap nepean inga\" cap bank burnt, isolated line and cut away droppers, taged pole with do not operate tag, all ok on completion. Fire ignition report attached Notification Number: 001000878648",null,null," - poles / columns (minor road)"]
[17,85,"2023-03-30","05:06:00",-37.889265989000002,145.04509075000001,"1227 Glen Huntly Rd, Carnegie VIC 3163, Australia",2328370,"CFD15","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1695629,"20230404UTD_01","UE crew responded to reports of pole fire from FRV, on arrival the crew discovered a 3-phase junction box displayed severe fire damage and a molten plastic singed grass on nature strip underneath. Replaced junction box and service.",null,null,"Other "]
[17,86,"2023-04-08","15:35:25",-38.475292480999997,144.98127393999999,"180 Punchbowl Rd, Flinders VIC 3929, Australia",1312758,"RBD21","22kV AC","Rural"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Moderate",0.33400000000000002,0.33400000000000002,1698796,"20230504UTD_01","Crew investigated reports of wire down in strong winds and on arrival discovered a road reserve Pine tree limb from outside clearance space had failed and brough down HV conductor igniting a small section of the branch. Conductor repaired supply restored.",null,null," - connection box"]
[17,87,"2023-04-11","12:17:25",-37.773899905,145.14294773,"25 Kolor Way, Templestowe VIC 3106, Australia",7060933,"DC 02","Low voltage AC (<1kV)","Urban"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Moderate",0.33400000000000002,6.6800000000000012E-2,1699453,"20230413UTD_01","Crew were called to reports of a pillar on fire, on arrival they discovered that pillar had caught fire and singed adjacent grass. Replaced service cable holders and fuse holders.",null,null," - earth / earthing"]
[17,88,"2023-05-07","23:27:16",-37.767547196999999,145.09553302,"2 William St, Bulleen VIC 3105, Australia",7068175,"BU 06","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1706448,"20230522UTD_01","Crew was call to reports of a transformer on fire. On arrival the crew replaced a burnt out 400Amp gang operated krone box.  Some falling material from the box singed grass underneath. Crew replaced with a 1000Amp krone box"]
[17,89,"2023-05-08","06:18:14",-38.033533067,145.19385362,"5-9 Licola Cres, Dandenong South VIC 3175, Australia",9953671,"DVY34","22kV AC","Urban"," - measurement transformer (capacitive voltage transformer)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1706489,"20230522UTD_03","Crew were called by FRV in relation to a possible transformer fire.  On arrival the fire had extinguished itself and was on a cap bank not a transformer.  It seems the HV connection onto the Cap Bank bushing had overheated and caught fire. Cap Bank isolated until repairs can be completed."]
[17,90,"2023-05-18","01:35:43",-37.779848047000002,145.18491179,"4 Mullum Dr, Donvale VIC 3111, Australia",7067132,"NW 13","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1709151,"20230522UTD_02","Isolated supply to premise after fire at meter board. Supply isolated in pit. Damaged meter removed. Defect issued and left at front door. 3 phase 504 ami meter will be required for reco. CIA. Fire report attached to job.",null,null,"Extra low voltage AC (<50V)"]
[17,91,"2023-05-27","08:23:56",-37.96828215,145.17601023,"7 Leonard Ave, Noble Park VIC 3174, Australia",628097,"NP 25","Low voltage AC (<1kV)","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1711841,"20230605UTD_05","Crew were called to FRV reports of a pole fire. On arrival the crew discovered melted material from a burnt-out IPC had landed on a manhole underneath. Although the crew reported \"minimal evidence of a fire start\" the molten droplets in conjunction with the initial FRV comments means there was likely flames at some point.The IPC was replaced",null,null,"Low voltage AC (<1kV)"]
[17,92,"2023-06-08","09:03:01",-38.370884765,144.82481442,"2507 Nepean Hwy, Rye VIC 3941, Australia",1301551,"RBD14","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1714880,"20230704UTD_03","A UE crew attended a report of a fire at the top of a pole. On arrival the crew discovered that a Krone box had failed and caught fire. The Krone Box was replaced supply restored",null,null,"2.2kV AC"]
[17,93,"2023-06-19","06:27:52",-37.960099532999998,145.07483797,"309-313 Warrigal Rd, Cheltenham VIC 3192, Australia",1813906,"HT10","22kV AC","Urban"," - transformer (ground outdoor mounted)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1717297,"20230621UTD_01","MFB called to advise t/x on fire, MFB attended. Ground type transformer was on fire when crew arrived. Tracking water also caused issue at hv/lv bushings. Transformer replaced- supply restored.",null,null,"6.6kV AC"]
[17,94,"2023-06-19","18:25:35",-37.858105193999997,145.13705325000001,"487 Highbury Rd, Burwood East VIC 3151, Australia",7039551,"EB 21","Low voltage AC (<1kV)","Urban"," - lamps (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.05,1.0000000000000002E-2,1717511,"20230704UTD_01","Crew were called to FRV reports of a streetlight on fire, on attendance they discovered a burnt out 150 Sodium head that showed severe charring.  Street light head replaced.",null,null,"11kV AC"]
[0,95,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"12.7kV AC (SWER)"]
[0,96,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"22kV AC"]
[0,97,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"33kV AC"]
[0,98,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"66kV AC"]
[0,99,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"132kV AC"]
[0,100,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"220kV AC"]
[0,101,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"330kV AC"]
[0,102,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",{"$f":"IF(OR(P139=\"\",R139=\"\"),\"\",IF(AND(O139=\"within electric line construction area\",Q139=\"No forecast\"),1,P139*R139))","v":""},null,null,null,null,null,"500kV AC"]
[{"$f":"COUNTA(C140:O140,Q140,T140:V140)","v":0},103,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(O140=\"\",\"\",IF(O140=\"LBRA only\",0.2,IF(O140=\"HBRA only\",1,IF(O140=\"within electric line construction area\",19.8,IF(O140=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":""},null,"","",null,null,null,null,null,"Extra low voltage DC (<120V ripple free)"]
[0,104,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Low voltage DC (<1.5kV)"]
[0,105,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"600V DC"]
[0,106,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"1500V DC"]
[0,107,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Earthing cable"]
[0,108,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,109,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,110,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"single wire earth return (SWER)"]
[0,111,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"single phase"]
[0,112,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"two phase"]
[0,113,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"three phase"]
[0,114,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,115,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,116,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Negligible: no ground fire"]
[0,117,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Localised: less than 10 sq.m"]
[0,118,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Small: 10 - 1000 aq.m"]
[0,119,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Medium: 1000 sq.m - 10 ha"]
[0,120,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Large: more than 10 ha"]
[0,121,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,122,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,123,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Started in or originated from a distribution system"]
[0,124,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system"]
[0,125,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system"]
[0,126,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Started by lightning striking a distribution system or a part of a distribution system "]
[0,127,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Started by any other thing forming part of or coming into contact with a distribution system"]
[0,128,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,"Otherwise started by a distribution system"]
[0,129,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,130,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,{"$f":"IF(Q167=\"\",\"\",IF(C167>=DATE(2022,9,1),IF(Q167=\"No forecast\",0.05,IF(Q167=\"Moderate\",0.334,IF(Q167=\"High\",0.678,IF(Q167=\"Extreme\",2.272,4.754)))),0.05))","v":""},""]
[0,131,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,1]
[0,132,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,2]
[0,133,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,3]
[0,134,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",{"$f":"IF(OR(P171=\"\",R171=\"\"),\"\",IF(AND(O171=\"within electric line construction area\",Q171=\"No forecast\"),1,P171*R171))","v":""},null,null,null,null,null,4]
[0,135,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,5]
[0,136,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,6]
[0,137,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,7]
[0,138,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,8]
[0,139,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,9]
[0,140,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,10]
[0,141,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,{"$f":"Y177+1","v":11}]
[0,142,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,{"$f":"Y178+1","v":12}]
[0,143,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,13]
[0,144,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,14]
[0,145,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,15]
[0,146,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,16]
[0,147,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,17]
[0,148,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,18]
[0,149,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,19]
[0,150,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"","",null,null,null,null,null,20]
[0,151,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,152,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,153,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,154,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",{"$f":"IF(OR(P191=\"\",R191=\"\"),\"\",IF(AND(O191=\"within electric line construction area\",Q191=\"No forecast\"),1,P191*R191))","v":""}]
[0,155,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,156,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,157,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,158,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,159,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,160,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C198:O198,Q198,T198:V198)","v":0},161,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C199:O199,Q199,T199:V199)","v":0},162,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,163,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,164,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,165,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,166,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,167,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(O204=\"\",\"\",IF(O204=\"LBRA only\",0.2,IF(O204=\"HBRA only\",1,IF(O204=\"within electric line construction area\",19.8,IF(O204=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":""},null,"",""]
[0,168,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,169,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,170,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C208:O208,Q208,T208:V208)","v":0},171,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C209:O209,Q209,T209:V209)","v":0},172,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,173,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,174,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,175,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,176,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,177,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,178,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,179,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,180,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,181,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,182,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,183,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C221:O221,Q221,T221:V221)","v":0},184,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C222:O222,Q222,T222:V222)","v":0},185,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,186,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,187,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,188,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,189,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,190,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,191,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,192,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,193,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,194,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,{"$f":"IF(Q231=\"\",\"\",IF(C231>=DATE(2022,9,1),IF(Q231=\"No forecast\",0.05,IF(Q231=\"Moderate\",0.334,IF(Q231=\"High\",0.678,IF(Q231=\"Extreme\",2.272,4.754)))),0.05))","v":""},""]
[0,195,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,196,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C234:O234,Q234,T234:V234)","v":0},197,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(O234=\"\",\"\",IF(O234=\"LBRA only\",0.2,IF(O234=\"HBRA only\",1,IF(O234=\"within electric line construction area\",19.8,IF(O234=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":""},null,"",{"$f":"IF(OR(P234=\"\",R234=\"\"),\"\",IF(AND(O234=\"within electric line construction area\",Q234=\"No forecast\"),1,P234*R234))","v":""}]
[{"$f":"COUNTA(C235:O235,Q235,T235:V235)","v":0},198,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(O235=\"\",\"\",IF(O235=\"LBRA only\",0.2,IF(O235=\"HBRA only\",1,IF(O235=\"within electric line construction area\",19.8,IF(O235=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":""},null,"",{"$f":"IF(OR(P235=\"\",R235=\"\"),\"\",IF(AND(O235=\"within electric line construction area\",Q235=\"No forecast\"),1,P235*R235))","v":""}]
[0,199,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,200,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]

{"sheet":"3. Systems and Audit","index":4,"n_rows":29,"n_cols":5,"rows_kept":29,"cut":false,"hidden":false,"merged":[[28,1,29,4],[3,5,3,6],[4,5,4,6],[5,5,5,6],[6,1,6,4],[9,1,9,4],[14,1,14,4],[10,1,10,4],[13,1,13,4],[12,1,12,4],[11,1,11,4]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"United Energy"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2022/23"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"United Energy must provide:"}]
[]
[null,"Table 4 - Information or reporting systems"]
[null,"   (1) Name of any IT system used to collect fire start data or fault event data - i.e. SCADA system, or fault reporting system"]
[null,"   (2) Whether the fire recording or fault recording process has been audited or complies with a relevant Australian or industry standard - Yes or No"]
[null,"   (3) List any relevant Australian or industry standards that the fire recording or fault recording process complies with"]
[null,"   (4) Whether the data entered into or removed from the IT system has been audited - Yes or No"]
[]
[]
[null,"Table 4: Information or reporting systems"]
[]
[null,"Information or reporting systems","Name","System Audited","Relevant Standards"]
[null,"System 1","Geographical Information System (GIS)","Yes","N/A"]
[null,"System 2","Distribution Management System (DMS)","Yes","N/A"]
[null,"System 3 "]
[null,"System 4"]
[null,"System 5"]
[null,"System 6"]
[null,"System 7"]
[null,"System 8"]
[]
[null,"The SGSPAA Internal Audit function undertakes a programme of work in accordance with the SGSPAA Group Internal Audit Plan. This internal audit activity covers elements of the systems and process used for capturing, recording and maintaining fire start data."]