## Summary of network options
All values in real $FY24 million
Options Considered | Network Capital Cost | Customer Connection Cost | Combined Cost | Comments
Option 1 - New 132/33kV STS at Site 1 looped into 132kV Feeder 92B Sydney North BSP - Lane Cove STSS | 188.487 | 28.3254 | 216.8124 | Not pursued further due to upstream network constraints and site rezoned as residential high rise.
Option 2 - New 132/33kV STS at Site 1 looped into 132kV Feeders 92A & 92B Sydney North BSP - Lane Cove STSS | 251.9725 | 28.3254 | 280.2979 | Not commercially feasible. Expensive 132kV connections and site rezoned as residential high rise.
Option 3 - New 132kV STSS at Site 3 and 132/33kV STS at Site 1 looped into 132kV Feeder 92B | 200.4899 | 28.3254 | 228.8153 | Not pursued further due to upstream network constraints and need to acquire two sites.
Option 4 - New 132/33kV STS at Site 1 tee connected at East Ryde Transition Point to 132kV Feeders 92G & 92J | 178.6483 | 28.3254 | 206.9737 | Site rezoned as residential high rise (updated value is considerably higher than initial assessment).
Option 5 - New 132/33kV STS at Site 2 tee connected at East Ryde Transition Point to 132kV Feeders 92G & 92J | 162.3074 | 12.204 | 174.5115 | Community impact reduced due to customers located in close proximity to this site.
Option 6 - New STS with expanded 132kV busbar at Site 1 tee connected to 132kV Feeders 92G & 92J | 186.104 | 28.3254 | 214.4294 | Site rezoned as residential high rise. 132kV cable egress issues to connect customers. | This site cannot accommodate an expanded STS. It will require additonal land.
Option 7 - New STS with expanded 132kV busbar at Site 2 tee connected to 132kV Feeders 92G & 92J | 169.7631 | 12.204 | 181.9672 | 132kV cable egress issues if customers get connected to 132kV feeder bays.
Option 8 - New 132kV STSS (expandable) at Site 1 looped into 132kV Feeder 92B | 179.2407 | 125.5386 | 304.7793 | Not pursued further due to upstream network constraints and site rezoned as residential high rise. | 132kV supply gives customers more capacity, but inversely the customers will have less space available to add load
Option 9 - New 132kV STSS (expandable) at Site 1 tee connected to 132kV Feeders 92G & 92J | 168.7962 | 125.5386 | 294.3347 | 132kV feeder bay capacity would be underutilised. Likely to have 132kV cable egress issues. | 132kV supply gives customers more capacity, but inversely the customers will have less space available to add load
Option 10 - New 132kV STSS (expandable) at Site 2 tee connected to 132kV Feeders 92G & 92J | 152.4553 | 105.8972 | 258.3525 | 132kV feeder bay capacity would be underutilised. Likely to have 132kV cable egress issues. | 132kV supply gives customers more capacity, but inversely the customers will have less space available to add load
Option 11 - New 132kV STSS (expandable) at Site 3 looped into 132kV Feeder 92B | 185.2794 | 180.7468 | 366.0262 | Site not suitable for big STSS. Expansion requires compulsory acquisition and national park land clearing. | Likely to have project delays. 132kV supply gives customers more capacity, but inversely the customers will have less space available to add load
Note that Options 4 to 7 are considered credible network options
Other options were initially considered but later disregarded. Refer to the comments column for details.
An allowance for contingency is included to consider that options are at planning stage. No site specific investigations or concept design work has been undertaken.

## How options are defined
| How options are defined | Comments
1 | Three substation arrangements to connect new customers
| A new 132/33KV Subtransmission Substation (STS) | No issues
| A new 132 KV Subtransmission Switching Station (STSS) | Not the preferred choice for data centre customers, which predominantly use 33kV input supply modules.
| A 132/33KV STS with expanded 132kV busbar | Multiple supply choices for customers
Arrangement to be adjusted to have no expansion of 132kV busbar
2 | Three connections to the upstream 132kV transmission network
| Loop into Feeder 92B (feeder corridor 1) | Capacity available to meet initial requirements. It requires twin 2000mm2 cable per phase to maintain feeder rating capacity.
| Loop into Feeders 92A & 92B (feeder corridor 1) | Cost prohibitive. It requires twin 2000mm2 cables per phase and per feeder to maintain feeder rating capacity.
| Tee connection from Feeders 92G & 92J (feeder corridor 2) | Capacity available to meet initial requirements. It requires single 2000mm2 cable per phase to maintain feeder rating capacity.
Note there are future capex requirements, which are common to all in terms of scope but different in terms of timing (sooner for connections to Feeder 92B or 92A/92B). They all assume a tee off from feeders 926 & 927 is feasible.
Additional notes
Looping into Feeder 92B requires cable connections capable to achieve 550MVA capacity.
New fibre optic links required
In the case of connections to Feeder 92B, the only feasible cut-in point is near sport grounds (i.e. Site 3)
Other locations are ruled out due to difficult access.
Approximate length of underground cables required is between 3.0 and 3.9kms
Looping into Feeders 92A & 92B require cable connections capable to achieve 550MVA capacity.
This capacity cannot be achieved with 4x132kV feeders in the same route. A second location is required to cut into the tower lines.
This will involve clearing of Lane Cove National Park land, requiring consultation/negotiations and impacting delivery time.
Cutting into both feeders will result in better management of 132kV load flows compared to cutting into one feeder only.
UGOH pole farm from cutting into both feeders will have negative visual impact against national park surroundings.
Approximate length of underground cables required is between 3.0 and 3.9kms
Tee off from Feeders 92G and 92J is feasible with single 2000mm2 cable. The 290MVA rating per feeder can be achieved with this arrangement.
No communication upgrades are required in this option.
Two 132kV underground cables are required (sngle 2000mm2 cable per phase). Approximate length is between 6.4 and 7.1kms
This will impact a large number of residents but this has been done previously.
3 | Three sites proposed to accommodate a substation
This site has been rezoned as residential high rise and its value has increased significantly. It could have limitations to accmmodate a substation with room for future expansion
Large site capable to accommodate any of the substation arrangements.
This site is too small for an STS but could be suitable for a small STSS. It is only an alternative to avoid the need ot twin 2000mm2 cables per phase to connect to the new Wallumatta STS.
Additional notes
Site 1
Site 2
Site 3
The combination of these parameters leads to 27 options, but:
Site 3 is a site only suitable to accommodate a small switching station
Site 1 is considerably more expensive and make connection to customers more expensive
Connections to Feeders 92A & 92B are considerable more expensive and will require additional augmentation sooner than the alternative
Connection to Feeder 92B will require additional augmentation sooner than the alternative to connect to Feeders 92G and 92J
Consideration of these barriers can simplify the analysis to 4 options
Two substation types: a 132/33kV STS or a 132/33kV with expanded 132kV busbar
Two sites: Site 1 or Site 2
One connection to 132kV network: connection to Feeders 92G and 92J

## Cashflow distribution
Cashflow distribution for Options 4 to 7
| 2025 | 2026 | 2027 | 2028 | 2029
Item
Acquisition of Property | 100%
Construction of a new 132/33kV subtransmission substation | 1% | 9% | 30% | 50% | 10%
Installation of 132kV feeder connections | 1% | 9% | 45% | 45%
Target Commissioning year is FY29

## Option 1
Option 1 - New 132/33kV STS at Site 1 looped into 132kV Feeder 92B Sydney North BSP - Lane Cove STSS
| New Assets |  | Quantity | Unit of Measure | Unit rate code | Description | Unit Rate ($FY22) | Cost ($FY22) | Escalation to $FY24 | Baseline - including contingency allowance and property update | Baseline including 40% contingency | Comments
Initial requirements (2025-2029)
Install a new 132/33kV STS (Wallumatta STS) with 3x120MVA transformers and 3x33kV switchgroups
|  | Acquisition of property to establish a new STS (Site 1) | 1 | each
|  | STS IDID 3x132/33Tx 9x132 18x33 expandable | 1 | each | [7 empty] | Provided by Estimating & Unit Rates (July 2024). It excludes the installation of a capacitor bank as well as civil works to for a 4th Tx bay
132kV connections to loop into Feeder 92B
|  | 3.2km x 2 x twin 2000mm2 cable per phase | 6.5 | km |  | 132kV Double Duct Bank 2000mm2 CU1 |  |  | 1.041 |  |  | Only feasible cut-in point to Feeder 92B is at Tower 53/54 near sports grounds. Other locations ruled out due to difficult access. Unit rate provided by Estimating & Unit Rates (July 2023).
|  | UGOH poles | 2 | each | SP_0243 | TM132UGOH |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV Joint Bays | 12 | each | SP_0255 | 132kV STJ (XLPE - XLPE) |  |  | 1.1225 |  |  | Assumes 2 x 132kV Joint Bays per km per circuit
|  | Allowance for Bore under M2 | 2 | each | N/A | M2 crossing Under Bore - 12 ducts |  |  | 1.041 |  |  | Based on actual cost of Horizontal Directional Drilling for Centenary Drive 132kV underbore (132kV ductline Chullora) completed in 2022. Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV terminations at substation site | 4 | each | SP_0235 | TM132IN |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
|  | National Park Clearing | 1 |  | N/A |  |  |  | 1.041 |  |  | Assume 25 large trees per 1000m2. No allowance for environmental approvals. This is required for the installation of 2 sets of UGOHs from the 132kV towerline. Unit rate provided by Estimating & Unit Rates (July 2023)
Communications upgrades
|  | OPGW cable installation on Feeder 92B | 25 | km | N/A |  |  |  | 1.041 |  |  | Based on cost estimates for OPGW cable installed in project SM-27603 (Replace Fdr 926 OHEW replacement with OPGW). Unit rates provided by Estimating & Unit Rates (July 2023)
18857128
[10 empty] | 188487005.8608 | 227176574.0405
Comments
This option is no longer considered feasible due to
Rating constraints at Feeder 92B due to additional loads at Lane Cove STSS which will reduce capacity available.
Under N-1 conditions, an overload will occur on tee connection 92A(2) to Macquarie Park Zone Substation. Additional project required to address this issue.
In addition, proposed site has been impacted by NSW Department of Planning, Housing and Infrastructure (DPHI) rezoning of Macquarie Park area. It is now available for residential high rise development.
This option involves:
Acquisition of property in the Macquarie Park area (Site 1)
Construction of a new 132/33kV subtransmission substation, comprising:
3 x 132/33kV 120MVA transformer units
New switchroom building to house circuit breakers and associated control/protection rooms
9 x 132kV indoor GIS circuit breakers
18 x 33kV indoor GIS cuircuit breakers
Installation of two 132kV feeder connections to loop into Feeder 92B, comprising:
Two 132kV Underground to Overhead connection (UGOH) pole structures to connect to overhead (OH) 132kV feeder 92B
Allowance for site clearing / vegetation removal
Construct 3.2km of dual circuit ductline from Site 3 (near towers 53 and 54 of Feeder 92B) to substation site. This requires two cables per phase (i.e.x twelve ducts) to achieve 550MVA rating of feeder 92B.
Construction of 200 metres of bore under M2 (i.e., 4 bores x 3 ducts) to enable crossing of the motorway.
Installation of new twin 2000mm2 cross-linked polyethylene (XLPE) cables - i.e., two circuits x two cables per phase x three phases 132kV CU1- to the substation site.
Installation of 12 x 132kV joint bays, considering two joint bays per km.
Installation of new twin 2000mm2 XLPE cables to the substation site.
132kV termination cable works at substation cable basement.
Upgrade telecommunication capability by installing 25km of Optical Ground Wire (OPGW) to replace existing, highly loaded All-Dielectric Self-Supporting (ADSS) fiber optic cable.

## Option 2
Option 2 - New 132/33kV STS at Site 1 looped into 132kV Feeders 92A & 92B Sydney North BSP - Lane Cove STSS
| New Assets |  | Quantity | Unit of Measure | Unit rate code | Description | Unit Rate ($FY22) | Cost ($FY22) | Escalation to $FY24 | Baseline - including contingency allowance and property update | Baseline including 40% contingency | Comments
Initial requirements (2025-2029)
Install a new 132/33kV STS (Wallumatta STS) with 3x120MVA transformers and 3x33kV switchgroups
|  | Acquisition of property to establish a new STS (Site 1) | 1 | each
|  | STS IDID 3x132/33Tx 9x132 18x33 expandable | 1 | each | [7 empty] | Provided by Estimating & Unit Rates (July 2024). It excludes the installation of a capacitor bank as well as civil works to for a 4th Tx bay
|  | 2x132kV indoor GIS circuit breakers | 2 | each | SP_0303 | Additional 132kV GIS TX SG (STS) |  |  | 1.1225 |  |  | Equipment cost only (installation/commissioning cost absorbed by STS component).
132kV connections to loop into Feeders 92A & 92B
|  | 3.2km x 2 x twin 2000mm2 cable per phase | 6.5 | km |  | 132kV Double Duct Bank 2000mm2 CU1 |  |  | 1.041 |  |  | Only feasible cut-in point to Feeder 92B is at Tower 53/54 near sports grounds. Other locations ruled out due to difficult access. Unit rate provided by Estimating & Unit Rates (July 2023).
|  | UGOH poles | 2 | each | SP_0244 | Building Demolition (Zone) |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV Joint Bays | 12 | each | SP_0256 | 33kV STJ |  |  | 1.1225 |  |  | Assumes 2 x 132kV Joint Bays per km per circuit
|  | Allowance for Bore under M2 | 2 | each | N/A | M2 crossing Under Bore - 12 ducts |  |  | 1.041 |  |  | Based on actual cost of Horizontal Directional Drilling for Centenary Drive 132kV underbore (132kV ductline Chullora) completed in 2022. Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV terminations at substation site | 4 | each | SP_0236 | TM132OD |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
|  | National Park Clearing | 1 |  | N/A |  |  |  | 1.041 |  |  | Assume 25 large trees per 1000m2. No allowance for environmental approvals. This is required for the installation of 2 sets of UGOHs from the 132kV towerline. Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 3.2km x 2 x twin 2000mm2 cable per phase | 6.5 | km |  | 132kV Double Duct Bank 2000mm2 CU1 |  |  | 1.041 |  |  | Only feasible cut-in point to Feeder 92B is at Tower 53/54 near sports grounds. Other locations ruled out due to difficult access. Unit rate provided by Estimating & Unit Rates (July 2023).
|  | UGOH poles | 2 | each | SP_0258 | 33kV Oil 1SC (Cable Only) |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV Joint Bays | 12 | each | SP_0264 | Additional 132kV GIS TX SG (Zone) |  |  | 1.1225 |  |  | Assumes 2 x 132kV Joint Bays per km per circuit
|  | Allowance for Bore under M2 | 2 | each | N/A | M2 crossing Under Bore - 12 ducts |  |  | 1.041 |  |  | Based on actual cost of Horizontal Directional Drilling for Centenary Drive 132kV underbore (132kV ductline Chullora) completed in 2022. Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV terminations at substation site | 4 | each | SP_0246 | 11kV OH Underbuilt |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
|  | National Park Clearing | 1 |  | N/A |  |  |  | 1.041 |  |  | Assume 25 large trees per 1000m2. No allowance for environmental approvals. This is required for the installation of 2 sets of UGOHs from the 132kV towerline. Unit rate provided by Estimating & Unit Rates (July 2023)
Communications upgrades
|  | OPGW cable installation on Feeder 92B | 25 | km | N/A |  |  |  | 1.041 |  |  | Based on cost estimates for OPGW cable installed in project SM-27603 (Replace Fdr 926 OHEW replacement with OPGW). Unit rates provided by Estimating & Unit Rates (July 2023)
| Contingency allowance | [8 empty] | 18857128
[10 empty] | 251972458.5855 | 313726273.948
Comments
Whilst cutting into both feeders will result in better management of 132kV load flows compared to cutting into one feeder only, this opton is materially more expensive due to the need ot twin cables to maintain the rating capacity of the network.
The arrangement of four x 132kV feeders to the new STS will require two different routes, to be able to achieve the 550MVA rating capacity of feeders 92A 7 92B.
In addition, proposed site has been impacted by NSW Department of Planning, Housing and Infrastructure (DPHI) rezoning of Macquarie Park area. It is now available for residential high rise development, and the value is likely to increase significantly (i.e., more than double).
This option involves:
Acquisition of property in the Macquarie Park area (Site 1)
Construction of a new 132/33kV subtransmission substation, comprising:
3 x 132/33kV 120MVA transformer units
New switchroom building to house circuit breakers and associated control/protection rooms
9 x 132kV indoor GIS circuit breakers
18 x 33kV indoor GIS cuircuit breakers
Installation of two 132kV feeder connections to loop into Feeder 92B, comprising:
Two 132kV Underground to Overhead connection (UGOH) pole structures to connect to overhead (OH) 132kV feeder 92B
Allowance for site clearing / vegetation removal
Construct 3.2km of dual circuit ductline from Kangaroo Point (near towers 53 and 54 of Feeder 92B) to substation site. This requires two cables per phase (i.e.x twelve ducts) to achieve 550MVA rating of feeder 92B.
Construction of 200 metres of bore under M2 (i.e., 4 bores x 3 ducts) to enable crossing of the motorway.
Installation of new twin 2000mm2 cross-linked polyethylene (XLPE) cables - i.e., two circuits x two cables per phase x three phases 132kV CU1- to the substation site.
Installation of 12 x 132kV joint bays, considering two joint bays per km.
Installation of new twin 2000mm2 XLPE cables to the substation site.
132kV termination cable works at substation cable basement.
Installation of two 132kV feeder connections to loop into Feeder 92A, with the same components as described for Feeder 92B above.
Upgrade telecommunication capability by installing 25km of Optical Ground Wire (OPGW) to replace existing, highly loaded All-Dielectric Self-Supporting (ADSS) fiber optic cable.

## Option 3
Option 3 - New 132kV STSS at Site 3 and 132/33kV STS at Site 1 looped into 132kV Feeder 92B
| New Assets |  | Quantity | Unit of Measure | Unit rate code | Description | Unit Rate ($FY22) | Cost ($FY22) | Escalation to $FY24 | Baseline - including contingency allowance and property update | Baseline including 40% contingency | Comments
Initial requirements (2025-2029)
Install a new 132kV STSS (Site 3)
|  | Acquisition of property to establish a new STSS (Site 3) | 1 | each | [7 empty] | This site is too small for an STS but could be suitable for a small switching station
|  | STSS ID 5x132kV indoor GIS circuit breakers | 1 | each | [7 empty] | Provided by Estimating & Unit Rates for RFR response (July 2023)
132kV connections to loop into Feeder 92B to new STSS
|  | 0.1km x 2 x 132kV overhead circuits | 0.1 | km | SP_0220 | OH132CDC (132kV Concrete 2SC Clearng) |  |  | 1.1225 |  |  | Overhead connections
|  | UGOH poles | 2 | each | SP_0243 | TM132UGOH |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 0.1km x 2 x twin 2000mm2 cable per phase | 0.2 | km |  | 132kV Double Duct Bank 2000mm2 CU1 |  |  | 1.041 |  |  | Underground connections. Scale factor applied to consider unit rate is for the 1st km.
|  | National Park Clearing | 1 |  | N/A |  |  |  | 1.041 |  |  | Assume 25 large trees per 1000m2. No allowance for environmental approvals. This is required for the installation of 2 sets of UGOHs from the 132kV towerline. Unit rate provided by Estimating & Unit Rates (July 2023)
Install a new 132/33kV STS (Wallumatta STS) with 3x120MVA transformers and 3x33kV switchgroups
|  | Acquisition of property to establish a new STS (Site 1) | 1 | each
|  | STS IDID 3x132/33Tx 9x132 18x33 expandable | 1 | each | [7 empty] | Provided by Estimating & Unit Rates (July 2024). It excludes the installation of a capacitor bank as well as civil works to for a 4th Tx bay
132kV connections from new STSS to Wallumatta STS
|  | 3.1km x 2 x single 2000mm2 cable per phase | 3.1 | km |  | 132kV Double Duct Bank 2000mm2 CU1 |  |  | 1.041 |  |  | Only feasible cut-in point to Feeder 92B is at Tower 53/54 near sports grounds. Other locations ruled out due to difficult access. Unit rate provided by Estimating & Unit Rates (July 2023).
|  | 132kV Joint Bays | 6 | each | SP_0265 | Additional 132kV GIS Fdr SG (Zone) |  |  | 1.1225 |  |  | Assumes 2 x 132kV Joint Bays per km per circuit
|  | Allowance for Bore under M2 | 2 | each | N/A | M2 crossing Under Bore - 12 ducts |  |  | 1.041 |  |  | Based on actual cost of Horizontal Directional Drilling for Centenary Drive 132kV underbore (132kV ductline Chullora) completed in 2022. Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV terminations at substation site | 2 | each | SP_0235 | TM132IN |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
Communications upgrades
|  | OPGW cable installation on Feeder 92B | 25 | km | N/A |  |  |  | 1.041 |  |  | Based on cost estimates for OPGW cable installed in project SM-27603 (Replace Fdr 926 OHEW replacement with OPGW). Unit rates provided by Estimating & Unit Rates (July 2023)
| Contingency allowance | [8 empty] | 18857128
[10 empty] | 200489930.7269 | 238325357.3896
Comments
By including a new 132kV STSS, this option significantly reduces the 132kV feeder connection costs, due to only requiring 290MVA instead of 550MVA to connect the new STS. However,
This option is no longer considered feasible due to
Rating constraints at Feeder 92B due to additional loads at Lane Cove STSS which will reduce capacity available.
A second property is required (Site 3). This location requires land clearing within the Lane Cove National Park. Negative community impact expected in case of national park land clearing requirements
High risks of delays due to need to buy two land parcels and environmental approvals.
In addition, Site 1 has been impacted by NSW Department of Planning, Housing and Infrastructure (DPHI) rezoning of Macquarie Park area. It is now available for residential high rise development.
This option involves:
Acquisition of two properties, one in close proximity to Lane Cove National Park (Site 3) and a second site in the Macquarie Park area (Site 1)
Installation of two 132kV feeder connections to loop into Feeder 92B, comprising:
Two 132kV Underground to Overhead connection (UGOH) pole structures to connect to overhead (OH) 132kV feeder 92B
Allowance for site clearing / vegetation removal
Construct 0.1km of dual circuit ductline from Site 3 (near towers 53 and 54 of Feeder 92B) to substation site. This requires two cables per phase (i.e.x twelve ducts) to achieve 550MVA rating of feeder 92B.
Installation of new twin 2000mm2 cross-linked polyethylene (XLPE) cables - i.e., two circuits x two cables per phase x three phases 132kV CU1- to reach Site 3.
Construction of a new 132kV substransmission switching station, comprising
New switchroom building to house circuit breakers and associated control/protection rooms
5 x 132kV indoor GIS circuit breakers
Installation of two 132kV feeder connections to the new Wallumatta STS, comprising:
Construct 3.1km of dual circuit ductline from Site 3 to substation site. This requires single cables per phase (i.e.x six ducts) to achieve 290MVA rating capacity.
Construction of 200 metres of bore under M2 (i.e., 2 bores x 3 ducts) to enable crossing of the motorway.
Installation of new single 2000mm2 cross-linked polyethylene (XLPE) cables - i.e., two circuits x three phases 132kV CU1- between Site 3 and the substation site.
Installation of 6 x 132kV joint bays, considering two joint bays per km.
Installation of new 2000mm2 XLPE cables between Site 3 and the substation site.
132kV termination cable works at substation cable basement.
Construction of a new 132/33kV subtransmission substation, comprising:
3 x 132/33kV 120MVA transformer units
New switchroom building to house circuit breakers and associated control/protection rooms
9 x 132kV indoor GIS circuit breakers
18 x 33kV indoor GIS cuircuit breakers
Upgrade telecommunication capability by installing 25km of Optical Ground Wire (OPGW) to replace existing, highly loaded All-Dielectric Self-Supporting (ADSS) fiber optic cable.

## Option 4
Option 4 - New 132/33kV STS at Site 1 tee connected at East Ryde Transition Point to 132kV Feeders 92G & 92J
| New Assets |  | Quantity | Unit of Measure | Unit rate code | Description | Unit Rate ($FY22) | Cost ($FY22) | Escalation to $FY24 | Baseline cost excluding contingency | Baseline - including contingency allowance and property update | Baseline including 40% contingency (RIT-D sensitivity test) | Comments
Initial requirements (2025-2029)
Install a new 132/33kV STS (Wallumatta STS) with 3x120MVA transformers and 3x33kV switchgroups
|  | Acquisition of property to establish a new STS (Site 1) | 1 | each
|  | STS IDID 3x132/33Tx 10x132 18x33 expandable | 1 | each | [8 empty] | Provided by Estimating & Unit Rates (July 2024). It excludes the installation of a capacitor bank as well as civil works to for a 4th Tx bay
132kV connections to tee off from Feeder 92G & 92J
|  | 6.4km x 2 x single 2000mm2 cable per phase | 6.4 | km |  | 132kV Double Duct Bank 2000mm2 CU1 |  |  | 1.041 |  |  |  | Unit rate provided by Estimating & Unit Rates (July 2023).
|  | UGOH poles | 2 | each | SP_0243 | TM132UGOH |  |  | 1.041 |  |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV Joint Bays | 12 | each | SP_0255 | 132kV STJ (XLPE - XLPE) |  |  | 1.1225 |  |  |  | Assumes 2 x 132kV Joint Bays per km per circuit
|  | Allowance for Bore under major roads | 2 | each | N/A | Under Bore Civil works |  |  | 1.041 |  |  |  | Based on actual cost of Horizontal Directional Drilling for Centenary Drive 132kV underbore (132kV ductline Chullora) completed in 2022. Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV terminations at substation site | 2 | each | SP_0235 | TM132IN |  |  | 1.041 |  |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
| Contingency allowance | [9 empty] | 18857128
[10 empty] | 159791183.8145 | 178648311.8145 | 211570167.9923
Comments
No need to loop into these feeders. A tee connection is possible.
Proposed site has been impacted by NSW Department of Planning, Housing and Infrastructure (DPHI) rezoning of Macquarie Park area. It is now available for residential high rise development.
This option involves:
Acquisition of property in the Macquarie Park area
Construction of a new 132/33kV subtransmission substation, comprising:
3 x 132/33kV 120MVA transformer units
New switchroom building to house circuit breakers and associated control/protection rooms
9 x 132kV indoor GIS circuit breakers
18 x 33kV indoor GIS cuircuit breakers
Installation of two 132kV feeder connections to tee off from East Ryde Transition Point to the new Wallumatta STS, comprising:
Two 132kV Underground to Overhead connection (UGOH) pole structures to connect to East Ryde Transition Point
Construct 6.4km of dual circuit ductline from transition Point to substation site. This requires single cables per phase (i.e.x six ducts) to achieve 290MVA rating capacity.
Construction of 200 metres of bore (i.e., 2 bores x 3 ducts) to enable crossing of major roads.
Installation of new single 2000mm2 cross-linked polyethylene (XLPE) cables - i.e., two circuits x three phases 132kV CU1- between East Ryde Transition Point and the substation site.
Installation of 12 x 132kV joint bays, considering two joint bays per km.
132kV termination cable works at substation cable basement.

## Option 5
Option 5 - New 132/33kV STS at Site 2 tee connected at East Ryde Transition Point to 132kV Feeders 92G & 92J
| New Assets |  | Quantity | Unit of Measure | Unit rate code | Description | Unit Rate ($FY23) | Cost ($FY22) | Escalation to $FY24 | Baseline cost excluding contingency | Baseline - including contingency allowance and property update | Cost including 40% contingency (RIT-D sensitivity test) | Comments
Initial requirements (2025-2029)
Install a new 132/33kV STS (Wallumatta STS) with 3x120MVA transformers and 3x33kV switchgroups
|  | Acquisition of property to establish a new STS (Site 2) | 1 | each
|  | STS IDID 3x132/33Tx 9x132 18x33 expandable | 1 | each | [8 empty] | Provided by Estimating & Unit Rates (July 2024). It excludes the installation of a capacitor bank as well as civil works to for a 4th Tx bay
132kV connections to tee off from Feeder 92G & 92J
|  | 7.1km x 2 x single 2000mm2 cable per phase | 7.1 | km |  | 132kV Double Duct Bank 2000mm2 CU1 |  |  | 1.041 |  |  |  | Unit rate provided by Estimating & Unit Rates (July 2023).
|  | UGOH poles | 2 | each | SP_0243 | TM132UGOH |  |  | 1.041 |  |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV Joint Bays | 12 | each | SP_0255 | 132kV STJ (XLPE - XLPE) |  |  | 1.1225 |  |  |  | Assumes 2 x 132kV Joint Bays per km per circuit
|  | Allowance for Bore under major roads | 2 | each | N/A | Under Bore Civil works |  |  | 1.041 |  |  |  | Based on actual cost of Horizontal Directional Drilling for Centenary Drive 132kV underbore (132kV ductline Chullora) completed in 2022. Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV terminations at substation site | 2 | each | SP_0235 | TM132IN |  |  | 1.041 |  |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
| Contingency allowance | [9 empty] | 18857128
[10 empty] | 143450319.1438 | 162307447.1438 | 193585191.8388
Comments
No need to loop into these feeders. A tee connection is possible.
Customers will be located in close proximity to this site.
This option involves:
Acquisition of property in the Macquarie Park area
Construction of a new 132/33kV subtransmission substation, comprising:
3 x 132/33kV 120MVA transformer units
New switchroom building to house circuit breakers and associated control/protection rooms
9 x 132kV indoor GIS circuit breakers
18 x 33kV indoor GIS cuircuit breakers
Installation of two 132kV feeder connections to tee off from East Ryde Transition Point to the new Wallumatta STS, comprising:
Two 132kV Underground to Overhead connection (UGOH) pole structures to connect to East Ryde Transition Point
Construct 7.1km of dual circuit ductline from transition Point to substation site. This requires single cables per phase (i.e.x six ducts) to achieve 290MVA rating capacity.
Construction of 200 metres of bore (i.e., 2 bores x 3 ducts) to enable crossing of major roads.
Installation of new single 2000mm2 cross-linked polyethylene (XLPE) cables - i.e., two circuits x three phases 132kV CU1- between East Ryde Transition Point and the substation site.
Installation of 12 x 132kV joint bays, considering two joint bays per km.
132kV termination cable works at substation cable basement.

## Option 6
Option 6 - New STS with expanded 132kV busbar at Site 1 tee connected to 132kV Feeders 92G & 92J
| New Assets |  | Quantity | Unit of Measure | Unit rate code | Description | Unit Rate ($FY22) | Cost ($FY22) | Escalation to $FY24 | Baseline cost excluding contingency | Baseline - including contingency allowance and property update | Cost including 40% contingency (RIT-D sensitivity test) | Comments
Initial requirements (2025-2029)
Install a new 132/33kV STS (Wallumatta STS) with 3x120MVA transformers, 132kV bays for customer connections and 3x33kV switchgroups
|  | Acquisition of property to establish a new STS (Site 1) | 1 | each
|  | STS IDID 3x132/33Tx 14x132 18x33 expandable | 1 | each | [8 empty] | Provided by Estimating & Unit Rates (July 2024)
|  | 132kV Cable egress works to enable connections | [10 empty] | Allowance for civil works to address 132kV cable egress issues at Site 1. Assumes 50% of similar works undertaken at Alexandria STS (refer to the "132kV Ductline Work" tab) completed in FY20, escalated to FY24 dollars.
132kV connections to tee off from Feeder 92J & 92G
|  | 6.4km x 2 x single 2000mm2 cable per phase | 6.4 | km |  | 132kV Double Duct Bank 2000mm2 CU1 |  |  | 1.041 |  |  |  | Unit rate provided by Estimating & Unit Rates (July 2023).
|  | UGOH poles | 2 | each | SP_0243 | TM132UGOH |  |  | 1.041 |  |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV Joint Bays | 12 | each | SP_0255 | 132kV STJ (XLPE - XLPE) |  |  | 1.1225 |  |  |  | Assumes 2 x 132kV Joint Bays per km per circuit
|  | Allowance for Bore under major roads | 2 | each | N/A | Under Bore Civil works |  |  | 1.041 |  |  |  | Based on actual cost of Horizontal Directional Drilling for Centenary Drive 132kV underbore (132kV ductline Chullora) completed in 2022. Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV terminations at substation site | 2 | each | SP_0235 | TM132IN |  |  | 1.041 |  |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
| Contingency allowance | [9 empty] | 18857128
[10 empty] | 167246879.7821 | 186104007.7821 | 222008142.347
Comments
No need to loop into these feeders. A tee connection is possible.
Proposed site has been impacted by NSW Department of Planning, Housing and Infrastructure (DPHI) rezoning of Macquarie Park area. It is now available for residential high rise development.
This option involves:
Acquisition of property in the Macquarie Park area
Construction of a new 132/33kV subtransmission substation, comprising:
3 x 132/33kV 120MVA transformer units
New switchroom building to house circuit breakers and associated control/protection rooms
14 x 132kV indoor GIS circuit breakers
18 x 33kV indoor GIS cuircuit breakers
Installation of two 132kV feeder connections to tee off from East Ryde Transition Point to the new Wallumatta STS, comprising:
Two 132kV Underground to Overhead connection (UGOH) pole structures to connect to East Ryde Transition Point
Construct 6.4km of dual circuit ductline from transition Point to substation site. This requires single cables per phase (i.e.x six ducts) to achieve 290MVA rating capacity.
Construction of 200 metres of bore (i.e., 2 bores x 3 ducts) to enable crossing of major roads.
Installation of new single 2000mm2 cross-linked polyethylene (XLPE) cables - i.e., two circuits x three phases 132kV CU1- between East Ryde Transition Point and the substation site.
Installation of 12 x 132kV joint bays, considering two joint bays per km.
132kV termination cable works at substation cable basement.

## Option 7
Option 7 - New STS with expanded 132kV busbar at Site 2 tee connected to 132kV Feeders 92G & 92J
| New Assets |  | Quantity | Unit of Measure | Unit rate code | Description | Unit Rate ($FY22) | Cost ($FY22) | Escalation to $FY24 | Baseline cost excluding contingency | Baseline - including contingency allowance and property update | Cost including 40% contingency (RIT-D sensitivity test) | Comments
Initial requirements (2025-2029)
Install a new 132/33kV STS (Wallumatta STS) with 3x120MVA transformers, 132kV bays for customer connections and 3x33kV switchgroups
|  | Acquisition of property to establish a new STS (Site 2) | 1 | each
|  | STS IDID 3x132/33Tx 14x132 18x33 expandable | 1 | each | [8 empty] | Provided by Estimating & Unit Rates (July 2024)
|  | 132kV Cable egress works to enable connections | [10 empty] | Allowance for civil works to address 132kV cable egress issues at Site 2. Assumes 50% of similar works undertaken at Alexandria STS (refer to the "132kV Ductline Work" tab) completed in FY20, escalated to FY24 dollars.
132kV connections to tee off from Feeder 92J & 92G
|  | 7.1km x 2 x single 2000mm2 cable per phase | 7.1 | km |  | 132kV Double Duct Bank 2000mm2 CU1 |  |  | 1.041 |  |  |  | Unit rate provided by Estimating & Unit Rates (July 2023).
|  | UGOH poles | 2 | each | SP_0243 | TM132UGOH |  |  | 1.041 |  |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV Joint Bays | 12 | each | SP_0255 | 132kV STJ (XLPE - XLPE) |  |  | 1.1225 |  |  |  | Assumes 2 x 132kV Joint Bays per km per circuit
|  | Allowance for Bore under major roads | 2 | each | N/A | Under Bore Civil works |  |  | 1.041 |  |  |  | Based on actual cost of Horizontal Directional Drilling for Centenary Drive 132kV underbore (132kV ductline Chullora) completed in 2022. Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV terminations at substation site | 2 | each | SP_0235 | TM132IN |  |  | 1.041 |  |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
18857128
[10 empty] | 150906015.1115 | 169763143.1115 | 204023166.1935
Comments
No need to loop into these feeders. A tee connection is possible.
Customers will be located in close proximity to this site.
This option involves:
Acquisition of property in the Macquarie Park area
Construction of a new 132/33kV subtransmission substation, comprising:
3 x 132/33kV 120MVA transformer units
New switchroom building to house circuit breakers and associated control/protection rooms
14 x 132kV indoor GIS circuit breakers
18 x 33kV indoor GIS cuircuit breakers
Installation of two 132kV feeder connections to tee off from East Ryde Transition Point to the new Wallumatta STS, comprising:
Two 132kV Underground to Overhead connection (UGOH) pole structures to connect to East Ryde Transition Point
Construct 7.1km of dual circuit ductline from transition Point to substation site. This requires single cables per phase (i.e.x six ducts) to achieve 290MVA rating capacity.
Construction of 200 metres of bore (i.e., 2 bores x 3 ducts) to enable crossing of major roads.
Installation of new single 2000mm2 cross-linked polyethylene (XLPE) cables - i.e., two circuits x three phases 132kV CU1- between East Ryde Transition Point and the substation site.
Installation of 12 x 132kV joint bays, considering two joint bays per km.
132kV termination cable works at substation cable basement.

## Option 8
Option 8 - New 132kV STSS (expandable) at Site 1 looped into 132kV Feeder 92B
| New Assets |  | Quantity | Unit of Measure | Unit rate code | Description | Unit Rate ($FY22) | Cost ($FY22) | Escalation to $FY24 | Baseline - including contingency allowance and property update | Baseline including 40% contingency | Comments
Initial requirements (2025-2029)
Install a new 132kV STSS (Site 1)
|  | Acquisition of property to establish a new STS | 1 | each
|  | STSS ID 21x132kV indoor GIS circuit breakers | 1 | each | [7 empty] | Provided by Estimating & Unit Rates (July 2024)
|  | 132kV Cable egress works to enable connections | [9 empty] | Allowance for civil works to address 132kV cable egress issues at Site 1. Assumes 50% of similar works undertaken at Alexandria STS (refer to the "132kV Ductline Work" tab) completed in FY20, escalated to FY24 dollars.
132kV connections to tee off from Feeder 92B
|  | 3.2km x 2 x twin 2000mm2 cable per phase | 6.5 | km |  | 132kV Double Duct Bank 2000mm2 CU1 |  |  | 1.041 |  |  | Only feasible cut-in point to Feeder 92B is at Tower 53/54 near sports grounds. Other locations ruled out due to difficult access. Congested unit rate assumed to consider 2000mm2 Cu1
|  | UGOH poles | 2 | each | SP_0243 | TM132UGOH |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV Joint Bays | 12 | each | SP_0255 | 132kV STJ (XLPE - XLPE) |  |  | 1.1225 |  |  | Assumes 2 x 132kV Joint Bays per km per circuit
|  | 132kV terminations at substation site | 4 | each | SP_0235 | TM132IN |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
|  | M2 Under Bore | 2 | each | N/A | M2 crossing Under Bore - 6 ducts |  |  | 1.041 |  |  | Based on actual cost of Horizontal Directional Drilling for Centenary Drive 132kV underbore (132kV ductline Chullora) completed in 2022.
|  | National Park Clearing | 1 |  | N/A |  |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
Communications upgrades
|  | OPGW cable installation on Feeder 92B | 25 | km | N/A |  |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
| Contingency allowance | [8 empty] | 18857128
[10 empty] | 179240726.9365 | 214231783.5465
Comments
This option is not considered feasible because:
The customers prefer 33kV input supply.
Assets will be underutilised, as customers require 90MVA N-1 and each feeder bay can provide over 250MVA.
Significant 132kV cable egress issues
Rating constraints at Feeder 92B due to additional loads at Lane Cove STSS which will impact capacity available
Under N-1 conditions, an overload will occur on tee connection 92A(2) to Macquarie Park Zone Substation. Additional project required to address this issue.
In addition, proposed site has been impacted by NSW Department of Planning, Housing and Infrastructure (DPHI) rezoning of Macquarie Park area. It is now available for residential high rise development.
This option involves:
Acquisition of property in the Macquarie Park area
Construction of a new 132kV subtransmission switching station, comprising:
New switchroom building to house circuit breakers and associated control/protection rooms
21 x 132kV indoor GIS circuit breakers
Installation of two 132kV feeder connections to loop into Feeder 92B, comprising:
Two 132kV Underground to Overhead connection (UGOH) pole structures to connect to overhead (OH) 132kV feeder 92B
Allowance for site clearing / vegetation removal
Construct 3.2km of dual circuit ductline from Site 3 (near towers 53 and 54 of Feeder 92B) to substation site. This requires two cables per phase (i.e.x twelve ducts) to achieve 550MVA rating of feeder 92B.
Construction of 200 metres of bore under M2 (i.e., 4 bores x 3 ducts) to enable crossing of the motorway.
Installation of new twin 2000mm2 cross-linked polyethylene (XLPE) cables - i.e., two circuits x two cables per phase x three phases 132kV CU1- between Site 3 and the substation site.
Installation of 12 x 132kV joint bays, considering two joint bays per km.
Installation of new twin 2000mm2 XLPE cables between Site 3 and the substation site.
132kV termination cable works at substation cable basement.
Upgrade telecommunication capability by installing 25km of Optical Ground Wire (OPGW) to replace existing, highly loaded All-Dielectric Self-Supporting (ADSS) fiber optic cable.

## Option 9
Option 9 - New 132kV STSS (expandable) at Site 1 tee connected to 132kV Feeders 92G & 92J
| New Assets |  | Quantity | Unit of Measure | Unit rate code | Description | Unit Rate ($FY22) | Cost ($FY22) | Escalation to $FY24 | Baseline - including contingency allowance and property update | Baseline including 40% contingency | Comments
Initial requirements (2025-2029)
Install a new 132kV STSS (Site 1)
|  | Acquisition of property to establish a new STS | 1 | each
|  | STSS ID 21x132kV indoor GIS circuit breakers | 1 | each | [7 empty] | Provided by Estimating & Unit Rates (July 2024)
|  | 132kV Cable egress works | [9 empty] | Allowance for civil works to address 132kV cable egress issues at Site 1. Assumes 50% of similar works undertaken at Alexandria STS (refer to the "132kV Ductline Work" tab) completed in FY20, escalated to FY24 dollars.
132kV connections to loop into Feeders 92G & 92J
|  | 6.4km x 2 x single 2000mm2 cable per phase | 6.4 | km |  | 132kV Double Duct Bank 2000mm2 CU1 |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023).
|  | UGOH poles | 2 | each | SP_0243 | TM132UGOH |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV Joint Bays | 12 | each | SP_0255 | 132kV STJ (XLPE - XLPE) |  |  | 1.1225 |  |  | Assumes 2 x 132kV Joint Bays per km per circuit
|  | Allowance for Bore under major roads | 2 | each | N/A | Under Bore Civil works |  |  | 1.041 |  |  | Based on actual cost of Horizontal Directional Drilling for Centenary Drive 132kV underbore (132kV ductline Chullora) completed in 2022. Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV terminations at substation site | 2 | each | SP_0235 | TM132IN |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
| Contingency allowance | [8 empty] | 18857128
[10 empty] | 168796184.2121 | 200597189.349
Comments
This option is not considered feasible because:
The customers prefer 33kV input supply.
Assets will be underutilised, as customers require 90MVA N-1 and each feeder bay can provide over 250MVA.
Significant 132kV cable egress issues
In addition, proposed site has been impacted by NSW Department of Planning, Housing and Infrastructure (DPHI) rezoning of Macquarie Park area. It is now available for residential high rise development.
This option involves:
Acquisition of property in the Macquarie Park area
Construction of a new 132kV subtransmission switching station, comprising:
New switchroom building to house circuit breakers and associated control/protection rooms
21 x 132kV indoor GIS circuit breakers
Installation of two 132kV feeder connections to tee off from East Ryde Transition Point to the new Wallumatta STS, comprising:
Two 132kV Underground to Overhead connection (UGOH) pole structures to connect to East Ryde Transition Point
Construct 6.4km of dual circuit ductline from transition Point to substation site. This requires single cables per phase (i.e.x six ducts) to achieve 290MVA rating capacity.
Construction of 200 metres of bore (i.e., 2 bores x 3 ducts) to enable crossing of major roads.
Installation of new single 2000mm2 cross-linked polyethylene (XLPE) cables - i.e., two circuits x three phases 132kV CU1- between East Ryde Transition Point and substation site.
Installation of 12 x 132kV joint bays, considering two joint bays per km.
132kV termination cable works at substation cable basement.

## Option 10
Option 10 - New 132kV STSS (expandable) at Site 2 tee connected to 132kV Feeders 92G & 92J
| New Assets |  | Quantity | Unit of Measure | Unit rate code | Description | Unit Rate ($FY22) | Cost ($FY22) | Escalation to $FY24 | Baseline - including contingency allowance and property update | Baseline including 40% contingency | Comments
Initial requirements (2025-2029)
Install a new 132kV STSS (Site 2)
|  | Acquisition of property to establish a new STS | 1 | each
|  | STSS ID 21x132kV indoor GIS circuit breakers | 1 | each | [7 empty] | Provided by Estimating & Unit Rates (July 2024)
|  | 132kV Cable egress works | [9 empty] | Allowance for civil works to address 132kV cable egress issues at Site 2. Assumes 50% of similar works undertaken at Alexandria STS (refer to the "132kV Ductline Work" tab) completed in FY20, escalated to FY24 dollars.
132kV connections to tee off from Feeder 92J & 92G
|  | 7.1km x 2 x single 2000mm2 cable per phase | 7.1 | km |  | 132kV Double Duct Bank 2000mm2 CU1 |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023).
|  | UGOH poles | 2 | each | SP_0243 | TM132UGOH |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV Joint Bays | 12 | each | SP_0255 | 132kV STJ (XLPE - XLPE) |  |  | 1.1225 |  |  | Assumes 2 x 132kV Joint Bays per km per circuit
|  | Allowance for Bore under major roads | 2 | each | N/A | Under Bore Civil works |  |  | 1.041 |  |  | Based on actual cost of Horizontal Directional Drilling for Centenary Drive 132kV underbore (132kV ductline Chullora) completed in 2022. Unit rate provided by Estimating & Unit Rates (July 2023)
|  | 132kV terminations at substation site | 2 | each | SP_0235 | TM132IN |  |  | 1.041 |  |  | Unit rate provided by Estimating & Unit Rates (July 2023)
| Contingency allowance | [8 empty] | 18857128
[10 empty] | 152455319.5415 | 179792213.1955
Comments
This option is not considered feasible because:
The customers prefer 33kV input supply.
Assets will be underutilised, as customers require 90MVA N-1 and each feeder bay can provide over 250MVA.
Significant 132kV cable egress issues
This option involves:
Acquisition of property in the Macquarie Park area
Construction of a new 132kV subtransmission switching station, comprising:
New switchroom building to house circuit breakers and associated control/protection rooms
21 x 132kV indoor GIS circuit breakers
Installation of two 132kV feeder connections to tee off from East Ryde Transition Point to the new Wallumatta STS, comprising:
Two 132kV Underground to Overhead connection (UGOH) pole structures to connect to East Ryde Transition Point
Construct 7.1km of dual circuit ductline from transition Point to substation site. This requires single cables per phase (i.e.x six ducts) to achieve 290MVA rating capacity.
Construction of 200 metres of bore (i.e., 2 bores x 3 ducts) to enable crossing of major roads.
Installation of new single 2000mm2 cross-linked polyethylene (XLPE) cables - i.e., two circuits x three phases 132kV CU1- between East Ryde Transition Point and the substation site.
Installation of 12 x 132kV joint bays, considering two joint bays per km.
132kV termination cable works at substation cable basement.

## Option 11
Option 11 - New 132kV STSS (expandable) at Site 3 looped into 132kV Feeder 92B
| New Assets |  | Quantity | Unit of Measure | Unit rate code | Description | Unit Rate ($FY22) | Cost ($FY22) | Escalation to $FY24 | Baseline - including contingency allowance | Baseline including 40% contingency | Comments
Initial requirements (2025-2029)
Install a new 132kV STSS (Site 3)
|  | Acquisition of property to establish a new STS | 1 | each | [7 empty] | This site cannot accommodate a large switching station.
|  | STSS ID 21x132kV indoor GIS circuit breakers | 1 | each | [7 empty] | Provided by Estimating & Unit Rates (July 2024)
132kV Cable egress works
|  | Land clearing | 2 |  | N/A |  |  |  | 1.041
132kV connections to tee off from Feeder 92B to new STSS
|  | 0.1km x 2 x 132kV overhead circuits | 0.1 | km | SP_0220 | OH132CDC (132kV Concrete 2SC Clearng) |  |  | 1.1225 |  |  | Overhead connections
|  | UGOH poles | 2 | each | SP_0243 | TM132UGOH |  |  | 1.1225
|  | 0.1km x 2 x twin 2000mm2 cable per phase | 0.2 | km |  | 132kV Double Duct Bank 2000mm2 CU1 |  |  | 1.041 |  |  | Underground connections. Scale factor applied to consider unit rate is for the 1st km.
|  | National Park Clearing | 1 |  | N/A |  |  |  | 1.041 |  |  | Assumes 25 large trees per 1000m2. No allowance for environmental approvals. This is required for the installation of 2 sets of UGOHs from the 132kV towerline.
Communications upgrades
|  | OPGW cable installation on Feeder 92B | 25 | km | N/A |  |  |  | 1.041 |  |  | Based on cost estimates for OPGW cable installed in project SM-27603 (Replace Fdr 926 OHEW replacement with OPGW).
| Contingency allowance | [8 empty] | 18857128
[10 empty] | 185279396.0717 | 213249134.5687
Comments
This option is considered not feasible due to the issues with the site, such as:
The site will require significant national park land clearing and environmental approvals.
Land acquisition is likely to cause time delays, due to national park negotiations and.
Compulsory acquisition of sport grounds. Acquisition plus legal costs are considerable.
Negative community impact expected in case of national park land clearing requirements and use of sports grounds

## Unit rates $FY22
Standard Project | Project Name | Contract Services | Direct | Indirect | Material | Grand Total

## Escalation factors
This sheet uses inflation as it is applied by the AER. |  |  |  |  | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast
Financial year ending |  |  |  | 1999-06-30 | 2000-06-30 | 2001-06-30 | 2002-06-30 | 2003-06-30 | 2004-06-30 | 2005-06-30 | 2006-06-30 | 2007-06-30 | 2008-06-30 | 2009-06-30 | 2010-06-30 | 2011-06-30 | 2012-06-30 | 2013-06-30 | 2014-06-30 | 2015-06-30 | 2016-06-30 | 2017-06-30 | 2018-06-30 | 2019-06-30 | 2020-06-30 | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30 | 2027-06-30 | 2028-06-30 | 2029-06-30
| CPI |  |  |  | 1.465% | 4.475% | 4.381% | 3.003% | 2.771% | 2.344% | 2.669% | 3.538% | 2.332% | 4.353% | 1.82% | 2.845% | 3.389% | 1.763% | 2.45% | 2.488% | 1.508% | 1.277% | 1.949% | 1.911% | 1.84% | 0.8606% | 3.498% | 7.832% | 4.1% | 2.8% | 2.8% | 2.8% | 2.8% | 2.8%
Table 1 - To escalate Real Regulatory Expenditure Allowances, select year and multiply with the index
| CPI indexes (real to real) |  | To Real (select year) |  | 2000-06-30 | 2001-06-30 | 2002-06-30 | 2003-06-30 | 2004-06-30 | 2005-06-30 | 2006-06-30 | 2007-06-30 | 2008-06-30 | 2009-06-30 | 2010-06-30 | 2011-06-30 | 2012-06-30 | 2013-06-30 | 2014-06-30 | 2015-06-30 | 2016-06-30 | 2017-06-30 | 2018-06-30 | 2019-06-30 | 2020-06-30 | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30 | 2027-06-30 | 2028-06-30 | 2029-06-30
| CPI indexes (real to nominal) |  | To Nominal (each year)
From Real (select year)
|  | 2000-06-30 |  |  | 1 | 1.0448 | 1.0905 | 1.1233 | 1.1544 | 1.1814 | 1.213 | 1.2559 | 1.2852 | 1.3411 | 1.3655 | 1.4044 | 1.452 | 1.4776 | 1.5138 | 1.5515 | 1.5749 | 1.595 | 1.626 | 1.6571 | 1.6876 | 1.7021 | 1.7617 | 1.8997 | 1.9776 | 2.0329 | 2.0898 | 2.1483 | 2.2085 | 2.2703
|  | 2001-06-30 |  |  | 0.95717 | 1 | 1.0438 | 1.0752 | 1.1049 | 1.1308 | 1.161 | 1.2021 | 1.2301 | 1.2837 | 1.307 | 1.3442 | 1.3898 | 1.4143 | 1.4489 | 1.485 | 1.5074 | 1.5266 | 1.5564 | 1.5861 | 1.6153 | 1.6292 | 1.6862 | 1.8183 | 1.8928 | 1.9458 | 2.0003 | 2.0563 | 2.1139 | 2.1731
|  | 2002-06-30 |  |  | 0.91699 | 0.95803 | 1 | 1.03 | 1.0586 | 1.0834 | 1.1123 | 1.1517 | 1.1785 | 1.2298 | 1.2522 | 1.2878 | 1.3315 | 1.3549 | 1.3881 | 1.4227 | 1.4441 | 1.4626 | 1.4911 | 1.5196 | 1.5475 | 1.5609 | 1.6155 | 1.742 | 1.8134 | 1.8642 | 1.9164 | 1.97 | 2.0252 | 2.0819
|  | 2003-06-30 |  |  | 0.89026 | 0.9301 | 0.97084 | 1 | 1.0277 | 1.0518 | 1.0799 | 1.1181 | 1.1442 | 1.194 | 1.2157 | 1.2503 | 1.2926 | 1.3154 | 1.3477 | 1.3812 | 1.402 | 1.4199 | 1.4476 | 1.4753 | 1.5024 | 1.5153 | 1.5684 | 1.6912 | 1.7605 | 1.8098 | 1.8605 | 1.9126 | 1.9661 | 2.0212
|  | 2004-06-30 |  |  | 0.86626 | 0.90502 | 0.94467 | 0.97304 | 1 | 1.0234 | 1.0507 | 1.0879 | 1.1133 | 1.1618 | 1.1829 | 1.2166 | 1.2578 | 1.28 | 1.3113 | 1.344 | 1.3642 | 1.3816 | 1.4086 | 1.4355 | 1.4619 | 1.4745 | 1.5261 | 1.6456 | 1.7131 | 1.761 | 1.8103 | 1.861 | 1.9131 | 1.9667
|  | 2005-06-30 |  |  | 0.84642 | 0.8843 | 0.92304 | 0.95076 | 0.9771 | 1 | 1.0267 | 1.063 | 1.0878 | 1.1352 | 1.1558 | 1.1887 | 1.229 | 1.2507 | 1.2813 | 1.3132 | 1.333 | 1.35 | 1.3763 | 1.4026 | 1.4284 | 1.4407 | 1.4911 | 1.6079 | 1.6738 | 1.7207 | 1.7689 | 1.8184 | 1.8693 | 1.9216
|  | 2006-06-30 |  |  | 0.82442 | 0.86131 | 0.89904 | 0.92604 | 0.9517 | 0.97401 | 1 | 1.0354 | 1.0595 | 1.1057 | 1.1258 | 1.1578 | 1.197 | 1.2181 | 1.248 | 1.279 | 1.2983 | 1.3149 | 1.3405 | 1.3662 | 1.3913 | 1.4033 | 1.4524 | 1.5661 | 1.6303 | 1.676 | 1.7229 | 1.7711 | 1.8207 | 1.8717
|  | 2007-06-30 |  |  | 0.79624 | 0.83188 | 0.86832 | 0.8944 | 0.91918 | 0.94072 | 0.96582 | 1 | 1.0233 | 1.0679 | 1.0873 | 1.1182 | 1.1561 | 1.1765 | 1.2053 | 1.2353 | 1.254 | 1.27 | 1.2947 | 1.3195 | 1.3438 | 1.3553 | 1.4027 | 1.5126 | 1.5746 | 1.6187 | 1.664 | 1.7106 | 1.7585 | 1.8077
|  | 2008-06-30 |  |  | 0.77809 | 0.81292 | 0.84853 | 0.87401 | 0.89823 | 0.91928 | 0.94381 | 0.97721 | 1 | 1.0435 | 1.0625 | 1.0928 | 1.1298 | 1.1497 | 1.1779 | 1.2072 | 1.2254 | 1.241 | 1.2652 | 1.2894 | 1.3131 | 1.3244 | 1.3708 | 1.4781 | 1.5387 | 1.5818 | 1.6261 | 1.6716 | 1.7184 | 1.7665
|  | 2009-06-30 |  |  | 0.74564 | 0.77901 | 0.81314 | 0.83755 | 0.86076 | 0.88093 | 0.90444 | 0.93645 | 0.95829 | 1 | 1.0182 | 1.0472 | 1.0827 | 1.1017 | 1.1287 | 1.1568 | 1.1743 | 1.1893 | 1.2124 | 1.2356 | 1.2584 | 1.2692 | 1.3136 | 1.4165 | 1.4745 | 1.5158 | 1.5583 | 1.6019 | 1.6467 | 1.6928
|  | 2010-06-30 |  |  | 0.73231 | 0.76508 | 0.7986 | 0.82258 | 0.84537 | 0.86519 | 0.88828 | 0.91971 | 0.94116 | 0.98212 | 1 | 1.0285 | 1.0633 | 1.0821 | 1.1086 | 1.1361 | 1.1533 | 1.168 | 1.1908 | 1.2135 | 1.2359 | 1.2465 | 1.2901 | 1.3911 | 1.4482 | 1.4887 | 1.5304 | 1.5733 | 1.6173 | 1.6626
|  | 2011-06-30 |  |  | 0.71205 | 0.74392 | 0.77651 | 0.79983 | 0.82199 | 0.84125 | 0.8637 | 0.89426 | 0.91512 | 0.95495 | 0.97233 | 1 | 1.0339 | 1.0521 | 1.0779 | 1.1047 | 1.1214 | 1.1357 | 1.1578 | 1.18 | 1.2017 | 1.212 | 1.2544 | 1.3527 | 1.4081 | 1.4475 | 1.4881 | 1.5297 | 1.5726 | 1.6166
|  | 2012-06-30 |  |  | 0.68871 | 0.71953 | 0.75105 | 0.77361 | 0.79504 | 0.81367 | 0.83539 | 0.86495 | 0.88512 | 0.92365 | 0.94046 | 0.96722 | 1 | 1.0176 | 1.0426 | 1.0685 | 1.0846 | 1.0985 | 1.1199 | 1.1413 | 1.1623 | 1.1723 | 1.2133 | 1.3083 | 1.362 | 1.4001 | 1.4393 | 1.4796 | 1.521 | 1.5636
|  | 2013-06-30 |  |  | 0.67678 | 0.70707 | 0.73804 | 0.76021 | 0.78127 | 0.79958 | 0.82092 | 0.84997 | 0.86979 | 0.90765 | 0.92417 | 0.95046 | 0.98268 | 1 | 1.0245 | 1.05 | 1.0658 | 1.0794 | 1.1005 | 1.1215 | 1.1421 | 1.152 | 1.1923 | 1.2857 | 1.3384 | 1.3758 | 1.4144 | 1.454 | 1.4947 | 1.5365
|  | 2014-06-30 |  |  | 0.66059 | 0.69016 | 0.72039 | 0.74203 | 0.76259 | 0.78046 | 0.80129 | 0.82964 | 0.84899 | 0.88594 | 0.90207 | 0.92773 | 0.95918 | 0.97609 | 1 | 1.0249 | 1.0403 | 1.0536 | 1.0742 | 1.0947 | 1.1148 | 1.1244 | 1.1638 | 1.2549 | 1.3064 | 1.3429 | 1.3805 | 1.4192 | 1.4589 | 1.4998
|  | 2015-06-30 |  |  | 0.64456 | 0.6734 | 0.7029 | 0.72401 | 0.74407 | 0.76151 | 0.78184 | 0.8095 | 0.82838 | 0.86444 | 0.88017 | 0.90521 | 0.93589 | 0.95239 | 0.97572 | 1 | 1.0151 | 1.028 | 1.0481 | 1.0681 | 1.0878 | 1.0971 | 1.1355 | 1.2244 | 1.2746 | 1.3103 | 1.347 | 1.3847 | 1.4235 | 1.4634
|  | 2016-06-30 |  |  | 0.63498 | 0.6634 | 0.69246 | 0.71326 | 0.73302 | 0.7502 | 0.77022 | 0.79747 | 0.81607 | 0.85159 | 0.86709 | 0.89176 | 0.92199 | 0.93824 | 0.96123 | 0.98514 | 1 | 1.0128 | 1.0325 | 1.0522 | 1.0716 | 1.0808 | 1.1186 | 1.2062 | 1.2557 | 1.2909 | 1.327 | 1.3642 | 1.4024 | 1.4416
|  | 2017-06-30 |  |  | 0.62697 | 0.65503 | 0.68373 | 0.70426 | 0.72377 | 0.74074 | 0.76051 | 0.78742 | 0.80578 | 0.84085 | 0.85616 | 0.88052 | 0.91036 | 0.92641 | 0.94911 | 0.97272 | 0.98739 | 1 | 1.0195 | 1.039 | 1.0581 | 1.0672 | 1.1045 | 1.191 | 1.2399 | 1.2746 | 1.3103 | 1.347 | 1.3847 | 1.4234
|  | 2018-06-30 |  |  | 0.61499 | 0.64251 | 0.67066 | 0.6908 | 0.70994 | 0.72658 | 0.74597 | 0.77237 | 0.79038 | 0.82478 | 0.83979 | 0.86369 | 0.89296 | 0.9087 | 0.93096 | 0.95413 | 0.96852 | 0.98089 | 1 | 1.0191 | 1.0379 | 1.0468 | 1.0834 | 1.1683 | 1.2162 | 1.2502 | 1.2852 | 1.3212 | 1.3582 | 1.3962
|  | 2019-06-30 |  |  | 0.60346 | 0.63046 | 0.65808 | 0.67784 | 0.69663 | 0.71295 | 0.73198 | 0.75788 | 0.77556 | 0.80931 | 0.82404 | 0.84749 | 0.87621 | 0.89166 | 0.9135 | 0.93623 | 0.95035 | 0.96249 | 0.98124 | 1 | 1.0184 | 1.0272 | 1.0631 | 1.1464 | 1.1934 | 1.2268 | 1.2611 | 1.2964 | 1.3327 | 1.37
|  | 2020-06-30 |  |  | 0.59255 | 0.61907 | 0.64619 | 0.66559 | 0.68404 | 0.70007 | 0.71875 | 0.74418 | 0.76154 | 0.79469 | 0.80915 | 0.83217 | 0.86038 | 0.87554 | 0.89699 | 0.91931 | 0.93318 | 0.94509 | 0.96351 | 0.98193 | 1 | 1.0086 | 1.0439 | 1.1256 | 1.1718 | 1.2046 | 1.2383 | 1.273 | 1.3086 | 1.3453
|  | 2021-06-30 |  |  | 0.58749 | 0.61379 | 0.64067 | 0.65991 | 0.6782 | 0.69409 | 0.71262 | 0.73783 | 0.75504 | 0.78791 | 0.80225 | 0.82507 | 0.85304 | 0.86807 | 0.88934 | 0.91147 | 0.92522 | 0.93703 | 0.95529 | 0.97355 | 0.99147 | 1 | 1.035 | 1.116 | 1.1618 | 1.1943 | 1.2278 | 1.2621 | 1.2975 | 1.3338
|  | 2022-06-30 |  |  | 0.56764 | 0.59304 | 0.61902 | 0.63761 | 0.65528 | 0.67063 | 0.68853 | 0.71289 | 0.72952 | 0.76127 | 0.77513 | 0.79718 | 0.8242 | 0.83873 | 0.85928 | 0.88066 | 0.89394 | 0.90536 | 0.923 | 0.94064 | 0.95796 | 0.9662 | 1 | 1.0783 | 1.1225 | 1.154 | 1.1863 | 1.2195 | 1.2536 | 1.2887
|  | 2023-06-30 |  |  | 0.52641 | 0.54997 | 0.57406 | 0.5913 | 0.60768 | 0.62192 | 0.63852 | 0.66112 | 0.67654 | 0.70598 | 0.71883 | 0.73929 | 0.76434 | 0.77782 | 0.79687 | 0.8167 | 0.82902 | 0.8396 | 0.85596 | 0.87232 | 0.88838 | 0.89602 | 0.92737 | 1 | 1.041 | 1.0701 | 1.1001 | 1.1309 | 1.1626 | 1.1951
|  | 2024-06-30 |  |  | 0.50568 | 0.52831 | 0.55145 | 0.56801 | 0.58375 | 0.59743 | 0.61337 | 0.63508 | 0.64989 | 0.67818 | 0.69052 | 0.71017 | 0.73424 | 0.74718 | 0.76549 | 0.78453 | 0.79636 | 0.80653 | 0.82225 | 0.83797 | 0.85339 | 0.86073 | 0.89085 | 0.96061 | 1 | 1.028 | 1.0568 | 1.0864 | 1.1168 | 1.1481
|  | 2025-06-30 |  |  | 0.4919 | 0.51392 | 0.53643 | 0.55254 | 0.56785 | 0.58116 | 0.59667 | 0.61778 | 0.63219 | 0.65971 | 0.67172 | 0.69083 | 0.71424 | 0.72683 | 0.74464 | 0.76316 | 0.77468 | 0.78457 | 0.79986 | 0.81515 | 0.83015 | 0.83729 | 0.86658 | 0.93445 | 0.97276 | 1 | 1.028 | 1.0568 | 1.0864 | 1.1168
|  | 2026-06-30 |  |  | 0.47851 | 0.49992 | 0.52182 | 0.53749 | 0.55239 | 0.56533 | 0.58042 | 0.60096 | 0.61497 | 0.64174 | 0.65342 | 0.67201 | 0.69479 | 0.70704 | 0.72436 | 0.74238 | 0.75358 | 0.7632 | 0.77807 | 0.79294 | 0.80754 | 0.81449 | 0.84298 | 0.909 | 0.94627 | 0.97276 | 1 | 1.028 | 1.0568 | 1.0864
|  | 2027-06-30 |  |  | 0.46547 | 0.48631 | 0.50761 | 0.52285 | 0.53734 | 0.54993 | 0.56461 | 0.58459 | 0.59822 | 0.62426 | 0.63562 | 0.65371 | 0.67587 | 0.68778 | 0.70463 | 0.72216 | 0.73305 | 0.74241 | 0.75688 | 0.77135 | 0.78555 | 0.79231 | 0.82002 | 0.88425 | 0.9205 | 0.94627 | 0.97276 | 1 | 1.028 | 1.0568
|  | 2028-06-30 |  |  | 0.4528 | 0.47306 | 0.49378 | 0.50861 | 0.52271 | 0.53496 | 0.54923 | 0.56867 | 0.58193 | 0.60726 | 0.61831 | 0.63591 | 0.65746 | 0.66905 | 0.68544 | 0.70249 | 0.71309 | 0.72219 | 0.73627 | 0.75034 | 0.76415 | 0.77073 | 0.79769 | 0.86016 | 0.89543 | 0.9205 | 0.94627 | 0.97276 | 1 | 1.028
|  | 2029-06-30 |  |  | 0.44047 | 0.46018 | 0.48034 | 0.49476 | 0.50847 | 0.52039 | 0.53427 | 0.55318 | 0.56608 | 0.59072 | 0.60147 | 0.61859 | 0.63955 | 0.65083 | 0.66677 | 0.68336 | 0.69367 | 0.70253 | 0.71622 | 0.7299 | 0.74334 | 0.74974 | 0.77596 | 0.83674 | 0.87104 | 0.89543 | 0.9205 | 0.94627 | 0.97276 | 1
Table 2 - To escalate Actual or Forecast Nominal Expenditure to Real, select year(s) and multiply with the index
| CPI indexes (nominal to real) |  | From Nominal (each year) |  | 2000-06-30 | 2001-06-30 | 2002-06-30 | 2003-06-30 | 2004-06-30 | 2005-06-30 | 2006-06-30 | 2007-06-30 | 2008-06-30 | 2009-06-30 | 2010-06-30 | 2011-06-30 | 2012-06-30 | 2013-06-30 | 2014-06-30 | 2015-06-30 | 2016-06-30 | 2017-06-30 | 2018-06-30 | 2019-06-30 | 2020-06-30 | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30 | 2027-06-30 | 2028-06-30 | 2029-06-30
To Real (select year)
|  | 2000-06-30 |  |  | 1.0073 | 0.97835 | 0.93686 | 0.90353 | 0.87817 | 0.85628 | 0.83535 | 0.81021 | 0.78712 | 0.76169 | 0.73894 | 0.72211 | 0.70028 | 0.68272 | 0.66864 | 0.65253 | 0.63975 | 0.63096 | 0.62095 | 0.6092 | 0.59798 | 0.59002 | 0.57748 | 0.54663 | 0.51594 | 0.49874 | 0.48516 | 0.47195 | 0.45909 | 0.44659
|  | 2001-06-30 |  |  | 1.0524 | 1.0221 | 0.97879 | 0.94396 | 0.91747 | 0.8946 | 0.87273 | 0.84647 | 0.82234 | 0.79578 | 0.77201 | 0.75443 | 0.73162 | 0.71327 | 0.69856 | 0.68173 | 0.66838 | 0.6592 | 0.64874 | 0.63646 | 0.62474 | 0.61642 | 0.60332 | 0.5711 | 0.53903 | 0.52106 | 0.50687 | 0.49307 | 0.47964 | 0.46657
|  | 2002-06-30 |  |  | 1.0985 | 1.0669 | 1.0217 | 0.98531 | 0.95767 | 0.93379 | 0.91096 | 0.88355 | 0.85837 | 0.83064 | 0.80583 | 0.78748 | 0.76367 | 0.74452 | 0.72916 | 0.71159 | 0.69766 | 0.68808 | 0.67716 | 0.66434 | 0.65211 | 0.64343 | 0.62975 | 0.59612 | 0.56264 | 0.54389 | 0.52908 | 0.51467 | 0.50065 | 0.48701
|  | 2003-06-30 |  |  | 1.1315 | 1.099 | 1.0524 | 1.0149 | 0.98643 | 0.96183 | 0.93832 | 0.91008 | 0.88414 | 0.85559 | 0.83004 | 0.81112 | 0.78661 | 0.76688 | 0.75106 | 0.73296 | 0.71861 | 0.70874 | 0.6975 | 0.68429 | 0.67169 | 0.66275 | 0.64867 | 0.61402 | 0.57954 | 0.56022 | 0.54497 | 0.53012 | 0.51568 | 0.50164
|  | 2004-06-30 |  |  | 1.1628 | 1.1294 | 1.0815 | 1.043 | 1.0138 | 0.98848 | 0.96432 | 0.9353 | 0.90864 | 0.87929 | 0.85303 | 0.8336 | 0.8084 | 0.78812 | 0.77187 | 0.75327 | 0.73853 | 0.72838 | 0.71682 | 0.70325 | 0.6903 | 0.68111 | 0.66664 | 0.63103 | 0.5956 | 0.57575 | 0.56006 | 0.54481 | 0.52997 | 0.51554
|  | 2005-06-30 |  |  | 1.1901 | 1.1559 | 1.1069 | 1.0675 | 1.0375 | 1.0117 | 0.98692 | 0.95722 | 0.92994 | 0.8999 | 0.87303 | 0.85314 | 0.82735 | 0.8066 | 0.78996 | 0.77093 | 0.75583 | 0.74545 | 0.73362 | 0.71973 | 0.70648 | 0.69707 | 0.68226 | 0.64582 | 0.60955 | 0.58924 | 0.57319 | 0.55758 | 0.54239 | 0.52762
|  | 2006-06-30 |  |  | 1.2218 | 1.1867 | 1.1364 | 1.096 | 1.0652 | 1.0386 | 1.0133 | 0.98276 | 0.95475 | 0.92392 | 0.89632 | 0.8759 | 0.84943 | 0.82812 | 0.81104 | 0.7915 | 0.776 | 0.76535 | 0.7532 | 0.73894 | 0.72533 | 0.71568 | 0.70047 | 0.66306 | 0.62582 | 0.60496 | 0.58849 | 0.57246 | 0.55687 | 0.5417
|  | 2007-06-30 |  |  | 1.2651 | 1.2287 | 1.1766 | 1.1347 | 1.1029 | 1.0754 | 1.0491 | 1.0175 | 0.98854 | 0.95661 | 0.92804 | 0.9069 | 0.87948 | 0.85742 | 0.83974 | 0.81951 | 0.80346 | 0.79243 | 0.77985 | 0.76509 | 0.751 | 0.741 | 0.72526 | 0.68652 | 0.64797 | 0.62637 | 0.60931 | 0.59272 | 0.57657 | 0.56087
|  | 2008-06-30 |  |  | 1.2946 | 1.2574 | 1.204 | 1.1612 | 1.1286 | 1.1005 | 1.0736 | 1.0413 | 1.0116 | 0.97892 | 0.94969 | 0.92805 | 0.9 | 0.87742 | 0.85933 | 0.83862 | 0.8222 | 0.81091 | 0.79804 | 0.78293 | 0.76852 | 0.75828 | 0.74217 | 0.70253 | 0.66308 | 0.64098 | 0.62352 | 0.60654 | 0.59002 | 0.57395
|  | 2009-06-30 |  |  | 1.3509 | 1.3121 | 1.2565 | 1.2117 | 1.1777 | 1.1484 | 1.1203 | 1.0866 | 1.0556 | 1.0215 | 0.99102 | 0.96844 | 0.93917 | 0.91561 | 0.89673 | 0.87512 | 0.85799 | 0.84621 | 0.83278 | 0.81701 | 0.80197 | 0.79129 | 0.77448 | 0.73311 | 0.69194 | 0.66888 | 0.65066 | 0.63294 | 0.6157 | 0.59893
|  | 2010-06-30 |  |  | 1.3755 | 1.336 | 1.2793 | 1.2338 | 1.1992 | 1.1693 | 1.1407 | 1.1064 | 1.0748 | 1.0401 | 1.0091 | 0.98607 | 0.95626 | 0.93228 | 0.91305 | 0.89105 | 0.87361 | 0.86161 | 0.84794 | 0.83188 | 0.81656 | 0.80569 | 0.78857 | 0.74645 | 0.70454 | 0.68105 | 0.6625 | 0.64446 | 0.62691 | 0.60984
|  | 2011-06-30 |  |  | 1.4146 | 1.374 | 1.3157 | 1.2689 | 1.2333 | 1.2026 | 1.1732 | 1.1379 | 1.1054 | 1.0697 | 1.0378 | 1.0141 | 0.98347 | 0.9588 | 0.93903 | 0.9164 | 0.89846 | 0.88612 | 0.87206 | 0.85555 | 0.8398 | 0.82862 | 0.81101 | 0.76769 | 0.72458 | 0.70043 | 0.68135 | 0.6628 | 0.64475 | 0.62719
|  | 2012-06-30 |  |  | 1.4626 | 1.4206 | 1.3603 | 1.3119 | 1.2751 | 1.2433 | 1.2129 | 1.1764 | 1.1429 | 1.106 | 1.0729 | 1.0485 | 1.0168 | 0.9913 | 0.97086 | 0.94747 | 0.92891 | 0.91616 | 0.90162 | 0.88455 | 0.86826 | 0.8567 | 0.8385 | 0.79371 | 0.74914 | 0.72417 | 0.70445 | 0.68526 | 0.6666 | 0.64844
|  | 2013-06-30 |  |  | 1.4884 | 1.4456 | 1.3843 | 1.335 | 1.2976 | 1.2652 | 1.2343 | 1.1972 | 1.163 | 1.1255 | 1.0919 | 1.067 | 1.0347 | 1.0088 | 0.98797 | 0.96417 | 0.94529 | 0.93231 | 0.91751 | 0.90014 | 0.88357 | 0.8718 | 0.85328 | 0.8077 | 0.76234 | 0.73694 | 0.71687 | 0.69734 | 0.67835 | 0.65987
|  | 2014-06-30 |  |  | 1.5248 | 1.481 | 1.4182 | 1.3677 | 1.3294 | 1.2962 | 1.2645 | 1.2265 | 1.1915 | 1.153 | 1.1186 | 1.0931 | 1.0601 | 1.0335 | 1.0122 | 0.98779 | 0.96845 | 0.95515 | 0.93999 | 0.92219 | 0.90521 | 0.89316 | 0.87418 | 0.82749 | 0.78102 | 0.75499 | 0.73443 | 0.71443 | 0.69497 | 0.67604
|  | 2015-06-30 |  |  | 1.5628 | 1.5179 | 1.4535 | 1.4018 | 1.3624 | 1.3285 | 1.296 | 1.257 | 1.2212 | 1.1817 | 1.1464 | 1.1203 | 1.0865 | 1.0592 | 1.0374 | 1.0124 | 0.99254 | 0.97891 | 0.96338 | 0.94514 | 0.92773 | 0.91538 | 0.89593 | 0.84808 | 0.80045 | 0.77377 | 0.7527 | 0.7322 | 0.71226 | 0.69286
|  | 2016-06-30 |  |  | 1.5863 | 1.5408 | 1.4754 | 1.4229 | 1.383 | 1.3485 | 1.3155 | 1.276 | 1.2396 | 1.1996 | 1.1637 | 1.1372 | 1.1028 | 1.0752 | 1.053 | 1.0276 | 1.0075 | 0.99368 | 0.97791 | 0.95939 | 0.94173 | 0.92919 | 0.90944 | 0.86087 | 0.81253 | 0.78545 | 0.76405 | 0.74324 | 0.723 | 0.70331
|  | 2017-06-30 |  |  | 1.6066 | 1.5604 | 1.4943 | 1.4411 | 1.4007 | 1.3657 | 1.3323 | 1.2923 | 1.2554 | 1.2149 | 1.1786 | 1.1517 | 1.1169 | 1.0889 | 1.0665 | 1.0408 | 1.0204 | 1.0064 | 0.9904 | 0.97164 | 0.95375 | 0.94105 | 0.92106 | 0.87186 | 0.8229 | 0.79548 | 0.77381 | 0.75274 | 0.73223 | 0.71229
|  | 2018-06-30 |  |  | 1.6379 | 1.5908 | 1.5234 | 1.4692 | 1.4279 | 1.3923 | 1.3583 | 1.3174 | 1.2799 | 1.2385 | 1.2016 | 1.1742 | 1.1387 | 1.1101 | 1.0872 | 1.061 | 1.0403 | 1.026 | 1.0097 | 0.99058 | 0.97234 | 0.95939 | 0.93901 | 0.88885 | 0.83894 | 0.81098 | 0.78889 | 0.7674 | 0.7465 | 0.72617
|  | 2019-06-30 |  |  | 1.6692 | 1.6212 | 1.5525 | 1.4973 | 1.4552 | 1.419 | 1.3843 | 1.3426 | 1.3043 | 1.2622 | 1.2245 | 1.1966 | 1.1605 | 1.1313 | 1.108 | 1.0813 | 1.0601 | 1.0456 | 1.029 | 1.0095 | 0.99092 | 0.97773 | 0.95695 | 0.90584 | 0.85497 | 0.82648 | 0.80397 | 0.78207 | 0.76077 | 0.74005
|  | 2020-06-30 |  |  | 1.6999 | 1.6511 | 1.5811 | 1.5248 | 1.482 | 1.4451 | 1.4097 | 1.3673 | 1.3284 | 1.2855 | 1.2471 | 1.2186 | 1.1818 | 1.1522 | 1.1284 | 1.1012 | 1.0797 | 1.0648 | 1.0479 | 1.0281 | 1.0092 | 0.99572 | 0.97457 | 0.92251 | 0.87071 | 0.84169 | 0.81877 | 0.79647 | 0.77477 | 0.75367
|  | 2021-06-30 |  |  | 1.7146 | 1.6653 | 1.5947 | 1.5379 | 1.4948 | 1.4575 | 1.4219 | 1.3791 | 1.3398 | 1.2965 | 1.2578 | 1.2291 | 1.192 | 1.1621 | 1.1381 | 1.1107 | 1.0889 | 1.074 | 1.057 | 1.0369 | 1.0178 | 1.0043 | 0.98295 | 0.93045 | 0.8782 | 0.84893 | 0.82581 | 0.80332 | 0.78144 | 0.76016
|  | 2022-06-30 |  |  | 1.7746 | 1.7235 | 1.6505 | 1.5917 | 1.5471 | 1.5085 | 1.4716 | 1.4273 | 1.3867 | 1.3419 | 1.3018 | 1.2721 | 1.2337 | 1.2027 | 1.1779 | 1.1496 | 1.127 | 1.1116 | 1.0939 | 1.0732 | 1.0535 | 1.0394 | 1.0173 | 0.963 | 0.90892 | 0.87863 | 0.8547 | 0.83142 | 0.80878 | 0.78675
|  | 2023-06-30 |  |  | 1.9135 | 1.8585 | 1.7797 | 1.7164 | 1.6682 | 1.6266 | 1.5869 | 1.5391 | 1.4953 | 1.447 | 1.4037 | 1.3718 | 1.3303 | 1.2969 | 1.2702 | 1.2396 | 1.2153 | 1.1986 | 1.1796 | 1.1573 | 1.136 | 1.1208 | 1.097 | 1.0384 | 0.98011 | 0.94744 | 0.92164 | 0.89654 | 0.87212 | 0.84837
|  | 2024-06-30 |  |  | 1.992 | 1.9347 | 1.8527 | 1.7868 | 1.7366 | 1.6933 | 1.6519 | 1.6022 | 1.5566 | 1.5063 | 1.4613 | 1.428 | 1.3848 | 1.3501 | 1.3223 | 1.2904 | 1.2651 | 1.2478 | 1.228 | 1.2047 | 1.1825 | 1.1668 | 1.142 | 1.081 | 1.0203 | 0.98629 | 0.95943 | 0.9333 | 0.90788 | 0.88315
|  | 2025-06-30 |  |  | 2.0478 | 1.9889 | 1.9046 | 1.8368 | 1.7853 | 1.7407 | 1.6982 | 1.6471 | 1.6001 | 1.5485 | 1.5022 | 1.468 | 1.4236 | 1.3879 | 1.3593 | 1.3265 | 1.3006 | 1.2827 | 1.2623 | 1.2384 | 1.2156 | 1.1995 | 1.174 | 1.1113 | 1.0489 | 1.0139 | 0.98629 | 0.95943 | 0.9333 | 0.90788
|  | 2026-06-30 |  |  | 2.1051 | 2.0446 | 1.9579 | 1.8882 | 1.8352 | 1.7895 | 1.7457 | 1.6932 | 1.6449 | 1.5918 | 1.5443 | 1.5091 | 1.4635 | 1.4268 | 1.3973 | 1.3637 | 1.337 | 1.3186 | 1.2977 | 1.2731 | 1.2497 | 1.233 | 1.2068 | 1.1424 | 1.0782 | 1.0423 | 1.0139 | 0.98629 | 0.95943 | 0.9333
|  | 2027-06-30 |  |  | 2.164 | 2.1018 | 2.0127 | 1.9411 | 1.8866 | 1.8396 | 1.7946 | 1.7406 | 1.691 | 1.6364 | 1.5875 | 1.5513 | 1.5044 | 1.4667 | 1.4365 | 1.4019 | 1.3744 | 1.3555 | 1.334 | 1.3088 | 1.2847 | 1.2676 | 1.2406 | 1.1744 | 1.1084 | 1.0715 | 1.0423 | 1.0139 | 0.98629 | 0.95943
|  | 2028-06-30 |  |  | 2.2246 | 2.1607 | 2.0691 | 1.9954 | 1.9394 | 1.8911 | 1.8449 | 1.7893 | 1.7383 | 1.6822 | 1.632 | 1.5948 | 1.5466 | 1.5078 | 1.4767 | 1.4411 | 1.4129 | 1.3935 | 1.3714 | 1.3454 | 1.3206 | 1.303 | 1.2754 | 1.2072 | 1.1394 | 1.1015 | 1.0715 | 1.0423 | 1.0139 | 0.98629
|  | 2029-06-30 |  |  | 2.2869 | 2.2212 | 2.127 | 2.0513 | 1.9937 | 1.944 | 1.8965 | 1.8394 | 1.787 | 1.7293 | 1.6776 | 1.6394 | 1.5899 | 1.55 | 1.518 | 1.4814 | 1.4524 | 1.4325 | 1.4098 | 1.3831 | 1.3576 | 1.3395 | 1.3111 | 1.241 | 1.1713 | 1.1323 | 1.1015 | 1.0715 | 1.0423 | 1.0139

## New STSS 21x132
Estimate Summary
E_RFR_2.12 - 132kV STSS
|  |  |  | Labour Hours | Direct Labour | Indirect Labour | Total Labour | Material | Contracted Services | Contingency | Other/Esc | Total Cost
Total Estimate Cost
|  | Assumptions |  |  |  |  | Total excluding contingency
|  | 1 | No Allowance for Land cost
|  | 2 | Estimate is based on Planning estimate FY24-29
|  | 3 | No allowance for Escalation
|  | 4 | No allowance for any legal or easement cost
|  | 5 | Price includes 40% Contingency
|  | 6 | Civil cost includes ;
Building Size proportionate to Alexandria STS
No Rock excavation allowed
No allowance for cost associated with Aboriginal heritage items
No Allowance for contaminated soil
|  | 7 | 21 ABB GIS Switchgears included
|  | 8 | Protection - As per RFR Design Brief
18 x Feeder Protection scheme
3 x Bus Bar Protectiom
1 x Miscellaneous Signal scheme
1 x Distribution System with HMI
1 x Control Communication scheme
3 x DC Link Panel scheme
1 x LAN A & B panel scheme
2 x Phone & Security Cabinet
4 x HVC PQ Metering scheme
|  | 9 | Two 277AH 110V Battery & Charger
|  | 10 | Two 50V battery & Charger
|  | 11 | Two type 12 DC Bord
|  | 12 | Two Aux Transformers
|  | 13 | 2 Lightning Mast
|  | 14 | Substation light & Power

## New STS 3Tx 9x132 18x33
Estimate Summary
E_RFR_2.10 - 132KV STS (132/33KV)
|  |  |  | Labour Hours | Direct Labour | Indirect Labour | Total Labour | Material | Contracted Services | Contingency | Other/Esc | Total Cost
Total Estimate Cost
| Assumptions | [5 empty] | Total excluding contingency
| 1 | No Allowance for Land cost
| 2 | Estimate is based on Planning estimate FY24-29
| 3 | No allowance for Escalation
| 4 | No allowance for any legal or easement cost
| 5 | Price includes 40% Contingency
| 6 | Civil cost includes ;
Building Size as per Alexandria STS
4 Transformer bays (3 for new TX and one additional for future TX)
No Rock excavation allowed
No allowance for cost associated with Aboriginal heritage items
No Allowance for contaminated soil
| 7 | 3 x 132/33 kV 120MVA transformers included
| 8 | 9 ABB GIS Switchgears included
| 9 | 132KV - Protection
2 x 132 FDR Protection Scheme
3 x 132 Bus Bar protection Scheme
3 x 132KV/11KV TX protection scheme
2 x Miscellaneous Signal scheme
4 x HVC PQ Metering scheme
3 x TX Metering schme
1 x UnderFreq Load Shedding scheme
3 x VR scheme
|  |  | 1 x 132KV Auto closing scheme |  |  |  | Additional Notes
|  |  | 1 x Distribution System with HMI |  |  |  | 1) Remove cost of cap bank is approx. $0.5M reduction
|  |  | 1 x Control Comunication scheme |  |  |  | 2) Remove civl cost of 4th Tx bay is approx. $0.5M reduction
3 x DC Link scheme
1 x LAN A& B Protection shceme
2 x Phone & Security Cabinet
| 10 | 33kV Switchgears
12 x 33kV 1250A Feder protection
3 x Transformer
3 x Bus section
| 11 | 33KV - Protection
12 x 33KV Fdr Protection scheme
3 x DC Link scheme
3 x 33KV Bus bar protection scheme
2 x UnderFreq Load Shedding scheme
| 12 | 33kV Capacitor Bank
Dead tank CB<=1250A
Low Disconnector 1600A
1250A Caps bank Panel
| 13 | Ripple Filter | Ripple filter panel
Dead tank CB<=1250A
Low Disconnector 1600A
| 14 | Two 277AH 110V Battery 7 Charger
| 15 | Two 50V battery & Charger
| 16 | Two type 12 DC Bord
| 17 | Two Aux Transformers
| 18 | 4 Lightning Mast
| 19 | Substation light & Power
Note on K9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: $1M deduction to exclude cap bank and civil cost of 4th Tx bay,

## New STS 3Tx 10x132 18x33
Estimate Summary
E_RFR_2.10 - 132KV STS (132/33KV)
|  |  |  | Labour Hours | Direct Labour | Indirect Labour | Total Labour | Material | Contracted Services | Contingency | Other/Esc | Total Cost
Total Estimate Cost
| Assumptions | [5 empty] | Total excluding contingency
| 1 | No Allowance for Land cost
| 2 | Estimate is based on Planning estimate FY24-29
| 3 | No allowance for Escalation
| 4 | No allowance for any legal or easement cost
| 5 | Price includes 40% Contingency
| 6 | Civil cost includes ;
Building Size as per Alexandria STS
4 Transformer bays (3 for new TX and one additional for future TX)
No Rock excavation allowed
No allowance for cost associated with Aboriginal heritage items
No Allowance for contaminated soil
| 7 | 3 x 132/33 kV 120MVA transformers included
| 8 | 10 ABB GIS Switchgears included
| 9 | 132KV - Protection
2 x 132 FDR Protection Scheme
3 x 132 Bus Bar protection Scheme
3 x 132KV/11KV TX protection scheme
2 x Miscellaneous Signal scheme
4 x HVC PQ Metering scheme
3 x TX Metering schme
1 x UnderFreq Load Shedding scheme
3 x VR scheme
|  |  | 1 x 132KV Auto closing scheme |  |  |  | Additional Notes
|  |  | 1 x Distribution System with HMI |  |  |  | 1) Remove cost of cap bank is approx. $0.5M reduction
|  |  | 1 x Control Comunication scheme |  |  |  | 2) Remove civl cost of 4th Tx bay is approx. $0.5M reduction
3 x DC Link scheme
1 x LAN A& B Protection shceme
2 x Phone & Security Cabinet
| 10 | 33kV Switchgears
12 x 33kV 1250A Feder protection
|  |  | 3 x Transformer | [9 empty] | =
3 x Bus section
| 11 | 33KV - Protection
12 x 33KV Fdr Protection scheme
3 x DC Link scheme
3 x 33KV Bus bar protection scheme
2 x UnderFreq Load Shedding scheme
| 12 | 33kV Capacitor Bank
Dead tank CB<=1250A
Low Disconnector 1600A
1250A Caps bank Panel
| 13 | Ripple Filter | Ripple filter panel
Dead tank CB<=1250A
Low Disconnector 1600A
| 14 | Two 277AH 110V Battery 7 Charger
| 15 | Two 50V battery & Charger
| 16 | Two type 12 DC Bord
| 17 | Two Aux Transformers
| 18 | 4 Lightning Mast
| 19 | Substation light & Power
Note on K9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: $1M deduction to exclude cap bank and civil cost of 4th Tx bay,

## New STS 3Tx 14x132 18x33
Estimate Summary
E_RFR_2.10 - 132KV STS (132/33KV)
|  |  |  | Labour Hours | Direct Labour | Indirect Labour | Total Labour | Material | Contracted Services | Contingency | Other/Esc | Total Cost
Total Estimate Cost
| Assumptions | [5 empty] | Total excluding contingency
| 1 | No Allowance for Land cost
| 2 | Estimate is based on Planning estimate FY24-29
| 3 | No allowance for Escalation
| 4 | No allowance for any legal or easement cost
| 5 | Price includes 40% Contingency
| 6 | Civil cost includes ;
Building Size as per Alexandria STS
4 Transformer bays (3 for new TX and one additional for future TX)
No Rock excavation allowed
No allowance for cost associated with Aboriginal heritage items
No Allowance for contaminated soil
| 7 | 3 x 132/33 kV 120MVA transformers included
| 8 | 14 ABB GIS Switchgears included
| 9 | 132KV - Protection
3 x 132 FDR Protection Scheme
3 x 132 Bus Bar protection Scheme
3 x 132KV/11KV TX protection scheme
2 x Miscellaneous Signal scheme
4 x HVC PQ Metering
3 x TX Metering panel
1 x UnderFreq Load Shedding panel
3 x VR panel
1 x 132KV Auto closing panel
1 x Distribution System with HMI
1 x Control Comunication Panel
3 x DC Link Panel
1 x LAN A& B Protection scheme
2 x Phone & Security Cabinet
| 10 | 33kV Switchgears
12 x 33kV 1250A Feder
3 x Transformer
3 x Bus section
| 11 | 33KV - Protection
12 x 33KV Fdr Protection scheme
3 x DC Link Panel
3 x 33KV Bus bar protection scheme
2 x UnderFreq Load Shedding scheme
| 12 | 33kV Capacitor Bank
Dead tank CB<=1250A
Low Disconnector 1600A
1250A Caps bank Panel
| 13 | Ripple Filter | Ripple filter panel
Dead tank CB<=1250A
Low Disconnector 1600A
| 14 | Two 277AH 110V Battery 7 Charger
| 15 | Two 50V battery & Charger
| 16 | Two type 12 DC Bord
| 17 | Two Aux Transformers
| 18 | 4 Lightning Mast
| 19 | Substation light & Power

## New STSS 5x132
E_RFR_2.2 - 132kV STSS
|  |  | Labour Hours | Direct Labour | Indirect Labour | Total Labour | Material | Contracted Services | Contingency | Other/Esc | Total Cost | Total excluding contingency
Total Estimate Cost
Assumptions
1 | No Allowance for Land cost
2 | Estimate is based on Planning estimate FY24-29
3 | No allowance for Escalation
4 | No allowance for any legal or easement cost
5 | Price includes 40% Contingency
6 | Civil cost includes ;
Building Size proportionate to Alexandria STS
No Rock excavation allowed
No allowance for cost associated with Aboriginal heritage items
No Allowance for contaminated soil
7 | No Transformers - NA
8 | 5 ABB GIS Switchgears included (2x Fdr+ 2Tx +1 BS)
9 | Protection - As per RFR Design Brief
10 | Two 277AH 110V Battery 7 Charger
11 | Two 50V battery & Charger
12 | Two type 12 DC Bord
13 | Two Aux Transformers
14 | 2 Lightning Mast
15 | Substation light & Power

## New 132kV Duct Bank
E_RFR_2.3 - 132kV Double Duct Bank/km - 2000mm2CU1 Cable & Larger trench profile
|  | Labour Hours | Direct Labour | Indirect Labour | Total Labour | Material | Contracted Services | Contingency | Other/Esc | Total Cost | Cost excluding contingency
Total Estimate Cost
Assumptions
1 | Estimate for 1km of 132kV double duct bank (6 ducts)
2 | Assume trenching on Local roadway and include 45m of RMS road
3 | Assume 30% Rock excavation
4 | Assume all local road trenching on day works and RMS as night works
5 | Assume 2 DTS pits, 2 Coms Pit and 4 Cross bonding link boxes per 1km
6 | Assume 2000mm2 132kv CU1 cables (two circuits)
7 | No Allowance for termination works at Substation
8 | No allowance for trenching in substation yard
9 | 40% Contingency
10 | No Allowance for escalation
11 | No allowance for cost associated with Aboriginal heritage items
12 | No Allowance for contaminated soil
E_RFR_2.3 - 132kV Double Duct Bank/km 1600mm2CU1 Cable & Standard trench profile
|  | Labour Hours | Direct Labour | Indirect Labour | Total Labour | Material | Contracted Services | Contingency | Other/Esc | Total Cost | Cost excluding contingency
Total Estimate Cost

## Scaling Factors for UG cables
Distances in kilometres
Lower | Unit factor | Upper | Formula | Scaling factor
Adjustment
0.05 | 0.1 | 0.14 | 0.175 | 1.75
0.15 | 0.2 | 0.24 | 0.275 | 1.375
0.25 | 0.3 | 0.34 | 0.375 | 1.25
0.35 | 0.4 | 0.44 | 0.475 | 1.1875
0.45 | 0.5 | 0.54 | 0.6 | 1.2
0.55 | 0.6 | 0.64 | 0.725 | 1.2083
0.65 | 0.7 | 0.74 | 0.825 | 1.1786
0.75 | 0.8 | 0.84 | 0.9 | 1.125
0.85 | 0.9 | 0.94 | 0.95 | 1.0556
0.95 | 1 | 1.1 | 1 | 1
1.11 | 2 | 2.49 | 1.7 | 0.85
2.5 | 3 | 3.49 | 2.49 | 0.83
3.5 | 4 | 4.49 | 3.24 | 0.81
4.5 | 5 | 5.49 | 3.95 | 0.79
5.5 | 6 | 6.49 | 4.62 | 0.77
6.5 | 7 | 7.49 | 5.25 | 0.75
7.5 | 8 | 8.49 | 5.84 | 0.73
8.5 | 9 | 9.49 | 6.39 | 0.71
9.5 | 10 | 10.49 | 6.9 | 0.69

## 132KV UGOH
E_RFR_2.4 - 132kV UGOH
|  | Labour Hours | Direct Labour | Indirect Labour | Total Labour | Material | Contracted Services | Contingency | Other/Esc | Total Cost | Cost excluding contingency
Total Estimate Cost
Assumptions
1 | Estimate based on 132kV UGOH at Fdr 923 & 924 SJ-10048
2 | No Allowance for access tracks (Access Track may cost approximately $109,066.50/km)
3 | No allowance for site clearing / vegetation removal
4 | No allowance for UG joint bays
5 | Assume Steel pole 32m / 160kN
6 | No allowance for cost associated with Aboriginal heritage items
7 | No Allowance for contaminated soil
8 | No Allowance for Rock Bore
9 | No allowance for Escalation

## Under Bore
E_RFR_2.5 - M2 Under Bore - 6 Ducts (Two Bores x 3 ducts)
|  | Labour Hours | Direct Labour | Indirect Labour | Total Labour | Material | Contracted Services | Contingency | Other/Esc | Total Cost | Cost excluding contingency
Total Estimate Cost
E_RFR_2.5 - M2 Under Bore - 12 Ducts (4 Bores x 3 Ducts)
|  | Labour Hours | Direct Labour | Indirect Labour | Total Labour | Material | Contracted Services | Contingency | Other/Esc | Total Cost | Cost excluding contingency
Total Estimate Cost
Assumptions
1 | Estimate based on Actual cost of HDD Centenary dr SM-28637 in 2020
2 | Assume Bore length is 200m
3 | Quotation price escalated by 15%
4 | Ausgrid hrs based on actuals in SM-28637
5 | No allowance for Escalation

## 132kV Ductline Work
132kV Ductline Work
It assumes half of the cost incurred on Alexandria STS to address cable congestion issues in the vicinity of the new STSS
Project SJ-00270 - 33kV & 132kV ductlines
Construction of cable bridge over a stormwater culvert to facilitate replacement of 132kV fdr 264, installation of 132kV feeder 9RG and a 33kV supply path to Sydney Airport
installation of 850m of 132kV ductlines from Beaconsfield BSP, including the construction of a bridge to cross Alexandria Canal
Gate 3 estimates

## Contestable Connection Works
Contestable Customer Connection Works
Assumptions
For 33kV direct supply
Talavera Rd
It assumes an average distance of 300metres between Talavera Rd site and the customer private substation
Unit Rate | Quantity | Lower Bound Unit Rate | Upper Bound Unit Rate | Scaling Factor | Lower Bound | Baseline | Upper Bound
For each of the three customers requiring 90MVA N-1 supply
0 | 0.3 |  |  | 1.25
33kV cable terminations | 2 |  |  | 1
Combined customer connection costs (4 customers) |  |  |  |  | 12204023.8493 | 13831740.6472 | 17085633.389
Byfield St
It assumes an average distance of 900metres between Byfield St site and the customer private substation
Unit Rate | Quantity | Lower Bound Unit Rate | Upper Bound Unit Rate | Scaling Factor | Lower Bound | Baseline | Upper Bound
For each of the three customers requiring 90MVA N-1 supply
0 | 0.9 |  |  | 1.0556
33kV cable terminations | 2 |  |  | 1
Combined customer connection costs (4 customers) |  |  |  |  | 28325396.1 | 32293328.4723 | 39655554.54
For 132kV direct supply
Zone Substation works
A 132kV busbar with 6x132kV GIS indoor circuit breakers (refer to block estimate for New STSS 5x132) plus extra circuit breaker (material costs only).
2 x 120MVA 132/33kV transformers
Values in real FY24 dollars
Unit Rate | Quantity | Lower Bound Unit Rate | Upper Bound Unit Rate |  | Lower Bound | Baseline | Upper Bound
STSS ID 5x132kV indoor GIS circuit breakers | 1
TX 120MVA | 2
Extra 132kV switchgear (indoor GIS) | 1 | [6 empty] | Only material costs included. It assumes labour + PM + installation costs can be absorbed by the other components
[5 empty] | 23505396.2427 | 26439560.5049 | 32907554.7397
STSS ID 5x132kV indoor GIS circuit breakers | 1
TX 60MVA | 2
Extra 132kV switchgear (indoor GIS) | 1 | [6 empty] | Only material costs included. It assumes labour + PM + installation costs can be absorbed by the other components
[5 empty] | 21193894.4844 | 23781333.4706 | 29671452.2782
132kV cable connection works
Site 1
It assumes a distance of 900metres between Site 1 and the customer private substation
Unit Rate | Quantity | Lower Bound Unit Rate | Upper Bound Unit Rate | Scaling Factor | Lower Bound | Baseline | Upper Bound
11C Urban 132kvUG (800mm 2CS) | 0.9 |  |  | 1.0556
132kV cable terminations | 2 |  |  | 1
Or
If the six ducts required for these two circuits can be installed in a trench with same width as the 33kV case
11C Urban 132kvUG (800mm 2CS) using 33kV trench profile extended | 0.9 |  |  | 1.0556
132kV cable terminations | 2 |  |  | 1
Average customer connection cost |  |  |  |  | 32077305.0075 | 36227724.9283 | 44908227.0105
Combined customer connection costs (4 customers) |  |  |  |  | 125538551.274 | 141764468.8049 | 175753971.7837
Site 2
It assumes a distance of 300metres between Site 2 and the customer private substation
Unit Rate | Quantity | Lower Bound Unit Rate | Upper Bound Unit Rate | Scaling Factor | Lower Bound | Baseline | Upper Bound
11C Urban 132kvUG (800mm 2CS) | 0.3 |  |  | 1.25
132kV cable terminations | 2 |  |  | 1
Or
If the six ducts required for these two circuits can be installed in a trench with same width as the 33kV case
11C Urban 132kvUG (800mm 2CS) using 33kV trench profile extended | 0.3 |  |  | 1.25
132kV cable terminations | 2 |  |  | 1
Average customer connection cost |  |  |  |  | 27166961.3063 | 30598801.438 | 38033745.8288
Combined customer connection costs (4 customers) |  |  |  |  | 105897176.4693 | 119248774.8434 | 148256047.057
There are also space implications and expertise implications.
For 132kV direct supply from Site 3
Unit Rate | Quantity | Lower Bound Unit Rate | Upper Bound Unit Rate | Scaling Factor | Lower Bound | Baseline | Upper Bound
11C Urban 132kvUG (800mm 2CS) | 3.5 |  |  | 0.81
Allowance for Bore under M2 | 1 |  |  | 1
132kV cable terminations | 2 |  |  | 1
[5 empty] | 51193274.7092 | 58144772.5436 | 71670584.5929
Combined customer connection costs (4 customers) |  |  |  |  | 180746785.4339 | 205033119.0687 | 253045499.6075

## 132kV Termination
E_RFR_2.3 - TERMINATION AT SUB - Per Circuit
|  | Labour Hours | Direct Labour | Indirect Labour | Total Labour | Material | Contracted Services | Contingency | Other/Esc | Total Cost | Cost excluding contingency
Total Estimate Cost
Assumptions
1 | No trenching inside the sub alowed
2 | Estimate is only for terminate 132kV 200mm2 CU1 cable one circiut only (3 cables for 1 circuit)
3 | No Operator hrs allowed (New Substation)
4 | Fibber termination not include (include in substation estimate)

## OPWG Installation
E_RFR_2.8 - OPGW Cable Replacement
|  |  | Labour Hours | Direct Labour | Indirect Labour | Total Labour | Material | Contracted Services | Contingency | Other/Esc | Total Cost | Cost excluding contingency
Total Estimate Cost
Assumptions
| 1 | Estimate based on OPGW cable install in towers SM-27603
| 2 | No Allowance for access tracks (exsisting twoers - access track clearing works will be done under maintenance contract )
| 3 | Minimum vegitation clearance allowed
| 4 | Cost per km. Assume pulling cable span 1740m.
| 5 | Assume 6 towers per 1740m span (include two termination towres)
| 6 | No allowance for cost associated with Aboriginal heritage items
| 7 | No allowance for Escalation

## Land Clearing
E_RFR_2.6 - Clearing national Park
|  | Labour Hours | Direct Labour | Indirect Labour | Total Labour | Material | Contracted Services | Contingency | Other/Esc | Total Cost | Cost excluding contingency
Total Estimate Cost
Assumptions
1 | Assume 25 large trees per 1000m2
2 | No Allowance for external project development cost
3 | No Allowance for Environmental approvals, ESR's
4 | No allowance for Escalation