## Cover
CitiPower
Regulatory proposal 2026-31
CBD security of supply
| Model number: | 3.01
2025-01-31
12

## Summary
CitiPower
CBD security of supply
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Construct new feeders from MG to JA |  | -10.2153 | 16.338 | 6.1227
| Option 3 | Construct new feeders from MG to JA and rebuild J |  | -43.2369 | 19.7171 | -23.5198
| Option 4 | Rebuild J zone substation |  | -33.0216 | 19.4019 | -13.6198
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | Construct new feeders from MG to JA |  | 6.1227
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 8.813 | 10.3165 | 0 | 0 | 0 |  | 19.1295
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
| Capex and risk ($M, 2026) |  | Value of expected unserved energy ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 6.1227 | -23.5198 | -13.6198 |  |  | Option 2
| Capex 10% higher |  | 0 | 5.1012 | -27.8435 | -16.9219 |  |  | Option 2
| Capex 10% lower |  | 0 | 7.1443 | -19.1961 | -10.3176 |  |  | Option 2
| Total benefits 10% higher |  | 0 | 7.7565 | -21.5481 | -11.6796 |  |  | Option 2
| Total benefits 10% lower |  | 0 | 4.4889 | -25.4915 | -15.5599 |  |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  | 0 | 3.4674 | -29.8152 | -18.8621 |  |  | Option 2
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
CitiPower
CBD security of supply
Project
|  | Business: | CitiPower
|  | Descripton: | CBD security of supply
|  | Date of cost inputs: | December |  | 2023
|  | Option | Description
|  | Option 1 (base case) | No change to existing practices
|  | Option 2 | Construct new feeders from MG to JA
|  | Option 3 | Construct new feeders from MG to JA and rebuild J
|  | Option 4 | Rebuild J zone substation
Option 5
|  | Compliance project | No
|  | Expenditure starts | 2025-26 | [start]
Timing & WACC
|  | Input dollars |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  | 3.5% | [real_disc]
|  | VCR date |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  | 20 | [years]\
|  | Output dollars |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | JA |  | Little Bourke Street | 53187.1756 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  | 1
|  | Harm to property from bushfire |  |  | 1
|  | Harm to environment |  |  | 1
|  | Safety - Public trespass |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  | 3
|  | Safety from bushfire in HBRA |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  | 10
^ Public or employee
|  | Incident type |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  | 20%
Other benefits
| ENVIRONMENTAL | [7 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  | Value
|  | Reliability in worst-served areas |  |  | 0 | 2023-12-31 | per MWh
|  | Network resilience |  |  | 0 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  | 4220.9954 | 2023-12-31 | per MWh
|  | Aesthetics |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Communication |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[5 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  | 10% | -10%

## Option1 (base case)
CitiPower
CBD security of supply
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2025-06-30 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0.05164 | 0.26939 | 0.80117 | 1.8215 | 3.4732 | 6.2295 | 12.121 | 23.3084 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513
| Energy at risk value | $/MWh | 53187.1756 | 2023-12-31 |  | 2746.5924 | 14327.9287 | 42612.1338 | 96878.5908 | 184730.87 | 331327.8236 | 644684.1318 | 1239706.7792 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145
| Safety consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 2746.5924 | 14327.9287 | 42612.1338 | 96878.5908 | 184730.87 | 331327.8236 | 644684.1318 | 1239706.7792 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
CitiPower
CBD security of supply
OPTION 2 | Construct new feeders from MG to JA
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Jumbo feeders from MG ZSS |  | 50 | 2023-12-31 | 0 | 7918867.3 | 9269805.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 7918867.3 | 9269805.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0.05164 | 0.26939 | 0 | 0 | 0 | 0.70768 | 1.6936 | 3.6944 | 6.5695 | 6.5695 | 6.5695 | 6.5695 | 6.5695 | 6.5695 | 6.5695 | 6.5695 | 6.5695 | 6.5695 | 6.5695 | 6.5695 | 6.5695 | 6.5695 | 6.5695 | 6.5695 | 6.5695
| Energy at risk value | $/MWh | 53187.1756 | 2023-12-31 | 2746.5924 | 14327.9287 | 0 | 0 | 0 | 37639.5361 | 90078.1558 | 196494.1399 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 2746.5924 | 14327.9287 | 0 | 0 | 0 | 37639.5361 | 90078.1558 | 196494.1399 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621 | 349415.0621
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 42612.1338 | 96878.5908 | 184730.87 | 293688.2875 | 554605.9761 | 1043212.6393 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524
Capital expenditure
| Jumbo feeders from MG ZSS |  |  | 2023-12-31 | 0 | -7918867.3 | -9269805.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Jumbo feeders from MG ZSS |  |  | 2023-12-31 | 0 | -7918867.3 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099 | -17188673.0099
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Jumbo feeders from MG ZSS |  |  | 2023-12-31 | 0 | 0 | -337610.6886 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | -337610.6886 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | -337610.6886 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 42612.1338 | 96878.5908 | 184730.87 | 293688.2875 | 554605.9761 | 1043212.6393 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | -294998.5548 | -635938.3022 | -548086.0229 | -439128.6054 | -178210.9169 | 310395.7464 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595
| First capex year |  |  | 2
| First year |  |  | 2
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | 0 | -294998.5548 | -635938.3022 | -548086.0229 | -439128.6054 | -178210.9169 | 310395.7464 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595
| Total annualised capex |  |  |  | 0 | 0 | -337610.6886 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929 | -732816.8929
| Total benefits |  |  |  | 0 | 0 | 42612.1338 | 96878.5908 | 184730.87 | 293688.2875 | 554605.9761 | 1043212.6393 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524 | 1621238.2524
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | 0 | -328759.6236 | -709219.9915 | -621367.7122 | -512410.2947 | -251492.6062 | 237114.0571 | 815139.6702 | 815139.6702 | 815139.6702 | 815139.6702 | 815139.6702 | 815139.6702 | 815139.6702 | 815139.6702 | 815139.6702 | 815139.6702 | 815139.6702 | 815139.6702 | 815139.6702 | 815139.6702 | 815139.6702 | 815139.6702 | 815139.6702
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | 0 | -261237.4859 | -562656.6129 | -474804.3336 | -365846.9161 | -104929.2276 | 383677.4356 | 961703.0488 | 961703.0488 | 961703.0488 | 961703.0488 | 961703.0488 | 961703.0488 | 961703.0488 | 961703.0488 | 961703.0488 | 961703.0488 | 961703.0488 | 961703.0488 | 961703.0488 | 961703.0488 | 961703.0488 | 961703.0488 | 961703.0488
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | 0 | -290737.3414 | -626250.4431 | -529612.9359 | -409759.7766 | -122750.3193 | 414717.0103 | 1050545.1847 | 1050545.1847 | 1050545.1847 | 1050545.1847 | 1050545.1847 | 1050545.1847 | 1050545.1847 | 1050545.1847 | 1050545.1847 | 1050545.1847 | 1050545.1847 | 1050545.1847 | 1050545.1847 | 1050545.1847 | 1050545.1847 | 1050545.1847 | 1050545.1847
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | 0 | -299259.7681 | -645626.1613 | -566559.1099 | -468497.4342 | -233671.5145 | 206074.4824 | 726297.5342 | 726297.5342 | 726297.5342 | 726297.5342 | 726297.5342 | 726297.5342 | 726297.5342 | 726297.5342 | 726297.5342 | 726297.5342 | 726297.5342 | 726297.5342 | 726297.5342 | 726297.5342 | 726297.5342 | 726297.5342 | 726297.5342
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | 0 | -333020.837 | -718907.8505 | -639840.7992 | -541779.1234 | -306953.2038 | 132792.7931 | 653015.8449 | 653015.8449 | 653015.8449 | 653015.8449 | 653015.8449 | 653015.8449 | 653015.8449 | 653015.8449 | 653015.8449 | 653015.8449 | 653015.8449 | 653015.8449 | 653015.8449 | 653015.8449 | 653015.8449 | 653015.8449 | 653015.8449
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | -294998.5548 | -635938.3022 | -548086.0229 | -439128.6054 | -178210.9169 | 310395.7464 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | -294998.5548 | -635938.3022 | -548086.0229 | -439128.6054 | -178210.9169 | 310395.7464 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | -294998.5548 | -635938.3022 | -548086.0229 | -439128.6054 | -178210.9169 | 310395.7464 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595 | 888421.3595

## Option3
CitiPower
CBD security of supply
OPTION 3 | Construct new feeders from MG to JA and rebuild J
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Jumbo feeders MG ZSS to Docklands & rebuild J ZSS |  | 50 | 2023-12-31 | 0 | 7918867.3 | 27869805.7099 | 24800000 | 18600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 7918867.3 | 27869805.7099 | 24800000 | 18600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0.05164 | 0.26939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 53187.1756 | 2023-12-31 | 2746.5924 | 14327.9287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 2746.5924 | 14327.9287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 42612.1338 | 96878.5908 | 184730.87 | 331327.8236 | 644684.1318 | 1239706.7792 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145
Capital expenditure
| Jumbo feeders MG ZSS to Docklands & rebuild J ZSS |  |  | 2023-12-31 | 0 | -7918867.3 | -27869805.7099 | -24800000 | -18600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Jumbo feeders MG ZSS to Docklands & rebuild J ZSS |  |  | 2023-12-31 | 0 | -7918867.3 | -35788673.0099 | -60588673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099 | -79188673.0099
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Jumbo feeders MG ZSS to Docklands & rebuild J ZSS |  |  | 2023-12-31 | 0 | 0 | -337610.6886 | -1525803.8909 | -2583119.8881 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | -337610.6886 | -1525803.8909 | -2583119.8881 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | -337610.6886 | -1525803.8909 | -2583119.8881 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 42612.1338 | 96878.5908 | 184730.87 | 331327.8236 | 644684.1318 | 1239706.7792 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | -294998.5548 | -1428925.3001 | -2398389.0181 | -3044779.0624 | -2731422.7542 | -2136400.1068 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715
| First capex year |  |  | 2
| First year |  |  | 2
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | 0 | -294998.5548 | -1428925.3001 | -2398389.0181 | -3044779.0624 | -2731422.7542 | -2136400.1068 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715
| Total annualised capex |  |  |  | 0 | 0 | -337610.6886 | -1525803.8909 | -2583119.8881 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861 | -3376106.8861
| Total benefits |  |  |  | 0 | 0 | 42612.1338 | 96878.5908 | 184730.87 | 331327.8236 | 644684.1318 | 1239706.7792 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | 0 | -328759.6236 | -1581505.6892 | -2656701.0069 | -3382389.751 | -3069033.4428 | -2474010.7954 | -1743064.2601 | -1743064.2601 | -1743064.2601 | -1743064.2601 | -1743064.2601 | -1743064.2601 | -1743064.2601 | -1743064.2601 | -1743064.2601 | -1743064.2601 | -1743064.2601 | -1743064.2601 | -1743064.2601 | -1743064.2601 | -1743064.2601 | -1743064.2601 | -1743064.2601
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | 0 | -261237.4859 | -1276344.911 | -2140077.0293 | -2707168.3738 | -2393812.0656 | -1798789.4182 | -1067842.8829 | -1067842.8829 | -1067842.8829 | -1067842.8829 | -1067842.8829 | -1067842.8829 | -1067842.8829 | -1067842.8829 | -1067842.8829 | -1067842.8829 | -1067842.8829 | -1067842.8829 | -1067842.8829 | -1067842.8829 | -1067842.8829 | -1067842.8829 | -1067842.8829
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | 0 | -290737.3414 | -1419237.441 | -2379915.9311 | -3011646.2801 | -2666954.341 | -2012429.4289 | -1208388.2401 | -1208388.2401 | -1208388.2401 | -1208388.2401 | -1208388.2401 | -1208388.2401 | -1208388.2401 | -1208388.2401 | -1208388.2401 | -1208388.2401 | -1208388.2401 | -1208388.2401 | -1208388.2401 | -1208388.2401 | -1208388.2401 | -1208388.2401 | -1208388.2401
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | 0 | -299259.7681 | -1438613.1592 | -2416862.1051 | -3077911.8448 | -2795891.1674 | -2260370.7847 | -1602518.903 | -1602518.903 | -1602518.903 | -1602518.903 | -1602518.903 | -1602518.903 | -1602518.903 | -1602518.903 | -1602518.903 | -1602518.903 | -1602518.903 | -1602518.903 | -1602518.903 | -1602518.903 | -1602518.903 | -1602518.903 | -1602518.903
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | 0 | -333020.837 | -1591193.5483 | -2675174.0939 | -3415522.5334 | -3133501.856 | -2597981.4734 | -1940129.5916 | -1940129.5916 | -1940129.5916 | -1940129.5916 | -1940129.5916 | -1940129.5916 | -1940129.5916 | -1940129.5916 | -1940129.5916 | -1940129.5916 | -1940129.5916 | -1940129.5916 | -1940129.5916 | -1940129.5916 | -1940129.5916 | -1940129.5916 | -1940129.5916
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | -294998.5548 | -1428925.3001 | -2398389.0181 | -3044779.0624 | -2731422.7542 | -2136400.1068 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | -294998.5548 | -1428925.3001 | -2398389.0181 | -3044779.0624 | -2731422.7542 | -2136400.1068 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | -294998.5548 | -1428925.3001 | -2398389.0181 | -3044779.0624 | -2731422.7542 | -2136400.1068 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715 | -1405453.5715

## Option4
CitiPower
CBD security of supply
OPTION 4 | Rebuild J zone substation
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Rebuilding J ZSS and offloading JA ZSS. |  | 50 | 2023-12-31 | 0 | 0 | 18600000 | 24800000 | 18600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 18600000 | 24800000 | 18600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0.05164 | 0.26939 | 0.80117 | 1.8215 | 3.4732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 53187.1756 | 2023-12-31 | 2746.5924 | 14327.9287 | 42612.1338 | 96878.5908 | 184730.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 2746.5924 | 14327.9287 | 42612.1338 | 96878.5908 | 184730.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 331327.8236 | 644684.1318 | 1239706.7792 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145
Capital expenditure
| Rebuilding J ZSS and offloading JA ZSS. |  |  | 2023-12-31 | 0 | 0 | -18600000 | -24800000 | -18600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Rebuilding J ZSS and offloading JA ZSS. |  |  | 2023-12-31 | 0 | 0 | -18600000 | -43400000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000 | -62000000
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Rebuilding J ZSS and offloading JA ZSS. |  |  | 2023-12-31 | 0 | 0 | 0 | -792986.9979 | -1850302.9952 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | -792986.9979 | -1850302.9952 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | -792986.9979 | -1850302.9952 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 331327.8236 | 644684.1318 | 1239706.7792 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | -792986.9979 | -1850302.9952 | -2311962.1695 | -1998605.8613 | -1403583.2139 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786
| First capex year |  |  | 3
| First year |  |  | 3
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | 0 | 0 | -792986.9979 | -1850302.9952 | -2311962.1695 | -1998605.8613 | -1403583.2139 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786
| Total annualised capex |  |  |  | 0 | 0 | 0 | -792986.9979 | -1850302.9952 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931 | -2643289.9931
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 331327.8236 | 644684.1318 | 1239706.7792 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145 | 1970653.3145
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | 0 | 0 | -872285.6977 | -2035333.2947 | -2576291.1688 | -2262934.8606 | -1667912.2132 | -936965.6779 | -936965.6779 | -936965.6779 | -936965.6779 | -936965.6779 | -936965.6779 | -936965.6779 | -936965.6779 | -936965.6779 | -936965.6779 | -936965.6779 | -936965.6779 | -936965.6779 | -936965.6779 | -936965.6779 | -936965.6779 | -936965.6779
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | 0 | 0 | -713688.2981 | -1665272.6957 | -2047633.1702 | -1734276.862 | -1139254.2146 | -408307.6793 | -408307.6793 | -408307.6793 | -408307.6793 | -408307.6793 | -408307.6793 | -408307.6793 | -408307.6793 | -408307.6793 | -408307.6793 | -408307.6793 | -408307.6793 | -408307.6793 | -408307.6793 | -408307.6793 | -408307.6793 | -408307.6793
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | 0 | 0 | -792986.9979 | -1850302.9952 | -2278829.3871 | -1934137.4481 | -1279612.536 | -475571.3471 | -475571.3471 | -475571.3471 | -475571.3471 | -475571.3471 | -475571.3471 | -475571.3471 | -475571.3471 | -475571.3471 | -475571.3471 | -475571.3471 | -475571.3471 | -475571.3471 | -475571.3471 | -475571.3471 | -475571.3471 | -475571.3471
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | 0 | 0 | -792986.9979 | -1850302.9952 | -2345094.9518 | -2063074.2745 | -1527553.8918 | -869702.01 | -869702.01 | -869702.01 | -869702.01 | -869702.01 | -869702.01 | -869702.01 | -869702.01 | -869702.01 | -869702.01 | -869702.01 | -869702.01 | -869702.01 | -869702.01 | -869702.01 | -869702.01 | -869702.01
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | 0 | 0 | -872285.6977 | -2035333.2947 | -2609423.9512 | -2327403.2738 | -1791882.8911 | -1134031.0093 | -1134031.0093 | -1134031.0093 | -1134031.0093 | -1134031.0093 | -1134031.0093 | -1134031.0093 | -1134031.0093 | -1134031.0093 | -1134031.0093 | -1134031.0093 | -1134031.0093 | -1134031.0093 | -1134031.0093 | -1134031.0093 | -1134031.0093 | -1134031.0093
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | -792986.9979 | -1850302.9952 | -2311962.1695 | -1998605.8613 | -1403583.2139 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | -792986.9979 | -1850302.9952 | -2311962.1695 | -1998605.8613 | -1403583.2139 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | -792986.9979 | -1850302.9952 | -2311962.1695 | -1998605.8613 | -1403583.2139 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786 | -672636.6786

## Option5
CitiPower
CBD security of supply
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 53187.1756 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
CitiPower
CBD security of supply
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2025-06-30 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 23714702.3067 | 2026-06-30 |  | 3056.7174 | 15945.733 | 47423.5826 | 107817.4088 | 205589.3214 | 368738.925 | 717477.1233 | 1379685.3525 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 19735239.6953 | 2026-06-30 |  | 3056.7174 | 15945.733 | 47423.5826 | 107817.4088 | 205589.3214 | 368738.925 | 717477.1233 | 1379685.3525 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 4102824.193 | 2026-06-30 |  | 3056.7174 | 15945.733 | 0 | 0 | 0 | 41889.5157 | 100249.1188 | 218680.8133 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415
Option 2 | Capital expenditure | Option 2Capital expenditure | -17836084.2626 | 2026-06-30 |  | 0 | -8813007.5635 | -10316484.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 3397228.6601 | 2026-06-30 |  | 3056.7174 | 15945.733 | 0 | 0 | 0 | 41889.5157 | 100249.1188 | 218680.8133 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 388868.4415 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -10215286.6082 | 2026-06-30 |  | 0 | 0 | -375731.2049 | -815561.1877 | -815561.1877 | -815561.1877 | -815561.1877 | -815561.1877 | -815561.1877 | -815561.1877 | -815561.1877 | -815561.1877 | -815561.1877 | -815561.1877 | -815561.1877 | -815561.1877 | -815561.1877 | -815561.1877 | -815561.1877 | -815561.1877 | -815561.1877 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 16338011.0352 | 2026-06-30 |  | 0 | 0 | 47423.5826 | 107817.4088 | 205589.3214 | 326849.4093 | 617228.0045 | 1161004.5392 | 1804296.5539 | 1804296.5539 | 1804296.5539 | 1804296.5539 | 1804296.5539 | 1804296.5539 | 1804296.5539 | 1804296.5539 | 1804296.5539 | 1804296.5539 | 1804296.5539 | 1804296.5539 | 1804296.5539 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | 0 | -328307.6223 | -707743.7788 | -609971.8662 | -488711.7784 | -198333.1831 | 345443.3515 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 6122724.4271 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -10215286.6082 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 16338011.0352 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 18148.3579 | 2026-06-30 |  | 3056.7174 | 15945.733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Capital expenditure | Option 3Capital expenditure | -79031053.5765 | 2026-06-30 |  | 0 | -8813007.5635 | -31016659.2277 | -27600233.6311 | -20700175.2233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 18148.3579 | 2026-06-30 |  | 3056.7174 | 15945.733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -43236926.842 | 2026-06-30 |  | 0 | 0 | -375731.2049 | -1698086.4461 | -2874786.7907 | -3757312.0492 | -3757312.0492 | -3757312.0492 | -3757312.0492 | -3757312.0492 | -3757312.0492 | -3757312.0492 | -3757312.0492 | -3757312.0492 | -3757312.0492 | -3757312.0492 | -3757312.0492 | -3757312.0492 | -3757312.0492 | -3757312.0492 | -3757312.0492 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 19717091.3374 | 2026-06-30 |  | 0 | 0 | 47423.5826 | 107817.4088 | 205589.3214 | 368738.925 | 717477.1233 | 1379685.3525 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | 0 | -328307.6223 | -1590269.0373 | -2669197.4693 | -3388573.1241 | -3039834.9259 | -2377626.6967 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | -23519835.5045 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -43236926.842 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 19717091.3374 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 333354.454 | 2026-06-30 |  | 3056.7174 | 15945.733 | 47423.5826 | 107817.4088 | 205589.3214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | -61194969.314 | 2026-06-30 |  | 0 | 0 | -20700175.2233 | -27600233.6311 | -20700175.2233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 333354.454 | 2026-06-30 |  | 3056.7174 | 15945.733 | 47423.5826 | 107817.4088 | 205589.3214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | -33021640.2338 | 2026-06-30 |  | 0 | 0 | 0 | -882525.2584 | -2059225.603 | -2941750.8615 | -2941750.8615 | -2941750.8615 | -2941750.8615 | -2941750.8615 | -2941750.8615 | -2941750.8615 | -2941750.8615 | -2941750.8615 | -2941750.8615 | -2941750.8615 | -2941750.8615 | -2941750.8615 | -2941750.8615 | -2941750.8615 | -2941750.8615 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 19401885.2413 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 368738.925 | 717477.1233 | 1379685.3525 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 2193164.9955 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | -882525.2584 | -2059225.603 | -2573011.9365 | -2224273.7382 | -1562065.509 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | -13619754.9925 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | -33021640.2338 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 19401885.2413 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0.81556 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 0.0030567 | 0.015946 | 0.047424 | 0.10782 | 0.20559 | 0.36874 | 0.71748 | 1.3797 | 2.1932 | 2.1932 | 2.1932 | 2.1932 | 2.1932 | 2.1932 | 2.1932 | 2.1932 | 2.1932 | 2.1932 | 2.1932 | 2.1932 | 2.1932 | 2.1932 | 2.1932 | 2.1932 | 2.1932
[6 empty] | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
Energy at risk | Energy at risk (weighted) | 37.0513 |  |  | Energy at risk energy at risk (weighted) | 0.05164 | 0.26939 | 0.80117 | 1.8215 | 3.4732 | 6.2295 | 12.121 | 23.3084 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513
Option 1 (base case) | Energy at risk value | 1.9707 |  |  | Option 1 (base case) risk cost | 0.0027466 | 0.014328 | 0.042612 | 0.096879 | 0.18473 | 0.33133 | 0.64468 | 1.2397 | 1.9707 | 1.9707 | 1.9707 | 1.9707 | 1.9707 | 1.9707 | 1.9707 | 1.9707 | 1.9707 | 1.9707 | 1.9707 | 1.9707 | 1.9707 | 1.9707 | 1.9707 | 1.9707 | 1.9707

## Sensitivity_calcs
CitiPower
CBD security of supply
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
[7 empty] | 45838 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
PV
[25 empty] | 988735.3663 | 988735.3663 | 988735.3663 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 6122724.4271 |  | 0 | 0 | 0 | -328307.6223 | -707743.7788 | -609971.8662 | -488711.7784 | -198333.1831 | 345443.3515 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 5101195.7662 |  | 0 | 0 | 0 | -365880.7428 | -789299.8976 | -691527.985 | -570267.8971 | -279889.3019 | 263887.2327 | 907179.2475 | 907179.2475 | 907179.2475 | 907179.2475 | 907179.2475 | 907179.2475 | 907179.2475 | 907179.2475 | 907179.2475 | 907179.2475 | 907179.2475 | 907179.2475 | 907179.2475 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 7144253.0879 |  | 0 | 0 | 0 | -290734.5018 | -626187.6601 | -528415.7475 | -407155.6596 | -116777.0644 | 426999.4703 | 1070291.4851 | 1070291.4851 | 1070291.4851 | 1070291.4851 | 1070291.4851 | 1070291.4851 | 1070291.4851 | 1070291.4851 | 1070291.4851 | 1070291.4851 | 1070291.4851 | 1070291.4851 | 1070291.4851 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 7756525.5306 |  | 0 | 0 | 0 | -323565.264 | -696962.038 | -589412.9341 | -456026.8374 | -136610.3827 | 461543.8054 | 1169165.0217 | 1169165.0217 | 1169165.0217 | 1169165.0217 | 1169165.0217 | 1169165.0217 | 1169165.0217 | 1169165.0217 | 1169165.0217 | 1169165.0217 | 1169165.0217 | 1169165.0217 | 1169165.0217 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 4488923.3235 |  | 0 | 0 | 0 | -333049.9805 | -718525.5197 | -630530.7984 | -521396.7193 | -260055.9836 | 229342.8976 | 808305.7109 | 808305.7109 | 808305.7109 | 808305.7109 | 808305.7109 | 808305.7109 | 808305.7109 | 808305.7109 | 808305.7109 | 808305.7109 | 808305.7109 | 808305.7109 | 808305.7109 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 3467394.6627 |  | 0 | 0 | 0 | -370623.101 | -800081.6385 | -712086.9171 | -602952.8381 | -341612.1024 | 147786.7788 | 726749.5921 | 726749.5921 | 726749.5921 | 726749.5921 | 726749.5921 | 726749.5921 | 726749.5921 | 726749.5921 | 726749.5921 | 726749.5921 | 726749.5921 | 726749.5921 | 726749.5921 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 6122724.4271 |  | 0 | 0 | 0 | -328307.6223 | -707743.7788 | -609971.8662 | -488711.7784 | -198333.1831 | 345443.3515 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 6122724.4271 |  | 0 | 0 | 0 | -328307.6223 | -707743.7788 | -609971.8662 | -488711.7784 | -198333.1831 | 345443.3515 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 6122724.4271 |  | 0 | 0 | 0 | -328307.6223 | -707743.7788 | -609971.8662 | -488711.7784 | -198333.1831 | 345443.3515 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 988735.3663 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | -328307.6223 | -1590269.0373 | -2669197.4693 | -3388573.1241 | -3039834.9259 | -2377626.6967 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | -23519835.5045 |  | 0 | 0 | 0 | -328307.6223 | -1590269.0373 | -2669197.4693 | -3388573.1241 | -3039834.9259 | -2377626.6967 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | -27843528.1887 |  | 0 | 0 | 0 | -365880.7428 | -1760077.6819 | -2956676.1483 | -3764304.329 | -3415566.1308 | -2753357.9016 | -1939878.2586 | -1939878.2586 | -1939878.2586 | -1939878.2586 | -1939878.2586 | -1939878.2586 | -1939878.2586 | -1939878.2586 | -1939878.2586 | -1939878.2586 | -1939878.2586 | -1939878.2586 | -1939878.2586 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | -19196142.8203 |  | 0 | 0 | 0 | -290734.5018 | -1420460.3927 | -2381718.7902 | -3012841.9192 | -2664103.721 | -2001895.4918 | -1188415.8488 | -1188415.8488 | -1188415.8488 | -1188415.8488 | -1188415.8488 | -1188415.8488 | -1188415.8488 | -1188415.8488 | -1188415.8488 | -1188415.8488 | -1188415.8488 | -1188415.8488 | -1188415.8488 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | -21548126.3708 |  | 0 | 0 | 0 | -323565.264 | -1579487.2964 | -2648638.5371 | -3351699.2316 | -2968087.2135 | -2239658.1614 | -1344830.5541 | -1344830.5541 | -1344830.5541 | -1344830.5541 | -1344830.5541 | -1344830.5541 | -1344830.5541 | -1344830.5541 | -1344830.5541 | -1344830.5541 | -1344830.5541 | -1344830.5541 | -1344830.5541 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | -25491544.6383 |  | 0 | 0 | 0 | -333049.9805 | -1601050.7782 | -2689756.4014 | -3425447.0166 | -3111582.6382 | -2515595.2319 | -1783463.5532 | -1783463.5532 | -1783463.5532 | -1783463.5532 | -1783463.5532 | -1783463.5532 | -1783463.5532 | -1783463.5532 | -1783463.5532 | -1783463.5532 | -1783463.5532 | -1783463.5532 | -1783463.5532 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | -29815237.3225 |  | 0 | 0 | 0 | -370623.101 | -1770859.4228 | -2977235.0805 | -3801178.2215 | -3487313.8431 | -2891326.4369 | -2159194.7582 | -2159194.7582 | -2159194.7582 | -2159194.7582 | -2159194.7582 | -2159194.7582 | -2159194.7582 | -2159194.7582 | -2159194.7582 | -2159194.7582 | -2159194.7582 | -2159194.7582 | -2159194.7582 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -23519835.5045 |  | 0 | 0 | 0 | -328307.6223 | -1590269.0373 | -2669197.4693 | -3388573.1241 | -3039834.9259 | -2377626.6967 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -23519835.5045 |  | 0 | 0 | 0 | -328307.6223 | -1590269.0373 | -2669197.4693 | -3388573.1241 | -3039834.9259 | -2377626.6967 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -23519835.5045 |  | 0 | 0 | 0 | -328307.6223 | -1590269.0373 | -2669197.4693 | -3388573.1241 | -3039834.9259 | -2377626.6967 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | -1564147.0537 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | -13619754.9925 |  | 0 | 0 | 0 | 0 | -882525.2584 | -2059225.603 | -2573011.9365 | -2224273.7382 | -1562065.509 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | -16921919.0159 |  | 0 | 0 | 0 | 0 | -970777.7843 | -2265148.1634 | -2867187.0226 | -2518448.8244 | -1856240.5952 | -1042760.9522 | -1042760.9522 | -1042760.9522 | -1042760.9522 | -1042760.9522 | -1042760.9522 | -1042760.9522 | -1042760.9522 | -1042760.9522 | -1042760.9522 | -1042760.9522 | -1042760.9522 | -1042760.9522 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | -10317590.9691 |  | 0 | 0 | 0 | 0 | -794272.7326 | -1853303.0427 | -2278836.8503 | -1930098.6521 | -1267890.4229 | -454410.7799 | -454410.7799 | -454410.7799 | -454410.7799 | -454410.7799 | -454410.7799 | -454410.7799 | -454410.7799 | -454410.7799 | -454410.7799 | -454410.7799 | -454410.7799 | -454410.7799 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | -11679566.4684 |  | 0 | 0 | 0 | 0 | -882525.2584 | -2059225.603 | -2536138.0439 | -2152526.0259 | -1424096.9738 | -529269.3665 | -529269.3665 | -529269.3665 | -529269.3665 | -529269.3665 | -529269.3665 | -529269.3665 | -529269.3665 | -529269.3665 | -529269.3665 | -529269.3665 | -529269.3665 | -529269.3665 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | -15559943.5166 |  | 0 | 0 | 0 | 0 | -882525.2584 | -2059225.603 | -2609885.829 | -2296021.4505 | -1700034.0443 | -967902.3656 | -967902.3656 | -967902.3656 | -967902.3656 | -967902.3656 | -967902.3656 | -967902.3656 | -967902.3656 | -967902.3656 | -967902.3656 | -967902.3656 | -967902.3656 | -967902.3656 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | -18862107.54 |  | 0 | 0 | 0 | 0 | -970777.7843 | -2265148.1634 | -2904060.9151 | -2590196.5367 | -1994209.1304 | -1262077.4517 | -1262077.4517 | -1262077.4517 | -1262077.4517 | -1262077.4517 | -1262077.4517 | -1262077.4517 | -1262077.4517 | -1262077.4517 | -1262077.4517 | -1262077.4517 | -1262077.4517 | -1262077.4517 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | -13619754.9925 |  | 0 | 0 | 0 | 0 | -882525.2584 | -2059225.603 | -2573011.9365 | -2224273.7382 | -1562065.509 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | -13619754.9925 |  | 0 | 0 | 0 | 0 | -882525.2584 | -2059225.603 | -2573011.9365 | -2224273.7382 | -1562065.509 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | -13619754.9925 |  | 0 | 0 | 0 | 0 | -882525.2584 | -2059225.603 | -2573011.9365 | -2224273.7382 | -1562065.509 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | -748585.866 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 0 | 1 |  | 2027-28: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2025-26: Max; 2027-28: Preferred
NPV | None | 0 | 6.1227 | -23.5198 | -13.6198 |  |  | 2025-26: #NAME?; 2027-28: Option 2
sens1 | Capex 10% higher | 0 | 5.1012 | -27.8435 | -16.9219 |  |  | 2025-26: #NAME?; 2027-28: Option 2
sens2 | Capex 10% lower | 0 | 7.1443 | -19.1961 | -10.3176 |  |  | 2025-26: #NAME?; 2027-28: Option 2
sens3 | Total benefits 10% higher | 0 | 7.7565 | -21.5481 | -11.6796 |  |  | 2025-26: #NAME?; 2027-28: Option 2
sens4 | Total benefits 10% lower | 0 | 4.4889 | -25.4915 | -15.5599 |  |  | 2025-26: #NAME?; 2027-28: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 3.4674 | -29.8152 | -18.8621 |  |  | 2025-26: #NAME?; 2027-28: Option 2
sens | 0 | [6 empty] | 2025-26: #NAME?; 2027-28: #NAME?
sens | 0 | [6 empty] | 2025-26: #NAME?; 2027-28: #NAME?
sens | 0 | [6 empty] | 2025-26: #NAME?; 2027-28: #NAME?

## Misc_calcs
CitiPower
CBD security of supply
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2025-26
FIRST YEAR
| Option | First year | Option included
| Option 2 | 2 | TRUE
| Option 3 | 2 | TRUE
| Option 4 | 3 | TRUE
| Option 5 | Not used | FALSE
| First year | 2
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
CitiPower
CBD security of supply
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | FALSE |  |  | FALSE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
CitiPower
| Reliability in worst-served areas | per MWh | 0
| Network resilience | per MWh | 0
| Enabling solar exports | per MWh | 4220.9954
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.54769
| Customer value of time - business | per minute customer time | 0.54769
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020