## Cover
#NAME?
Regulatory proposal 2026-31
#NAME?
| Model number: | #NAME?
2025-01-31
12

## Summary
CitiPower
Collingwood supply area
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Install a third transformer and associated equipment at B |  | -4.5382 | 14.8201 | 10.2818
| Option 3 | Offload feeders at B to CW |  | -5.7482 | 14.154 | 8.4058
| Option 4 | Offload feeders at B via existing network to NR |  | -7.8199 | 14.154 | 6.334
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | Install a third transformer and associated equipment at B |  | 10.2818
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 4.0938 | 4.0938 | 0 | 0 | 0 |  | 8.1875
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
| Capex and risk ($M, 2026) |  | Value of expected unserved energy ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 10.2818 | 8.4058 | 6.334 |  |  | Option 2
| Capex 10% higher |  | 0 | 9.828 | 7.831 | 5.552 |  |  | Option 2
| Capex 10% lower |  | 0 | 10.7356 | 8.9806 | 7.116 |  |  | Option 2
| Total benefits 10% higher |  | 0 | 11.7638 | 9.8212 | 7.7494 |  |  | Option 2
| Total benefits 10% lower |  | 0 | 8.7998 | 6.9904 | 4.9186 |  |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  | 0 | 8.346 | 6.4156 | 4.1367 |  |  | Option 2
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
CitiPower
Collingwood supply area
Project
|  | Business: | CitiPower
|  | Descripton: | Collingwood supply area
|  | Date of cost inputs: | December |  | 2023
|  | Option | Description
|  | Option 1 (base case) | No change to existing practices
|  | Option 2 | Install a third transformer and associated equipment at B
|  | Option 3 | Offload feeders at B to CW
|  | Option 4 | Offload feeders at B via existing network to NR
Option 5
|  | Compliance project | No
|  | Expenditure starts | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  | 3.5% | [real_disc]
|  | VCR date |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  | 20 | [years]\
|  | Output dollars |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | Network average |  | Network average | 43815.4862 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  | 1
|  | Harm to property from bushfire |  |  | 1
|  | Harm to environment |  |  | 1
|  | Safety - Public trespass |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  | 3
|  | Safety from bushfire in HBRA |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  | 10
^ Public or employee
|  | Incident type |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  | 20%
Other benefits
| ENVIRONMENTAL | [7 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  | Value
|  | Reliability in worst-served areas |  |  | 0 | 2023-12-31 | per MWh
|  | Network resilience |  |  | 0 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  | 4220.9954 | 2023-12-31 | per MWh
|  | Aesthetics |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Communication |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[5 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  | 10% | -10%

## Option1 (base case)
CitiPower
Collingwood supply area
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 6.8 | 8.1 | 10.7 | 13.3 | 15.6 | 18.2 | 22.5 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 |  | 297945.3063 | 354905.4384 | 468825.7026 | 582745.9668 | 683521.5851 | 797441.8493 | 985848.4401 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684
| Safety consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 297945.3063 | 354905.4384 | 468825.7026 | 582745.9668 | 683521.5851 | 797441.8493 | 985848.4401 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
CitiPower
Collingwood supply area
OPTION 2 | Install a third transformer and associated equipment at B
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Install 3rd Tx at B |  | 50 | 2023-12-31 | 3678417.8 | 3678417.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 3678417.8 | 3678417.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 297945.3063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 297945.3063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 354905.4384 | 468825.7026 | 582745.9668 | 683521.5851 | 797441.8493 | 985848.4401 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684
Capital expenditure
| Install 3rd Tx at B |  |  | 2023-12-31 | -3678417.8 | -3678417.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Install 3rd Tx at B |  |  | 2023-12-31 | -3678417.8 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6 | -7356835.6
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Install 3rd Tx at B |  |  | 2023-12-31 | 0 | -156824.5961 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -156824.5961 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923
| Annualised capex |  |  | 2023-12-31 | 0 | -156824.5961 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 354905.4384 | 468825.7026 | 582745.9668 | 683521.5851 | 797441.8493 | 985848.4401 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 198080.8423 | 155176.5103 | 269096.7745 | 369872.3928 | 483792.657 | 672199.2478 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | 198080.8423 | 155176.5103 | 269096.7745 | 369872.3928 | 483792.657 | 672199.2478 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761
| Total annualised capex |  |  |  | 0 | -156824.5961 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923 | -313649.1923
| Total benefits |  |  |  | 0 | 354905.4384 | 468825.7026 | 582745.9668 | 683521.5851 | 797441.8493 | 985848.4401 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684 | 1213688.9684
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | 182398.3827 | 123811.5911 | 237731.8553 | 338507.4736 | 452427.7378 | 640834.3285 | 868674.8569 | 868674.8569 | 868674.8569 | 868674.8569 | 868674.8569 | 868674.8569 | 868674.8569 | 868674.8569 | 868674.8569 | 868674.8569 | 868674.8569 | 868674.8569 | 868674.8569 | 868674.8569 | 868674.8569 | 868674.8569 | 868674.8569 | 868674.8569
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | 213763.3019 | 186541.4295 | 300461.6937 | 401237.312 | 515157.5762 | 703564.167 | 931404.6954 | 931404.6954 | 931404.6954 | 931404.6954 | 931404.6954 | 931404.6954 | 931404.6954 | 931404.6954 | 931404.6954 | 931404.6954 | 931404.6954 | 931404.6954 | 931404.6954 | 931404.6954 | 931404.6954 | 931404.6954 | 931404.6954 | 931404.6954
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | 233571.3861 | 202059.0806 | 327371.3712 | 438224.5513 | 563536.8419 | 770784.0918 | 1021408.673 | 1021408.673 | 1021408.673 | 1021408.673 | 1021408.673 | 1021408.673 | 1021408.673 | 1021408.673 | 1021408.673 | 1021408.673 | 1021408.673 | 1021408.673 | 1021408.673 | 1021408.673 | 1021408.673 | 1021408.673 | 1021408.673 | 1021408.673
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | 162590.2984 | 108293.94 | 210822.1778 | 301520.2343 | 404048.4721 | 573614.4038 | 778670.8793 | 778670.8793 | 778670.8793 | 778670.8793 | 778670.8793 | 778670.8793 | 778670.8793 | 778670.8793 | 778670.8793 | 778670.8793 | 778670.8793 | 778670.8793 | 778670.8793 | 778670.8793 | 778670.8793 | 778670.8793 | 778670.8793 | 778670.8793
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | 146907.8388 | 76929.0208 | 179457.2586 | 270155.3151 | 372683.5528 | 542249.4845 | 747305.9601 | 747305.9601 | 747305.9601 | 747305.9601 | 747305.9601 | 747305.9601 | 747305.9601 | 747305.9601 | 747305.9601 | 747305.9601 | 747305.9601 | 747305.9601 | 747305.9601 | 747305.9601 | 747305.9601 | 747305.9601 | 747305.9601 | 747305.9601
sens | 0 | 0% | 0% | Option 2sens | 0 | 198080.8423 | 155176.5103 | 269096.7745 | 369872.3928 | 483792.657 | 672199.2478 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761
sens | 0 | 0% | 0% | Option 2sens | 0 | 198080.8423 | 155176.5103 | 269096.7745 | 369872.3928 | 483792.657 | 672199.2478 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761
sens | 0 | 0% | 0% | Option 2sens | 0 | 198080.8423 | 155176.5103 | 269096.7745 | 369872.3928 | 483792.657 | 672199.2478 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761 | 900039.7761

## Option3
CitiPower
Collingwood supply area
OPTION 3 | Offload feeders at B to CW
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Permanent transfers to CW |  | 50 | 2023-12-31 | 8989836.3415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 8989836.3415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 6.8 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 297945.3063 | 13144.6459 | 13144.6459 | 13144.6459 | 13144.6459 | 43815.4862 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 297945.3063 | 13144.6459 | 13144.6459 | 13144.6459 | 13144.6459 | 43815.4862 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 341760.7926 | 455681.0567 | 569601.3209 | 670376.9392 | 753626.3631 | 928888.308 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363
Capital expenditure
| Permanent transfers to CW |  |  | 2023-12-31 | -8989836.3415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Permanent transfers to CW |  |  | 2023-12-31 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415 | -8989836.3415
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Permanent transfers to CW |  |  | 2023-12-31 | 0 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716
| Annualised capex |  |  | 2023-12-31 | 0 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 341760.7926 | 455681.0567 | 569601.3209 | 670376.9392 | 753626.3631 | 928888.308 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | -41509.2791 | 72410.9851 | 186331.2493 | 287106.8676 | 370356.2914 | 545618.2363 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | -41509.2791 | 72410.9851 | 186331.2493 | 287106.8676 | 370356.2914 | 545618.2363 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647
| Total annualised capex |  |  |  | 0 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716 | -383270.0716
| Total benefits |  |  |  | 0 | 341760.7926 | 455681.0567 | 569601.3209 | 670376.9392 | 753626.3631 | 928888.308 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | -79836.2862 | 34083.9779 | 148004.2421 | 248779.8604 | 332029.2843 | 507291.2292 | 735131.7575 | 735131.7575 | 735131.7575 | 735131.7575 | 735131.7575 | 735131.7575 | 735131.7575 | 735131.7575 | 735131.7575 | 735131.7575 | 735131.7575 | 735131.7575 | 735131.7575 | 735131.7575 | 735131.7575 | 735131.7575 | 735131.7575 | 735131.7575
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | -3182.2719 | 110737.9923 | 224658.2565 | 325433.8748 | 408683.2986 | 583945.2435 | 811785.7719 | 811785.7719 | 811785.7719 | 811785.7719 | 811785.7719 | 811785.7719 | 811785.7719 | 811785.7719 | 811785.7719 | 811785.7719 | 811785.7719 | 811785.7719 | 811785.7719 | 811785.7719 | 811785.7719 | 811785.7719 | 811785.7719 | 811785.7719
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | -7333.1998 | 117979.0908 | 243291.3814 | 354144.5615 | 445718.9277 | 638507.0671 | 889131.6483 | 889131.6483 | 889131.6483 | 889131.6483 | 889131.6483 | 889131.6483 | 889131.6483 | 889131.6483 | 889131.6483 | 889131.6483 | 889131.6483 | 889131.6483 | 889131.6483 | 889131.6483 | 889131.6483 | 889131.6483 | 889131.6483 | 889131.6483
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | -75685.3583 | 26842.8794 | 129371.1172 | 220069.1737 | 294993.6551 | 452729.4055 | 657785.8811 | 657785.8811 | 657785.8811 | 657785.8811 | 657785.8811 | 657785.8811 | 657785.8811 | 657785.8811 | 657785.8811 | 657785.8811 | 657785.8811 | 657785.8811 | 657785.8811 | 657785.8811 | 657785.8811 | 657785.8811 | 657785.8811 | 657785.8811
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | -114012.3655 | -11484.1277 | 91044.11 | 181742.1665 | 256666.648 | 414402.3984 | 619458.8739 | 619458.8739 | 619458.8739 | 619458.8739 | 619458.8739 | 619458.8739 | 619458.8739 | 619458.8739 | 619458.8739 | 619458.8739 | 619458.8739 | 619458.8739 | 619458.8739 | 619458.8739 | 619458.8739 | 619458.8739 | 619458.8739 | 619458.8739
sens | 0 | 0% | 0% | Option 3sens | 0 | -41509.2791 | 72410.9851 | 186331.2493 | 287106.8676 | 370356.2914 | 545618.2363 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647
sens | 0 | 0% | 0% | Option 3sens | 0 | -41509.2791 | 72410.9851 | 186331.2493 | 287106.8676 | 370356.2914 | 545618.2363 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647
sens | 0 | 0% | 0% | Option 3sens | 0 | -41509.2791 | 72410.9851 | 186331.2493 | 287106.8676 | 370356.2914 | 545618.2363 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647 | 773458.7647

## Option4
CitiPower
Collingwood supply area
OPTION 4 | Offload feeders at B via existing network to NR
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Permanent transfers to NR |  | 50 | 2023-12-31 | 12229979.8415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 12229979.8415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 6.8 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 297945.3063 | 13144.6459 | 13144.6459 | 13144.6459 | 13144.6459 | 43815.4862 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 297945.3063 | 13144.6459 | 13144.6459 | 13144.6459 | 13144.6459 | 43815.4862 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321 | 56960.1321
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 341760.7926 | 455681.0567 | 569601.3209 | 670376.9392 | 753626.3631 | 928888.308 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363
Capital expenditure
| Permanent transfers to NR |  |  | 2023-12-31 | -12229979.8415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Permanent transfers to NR |  |  | 2023-12-31 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415 | -12229979.8415
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Permanent transfers to NR |  |  | 2023-12-31 | 0 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086
| Annualised capex |  |  | 2023-12-31 | 0 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 341760.7926 | 455681.0567 | 569601.3209 | 670376.9392 | 753626.3631 | 928888.308 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | -179648.616 | -65728.3518 | 48191.9124 | 148967.5307 | 232216.9545 | 407478.8994 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | -179648.616 | -65728.3518 | 48191.9124 | 148967.5307 | 232216.9545 | 407478.8994 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278
| Total annualised capex |  |  |  | 0 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086 | -521409.4086
| Total benefits |  |  |  | 0 | 341760.7926 | 455681.0567 | 569601.3209 | 670376.9392 | 753626.3631 | 928888.308 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363 | 1156728.8363
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | -231789.5569 | -117869.2927 | -3949.0285 | 96826.5898 | 180076.0136 | 355337.9585 | 583178.4869 | 583178.4869 | 583178.4869 | 583178.4869 | 583178.4869 | 583178.4869 | 583178.4869 | 583178.4869 | 583178.4869 | 583178.4869 | 583178.4869 | 583178.4869 | 583178.4869 | 583178.4869 | 583178.4869 | 583178.4869 | 583178.4869 | 583178.4869
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | -127507.6752 | -13587.411 | 100332.8532 | 201108.4715 | 284357.8954 | 459619.8403 | 687460.3686 | 687460.3686 | 687460.3686 | 687460.3686 | 687460.3686 | 687460.3686 | 687460.3686 | 687460.3686 | 687460.3686 | 687460.3686 | 687460.3686 | 687460.3686 | 687460.3686 | 687460.3686 | 687460.3686 | 687460.3686 | 687460.3686 | 687460.3686
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | -145472.5368 | -20160.2462 | 105152.0445 | 216005.2246 | 307579.5908 | 500367.7302 | 750992.3114 | 750992.3114 | 750992.3114 | 750992.3114 | 750992.3114 | 750992.3114 | 750992.3114 | 750992.3114 | 750992.3114 | 750992.3114 | 750992.3114 | 750992.3114 | 750992.3114 | 750992.3114 | 750992.3114 | 750992.3114 | 750992.3114 | 750992.3114
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | -213824.6953 | -111296.4575 | -8768.2197 | 81929.8368 | 156854.3182 | 314590.0686 | 519646.5441 | 519646.5441 | 519646.5441 | 519646.5441 | 519646.5441 | 519646.5441 | 519646.5441 | 519646.5441 | 519646.5441 | 519646.5441 | 519646.5441 | 519646.5441 | 519646.5441 | 519646.5441 | 519646.5441 | 519646.5441 | 519646.5441 | 519646.5441
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | -265965.6361 | -163437.3984 | -60909.1606 | 29788.8959 | 104713.3773 | 262449.1278 | 467505.6033 | 467505.6033 | 467505.6033 | 467505.6033 | 467505.6033 | 467505.6033 | 467505.6033 | 467505.6033 | 467505.6033 | 467505.6033 | 467505.6033 | 467505.6033 | 467505.6033 | 467505.6033 | 467505.6033 | 467505.6033 | 467505.6033 | 467505.6033
sens | 0 | 0% | 0% | Option 4sens | 0 | -179648.616 | -65728.3518 | 48191.9124 | 148967.5307 | 232216.9545 | 407478.8994 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278
sens | 0 | 0% | 0% | Option 4sens | 0 | -179648.616 | -65728.3518 | 48191.9124 | 148967.5307 | 232216.9545 | 407478.8994 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278
sens | 0 | 0% | 0% | Option 4sens | 0 | -179648.616 | -65728.3518 | 48191.9124 | 148967.5307 | 232216.9545 | 407478.8994 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278 | 635319.4278

## Option5
CitiPower
Collingwood supply area
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
CitiPower
Collingwood supply area
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 18264123.1426 | 2026-06-30 |  | 331587.0994 | 394978.7507 | 521762.0534 | 648545.3561 | 760699.8162 | 887483.1189 | 1097163.1964 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 15145991.4486 | 2026-06-30 |  | 331587.0994 | 394978.7507 | 521762.0534 | 648545.3561 | 760699.8162 | 887483.1189 | 1097163.1964 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 325932.3371 | 2026-06-30 |  | 331587.0994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Capital expenditure | Option 2Capital expenditure | -7911813.1444 | 2026-06-30 |  | -4093757.6884 | -4093757.6884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 325932.3371 | 2026-06-30 |  | 331587.0994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -4538246.4602 | 2026-06-30 |  | 0 | -174532.0763 | -349064.1526 | -349064.1526 | -349064.1526 | -349064.1526 | -349064.1526 | -349064.1526 | -349064.1526 | -349064.1526 | -349064.1526 | -349064.1526 | -349064.1526 | -349064.1526 | -349064.1526 | -349064.1526 | -349064.1526 | -349064.1526 | -349064.1526 | -349064.1526 | 0 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 14820059.1115 | 2026-06-30 |  | 0 | 394978.7507 | 521762.0534 | 648545.3561 | 760699.8162 | 887483.1189 | 1097163.1964 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 1350729.8018 | 0 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | 220446.6744 | 172697.9008 | 299481.2034 | 411635.6635 | 538418.9662 | 748099.0438 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 10281812.6513 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -4538246.4602 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 14820059.1115 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 1138376.5271 | 2026-06-30 |  | 331587.0994 | 14628.8426 | 14628.8426 | 14628.8426 | 14628.8426 | 48762.8087 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513
Option 3 | Capital expenditure | Option 3Capital expenditure | -9834282.691 | 2026-06-30 |  | -10004902.5537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 992038.2166 | 2026-06-30 |  | 331587.0994 | 14628.8426 | 14628.8426 | 14628.8426 | 14628.8426 | 48762.8087 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -5748150.2963 | 2026-06-30 |  | 0 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | -426546.1097 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 14153953.232 | 2026-06-30 |  | 0 | 380349.9081 | 507133.2108 | 633916.5135 | 746070.9736 | 838720.3101 | 1033771.5451 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 0 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | -46196.2016 | 80587.1011 | 207370.4038 | 319524.8638 | 412174.2004 | 607225.4353 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | 8405802.9357 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -5748150.2963 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 14153953.232 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 1138376.5271 | 2026-06-30 |  | 331587.0994 | 14628.8426 | 14628.8426 | 14628.8426 | 14628.8426 | 48762.8087 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513
Option 4 | Capital expenditure | Option 4Capital expenditure | -13378784.051 | 2026-06-30 |  | -13610899.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 992038.2166 | 2026-06-30 |  | 331587.0994 | 14628.8426 | 14628.8426 | 14628.8426 | 14628.8426 | 48762.8087 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 63391.6513 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | -7819915.6891 | 2026-06-30 |  | 0 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | -580283.1248 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 14153953.232 | 2026-06-30 |  | 0 | 380349.9081 | 507133.2108 | 633916.5135 | 746070.9736 | 838720.3101 | 1033771.5451 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 1287338.1504 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | -199933.2167 | -73149.914 | 53633.3887 | 165787.8488 | 258437.1854 | 453488.4203 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 6334037.5429 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | -7819915.6891 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 14153953.232 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0.34906 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 0.33159 | 0.39498 | 0.52176 | 0.64855 | 0.7607 | 0.88748 | 1.0972 | 1.3507 | 1.3507 | 1.3507 | 1.3507 | 1.3507 | 1.3507 | 1.3507 | 1.3507 | 1.3507 | 1.3507 | 1.3507 | 1.3507 | 1.3507 | 1.3507 | 1.3507 | 1.3507 | 1.3507 | 1.3507
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 27.7 |  |  | Energy at risk energy at risk (weighted) | 6.8 | 8.1 | 10.7 | 13.3 | 15.6 | 18.2 | 22.5 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7
Option 1 (base case) | Energy at risk value | 1.2137 |  |  | Option 1 (base case) risk cost | 0.29795 | 0.35491 | 0.46883 | 0.58275 | 0.68352 | 0.79744 | 0.98585 | 1.2137 | 1.2137 | 1.2137 | 1.2137 | 1.2137 | 1.2137 | 1.2137 | 1.2137 | 1.2137 | 1.2137 | 1.2137 | 1.2137 | 1.2137 | 1.2137 | 1.2137 | 1.2137 | 1.2137 | 1.2137

## Sensitivity_calcs
CitiPower
Collingwood supply area
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
[7 empty] | 46203 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 1001665.6491 | 1001665.6491 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 10281812.6513 |  | 0 | 0 | 220446.6744 | 172697.9008 | 299481.2034 | 411635.6635 | 538418.9662 | 748099.0438 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 0 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 9827988.0053 |  | 0 | 0 | 202993.4667 | 137791.4855 | 264574.7882 | 376729.2483 | 503512.551 | 713192.6285 | 966759.2339 | 966759.2339 | 966759.2339 | 966759.2339 | 966759.2339 | 966759.2339 | 966759.2339 | 966759.2339 | 966759.2339 | 966759.2339 | 966759.2339 | 966759.2339 | 966759.2339 | 0 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 10735637.2973 |  | 0 | 0 | 237899.882 | 207604.316 | 334387.6187 | 446542.0788 | 573325.3815 | 783005.459 | 1036572.0644 | 1036572.0644 | 1036572.0644 | 1036572.0644 | 1036572.0644 | 1036572.0644 | 1036572.0644 | 1036572.0644 | 1036572.0644 | 1036572.0644 | 1036572.0644 | 1036572.0644 | 1036572.0644 | 0 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 11763818.5624 |  | 0 | 0 | 259944.5495 | 224874.1061 | 364335.7391 | 487705.6451 | 627167.2781 | 857815.3634 | 1136738.6293 | 1136738.6293 | 1136738.6293 | 1136738.6293 | 1136738.6293 | 1136738.6293 | 1136738.6293 | 1136738.6293 | 1136738.6293 | 1136738.6293 | 1136738.6293 | 1136738.6293 | 1136738.6293 | 0 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 8799806.7401 |  | 0 | 0 | 180948.7993 | 120521.6954 | 234626.6678 | 335565.6819 | 449670.6543 | 638382.7241 | 866592.669 | 866592.669 | 866592.669 | 866592.669 | 866592.669 | 866592.669 | 866592.669 | 866592.669 | 866592.669 | 866592.669 | 866592.669 | 866592.669 | 866592.669 | 0 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 8345982.0941 |  | 0 | 0 | 163495.5917 | 85615.2801 | 199720.2526 | 300659.2666 | 414764.2391 | 603476.3088 | 831686.2537 | 831686.2537 | 831686.2537 | 831686.2537 | 831686.2537 | 831686.2537 | 831686.2537 | 831686.2537 | 831686.2537 | 831686.2537 | 831686.2537 | 831686.2537 | 831686.2537 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 10281812.6513 |  | 0 | 0 | 220446.6744 | 172697.9008 | 299481.2034 | 411635.6635 | 538418.9662 | 748099.0438 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 10281812.6513 |  | 0 | 0 | 220446.6744 | 172697.9008 | 299481.2034 | 411635.6635 | 538418.9662 | 748099.0438 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 10281812.6513 |  | 0 | 0 | 220446.6744 | 172697.9008 | 299481.2034 | 411635.6635 | 538418.9662 | 748099.0438 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 1001665.6491 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | -46196.2016 | 80587.1011 | 207370.4038 | 319524.8638 | 412174.2004 | 607225.4353 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 8405802.9357 |  | 0 | 0 | -46196.2016 | 80587.1011 | 207370.4038 | 319524.8638 | 412174.2004 | 607225.4353 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 0 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 7830987.9061 |  | 0 | 0 | -88850.8126 | 37932.4901 | 164715.7928 | 276870.2529 | 369519.5895 | 564570.8244 | 818137.4298 | 818137.4298 | 818137.4298 | 818137.4298 | 818137.4298 | 818137.4298 | 818137.4298 | 818137.4298 | 818137.4298 | 818137.4298 | 818137.4298 | 818137.4298 | 818137.4298 | 0 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 8980617.9653 |  | 0 | 0 | -3541.5907 | 123241.712 | 250025.0147 | 362179.4748 | 454828.8114 | 649880.0463 | 903446.6517 | 903446.6517 | 903446.6517 | 903446.6517 | 903446.6517 | 903446.6517 | 903446.6517 | 903446.6517 | 903446.6517 | 903446.6517 | 903446.6517 | 903446.6517 | 903446.6517 | 0 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 9821198.2589 |  | 0 | 0 | -8161.2108 | 131300.4221 | 270762.0551 | 394131.9612 | 496046.2314 | 710602.5898 | 989525.8558 | 989525.8558 | 989525.8558 | 989525.8558 | 989525.8558 | 989525.8558 | 989525.8558 | 989525.8558 | 989525.8558 | 989525.8558 | 989525.8558 | 989525.8558 | 989525.8558 | 0 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | 6990407.6125 |  | 0 | 0 | -84231.1924 | 29873.78 | 143978.7524 | 244917.7665 | 328302.1694 | 503848.2808 | 732058.2257 | 732058.2257 | 732058.2257 | 732058.2257 | 732058.2257 | 732058.2257 | 732058.2257 | 732058.2257 | 732058.2257 | 732058.2257 | 732058.2257 | 732058.2257 | 732058.2257 | 0 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | 6415592.5829 |  | 0 | 0 | -126885.8034 | -12780.831 | 101324.1414 | 202263.1555 | 285647.5584 | 461193.6699 | 689403.6147 | 689403.6147 | 689403.6147 | 689403.6147 | 689403.6147 | 689403.6147 | 689403.6147 | 689403.6147 | 689403.6147 | 689403.6147 | 689403.6147 | 689403.6147 | 689403.6147 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 8405802.9357 |  | 0 | 0 | -46196.2016 | 80587.1011 | 207370.4038 | 319524.8638 | 412174.2004 | 607225.4353 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 8405802.9357 |  | 0 | 0 | -46196.2016 | 80587.1011 | 207370.4038 | 319524.8638 | 412174.2004 | 607225.4353 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 8405802.9357 |  | 0 | 0 | -46196.2016 | 80587.1011 | 207370.4038 | 319524.8638 | 412174.2004 | 607225.4353 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 860792.0407 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 6334037.5429 |  | 0 | 0 | -199933.2167 | -73149.914 | 53633.3887 | 165787.8488 | 258437.1854 | 453488.4203 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 5552045.974 |  | 0 | 0 | -257961.5291 | -131178.2265 | -4394.9238 | 107759.5363 | 200408.8729 | 395460.1078 | 649026.7132 | 649026.7132 | 649026.7132 | 649026.7132 | 649026.7132 | 649026.7132 | 649026.7132 | 649026.7132 | 649026.7132 | 649026.7132 | 649026.7132 | 649026.7132 | 649026.7132 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 7116029.1118 |  | 0 | 0 | -141904.9042 | -15121.6015 | 111661.7012 | 223816.1613 | 316465.4979 | 511516.7328 | 765083.3382 | 765083.3382 | 765083.3382 | 765083.3382 | 765083.3382 | 765083.3382 | 765083.3382 | 765083.3382 | 765083.3382 | 765083.3382 | 765083.3382 | 765083.3382 | 765083.3382 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 7749432.8661 |  | 0 | 0 | -161898.2259 | -22436.5929 | 117025.0401 | 240394.9462 | 342309.2164 | 556865.5748 | 835788.8407 | 835788.8407 | 835788.8407 | 835788.8407 | 835788.8407 | 835788.8407 | 835788.8407 | 835788.8407 | 835788.8407 | 835788.8407 | 835788.8407 | 835788.8407 | 835788.8407 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 4918642.2197 |  | 0 | 0 | -237968.2075 | -123863.2351 | -9758.2626 | 91180.7514 | 174565.1544 | 350111.2658 | 578321.2106 | 578321.2106 | 578321.2106 | 578321.2106 | 578321.2106 | 578321.2106 | 578321.2106 | 578321.2106 | 578321.2106 | 578321.2106 | 578321.2106 | 578321.2106 | 578321.2106 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 4136650.6508 |  | 0 | 0 | -295996.52 | -181891.5475 | -67786.5751 | 33152.439 | 116536.8419 | 292082.9533 | 520292.8982 | 520292.8982 | 520292.8982 | 520292.8982 | 520292.8982 | 520292.8982 | 520292.8982 | 520292.8982 | 520292.8982 | 520292.8982 | 520292.8982 | 520292.8982 | 520292.8982 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 6334037.5429 |  | 0 | 0 | -199933.2167 | -73149.914 | 53633.3887 | 165787.8488 | 258437.1854 | 453488.4203 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 6334037.5429 |  | 0 | 0 | -199933.2167 | -73149.914 | 53633.3887 | 165787.8488 | 258437.1854 | 453488.4203 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 6334037.5429 |  | 0 | 0 | -199933.2167 | -73149.914 | 53633.3887 | 165787.8488 | 258437.1854 | 453488.4203 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 707055.0257 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 0 | 1 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 10.2818 | 8.4058 | 6.334 |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens1 | Capex 10% higher | 0 | 9.828 | 7.831 | 5.552 |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens2 | Capex 10% lower | 0 | 10.7356 | 8.9806 | 7.116 |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens3 | Total benefits 10% higher | 0 | 11.7638 | 9.8212 | 7.7494 |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens4 | Total benefits 10% lower | 0 | 8.7998 | 6.9904 | 4.9186 |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 8.346 | 6.4156 | 4.1367 |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Misc_calcs
CitiPower
Collingwood supply area
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 1 | TRUE
| Option 3 | 1 | TRUE
| Option 4 | 1 | TRUE
| Option 5 | Not used | FALSE
| First year | 1
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
CitiPower
Collingwood supply area
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | FALSE |  |  | FALSE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
CitiPower
| Reliability in worst-served areas | per MWh | 0
| Network resilience | per MWh | 0
| Enabling solar exports | per MWh | 4220.9954
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.54769
| Customer value of time - business | per minute customer time | 0.54769
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020