## Cover
CitiPower
Regulatory proposal 2026-31
Brunswick modernisation
| Model number: | 3.05
2025-01-31
12

## Summary
CitiPower
Brunswick modernisation
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Rebuild the C zone substation with transfers from CW and WB |  | -52.2375 | 106.7568 | 54.5192
| Option 3 | New third transformer at CW |  | -36.1951 | 106.5474 | 70.3523
| Option 4 | 0
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 3 | New third transformer at CW |  | 70.3523
PREFERRED OPTION
Preferred Option
Option 3
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 26.8768 | 19.4749 | 0 | 6.0765 | 6.0765 |  | 58.5047
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
| Capex and risk ($M, 2026) |  | Value of expected unserved energy ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 54.5192 | 70.3523 |  |  |  | Option 3
| Capex 10% higher |  | 0 | 49.2955 | 66.7328 |  |  |  | Option 3
| Capex 10% lower |  | 0 | 59.743 | 73.9718 |  |  |  | Option 3
| Total benefits 10% higher |  | 0 | 65.1949 | 81.007 |  |  |  | Option 3
| Total benefits 10% lower |  | 0 | 43.8435 | 59.6975 |  |  |  | Option 3
| Capex 10% higher & Total benefits 10% lower |  | 0 | 38.6198 | 56.078 |  |  |  | Option 3
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
CitiPower
Brunswick modernisation
Project
|  | Business: | CitiPower
|  | Descripton: | Brunswick modernisation
|  | Date of cost inputs: | December |  | 2023
|  | Option | Description
|  | Option 1 (base case) | No change to existing practices
|  | Option 2 | Rebuild the C zone substation with transfers from CW and WB
|  | Option 3 | New third transformer at CW
Option 4
Option 5
|  | Compliance project | No
|  | Expenditure starts | 2024-25 | [start]
Timing & WACC
|  | Input dollars |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  | 3.5% | [real_disc]
|  | VCR date |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  | 20 | [years]\
|  | Output dollars |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | CW |  | Collingwood | 47477.1919 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  | 1
|  | Harm to property from bushfire |  |  | 1
|  | Harm to environment |  |  | 1
|  | Safety - Public trespass |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  | 3
|  | Safety from bushfire in HBRA |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  | 10
^ Public or employee
|  | Incident type |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  | 20%
Other benefits
| ENVIRONMENTAL | [7 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  | Value
|  | Reliability in worst-served areas |  |  | 0 | 2023-12-31 | per MWh
|  | Network resilience |  |  | 0 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  | 4220.9954 | 2023-12-31 | per MWh
|  | Aesthetics |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Communication |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[5 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  | 10% | -10%

## Option1 (base case)
CitiPower
Brunswick modernisation
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2024-06-30 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0.16659 | 0.61123 | 1.8959 | 4.9067 | 10.7413 | 20.4516 | 35.2301 | 63.1878 | 131.1682 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818
| Energy at risk value | $/MWh | 47477.1919 | 2023-12-31 |  | 7909.4069 | 29019.4019 | 90012.5682 | 232954.9579 | 509967.2237 | 970982.996 | 1672624.3084 | 2999976.9371 | 6227500.1637 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657
| Safety consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 7909.4069 | 29019.4019 | 90012.5682 | 232954.9579 | 509967.2237 | 970982.996 | 1672624.3084 | 2999976.9371 | 6227500.1637 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
CitiPower
Brunswick modernisation
OPTION 2 | Rebuild the C zone substation with transfers from CW and WB
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Rebuild C + transfers |  | 50 | 2023-12-31 | 0 | 0 | 0 | 0 | 9735575.1426 | 19471150.2851 | 19471150.2851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK offload to WB |  | 50 | 2023-12-31 | 1050000 | 6875000 | 7245000 | 17499000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F offload to CW |  | 50 | 2023-12-31 | 1050000 | 6875000 | 16905000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 2100000 | 13750000 | 24150000 | 17499000 | 9735575.1426 | 19471150.2851 | 19471150.2851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0.13854 | 0.31343 | 1.8649 | 2.6376 | 3.5077 | 4.4111 | 5.5882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 47477.1919 | 2023-12-31 | 6577.3493 | 14880.5965 | 88541.2589 | 125225.4318 | 166536.553 | 209426.3913 | 265310.2868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 6577.3493 | 14880.5965 | 88541.2589 | 125225.4318 | 166536.553 | 209426.3913 | 265310.2868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 1332.0577 | 14138.8054 | 1471.3093 | 107729.5261 | 343430.6707 | 761556.6047 | 1407314.0216 | 2999976.9371 | 6227500.1637 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657
Capital expenditure
| Rebuild C + transfers |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -9735575.1426 | -19471150.2851 | -19471150.2851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK offload to WB |  |  | 2023-12-31 | -1050000 | -6875000 | -7245000 | -17499000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F offload to CW |  |  | 2023-12-31 | -1050000 | -6875000 | -16905000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Rebuild C + transfers |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -9735575.1426 | -29206725.4277 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128 | -48677875.7128
| BK offload to WB |  |  | 2023-12-31 | -1050000 | -7925000 | -15170000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000
| F offload to CW |  |  | 2023-12-31 | -1050000 | -7925000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000
Annualised capex
| Annualised capex - Rebuild C + transfers |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | -415063.6831 | -1245191.0493 | -2075318.4155 | -2075318.4155 | -2075318.4155 | -2075318.4155 | -2075318.4155 | -2075318.4155 | -2075318.4155 | -2075318.4155 | -2075318.4155 | -2075318.4155 | -2075318.4155 | -2075318.4155 | -2075318.4155 | -2075318.4155 | -2075318.4155 | -2075318.4155 | -2075318.4155 | -2075318.4155
| Annualised capex - BK offload to WB |  |  | 2023-12-31 | 0 | -44765.395 | -337872.1483 | -646753.3741 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578
| Annualised capex - F offload to CW |  |  | 2023-12-31 | 0 | -44765.395 | -337872.1483 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085
| Total annualised capex |  |  | 2023-12-31 | 0 | -89530.7901 | -675744.2966 | -1705348.3827 | -2451395.6664 | -2866459.3495 | -3696586.7156 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818
| Annualised capex |  |  | 2023-12-31 | 0 | -89530.7901 | -675744.2966 | -1705348.3827 | -2451395.6664 | -2866459.3495 | -3696586.7156 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 1332.0577 | 14138.8054 | 1471.3093 | 107729.5261 | 343430.6707 | 761556.6047 | 1407314.0216 | 2999976.9371 | 6227500.1637 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 1332.0577 | -75391.9847 | -674272.9873 | -1597618.8566 | -2107964.9957 | -2104902.7448 | -2289272.6941 | -1526737.1447 | 1700786.0818 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 1332.0577 | -75391.9847 | -674272.9873 | -1597618.8566 | -2107964.9957 | -2104902.7448 | -2289272.6941 | -1526737.1447 | 1700786.0818 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839
| Total annualised capex |  |  |  | 0 | -89530.7901 | -675744.2966 | -1705348.3827 | -2451395.6664 | -2866459.3495 | -3696586.7156 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818 | -4526714.0818
| Total benefits |  |  |  | 1332.0577 | 14138.8054 | 1471.3093 | 107729.5261 | 343430.6707 | 761556.6047 | 1407314.0216 | 2999976.9371 | 6227500.1637 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657 | 12917681.3657
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 1332.0577 | -84345.0637 | -741847.417 | -1768153.6948 | -2353104.5623 | -2391548.6797 | -2658931.3656 | -1979408.5529 | 1248114.6736 | 7938295.8757 | 7938295.8757 | 7938295.8757 | 7938295.8757 | 7938295.8757 | 7938295.8757 | 7938295.8757 | 7938295.8757 | 7938295.8757 | 7938295.8757 | 7938295.8757 | 7938295.8757 | 7938295.8757 | 7938295.8757 | 7938295.8757 | 7938295.8757
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 1332.0577 | -66438.9057 | -606698.5577 | -1427084.0183 | -1862825.4291 | -1818256.8098 | -1919614.0225 | -1074065.7366 | 2153457.49 | 8843638.6921 | 8843638.6921 | 8843638.6921 | 8843638.6921 | 8843638.6921 | 8843638.6921 | 8843638.6921 | 8843638.6921 | 8843638.6921 | 8843638.6921 | 8843638.6921 | 8843638.6921 | 8843638.6921 | 8843638.6921 | 8843638.6921 | 8843638.6921
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 1465.2634 | -73978.1042 | -674125.8564 | -1586845.904 | -2073621.9286 | -2028747.0843 | -2148541.2919 | -1226739.451 | 2323536.0982 | 9682735.4205 | 9682735.4205 | 9682735.4205 | 9682735.4205 | 9682735.4205 | 9682735.4205 | 9682735.4205 | 9682735.4205 | 9682735.4205 | 9682735.4205 | 9682735.4205 | 9682735.4205 | 9682735.4205 | 9682735.4205 | 9682735.4205 | 9682735.4205
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 1198.8519 | -76805.8653 | -674420.1183 | -1608391.8092 | -2142308.0628 | -2181058.4052 | -2430004.0962 | -1826734.8384 | 1078036.0655 | 7099199.1473 | 7099199.1473 | 7099199.1473 | 7099199.1473 | 7099199.1473 | 7099199.1473 | 7099199.1473 | 7099199.1473 | 7099199.1473 | 7099199.1473 | 7099199.1473 | 7099199.1473 | 7099199.1473 | 7099199.1473 | 7099199.1473 | 7099199.1473
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 1198.8519 | -85758.9443 | -741994.5479 | -1778926.6474 | -2387447.6294 | -2467704.3402 | -2799662.7678 | -2279406.2466 | 625364.6573 | 6646527.7391 | 6646527.7391 | 6646527.7391 | 6646527.7391 | 6646527.7391 | 6646527.7391 | 6646527.7391 | 6646527.7391 | 6646527.7391 | 6646527.7391 | 6646527.7391 | 6646527.7391 | 6646527.7391 | 6646527.7391 | 6646527.7391 | 6646527.7391
sens | 0 | 0% | 0% | Option 2sens | 1332.0577 | -75391.9847 | -674272.9873 | -1597618.8566 | -2107964.9957 | -2104902.7448 | -2289272.6941 | -1526737.1447 | 1700786.0818 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839
sens | 0 | 0% | 0% | Option 2sens | 1332.0577 | -75391.9847 | -674272.9873 | -1597618.8566 | -2107964.9957 | -2104902.7448 | -2289272.6941 | -1526737.1447 | 1700786.0818 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839
sens | 0 | 0% | 0% | Option 2sens | 1332.0577 | -75391.9847 | -674272.9873 | -1597618.8566 | -2107964.9957 | -2104902.7448 | -2289272.6941 | -1526737.1447 | 1700786.0818 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839 | 8390967.2839

## Option3
CitiPower
Brunswick modernisation
OPTION 3 | New third transformer at CW
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| 3rd Tx at CW |  | 50 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 5460000 | 5460000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK offload to WB |  | 50 | 2023-12-31 | 1050000 | 6875000 | 7245000 | 17499000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F offload to CW |  | 50 | 2023-12-31 | 1050000 | 6875000 | 16905000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 2100000 | 13750000 | 24150000 | 17499000 | 0 | 5460000 | 5460000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0.13854 | 0.31343 | 2.2244 | 2.6376 | 3.5077 | 4.4111 | 5.5882 | 0.27653 | 0.38409 | 0.45969 | 0.46695 | 0.46695 | 0.46695 | 0.46695 | 0.46695 | 0.46695 | 0.46695 | 0.46695 | 0.46695 | 0.46695 | 0.46695 | 0.46695 | 0.46695 | 0.46695 | 0.46695
| Energy at risk value | $/MWh | 47477.1919 | 2023-12-31 | 6577.3493 | 14880.5965 | 105608.0527 | 125225.4318 | 166536.553 | 209426.3913 | 265310.2868 | 13128.6316 | 18235.3432 | 21824.8539 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 6577.3493 | 14880.5965 | 105608.0527 | 125225.4318 | 166536.553 | 209426.3913 | 265310.2868 | 13128.6316 | 18235.3432 | 21824.8539 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678 | 22169.2678
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 1332.0577 | 14138.8054 | -15595.4845 | 107729.5261 | 343430.6707 | 761556.6047 | 1407314.0216 | 2986848.3054 | 6209264.8204 | 12895856.5119 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979
Capital expenditure
| 3rd Tx at CW |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | -5460000 | -5460000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK offload to WB |  |  | 2023-12-31 | -1050000 | -6875000 | -7245000 | -17499000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F offload to CW |  |  | 2023-12-31 | -1050000 | -6875000 | -16905000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| 3rd Tx at CW |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | -5460000 | -10920000 | -10920000 | -10920000 | -10920000 | -10920000 | -10920000 | -10920000 | -10920000 | -10920000 | -10920000 | -10920000 | -10920000 | -10920000 | -10920000 | -10920000 | -10920000 | -10920000 | -10920000 | -10920000
| BK offload to WB |  |  | 2023-12-31 | -1050000 | -7925000 | -15170000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000 | -32669000
| F offload to CW |  |  | 2023-12-31 | -1050000 | -7925000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000 | -24830000
Annualised capex
| Annualised capex - 3rd Tx at CW |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | -232780.0542 | -465560.1085 | -465560.1085 | -465560.1085 | -465560.1085 | -465560.1085 | -465560.1085 | -465560.1085 | -465560.1085 | -465560.1085 | -465560.1085 | -465560.1085 | -465560.1085 | -465560.1085 | -465560.1085 | -465560.1085 | -465560.1085 | -465560.1085 | -465560.1085
| Annualised capex - BK offload to WB |  |  | 2023-12-31 | 0 | -44765.395 | -337872.1483 | -646753.3741 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578 | -1392800.6578
| Annualised capex - F offload to CW |  |  | 2023-12-31 | 0 | -44765.395 | -337872.1483 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085 | -1058595.0085
| Total annualised capex |  |  | 2023-12-31 | 0 | -89530.7901 | -675744.2966 | -1705348.3827 | -2451395.6664 | -2451395.6664 | -2684175.7206 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748
| Annualised capex |  |  | 2023-12-31 | 0 | -89530.7901 | -675744.2966 | -1705348.3827 | -2451395.6664 | -2451395.6664 | -2684175.7206 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 1332.0577 | 14138.8054 | -15595.4845 | 107729.5261 | 343430.6707 | 761556.6047 | 1407314.0216 | 2986848.3054 | 6209264.8204 | 12895856.5119 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 1332.0577 | -75391.9847 | -691339.7811 | -1597618.8566 | -2107964.9957 | -1689839.0617 | -1276861.699 | 69892.5306 | 3292309.0456 | 9978900.737 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 1332.0577 | -75391.9847 | -691339.7811 | -1597618.8566 | -2107964.9957 | -1689839.0617 | -1276861.699 | 69892.5306 | 3292309.0456 | 9978900.737 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231
| Total annualised capex |  |  |  | 0 | -89530.7901 | -675744.2966 | -1705348.3827 | -2451395.6664 | -2451395.6664 | -2684175.7206 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748 | -2916955.7748
| Total benefits |  |  |  | 1332.0577 | 14138.8054 | -15595.4845 | 107729.5261 | 343430.6707 | 761556.6047 | 1407314.0216 | 2986848.3054 | 6209264.8204 | 12895856.5119 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979 | 12895512.0979
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 1332.0577 | -84345.0637 | -758914.2108 | -1768153.6948 | -2353104.5623 | -1934978.6283 | -1545279.2711 | -221803.0469 | 3000613.4681 | 9687205.1595 | 9686860.7456 | 9686860.7456 | 9686860.7456 | 9686860.7456 | 9686860.7456 | 9686860.7456 | 9686860.7456 | 9686860.7456 | 9686860.7456 | 9686860.7456 | 9686860.7456 | 9686860.7456 | 9686860.7456 | 9686860.7456 | 9686860.7456
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 1332.0577 | -66438.9057 | -623765.3515 | -1427084.0183 | -1862825.4291 | -1444699.495 | -1008444.127 | 361588.1081 | 3584004.6231 | 10270596.3145 | 10270251.9006 | 10270251.9006 | 10270251.9006 | 10270251.9006 | 10270251.9006 | 10270251.9006 | 10270251.9006 | 10270251.9006 | 10270251.9006 | 10270251.9006 | 10270251.9006 | 10270251.9006 | 10270251.9006 | 10270251.9006 | 10270251.9006
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 1465.2634 | -73978.1042 | -692899.3296 | -1586845.904 | -2073621.9286 | -1613683.4012 | -1136130.2969 | 368577.3611 | 3913235.5276 | 11268486.3882 | 11268107.5329 | 11268107.5329 | 11268107.5329 | 11268107.5329 | 11268107.5329 | 11268107.5329 | 11268107.5329 | 11268107.5329 | 11268107.5329 | 11268107.5329 | 11268107.5329 | 11268107.5329 | 11268107.5329 | 11268107.5329 | 11268107.5329
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 1198.8519 | -76805.8653 | -689780.2327 | -1608391.8092 | -2142308.0628 | -1765994.7221 | -1417593.1012 | -228792.2999 | 2671382.5636 | 8689315.0858 | 8689005.1133 | 8689005.1133 | 8689005.1133 | 8689005.1133 | 8689005.1133 | 8689005.1133 | 8689005.1133 | 8689005.1133 | 8689005.1133 | 8689005.1133 | 8689005.1133 | 8689005.1133 | 8689005.1133 | 8689005.1133 | 8689005.1133
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 1198.8519 | -85758.9443 | -757354.6623 | -1778926.6474 | -2387447.6294 | -2011134.2888 | -1686010.6733 | -520487.8774 | 2379686.9861 | 8397619.5084 | 8397309.5358 | 8397309.5358 | 8397309.5358 | 8397309.5358 | 8397309.5358 | 8397309.5358 | 8397309.5358 | 8397309.5358 | 8397309.5358 | 8397309.5358 | 8397309.5358 | 8397309.5358 | 8397309.5358 | 8397309.5358 | 8397309.5358
sens | 0 | 0% | 0% | Option 3sens | 1332.0577 | -75391.9847 | -691339.7811 | -1597618.8566 | -2107964.9957 | -1689839.0617 | -1276861.699 | 69892.5306 | 3292309.0456 | 9978900.737 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231
sens | 0 | 0% | 0% | Option 3sens | 1332.0577 | -75391.9847 | -691339.7811 | -1597618.8566 | -2107964.9957 | -1689839.0617 | -1276861.699 | 69892.5306 | 3292309.0456 | 9978900.737 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231
sens | 0 | 0% | 0% | Option 3sens | 1332.0577 | -75391.9847 | -691339.7811 | -1597618.8566 | -2107964.9957 | -1689839.0617 | -1276861.699 | 69892.5306 | 3292309.0456 | 9978900.737 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231 | 9978556.3231

## Option4
CitiPower
Brunswick modernisation
OPTION 4 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 47477.1919 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option5
CitiPower
Brunswick modernisation
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 47477.1919 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
CitiPower
Brunswick modernisation
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2024-06-30 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 140768686.3424 | 2026-06-30 |  | 8802.479 | 32296.0593 | 100176.1255 | 259258.5187 | 567548.9725 | 1080619.2557 | 1861484.7455 | 3338712.2722 | 6930663.6877 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 107581409.5959 | 2026-06-30 |  | 8802.479 | 32296.0593 | 100176.1255 | 259258.5187 | 567548.9725 | 1080619.2557 | 1861484.7455 | 3338712.2722 | 6930663.6877 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 824654.7202 | 2026-06-30 |  | 7320.0152 | 16560.804 | 98538.6867 | 139364.9667 | 185340.6359 | 233073.2793 | 295267.1734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Capital expenditure | Option 2Capital expenditure | -103300544.4895 | 2026-06-30 |  | -2337116.5575 | -15302548.8882 | -26876840.411 | -19474858.3996 | -10834844.6963 | -21669689.3926 | -21669689.3926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 824654.7202 | 2026-06-30 |  | 7320.0152 | 16560.804 | 98538.6867 | 139364.9667 | 185340.6359 | 233073.2793 | 295267.1734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -52237542.5039 | 2026-06-30 |  | 0 | -99639.9485 | -752044.3735 | -1897903.7816 | -2728189.2385 | -3190118.8605 | -4113978.1044 | -5037837.3484 | -5037837.3484 | -5037837.3484 | -5037837.3484 | -5037837.3484 | -5037837.3484 | -5037837.3484 | -5037837.3484 | -5037837.3484 | -5037837.3484 | -5037837.3484 | -5037837.3484 | -5037837.3484 | 0 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 106756754.8757 | 2026-06-30 |  | 1482.4638 | 15735.2553 | 1637.4387 | 119893.552 | 382208.3365 | 847545.9763 | 1566217.5721 | 3338712.2722 | 6930663.6877 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 14376250.9543 | 0 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 1482.4638 | -83904.6932 | -750406.9347 | -1778010.2296 | -2345980.9019 | -2342572.8841 | -2547760.5323 | -1699125.0761 | 1892826.3393 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 54519212.3718 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -52237542.5039 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 106756754.8757 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 1090981.7171 | 2026-06-30 |  | 7320.0152 | 16560.804 | 117532.5374 | 139364.9667 | 185340.6359 | 233073.2793 | 295267.1734 | 14611.0202 | 20294.3441 | 24289.1559 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585
Option 3 | Capital expenditure | Option 3Capital expenditure | -68645735.1931 | 2026-06-30 |  | -2337116.5575 | -15302548.8882 | -26876840.411 | -19474858.3996 | 0 | -6076503.0494 | -6076503.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 1034025.8591 | 2026-06-30 |  | 7320.0152 | 16560.804 | 117532.5374 | 139364.9667 | 185340.6359 | 233073.2793 | 295267.1734 | 14611.0202 | 20294.3441 | 24289.1559 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 24672.4585 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -36195105.083 | 2026-06-30 |  | 0 | -99639.9485 | -752044.3735 | -1897903.7816 | -2728189.2385 | -2728189.2385 | -2987253.1047 | -3246316.9709 | -3246316.9709 | -3246316.9709 | -3246316.9709 | -3246316.9709 | -3246316.9709 | -3246316.9709 | -3246316.9709 | -3246316.9709 | -3246316.9709 | -3246316.9709 | -3246316.9709 | -3246316.9709 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 106547383.7368 | 2026-06-30 |  | 1482.4638 | 15735.2553 | -17356.4119 | 119893.552 | 382208.3365 | 847545.9763 | 1566217.5721 | 3324101.252 | 6910369.3436 | 14351961.7984 | 14351578.4958 | 14351578.4958 | 14351578.4958 | 14351578.4958 | 14351578.4958 | 14351578.4958 | 14351578.4958 | 14351578.4958 | 14351578.4958 | 14351578.4958 | 0 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 1482.4638 | -83904.6932 | -769400.7854 | -1778010.2296 | -2345980.9019 | -1880643.2621 | -1421035.5326 | 77784.2812 | 3664052.3728 | 11105644.8276 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | 70352278.6537 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -36195105.083 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 106547383.7368 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 0 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | 0 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 0 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49
Option 3 | Annualised capex | -1 |  |  | Option 3 annualised capex | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 3.2463 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 0.0088025 | 0.032296 | 0.10018 | 0.25926 | 0.56755 | 1.0806 | 1.8615 | 3.3387 | 6.9307 | 14.3763 | 14.3763 | 14.3763 | 14.3763 | 14.3763 | 14.3763 | 14.3763 | 14.3763 | 14.3763 | 14.3763 | 14.3763 | 14.3763 | 14.3763 | 14.3763 | 14.3763 | 14.3763
[6 empty] | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49
Energy at risk | Energy at risk (weighted) | 272.0818 |  |  | Energy at risk energy at risk (weighted) | 0.16659 | 0.61123 | 1.8959 | 4.9067 | 10.7413 | 20.4516 | 35.2301 | 63.1878 | 131.1682 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818 | 272.0818
Option 1 (base case) | Energy at risk value | 12.9177 |  |  | Option 1 (base case) risk cost | 0.0079094 | 0.029019 | 0.090013 | 0.23295 | 0.50997 | 0.97098 | 1.6726 | 3 | 6.2275 | 12.9177 | 12.9177 | 12.9177 | 12.9177 | 12.9177 | 12.9177 | 12.9177 | 12.9177 | 12.9177 | 12.9177 | 12.9177 | 12.9177 | 12.9177 | 12.9177 | 12.9177 | 12.9177

## Sensitivity_calcs
CitiPower
Brunswick modernisation
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
[7 empty] | 45473 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49
PV
[25 empty] | 9338413.6059 | 9338413.6059 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 54519212.3718 |  | 0 | 1482.4638 | -83904.6932 | -750406.9347 | -1778010.2296 | -2345980.9019 | -2342572.8841 | -2547760.5323 | -1699125.0761 | 1892826.3393 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 0 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 49295458.1214 |  | 0 | 1482.4638 | -93868.6881 | -825611.3721 | -1967800.6078 | -2618799.8258 | -2661584.7702 | -2959158.3428 | -2202908.811 | 1389042.6045 | 8834629.8711 | 8834629.8711 | 8834629.8711 | 8834629.8711 | 8834629.8711 | 8834629.8711 | 8834629.8711 | 8834629.8711 | 8834629.8711 | 8834629.8711 | 8834629.8711 | 0 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 59742966.6221 |  | 0 | 1482.4638 | -73940.6984 | -675202.4974 | -1588219.8515 | -2073161.9781 | -2023560.9981 | -2136362.7219 | -1195341.3413 | 2396610.0742 | 9842197.3408 | 9842197.3408 | 9842197.3408 | 9842197.3408 | 9842197.3408 | 9842197.3408 | 9842197.3408 | 9842197.3408 | 9842197.3408 | 9842197.3408 | 9842197.3408 | 0 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 65194887.8593 |  | 0 | 1630.7102 | -82331.1677 | -750243.1909 | -1766020.8744 | -2307760.0683 | -2257818.2865 | -2391138.7751 | -1365253.8489 | 2585892.7081 | 10776038.7014 | 10776038.7014 | 10776038.7014 | 10776038.7014 | 10776038.7014 | 10776038.7014 | 10776038.7014 | 10776038.7014 | 10776038.7014 | 10776038.7014 | 10776038.7014 | 0 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 43843536.8842 |  | 0 | 1334.2174 | -85478.2188 | -750570.6786 | -1789999.5848 | -2384201.7356 | -2427327.4818 | -2704382.2895 | -2032996.3034 | 1199759.9705 | 7900788.5105 | 7900788.5105 | 7900788.5105 | 7900788.5105 | 7900788.5105 | 7900788.5105 | 7900788.5105 | 7900788.5105 | 7900788.5105 | 7900788.5105 | 7900788.5105 | 0 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 38619782.6338 |  | 0 | 1334.2174 | -95442.2136 | -825775.116 | -1979789.963 | -2657020.6594 | -2746339.3678 | -3115780.1 | -2536780.0382 | 695976.2357 | 7397004.7757 | 7397004.7757 | 7397004.7757 | 7397004.7757 | 7397004.7757 | 7397004.7757 | 7397004.7757 | 7397004.7757 | 7397004.7757 | 7397004.7757 | 7397004.7757 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 54519212.3718 |  | 0 | 1482.4638 | -83904.6932 | -750406.9347 | -1778010.2296 | -2345980.9019 | -2342572.8841 | -2547760.5323 | -1699125.0761 | 1892826.3393 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 54519212.3718 |  | 0 | 1482.4638 | -83904.6932 | -750406.9347 | -1778010.2296 | -2345980.9019 | -2342572.8841 | -2547760.5323 | -1699125.0761 | 1892826.3393 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 54519212.3718 |  | 0 | 1482.4638 | -83904.6932 | -750406.9347 | -1778010.2296 | -2345980.9019 | -2342572.8841 | -2547760.5323 | -1699125.0761 | 1892826.3393 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 9338413.6059 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 1482.4638 | -83904.6932 | -769400.7854 | -1778010.2296 | -2345980.9019 | -1880643.2621 | -1421035.5326 | 77784.2812 | 3664052.3728 | 11105644.8276 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 70352278.6537 |  | 0 | 1482.4638 | -83904.6932 | -769400.7854 | -1778010.2296 | -2345980.9019 | -1880643.2621 | -1421035.5326 | 77784.2812 | 3664052.3728 | 11105644.8276 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 0 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 66732768.1454 |  | 0 | 1482.4638 | -93868.6881 | -844605.2227 | -1967800.6078 | -2618799.8258 | -2153462.186 | -1719760.8431 | -246847.4159 | 3339420.6757 | 10781013.1305 | 10780629.8279 | 10780629.8279 | 10780629.8279 | 10780629.8279 | 10780629.8279 | 10780629.8279 | 10780629.8279 | 10780629.8279 | 10780629.8279 | 10780629.8279 | 0 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 73971789.1621 |  | 0 | 1482.4638 | -73940.6984 | -694196.348 | -1588219.8515 | -2073161.9781 | -1607824.3383 | -1122310.2221 | 402415.9783 | 3988684.0698 | 11430276.5247 | 11429893.222 | 11429893.222 | 11429893.222 | 11429893.222 | 11429893.222 | 11429893.222 | 11429893.222 | 11429893.222 | 11429893.222 | 11429893.222 | 0 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 81007017.0274 |  | 0 | 1630.7102 | -82331.1677 | -771136.4266 | -1766020.8744 | -2307760.0683 | -1795888.6645 | -1264413.7754 | 410194.4064 | 4355089.3071 | 12540841.0074 | 12540419.3745 | 12540419.3745 | 12540419.3745 | 12540419.3745 | 12540419.3745 | 12540419.3745 | 12540419.3745 | 12540419.3745 | 12540419.3745 | 12540419.3745 | 0 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | 59697540.2801 |  | 0 | 1334.2174 | -85478.2188 | -767665.1442 | -1789999.5848 | -2384201.7356 | -1965397.8598 | -1577657.2898 | -254625.844 | 2973015.4384 | 9670448.6477 | 9670103.6754 | 9670103.6754 | 9670103.6754 | 9670103.6754 | 9670103.6754 | 9670103.6754 | 9670103.6754 | 9670103.6754 | 9670103.6754 | 9670103.6754 | 0 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | 56078029.7718 |  | 0 | 1334.2174 | -95442.2136 | -842869.5815 | -1979789.963 | -2657020.6594 | -2238216.7836 | -1876382.6003 | -579257.5411 | 2648383.7413 | 9345816.9506 | 9345471.9783 | 9345471.9783 | 9345471.9783 | 9345471.9783 | 9345471.9783 | 9345471.9783 | 9345471.9783 | 9345471.9783 | 9345471.9783 | 9345471.9783 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 70352278.6537 |  | 0 | 1482.4638 | -83904.6932 | -769400.7854 | -1778010.2296 | -2345980.9019 | -1880643.2621 | -1421035.5326 | 77784.2812 | 3664052.3728 | 11105644.8276 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 70352278.6537 |  | 0 | 1482.4638 | -83904.6932 | -769400.7854 | -1778010.2296 | -2345980.9019 | -1880643.2621 | -1421035.5326 | 77784.2812 | 3664052.3728 | 11105644.8276 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 70352278.6537 |  | 0 | 1482.4638 | -83904.6932 | -769400.7854 | -1778010.2296 | -2345980.9019 | -1880643.2621 | -1421035.5326 | 77784.2812 | 3664052.3728 | 11105644.8276 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 11105261.525 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 1 | 1 |  | 2026-27: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2024-25: Max; 2026-27: Preferred
NPV | None | 0 | 54.5192 | 70.3523 |  |  |  | 2024-25: #NAME?; 2026-27: Option 3
sens1 | Capex 10% higher | 0 | 49.2955 | 66.7328 |  |  |  | 2024-25: #NAME?; 2026-27: Option 3
sens2 | Capex 10% lower | 0 | 59.743 | 73.9718 |  |  |  | 2024-25: #NAME?; 2026-27: Option 3
sens3 | Total benefits 10% higher | 0 | 65.1949 | 81.007 |  |  |  | 2024-25: #NAME?; 2026-27: Option 3
sens4 | Total benefits 10% lower | 0 | 43.8435 | 59.6975 |  |  |  | 2024-25: #NAME?; 2026-27: Option 3
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 38.6198 | 56.078 |  |  |  | 2024-25: #NAME?; 2026-27: Option 3
sens | 0 | [6 empty] | 2024-25: #NAME?; 2026-27: #NAME?
sens | 0 | [6 empty] | 2024-25: #NAME?; 2026-27: #NAME?
sens | 0 | [6 empty] | 2024-25: #NAME?; 2026-27: #NAME?

## Misc_calcs
CitiPower
Brunswick modernisation
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2024-25
FIRST YEAR
| Option | First year | Option included
| Option 2 | 1 | TRUE
| Option 3 | 1 | TRUE
| Option 4 | Not used | FALSE
| Option 5 | Not used | FALSE
| First year | 1
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
CitiPower
Brunswick modernisation
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | TRUE | Not used |  | TRUE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
CitiPower
| Reliability in worst-served areas | per MWh | 0
| Network resilience | per MWh | 0
| Enabling solar exports | per MWh | 4220.9954
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.54769
| Customer value of time - business | per minute customer time | 0.54769
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020