## Cover
CitiPower
Regulatory proposal 2026-31
VM transformer
| Model number: | 4.03
2025-01-31
15

## Summary
CitiPower
VM transformer replacement
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Replace #1 transformer completed in 2030-31 |  | -3.0641 | 10.9421 | 7.8779
| Option 3 | Refurbish #1 transformer completed in 2029-30 |  | -0.49333 | 0.67457 | 0.18124
| Option 4 | 0
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | Replace #1 transformer completed in 2030-31 |  | 7.8779
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 0 | 0 | 0 | 2.0682 | 4.1364 |  | 6.2046
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
| Capex and risk ($M, 2026) |  | Value of expected unserved energy ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 7.8779 | 0.18124 |  |  |  | Option 2
| Capex 10% higher |  | 0 | 7.5715 | 0.1319 |  |  |  | Option 2
| Capex 10% lower |  | 0 | 8.1843 | 0.23057 |  |  |  | Option 2
| Total benefits 10% higher |  | 0 | 8.9721 | 0.24869 |  |  |  | Option 2
| Total benefits 10% lower |  | 0 | 6.7837 | 0.11378 |  |  |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  | 0 | 6.4773 | 0.064445 |  |  |  | Option 2
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
CitiPower
VM transformer replacement
Project
|  | Business: |  | CitiPower
|  | Descripton: |  | VM transformer replacement
|  | Date of cost inputs: |  | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Replace #1 transformer completed in 2030-31
|  | Option 3 |  | Refurbish #1 transformer completed in 2029-30
Option 4
Option 5
|  | Compliance project |  | No
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | NC |  | Northcote | 35890.6966 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 0 | 2023-12-31 | per MWh
|  | Network resilience |  |  |  | 0 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 4220.9954 | 2023-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
CitiPower
VM transformer replacement
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 35890.6966 | 2023-12-31 |  | 314043.2114 | 366725.751 | 435144.5083 | 513527.9984 | 576691.9911 | 648806.7666 | 774247.6929 | 946170.4447 | 1075915.541 | 1105431.7594 | 1135299.9251 | 1165519.6523 | 1196090.5882 | 1227012.4118 | 1258284.8332 | 1289907.5928 | 1321880.4603 | 1354203.2342 | 1386875.7408 | 1419897.8336 | 1453269.3926 | 1486990.3239 | 1521060.5586 | 1555480.0525 | 1590248.7857
| Safety risk | (after DF) |  | 2023-12-31 |  | 703.1232 | 724.2438 | 745.623 | 767.2593 | 789.1514 | 811.2981 | 833.6981 | 856.3502 | 879.2531 | 902.4057 | 925.8069 | 949.4554 | 973.3502 | 997.4903 | 1021.8744 | 1046.5017 | 1071.371 | 1096.4814 | 1121.8318 | 1147.4212 | 1173.2488 | 1199.3136 | 1199.3136 | 1199.3136 | 1199.3136
| Unplanned replacement risk |  |  | 2023-12-31 |  | 26504.4365 | 27300.5861 | 28106.4797 | 28922.0666 | 29747.2974 | 30582.1237 | 31426.4982 | 32280.3745 | 33143.7072 | 34016.4519 | 34898.5651 | 35790.0041 | 36690.727 | 37600.6927 | 38519.8612 | 39448.1927 | 40385.6486 | 41332.1907 | 42287.7817 | 43252.3848 | 44225.964 | 45208.4837 | 45208.4837 | 45208.4837 | 45208.4837
| Unplanned fault risk |  |  | 2023-12-31 |  | 2644.8598 | 2724.3071 | 2804.7267 | 2886.1135 | 2968.4627 | 3051.7695 | 3136.0291 | 3221.2368 | 3307.3882 | 3394.4788 | 3482.5043 | 3571.4604 | 3661.3429 | 3752.1478 | 3843.871 | 3936.5085 | 4030.0566 | 4124.5114 | 4219.8692 | 4316.1263 | 4413.2791 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241
| Enviromental risk | (after DF) |  | 2023-12-31 |  | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75
| Noise cost |  |  | 2023-12-31 |  | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
| Total risk cost |  |  |  |  | 398184.3808 | 451763.638 | 521090.0876 | 600392.1878 | 664485.6527 | 737540.708 | 863932.6682 | 1036817.1562 | 1167534.6395 | 1198033.8459 | 1228895.5514 | 1260119.3222 | 1291704.7583 | 1323651.4926 | 1355959.1897 | 1388627.5457 | 1421656.2865 | 1455045.1677 | 1488793.9734 | 1522902.5159 | 1557370.6346 | 1592198.1954 | 1626268.4301 | 1660687.924 | 1695456.6571
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
CitiPower
VM transformer replacement
OPTION 2 | Replace #1 transformer completed in 2030-31
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Replace 1 transformer |  | 50 | 2023-12-31 | 0 | 0 | 0 | 1858359.5333 | 3716719.0667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 1858359.5333 | 3716719.0667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 35890.6966 | 2023-12-31 | 314043.2114 | 366725.751 | 435144.5083 | 513527.9984 | 576691.9911 | 59031.5183 | 103711.6386 | 158627.1832 | 210911.8415 | 243669.5959 | 275020.296 | 305426.9396 | 335188.7206 | 364511.3519 | 393542.8668 | 422393.5785 | 451147.9961 | 479872.3295 | 508619.4251 | 537432.1278 | 566345.6416 | 595389.2286 | 624587.4596 | 653961.1508 | 683528.0795
| Safety risk | (after DF) |  | 2023-12-31 | 703.1232 | 724.2438 | 745.623 | 767.2593 | 789.1514 | 589.6847 | 605.7326 | 622.1837 | 639.0089 | 656.1899 | 673.7134 | 691.5691 | 709.7485 | 728.2447 | 747.0515 | 766.1635 | 785.5761 | 805.285 | 825.2862 | 845.5761 | 866.1516 | 887.0094 | 887.0094 | 887.0094 | 887.0094
| Unplanned replacement risk |  |  | 2023-12-31 | 26504.4365 | 27300.5861 | 28106.4797 | 28922.0666 | 29747.2974 | 22228.3411 | 22833.2701 | 23453.3979 | 24087.6298 | 24735.2729 | 25395.8266 | 26068.9019 | 26754.1819 | 27451.4002 | 28160.3276 | 28880.7626 | 29612.5261 | 30355.4566 | 31109.4073 | 31874.2437 | 32649.8413 | 33436.0847 | 33436.0847 | 33436.0847 | 33436.0847
| Unplanned fault risk |  |  | 2023-12-31 | 2644.8598 | 2724.3071 | 2804.7267 | 2886.1135 | 2968.4627 | 2218.1512 | 2278.5166 | 2340.3988 | 2403.6883 | 2468.3162 | 2534.2324 | 2601.3981 | 2669.7818 | 2739.3567 | 2810.1001 | 2881.9918 | 2955.014 | 3029.1505 | 3104.3868 | 3180.7093 | 3258.1056 | 3336.5643 | 3336.5643 | 3336.5643 | 3336.5643
| Enviromental risk | (after DF) |  | 2023-12-31 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5
| Noise cost |  |  | 2023-12-31 | 50000 | 50000 | 50000 | 50000 | 50000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000
| Total risk cost |  |  |  | 398184.3808 | 451763.638 | 521090.0876 | 600392.1878 | 664485.6527 | 109655.1953 | 155016.658 | 210630.6636 | 263629.6685 | 297116.875 | 329211.5684 | 360376.3087 | 390909.9327 | 421017.8535 | 450847.846 | 480509.9965 | 510088.6123 | 539649.7216 | 569246.0054 | 598920.1568 | 628707.2401 | 658636.3871 | 687834.618 | 717208.3093 | 746775.2379
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - residential | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - business | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 627885.5127 | 708916.0103 | 826186.4926 | 903904.971 | 900916.9709 | 899683.9829 | 899743.0135 | 900794.8256 | 902633.639 | 905111.3438 | 908117.5492 | 911567.6742 | 915395.446 | 919547.9681 | 923982.3591 | 928663.3945 | 933561.8083 | 938433.812 | 943479.6147 | 948681.4192
Capital expenditure
| Replace 1 transformer |  |  | 2023-12-31 | 0 | 0 | 0 | -1858359.5333 | -3716719.0667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Replace 1 transformer |  |  | 2023-12-31 | 0 | 0 | 0 | -1858359.5333 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6 | -5575078.6
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Replace 1 transformer |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -79228.7606 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -79228.7606 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -79228.7606 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 627885.5127 | 708916.0103 | 826186.4926 | 903904.971 | 900916.9709 | 899683.9829 | 899743.0135 | 900794.8256 | 902633.639 | 905111.3438 | 908117.5492 | 911567.6742 | 915395.446 | 919547.9681 | 923982.3591 | 928663.3945 | 933561.8083 | 938433.812 | 943479.6147 | 948681.4192
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -79228.7606 | 390199.2309 | 471229.7284 | 588500.2108 | 666218.6892 | 663230.6891 | 661997.7011 | 662056.7317 | 663108.5438 | 664947.3572 | 667425.0619 | 670431.2674 | 673881.3923 | 677709.1642 | 681861.6862 | 686296.0772 | 690977.1127 | 695875.5264 | 700747.5302 | 705793.3329 | 710995.1373
| First capex year |  |  | 4
| First year |  |  | 4
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | 0 | 0 | 0 | -79228.7606 | 390199.2309 | 471229.7284 | 588500.2108 | 666218.6892 | 663230.6891 | 661997.7011 | 662056.7317 | 663108.5438 | 664947.3572 | 667425.0619 | 670431.2674 | 673881.3923 | 677709.1642 | 681861.6862 | 686296.0772 | 690977.1127 | 695875.5264 | 700747.5302 | 705793.3329 | 710995.1373
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | -79228.7606 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818 | -237686.2818
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 627885.5127 | 708916.0103 | 826186.4926 | 903904.971 | 900916.9709 | 899683.9829 | 899743.0135 | 900794.8256 | 902633.639 | 905111.3438 | 908117.5492 | 911567.6742 | 915395.446 | 919547.9681 | 923982.3591 | 928663.3945 | 933561.8083 | 938433.812 | 943479.6147 | 948681.4192
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | 0 | 0 | 0 | -87151.6367 | 366430.6027 | 447461.1002 | 564731.5826 | 642450.061 | 639462.0609 | 638229.0729 | 638288.1035 | 639339.9156 | 641178.729 | 643656.4337 | 646662.6392 | 650112.7642 | 653940.536 | 658093.058 | 662527.4491 | 667208.4845 | 672106.8983 | 676978.902 | 682024.7047 | 687226.5091
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | 0 | 0 | 0 | -71305.8846 | 413967.8591 | 494998.3566 | 612268.8389 | 689987.3174 | 686999.3172 | 685766.3293 | 685825.3598 | 686877.172 | 688715.9854 | 691193.6901 | 694199.8955 | 697650.0205 | 701477.7924 | 705630.3144 | 710064.7054 | 714745.7409 | 719644.1546 | 724516.1584 | 729561.9611 | 734763.7655
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | 0 | 0 | 0 | -79228.7606 | 452987.7822 | 542121.3294 | 671118.86 | 756609.1863 | 753322.3862 | 751966.0994 | 752031.033 | 753188.0263 | 755210.7211 | 757936.1963 | 761243.0223 | 765038.1598 | 769248.7088 | 773816.483 | 778694.3132 | 783843.4521 | 789231.7073 | 794590.9114 | 800141.2943 | 805863.2792
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | 0 | 0 | 0 | -79228.7606 | 327410.6796 | 400338.1274 | 505881.5615 | 575828.1921 | 573138.992 | 572029.3028 | 572082.4303 | 573029.0612 | 574683.9933 | 576913.9275 | 579619.5124 | 582724.6249 | 586169.6196 | 589906.8894 | 593897.8413 | 598110.7732 | 602519.3456 | 606904.149 | 611445.3714 | 616126.9954
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | 0 | 0 | 0 | -87151.6367 | 303642.0514 | 376569.4992 | 482112.9333 | 552059.5639 | 549370.3638 | 548260.6746 | 548313.8021 | 549260.433 | 550915.3651 | 553145.2994 | 555850.8842 | 558955.9967 | 562400.9914 | 566138.2612 | 570129.2131 | 574342.1451 | 578750.7174 | 583135.5208 | 587676.7432 | 592358.3672
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 0 | 0 | -79228.7606 | 390199.2309 | 471229.7284 | 588500.2108 | 666218.6892 | 663230.6891 | 661997.7011 | 662056.7317 | 663108.5438 | 664947.3572 | 667425.0619 | 670431.2674 | 673881.3923 | 677709.1642 | 681861.6862 | 686296.0772 | 690977.1127 | 695875.5264 | 700747.5302 | 705793.3329 | 710995.1373
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 0 | 0 | -79228.7606 | 390199.2309 | 471229.7284 | 588500.2108 | 666218.6892 | 663230.6891 | 661997.7011 | 662056.7317 | 663108.5438 | 664947.3572 | 667425.0619 | 670431.2674 | 673881.3923 | 677709.1642 | 681861.6862 | 686296.0772 | 690977.1127 | 695875.5264 | 700747.5302 | 705793.3329 | 710995.1373
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 0 | 0 | -79228.7606 | 390199.2309 | 471229.7284 | 588500.2108 | 666218.6892 | 663230.6891 | 661997.7011 | 662056.7317 | 663108.5438 | 664947.3572 | 667425.0619 | 670431.2674 | 673881.3923 | 677709.1642 | 681861.6862 | 686296.0772 | 690977.1127 | 695875.5264 | 700747.5302 | 705793.3329 | 710995.1373

## Option3
CitiPower
VM transformer replacement
OPTION 3 | Refurbish #1 transformer completed in 2029-30
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Refurbish 1 transformer |  | 10 | 2023-12-31 | 0 | 0 | 0 | 500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 35890.6966 | 2023-12-31 | 314043.2114 | 366725.751 | 435144.5083 | 513527.9984 | 552672.9018 | 621750.9518 | 742002.3231 | 906855.2676 | 1031279.0303 | 1059540.5427 | 1088138.0036 | 1117071.014 | 1146339.206 | 1175942.2423 | 1205879.8148 | 1236151.6445 | 1266757.4801 | 1297697.0979 | 1328970.3003 | 1360576.9159 | 1392516.7983 | 1424789.8259 | 1457395.901 | 1490334.9492 | 1523606.9193
| Safety risk | (after DF) |  | 2023-12-31 | 703.1232 | 724.2438 | 745.623 | 767.2593 | 784.8505 | 806.861 | 829.1229 | 851.6352 | 874.3967 | 897.4061 | 920.6623 | 944.1643 | 967.9108 | 991.9009 | 1016.1334 | 1040.6073 | 1065.3216 | 1090.2753 | 1115.4674 | 1140.897 | 1166.563 | 1192.4646 | 1192.4646 | 1192.4646 | 1192.4646
| Unplanned replacement risk |  |  | 2023-12-31 | 26504.4365 | 27300.5861 | 28106.4797 | 28922.0666 | 28936.6837 | 29745.8256 | 30564.1866 | 31391.7222 | 32228.3888 | 33074.1437 | 33928.9448 | 34792.7512 | 35665.5226 | 36547.2195 | 37437.8032 | 38337.2356 | 39245.4794 | 40162.4981 | 41088.2555 | 42022.7163 | 42965.8459 | 43917.61 | 43917.61 | 43917.61 | 43917.61
| Unplanned fault risk |  |  | 2023-12-31 | 2644.8598 | 2724.3071 | 2804.7267 | 2886.1135 | 2968.4627 | 3051.7695 | 3136.0291 | 3221.2368 | 3307.3882 | 3394.4788 | 3482.5043 | 3571.4604 | 3661.3429 | 3752.1478 | 3843.871 | 3936.5085 | 4030.0566 | 4124.5114 | 4219.8692 | 4316.1263 | 4413.2791 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241
| Enviromental risk | (after DF) |  | 2023-12-31 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125
| Noise cost |  |  | 2023-12-31 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
| Total risk cost |  |  |  | 398184.3808 | 451763.638 | 521090.0876 | 600392.1878 | 637801.0238 | 707793.5328 | 828969.7867 | 994757.9868 | 1120127.329 | 1149344.6962 | 1178908.24 | 1208817.5148 | 1239072.1073 | 1269671.6354 | 1300615.7473 | 1331904.1209 | 1363536.4628 | 1395512.5077 | 1427832.0174 | 1460494.7805 | 1493500.6113 | 1526849.3496 | 1559455.4247 | 1592394.4729 | 1625666.443
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 26684.6289 | 29747.1752 | 34962.8816 | 42059.1693 | 47407.3105 | 48689.1496 | 49987.3114 | 51301.8074 | 52632.651 | 53979.8572 | 55343.4425 | 56723.4248 | 58119.8237 | 59532.66 | 60961.956 | 62407.7354 | 63870.0232 | 65348.8458 | 66813.0054 | 68293.4511 | 69790.2141
Capital expenditure
| Refurbish 1 transformer |  |  | 2023-12-31 | 0 | 0 | 0 | -500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Refurbish 1 transformer |  |  | 2023-12-31 | 0 | 0 | 0 | -500000 | -500000 | -500000 | -500000 | -500000 | -500000 | -500000 | -500000 | -500000 | -500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Refurbish 1 transformer |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 26684.6289 | 29747.1752 | 34962.8816 | 42059.1693 | 47407.3105 | 48689.1496 | 49987.3114 | 51301.8074 | 52632.651 | 53979.8572 | 55343.4425 | 56723.4248 | 58119.8237 | 59532.66 | 60961.956 | 62407.7354 | 63870.0232 | 65348.8458 | 66813.0054 | 68293.4511 | 69790.2141
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -33436.055 | -30373.5087 | -25157.8024 | -18061.5146 | -12713.3735 | -11431.5343 | -10133.3726 | -8818.8766 | -7488.033 | -6140.8267 | 55343.4425 | 56723.4248 | 58119.8237 | 59532.66 | 60961.956 | 62407.7354 | 63870.0232 | 65348.8458 | 66813.0054 | 68293.4511 | 69790.2141
| First capex year |  |  | 4
| First year |  |  | 4
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | 0 | 0 | 0 | -33436.055 | -30373.5087 | -25157.8024 | -18061.5146 | -12713.3735 | -11431.5343 | -10133.3726 | -8818.8766 | -7488.033 | -6140.8267 | 55343.4425 | 56723.4248 | 58119.8237 | 59532.66 | 60961.956 | 62407.7354 | 63870.0232 | 65348.8458 | 66813.0054 | 68293.4511 | 69790.2141
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 26684.6289 | 29747.1752 | 34962.8816 | 42059.1693 | 47407.3105 | 48689.1496 | 49987.3114 | 51301.8074 | 52632.651 | 53979.8572 | 55343.4425 | 56723.4248 | 58119.8237 | 59532.66 | 60961.956 | 62407.7354 | 63870.0232 | 65348.8458 | 66813.0054 | 68293.4511 | 69790.2141
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | 0 | 0 | 0 | -39448.1234 | -36385.5771 | -31169.8708 | -24073.583 | -18725.4418 | -17443.6027 | -16145.441 | -14830.945 | -13500.1013 | -12152.8951 | 55343.4425 | 56723.4248 | 58119.8237 | 59532.66 | 60961.956 | 62407.7354 | 63870.0232 | 65348.8458 | 66813.0054 | 68293.4511 | 69790.2141
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | 0 | 0 | 0 | -27423.9866 | -24361.4403 | -19145.734 | -12049.4462 | -6701.3051 | -5419.4659 | -4121.3042 | -2806.8082 | -1475.9646 | -128.7583 | 55343.4425 | 56723.4248 | 58119.8237 | 59532.66 | 60961.956 | 62407.7354 | 63870.0232 | 65348.8458 | 66813.0054 | 68293.4511 | 69790.2141
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | 0 | 0 | 0 | -30767.5921 | -27398.7912 | -21661.5142 | -13855.5977 | -7972.6424 | -6562.6193 | -5134.6414 | -3688.6958 | -2224.7679 | -742.841 | 60877.7867 | 62395.7673 | 63931.8061 | 65485.926 | 67058.1516 | 68648.509 | 70257.0256 | 71883.7303 | 73494.3059 | 75122.7962 | 76769.2355
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | 0 | 0 | 0 | -36104.5179 | -33348.2263 | -28654.0905 | -22267.4316 | -17454.1045 | -16300.4493 | -15132.1037 | -13949.0573 | -12751.298 | -11538.8125 | 49809.0982 | 51051.0823 | 52307.8413 | 53579.394 | 54865.7604 | 56166.9619 | 57483.0209 | 58813.9612 | 60131.7048 | 61464.106 | 62811.1927
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | 0 | 0 | 0 | -42116.5863 | -39360.2947 | -34666.1589 | -28279.5 | -23466.1729 | -22312.5176 | -21144.1721 | -19961.1257 | -18763.3664 | -17550.8809 | 49809.0982 | 51051.0823 | 52307.8413 | 53579.394 | 54865.7604 | 56166.9619 | 57483.0209 | 58813.9612 | 60131.7048 | 61464.106 | 62811.1927
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 0 | -33436.055 | -30373.5087 | -25157.8024 | -18061.5146 | -12713.3735 | -11431.5343 | -10133.3726 | -8818.8766 | -7488.033 | -6140.8267 | 55343.4425 | 56723.4248 | 58119.8237 | 59532.66 | 60961.956 | 62407.7354 | 63870.0232 | 65348.8458 | 66813.0054 | 68293.4511 | 69790.2141
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 0 | -33436.055 | -30373.5087 | -25157.8024 | -18061.5146 | -12713.3735 | -11431.5343 | -10133.3726 | -8818.8766 | -7488.033 | -6140.8267 | 55343.4425 | 56723.4248 | 58119.8237 | 59532.66 | 60961.956 | 62407.7354 | 63870.0232 | 65348.8458 | 66813.0054 | 68293.4511 | 69790.2141
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 0 | -33436.055 | -30373.5087 | -25157.8024 | -18061.5146 | -12713.3735 | -11431.5343 | -10133.3726 | -8818.8766 | -7488.033 | -6140.8267 | 55343.4425 | 56723.4248 | 58119.8237 | 59532.66 | 60961.956 | 62407.7354 | 63870.0232 | 65348.8458 | 66813.0054 | 68293.4511 | 69790.2141

## Option4
CitiPower
VM transformer replacement
OPTION 4 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 35890.6966 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option5
CitiPower
VM transformer replacement
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 35890.6966 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
CitiPower
VM transformer replacement
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 18470485.4905 | 2026-06-30 |  | 349502.6615 | 408133.726 | 484277.8263 | 571511.8037 | 641807.81 | 722065.2557 | 861670.0488 | 1053005.0536 | 1197400.0121 | 1230248.9848 | 1263489.6441 | 1297121.5607 | 1331144.3419 | 1365557.6304 | 1400361.1036 | 1435554.4727 | 1471137.4813 | 1507109.9051 | 1543471.5509 | 1580222.2556 | 1617361.8857 | 1654890.3366 | 1692807.5316 | 1731113.4217 | 1769807.9845
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 18587220.4407 | 2026-06-30 |  | 443144.433 | 502773.4659 | 579927.7485 | 668184.0586 | 739514.4863 | 820818.3812 | 961481.5921 | 1153886.9251 | 1299364.0655 | 1333307.0179 | 1367653.4002 | 1402402.7297 | 1437554.561 | 1473108.4855 | 1509064.1303 | 1545421.1568 | 1582179.2601 | 1619338.1682 | 1656897.6409 | 1694857.4692 | 1733217.4744 | 1771977.5072 | 1809894.7023 | 1848200.5924 | 1886895.1551
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 7149730.1462 | 2026-06-30 |  | 349502.6615 | 408133.726 | 484277.8263 | 571511.8037 | 641807.81 | 65696.9233 | 115421.9942 | 176538.1983 | 234726.4557 | 271182.9749 | 306073.5654 | 339913.5037 | 373035.766 | 405669.2933 | 437978.8334 | 470087.1553 | 502088.3103 | 534055.9842 | 566048.9904 | 598115.0116 | 630293.2267 | 662616.2021 | 695111.2826 | 727801.635 | 760707.0438
Option 2 | Capital expenditure | Option 2Capital expenditure | -5376726.415 | 2026-06-30 |  | 0 | 0 | 0 | -2068191.8262 | -4136383.6525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 7645154.8669 | 2026-06-30 |  | 443144.433 | 502773.4659 | 579927.7485 | 668184.0586 | 739514.4863 | 122036.6535 | 172519.999 | 234413.5292 | 293396.792 | 330665.1276 | 366383.7179 | 401067.3514 | 435048.6077 | 468556.0936 | 501754.2694 | 534765.6518 | 567684.0674 | 600582.9998 | 633521.0783 | 666545.8167 | 699696.2383 | 733004.7646 | 765499.845 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -3064129.7544 | 2026-06-30 |  | 0 | 0 | 0 | 0 | -88174.6896 | -264524.0689 | -264524.0689 | -264524.0689 | -264524.0689 | -264524.0689 | -264524.0689 | -264524.0689 | -264524.0689 | -264524.0689 | -264524.0689 | -264524.0689 | -264524.0689 | -264524.0689 | -264524.0689 | -264524.0689 | -264524.0689 | -264524.0689 | -264524.0689 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 10942065.5738 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 698781.7276 | 788961.5931 | 919473.3959 | 1005967.2734 | 1002641.8903 | 1001269.6824 | 1001335.3783 | 1002505.9533 | 1004552.392 | 1007309.8609 | 1010655.5049 | 1014495.1927 | 1018755.1684 | 1023376.5626 | 1028311.6525 | 1033521.236 | 1038972.7427 | 1044394.8572 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | -88174.6896 | 434257.6587 | 524437.5241 | 654949.327 | 741443.2045 | 738117.8214 | 736745.6134 | 736811.3093 | 737981.8843 | 740028.323 | 742785.792 | 746131.436 | 749971.1237 | 754231.0994 | 758852.4937 | 763787.5835 | 768997.1671 | 774448.6737 | 779870.7883 | 0 | 0
Option 2 | NPV | Option 2NPV | 7877935.8194 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -3064129.7544 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 10942065.5738 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 17770699.465 | 2026-06-30 |  | 349502.6615 | 408133.726 | 484277.8263 | 571511.8037 | 615076.6618 | 691954.4972 | 825783.769 | 1009250.6957 | 1147723.4748 | 1179176.0693 | 1211002.5452 | 1243202.4584 | 1275775.3995 | 1308720.9929 | 1342038.8959 | 1375728.798 | 1409790.4196 | 1444223.5114 | 1479027.8539 | 1514203.2561 | 1549749.5552 | 1585666.6157 | 1621954.329 | 1658612.6124 | 1695641.4086
Option 3 | Capital expenditure | Option 3Capital expenditure | -493332.6482 | 2026-06-30 |  | 0 | 0 | 0 | -556456.3232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 17912652.6115 | 2026-06-30 |  | 443144.433 | 502773.4659 | 579927.7485 | 668184.0586 | 709816.8253 | 787712.3737 | 922570.9591 | 1107078.7437 | 1246603.8701 | 1279120.2475 | 1312021.8893 | 1345308.2995 | 1378979.0181 | 1413033.6198 | 1447471.7133 | 1482292.9399 | 1517496.9733 | 1553083.518 | 1589052.3091 | 1625403.1112 | 1662135.7178 | 1699249.9504 | 1735537.6636 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -493332.6482 | 2026-06-30 |  | 0 | 0 | 0 | 0 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 674567.8292 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 29697.661 | 33106.0075 | 38910.633 | 46808.1814 | 52760.1954 | 54186.7704 | 55631.511 | 57094.4302 | 58575.5429 | 60074.8657 | 61592.417 | 63128.2168 | 64682.2868 | 66254.6502 | 67845.3318 | 69454.358 | 71081.7566 | 72727.5569 | 74357.0386 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | -37211.4085 | -33803.062 | -27998.4364 | -20100.888 | -14148.8741 | -12722.2991 | -11277.5585 | -9814.6393 | -8333.5266 | -6834.2037 | 61592.417 | 63128.2168 | 64682.2868 | 66254.6502 | 67845.3318 | 69454.358 | 71081.7566 | 72727.5569 | 74357.0386 | 0 | 0
Option 3 | NPV | Option 3NPV | 181235.181 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -493332.6482 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 674567.8292 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 0 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | 0 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 0 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0.26452 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 0.44314 | 0.50277 | 0.57993 | 0.66818 | 0.73951 | 0.82082 | 0.96148 | 1.1539 | 1.2994 | 1.3333 | 1.3677 | 1.4024 | 1.4376 | 1.4731 | 1.5091 | 1.5454 | 1.5822 | 1.6193 | 1.6569 | 1.6949 | 1.7332 | 1.772 | 1.8099 | 1.8482 | 1.8869
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 0 |  |  | Energy at risk energy at risk (weighted) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Energy at risk value | 1.5902 |  |  | Option 1 (base case) risk cost | 0.31404 | 0.36673 | 0.43514 | 0.51353 | 0.57669 | 0.64881 | 0.77425 | 0.94617 | 1.0759 | 1.1054 | 1.1353 | 1.1655 | 1.1961 | 1.227 | 1.2583 | 1.2899 | 1.3219 | 1.3542 | 1.3869 | 1.4199 | 1.4533 | 1.487 | 1.5211 | 1.5555 | 1.5902

## Sensitivity_calcs
CitiPower
VM transformer replacement
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
[7 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 758852.4937 | 763787.5835 | 768997.1671 | 774448.6737 | 779870.7883 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 7877935.8194 |  | 0 | 0 | 0 | 0 | 0 | -88174.6896 | 434257.6587 | 524437.5241 | 654949.327 | 741443.2045 | 738117.8214 | 736745.6134 | 736811.3093 | 737981.8843 | 740028.323 | 742785.792 | 746131.436 | 749971.1237 | 754231.0994 | 758852.4937 | 763787.5835 | 768997.1671 | 774448.6737 | 779870.7883 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 7571522.844 |  | 0 | 0 | 0 | 0 | 0 | -96992.1586 | 407805.2518 | 497985.1172 | 628496.9201 | 714990.7976 | 711665.4145 | 710293.2065 | 710358.9024 | 711529.4774 | 713575.9161 | 716333.3851 | 719679.0291 | 723518.7168 | 727778.6925 | 732400.0868 | 737335.1767 | 742544.7602 | 747996.2668 | 753418.3814 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 8184348.7949 |  | 0 | 0 | 0 | 0 | 0 | -79357.2207 | 460710.0656 | 550889.931 | 681401.7339 | 767895.6114 | 764570.2282 | 763198.0203 | 763263.7162 | 764434.2912 | 766480.7299 | 769238.1988 | 772583.8429 | 776423.5306 | 780683.5063 | 785304.9006 | 790239.9904 | 795449.574 | 800901.0806 | 806323.1952 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 8972142.3768 |  | 0 | 0 | 0 | 0 | 0 | -88174.6896 | 504135.8314 | 603333.6834 | 746896.6666 | 842039.9318 | 838382.0104 | 836872.5817 | 836944.8471 | 838232.4796 | 840483.5622 | 843516.778 | 847196.9865 | 851420.643 | 856106.6163 | 861190.15 | 866618.7488 | 872349.2907 | 878345.948 | 884310.274 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 6783729.262 |  | 0 | 0 | 0 | 0 | 0 | -88174.6896 | 364379.4859 | 445541.3648 | 563001.9874 | 640846.4771 | 637853.6323 | 636618.6452 | 636677.7715 | 637731.289 | 639573.0838 | 642054.8059 | 645065.8855 | 648521.6045 | 652355.5826 | 656514.8374 | 660956.4183 | 665645.0435 | 670551.3994 | 675431.3026 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 6477316.2866 |  | 0 | 0 | 0 | 0 | 0 | -96992.1586 | 337927.079 | 419088.9579 | 536549.5805 | 614394.0703 | 611401.2254 | 610166.2383 | 610225.3646 | 611278.8821 | 613120.6769 | 615602.399 | 618613.4786 | 622069.1976 | 625903.1757 | 630062.4305 | 634504.0114 | 639192.6366 | 644098.9926 | 648978.8957 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 7877935.8194 |  | 0 | 0 | 0 | 0 | 0 | -88174.6896 | 434257.6587 | 524437.5241 | 654949.327 | 741443.2045 | 738117.8214 | 736745.6134 | 736811.3093 | 737981.8843 | 740028.323 | 742785.792 | 746131.436 | 749971.1237 | 754231.0994 | 758852.4937 | 763787.5835 | 768997.1671 | 774448.6737 | 779870.7883 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 7877935.8194 |  | 0 | 0 | 0 | 0 | 0 | -88174.6896 | 434257.6587 | 524437.5241 | 654949.327 | 741443.2045 | 738117.8214 | 736745.6134 | 736811.3093 | 737981.8843 | 740028.323 | 742785.792 | 746131.436 | 749971.1237 | 754231.0994 | 758852.4937 | 763787.5835 | 768997.1671 | 774448.6737 | 779870.7883 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 7877935.8194 |  | 0 | 0 | 0 | 0 | 0 | -88174.6896 | 434257.6587 | 524437.5241 | 654949.327 | 741443.2045 | 738117.8214 | 736745.6134 | 736811.3093 | 737981.8843 | 740028.323 | 742785.792 | 746131.436 | 749971.1237 | 754231.0994 | 758852.4937 | 763787.5835 | 768997.1671 | 774448.6737 | 779870.7883 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 0 | -37211.4085 | -33803.062 | -27998.4364 | -20100.888 | -14148.8741 | -12722.2991 | -11277.5585 | -9814.6393 | -8333.5266 | -6834.2037 | 61592.417 | 63128.2168 | 64682.2868 | 66254.6502 | 67845.3318 | 69454.358 | 71081.7566 | 72727.5569 | 74357.0386 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 181235.181 |  | 0 | 0 | 0 | 0 | 0 | -37211.4085 | -33803.062 | -27998.4364 | -20100.888 | -14148.8741 | -12722.2991 | -11277.5585 | -9814.6393 | -8333.5266 | -6834.2037 | 61592.417 | 63128.2168 | 64682.2868 | 66254.6502 | 67845.3318 | 69454.358 | 71081.7566 | 72727.5569 | 74357.0386 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 131901.9161 |  | 0 | 0 | 0 | 0 | 0 | -43902.3154 | -40493.9689 | -34689.3434 | -26791.795 | -20839.781 | -19413.206 | -17968.4654 | -16505.5462 | -15024.4335 | -13525.1107 | 61592.417 | 63128.2168 | 64682.2868 | 66254.6502 | 67845.3318 | 69454.358 | 71081.7566 | 72727.5569 | 74357.0386 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 230568.4458 |  | 0 | 0 | 0 | 0 | 0 | -30520.5015 | -27112.155 | -21307.5295 | -13409.9811 | -7457.9671 | -6031.3921 | -4586.6515 | -3123.7323 | -1642.6196 | -143.2968 | 61592.417 | 63128.2168 | 64682.2868 | 66254.6502 | 67845.3318 | 69454.358 | 71081.7566 | 72727.5569 | 74357.0386 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 248691.9639 |  | 0 | 0 | 0 | 0 | 0 | -34241.6423 | -30492.4612 | -24107.3731 | -15420.0699 | -8872.8546 | -7303.622 | -5714.4074 | -4105.1963 | -2475.9723 | -826.7172 | 67751.6587 | 69441.0385 | 71150.5155 | 72880.1152 | 74629.865 | 76399.7938 | 78189.9323 | 80000.3126 | 81792.7425 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | 113778.398 |  | 0 | 0 | 0 | 0 | 0 | -40181.1746 | -37113.6627 | -31889.4997 | -24781.7062 | -19424.8936 | -18140.9761 | -16840.7096 | -15524.0823 | -14191.0809 | -12841.6903 | 55433.1753 | 56815.3951 | 58214.0581 | 59629.1852 | 61060.7986 | 62508.9222 | 63973.5809 | 65454.8012 | 66921.3348 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | 64445.1332 |  | 0 | 0 | 0 | 0 | 0 | -46872.0815 | -43804.5697 | -38580.4067 | -31472.6131 | -26115.8006 | -24831.8831 | -23531.6165 | -22214.9892 | -20881.9878 | -19532.5973 | 55433.1753 | 56815.3951 | 58214.0581 | 59629.1852 | 61060.7986 | 62508.9222 | 63973.5809 | 65454.8012 | 66921.3348 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 181235.181 |  | 0 | 0 | 0 | 0 | 0 | -37211.4085 | -33803.062 | -27998.4364 | -20100.888 | -14148.8741 | -12722.2991 | -11277.5585 | -9814.6393 | -8333.5266 | -6834.2037 | 61592.417 | 63128.2168 | 64682.2868 | 66254.6502 | 67845.3318 | 69454.358 | 71081.7566 | 72727.5569 | 74357.0386 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 181235.181 |  | 0 | 0 | 0 | 0 | 0 | -37211.4085 | -33803.062 | -27998.4364 | -20100.888 | -14148.8741 | -12722.2991 | -11277.5585 | -9814.6393 | -8333.5266 | -6834.2037 | 61592.417 | 63128.2168 | 64682.2868 | 66254.6502 | 67845.3318 | 69454.358 | 71081.7566 | 72727.5569 | 74357.0386 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 181235.181 |  | 0 | 0 | 0 | 0 | 0 | -37211.4085 | -33803.062 | -27998.4364 | -20100.888 | -14148.8741 | -12722.2991 | -11277.5585 | -9814.6393 | -8333.5266 | -6834.2037 | 61592.417 | 63128.2168 | 64682.2868 | 66254.6502 | 67845.3318 | 69454.358 | 71081.7566 | 72727.5569 | 74357.0386 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 1 | 1 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 7.8779 | 0.18124 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens1 | Capex 10% higher | 0 | 7.5715 | 0.1319 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens2 | Capex 10% lower | 0 | 8.1843 | 0.23057 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens3 | Total benefits 10% higher | 0 | 8.9721 | 0.24869 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens4 | Total benefits 10% lower | 0 | 6.7837 | 0.11378 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 6.4773 | 0.064445 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Workings_costs
CitiPower
VM transformer replacement
WORKINGS - COSTS
Option 1 - continue existing maintenance with no proactive replacement cost
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
Relay annual maintenance cost ($)
|  | Total opex cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - Replace #1 transformer completed in 2030-31
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | Tx capex profile ($) | 2029-30: 1858359.5333; 2030-31: 3716719.0667
|  | Total capex ($) | 0 | 0 | 0 | 1858359.5333 | 3716719.0667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
SWBD online monitoring annual cost ($)
|  | Total opex cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Refurbish #1 transformer completed in 2029-30
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | Tx capex profile ($) | 2029-30: 500000
|  | Total capex ($) | 0 | 0 | 0 | 500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
SWBD online monitoring annual cost ($)
|  | Total opex cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Workings_risks
CitiPower
VM transformer replacement
WORKINGS - RISKS
Option 1 - continue existing maintenance with no proactive replacement cost
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Transformer risks
|  | Energy at Risk ($, Weighted) | 314043.2114 | 366725.751 | 435144.5083 | 513527.9984 | 576691.9911 | 648806.7666 | 774247.6929 | 946170.4447 | 1075915.541 | 1105431.7594 | 1135299.9251 | 1165519.6523 | 1196090.5882 | 1227012.4118 | 1258284.8332 | 1289907.5928 | 1321880.4603 | 1354203.2342 | 1386875.7408 | 1419897.8336 | 1453269.3926 | 1486990.3239 | 1521060.5586 | 1555480.0525 | 1590248.7857
|  | Safety risk | 703.1232 | 724.2438 | 745.623 | 767.2593 | 789.1514 | 811.2981 | 833.6981 | 856.3502 | 879.2531 | 902.4057 | 925.8069 | 949.4554 | 973.3502 | 997.4903 | 1021.8744 | 1046.5017 | 1071.371 | 1096.4814 | 1121.8318 | 1147.4212 | 1173.2488 | 1199.3136 | 1199.3136 | 1199.3136 | 1199.3136
|  | Unplanned replacement risk | 26504.4365 | 27300.5861 | 28106.4797 | 28922.0666 | 29747.2974 | 30582.1237 | 31426.4982 | 32280.3745 | 33143.7072 | 34016.4519 | 34898.5651 | 35790.0041 | 36690.727 | 37600.6927 | 38519.8612 | 39448.1927 | 40385.6486 | 41332.1907 | 42287.7817 | 43252.3848 | 44225.964 | 45208.4837 | 45208.4837 | 45208.4837 | 45208.4837
|  | Unplanned fault risk | 2644.8598 | 2724.3071 | 2804.7267 | 2886.1135 | 2968.4627 | 3051.7695 | 3136.0291 | 3221.2368 | 3307.3882 | 3394.4788 | 3482.5043 | 3571.4604 | 3661.3429 | 3752.1478 | 3843.871 | 3936.5085 | 4030.0566 | 4124.5114 | 4219.8692 | 4316.1263 | 4413.2791 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241
|  | Enviromental risk | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75
|  | Noise cost | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
|  | Total transformer risks | 398184.3808 | 451763.638 | 521090.0876 | 600392.1878 | 664485.6527 | 737540.708 | 863932.6682 | 1036817.1562 | 1167534.6395 | 1198033.8459 | 1228895.5514 | 1260119.3222 | 1291704.7583 | 1323651.4926 | 1355959.1897 | 1388627.5457 | 1421656.2865 | 1455045.1677 | 1488793.9734 | 1522902.5159 | 1557370.6346 | 1592198.1954 | 1626268.4301 | 1660687.924 | 1695456.6571
Option 2 - Replace #1 transformer completed in 2030-31
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Transformer risks
|  | Energy at Risk ($, Weighted) | 314043.2114 | 366725.751 | 435144.5083 | 513527.9984 | 576691.9911 | 59031.5183 | 103711.6386 | 158627.1832 | 210911.8415 | 243669.5959 | 275020.296 | 305426.9396 | 335188.7206 | 364511.3519 | 393542.8668 | 422393.5785 | 451147.9961 | 479872.3295 | 508619.4251 | 537432.1278 | 566345.6416 | 595389.2286 | 624587.4596 | 653961.1508 | 683528.0795
|  | Safety risk | 703.1232 | 724.2438 | 745.623 | 767.2593 | 789.1514 | 589.6847 | 605.7326 | 622.1837 | 639.0089 | 656.1899 | 673.7134 | 691.5691 | 709.7485 | 728.2447 | 747.0515 | 766.1635 | 785.5761 | 805.285 | 825.2862 | 845.5761 | 866.1516 | 887.0094 | 887.0094 | 887.0094 | 887.0094
|  | Unplanned replacement risk | 26504.4365 | 27300.5861 | 28106.4797 | 28922.0666 | 29747.2974 | 22228.3411 | 22833.2701 | 23453.3979 | 24087.6298 | 24735.2729 | 25395.8266 | 26068.9019 | 26754.1819 | 27451.4002 | 28160.3276 | 28880.7626 | 29612.5261 | 30355.4566 | 31109.4073 | 31874.2437 | 32649.8413 | 33436.0847 | 33436.0847 | 33436.0847 | 33436.0847
|  | Unplanned fault risk | 2644.8598 | 2724.3071 | 2804.7267 | 2886.1135 | 2968.4627 | 2218.1512 | 2278.5166 | 2340.3988 | 2403.6883 | 2468.3162 | 2534.2324 | 2601.3981 | 2669.7818 | 2739.3567 | 2810.1001 | 2881.9918 | 2955.014 | 3029.1505 | 3104.3868 | 3180.7093 | 3258.1056 | 3336.5643 | 3336.5643 | 3336.5643 | 3336.5643
|  | Enviromental risk | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5
|  | Noise cost | 50000 | 50000 | 50000 | 50000 | 50000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000
|  | Total transformer risks | 398184.3808 | 451763.638 | 521090.0876 | 600392.1878 | 664485.6527 | 109655.1953 | 155016.658 | 210630.6636 | 263629.6685 | 297116.875 | 329211.5684 | 360376.3087 | 390909.9327 | 421017.8535 | 450847.846 | 480509.9965 | 510088.6123 | 539649.7216 | 569246.0054 | 598920.1568 | 628707.2401 | 658636.3871 | 687834.618 | 717208.3093 | 746775.2379
Option 3 - Refurbish #1 transformer completed in 2029-30
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Transformer risks
|  | Energy at Risk ($, Weighted) | 314043.2114 | 366725.751 | 435144.5083 | 513527.9984 | 552672.9018 | 621750.9518 | 742002.3231 | 906855.2676 | 1031279.0303 | 1059540.5427 | 1088138.0036 | 1117071.014 | 1146339.206 | 1175942.2423 | 1205879.8148 | 1236151.6445 | 1266757.4801 | 1297697.0979 | 1328970.3003 | 1360576.9159 | 1392516.7983 | 1424789.8259 | 1457395.901 | 1490334.9492 | 1523606.9193
|  | Safety risk | 703.1232 | 724.2438 | 745.623 | 767.2593 | 784.8505 | 806.861 | 829.1229 | 851.6352 | 874.3967 | 897.4061 | 920.6623 | 944.1643 | 967.9108 | 991.9009 | 1016.1334 | 1040.6073 | 1065.3216 | 1090.2753 | 1115.4674 | 1140.897 | 1166.563 | 1192.4646 | 1192.4646 | 1192.4646 | 1192.4646
|  | Unplanned replacement risk | 26504.4365 | 27300.5861 | 28106.4797 | 28922.0666 | 28936.6837 | 29745.8256 | 30564.1866 | 31391.7222 | 32228.3888 | 33074.1437 | 33928.9448 | 34792.7512 | 35665.5226 | 36547.2195 | 37437.8032 | 38337.2356 | 39245.4794 | 40162.4981 | 41088.2555 | 42022.7163 | 42965.8459 | 43917.61 | 43917.61 | 43917.61 | 43917.61
|  | Unplanned fault risk | 2644.8598 | 2724.3071 | 2804.7267 | 2886.1135 | 2968.4627 | 3051.7695 | 3136.0291 | 3221.2368 | 3307.3882 | 3394.4788 | 3482.5043 | 3571.4604 | 3661.3429 | 3752.1478 | 3843.871 | 3936.5085 | 4030.0566 | 4124.5114 | 4219.8692 | 4316.1263 | 4413.2791 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241
|  | Enviromental risk | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125
|  | Noise cost | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
|  | Total transformer risks | 398184.3808 | 451763.638 | 521090.0876 | 600392.1878 | 637801.0238 | 707793.5328 | 828969.7867 | 994757.9868 | 1120127.329 | 1149344.6962 | 1178908.24 | 1208817.5148 | 1239072.1073 | 1269671.6354 | 1300615.7473 | 1331904.1209 | 1363536.4628 | 1395512.5077 | 1427832.0174 | 1460494.7805 | 1493500.6113 | 1526849.3496 | 1559455.4247 | 1592394.4729 | 1625666.443

## Tx risks
CitiPower
VM transformer replacement
Input Data - Station Configuration |  | Constants |  |  | POF METHOD | WEIBULL | Modifier (x) | Comment
Substation: | VM | Major Failure CoC |  |  | PoF (#1) | 0.1409% | 100%
Asset Type | Transformer | Minor Failure CoC |  |  | PoF (#2) | 0.1409% | 100%
VCR | 52.307 | Major Failure CoC - used | 6690094.32 |  | PoF (#3) | 0.1027% | 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 166900 |  | PoF (#4) | 0% | 100%
Scenario #1: VM - Transformer | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 0% | 0 | Energy | 3121.1657 | 4470.4842 | 5178.0514 | 6101.7281 | 7142.8805 | 8077.9021 | 9122.1485 | 10884.5326 | 13572.3912 | 15425.591 | 15850.4329 | 16280.41 | 16715.5188 | 17155.7564 | 17601.1201 | 18051.6079 | 18507.2181 | 18967.9495 | 19433.8014 | 19904.7734 | 20380.8654 | 20862.078 | 21348.4119 | 21839.8684 | 22336.4489 | 22838.1555 | 23344.9902 | 23856.9559 | 23856.9559 | 23856.9559 | 23856.9559 | 23856.9559
Online Monitoring | 0% | 50000 | Energy | 6139.5444 | 9581.6925 | 11287.9677 | 13492.7985 | 16058.5354 | 17902.0279 | 20061.0634 | 23942.7241 | 28627.0606 | 32571.107 | 33460.7698 | 34360.8786 | 35271.417 | 36192.3697 | 37123.7222 | 38065.4607 | 39017.5727 | 39980.0463 | 40952.8705 | 41936.035 | 42929.5304 | 43933.3481 | 44947.4803 | 45971.9197 | 47006.66 | 48051.6953 | 49107.0206 | 50172.6316 | 50172.6316 | 50172.6316 | 50172.6316 | 50172.6316
Physical Separation | 0% | 300000 | Energy | 3121.1657 | 4470.4842 | 5178.0514 | 6101.7281 | 7142.8805 | 8077.9021 | 9122.1485 | 10884.5326 | 13572.3912 | 15425.591 | 15850.4329 | 16280.41 | 16715.5188 | 17155.7564 | 17601.1201 | 18051.6079 | 18507.2181 | 18967.9495 | 19433.8014 | 19904.7734 | 20380.8654 | 20862.078 | 21348.4119 | 21839.8684 | 22336.4489 | 22838.1555 | 23344.9902 | 23856.9559 | 23856.9559 | 23856.9559 | 23856.9559 | 23856.9559
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.3844% | 0.3962% | 0.4081% | 0.4201% | 0.4323% | 0.4446% | 0.4571% | 0.4697% | 0.4825% | 0.4954% | 0.5085% | 0.5216% | 0.535% | 0.5484% | 0.562% | 0.5758% | 0.5897% | 0.6037% | 0.6178% | 0.6321% | 0.6465% | 0.6611% | 0.6758% | 0.6758% | 0.6758% | 0.6758% | 0.6758% | 0.6758% | 0.6758% | 0.6758% | 0.6758% | 0.6758%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 1.538% | 1.585% | 1.632% | 1.68% | 1.729% | 1.779% | 1.829% | 1.879% | 1.93% | 1.982% | 2.034% | 2.087% | 2.14% | 2.194% | 2.248% | 2.303% | 2.359% | 2.415% | 2.471% | 2.528% | 2.586% | 2.644% | 2.703% | 2.703% | 2.703% | 2.703% | 2.703% | 2.703% | 2.703% | 2.703% | 2.703% | 2.703%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 210623.5135 | 314043.2114 | 366725.751 | 435144.5083 | 513527.9984 | 576691.9911 | 648806.7666 | 774247.6929 | 946170.4447 | 1075915.541 | 1105431.7594 | 1135299.9251 | 1165519.6523 | 1196090.5882 | 1227012.4118 | 1258284.8332 | 1289907.5928 | 1321880.4603 | 1354203.2342 | 1386875.7408 | 1419897.8336 | 1453269.3926 | 1486990.3239 | 1521060.5586 | 1555480.0525 | 1590248.7857 | 1625366.7614 | 1660834.0063 | 1660834.0063 | 1660834.0063 | 1660834.0063 | 1660834.0063
Replace 1 Asset | 0% | 5575078.6 | Safety Risk | 682.2624 | 703.1232 | 724.2438 | 745.623 | 767.2593 | 789.1514 | 811.2981 | 833.6981 | 856.3502 | 879.2531 | 902.4057 | 925.8069 | 949.4554 | 973.3502 | 997.4903 | 1021.8744 | 1046.5017 | 1071.371 | 1096.4814 | 1121.8318 | 1147.4212 | 1173.2488 | 1199.3136 | 1199.3136 | 1199.3136 | 1199.3136 | 1199.3136 | 1199.3136 | 1199.3136 | 1199.3136 | 1199.3136 | 1199.3136
Replace 2 Assets | 0% | 0 | Unplanned Replacement Risk | 25718.0825 | 26504.4365 | 27300.5861 | 28106.4797 | 28922.0666 | 29747.2974 | 30582.1237 | 31426.4982 | 32280.3745 | 33143.7072 | 34016.4519 | 34898.5651 | 35790.0041 | 36690.727 | 37600.6927 | 38519.8612 | 39448.1927 | 40385.6486 | 41332.1907 | 42287.7817 | 43252.3848 | 44225.964 | 45208.4837 | 45208.4837 | 45208.4837 | 45208.4837 | 45208.4837 | 45208.4837 | 45208.4837 | 45208.4837 | 45208.4837 | 45208.4837
Replace 3 Assets | 0% | 0 | Unplanned Fault Risk | 2566.3901 | 2644.8598 | 2724.3071 | 2804.7267 | 2886.1135 | 2968.4627 | 3051.7695 | 3136.0291 | 3221.2368 | 3307.3882 | 3394.4788 | 3482.5043 | 3571.4604 | 3661.3429 | 3752.1478 | 3843.871 | 3936.5085 | 4030.0566 | 4124.5114 | 4219.8692 | 4316.1263 | 4413.2791 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Total Life Cycle Cost | 293878.9985 | 398184.3808 | 451763.638 | 521090.0876 | 600392.1878 | 664485.6527 | 737540.708 | 863932.6682 | 1036817.1562 | 1167534.6395 | 1198033.8459 | 1228895.5514 | 1260119.3222 | 1291704.7583 | 1323651.4926 | 1355959.1897 | 1388627.5457 | 1421656.2865 | 1455045.1677 | 1488793.9734 | 1522902.5159 | 1557370.6346 | 1592198.1954 | 1626268.4301 | 1660687.924 | 1695456.6571 | 1730574.6329 | 1766041.8778 | 1766041.8778 | 1766041.8778 | 1766041.8778 | 1766041.8778
Input Data - Station Configuration |  | Constants |  | PoF (#4) 2026: POF METHOD; 0% 2027: WEIBULL; 100% 2028: Modifier (x); 100% 2029: Comment
Substation: | VM | Major Failure CoC |  | PoF (#4) 2026: PoF (#1); 0% 2027: 0.1409%; 100% 2028: 100%
Asset Type | Transformer | Minor Failure CoC |  | PoF (#4) 2026: PoF (#2); 0% 2027: 0.1409%; 100% 2028: 100%
VCR | 52.307 | Major Failure CoC - used | 6690094.32 | PoF (#4) 2026: PoF (#3); 0% 2027: 0.1027%; 100% 2028: 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 166900 | PoF (#4) 2026: PoF (#4); 0% 2027: 0%; 100% 2028: 100%
Scenario #2: VM - Transformer | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 0% | 0 | Energy | 3100.1606 | 4449.1613 | 5156.4108 | 6079.7701 | 7120.6052 | 8055.3096 | 822.3999 | 1440.6918 | 2245.0571 | 2981.0864 | 3444.7659 | 3888.7406 | 4319.5511 | 4741.4246 | 5157.2681 | 5569.1739 | 5978.7014 | 6387.0456 | 6795.1428 | 7203.7407 | 7613.4456 | 8024.7558 | 8438.0858 | 8853.7837 | 9272.1446 | 9693.4207 | 10117.8291 | 10545.5579 | 10545.5579 | 10545.5579 | 10545.5579 | 10545.5579
Online Monitoring | 0% | 50000 | Energy | 6118.5393 | 9560.3696 | 11266.3272 | 13470.8405 | 16036.2601 | 17879.4353 | 1842.9291 | 3247.5482 | 4870.2621 | 6484.77 | 7490.3829 | 8452.3072 | 9384.7866 | 10297.0242 | 11195.3465 | 12084.3049 | 12967.2908 | 13846.9014 | 14725.171 | 15603.7229 | 16483.8727 | 17366.7011 | 18253.1058 | 19143.8403 | 20039.5425 | 20940.7568 | 21847.9512 | 22761.5303 | 22761.5303 | 22761.5303 | 22761.5303 | 22761.5303
Physical Separation | 0% | 300000 | Energy | 3100.1606 | 4449.1613 | 5156.4108 | 6079.7701 | 7120.6052 | 8055.3096 | 822.3999 | 1440.6918 | 2245.0571 | 2981.0864 | 3444.7659 | 3888.7406 | 4319.5511 | 4741.4246 | 5157.2681 | 5569.1739 | 5978.7014 | 6387.0456 | 6795.1428 | 7203.7407 | 7613.4456 | 8024.7558 | 8438.0858 | 8853.7837 | 9272.1446 | 9693.4207 | 10117.8291 | 10545.5579 | 10545.5579 | 10545.5579 | 10545.5579 | 10545.5579
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.3844% | 0.3962% | 0.4081% | 0.4201% | 0.4323% | 0.4446% | 0.3323% | 0.3413% | 0.3506% | 0.36% | 0.3697% | 0.3796% | 0.3897% | 0.3999% | 0.4103% | 0.4209% | 0.4317% | 0.4426% | 0.4537% | 0.465% | 0.4764% | 0.488% | 0.4998% | 0.4998% | 0.4998% | 0.4998% | 0.4998% | 0.4998% | 0.4998% | 0.4998% | 0.4998% | 0.4998%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 1.538% | 1.585% | 1.632% | 1.68% | 1.729% | 1.779% | 1.329% | 1.365% | 1.402% | 1.44% | 1.479% | 1.518% | 1.559% | 1.6% | 1.641% | 1.684% | 1.727% | 1.771% | 1.815% | 1.86% | 1.906% | 1.952% | 1.999% | 1.999% | 1.999% | 1.999% | 1.999% | 1.999% | 1.999% | 1.999% | 1.999% | 1.999%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 209524.8 | 312927.8723 | 365593.7982 | 433995.9509 | 512362.8426 | 575510.2407 | 59031.5183 | 103711.6386 | 158627.1832 | 210911.8415 | 243669.5959 | 275020.296 | 305426.9396 | 335188.7206 | 364511.3519 | 393542.8668 | 422393.5785 | 451147.9961 | 479872.3295 | 508619.4251 | 537432.1278 | 566345.6416 | 595389.2286 | 624587.4596 | 653961.1508 | 683528.0795 | 713303.5364 | 743300.7597 | 743300.7597 | 743300.7597 | 743300.7597 | 743300.7597
Replace 1 Asset | 100% | 5575078.6 | Safety Risk | 682.2624 | 703.1232 | 724.2438 | 745.623 | 767.2593 | 789.1514 | 589.6847 | 605.7326 | 622.1837 | 639.0089 | 656.1899 | 673.7134 | 691.5691 | 709.7485 | 728.2447 | 747.0515 | 766.1635 | 785.5761 | 805.285 | 825.2862 | 845.5761 | 866.1516 | 887.0094 | 887.0094 | 887.0094 | 887.0094 | 887.0094 | 887.0094 | 887.0094 | 887.0094 | 887.0094 | 887.0094
Replace 2 Assets | 0% | 0 | Unplanned Replacement Risk | 25718.0825 | 26504.4365 | 27300.5861 | 28106.4797 | 28922.0666 | 29747.2974 | 22228.3411 | 22833.2701 | 23453.3979 | 24087.6298 | 24735.2729 | 25395.8266 | 26068.9019 | 26754.1819 | 27451.4002 | 28160.3276 | 28880.7626 | 29612.5261 | 30355.4566 | 31109.4073 | 31874.2437 | 32649.8413 | 33436.0847 | 33436.0847 | 33436.0847 | 33436.0847 | 33436.0847 | 33436.0847 | 33436.0847 | 33436.0847 | 33436.0847 | 33436.0847
Replace 3 Assets | 0% | 0 | Unplanned Fault Risk | 2566.3901 | 2644.8598 | 2724.3071 | 2804.7267 | 2886.1135 | 2968.4627 | 2218.1512 | 2278.5166 | 2340.3988 | 2403.6883 | 2468.3162 | 2534.2324 | 2601.3981 | 2669.7818 | 2739.3567 | 2810.1001 | 2881.9918 | 2955.014 | 3029.1505 | 3104.3868 | 3180.7093 | 3258.1056 | 3336.5643 | 3336.5643 | 3336.5643 | 3336.5643 | 3336.5643 | 3336.5643 | 3336.5643 | 3336.5643 | 3336.5643 | 3336.5643
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 4288.75 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5 | 587.5
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 0 | 0 | 0 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818 | 237686.2818
|  |  | Total Life Cycle Cost | 267780.2849 | 372069.0418 | 425631.6853 | 494941.5302 | 574227.032 | 638303.9023 | 347341.4771 | 392702.9398 | 448316.9454 | 501315.9503 | 534803.1568 | 566897.8503 | 598062.5905 | 628596.2145 | 658704.1354 | 688534.1278 | 718196.2783 | 747774.8941 | 777336.0035 | 806932.2872 | 836606.4387 | 866393.5219 | 896322.6689 | 925520.8999 | 954894.5911 | 984461.5198 | 1014236.9767 | 1044234.2 | 1044234.2 | 1044234.2 | 1044234.2 | 1044234.2
Input Data - Station Configuration |  | Constants |  | PoF (#4) 2026: POF METHOD; 0% 2027: WEIBULL; 100% 2028: Modifier (x); 100% 2029: Comment
Substation: | VM | Major Failure CoC |  | PoF (#4) 2026: PoF (#1); 0% 2027: 0.1409%; 100% 2028: 100%
Asset Type | Transformer | Minor Failure CoC |  | PoF (#4) 2026: PoF (#2); 0% 2027: 0.1409%; 100% 2028: 100%
VCR | 52.307 | Major Failure CoC - used | 6690094.32 | PoF (#4) 2026: PoF (#3); 0% 2027: 0.09245%; 100% 2028: 90%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 166900 | PoF (#4) 2026: PoF (#4); 0% 2027: 0%; 100% 2028: 100%
Scenario #3: VM - Transformer | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 0% | 0 | Energy | 2997.388 | 4290.7166 | 4967.9822 | 5851.9685 | 6847.5033 | 7741.3634 | 8739.9615 | 10426.4791 | 13000.1407 | 14774.9157 | 15181.3624 | 15592.7056 | 16008.9414 | 16430.0665 | 16856.078 | 17286.9734 | 17722.7506 | 18163.408 | 18608.9443 | 19059.3587 | 19514.6507 | 19974.8203 | 20439.8677 | 20909.7935 | 21384.5987 | 21864.2846 | 22348.8529 | 22838.3056 | 22838.3056 | 22838.3056 | 22838.3056 | 22838.3056
Online Monitoring | 0% | 50000 | Energy | 5887.0894 | 9180.1838 | 10814.2693 | 12926.7273 | 15387.7525 | 17156.6365 | 19228.665 | 22956.6364 | 27456.8998 | 31244.8283 | 32097.4552 | 32960.0658 | 33832.6435 | 34715.1728 | 35607.6389 | 36510.0281 | 37422.3274 | 38344.5245 | 39276.6082 | 40218.5677 | 41170.3934 | 42132.076 | 43103.6072 | 44084.9793 | 45076.1852 | 46077.2187 | 47088.074 | 48108.7461 | 48108.7461 | 48108.7461 | 48108.7461 | 48108.7461
Physical Separation | 0% | 300000 | Energy | 2997.388 | 4290.7166 | 4967.9822 | 5851.9685 | 6847.5033 | 7741.3634 | 8739.9615 | 10426.4791 | 13000.1407 | 14774.9157 | 15181.3624 | 15592.7056 | 16008.9414 | 16430.0665 | 16856.078 | 17286.9734 | 17722.7506 | 18163.408 | 18608.9443 | 19059.3587 | 19514.6507 | 19974.8203 | 20439.8677 | 20909.7935 | 21384.5987 | 21864.2846 | 22348.8529 | 22838.3056 | 22838.3056 | 22838.3056 | 22838.3056 | 22838.3056
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.3741% | 0.3855% | 0.3971% | 0.4088% | 0.4206% | 0.4325% | 0.4446% | 0.4569% | 0.4692% | 0.4817% | 0.4944% | 0.5072% | 0.5201% | 0.5331% | 0.5463% | 0.5596% | 0.573% | 0.5866% | 0.6003% | 0.6142% | 0.6281% | 0.6422% | 0.6565% | 0.6565% | 0.6565% | 0.6565% | 0.6565% | 0.6565% | 0.6565% | 0.6565% | 0.6565% | 0.6565%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 1.538% | 1.585% | 1.632% | 1.68% | 1.729% | 1.779% | 1.829% | 1.879% | 1.93% | 1.982% | 2.034% | 2.087% | 2.14% | 2.194% | 2.248% | 2.303% | 2.359% | 2.415% | 2.471% | 2.528% | 2.586% | 2.644% | 2.703% | 2.703% | 2.703% | 2.703% | 2.703% | 2.703% | 2.703% | 2.703% | 2.703% | 2.703%
Bunded | 0 | 300000
Refurbish Assets | 1 | 500000 | Energy at Risk ($, Weighted) | 202129.8574 | 301160.5214 | 351600.7665 | 417116.7387 | 492186.7972 | 552672.9018 | 621750.9518 | 742002.3231 | 906855.2676 | 1031279.0303 | 1059540.5427 | 1088138.0036 | 1117071.014 | 1146339.206 | 1175942.2423 | 1205879.8148 | 1236151.6445 | 1266757.4801 | 1297697.0979 | 1328970.3003 | 1360576.9159 | 1392516.7983 | 1424789.8259 | 1457395.901 | 1490334.9492 | 1523606.9193 | 1557211.7821 | 1591149.5306 | 1591149.5306 | 1591149.5306 | 1591149.5306 | 1591149.5306
Replace 1 Asset | 0% | 5575078.6 | Safety Risk | 678.6163 | 699.3497 | 720.3412 | 741.5894 | 763.0929 | 784.8505 | 806.861 | 829.1229 | 851.6352 | 874.3967 | 897.4061 | 920.6623 | 944.1643 | 967.9108 | 991.9009 | 1016.1334 | 1040.6073 | 1065.3216 | 1090.2753 | 1115.4674 | 1140.897 | 1166.563 | 1192.4646 | 1192.4646 | 1192.4646 | 1192.4646 | 1192.4646 | 1192.4646 | 1192.4646 | 1192.4646 | 1192.4646 | 1192.4646
Replace 2 Assets | 0% | 0 | Unplanned Replacement Risk | 25030.8908 | 25793.2334 | 26565.0333 | 27346.2405 | 28136.8065 | 28936.6837 | 29745.8256 | 30564.1866 | 31391.7222 | 32228.3888 | 33074.1437 | 33928.9448 | 34792.7512 | 35665.5226 | 36547.2195 | 37437.8032 | 38337.2356 | 39245.4794 | 40162.4981 | 41088.2555 | 42022.7163 | 42965.8459 | 43917.61 | 43917.61 | 43917.61 | 43917.61 | 43917.61 | 43917.61 | 43917.61 | 43917.61 | 43917.61 | 43917.61
Replace 3 Assets | 0% | 0 | Unplanned Fault Risk | 2566.3901 | 2644.8598 | 2724.3071 | 2804.7267 | 2886.1135 | 2968.4627 | 3051.7695 | 3136.0291 | 3221.2368 | 3307.3882 | 3394.4788 | 3482.5043 | 3571.4604 | 3661.3429 | 3752.1478 | 3843.871 | 3936.5085 | 4030.0566 | 4124.5114 | 4219.8692 | 4316.1263 | 4413.2791 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241 | 4511.3241
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125 | 2438.125
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 0 | 0 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839
|  |  | Total Life Cycle Cost | 282843.8796 | 382736.0894 | 434048.573 | 500447.4202 | 576410.9351 | 697921.7077 | 767914.2167 | 889090.4706 | 1054878.6708 | 1180248.013 | 1209465.3802 | 1239028.9239 | 1268938.1988 | 1299192.7913 | 1329792.3193 | 1360736.4312 | 1392024.8048 | 1423657.1467 | 1455633.1916 | 1487952.7013 | 1520615.4644 | 1553621.2953 | 1586970.0335 | 1619576.1086 | 1652515.1569 | 1685787.1269 | 1719391.9898 | 1753329.7382 | 1753329.7382 | 1753329.7382 | 1753329.7382 | 1753329.7382

## Misc_calcs
CitiPower
VM transformer replacement
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 4 | TRUE
| Option 3 | 4 | TRUE
| Option 4 | Not used | FALSE
| Option 5 | Not used | FALSE
| First year | 4
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
CitiPower
VM transformer replacement
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | TRUE | Not used |  | TRUE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
CitiPower
| Reliability in worst-served areas | per MWh | 0
| Network resilience | per MWh | 0
| Enabling solar exports | per MWh | 4220.9954
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.54769
| Customer value of time - business | per minute customer time | 0.54769
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020