## Cover
CitiPower
Regulatory proposal 2026-31
VM switchboard and relay
| Model number: | 4.05
2025-01-31
15

## Summary
CitiPower
VM switchboard and relay replacement
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | SWBD and relay replacement in 2030-31 |  | -8.9386 | 22.7663 | 13.8277
| Option 3 | Relay replacement in 2030-31 and SWBD replacement in 2035-36 |  | -8.375 | 19.6255 | 11.2505
| Option 4 | 0
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | SWBD and relay replacement in 2030-31 |  | 13.8277
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 0 | 0 | 5.1071 | 5.1071 | 5.1071 |  | 15.3212
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
| Capex and risk ($M, 2026) |  | Value of expected unserved energy ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 13.8277 | 11.2505 |  |  |  | Option 2
| Capex 10% higher |  | 0 | 12.9338 | 10.413 |  |  |  | Option 2
| Capex 10% lower |  | 0 | 14.7215 | 12.088 |  |  |  | Option 2
| Total benefits 10% higher |  | 0 | 16.1043 | 13.2131 |  |  |  | Option 2
| Total benefits 10% lower |  | 0 | 11.551 | 9.288 |  |  |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  | 0 | 10.6572 | 8.4505 |  |  |  | Option 2
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
CitiPower
VM switchboard and relay replacement
Project
|  | Business: |  | CitiPower
|  | Descripton: |  | VM switchboard and relay replacement
|  | Date of cost inputs: |  | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | SWBD and relay replacement in 2030-31
|  | Option 3 |  | Relay replacement in 2030-31 and SWBD replacement in 2035-36
Option 4
Option 5
|  | Compliance project |  | No
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | VM |  | Victoria Market | 52306.6712 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 0 | 2023-12-31 | per MWh
|  | Network resilience |  |  |  | 0 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 4220.9954 | 2023-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
CitiPower
VM switchboard and relay replacement
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 52306.6712 | 2023-12-31 |  | 658317.708 | 708090.0911 | 767612.5051 | 832418.6851 | 888244.0156 | 949558.865 | 1039706.3871 | 1152896.4484 | 1243971.2818 | 1288652.1129 | 1337673.4892 | 1391477.2732 | 1450554.8494 | 1515454.2286 | 1586788.7569 | 1665247.9882 | 1751611.5102 | 1846766.8687 | 1950179.1851 | 2063483.4042 | 2187921.6504 | 2324738.1455 | 2475197.9336 | 2640755.604 | 2822991.4674
| Safety risk | (after DF) |  | 2023-12-31 |  | 3713.0877 | 3939.5466 | 4254.8708 | 4764.0818 | 5415.9615 | 6262.8159 | 7353.8932 | 8794.2426 | 10713.2549 | 13294.8764 | 16811.0754 | 21652.7239 | 28383.0189 | 37815.2865 | 51126.4285 | 70022.5284 | 96980.864 | 135603.9718 | 149534.9206 | 159711.212 | 168635.4894 | 170966.215 | 172468.5328 | 174122.9989 | 175945.7015
| Unplanned replacement |  |  | 2023-12-31 |  | 92461.413 | 98535.8036 | 105314.866 | 113047.555 | 121679.3642 | 131362.414 | 142262.8983 | 154648.9833 | 168837.0309 | 185249.8412 | 204478.3255 | 227337.9094 | 254966.1168 | 288964.4414 | 331604.9649 | 386131.7524 | 457201.1358 | 551525.7705 | 601895.1507 | 646993.5996 | 691617.3115 | 731351.049 | 774000.8022 | 820897.8664 | 872475.2638
| Unplanned fault | (after DF) |  | 2023-12-31 |  | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7
| Environmental risk |  |  | 2023-12-31 |  | 299.6999 | 317.2015 | 345.8159 | 400.1835 | 472.984 | 571.422 | 702.2538 | 880.0802 | 1122.9116 | 1456.4228 | 1918.6664 | 2564.4213 | 3472.7174 | 4757.7956 | 6585.0891 | 9194.5548 | 12934.7698 | 18312.8168 | 20205.188 | 21561.4847 | 22733.6315 | 22967.7681 | 23075.5868 | 23194.2406 | 23324.8606
| Other risk |  |  | 2023-12-31 |  | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001
| Total risk cost |  |  |  |  | 805440.6086 | 861531.3428 | 928176.7578 | 1001279.2054 | 1066461.0253 | 1138404.2169 | 1240674.1323 | 1367868.4544 | 1475293.1792 | 1539301.9532 | 1611530.2565 | 1693681.0278 | 1788025.4027 | 1897640.452 | 2026753.9395 | 2181245.5238 | 2369376.9798 | 2602858.1278 | 2772463.1444 | 2942398.4004 | 3121556.7829 | 3300671.8776 | 3495391.5554 | 3709619.4099 | 3945385.9933
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
CitiPower
VM switchboard and relay replacement
OPTION 2 | SWBD and relay replacement in 2030-31
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Switchboard |  | 50 | 2023-12-31 | 0 | 0 | 2753359.964 | 2753359.964 | 2753359.964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Relays |  | 25 | 2023-12-31 | 0 | 0 | 1835573.3094 | 1835573.3094 | 1835573.3094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 4588933.2734 | 4588933.2734 | 4588933.2734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 52306.6712 | 2023-12-31 | 658317.708 | 708090.0911 | 767612.5051 | 832418.6851 | 888244.0156 | 67387.2764 | 73915.3175 | 82740.5604 | 88587.0785 | 88593.8136 | 88603.1998 | 88616.3398 | 88634.8036 | 88661.4798 | 88699.6392 | 88753.9778 | 88831.606 | 88942.8316 | 89102.6204 | 89332.7337 | 89664.8577 | 90145.1923 | 90883.0802 | 91976.2235 | 92361.1221
| Safety risk | (after DF) |  | 2023-12-31 | 3713.0877 | 3939.5466 | 4254.8708 | 4764.0818 | 5415.9615 | 1726.7071 | 1726.7071 | 1726.7071 | 1791.5269 | 2023.0967 | 2352.7656 | 2820.0103 | 3475.956 | 4417.4179 | 5759.801 | 7668.7823 | 10392.2131 | 14288.8204 | 19878.5801 | 27916.2481 | 39498.804 | 56222.6069 | 80601.4592 | 116023.9113 | 126219.1383
| Unplanned replacement |  |  | 2023-12-31 | 92461.413 | 98535.8036 | 105314.866 | 113047.555 | 121679.3642 | 5121.83 | 5121.83 | 5121.83 | 5242.084 | 5671.6928 | 6283.2559 | 7150.0018 | 8366.7943 | 10113.2767 | 12603.5327 | 16144.9029 | 21197.1925 | 28425.9043 | 38795.693 | 53706.7853 | 75194.3196 | 106219.9182 | 151290.0279 | 216694.681 | 235182.53
| Unplanned fault | (after DF) |  | 2023-12-31 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
| Environmental risk |  |  | 2023-12-31 | 299.6999 | 317.2015 | 345.8159 | 400.1835 | 472.984 | 235.7187 | 235.7187 | 235.7187 | 244.8524 | 277.4824 | 323.9357 | 389.7748 | 482.2036 | 614.864 | 804.0174 | 1073.0093 | 1456.764 | 2005.8291 | 2793.4732 | 3926.0476 | 5558.1252 | 7914.6453 | 11349.805 | 16341.0766 | 17777.6132
| Other risk |  |  | 2023-12-31 | 50001 | 50001 | 50001 | 50001 | 50001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 805440.6086 | 861531.3428 | 928176.7578 | 1001279.2054 | 1066461.0253 | 74547.7322 | 81075.7733 | 89901.0162 | 95941.7418 | 96642.2856 | 97639.357 | 99052.3267 | 101035.9576 | 103883.2384 | 107943.1903 | 113716.8724 | 121953.9757 | 133739.5853 | 150646.5667 | 174958.0147 | 209992.3064 | 260578.5626 | 334200.5723 | 441112.0925 | 471616.6036
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - residential | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - business | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex saving |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 1063856.4847 | 1159598.359 | 1277967.4382 | 1379351.4374 | 1442659.6677 | 1513890.8995 | 1594628.7011 | 1686989.445 | 1793757.2136 | 1918810.7491 | 2067528.6514 | 2247423.0041 | 2469118.5425 | 2621816.5776 | 2767440.3857 | 2911564.4765 | 3040093.3149 | 3161190.9831 | 3268507.3174 | 3473769.3897
Capital expenditure
| Switchboard |  |  | 2023-12-31 | 0 | 0 | -2753359.964 | -2753359.964 | -2753359.964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Relays |  |  | 2023-12-31 | 0 | 0 | -1835573.3094 | -1835573.3094 | -1835573.3094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Switchboard |  |  | 2023-12-31 | 0 | 0 | -2753359.964 | -5506719.9281 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921 | -8260079.8921
| Relays |  |  | 2023-12-31 | 0 | 0 | -1835573.3094 | -3671146.6187 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Switchboard |  |  | 2023-12-31 | 0 | 0 | 0 | -117385.949 | -234771.8981 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471 | -352157.8471
| Annualised capex - Relays |  |  | 2023-12-31 | 0 | 0 | 0 | -111371.64 | -222743.2799 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | -228757.589 | -457515.178 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | -228757.589 | -457515.178 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 1063856.4847 | 1159598.359 | 1277967.4382 | 1379351.4374 | 1442659.6677 | 1513890.8995 | 1594628.7011 | 1686989.445 | 1793757.2136 | 1918810.7491 | 2067528.6514 | 2247423.0041 | 2469118.5425 | 2621816.5776 | 2767440.3857 | 2911564.4765 | 3040093.3149 | 3161190.9831 | 3268507.3174 | 3473769.3897
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | -228757.589 | -457515.178 | 427583.7176 | 523325.592 | 641694.6712 | 743078.6703 | 806386.9006 | 877618.1324 | 958355.9341 | 1050716.678 | 1157484.4466 | 1282537.9821 | 1431255.8844 | 1611150.237 | 1832845.7754 | 1985543.8106 | 2131167.6187 | 2275291.7094 | 2403820.5479 | 2524918.2161 | 2632234.5504 | 2837496.6227
| First capex year |  |  | 3
| First year |  |  | 3
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | 0 | 0 | -228757.589 | -457515.178 | 427583.7176 | 523325.592 | 641694.6712 | 743078.6703 | 806386.9006 | 877618.1324 | 958355.9341 | 1050716.678 | 1157484.4466 | 1282537.9821 | 1431255.8844 | 1611150.237 | 1832845.7754 | 1985543.8106 | 2131167.6187 | 2275291.7094 | 2403820.5479 | 2524918.2161 | 2632234.5504 | 2837496.6227
| Total annualised capex |  |  |  | 0 | 0 | 0 | -228757.589 | -457515.178 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767 | -686272.767
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 1113856.4847 | 1209598.359 | 1327967.4382 | 1429351.4374 | 1492659.6677 | 1563890.8995 | 1644628.7011 | 1736989.445 | 1843757.2136 | 1968810.7491 | 2117528.6514 | 2297423.0041 | 2519118.5425 | 2671816.5776 | 2817440.3857 | 2961564.4765 | 3090093.3149 | 3211190.9831 | 3318507.3174 | 3523769.3897
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | 0 | 0 | -251633.3479 | -503266.6958 | 358956.4409 | 454698.3153 | 573067.3945 | 674451.3936 | 737759.6239 | 808990.8557 | 889728.6574 | 982089.4013 | 1088857.1699 | 1213910.7054 | 1362628.6077 | 1542522.9603 | 1764218.4987 | 1916916.5339 | 2062540.342 | 2206664.4327 | 2335193.2712 | 2456290.9394 | 2563607.2737 | 2768869.346
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | 0 | 0 | -205881.8301 | -411763.6602 | 496210.9944 | 591952.8687 | 710321.9479 | 811705.947 | 875014.1773 | 946245.4091 | 1026983.2108 | 1119343.9547 | 1226111.7233 | 1351165.2588 | 1499883.1611 | 1679777.5137 | 1901473.0521 | 2054171.0873 | 2199794.8954 | 2343918.9861 | 2472447.8246 | 2593545.4928 | 2700861.8271 | 2906123.8994
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | 0 | 0 | -228757.589 | -457515.178 | 538969.3661 | 644285.4279 | 774491.415 | 886013.8141 | 955652.8674 | 1034007.2224 | 1122818.8042 | 1224415.6225 | 1341860.168 | 1479419.057 | 1643008.7496 | 1840892.5374 | 2084757.6297 | 2252725.4684 | 2412911.6573 | 2571448.1571 | 2712829.8794 | 2846037.3144 | 2964085.2821 | 3189873.5617
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | 0 | 0 | -228757.589 | -457515.178 | 316198.0692 | 402365.7561 | 508897.9274 | 600143.5266 | 657120.9339 | 721229.0425 | 793893.0639 | 877017.7335 | 973108.7252 | 1085656.9072 | 1219503.0193 | 1381407.9366 | 1580933.9212 | 1718362.1528 | 1849423.5801 | 1979135.2618 | 2094811.2164 | 2203799.1178 | 2300383.8186 | 2485119.6837
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | 0 | 0 | -251633.3479 | -503266.6958 | 247570.7925 | 333738.4794 | 440270.6506 | 531516.2499 | 588493.6572 | 652601.7658 | 725265.7872 | 808390.4568 | 904481.4485 | 1017029.6305 | 1150875.7426 | 1312780.6599 | 1512306.6445 | 1649734.8761 | 1780796.3034 | 1910507.9851 | 2026183.9397 | 2135171.8411 | 2231756.5419 | 2416492.407
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 0 | -228757.589 | -457515.178 | 427583.7176 | 523325.592 | 641694.6712 | 743078.6703 | 806386.9006 | 877618.1324 | 958355.9341 | 1050716.678 | 1157484.4466 | 1282537.9821 | 1431255.8844 | 1611150.237 | 1832845.7754 | 1985543.8106 | 2131167.6187 | 2275291.7094 | 2403820.5479 | 2524918.2161 | 2632234.5504 | 2837496.6227
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 0 | -228757.589 | -457515.178 | 427583.7176 | 523325.592 | 641694.6712 | 743078.6703 | 806386.9006 | 877618.1324 | 958355.9341 | 1050716.678 | 1157484.4466 | 1282537.9821 | 1431255.8844 | 1611150.237 | 1832845.7754 | 1985543.8106 | 2131167.6187 | 2275291.7094 | 2403820.5479 | 2524918.2161 | 2632234.5504 | 2837496.6227
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 0 | -228757.589 | -457515.178 | 427583.7176 | 523325.592 | 641694.6712 | 743078.6703 | 806386.9006 | 877618.1324 | 958355.9341 | 1050716.678 | 1157484.4466 | 1282537.9821 | 1431255.8844 | 1611150.237 | 1832845.7754 | 1985543.8106 | 2131167.6187 | 2275291.7094 | 2403820.5479 | 2524918.2161 | 2632234.5504 | 2837496.6227

## Option3
CitiPower
VM switchboard and relay replacement
OPTION 3 | Relay replacement in 2030-31 and SWBD replacement in 2035-36
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Switchboard |  | 50 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3671146.6187 | 3671146.6187 | 3671146.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Relays |  | 25 | 2023-12-31 | 0 | 0 | 1835573.3094 | 1835573.3094 | 1835573.3094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 1835573.3094 | 1835573.3094 | 1835573.3094 | 0 | 0 | 3671146.6187 | 3671146.6187 | 3671146.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 52306.6712 | 2023-12-31 | 658317.708 | 708090.0911 | 767612.5051 | 832418.6851 | 888244.0156 | 580101.2651 | 636351.2284 | 712385.7439 | 762723.945 | 762730.6802 | 88603.1998 | 88616.3398 | 88634.8036 | 88661.4798 | 88699.6392 | 88753.9778 | 88831.606 | 88942.8316 | 89102.6204 | 89332.7337 | 89664.8577 | 90145.1923 | 90883.0802 | 91976.2235 | 92361.1221
| Safety risk | (after DF) |  | 2023-12-31 | 3713.0877 | 3939.5466 | 4254.8708 | 4764.0818 | 5415.9615 | 2126.0331 | 2126.0331 | 2126.0331 | 2190.8529 | 2422.4227 | 2352.7656 | 2820.0103 | 3475.956 | 4417.4179 | 5759.801 | 7668.7823 | 10392.2131 | 14288.8204 | 19878.5801 | 27916.2481 | 39498.804 | 56222.6069 | 80601.4592 | 116023.9113 | 126219.1383
| Unplanned replacement |  |  | 2023-12-31 | 92461.413 | 98535.8036 | 105314.866 | 113047.555 | 121679.3642 | 26241.3524 | 26241.3524 | 26241.3524 | 26361.6064 | 26791.2153 | 6283.2559 | 7150.0018 | 8366.7943 | 10113.2767 | 12603.5327 | 16144.9029 | 21197.1925 | 28425.9043 | 38795.693 | 53706.7853 | 75194.3196 | 106219.9182 | 151290.0279 | 216694.681 | 235182.53
| Unplanned fault |  |  | 2023-12-31 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
| Environmental risk |  |  | 2023-12-31 | 299.6999 | 317.2015 | 345.8159 | 400.1835 | 472.984 | 235.7187 | 235.7187 | 235.7187 | 244.8524 | 277.4824 | 323.9357 | 389.7748 | 482.2036 | 614.864 | 804.0174 | 1073.0093 | 1456.764 | 2005.8291 | 2793.4732 | 3926.0476 | 5558.1252 | 7914.6453 | 11349.805 | 16341.0766 | 17777.6132
| Other risk |  |  | 2023-12-31 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 805440.6086 | 861531.3428 | 928176.7578 | 1001279.2054 | 1066461.0253 | 659353.0693 | 715603.0326 | 791637.5481 | 842169.9568 | 842870.5006 | 97639.357 | 99052.3267 | 101035.9576 | 103883.2384 | 107943.1903 | 113716.8724 | 121953.9757 | 133739.5853 | 150646.5667 | 174958.0147 | 209992.3064 | 260578.5626 | 334200.5723 | 441112.0925 | 471616.6036
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex saving |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 479051.1476 | 525071.0997 | 576230.9063 | 633123.2224 | 696431.4527 | 1513890.8995 | 1594628.7011 | 1686989.445 | 1793757.2136 | 1918810.7491 | 2067528.6514 | 2247423.0041 | 2469118.5425 | 2621816.5776 | 2767440.3857 | 2911564.4765 | 3040093.3149 | 3161190.9831 | 3268507.3174 | 3473769.3897
Capital expenditure
| Switchboard |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3671146.6187 | -3671146.6187 | -3671146.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Relays |  |  | 2023-12-31 | 0 | 0 | -1835573.3094 | -1835573.3094 | -1835573.3094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Switchboard |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3671146.6187 | -7342293.2374 | -11013439.8562 | -11013439.8562 | -11013439.8562 | -11013439.8562 | -11013439.8562 | -11013439.8562 | -11013439.8562 | -11013439.8562 | -11013439.8562 | -11013439.8562 | -11013439.8562 | -11013439.8562 | -11013439.8562 | -11013439.8562 | -11013439.8562 | -11013439.8562
| Relays |  |  | 2023-12-31 | 0 | 0 | -1835573.3094 | -3671146.6187 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281 | -5506719.9281
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Switchboard |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -156514.5987 | -313029.1974 | -469543.7962 | -469543.7962 | -469543.7962 | -469543.7962 | -469543.7962 | -469543.7962 | -469543.7962 | -469543.7962 | -469543.7962 | -469543.7962 | -469543.7962 | -469543.7962 | -469543.7962 | -469543.7962 | -469543.7962
| Annualised capex - Relays |  |  | 2023-12-31 | 0 | 0 | 0 | -111371.64 | -222743.2799 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199 | -334114.9199
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | -111371.64 | -222743.2799 | -334114.9199 | -334114.9199 | -334114.9199 | -490629.5186 | -647144.1174 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | -111371.64 | -222743.2799 | -334114.9199 | -334114.9199 | -334114.9199 | -490629.5186 | -647144.1174 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 479051.1476 | 525071.0997 | 576230.9063 | 633123.2224 | 696431.4527 | 1513890.8995 | 1594628.7011 | 1686989.445 | 1793757.2136 | 1918810.7491 | 2067528.6514 | 2247423.0041 | 2469118.5425 | 2621816.5776 | 2767440.3857 | 2911564.4765 | 3040093.3149 | 3161190.9831 | 3268507.3174 | 3473769.3897
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | -111371.64 | -222743.2799 | 144936.2277 | 190956.1798 | 242115.9864 | 142493.7038 | 49287.3353 | 760232.1834 | 840969.985 | 933330.729 | 1040098.4976 | 1165152.0331 | 1313869.9354 | 1493764.288 | 1715459.8264 | 1868157.8616 | 2013781.6697 | 2157905.7604 | 2286434.5989 | 2407532.2671 | 2514848.6014 | 2720110.6736
| First capex year |  |  | 3
| First year |  |  | 3
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | 0 | 0 | -111371.64 | -222743.2799 | 144936.2277 | 190956.1798 | 242115.9864 | 142493.7038 | 49287.3353 | 760232.1834 | 840969.985 | 933330.729 | 1040098.4976 | 1165152.0331 | 1313869.9354 | 1493764.288 | 1715459.8264 | 1868157.8616 | 2013781.6697 | 2157905.7604 | 2286434.5989 | 2407532.2671 | 2514848.6014 | 2720110.6736
| Total annualised capex |  |  |  | 0 | 0 | 0 | -111371.64 | -222743.2799 | -334114.9199 | -334114.9199 | -334114.9199 | -490629.5186 | -647144.1174 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161 | -803658.7161
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 479051.1476 | 525071.0997 | 576230.9063 | 633123.2224 | 696431.4527 | 1563890.8995 | 1644628.7011 | 1736989.445 | 1843757.2136 | 1968810.7491 | 2117528.6514 | 2297423.0041 | 2519118.5425 | 2671816.5776 | 2817440.3857 | 2961564.4765 | 3090093.3149 | 3211190.9831 | 3318507.3174 | 3523769.3897
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | 0 | 0 | -122508.804 | -245017.6079 | 111524.7357 | 157544.6878 | 208704.4944 | 93430.7519 | -15427.0764 | 679866.3118 | 760604.1134 | 852964.8574 | 959732.626 | 1084786.1615 | 1233504.0638 | 1413398.4164 | 1635093.9548 | 1787791.99 | 1933415.798 | 2077539.8888 | 2206068.7273 | 2327166.3954 | 2434482.7297 | 2639744.802
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | 0 | 0 | -100234.476 | -200468.9519 | 178347.7197 | 224367.6718 | 275527.4784 | 191556.6556 | 114001.7471 | 840598.055 | 921335.8566 | 1013696.6006 | 1120464.3692 | 1245517.9047 | 1394235.807 | 1574130.1596 | 1795825.698 | 1948523.7332 | 2094147.5413 | 2238271.632 | 2366800.4705 | 2487898.1387 | 2595214.473 | 2800476.5452
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | 0 | 0 | -111371.64 | -222743.2799 | 192841.3424 | 243463.2898 | 299739.077 | 205806.026 | 118930.4806 | 916621.2733 | 1005432.8551 | 1107029.6735 | 1224474.2189 | 1362033.108 | 1525622.8005 | 1723506.5884 | 1967371.6807 | 2135339.5193 | 2295525.7082 | 2454062.2081 | 2595443.9304 | 2728651.3654 | 2846699.3331 | 3072487.6126
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | 0 | 0 | -111371.64 | -222743.2799 | 97031.1129 | 138449.0698 | 184492.8958 | 79181.3815 | -20355.8099 | 603843.0934 | 676507.1149 | 759631.7845 | 855722.7762 | 968270.9582 | 1102117.0702 | 1264021.9876 | 1463547.9722 | 1600976.2038 | 1732037.6311 | 1861749.3128 | 1977425.2674 | 2086413.1687 | 2182997.8696 | 2367733.7347
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | 0 | 0 | -122508.804 | -245017.6079 | 63619.6209 | 105037.5778 | 151081.4038 | 30118.4297 | -85070.2217 | 523477.2218 | 596141.2433 | 679265.9129 | 775356.9046 | 887905.0865 | 1021751.1986 | 1183656.116 | 1383182.1006 | 1520610.3322 | 1651671.7595 | 1781383.4412 | 1897059.3958 | 2006047.2971 | 2102631.998 | 2287367.8631
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | -111371.64 | -222743.2799 | 144936.2277 | 190956.1798 | 242115.9864 | 142493.7038 | 49287.3353 | 760232.1834 | 840969.985 | 933330.729 | 1040098.4976 | 1165152.0331 | 1313869.9354 | 1493764.288 | 1715459.8264 | 1868157.8616 | 2013781.6697 | 2157905.7604 | 2286434.5989 | 2407532.2671 | 2514848.6014 | 2720110.6736
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | -111371.64 | -222743.2799 | 144936.2277 | 190956.1798 | 242115.9864 | 142493.7038 | 49287.3353 | 760232.1834 | 840969.985 | 933330.729 | 1040098.4976 | 1165152.0331 | 1313869.9354 | 1493764.288 | 1715459.8264 | 1868157.8616 | 2013781.6697 | 2157905.7604 | 2286434.5989 | 2407532.2671 | 2514848.6014 | 2720110.6736
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | -111371.64 | -222743.2799 | 144936.2277 | 190956.1798 | 242115.9864 | 142493.7038 | 49287.3353 | 760232.1834 | 840969.985 | 933330.729 | 1040098.4976 | 1165152.0331 | 1313869.9354 | 1493764.288 | 1715459.8264 | 1868157.8616 | 2013781.6697 | 2157905.7604 | 2286434.5989 | 2407532.2671 | 2514848.6014 | 2720110.6736

## Option4
CitiPower
VM switchboard and relay replacement
OPTION 4 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 52306.6712 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option5
CitiPower
VM switchboard and relay replacement
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 52306.6712 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
CitiPower
VM switchboard and relay replacement
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 26052664.8966 | 2026-06-30 |  | 732650.1025 | 788042.4172 | 854285.6645 | 926409.2818 | 988537.9981 | 1056776.0693 | 1157102.3867 | 1283073.0374 | 1384431.3713 | 1434157.2333 | 1488713.7429 | 1548592.6545 | 1614340.8363 | 1686568.176 | 1765957.2748 | 1853275.5455 | 1949390.6013 | 2055290.2031 | 2170379.0779 | 2296476.7762 | 2434965.6741 | 2587230.4817 | 2754679.0827 | 2938930.3078 | 3141742.9048
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 28326359.7226 | 2026-06-30 |  | 896385.0392 | 958809.1266 | 1032979.6518 | 1114336.2903 | 1186877.962 | 1266944.4497 | 1380761.9319 | 1522318.1016 | 1641872.4363 | 1713108.6104 | 1793492.4025 | 1884919.0348 | 1989916.0827 | 2111908.0574 | 2255600.0904 | 2427535.7284 | 2636909.6049 | 2896753.7273 | 3085509.2951 | 3274632.3906 | 3474020.0202 | 3673359.4742 | 3890065.4662 | 4128482.3546 | 4390869.967
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 5090657.0201 | 2026-06-30 |  | 732650.1025 | 788042.4172 | 854285.6645 | 926409.2818 | 988537.9981 | 74996.1521 | 82261.2916 | 92083.0161 | 98589.68 | 98597.1756 | 98607.6216 | 98622.2452 | 98642.7939 | 98672.4821 | 98714.9502 | 98775.4243 | 98861.8177 | 98985.6021 | 99163.4331 | 99419.5291 | 99789.1541 | 100323.7245 | 101144.9293 | 102361.5023 | 102789.8608
Option 2 | Capital expenditure | Option 2Capital expenditure | -13588582.5461 | 2026-06-30 |  | 0 | 0 | -5107081.8735 | -5107081.8735 | -5107081.8735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 6163052.4654 | 2026-06-30 |  | 896385.0392 | 958809.1266 | 1032979.6518 | 1114336.2903 | 1186877.962 | 82965.1139 | 90230.2535 | 100051.9779 | 106774.7778 | 107554.4218 | 108664.0752 | 110236.587 | 112444.195 | 115612.9697 | 120131.3416 | 126556.9454 | 135724.1218 | 148840.4758 | 167656.4693 | 194712.9872 | 233703.0934 | 290001.1777 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -8938649.9902 | 2026-06-30 |  | 0 | 0 | 0 | -254587.2138 | -509174.4275 | -763761.6413 | -763761.6413 | -763761.6413 | -763761.6413 | -763761.6413 | -763761.6413 | -763761.6413 | -763761.6413 | -763761.6413 | -763761.6413 | -763761.6413 | -763761.6413 | -763761.6413 | -763761.6413 | -763761.6413 | -763761.6413 | -763761.6413 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 22163307.2572 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 1183979.3358 | 1290531.6785 | 1422266.1237 | 1535097.6585 | 1605554.1886 | 1684828.3273 | 1774682.4478 | 1877471.8878 | 1996295.0877 | 2135468.7488 | 2300978.783 | 2501185.4831 | 2747913.2514 | 2917852.8258 | 3079919.4035 | 3240316.9267 | 3383358.2965 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 603025.0714 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | -254587.2138 | -509174.4275 | 475863.3268 | 582415.6695 | 714150.1147 | 826981.6495 | 897438.1796 | 976712.3183 | 1066566.4388 | 1169355.8788 | 1288179.0787 | 1427352.7398 | 1592862.774 | 1793069.4741 | 2039797.2424 | 2209736.8168 | 2371803.3945 | 2532200.9177 | 2675242.2875 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 13827682.3384 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -8938649.9902 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 22766332.3286 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 7705936.0217 | 2026-06-30 |  | 732650.1025 | 788042.4172 | 854285.6645 | 926409.2818 | 988537.9981 | 645602.0341 | 708203.3296 | 792823.1035 | 848845.1241 | 848852.6198 | 98607.6216 | 98622.2452 | 98642.7939 | 98672.4821 | 98714.9502 | 98775.4243 | 98861.8177 | 98985.6021 | 99163.4331 | 99419.5291 | 99789.1541 | 100323.7245 | 101144.9293 | 102361.5023 | 102789.8608
Option 3 | Capital expenditure | Option 3Capital expenditure | -14588410.522 | 2026-06-30 |  | 0 | 0 | -2042832.7494 | -2042832.7494 | -2042832.7494 | 0 | 0 | -4085665.4988 | -4085665.4988 | -4085665.4988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 9088626.9438 | 2026-06-30 |  | 896385.0392 | 958809.1266 | 1032979.6518 | 1114336.2903 | 1186877.962 | 733802.3693 | 796403.6648 | 881023.4387 | 937261.5953 | 938041.2394 | 108664.0752 | 110236.587 | 112444.195 | 115612.9697 | 120131.3416 | 126556.9454 | 135724.1218 | 148840.4758 | 167656.4693 | 194712.9872 | 233703.0934 | 290001.1777 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -8375022.6365 | 2026-06-30 |  | 0 | 0 | 0 | -123946.9066 | -247893.8132 | -371840.7197 | -371840.7197 | -371840.7197 | -546027.796 | -720214.8723 | -894401.9485 | -894401.9485 | -894401.9485 | -894401.9485 | -894401.9485 | -894401.9485 | -894401.9485 | -894401.9485 | -894401.9485 | -894401.9485 | -894401.9485 | -894401.9485 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 19237732.7788 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 533142.0804 | 584358.2672 | 641294.6629 | 704610.8409 | 775067.3711 | 1684828.3273 | 1774682.4478 | 1877471.8878 | 1996295.0877 | 2135468.7488 | 2300978.783 | 2501185.4831 | 2747913.2514 | 2917852.8258 | 3079919.4035 | 3240316.9267 | 3383358.2965 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 387815.1443 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | -123946.9066 | -247893.8132 | 161301.3607 | 212517.5474 | 269453.9432 | 158583.0449 | 54852.4988 | 846072.0111 | 935926.1316 | 1038715.5716 | 1157538.7715 | 1296712.4326 | 1462222.4668 | 1662429.1669 | 1909156.9352 | 2079096.5096 | 2241163.0873 | 2401560.6105 | 2544601.9803 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | 11250525.2866 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -8375022.6365 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 19625547.9231 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 0 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | 0 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 0 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0.76376 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 0.89639 | 0.95881 | 1.033 | 1.1143 | 1.1869 | 1.2669 | 1.3808 | 1.5223 | 1.6419 | 1.7131 | 1.7935 | 1.8849 | 1.9899 | 2.1119 | 2.2556 | 2.4275 | 2.6369 | 2.8968 | 3.0855 | 3.2746 | 3.474 | 3.6734 | 3.8901 | 4.1285 | 4.3909
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 0 |  |  | Energy at risk energy at risk (weighted) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Energy at risk value | 2.823 |  |  | Option 1 (base case) risk cost | 0.65832 | 0.70809 | 0.76761 | 0.83242 | 0.88824 | 0.94956 | 1.0397 | 1.1529 | 1.244 | 1.2887 | 1.3377 | 1.3915 | 1.4506 | 1.5155 | 1.5868 | 1.6652 | 1.7516 | 1.8468 | 1.9502 | 2.0635 | 2.1879 | 2.3247 | 2.4752 | 2.6408 | 2.823

## Sensitivity_calcs
CitiPower
VM switchboard and relay replacement
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
[7 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 2209736.8168 | 2371803.3945 | 2532200.9177 | 2675242.2875 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 13827682.3384 |  | 0 | 0 | 0 | 0 | -254587.2138 | -509174.4275 | 475863.3268 | 582415.6695 | 714150.1147 | 826981.6495 | 897438.1796 | 976712.3183 | 1066566.4388 | 1169355.8788 | 1288179.0787 | 1427352.7398 | 1592862.774 | 1793069.4741 | 2039797.2424 | 2209736.8168 | 2371803.3945 | 2532200.9177 | 2675242.2875 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 12933817.3394 |  | 0 | 0 | 0 | 0 | -280045.9352 | -560091.8703 | 399487.1626 | 506039.5054 | 637773.9506 | 750605.4854 | 821062.0155 | 900336.1542 | 990190.2746 | 1092979.7146 | 1211802.9145 | 1350976.5757 | 1516486.6099 | 1716693.3099 | 1963421.0783 | 2133360.6527 | 2295427.2303 | 2455824.7536 | 2598866.1234 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 14721547.3374 |  | 0 | 0 | 0 | 0 | -229128.4924 | -458256.9848 | 552239.4909 | 658791.8336 | 790526.2788 | 903357.8136 | 973814.3437 | 1053088.4824 | 1142942.6029 | 1245732.0429 | 1364555.2428 | 1503728.9039 | 1669238.9382 | 1869445.6382 | 2116173.4066 | 2286112.981 | 2448179.5586 | 2608577.0819 | 2751618.4516 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 16104315.5713 |  | 0 | 0 | 0 | 0 | -254587.2138 | -509174.4275 | 599825.8236 | 717033.4006 | 861941.2903 | 986055.9786 | 1063558.1617 | 1150759.7143 | 1249599.2468 | 1362667.6308 | 1493373.1507 | 1646464.1779 | 1828525.2156 | 2048752.5856 | 2320153.1308 | 2507086.6627 | 2685359.8981 | 2861797.1736 | 3019142.6804 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 11551049.1056 |  | 0 | 0 | 0 | 0 | -254587.2138 | -509174.4275 | 351900.83 | 447797.9384 | 566358.9391 | 667907.3204 | 731318.1975 | 802664.9223 | 883533.6308 | 976044.1267 | 1082985.0067 | 1208241.3017 | 1357200.3325 | 1537386.3625 | 1759441.354 | 1912386.971 | 2058246.8909 | 2202604.6618 | 2331341.8946 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 10657184.1066 |  | 0 | 0 | 0 | 0 | -280045.9352 | -560091.8703 | 275524.6658 | 371421.7743 | 489982.775 | 591531.1563 | 654942.0334 | 726288.7582 | 807157.4666 | 899667.9626 | 1006608.8425 | 1131865.1376 | 1280824.1684 | 1461010.1984 | 1683065.1899 | 1836010.8069 | 1981870.7268 | 2126228.4977 | 2254965.7305 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 13827682.3384 |  | 0 | 0 | 0 | 0 | -254587.2138 | -509174.4275 | 475863.3268 | 582415.6695 | 714150.1147 | 826981.6495 | 897438.1796 | 976712.3183 | 1066566.4388 | 1169355.8788 | 1288179.0787 | 1427352.7398 | 1592862.774 | 1793069.4741 | 2039797.2424 | 2209736.8168 | 2371803.3945 | 2532200.9177 | 2675242.2875 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 13827682.3384 |  | 0 | 0 | 0 | 0 | -254587.2138 | -509174.4275 | 475863.3268 | 582415.6695 | 714150.1147 | 826981.6495 | 897438.1796 | 976712.3183 | 1066566.4388 | 1169355.8788 | 1288179.0787 | 1427352.7398 | 1592862.774 | 1793069.4741 | 2039797.2424 | 2209736.8168 | 2371803.3945 | 2532200.9177 | 2675242.2875 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 13827682.3384 |  | 0 | 0 | 0 | 0 | -254587.2138 | -509174.4275 | 475863.3268 | 582415.6695 | 714150.1147 | 826981.6495 | 897438.1796 | 976712.3183 | 1066566.4388 | 1169355.8788 | 1288179.0787 | 1427352.7398 | 1592862.774 | 1793069.4741 | 2039797.2424 | 2209736.8168 | 2371803.3945 | 2532200.9177 | 2675242.2875 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | -123946.9066 | -247893.8132 | 161301.3607 | 212517.5474 | 269453.9432 | 158583.0449 | 54852.4988 | 846072.0111 | 935926.1316 | 1038715.5716 | 1157538.7715 | 1296712.4326 | 1462222.4668 | 1662429.1669 | 1909156.9352 | 2079096.5096 | 2241163.0873 | 2401560.6105 | 2544601.9803 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 11250525.2866 |  | 0 | 0 | 0 | 0 | -123946.9066 | -247893.8132 | 161301.3607 | 212517.5474 | 269453.9432 | 158583.0449 | 54852.4988 | 846072.0111 | 935926.1316 | 1038715.5716 | 1157538.7715 | 1296712.4326 | 1462222.4668 | 1662429.1669 | 1909156.9352 | 2079096.5096 | 2241163.0873 | 2401560.6105 | 2544601.9803 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 10413023.023 |  | 0 | 0 | 0 | 0 | -136341.5972 | -272683.1945 | 124117.2887 | 175333.4755 | 232269.8712 | 103980.2653 | -17168.9884 | 756631.8163 | 846485.9367 | 949275.3767 | 1068098.5766 | 1207272.2377 | 1372782.272 | 1572988.972 | 1819716.7404 | 1989656.3148 | 2151722.8924 | 2312120.4157 | 2455161.7854 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 12088027.5503 |  | 0 | 0 | 0 | 0 | -111552.2159 | -223104.4318 | 198485.4327 | 249701.6194 | 306638.0151 | 213185.8245 | 126873.986 | 935512.206 | 1025366.3264 | 1128155.7664 | 1246978.9663 | 1386152.6275 | 1551662.6617 | 1751869.3617 | 1998597.1301 | 2168536.7045 | 2330603.2821 | 2491000.8054 | 2634042.1751 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 13213080.0789 |  | 0 | 0 | 0 | 0 | -123946.9066 | -247893.8132 | 214615.5687 | 270953.3741 | 333583.4095 | 229044.129 | 132359.2359 | 1020119.4071 | 1118958.9396 | 1232027.3236 | 1362732.8435 | 1515823.8707 | 1697884.9084 | 1918112.2784 | 2189512.8236 | 2376446.3555 | 2554719.5909 | 2731156.8664 | 2888502.3732 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | 9287970.4943 |  | 0 | 0 | 0 | 0 | -123946.9066 | -247893.8132 | 107987.1527 | 154081.7207 | 205324.4769 | 88121.9608 | -22654.2383 | 672024.6151 | 752893.3236 | 845403.8196 | 952344.6995 | 1077600.9945 | 1226560.0253 | 1406746.0553 | 1628801.0469 | 1781746.6638 | 1927606.5837 | 2071964.3546 | 2200701.5874 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | 8450468.2307 |  | 0 | 0 | 0 | 0 | -136341.5972 | -272683.1945 | 70803.0807 | 116897.6487 | 168140.4049 | 33519.1812 | -94675.7255 | 582584.4203 | 663453.1287 | 755963.6247 | 862904.5046 | 988160.7996 | 1137119.8304 | 1317305.8605 | 1539360.852 | 1692306.469 | 1838166.3888 | 1982524.1598 | 2111261.3926 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 11250525.2866 |  | 0 | 0 | 0 | 0 | -123946.9066 | -247893.8132 | 161301.3607 | 212517.5474 | 269453.9432 | 158583.0449 | 54852.4988 | 846072.0111 | 935926.1316 | 1038715.5716 | 1157538.7715 | 1296712.4326 | 1462222.4668 | 1662429.1669 | 1909156.9352 | 2079096.5096 | 2241163.0873 | 2401560.6105 | 2544601.9803 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 11250525.2866 |  | 0 | 0 | 0 | 0 | -123946.9066 | -247893.8132 | 161301.3607 | 212517.5474 | 269453.9432 | 158583.0449 | 54852.4988 | 846072.0111 | 935926.1316 | 1038715.5716 | 1157538.7715 | 1296712.4326 | 1462222.4668 | 1662429.1669 | 1909156.9352 | 2079096.5096 | 2241163.0873 | 2401560.6105 | 2544601.9803 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 11250525.2866 |  | 0 | 0 | 0 | 0 | -123946.9066 | -247893.8132 | 161301.3607 | 212517.5474 | 269453.9432 | 158583.0449 | 54852.4988 | 846072.0111 | 935926.1316 | 1038715.5716 | 1157538.7715 | 1296712.4326 | 1462222.4668 | 1662429.1669 | 1909156.9352 | 2079096.5096 | 2241163.0873 | 2401560.6105 | 2544601.9803 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 1 | 1 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 13.8277 | 11.2505 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens1 | Capex 10% higher | 0 | 12.9338 | 10.413 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens2 | Capex 10% lower | 0 | 14.7215 | 12.088 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens3 | Total benefits 10% higher | 0 | 16.1043 | 13.2131 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens4 | Total benefits 10% lower | 0 | 11.551 | 9.288 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 10.6572 | 8.4505 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Workings_costs
CitiPower
VM switchboard and relay replacement
WORKINGS - COSTS
Option 1 - continue existing maintenance with no proactive replacement cost
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
|  | SWBD online monitoring annual cost ($) | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
Relay annual maintenance cost ($)
|  | Total opex cost ($) | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
Option 2 - Combined replacement of SWBD (i.e. all three buses) and relays completed in 2030-31
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | SWBD capex profile ($) | 2028-29: 2753359.964; 2029-30: 2753359.964; 2030-31: 2753359.964
|  | Relay capex profile ($) | 2028-29: 1835573.3094; 2029-30: 1835573.3094; 2030-31: 1835573.3094
|  | Total capex ($) | 0 | 0 | 4588933.2734 | 4588933.2734 | 4588933.2734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
|  | SWBD online monitoring annual cost ($) | 2026-27: 50000; 2027-28: 50000; 2028-29: 50000; 2029-30: 50000; 2030-31: 50000
|  | Relay annual maintenance cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total opex cost ($) | 50000 | 50000 | 50000 | 50000 | 50000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Relay replacement completed in 2030-31 and SWBD replacement completed in 2035-36
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | SWBD capex profile ($) | 2033-34: 3671146.6187; 2034-35: 3671146.6187; 2035-36: 3671146.6187
|  | Relay capex profile ($) | 2028-29: 1835573.3094; 2029-30: 1835573.3094; 2030-31: 1835573.3094
|  | Total capex ($) | 0 | 0 | 1835573.3094 | 1835573.3094 | 1835573.3094 | 0 | 0 | 3671146.6187 | 3671146.6187 | 3671146.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
|  | SWBD online monitoring annual cost ($) | 2026-27: 50000; 2027-28: 50000; 2028-29: 50000; 2029-30: 50000; 2030-31: 50000; 2031-32: 50000; 2032-33: 50000; 2033-34: 50000; 2034-35: 50000; 2035-36: 50000
|  | Relay annual maintenance cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total opex cost ($) | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Workings_risks
CitiPower
VM switchboard and relay replacement
WORKINGS - RISKS
Option 1 - continue existing maintenance with no proactive replacement cost
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
SWBD risks
|  | Energy at Risk ($) | 418503.1111 | 446847.4232 | 482877.0848 | 521900.2142 | 549487.8435 | 579868.3587 | 636118.322 | 712152.8375 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534
|  | Safety Risk | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695
|  | Unplanned Replacement Risk | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588
|  | Unplanned Fault Risk | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7
|  | Other risk | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001
|  | Total SWBD risks | 493539.8394 | 521884.1514 | 557913.8131 | 596936.9424 | 624524.5717 | 654905.087 | 711155.0503 | 787189.5658 | 837525.8817 | 837525.8817 | 837525.8817 | 837525.8817 | 837525.8817 | 837525.8817 | 837525.8817 | 837525.8817 | 837525.8817 | 837525.8817 | 837525.8817 | 837525.8817 | 837525.8817 | 837525.8817 | 837525.8817 | 837525.8817 | 837525.8817
Relay risks
|  | Environment risk ($) | 299.6999 | 317.2015 | 345.8159 | 400.1835 | 472.984 | 571.422 | 702.2538 | 880.0802 | 1122.9116 | 1456.4228 | 1918.6664 | 2564.4213 | 3472.7174 | 4757.7956 | 6585.0891 | 9194.5548 | 12934.7698 | 18312.8168 | 20205.188 | 21561.4847 | 22733.6315 | 22967.7681 | 23075.5868 | 23194.2406 | 23324.8606 | 23468.7027
|  | Energy at Risk ($) | 239814.5968 | 261242.6679 | 284735.4203 | 310518.4709 | 338756.1721 | 369690.5062 | 403588.0651 | 440743.6108 | 481482.1284 | 526162.9595 | 575184.3358 | 628988.1198 | 688065.696 | 752965.0751 | 824299.6035 | 902758.8348 | 989122.3568 | 1084277.7153 | 1187690.0317 | 1300994.2508 | 1425432.497 | 1562248.9921 | 1712708.7802 | 1878266.4506 | 2060502.314 | 2261172.8632
|  | Safety Risk | 3260.5182 | 3486.9771 | 3802.3013 | 4311.5123 | 4963.392 | 5810.2465 | 6901.3237 | 8341.6732 | 10260.6854 | 12842.3069 | 16358.5059 | 21200.1544 | 27930.4495 | 37362.717 | 50673.8591 | 69569.959 | 96528.2945 | 135151.4024 | 149082.3511 | 159258.6425 | 168182.92 | 170513.6456 | 172015.9633 | 173670.4294 | 175493.132 | 177501.9713
|  | Unplanned Replacement Risk | 68525.9542 | 74600.3448 | 81379.4072 | 89112.0962 | 97743.9054 | 107426.9553 | 118327.4395 | 130713.5245 | 144901.5721 | 161314.3824 | 180542.8667 | 203402.4506 | 231030.6581 | 265028.9826 | 307669.5062 | 362196.2936 | 433265.677 | 527590.3117 | 577959.6919 | 623058.1408 | 667681.8528 | 707415.5902 | 750065.3434 | 796962.4076 | 848539.8051 | 905275.9937
|  | Total relay risks | 311900.7692 | 339647.1914 | 370262.9447 | 404342.263 | 441936.4536 | 483499.1299 | 529519.0821 | 580678.8887 | 637767.2975 | 701776.0716 | 774004.3748 | 856155.1461 | 950499.521 | 1060114.5704 | 1189228.0578 | 1343719.6422 | 1531851.0981 | 1765332.2461 | 1934937.2627 | 2104872.5188 | 2284030.9012 | 2463145.9959 | 2657865.6737 | 2872093.5282 | 3107860.1117
Total SWBD and relay risk
|  | Energy at Risk ($) | 658317.708 | 708090.0911 | 767612.5051 | 832418.6851 | 888244.0156 | 949558.865 | 1039706.3871 | 1152896.4484 | 1243971.2818 | 1288652.1129 | 1337673.4892 | 1391477.2732 | 1450554.8494 | 1515454.2286 | 1586788.7569 | 1665247.9882 | 1751611.5102 | 1846766.8687 | 1950179.1851 | 2063483.4042 | 2187921.6504 | 2324738.1455 | 2475197.9336 | 2640755.604 | 2822991.4674
|  | Safety risk | 3713.0877 | 3939.5466 | 4254.8708 | 4764.0818 | 5415.9615 | 6262.8159 | 7353.8932 | 8794.2426 | 10713.2549 | 13294.8764 | 16811.0754 | 21652.7239 | 28383.0189 | 37815.2865 | 51126.4285 | 70022.5284 | 96980.864 | 135603.9718 | 149534.9206 | 159711.212 | 168635.4894 | 170966.215 | 172468.5328 | 174122.9989 | 175945.7015
|  | Unplanned replacement | 92461.413 | 98535.8036 | 105314.866 | 113047.555 | 121679.3642 | 131362.414 | 142262.8983 | 154648.9833 | 168837.0309 | 185249.8412 | 204478.3255 | 227337.9094 | 254966.1168 | 288964.4414 | 331604.9649 | 386131.7524 | 457201.1358 | 551525.7705 | 601895.1507 | 646993.5996 | 691617.3115 | 731351.049 | 774000.8022 | 820897.8664 | 872475.2638
|  | Unplanned fault | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7
|  | Environmental risk | 299.6999 | 317.2015 | 345.8159 | 400.1835 | 472.984 | 571.422 | 702.2538 | 880.0802 | 1122.9116 | 1456.4228 | 1918.6664 | 2564.4213 | 3472.7174 | 4757.7956 | 6585.0891 | 9194.5548 | 12934.7698 | 18312.8168 | 20205.188 | 21561.4847 | 22733.6315 | 22967.7681 | 23075.5868 | 23194.2406 | 23324.8606
|  | Other risk | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001
|  | Total SWBD and relay risks | 805440.6086 | 861531.3428 | 928176.7578 | 1001279.2054 | 1066461.0253 | 1138404.2169 | 1240674.1323 | 1367868.4544 | 1475293.1792 | 1539301.9532 | 1611530.2565 | 1693681.0278 | 1788025.4027 | 1897640.452 | 2026753.9395 | 2181245.5238 | 2369376.9798 | 2602858.1278 | 2772463.1444 | 2942398.4004 | 3121556.7829 | 3300671.8776 | 3495391.5554 | 3709619.4099 | 3945385.9933
Option 2 - Combined replacement of SWBD (i.e. all three buses) and relays completed in 2030-31
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
SWBD risks
|  | Energy at Risk ($) | 418503.1111 | 446847.4232 | 482877.0848 | 521900.2142 | 549487.8435 | 67154.3701 | 73682.4112 | 82507.6541 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869
|  | Safety Risk | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435
|  | Unplanned Replacement Risk | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363
|  | Unplanned Fault Risk | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
|  | Other risk | 50001 | 50001 | 50001 | 50001 | 50001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total SWBD risks | 493539.8394 | 521884.1514 | 557913.8131 | 596936.9424 | 624524.5717 | 70099.7499 | 76627.791 | 85453.0339 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667
Relay risks
|  | Environment risk ($) | 299.6999 | 317.2015 | 345.8159 | 400.1835 | 472.984 | 235.7187 | 235.7187 | 235.7187 | 244.8524 | 277.4824 | 323.9357 | 389.7748 | 482.2036 | 614.864 | 804.0174 | 1073.0093 | 1456.764 | 2005.8291 | 2793.4732 | 3926.0476 | 5558.1252 | 7914.6453 | 11349.805 | 16341.0766 | 17777.6132 | 18546.6
|  | Energy at Risk ($) | 239814.5968 | 261242.6679 | 284735.4203 | 310518.4709 | 338756.1721 | 232.9063 | 232.9063 | 232.9063 | 234.7916 | 241.5268 | 250.913 | 264.0529 | 282.5168 | 309.1929 | 347.3524 | 401.6909 | 479.3191 | 590.5447 | 750.3336 | 980.4468 | 1312.5708 | 1792.9054 | 2530.7933 | 3623.9366 | 4008.8352 | 4282.2028
|  | Safety Risk | 3260.5182 | 3486.9771 | 3802.3013 | 4311.5123 | 4963.392 | 1673.4636 | 1673.4636 | 1673.4636 | 1738.2835 | 1969.8533 | 2299.5221 | 2766.7668 | 3422.7125 | 4364.1744 | 5706.5575 | 7615.5389 | 10338.9696 | 14235.5769 | 19825.3367 | 27863.0047 | 39445.5605 | 56169.3634 | 80548.2157 | 115970.6679 | 126165.8949 | 131623.6616
|  | Unplanned Replacement Risk | 68525.9542 | 74600.3448 | 81379.4072 | 89112.0962 | 97743.9054 | 2305.8937 | 2305.8937 | 2305.8937 | 2426.1477 | 2855.7565 | 3467.3196 | 4334.0655 | 5550.858 | 7297.3404 | 9787.5964 | 13328.9666 | 18381.2562 | 25609.968 | 35979.7566 | 50890.849 | 72378.3832 | 103403.9818 | 148474.0916 | 213878.7447 | 232366.5937 | 241901.7582
|  | Total relay risks | 311900.7692 | 339647.1914 | 370262.9447 | 404342.263 | 441936.4536 | 4447.9823 | 4447.9823 | 4447.9823 | 4644.0751 | 5344.6189 | 6341.6903 | 7754.66 | 9738.2909 | 12585.5717 | 16645.5237 | 22419.2057 | 30656.309 | 42441.9187 | 59348.9001 | 83660.348 | 118694.6397 | 169280.896 | 242902.9056 | 349814.4258 | 380318.937
Total SWBD and relay risk
|  | Energy at Risk ($) | 658317.708 | 708090.0911 | 767612.5051 | 832418.6851 | 888244.0156 | 67387.2764 | 73915.3175 | 82740.5604 | 88587.0785 | 88593.8136 | 88603.1998 | 88616.3398 | 88634.8036 | 88661.4798 | 88699.6392 | 88753.9778 | 88831.606 | 88942.8316 | 89102.6204 | 89332.7337 | 89664.8577 | 90145.1923 | 90883.0802 | 91976.2235 | 92361.1221
|  | Safety risk | 3713.0877 | 3939.5466 | 4254.8708 | 4764.0818 | 5415.9615 | 1726.7071 | 1726.7071 | 1726.7071 | 1791.5269 | 2023.0967 | 2352.7656 | 2820.0103 | 3475.956 | 4417.4179 | 5759.801 | 7668.7823 | 10392.2131 | 14288.8204 | 19878.5801 | 27916.2481 | 39498.804 | 56222.6069 | 80601.4592 | 116023.9113 | 126219.1383
|  | Unplanned replacement | 92461.413 | 98535.8036 | 105314.866 | 113047.555 | 121679.3642 | 5121.83 | 5121.83 | 5121.83 | 5242.084 | 5671.6928 | 6283.2559 | 7150.0018 | 8366.7943 | 10113.2767 | 12603.5327 | 16144.9029 | 21197.1925 | 28425.9043 | 38795.693 | 53706.7853 | 75194.3196 | 106219.9182 | 151290.0279 | 216694.681 | 235182.53
|  | Unplanned fault | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
|  | Environmental risk | 299.6999 | 317.2015 | 345.8159 | 400.1835 | 472.984 | 235.7187 | 235.7187 | 235.7187 | 244.8524 | 277.4824 | 323.9357 | 389.7748 | 482.2036 | 614.864 | 804.0174 | 1073.0093 | 1456.764 | 2005.8291 | 2793.4732 | 3926.0476 | 5558.1252 | 7914.6453 | 11349.805 | 16341.0766 | 17777.6132
|  | Other risk | 50001 | 50001 | 50001 | 50001 | 50001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total SWBD and relay risks | 805440.6086 | 861531.3428 | 928176.7578 | 1001279.2054 | 1066461.0253 | 74547.7322 | 81075.7733 | 89901.0162 | 95941.7418 | 96642.2856 | 97639.357 | 99052.3267 | 101035.9576 | 103883.2384 | 107943.1903 | 113716.8724 | 121953.9757 | 133739.5853 | 150646.5667 | 174958.0147 | 209992.3064 | 260578.5626 | 334200.5723 | 441112.0925 | 471616.6036
Option 3 - Relay replacement completed in 2030-31 and SWBD replacement completed in 2035-36
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
SWBD risks
|  | Energy at Risk ($, Weighted) | 418503.1111 | 446847.4232 | 482877.0848 | 521900.2142 | 549487.8435 | 579868.3587 | 636118.322 | 712152.8375 | 762489.1534 | 762489.1534 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869
|  | Safety Risk | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435
|  | Unplanned Replacement Risk | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363
|  | Unplanned Fault Risk | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
|  | Other risk | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total SWBD risks | 493539.8394 | 521884.1514 | 557913.8131 | 596936.9424 | 624524.5717 | 654905.087 | 711155.0503 | 787189.5658 | 837525.8817 | 837525.8817 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667 | 91297.6667
Relay risks
|  | Environment risk ($) | 299.6999 | 317.2015 | 345.8159 | 400.1835 | 472.984 | 235.7187 | 235.7187 | 235.7187 | 244.8524 | 277.4824 | 323.9357 | 389.7748 | 482.2036 | 614.864 | 804.0174 | 1073.0093 | 1456.764 | 2005.8291 | 2793.4732 | 3926.0476 | 5558.1252 | 7914.6453 | 11349.805 | 16341.0766 | 17777.6132 | 18546.6
|  | Energy at Risk ($) | 239814.5968 | 261242.6679 | 284735.4203 | 310518.4709 | 338756.1721 | 232.9063 | 232.9063 | 232.9063 | 234.7916 | 241.5268 | 250.913 | 264.0529 | 282.5168 | 309.1929 | 347.3524 | 401.6909 | 479.3191 | 590.5447 | 750.3336 | 980.4468 | 1312.5708 | 1792.9054 | 2530.7933 | 3623.9366 | 4008.8352 | 4282.2028
|  | Safety Risk | 3260.5182 | 3486.9771 | 3802.3013 | 4311.5123 | 4963.392 | 1673.4636 | 1673.4636 | 1673.4636 | 1738.2835 | 1969.8533 | 2299.5221 | 2766.7668 | 3422.7125 | 4364.1744 | 5706.5575 | 7615.5389 | 10338.9696 | 14235.5769 | 19825.3367 | 27863.0047 | 39445.5605 | 56169.3634 | 80548.2157 | 115970.6679 | 126165.8949 | 131623.6616
|  | Unplanned Replacement Risk | 68525.9542 | 74600.3448 | 81379.4072 | 89112.0962 | 97743.9054 | 2305.8937 | 2305.8937 | 2305.8937 | 2426.1477 | 2855.7565 | 3467.3196 | 4334.0655 | 5550.858 | 7297.3404 | 9787.5964 | 13328.9666 | 18381.2562 | 25609.968 | 35979.7566 | 50890.849 | 72378.3832 | 103403.9818 | 148474.0916 | 213878.7447 | 232366.5937 | 241901.7582
|  | Total relay risks | 311900.7692 | 339647.1914 | 370262.9447 | 404342.263 | 441936.4536 | 4447.9823 | 4447.9823 | 4447.9823 | 4644.0751 | 5344.6189 | 6341.6903 | 7754.66 | 9738.2909 | 12585.5717 | 16645.5237 | 22419.2057 | 30656.309 | 42441.9187 | 59348.9001 | 83660.348 | 118694.6397 | 169280.896 | 242902.9056 | 349814.4258 | 380318.937
Total SWBD and relay risk
|  | Energy at Risk ($) | 658317.708 | 708090.0911 | 767612.5051 | 832418.6851 | 888244.0156 | 580101.2651 | 636351.2284 | 712385.7439 | 762723.945 | 762730.6802 | 88603.1998 | 88616.3398 | 88634.8036 | 88661.4798 | 88699.6392 | 88753.9778 | 88831.606 | 88942.8316 | 89102.6204 | 89332.7337 | 89664.8577 | 90145.1923 | 90883.0802 | 91976.2235 | 92361.1221
|  | Safety risk | 3713.0877 | 3939.5466 | 4254.8708 | 4764.0818 | 5415.9615 | 2126.0331 | 2126.0331 | 2126.0331 | 2190.8529 | 2422.4227 | 2352.7656 | 2820.0103 | 3475.956 | 4417.4179 | 5759.801 | 7668.7823 | 10392.2131 | 14288.8204 | 19878.5801 | 27916.2481 | 39498.804 | 56222.6069 | 80601.4592 | 116023.9113 | 126219.1383
|  | Unplanned replacement | 92461.413 | 98535.8036 | 105314.866 | 113047.555 | 121679.3642 | 26241.3524 | 26241.3524 | 26241.3524 | 26361.6064 | 26791.2153 | 6283.2559 | 7150.0018 | 8366.7943 | 10113.2767 | 12603.5327 | 16144.9029 | 21197.1925 | 28425.9043 | 38795.693 | 53706.7853 | 75194.3196 | 106219.9182 | 151290.0279 | 216694.681 | 235182.53
|  | Unplanned fault | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
|  | Environmental risk | 299.6999 | 317.2015 | 345.8159 | 400.1835 | 472.984 | 235.7187 | 235.7187 | 235.7187 | 244.8524 | 277.4824 | 323.9357 | 389.7748 | 482.2036 | 614.864 | 804.0174 | 1073.0093 | 1456.764 | 2005.8291 | 2793.4732 | 3926.0476 | 5558.1252 | 7914.6453 | 11349.805 | 16341.0766 | 17777.6132
|  | Other risk | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total SWBD and relay risks | 805440.6086 | 861531.3428 | 928176.7578 | 1001279.2054 | 1066461.0253 | 659353.0693 | 715603.0326 | 791637.5481 | 842169.9568 | 842870.5006 | 97639.357 | 99052.3267 | 101035.9576 | 103883.2384 | 107943.1903 | 113716.8724 | 121953.9757 | 133739.5853 | 150646.5667 | 174958.0147 | 209992.3064 | 260578.5626 | 334200.5723 | 441112.0925 | 471616.6036

## SWBD risks
CitiPower
VM switchboard and relay replacement
Input Data - Station Configuration |  | Constants |  |  | POF METHOD | FIXED | Modifier (x) | Comment
Substation: | VM | Major Failure CoC |  |  | PoF (#1) | 0.2125% | 100%
Asset Type | Indoor CB | Minor Failure CoC |  |  | PoF (#2) | 0.2125% | 100%
VCR | 52.307 | Major Failure CoC - used | 3754581.7691 |  | PoF (#3) | 0.2125% | 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 101600 |  | PoF (#4) | 0% | 100%
Scenario #1: VM - Indoor CB | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 0% | 0 | Energy | 6124.4034 | 7100.1686 | 7505.89 | 8023.706 | 8572.2202 | 9010.764 | 9475.7719 | 10300.8038 | 11541.7123 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066
Online Monitoring | 100% | 48309.1787 | Energy | 7965.4948 | 10102.6087 | 10962.2046 | 12050.0055 | 13256.9399 | 13991.7297 | 14842.75 | 16502.2796 | 18452.2274 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229 | 19941.0229
Physical Separation | 0% | 300000 | Energy | 6124.4034 | 7100.1686 | 7505.89 | 8023.706 | 8572.2202 | 9010.764 | 9475.7719 | 10300.8038 | 11541.7123 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066 | 12278.4066
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375% | 0.6375%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 349239.7571 | 418503.1111 | 446847.4232 | 482877.0848 | 521900.2142 | 549487.8435 | 579868.3587 | 636118.322 | 712152.8375 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534 | 762489.1534
Replace 1 Asset | 0% | 3128818.141 | Safety Risk | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695 | 452.5695
Replace 2 Assets | 0% | 6257636.2819 | Unplanned Replacement Risk | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588 | 23935.4588
Replace 3 Assets | 0% | 9386454.4229 | Unplanned Fault Risk | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7 | 647.7
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001 | 50001
|  | 0 | Option Capital Cost | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
|  |  | Total Life Cycle Cost | 474276.4853 | 543539.8394 | 571884.1514 | 607913.8131 | 646936.9424 | 674524.5717 | 704905.087 | 761155.0503 | 837189.5658 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817 | 887525.8817
Input Data - Station Configuration |  | Constants |  | PoF (#4) 2026: POF METHOD; 0% 2027: FIXED; 100% 2028: Modifier (x); 100% 2029: Comment
Substation: | VM | Major Failure CoC |  | PoF (#4) 2026: PoF (#1); 0% 2027: 0.25%; 100% 2028: 100%
Asset Type | Indoor CB | Minor Failure CoC |  | PoF (#4) 2026: PoF (#2); 0% 2027: 0.25%; 100% 2028: 100%
VCR | 52.307 | Major Failure CoC - used | 3754581.7691 | PoF (#4) 2026: PoF (#3); 0% 2027: 0.25%; 100% 2028: 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 101600 | PoF (#4) 2026: PoF (#4); 0% 2027: 0%; 100% 2028: 100%
Scenario #2: VM - Indoor CB | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 0% | 0 | Energy | 7228.2684 | 8380.0297 | 8858.8363 | 9469.8927 | 10117.1064 | 10634.5433 | 1097.2558 | 1192.9538 | 1336.9202 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107
Online Monitoring | 0% | 48309.1787 | Energy | 9402.8857 | 11924.3889 | 12938.5013 | 14221.7893 | 15645.5364 | 16512.3003 | 1719.2382 | 1911.951 | 2138.4299 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091
Physical Separation | 0% | 300000 | Energy | 7228.2684 | 8380.0297 | 8858.8363 | 9469.8927 | 10117.1064 | 10634.5433 | 1097.2558 | 1192.9538 | 1336.9202 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.00075 | 0.00075 | 0.00075 | 0.00075
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.00075 | 0.00075 | 0.00075 | 0.00075
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 412213.3483 | 493952.6534 | 527397.6605 | 569908.9151 | 615948.1628 | 648495.4073 | 67154.3701 | 73682.4112 | 82507.6541 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869
Replace 1 Asset | 0% | 3128818.141 | Safety Risk | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435
Replace 2 Assets | 0% | 6257636.2819 | Unplanned Replacement Risk | 28159.3633 | 28159.3633 | 28159.3633 | 28159.3633 | 28159.3633 | 28159.3633 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363
Replace 3 Assets | 0% | 9386454.4229 | Unplanned Fault Risk | 762 | 762 | 762 | 762 | 762 | 762 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 0 | 0 | 0 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717
|  |  | Total Life Cycle Cost | 441667.1463 | 523406.4513 | 556851.4584 | 599362.713 | 645401.9607 | 677949.2053 | 470279.1216 | 476807.1627 | 485632.4056 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384
Input Data - Station Configuration |  | Constants |  | PoF (#4) 2026: POF METHOD; 0% 2027: FIXED; 100% 2028: Modifier (x); 100% 2029: Comment
Substation: | VM | Major Failure CoC |  | PoF (#4) 2026: PoF (#1); 0% 2027: 0.25%; 100% 2028: 100%
Asset Type | Indoor CB | Minor Failure CoC |  | PoF (#4) 2026: PoF (#2); 0% 2027: 0.25%; 100% 2028: 100%
VCR | 52.307 | Major Failure CoC - used | 3754581.7691 | PoF (#4) 2026: PoF (#3); 0% 2027: 0.25%; 100% 2028: 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 101600 | PoF (#4) 2026: PoF (#4); 0% 2027: 0%; 100% 2028: 100%
Scenario #3: VM - Indoor CB | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 0% | 0 | Energy | 7228.2684 | 8380.0297 | 8858.8363 | 9469.8927 | 10117.1064 | 10634.5433 | 11183.178 | 12156.5364 | 13620.4793 | 14489.5398 | 14489.5398 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107
Online Monitoring | 0% | 48309.1787 | Energy | 9402.8857 | 11924.3889 | 12938.5013 | 14221.7893 | 15645.5364 | 16512.3003 | 17516.1435 | 19473.5876 | 21773.5019 | 23529.3758 | 23529.3758 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091 | 2311.4091
Physical Separation | 0% | 300000 | Energy | 7228.2684 | 8380.0297 | 8858.8363 | 9469.8927 | 10117.1064 | 10634.5433 | 11183.178 | 12156.5364 | 13620.4793 | 14489.5398 | 14489.5398 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107 | 1422.4107
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.00075 | 0.00075 | 0.00075 | 0.00075
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.00075 | 0.00075 | 0.00075 | 0.00075
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 412213.3483 | 493952.6534 | 527397.6605 | 569908.9151 | 615948.1628 | 648495.4073 | 684336.0198 | 750691.8495 | 840384.4573 | 899758.3695 | 899758.3695 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869 | 88352.2869
Replace 1 Asset | 0% | 3128818.141 | Safety Risk | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435
Replace 2 Assets | 0% | 6257636.2819 | Unplanned Replacement Risk | 28159.3633 | 28159.3633 | 28159.3633 | 28159.3633 | 28159.3633 | 28159.3633 | 28159.3633 | 28159.3633 | 28159.3633 | 28159.3633 | 28159.3633 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363 | 2815.9363
Replace 3 Assets | 0% | 9386454.4229 | Unplanned Fault Risk | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717 | 400179.3717
|  |  | Total Life Cycle Cost | 441667.1463 | 523406.4513 | 556851.4584 | 599362.713 | 645401.9607 | 677949.2053 | 713789.8177 | 780145.6474 | 869838.2553 | 929212.1674 | 929212.1674 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384 | 491477.0384

## Misc_calcs
CitiPower
VM switchboard and relay replacement
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 3 | TRUE
| Option 3 | 3 | TRUE
| Option 4 | Not used | FALSE
| Option 5 | Not used | FALSE
| First year | 3
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
CitiPower
VM switchboard and relay replacement
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | TRUE | Not used |  | TRUE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
|  |  | CitiPower | Powercor | United Energy
| Reliability in worst-served areas | per MWh | 0 | 151432.8174 | 0
| Network resilience | per MWh | 0 | 24590 | 38560
| Enabling solar exports | per MWh | 4220.9954 | 88.3577 | 862.6028
| Aesthetics | per customer impacted | 0 | 0 | 0
| Customer value of time - residential | per minute customer time | 0.54769 | 0.35181 | 0.34751
| Customer value of time - business | per minute customer time | 0.54769 | 0.35181 | 0.34751
| Communication | per customer impacted | 0 | 0 | 0
| Information accessibility | per customer impacted | 0 | 0 | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020