## Cover
CitiPower
Regulatory proposal 2026-31
AR switchboard and relay
| Model number: | 4.06
2025-01-31
15

## Summary
CitiPower
AR switchboard and relay replacement
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Combined replacement of SWBD (i.e. all three buses) and relays completed in 2027-28 |  | -5.6767 | 8.5256 | 2.8488
| Option 3 | Relay replacement completed in 2027-28 and SWBD replacement completed in 2032-33 |  | -5.3526 | 7.316 | 1.9634
| Option 4 | 0
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | Combined replacement of SWBD (i.e. all three buses) and relays completed in 2027-28 |  | 2.8488
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 5.7691 | 2.8845 | 0 | 0 | 0 |  | 8.6536
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
| Capex and risk ($M, 2026) |  | Value of expected unserved energy ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 2.8488 | 1.9634 |  |  |  | Option 2
| Capex 10% higher |  | 0 | 2.2812 | 1.4281 |  |  |  | Option 2
| Capex 10% lower |  | 0 | 3.4165 | 2.4987 |  |  |  | Option 2
| Total benefits 10% higher |  | 0 | 3.7014 | 2.695 |  |  |  | Option 2
| Total benefits 10% lower |  | 0 | 1.9963 | 1.2318 |  |  |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  | 0 | 1.4286 | 0.69653 |  |  |  | Option 2
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
CitiPower
AR switchboard and relay replacement
Project
|  | Business: |  | CitiPower
|  | Descripton: |  | AR switchboard and relay replacement
|  | Date of cost inputs: |  | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Combined replacement of SWBD (i.e. all three buses) and relays completed in 2027-28
|  | Option 3 |  | Relay replacement completed in 2027-28 and SWBD replacement completed in 2032-33
Option 4
Option 5
|  | Compliance project |  | No
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | AR |  | Armadale | 35599.4556 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 0 | 2023-12-31 | per MWh
|  | Network resilience |  |  |  | 0 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 4220.9954 | 2023-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
CitiPower
AR switchboard and relay replacement
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 35599.4556 | 2023-12-31 |  | 336084.8207 | 346315.3522 | 358493.5229 | 372893.2114 | 387162.4958 | 403655.2694 | 423752.4956 | 446271.5003 | 464664.8555 | 480442.7533 | 497877.9541 | 517182.2618 | 538603.2748 | 562432.239 | 589013.9187 | 618759.0418 | 652160.0327 | 689810.9524 | 732432.8238 | 780905.7795 | 836310.0091 | 899978.8305 | 973565.0515 | 1059126.9404 | 1159238.0759
| Safety risk | (after DF) |  | 2023-12-31 |  | 2050.4006 | 2194.2917 | 2351.153 | 2522.8295 | 2714.8681 | 2925.2007 | 3156.6006 | 3420.2583 | 3716.2647 | 4049.1464 | 4427.0381 | 4863.7394 | 5375.3855 | 5984.9643 | 6728.1393 | 7658.4479 | 8857.1693 | 10448.8102 | 12625.4494 | 15094.1632 | 16161.611 | 17393.6994 | 18827.3014 | 20510.1239 | 22504.379
| Unplanned replacement |  |  | 2023-12-31 |  | 68452.023 | 72738.2368 | 77410.5792 | 82510.4565 | 88114.0108 | 94233.4536 | 100920.3994 | 108246.879 | 116269.8114 | 125060.4296 | 134703.5361 | 145300.0645 | 156966.3844 | 169842.2074 | 184101.2635 | 199963.654 | 217716.2217 | 237743.7476 | 260577.0714 | 285874.3463 | 310731.7128 | 338311.069 | 368986.6932 | 403202.9757 | 441491.5055
| Unplanned fault | (after DF) |  | 2023-12-31 |  | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8
| Environmental risk |  |  | 2023-12-31 |  | 128.9099 | 139.288 | 150.6 | 162.9701 | 176.7421 | 191.8129 | 208.435 | 228.0291 | 250.4296 | 276.0708 | 305.8649 | 341.4864 | 384.8949 | 438.9628 | 508.2839 | 599.8916 | 724.6312 | 899.3189 | 1150.143 | 1434.7455 | 1513.1522 | 1604.4572 | 1711.8714 | 1839.6554 | 1993.5088
| < Other risk - enter description > |  |  | 2023-12-31
| Total risk cost |  |  |  |  | 407147.9543 | 421818.9687 | 438837.6551 | 458521.2675 | 478599.9167 | 501437.5365 | 528469.7306 | 558598.4667 | 585333.1612 | 610260.2001 | 637746.1932 | 668119.3522 | 701761.7397 | 739130.1734 | 780783.4054 | 827412.8353 | 879889.855 | 939334.6291 | 1007217.2876 | 1083740.8344 | 1165148.2851 | 1257719.8561 | 1363522.7175 | 1485111.4954 | 1625659.2692
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
CitiPower
AR switchboard and relay replacement
OPTION 2 | Combined replacement of SWBD (i.e. all three buses) and relays completed in 2027-28
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Switchboard |  | 50 | 2023-12-31 | 3110255.2472 | 1555127.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Relays |  | 25 | 2023-12-31 | 2073503.4982 | 1036751.7491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 5183758.7454 | 2591879.3727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 35599.4556 | 2023-12-31 | 336084.8207 | 346315.3522 | 30310.2977 | 30989.8721 | 31522.7969 | 32204.9794 | 33185.6685 | 34312.5741 | 34803.6491 | 34817.1755 | 34831.8165 | 34847.6667 | 34864.829 | 34883.4159 | 34903.5499 | 34925.3648 | 34949.0068 | 34974.6361 | 35002.4287 | 35047.7135 | 35110.3841 | 35187.0324 | 35282.2673 | 35402.3323 | 35556.501
| Safety risk | (after DF) |  | 2023-12-31 | 2050.4006 | 2194.2917 | 838.2455 | 862.252 | 888.3643 | 916.7734 | 947.6881 | 981.3361 | 1017.9668 | 1058.6903 | 1112.8121 | 1178.2774 | 1257.1584 | 1354.7676 | 1481.6417 | 1650.1209 | 1878.7531 | 2197.9738 | 2655.1262 | 3416.69 | 4596.3321 | 6353.0907 | 8408.0385 | 9089.996 | 9999.068
| Unplanned replacement |  |  | 2023-12-31 | 68452.023 | 72738.2368 | 6820.1262 | 7140.6845 | 7487.8071 | 7863.7784 | 8271.0845 | 8712.4306 | 9190.7613 | 9710.832 | 10292.8003 | 10936.0605 | 11647.9258 | 12442.0111 | 13339.7656 | 14368.5535 | 15568.098 | 16999.3978 | 18754.9489 | 21073.1482 | 24170.9965 | 28365.7466 | 33124.0529 | 35326.6702 | 37893.5276
| Unplanned fault | (after DF) |  | 2023-12-31 | 431.8 | 431.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8
| Environmental risk |  |  | 2023-12-31 | 128.9099 | 139.288 | 107.7807 | 110.7663 | 114.0165 | 117.5555 | 121.4097 | 125.608 | 130.1822 | 135.2849 | 142.2236 | 150.7042 | 161.0139 | 173.8962 | 190.8304 | 213.5497 | 244.6614 | 288.4478 | 351.5737 | 457.4756 | 622.165 | 868.0515 | 1155.8056 | 1249.8673 | 1375.7353
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 407147.9543 | 421818.9687 | 38127.2501 | 39154.3748 | 40063.7848 | 41153.8867 | 42576.6507 | 44182.7488 | 45193.3595 | 45772.7827 | 46430.4526 | 47163.5087 | 47981.727 | 48904.8908 | 49966.5876 | 51208.3889 | 52691.3193 | 54511.2555 | 56814.8775 | 60045.8273 | 64550.6777 | 70824.7212 | 78020.9643 | 81119.6658 | 84875.6319
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - residential | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - business | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex saving |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 400710.405 | 419366.8927 | 438536.132 | 460283.6498 | 485893.0799 | 514415.7179 | 540139.8017 | 564487.4174 | 591315.7406 | 620955.8434 | 653780.0126 | 690225.2827 | 730816.8177 | 776204.4464 | 827198.5357 | 884823.3736 | 950402.4101 | 1023695.0071 | 1100597.6074 | 1186895.1349 | 1285501.7532 | 1403991.8296 | 1540783.6373
Capital expenditure
| Switchboard |  |  | 2023-12-31 | -3110255.2472 | -1555127.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Relays |  |  | 2023-12-31 | -2073503.4982 | -1036751.7491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Switchboard |  |  | 2023-12-31 | -3110255.2472 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709 | -4665382.8709
| Relays |  |  | 2023-12-31 | -2073503.4982 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Switchboard |  |  | 2023-12-31 | 0 | -132601.7189 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783 | -198902.5783
| Annualised capex - Relays |  |  | 2023-12-31 | 0 | -125807.8247 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -258409.5436 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153
| Annualised capex |  |  | 2023-12-31 | 0 | -258409.5436 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 400710.405 | 419366.8927 | 438536.132 | 460283.6498 | 485893.0799 | 514415.7179 | 540139.8017 | 564487.4174 | 591315.7406 | 620955.8434 | 653780.0126 | 690225.2827 | 730816.8177 | 776204.4464 | 827198.5357 | 884823.3736 | 950402.4101 | 1023695.0071 | 1100597.6074 | 1186895.1349 | 1285501.7532 | 1403991.8296 | 1540783.6373
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | -258409.5436 | 13096.0896 | 31752.5774 | 50921.8166 | 72669.3345 | 98278.7646 | 126801.4025 | 152525.4863 | 176873.1021 | 203701.4253 | 233341.5281 | 266165.6973 | 302610.9673 | 343202.5024 | 388590.131 | 439584.2203 | 497209.0582 | 562788.0947 | 636080.6918 | 712983.292 | 799280.8196 | 897887.4379 | 1016377.5142 | 1153169.322
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | -258409.5436 | 13096.0896 | 31752.5774 | 50921.8166 | 72669.3345 | 98278.7646 | 126801.4025 | 152525.4863 | 176873.1021 | 203701.4253 | 233341.5281 | 266165.6973 | 302610.9673 | 343202.5024 | 388590.131 | 439584.2203 | 497209.0582 | 562788.0947 | 636080.6918 | 712983.292 | 799280.8196 | 897887.4379 | 1016377.5142 | 1153169.322
| Total annualised capex |  |  |  | 0 | -258409.5436 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153 | -387614.3153
| Total benefits |  |  |  | 0 | 0 | 400710.405 | 419366.8927 | 438536.132 | 460283.6498 | 485893.0799 | 514415.7179 | 540139.8017 | 564487.4174 | 591315.7406 | 620955.8434 | 653780.0126 | 690225.2827 | 730816.8177 | 776204.4464 | 827198.5357 | 884823.3736 | 950402.4101 | 1023695.0071 | 1100597.6074 | 1186895.1349 | 1285501.7532 | 1403991.8296 | 1540783.6373
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | -284250.4979 | -25665.3419 | -7008.8542 | 12160.3851 | 33907.9029 | 59517.3331 | 88039.971 | 113764.0548 | 138111.6706 | 164939.9937 | 194580.0966 | 227404.2658 | 263849.5358 | 304441.0709 | 349828.6995 | 400822.7888 | 458447.6267 | 524026.6632 | 597319.2602 | 674221.8605 | 760519.388 | 859126.0063 | 977616.0827 | 1114407.8904
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | -232568.5892 | 51857.5212 | 70514.0089 | 89683.2482 | 111430.766 | 137040.1961 | 165562.8341 | 191286.9179 | 215634.5336 | 242462.8568 | 272102.9596 | 304927.1288 | 341372.3989 | 381963.9339 | 427351.5626 | 478345.6518 | 535970.4898 | 601549.5263 | 674842.1233 | 751744.7236 | 838042.2511 | 936648.8694 | 1055138.9458 | 1191930.7535
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | -258409.5436 | 53167.1301 | 73689.2666 | 94775.4298 | 118697.6995 | 146868.0726 | 178242.9743 | 206539.4665 | 233321.8439 | 262832.9993 | 295437.1124 | 331543.6986 | 371633.4956 | 416284.1842 | 466210.5757 | 522304.0739 | 585691.3956 | 657828.3358 | 738450.1925 | 823043.0528 | 917970.333 | 1026437.6132 | 1156776.6972 | 1307247.6857
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | -258409.5436 | -26974.9509 | -10184.1119 | 7068.2034 | 26640.9695 | 49689.4566 | 75359.8308 | 98511.5062 | 120424.3604 | 144569.8512 | 171245.9437 | 200787.696 | 233588.4391 | 270120.8206 | 310969.6864 | 356864.3667 | 408726.7209 | 467747.8537 | 533711.1911 | 602923.5313 | 680591.3061 | 769337.2626 | 875978.3313 | 999090.9582
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | -284250.4979 | -65736.3824 | -48945.5434 | -31693.2281 | -12120.462 | 10928.0251 | 36598.3992 | 59750.0746 | 81662.9288 | 105808.4197 | 132484.5122 | 162026.2645 | 194827.0075 | 231359.3891 | 272208.2549 | 318102.9352 | 369965.2893 | 428986.4222 | 494949.7595 | 564162.0998 | 641829.8745 | 730575.831 | 837216.8998 | 960329.5267
sens | 0 | 0% | 0% | Option 2sens | 0 | -258409.5436 | 13096.0896 | 31752.5774 | 50921.8166 | 72669.3345 | 98278.7646 | 126801.4025 | 152525.4863 | 176873.1021 | 203701.4253 | 233341.5281 | 266165.6973 | 302610.9673 | 343202.5024 | 388590.131 | 439584.2203 | 497209.0582 | 562788.0947 | 636080.6918 | 712983.292 | 799280.8196 | 897887.4379 | 1016377.5142 | 1153169.322
sens | 0 | 0% | 0% | Option 2sens | 0 | -258409.5436 | 13096.0896 | 31752.5774 | 50921.8166 | 72669.3345 | 98278.7646 | 126801.4025 | 152525.4863 | 176873.1021 | 203701.4253 | 233341.5281 | 266165.6973 | 302610.9673 | 343202.5024 | 388590.131 | 439584.2203 | 497209.0582 | 562788.0947 | 636080.6918 | 712983.292 | 799280.8196 | 897887.4379 | 1016377.5142 | 1153169.322
sens | 0 | 0% | 0% | Option 2sens | 0 | -258409.5436 | 13096.0896 | 31752.5774 | 50921.8166 | 72669.3345 | 98278.7646 | 126801.4025 | 152525.4863 | 176873.1021 | 203701.4253 | 233341.5281 | 266165.6973 | 302610.9673 | 343202.5024 | 388590.131 | 439584.2203 | 497209.0582 | 562788.0947 | 636080.6918 | 712983.292 | 799280.8196 | 897887.4379 | 1016377.5142 | 1153169.322

## Option3
CitiPower
AR switchboard and relay replacement
OPTION 3 | Relay replacement completed in 2027-28 and SWBD replacement completed in 2032-33
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Switchboard |  | 50 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 4147006.9963 | 2073503.4982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Relays |  | 25 | 2023-12-31 | 2073503.4982 | 1036751.7491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 2073503.4982 | 1036751.7491 | 0 | 0 | 0 | 4147006.9963 | 2073503.4982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 35599.4556 | 2023-12-31 | 336084.8207 | 346315.3522 | 257660.3495 | 263405.6458 | 267892.328 | 273649.0559 | 281951.2543 | 34312.5741 | 34803.6491 | 34817.1755 | 34831.8165 | 34847.6667 | 34864.829 | 34883.4159 | 34903.5499 | 34925.3648 | 34949.0068 | 34974.6361 | 35002.4287 | 35047.7135 | 35110.3841 | 35187.0324 | 35282.2673 | 35402.3323 | 35556.501
| Safety risk | (after DF) |  | 2023-12-31 | 2050.4006 | 2194.2917 | 1104.4628 | 1128.4693 | 1154.5816 | 1182.9908 | 1213.9054 | 981.3361 | 1017.9668 | 1058.6903 | 1112.8121 | 1178.2774 | 1257.1584 | 1354.7676 | 1481.6417 | 1650.1209 | 1878.7531 | 2197.9738 | 2655.1262 | 3416.69 | 4596.3321 | 6353.0907 | 8408.0385 | 9089.996 | 9999.068
| Unplanned replacement |  |  | 2023-12-31 | 68452.023 | 72738.2368 | 22724.8405 | 23045.3988 | 23392.5214 | 23768.4928 | 24175.7988 | 8712.4306 | 9190.7613 | 9710.832 | 10292.8003 | 10936.0605 | 11647.9258 | 12442.0111 | 13339.7656 | 14368.5535 | 15568.098 | 16999.3978 | 18754.9489 | 21073.1482 | 24170.9965 | 28365.7466 | 33124.0529 | 35326.6702 | 37893.5276
| Unplanned fault |  |  | 2023-12-31 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8
| Environmental risk |  |  | 2023-12-31 | 128.9099 | 139.288 | 107.7807 | 110.7663 | 114.0165 | 117.5555 | 121.4097 | 125.608 | 130.1822 | 135.2849 | 142.2236 | 150.7042 | 161.0139 | 173.8962 | 190.8304 | 213.5497 | 244.6614 | 288.4478 | 351.5737 | 457.4756 | 622.165 | 868.0515 | 1155.8056 | 1249.8673 | 1375.7353
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 407147.9543 | 421818.9687 | 282029.2336 | 288122.0803 | 292985.2475 | 299149.8948 | 307894.1682 | 44182.7488 | 45193.3595 | 45772.7827 | 46430.4526 | 47163.5087 | 47981.727 | 48904.8908 | 49966.5876 | 51208.3889 | 52691.3193 | 54511.2555 | 56814.8775 | 60045.8273 | 64550.6777 | 70824.7212 | 78020.9643 | 81119.6658 | 84875.6319
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex saving |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 156808.4215 | 170399.1873 | 185614.6692 | 202287.6417 | 220575.5625 | 514415.7179 | 540139.8017 | 564487.4174 | 591315.7406 | 620955.8434 | 653780.0126 | 690225.2827 | 730816.8177 | 776204.4464 | 827198.5357 | 884823.3736 | 950402.4101 | 1023695.0071 | 1100597.6074 | 1186895.1349 | 1285501.7532 | 1403991.8296 | 1540783.6373
Capital expenditure
| Switchboard |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | -4147006.9963 | -2073503.4982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Relays |  |  | 2023-12-31 | -2073503.4982 | -1036751.7491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Switchboard |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | -4147006.9963 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945 | -6220510.4945
| Relays |  |  | 2023-12-31 | -2073503.4982 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472 | -3110255.2472
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Switchboard |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | -176802.2919 | -265203.4378 | -265203.4378 | -265203.4378 | -265203.4378 | -265203.4378 | -265203.4378 | -265203.4378 | -265203.4378 | -265203.4378 | -265203.4378 | -265203.4378 | -265203.4378 | -265203.4378 | -265203.4378 | -265203.4378 | -265203.4378 | -265203.4378 | -265203.4378
| Annualised capex - Relays |  |  | 2023-12-31 | 0 | -125807.8247 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -188711.737
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -125807.8247 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -365514.0289 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748
| Annualised capex |  |  | 2023-12-31 | 0 | -125807.8247 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -365514.0289 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 156808.4215 | 170399.1873 | 185614.6692 | 202287.6417 | 220575.5625 | 514415.7179 | 540139.8017 | 564487.4174 | 591315.7406 | 620955.8434 | 653780.0126 | 690225.2827 | 730816.8177 | 776204.4464 | 827198.5357 | 884823.3736 | 950402.4101 | 1023695.0071 | 1100597.6074 | 1186895.1349 | 1285501.7532 | 1403991.8296 | 1540783.6373
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | -125807.8247 | -31903.3155 | -18312.5497 | -3097.0678 | 13575.9047 | -144938.4664 | 60500.5431 | 86224.6269 | 110572.2427 | 137400.5658 | 167040.6686 | 199864.8378 | 236310.1079 | 276901.643 | 322289.2716 | 373283.3609 | 430908.1988 | 496487.2353 | 569779.8323 | 646682.4326 | 732979.9601 | 831586.5784 | 950076.6548 | 1086868.4625
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | -125807.8247 | -31903.3155 | -18312.5497 | -3097.0678 | 13575.9047 | -144938.4664 | 60500.5431 | 86224.6269 | 110572.2427 | 137400.5658 | 167040.6686 | 199864.8378 | 236310.1079 | 276901.643 | 322289.2716 | 373283.3609 | 430908.1988 | 496487.2353 | 569779.8323 | 646682.4326 | 732979.9601 | 831586.5784 | 950076.6548 | 1086868.4625
| Total annualised capex |  |  |  | 0 | -125807.8247 | -188711.737 | -188711.737 | -188711.737 | -188711.737 | -365514.0289 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748 | -453915.1748
| Total benefits |  |  |  | 0 | 0 | 156808.4215 | 170399.1873 | 185614.6692 | 202287.6417 | 220575.5625 | 514415.7179 | 540139.8017 | 564487.4174 | 591315.7406 | 620955.8434 | 653780.0126 | 690225.2827 | 730816.8177 | 776204.4464 | 827198.5357 | 884823.3736 | 950402.4101 | 1023695.0071 | 1100597.6074 | 1186895.1349 | 1285501.7532 | 1403991.8296 | 1540783.6373
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | -138388.6071 | -50774.4892 | -37183.7235 | -21968.2415 | -5295.269 | -181489.8693 | 15109.0256 | 40833.1094 | 65180.7252 | 92009.0483 | 121649.1512 | 154473.3204 | 190918.5904 | 231510.1255 | 276897.7541 | 327891.8434 | 385516.6813 | 451095.7178 | 524388.3148 | 601290.9151 | 687588.4426 | 786195.061 | 904685.1373 | 1041476.945
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | -113227.0422 | -13032.1418 | 558.624 | 15774.1059 | 32447.0784 | -108387.0635 | 105892.0606 | 131616.1444 | 155963.7601 | 182792.0833 | 212432.1861 | 245256.3553 | 281701.6254 | 322293.1604 | 367680.7891 | 418674.8783 | 476299.7163 | 541878.7528 | 615171.3498 | 692073.9501 | 778371.4776 | 876978.0959 | 995468.1723 | 1132259.98
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | -125807.8247 | -16222.4733 | -1272.631 | 15464.3991 | 33804.6689 | -122880.9102 | 111942.1149 | 140238.6071 | 167020.9844 | 196532.1399 | 229136.253 | 265242.8391 | 305332.6362 | 349983.3247 | 399909.7162 | 456003.2144 | 519390.5361 | 591527.4763 | 672149.333 | 756742.1933 | 851669.4736 | 960136.7538 | 1090475.8378 | 1240946.8262
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | -125807.8247 | -47584.1576 | -35352.4685 | -21658.5347 | -6652.8595 | -166996.0226 | 9058.9713 | 32210.6467 | 54123.5009 | 78268.9918 | 104945.0843 | 134486.8366 | 167287.5796 | 203819.9612 | 244668.827 | 290563.5073 | 342425.8614 | 401446.9943 | 467410.3316 | 536622.6719 | 614290.4466 | 703036.4031 | 809677.4718 | 932790.0988
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | -138388.6071 | -66455.3313 | -54223.6422 | -40529.7084 | -25524.0332 | -203547.4255 | -36332.5462 | -13180.8708 | 8731.9834 | 32877.4743 | 59553.5668 | 89095.3191 | 121896.0621 | 158428.4437 | 199277.3095 | 245171.9898 | 297034.344 | 356055.4768 | 422018.8141 | 491231.1544 | 568898.9291 | 657644.8856 | 764285.9544 | 887398.5813
sens | 0 | 0% | 0% | Option 3sens | 0 | -125807.8247 | -31903.3155 | -18312.5497 | -3097.0678 | 13575.9047 | -144938.4664 | 60500.5431 | 86224.6269 | 110572.2427 | 137400.5658 | 167040.6686 | 199864.8378 | 236310.1079 | 276901.643 | 322289.2716 | 373283.3609 | 430908.1988 | 496487.2353 | 569779.8323 | 646682.4326 | 732979.9601 | 831586.5784 | 950076.6548 | 1086868.4625
sens | 0 | 0% | 0% | Option 3sens | 0 | -125807.8247 | -31903.3155 | -18312.5497 | -3097.0678 | 13575.9047 | -144938.4664 | 60500.5431 | 86224.6269 | 110572.2427 | 137400.5658 | 167040.6686 | 199864.8378 | 236310.1079 | 276901.643 | 322289.2716 | 373283.3609 | 430908.1988 | 496487.2353 | 569779.8323 | 646682.4326 | 732979.9601 | 831586.5784 | 950076.6548 | 1086868.4625
sens | 0 | 0% | 0% | Option 3sens | 0 | -125807.8247 | -31903.3155 | -18312.5497 | -3097.0678 | 13575.9047 | -144938.4664 | 60500.5431 | 86224.6269 | 110572.2427 | 137400.5658 | 167040.6686 | 199864.8378 | 236310.1079 | 276901.643 | 322289.2716 | 373283.3609 | 430908.1988 | 496487.2353 | 569779.8323 | 646682.4326 | 732979.9601 | 831586.5784 | 950076.6548 | 1086868.4625

## Option4
CitiPower
AR switchboard and relay replacement
OPTION 4 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 35599.4556 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option5
CitiPower
AR switchboard and relay replacement
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 35599.4556 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
CitiPower
AR switchboard and relay replacement
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 10325736.7224 | 2026-06-30 |  | 374033.0472 | 385418.7351 | 398971.9753 | 414997.5708 | 430878.0378 | 449233.0542 | 471599.5113 | 496661.1964 | 517131.394 | 534690.8161 | 554094.6715 | 575578.6797 | 599418.3959 | 625937.9515 | 655521.0391 | 688624.7627 | 725797.1479 | 767699.3325 | 815133.7523 | 869079.9176 | 930739.9854 | 1001597.822 | 1083492.8579 | 1178715.7662 | 1290130.7149
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 10062231.0025 | 2026-06-30 |  | 453120.1073 | 469447.6648 | 488387.9761 | 510294.1173 | 532639.8999 | 558056.1758 | 588140.6464 | 621671.2979 | 651424.6774 | 679166.2943 | 709755.8036 | 743558.4763 | 780999.5148 | 822587.3174 | 868943.7259 | 920838.2082 | 979240.5471 | 1045397.3879 | 1120944.857 | 1206108.88 | 1296708.2615 | 1399732.3335 | 1517481.676 | 1652799.3646 | 1809216.7595
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 1294597.3088 | 2026-06-30 |  | 374033.0472 | 385418.7351 | 33732.7137 | 34489.0205 | 35082.1194 | 35841.3289 | 36932.7501 | 38186.8976 | 38733.4213 | 38748.4749 | 38764.7691 | 38782.409 | 38801.5091 | 38822.1947 | 38844.6021 | 38868.8802 | 38895.1917 | 38923.7148 | 38954.6456 | 39005.0436 | 39074.7905 | 39160.0934 | 39266.0815 | 39399.7033 | 39571.2796
Option 2 | Capital expenditure | Option 2Capital expenditure | -8410149.4558 | 2026-06-30 |  | -5769070.6637 | -2884535.3319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 1536649.5054 | 2026-06-30 |  | 453120.1073 | 469447.6648 | 42432.2988 | 43575.3989 | 44587.4927 | 45800.681 | 47384.093 | 49171.5399 | 50296.2613 | 50941.1087 | 51673.0378 | 52488.8653 | 53399.4708 | 54426.8714 | 55608.4473 | 56990.4637 | 58640.8356 | 60666.2657 | 63229.9956 | 66825.7605 | 0 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -5676741.9816 | 2026-06-30 |  | 0 | -287587.249 | -431380.8735 | -431380.8735 | -431380.8735 | -431380.8735 | -431380.8735 | -431380.8735 | -431380.8735 | -431380.8735 | -431380.8735 | -431380.8735 | -431380.8735 | -431380.8735 | -431380.8735 | -431380.8735 | -431380.8735 | -431380.8735 | -431380.8735 | -431380.8735 | 0 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 8525581.497 | 2026-06-30 |  | 0 | 0 | 445955.6772 | 466718.7184 | 488052.4072 | 512255.4948 | 540756.5535 | 572499.758 | 601128.4161 | 628225.1856 | 658082.7657 | 691069.611 | 727600.044 | 768160.446 | 813335.2787 | 863847.7446 | 920599.7114 | 984731.1223 | 1057714.8614 | 1139283.1195 | 0 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | -287587.249 | 14574.8038 | 35337.8449 | 56671.5337 | 80874.6213 | 109375.68 | 141118.8845 | 169747.5426 | 196844.3121 | 226701.8923 | 259688.7375 | 296219.1706 | 336779.5725 | 381954.4052 | 432466.8711 | 489218.8379 | 553350.2488 | 626333.9879 | 707902.246 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 2848839.5155 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -5676741.9816 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 8525581.497 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 2425179.9441 | 2026-06-30 |  | 374033.0472 | 385418.7351 | 286753.4614 | 293147.4744 | 298140.7597 | 304547.4949 | 313787.1166 | 38186.8976 | 38733.4213 | 38748.4749 | 38764.7691 | 38782.409 | 38801.5091 | 38822.1947 | 38844.6021 | 38868.8802 | 38895.1917 | 38923.7148 | 38954.6456 | 39005.0436 | 39074.7905 | 39160.0934 | 39266.0815 | 39399.7033 | 39571.2796
Option 3 | Capital expenditure | Option 3Capital expenditure | -9028955.9192 | 2026-06-30 |  | -2307628.2655 | -1153814.1327 | 0 | 0 | 0 | -4615256.531 | -2307628.2655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 2746220.3067 | 2026-06-30 |  | 453120.1073 | 469447.6648 | 313873.9007 | 320654.7068 | 326066.9872 | 332927.7011 | 342659.3135 | 49171.5399 | 50296.2613 | 50941.1087 | 51673.0378 | 52488.8653 | 53399.4708 | 54426.8714 | 55608.4473 | 56990.4637 | 58640.8356 | 60666.2657 | 63229.9956 | 66825.7605 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -5352621.5379 | 2026-06-30 |  | 0 | -140013.1191 | -210019.6786 | -210019.6786 | -210019.6786 | -210019.6786 | -406785.1852 | -505167.9384 | -505167.9384 | -505167.9384 | -505167.9384 | -505167.9384 | -505167.9384 | -505167.9384 | -505167.9384 | -505167.9384 | -505167.9384 | -505167.9384 | -505167.9384 | -505167.9384 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 7316010.6957 | 2026-06-30 |  | 0 | 0 | 174514.0754 | 189639.4104 | 206572.9127 | 225128.4747 | 245481.3329 | 572499.758 | 601128.4161 | 628225.1856 | 658082.7657 | 691069.611 | 727600.044 | 768160.446 | 813335.2787 | 863847.7446 | 920599.7114 | 984731.1223 | 1057714.8614 | 1139283.1195 | 0 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | -140013.1191 | -35505.6033 | -20380.2682 | -3446.7659 | 15108.796 | -161303.8522 | 67331.8195 | 95960.4777 | 123057.2472 | 152914.8273 | 185901.6726 | 222432.1056 | 262992.5075 | 308167.3403 | 358679.8062 | 415431.773 | 479563.1839 | 552546.923 | 634115.1811 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | 1963389.1578 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -5352621.5379 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 7316010.6957 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 0 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | 0 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 0 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0.43138 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 0.45312 | 0.46945 | 0.48839 | 0.51029 | 0.53264 | 0.55806 | 0.58814 | 0.62167 | 0.65142 | 0.67917 | 0.70976 | 0.74356 | 0.781 | 0.82259 | 0.86894 | 0.92084 | 0.97924 | 1.0454 | 1.1209 | 1.2061 | 1.2967 | 1.3997 | 1.5175 | 1.6528 | 1.8092
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 0 |  |  | Energy at risk energy at risk (weighted) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Energy at risk value | 1.1592 |  |  | Option 1 (base case) risk cost | 0.33608 | 0.34632 | 0.35849 | 0.37289 | 0.38716 | 0.40366 | 0.42375 | 0.44627 | 0.46466 | 0.48044 | 0.49788 | 0.51718 | 0.5386 | 0.56243 | 0.58901 | 0.61876 | 0.65216 | 0.68981 | 0.73243 | 0.78091 | 0.83631 | 0.89998 | 0.97357 | 1.0591 | 1.1592

## Sensitivity_calcs
CitiPower
AR switchboard and relay replacement
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
[7 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 626333.9879 | 707902.246 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 2848839.5155 |  | 0 | 0 | -287587.249 | 14574.8038 | 35337.8449 | 56671.5337 | 80874.6213 | 109375.68 | 141118.8845 | 169747.5426 | 196844.3121 | 226701.8923 | 259688.7375 | 296219.1706 | 336779.5725 | 381954.4052 | 432466.8711 | 489218.8379 | 553350.2488 | 626333.9879 | 707902.246 | 0 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 2281165.3173 |  | 0 | 0 | -316345.9739 | -28563.2836 | -7800.2424 | 13533.4464 | 37736.534 | 66237.5927 | 97980.7971 | 126609.4553 | 153706.2248 | 183563.8049 | 216550.6502 | 253081.0832 | 293641.4851 | 338816.3179 | 389328.7838 | 446080.7506 | 510212.1615 | 583195.9006 | 664764.1587 | 0 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 3416513.7136 |  | 0 | 0 | -258828.5241 | 57712.8911 | 78475.9323 | 99809.6211 | 124012.7087 | 152513.7674 | 184256.9718 | 212885.63 | 239982.3995 | 269839.9796 | 302826.8249 | 339357.2579 | 379917.6598 | 425092.4926 | 475604.9585 | 532356.9253 | 596488.3362 | 669472.0752 | 751040.3334 | 0 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 3701397.6652 |  | 0 | 0 | -287587.249 | 59170.3715 | 82009.7168 | 105476.7744 | 132100.1708 | 163451.3354 | 198368.8603 | 229860.3842 | 259666.8307 | 292510.1688 | 328795.6986 | 368979.175 | 413595.6171 | 463287.9331 | 518851.6456 | 581278.8091 | 651823.361 | 732105.474 | 821830.558 | 0 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 1996281.3658 |  | 0 | 0 | -287587.249 | -30020.764 | -11334.0269 | 7866.293 | 29649.0719 | 55300.0247 | 83868.9087 | 109634.701 | 134021.7936 | 160893.6157 | 190581.7764 | 223459.1662 | 259963.5279 | 300620.8773 | 346082.0967 | 397158.8668 | 454877.1366 | 520562.5018 | 593973.9341 | 0 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 1428607.1676 |  | 0 | 0 | -316345.9739 | -73158.8513 | -54472.1143 | -35271.7944 | -13489.0155 | 12161.9373 | 40730.8213 | 66496.6137 | 90883.7062 | 117755.5284 | 147443.6891 | 180321.0788 | 216825.4405 | 257482.79 | 302944.0093 | 354020.7795 | 411739.0492 | 477424.4144 | 550835.8467 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 2848839.5155 |  | 0 | 0 | -287587.249 | 14574.8038 | 35337.8449 | 56671.5337 | 80874.6213 | 109375.68 | 141118.8845 | 169747.5426 | 196844.3121 | 226701.8923 | 259688.7375 | 296219.1706 | 336779.5725 | 381954.4052 | 432466.8711 | 489218.8379 | 553350.2488 | 626333.9879 | 707902.246 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 2848839.5155 |  | 0 | 0 | -287587.249 | 14574.8038 | 35337.8449 | 56671.5337 | 80874.6213 | 109375.68 | 141118.8845 | 169747.5426 | 196844.3121 | 226701.8923 | 259688.7375 | 296219.1706 | 336779.5725 | 381954.4052 | 432466.8711 | 489218.8379 | 553350.2488 | 626333.9879 | 707902.246 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 2848839.5155 |  | 0 | 0 | -287587.249 | 14574.8038 | 35337.8449 | 56671.5337 | 80874.6213 | 109375.68 | 141118.8845 | 169747.5426 | 196844.3121 | 226701.8923 | 259688.7375 | 296219.1706 | 336779.5725 | 381954.4052 | 432466.8711 | 489218.8379 | 553350.2488 | 626333.9879 | 707902.246 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | -140013.1191 | -35505.6033 | -20380.2682 | -3446.7659 | 15108.796 | -161303.8522 | 67331.8195 | 95960.4777 | 123057.2472 | 152914.8273 | 185901.6726 | 222432.1056 | 262992.5075 | 308167.3403 | 358679.8062 | 415431.773 | 479563.1839 | 552546.923 | 634115.1811 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 1963389.1578 |  | 0 | 0 | -140013.1191 | -35505.6033 | -20380.2682 | -3446.7659 | 15108.796 | -161303.8522 | 67331.8195 | 95960.4777 | 123057.2472 | 152914.8273 | 185901.6726 | 222432.1056 | 262992.5075 | 308167.3403 | 358679.8062 | 415431.773 | 479563.1839 | 552546.923 | 634115.1811 | 0 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 1428127.0041 |  | 0 | 0 | -154014.431 | -56507.5711 | -41382.2361 | -24448.7338 | -5893.1719 | -201982.3707 | 16815.0257 | 45443.6838 | 72540.4534 | 102398.0335 | 135384.8788 | 171915.3118 | 212475.7137 | 257650.5464 | 308163.0123 | 364914.9792 | 429046.39 | 502030.1291 | 583598.3872 | 0 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 2498651.3116 |  | 0 | 0 | -126011.8072 | -14503.6354 | 621.6997 | 17555.2019 | 36110.7639 | -120625.3337 | 117848.6134 | 146477.2715 | 173574.041 | 203431.6212 | 236418.4664 | 272948.8995 | 313509.3014 | 358684.1341 | 409196.6 | 465948.5668 | 530079.9777 | 603063.7168 | 684631.9749 | 0 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 2694990.2274 |  | 0 | 0 | -140013.1191 | -18054.1957 | -1416.3272 | 17210.5254 | 37621.6435 | -136755.7189 | 124581.7953 | 156073.3193 | 185879.7658 | 218723.1039 | 255008.6337 | 295192.11 | 339808.5521 | 389500.8681 | 445064.5806 | 507491.7441 | 578036.2961 | 658318.4091 | 748043.493 | 0 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | 1231788.0883 |  | 0 | 0 | -140013.1191 | -52957.0108 | -39344.2092 | -24104.0572 | -7404.0515 | -185851.9855 | 10081.8437 | 35847.6361 | 60234.7286 | 87106.5508 | 116794.7115 | 149672.1012 | 186176.463 | 226833.8124 | 272295.0317 | 323371.8019 | 381090.0716 | 446775.4368 | 520186.8691 | 0 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | 696525.9345 |  | 0 | 0 | -154014.431 | -73958.9787 | -60346.1771 | -45106.0251 | -28406.0193 | -226530.504 | -40434.9501 | -14669.1578 | 9717.9348 | 36589.7569 | 66277.9177 | 99155.3074 | 135659.6691 | 176317.0186 | 221778.2379 | 272855.008 | 330573.2778 | 396258.643 | 469670.0753 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 1963389.1578 |  | 0 | 0 | -140013.1191 | -35505.6033 | -20380.2682 | -3446.7659 | 15108.796 | -161303.8522 | 67331.8195 | 95960.4777 | 123057.2472 | 152914.8273 | 185901.6726 | 222432.1056 | 262992.5075 | 308167.3403 | 358679.8062 | 415431.773 | 479563.1839 | 552546.923 | 634115.1811 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 1963389.1578 |  | 0 | 0 | -140013.1191 | -35505.6033 | -20380.2682 | -3446.7659 | 15108.796 | -161303.8522 | 67331.8195 | 95960.4777 | 123057.2472 | 152914.8273 | 185901.6726 | 222432.1056 | 262992.5075 | 308167.3403 | 358679.8062 | 415431.773 | 479563.1839 | 552546.923 | 634115.1811 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 1963389.1578 |  | 0 | 0 | -140013.1191 | -35505.6033 | -20380.2682 | -3446.7659 | 15108.796 | -161303.8522 | 67331.8195 | 95960.4777 | 123057.2472 | 152914.8273 | 185901.6726 | 222432.1056 | 262992.5075 | 308167.3403 | 358679.8062 | 415431.773 | 479563.1839 | 552546.923 | 634115.1811 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 1 | 1 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 2.8488 | 1.9634 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens1 | Capex 10% higher | 0 | 2.2812 | 1.4281 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens2 | Capex 10% lower | 0 | 3.4165 | 2.4987 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens3 | Total benefits 10% higher | 0 | 3.7014 | 2.695 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens4 | Total benefits 10% lower | 0 | 1.9963 | 1.2318 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 1.4286 | 0.69653 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Workings_costs
CitiPower
AR switchboard and relay replacement
WORKINGS - COSTS
Option 1 - continue existing maintenance with no proactive replacement cost
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
SWBD online monitoring annual cost ($)
Relay annual maintenance cost ($)
|  | Total opex cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - Combined replacement of SWBD (i.e. all three buses) and relays completed in 2030-31
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | SWBD capex profile ($) | 3110255.2472 | 1555127.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Relay capex profile ($) | 2073503.4982 | 1036751.7491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total capex ($) | 5183758.7454 | 2591879.3727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
|  | SWBD online monitoring annual cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Relay annual maintenance cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total opex cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Relay replacement completed in 2030-31 and SWBD replacement completed in 2035-36
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | SWBD capex profile ($) | 0 | 0 | 0 | 0 | 0 | 4147006.9963 | 2073503.4982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Relay capex profile ($) | 2073503.4982 | 1036751.7491 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total capex ($) | 2073503.4982 | 1036751.7491 | 0 | 0 | 0 | 4147006.9963 | 2073503.4982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
|  | SWBD online monitoring annual cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Relay annual maintenance cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total opex cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Workings_risks
CitiPower
AR switchboard and relay replacement
WORKINGS - RISKS
Option 1 - continue existing maintenance with no proactive replacement cost
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
SWBD risks
|  | Energy at Risk ($) | 250206.3836 | 253193.4101 | 257471.6793 | 263208.5256 | 267686.0733 | 273432.9245 | 281724.4418 | 291257.8158 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964
|  | Safety Risk | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713
|  | Unplanned Replacement Risk | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429
|  | Unplanned Fault Risk | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8
|  | Total SWBD risks | 268965.2395 | 271952.266 | 276230.5352 | 281967.3815 | 286444.9292 | 292191.7804 | 300483.2976 | 310016.6717 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523
Relay risks
|  | Environment risk ($) | 128.9099 | 139.288 | 150.6 | 162.9701 | 176.7421 | 191.8129 | 208.435 | 228.0291 | 250.4296 | 276.0708 | 305.8649 | 341.4864 | 384.8949 | 438.9628 | 508.2839 | 599.8916 | 724.6312 | 899.3189 | 1150.143 | 1434.7455 | 1513.1522 | 1604.4572 | 1711.8714 | 1839.6554 | 1993.5088
|  | Energy at Risk ($) | 85878.4371 | 93121.9421 | 101021.8436 | 109684.6858 | 119476.4225 | 130222.3449 | 142028.0538 | 155013.6845 | 169316.5591 | 185094.4569 | 202529.6577 | 221833.9654 | 243254.9784 | 267083.9425 | 293665.6223 | 323410.7454 | 356811.7363 | 394462.656 | 437084.5274 | 485557.483 | 540961.7127 | 604630.5341 | 678216.7551 | 763778.644 | 863889.7795
|  | Safety Risk | 1748.6876 | 1892.5787 | 2049.44 | 2221.1165 | 2413.1551 | 2623.4877 | 2854.8876 | 3118.5453 | 3414.5517 | 3747.4335 | 4125.3251 | 4562.0264 | 5073.6726 | 5683.2514 | 6426.4263 | 7356.7349 | 8555.4563 | 10147.0973 | 12323.7364 | 14792.4502 | 15859.898 | 17091.9864 | 18525.5884 | 20208.4109 | 22202.6661
|  | Unplanned Replacement Risk | 50426.6801 | 54712.8939 | 59385.2363 | 64485.1136 | 70088.6679 | 76208.1106 | 82895.0565 | 90221.5361 | 98244.4685 | 107035.0867 | 116678.1931 | 127274.7216 | 138941.0415 | 151816.8645 | 166075.9206 | 181938.3111 | 199690.8788 | 219718.4047 | 242551.7284 | 267849.0033 | 292706.3699 | 320285.7261 | 350961.3503 | 385177.6328 | 423466.1626
|  | Total relay risks | 138182.7148 | 149866.7027 | 162607.1199 | 176553.886 | 192154.9876 | 209245.7562 | 227986.433 | 248581.795 | 271226.0088 | 296153.0478 | 323639.0409 | 354012.1999 | 387654.5873 | 425023.0211 | 466676.2531 | 513305.683 | 565782.7027 | 625227.4768 | 693110.1353 | 769633.6821 | 851041.1328 | 943612.7038 | 1049415.5652 | 1171004.3431 | 1311552.1169
Total SWBD and relay risk
|  | Energy at Risk ($) | 336084.8207 | 346315.3522 | 358493.5229 | 372893.2114 | 387162.4958 | 403655.2694 | 423752.4956 | 446271.5003 | 464664.8555 | 480442.7533 | 497877.9541 | 517182.2618 | 538603.2748 | 562432.239 | 589013.9187 | 618759.0418 | 652160.0327 | 689810.9524 | 732432.8238 | 780905.7795 | 836310.0091 | 899978.8305 | 973565.0515 | 1059126.9404 | 1159238.0759
|  | Safety risk | 2050.4006 | 2194.2917 | 2351.153 | 2522.8295 | 2714.8681 | 2925.2007 | 3156.6006 | 3420.2583 | 3716.2647 | 4049.1464 | 4427.0381 | 4863.7394 | 5375.3855 | 5984.9643 | 6728.1393 | 7658.4479 | 8857.1693 | 10448.8102 | 12625.4494 | 15094.1632 | 16161.611 | 17393.6994 | 18827.3014 | 20510.1239 | 22504.379
|  | Unplanned replacement | 68452.023 | 72738.2368 | 77410.5792 | 82510.4565 | 88114.0108 | 94233.4536 | 100920.3994 | 108246.879 | 116269.8114 | 125060.4296 | 134703.5361 | 145300.0645 | 156966.3844 | 169842.2074 | 184101.2635 | 199963.654 | 217716.2217 | 237743.7476 | 260577.0714 | 285874.3463 | 310731.7128 | 338311.069 | 368986.6932 | 403202.9757 | 441491.5055
|  | Unplanned fault | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8
|  | Environmental risk | 128.9099 | 139.288 | 150.6 | 162.9701 | 176.7421 | 191.8129 | 208.435 | 228.0291 | 250.4296 | 276.0708 | 305.8649 | 341.4864 | 384.8949 | 438.9628 | 508.2839 | 599.8916 | 724.6312 | 899.3189 | 1150.143 | 1434.7455 | 1513.1522 | 1604.4572 | 1711.8714 | 1839.6554 | 1993.5088
|  | Total SWBD and relay risks | 407147.9543 | 421818.9687 | 438837.6551 | 458521.2675 | 478599.9167 | 501437.5365 | 528469.7306 | 558598.4667 | 585333.1612 | 610260.2001 | 637746.1932 | 668119.3522 | 701761.7397 | 739130.1734 | 780783.4054 | 827412.8353 | 879889.855 | 939334.6291 | 1007217.2876 | 1083740.8344 | 1165148.2851 | 1257719.8561 | 1363522.7175 | 1485111.4954 | 1625659.2692
Option 2 - Combined replacement of SWBD (i.e. all three buses) and relays completed in 2027-28
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
SWBD risks
|  | Energy at Risk ($) | 250206.3836 | 253193.4101 | 30121.6275 | 30792.7518 | 31316.5422 | 31988.848 | 32958.8559 | 34074.2079 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831
|  | Safety Risk | 301.713 | 301.713 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956
|  | Unplanned Replacement Risk | 18025.3429 | 18025.3429 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286
|  | Unplanned Fault Risk | 431.8 | 431.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8
|  | Total SWBD risks | 268965.2395 | 271952.266 | 32328.5517 | 32999.676 | 33523.4664 | 34195.7723 | 35165.7802 | 36281.1321 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073
Relay risks
|  | Environment risk ($) | 128.9099 | 139.288 | 107.7807 | 110.7663 | 114.0165 | 117.5555 | 121.4097 | 125.608 | 130.1822 | 135.2849 | 142.2236 | 150.7042 | 161.0139 | 173.8962 | 190.8304 | 213.5497 | 244.6614 | 288.4478 | 351.5737 | 457.4756 | 622.165 | 868.0515 | 1155.8056 | 1249.8673 | 1375.7353
|  | Energy at Risk ($) | 85878.4371 | 93121.9421 | 188.6702 | 197.1202 | 206.2548 | 216.1314 | 226.8125 | 238.3662 | 250.866 | 264.3923 | 279.0334 | 294.8836 | 312.0458 | 330.6327 | 350.7668 | 372.5817 | 396.2237 | 421.853 | 449.6456 | 494.9304 | 557.601 | 634.2493 | 729.4842 | 849.5491 | 1003.7179
|  | Safety Risk | 1748.6876 | 1892.5787 | 802.7498 | 826.7563 | 852.8686 | 881.2778 | 912.1924 | 945.8405 | 982.4712 | 1023.1946 | 1077.3165 | 1142.7817 | 1221.6628 | 1319.272 | 1446.146 | 1614.6253 | 1843.2574 | 2162.4782 | 2619.6305 | 3381.1943 | 4560.8364 | 6317.5951 | 8372.5429 | 9054.5004 | 9963.5724
|  | Unplanned Replacement Risk | 50426.6801 | 54712.8939 | 4699.4976 | 5020.0559 | 5367.1785 | 5743.1498 | 6150.4559 | 6591.802 | 7070.1327 | 7590.2034 | 8172.1717 | 8815.4319 | 9527.2972 | 10321.3825 | 11219.1371 | 12247.9249 | 13447.4694 | 14878.7692 | 16634.3204 | 18952.5196 | 22050.368 | 26245.118 | 31003.4243 | 33206.0417 | 35772.899
|  | Total relay risks | 138182.7148 | 149866.7027 | 5798.6984 | 6154.6988 | 6540.3184 | 6958.1145 | 7410.8705 | 7901.6167 | 8433.6521 | 9013.0753 | 9670.7452 | 10403.8014 | 11222.0197 | 12145.1834 | 13206.8803 | 14448.6816 | 15931.612 | 17751.5482 | 20055.1701 | 23286.1199 | 27790.9704 | 34065.0139 | 41261.2569 | 44359.9585 | 48115.9246
Total SWBD and relay risk
|  | Energy at Risk ($) | 336084.8207 | 346315.3522 | 30310.2977 | 30989.8721 | 31522.7969 | 32204.9794 | 33185.6685 | 34312.5741 | 34803.6491 | 34817.1755 | 34831.8165 | 34847.6667 | 34864.829 | 34883.4159 | 34903.5499 | 34925.3648 | 34949.0068 | 34974.6361 | 35002.4287 | 35047.7135 | 35110.3841 | 35187.0324 | 35282.2673 | 35402.3323 | 35556.501
|  | Safety risk | 2050.4006 | 2194.2917 | 838.2455 | 862.252 | 888.3643 | 916.7734 | 947.6881 | 981.3361 | 1017.9668 | 1058.6903 | 1112.8121 | 1178.2774 | 1257.1584 | 1354.7676 | 1481.6417 | 1650.1209 | 1878.7531 | 2197.9738 | 2655.1262 | 3416.69 | 4596.3321 | 6353.0907 | 8408.0385 | 9089.996 | 9999.068
|  | Unplanned replacement | 68452.023 | 72738.2368 | 6820.1262 | 7140.6845 | 7487.8071 | 7863.7784 | 8271.0845 | 8712.4306 | 9190.7613 | 9710.832 | 10292.8003 | 10936.0605 | 11647.9258 | 12442.0111 | 13339.7656 | 14368.5535 | 15568.098 | 16999.3978 | 18754.9489 | 21073.1482 | 24170.9965 | 28365.7466 | 33124.0529 | 35326.6702 | 37893.5276
|  | Unplanned fault | 431.8 | 431.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8
|  | Environmental risk | 128.9099 | 139.288 | 107.7807 | 110.7663 | 114.0165 | 117.5555 | 121.4097 | 125.608 | 130.1822 | 135.2849 | 142.2236 | 150.7042 | 161.0139 | 173.8962 | 190.8304 | 213.5497 | 244.6614 | 288.4478 | 351.5737 | 457.4756 | 622.165 | 868.0515 | 1155.8056 | 1249.8673 | 1375.7353
|  | Total SWBD and relay risks | 407147.9543 | 421818.9687 | 38127.2501 | 39154.3748 | 40063.7848 | 41153.8867 | 42576.6507 | 44182.7488 | 45193.3595 | 45772.7827 | 46430.4526 | 47163.5087 | 47981.727 | 48904.8908 | 49966.5876 | 51208.3889 | 52691.3193 | 54511.2555 | 56814.8775 | 60045.8273 | 64550.6777 | 70824.7212 | 78020.9643 | 81119.6658 | 84875.6319
Option 3 - Relay replacement completed in 2027-28 and SWBD replacement completed in 2032-33
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
SWBD risks
|  | Energy at Risk ($, Weighted) | 250206.3836 | 253193.4101 | 257471.6793 | 263208.5256 | 267686.0733 | 273432.9245 | 281724.4418 | 34074.2079 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831
|  | Safety Risk | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956
|  | Unplanned Replacement Risk | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286
|  | Unplanned Fault Risk | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8
|  | Total SWBD risks | 268965.2395 | 271952.266 | 276230.5352 | 281967.3815 | 286444.9292 | 292191.7804 | 300483.2976 | 36281.1321 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073 | 36759.7073
Relay risks
|  | Environment risk ($) | 128.9099 | 139.288 | 107.7807 | 110.7663 | 114.0165 | 117.5555 | 121.4097 | 125.608 | 130.1822 | 135.2849 | 142.2236 | 150.7042 | 161.0139 | 173.8962 | 190.8304 | 213.5497 | 244.6614 | 288.4478 | 351.5737 | 457.4756 | 622.165 | 868.0515 | 1155.8056 | 1249.8673 | 1375.7353
|  | Energy at Risk ($) | 85878.4371 | 93121.9421 | 188.6702 | 197.1202 | 206.2548 | 216.1314 | 226.8125 | 238.3662 | 250.866 | 264.3923 | 279.0334 | 294.8836 | 312.0458 | 330.6327 | 350.7668 | 372.5817 | 396.2237 | 421.853 | 449.6456 | 494.9304 | 557.601 | 634.2493 | 729.4842 | 849.5491 | 1003.7179
|  | Safety Risk | 1748.6876 | 1892.5787 | 802.7498 | 826.7563 | 852.8686 | 881.2778 | 912.1924 | 945.8405 | 982.4712 | 1023.1946 | 1077.3165 | 1142.7817 | 1221.6628 | 1319.272 | 1446.146 | 1614.6253 | 1843.2574 | 2162.4782 | 2619.6305 | 3381.1943 | 4560.8364 | 6317.5951 | 8372.5429 | 9054.5004 | 9963.5724
|  | Unplanned Replacement Risk | 50426.6801 | 54712.8939 | 4699.4976 | 5020.0559 | 5367.1785 | 5743.1498 | 6150.4559 | 6591.802 | 7070.1327 | 7590.2034 | 8172.1717 | 8815.4319 | 9527.2972 | 10321.3825 | 11219.1371 | 12247.9249 | 13447.4694 | 14878.7692 | 16634.3204 | 18952.5196 | 22050.368 | 26245.118 | 31003.4243 | 33206.0417 | 35772.899
|  | Total relay risks | 138182.7148 | 149866.7027 | 5798.6984 | 6154.6988 | 6540.3184 | 6958.1145 | 7410.8705 | 7901.6167 | 8433.6521 | 9013.0753 | 9670.7452 | 10403.8014 | 11222.0197 | 12145.1834 | 13206.8803 | 14448.6816 | 15931.612 | 17751.5482 | 20055.1701 | 23286.1199 | 27790.9704 | 34065.0139 | 41261.2569 | 44359.9585 | 48115.9246
Total SWBD and relay risk
|  | Energy at Risk ($) | 336084.8207 | 346315.3522 | 257660.3495 | 263405.6458 | 267892.328 | 273649.0559 | 281951.2543 | 34312.5741 | 34803.6491 | 34817.1755 | 34831.8165 | 34847.6667 | 34864.829 | 34883.4159 | 34903.5499 | 34925.3648 | 34949.0068 | 34974.6361 | 35002.4287 | 35047.7135 | 35110.3841 | 35187.0324 | 35282.2673 | 35402.3323 | 35556.501
|  | Safety risk | 2050.4006 | 2194.2917 | 1104.4628 | 1128.4693 | 1154.5816 | 1182.9908 | 1213.9054 | 981.3361 | 1017.9668 | 1058.6903 | 1112.8121 | 1178.2774 | 1257.1584 | 1354.7676 | 1481.6417 | 1650.1209 | 1878.7531 | 2197.9738 | 2655.1262 | 3416.69 | 4596.3321 | 6353.0907 | 8408.0385 | 9089.996 | 9999.068
|  | Unplanned replacement | 68452.023 | 72738.2368 | 22724.8405 | 23045.3988 | 23392.5214 | 23768.4928 | 24175.7988 | 8712.4306 | 9190.7613 | 9710.832 | 10292.8003 | 10936.0605 | 11647.9258 | 12442.0111 | 13339.7656 | 14368.5535 | 15568.098 | 16999.3978 | 18754.9489 | 21073.1482 | 24170.9965 | 28365.7466 | 33124.0529 | 35326.6702 | 37893.5276
|  | Unplanned fault | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8
|  | Environmental risk | 128.9099 | 139.288 | 107.7807 | 110.7663 | 114.0165 | 117.5555 | 121.4097 | 125.608 | 130.1822 | 135.2849 | 142.2236 | 150.7042 | 161.0139 | 173.8962 | 190.8304 | 213.5497 | 244.6614 | 288.4478 | 351.5737 | 457.4756 | 622.165 | 868.0515 | 1155.8056 | 1249.8673 | 1375.7353
|  | Total SWBD and relay risks | 407147.9543 | 421818.9687 | 282029.2336 | 288122.0803 | 292985.2475 | 299149.8948 | 307894.1682 | 44182.7488 | 45193.3595 | 45772.7827 | 46430.4526 | 47163.5087 | 47981.727 | 48904.8908 | 49966.5876 | 51208.3889 | 52691.3193 | 54511.2555 | 56814.8775 | 60045.8273 | 64550.6777 | 70824.7212 | 78020.9643 | 81119.6658 | 84875.6319

## SWBD risks
CitiPower
AR switchboard and relay replacement
Input Data - Station Configuration |  | Constants |  |  | POF METHOD | FIXED | Modifier (x) | Comment
Substation: | AR | Major Failure CoC |  |  | PoF (#1) | 0.2125% | 100%
Asset Type | Indoor CB | Minor Failure CoC |  |  | PoF (#2) | 0.2125% | 100%
VCR | 35.599 | Major Failure CoC - used | 4241257.1553 |  | PoF (#3) | 100% | 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 101600 |  | PoF (#4) | 0% | 100%
Scenario #1: AR - Indoor CB | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 0% | 0 | Energy | 6399.5285 | 6648.5723 | 6718.5302 | 6825.1669 | 6977.1383 | 7098.1143 | 7247.406 | 7453.572 | 7719.2009 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113
Online Monitoring | 100% | 0 | Energy | 7642.3661 | 7914.8867 | 8031.3436 | 8183.123 | 8365.6959 | 8502.6765 | 8692.4388 | 8987.7659 | 9260.6283 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652 | 9387.652
Physical Separation | 0% | 300000 | Energy | 6399.5285 | 6648.5723 | 6718.5302 | 6825.1669 | 6977.1383 | 7098.1143 | 7247.406 | 7453.572 | 7719.2009 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113 | 7828.9113
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 241089.9478 | 250206.3836 | 253193.4101 | 257471.6793 | 263208.5256 | 267686.0733 | 273432.9245 | 281724.4418 | 291257.8158 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964 | 295348.2964
Replace 1 Asset | 0% | 3534380.9628 | Safety Risk | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713
Replace 2 Assets | 0% | 7068761.9255 | Unplanned Replacement Risk | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429 | 18025.3429
Replace 3 Assets | 0% | 0 | Unplanned Fault Risk | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8 | 431.8
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Total Life Cycle Cost | 259848.8036 | 268965.2395 | 271952.266 | 276230.5352 | 281967.3815 | 286444.9292 | 292191.7804 | 300483.2976 | 310016.6717 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523 | 314107.1523
Input Data - Station Configuration |  | Constants |  | PoF (#4) 2026: POF METHOD; 0% 2027: FIXED; 100% 2028: Modifier (x); 100% 2029: Comment
Substation: | AR | Major Failure CoC |  | PoF (#4) 2026: PoF (#1); 0% 2027: 0.25%; 100% 2028: 100%
Asset Type | Indoor CB | Minor Failure CoC |  | PoF (#4) 2026: PoF (#2); 0% 2027: 0.25%; 100% 2028: 100%
VCR | 35.599 | Major Failure CoC - used | 4241257.1553 | PoF (#4) 2026: PoF (#3); 0% 2027: 100%; 100% 2028: 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 101600 | PoF (#4) 2026: PoF (#4); 0% 2027: 0%; 100% 2028: 100%
Scenario #2: AR - Indoor CB | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 0% | 0 | Energy | 7537.2255 | 7830.5548 | 7912.9529 | 798.489 | 816.2662 | 830.4169 | 847.8804 | 871.9972 | 903.0715 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055
Online Monitoring | 0% | 0 | Energy | 9001.1154 | 9322.0874 | 9459.2515 | 957.3153 | 978.6763 | 994.7034 | 1016.9071 | 1051.4618 | 1083.3916 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574
Physical Separation | 0% | 300000 | Energy | 7537.2255 | 7830.5548 | 7912.9529 | 798.489 | 816.2662 | 830.4169 | 847.8804 | 871.9972 | 903.0715 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.5% | 0.5% | 0.5% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 0.5% | 0.5% | 0.5% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 283951.5943 | 294689.0418 | 298207.2152 | 30121.6275 | 30792.7518 | 31316.5422 | 31988.848 | 32958.8559 | 34074.2079 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831
Replace 1 Asset | 0% | 3534380.9628 | Safety Risk | 354.9564 | 354.9564 | 354.9564 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956
Replace 2 Assets | 100% | 7068761.9255 | Unplanned Replacement Risk | 21206.2858 | 21206.2858 | 21206.2858 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286
Replace 3 Assets | 0% | 0 | Unplanned Fault Risk | 508 | 508 | 508 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429
|  |  | Total Life Cycle Cost | 306020.8365 | 316758.284 | 320276.4574 | 333696.0946 | 334367.219 | 334891.0093 | 335563.3152 | 336533.3231 | 337648.675 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503
Input Data - Station Configuration |  | Constants |  | PoF (#4) 2026: POF METHOD; 0% 2027: FIXED; 100% 2028: Modifier (x); 100% 2029: Comment
Substation: | AR | Major Failure CoC |  | PoF (#4) 2026: PoF (#1); 0% 2027: 0.25%; 100% 2028: 100%
Asset Type | Indoor CB | Minor Failure CoC |  | PoF (#4) 2026: PoF (#2); 0% 2027: 0.25%; 100% 2028: 100%
VCR | 35.599 | Major Failure CoC - used | 4241257.1553 | PoF (#4) 2026: PoF (#3); 0% 2027: 100%; 100% 2028: 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 101600 | PoF (#4) 2026: PoF (#4); 0% 2027: 0%; 100% 2028: 100%
Scenario #3: AR - Indoor CB | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 0% | 0 | Energy | 7537.2255 | 7830.5548 | 7912.9529 | 8038.5517 | 8217.5452 | 8360.0333 | 8535.8713 | 8778.6956 | 903.0715 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055
Online Monitoring | 0% | 0 | Energy | 9001.1154 | 9322.0874 | 9459.2515 | 9638.0136 | 9853.0416 | 10014.3719 | 10237.8642 | 10585.6872 | 1083.3916 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574 | 1098.2574
Physical Separation | 0% | 300000 | Energy | 7537.2255 | 7830.5548 | 7912.9529 | 8038.5517 | 8217.5452 | 8360.0333 | 8535.8713 | 8778.6956 | 903.0715 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055 | 915.9055
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 283951.5943 | 294689.0418 | 298207.2152 | 303246.1746 | 310003.0031 | 315276.6662 | 322045.2561 | 331810.9118 | 34074.2079 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831 | 34552.7831
Replace 1 Asset | 0% | 3534380.9628 | Safety Risk | 354.9564 | 354.9564 | 354.9564 | 354.9564 | 354.9564 | 354.9564 | 354.9564 | 354.9564 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956
Replace 2 Assets | 100% | 7068761.9255 | Unplanned Replacement Risk | 21206.2858 | 21206.2858 | 21206.2858 | 21206.2858 | 21206.2858 | 21206.2858 | 21206.2858 | 21206.2858 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286 | 2120.6286
Replace 3 Assets | 0% | 0 | Unplanned Fault Risk | 508 | 508 | 508 | 508 | 508 | 508 | 508 | 508 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8 | 50.8
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429 | 301367.5429
|  |  | Total Life Cycle Cost | 306020.8365 | 316758.284 | 320276.4574 | 325315.4168 | 332072.2453 | 337345.9084 | 344114.4984 | 353880.154 | 337648.675 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503 | 338127.2503

## Misc_calcs
CitiPower
AR switchboard and relay replacement
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 1 | TRUE
| Option 3 | 1 | TRUE
| Option 4 | Not used | FALSE
| Option 5 | Not used | FALSE
| First year | 1
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
CitiPower
AR switchboard and relay replacement
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | TRUE | Not used |  | TRUE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
|  |  | CitiPower | Powercor | United Energy
| Reliability in worst-served areas | per MWh | 0 | 151432.8174 | 0
| Network resilience | per MWh | 0 | 24590 | 38560
| Enabling solar exports | per MWh | 4220.9954 | 88.3577 | 862.6028
| Aesthetics | per customer impacted | 0 | 0 | 0
| Customer value of time - residential | per minute customer time | 0.54769 | 0.35181 | 0.34751
| Customer value of time - business | per minute customer time | 0.54769 | 0.35181 | 0.34751
| Communication | per customer impacted | 0 | 0 | 0
| Information accessibility | per customer impacted | 0 | 0 | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020