## Cover
CitiPower
Regulatory proposal 2026-31
HV switchboard and relay retirement R 22kV
| Model number: | 4.09
2025-01-31
15

## Summary
CitiPower
R switchboard and relay retirement
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Decomission switchboard and connect transformers and VR Cremorne feeders to RMU |  | -1.7264 | 2.6336 | 0.90719
| Option 3 | Decomission switchboard, direct connect transformers and connect VR Cremorne feeders to RTS |  | -2.8134 | 2.6817 | -0.13171
| Option 4 | 0
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | Decomission switchboard and connect transformers and VR Cremorne feeders to RMU |  | 0.90719
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 3.0049 | 0 | 0 | 0 | 0 |  | 3.0049
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
| Capex and risk ($M, 2026) |  | Value of expected unserved energy ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 0.90719 | -0.13171 |  |  |  | Option 2
| Capex 10% higher |  | 0 | 0.73455 | -0.41305 |  |  |  | Option 2
| Capex 10% lower |  | 0 | 1.0798 | 0.14963 |  |  |  | Option 2
| Total benefits 10% higher |  | 0 | 1.1706 | 0.13646 |  |  |  | Option 2
| Total benefits 10% lower |  | 0 | 0.64384 | -0.39987 |  |  |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  | 0 | 0.4712 | -0.68121 |  |  |  | Option 2
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
CitiPower
R switchboard and relay retirement
Project
|  | Business: |  | CitiPower
|  | Descripton: |  | R switchboard and relay retirement
|  | Date of cost inputs: |  | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Decomission switchboard and connect transformers and VR Cremorne feeders to RMU
|  | Option 3 |  | Decomission switchboard, direct connect transformers and connect VR Cremorne feeders to RTS
Option 4
Option 5
|  | Compliance project |  | No
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | R |  | Richmond | 50104.8931 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 0 | 2023-12-31 | per MWh
|  | Network resilience |  |  |  | 0 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 4220.9954 | 2023-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
CitiPower
R switchboard and relay retirement
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 50104.8931 | 2023-12-31 |  | 62651.8352 | 70757.5654 | 72315.8049 | 73067.1064 | 73501.1686 | 74168.9339 | 75600.1527 | 77678.4143 | 79142.5749 | 81331.1185 | 84472.403 | 88950.9565 | 95353.0581 | 104526.3293 | 117697.3909 | 136642.8094 | 163930.5748 | 203286.2336 | 210574.862 | 211126.0538 | 211797.8436 | 211967.4363 | 212167.28 | 212402.9401 | 212681.0251
| Safety risk | (after DF) |  | 2023-12-31 |  | 2031.4306 | 2314.1942 | 2672.3237 | 3130.1342 | 3751.8672 | 4579.9889 | 5637.9261 | 6992.9866 | 8733.2362 | 10974.4606 | 13869.9498 | 17619.5929 | 22489.7749 | 28834.7316 | 37127.1785 | 48000.1915 | 58750.7518 | 65901.9126 | 73824.6851 | 84515.3193 | 97566.7095 | 97588.8693 | 97613.9941 | 97642.5212 | 97674.9584
| Unplanned replacement risk |  |  | 2023-12-31 |  | 11476.5693 | 12124.3128 | 12967.6271 | 14098.4979 | 15579.0484 | 17506.9689 | 19979.0618 | 23158.9179 | 27262.4696 | 32577.4668 | 39493.3153 | 48510.1907 | 60310.6849 | 75814.4049 | 96265.6395 | 123355.3042 | 151149.0113 | 172084.2266 | 182437.3387 | 193105.318 | 206030.0779 | 206147.7773 | 206282.8175 | 206437.989 | 206616.5619
| Unplanned fault risk | (after DF) |  | 2023-12-31 |  | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762
| Environmental risk |  |  | 2023-12-31 |  | 207.6826 | 247.5274 | 297.7007 | 361.1701 | 447.3266 | 561.9833 | 708.199 | 895.1078 | 1134.6152 | 1442.2967 | 1838.6265 | 2350.3397 | 3012.7895 | 3872.7345 | 4992.2159 | 6453.8222 | 7867.0608 | 8728.0577 | 9817.7703 | 11322.903 | 13160.4239 | 13162.9133 | 13165.7074 | 13168.8473 | 13172.3797
| Other risk |  |  | 2023-12-31 |  | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000
| Total risk cost |  |  |  |  | 107129.5176 | 116205.5999 | 119015.4564 | 121418.9087 | 124041.4108 | 127579.8749 | 132687.3396 | 139487.4266 | 147034.8959 | 157087.3426 | 170436.2946 | 188193.0798 | 211928.3074 | 243810.2002 | 286844.4249 | 345214.1273 | 412459.3986 | 480762.4305 | 507416.6561 | 530831.5942 | 559317.0548 | 559628.9961 | 559991.799 | 560414.2977 | 560906.9251
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
CitiPower
R switchboard and relay retirement
OPTION 2 | Decomission switchboard and connect transformers and VR Cremorne feeders to RMU
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Retire switchboard and install RMU |  | 50 | 2023-12-31 | 2700000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 2700000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 50104.8931 | 2023-12-31 | 62651.8352 | 7842.928 | 7987.9704 | 8034.3897 | 8116.956 | 8407.768 | 8862.7347 | 9507.174 | 10268.8216 | 11353.3825 | 12888.8802 | 15074.0065 | 18210.9618 | 22684.0271 | 29079.1662 | 38243.5996 | 51403.4366 | 70334.5914 | 97611.2945 | 136967.1219 | 144255.9818 | 144807.4928 | 145479.7243 | 145649.9311 | 145850.6309
| Safety risk | (after DF) |  | 2023-12-31 | 2031.4306 | 647.5122 | 655.4521 | 665.22 | 680.6628 | 707.6864 | 787.1627 | 931.875 | 1127.5291 | 1393.4745 | 1756.7764 | 2255.6001 | 2944.4297 | 3897.3384 | 5220.4507 | 7063.8074 | 9639.8801 | 13249.9851 | 18371.118 | 25610.5299 | 33656.8555 | 44520.5737 | 57814.6612 | 58177.5166 | 58681.5091
| Unplanned replacement risk |  |  | 2023-12-31 | 11476.5693 | 1953.1879 | 1962.9287 | 1974.9121 | 2020.5786 | 2149.1929 | 2368.65 | 2707.7675 | 3175.8298 | 3825.1637 | 4730.1861 | 5998.582 | 7790.5551 | 10314.4315 | 13881.064 | 18936.4215 | 26121.1607 | 36356.6973 | 51060.8133 | 72143.3326 | 82707.5675 | 93676.719 | 107029.7759 | 107755.3611 | 108752.1978
| Unplanned fault risk | (after DF) |  | 2023-12-31 | 762 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
| Environmental risk |  |  | 2023-12-31 | 207.6826 | 80.1943 | 81.3126 | 82.6883 | 84.5719 | 87.3372 | 97.0818 | 115.4361 | 140.1436 | 173.5801 | 219.0556 | 281.2074 | 366.5868 | 484.1994 | 646.8155 | 872.4197 | 1186.381 | 1624.5381 | 2244.5088 | 3117.9417 | 4225.0648 | 5754.588 | 7626.3091 | 7676.8084 | 7747.0835
| Other risk |  |  | 2023-12-31 | 30000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 107129.5176 | 10600.0224 | 10763.8638 | 10833.4102 | 10978.9693 | 11428.1844 | 12191.8293 | 13338.4527 | 14788.5242 | 16821.8008 | 19671.0983 | 23685.596 | 29388.7335 | 37456.1965 | 48903.6964 | 65192.4482 | 88427.0584 | 121642.0119 | 169363.9346 | 237915.1261 | 264921.6696 | 288835.5735 | 318026.6705 | 319335.8172 | 321107.6212
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - residential | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - business | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex saving |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 105605.5775 | 108251.5925 | 110585.4985 | 113062.4415 | 116151.6905 | 120495.5103 | 126148.9739 | 132246.3717 | 140265.5418 | 150765.1963 | 164507.4838 | 182539.5739 | 206354.0037 | 237940.7285 | 280021.6791 | 324032.3402 | 359120.4186 | 338052.7214 | 292916.4681 | 294395.3852 | 270793.4226 | 241965.1285 | 241078.4805 | 239799.3039
Capital expenditure
| Retire switchboard and install RMU |  |  | 2023-12-31 | -2700000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Retire switchboard and install RMU |  |  | 2023-12-31 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000 | -2700000
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Retire switchboard and install RMU |  |  | 2023-12-31 | 0 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158
| Annualised capex |  |  | 2023-12-31 | 0 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 105605.5775 | 108251.5925 | 110585.4985 | 113062.4415 | 116151.6905 | 120495.5103 | 126148.9739 | 132246.3717 | 140265.5418 | 150765.1963 | 164507.4838 | 182539.5739 | 206354.0037 | 237940.7285 | 280021.6791 | 324032.3402 | 359120.4186 | 338052.7214 | 292916.4681 | 294395.3852 | 270793.4226 | 241965.1285 | 241078.4805 | 239799.3039
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | -9505.4383 | -6859.4233 | -4525.5173 | -2048.5743 | 1040.6747 | 5384.4945 | 11037.9581 | 17135.3559 | 25154.526 | 35654.1805 | 49396.468 | 67428.5581 | 91242.9879 | 122829.7126 | 164910.6632 | 208921.3244 | 244009.4027 | 222941.7056 | 177805.4522 | 179284.3694 | 155682.4068 | 126854.1127 | 125967.4647 | 124688.288
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | -9505.4383 | -6859.4233 | -4525.5173 | -2048.5743 | 1040.6747 | 5384.4945 | 11037.9581 | 17135.3559 | 25154.526 | 35654.1805 | 49396.468 | 67428.5581 | 91242.9879 | 122829.7126 | 164910.6632 | 208921.3244 | 244009.4027 | 222941.7056 | 177805.4522 | 179284.3694 | 155682.4068 | 126854.1127 | 125967.4647 | 124688.288
| Total annualised capex |  |  |  | 0 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158 | -115111.0158
| Total benefits |  |  |  | 0 | 105605.5775 | 108251.5925 | 110585.4985 | 113062.4415 | 116151.6905 | 120495.5103 | 126148.9739 | 132246.3717 | 140265.5418 | 150765.1963 | 164507.4838 | 182539.5739 | 206354.0037 | 237940.7285 | 280021.6791 | 324032.3402 | 359120.4186 | 338052.7214 | 292916.4681 | 294395.3852 | 270793.4226 | 241965.1285 | 241078.4805 | 239799.3039
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | -21016.5399 | -18370.5249 | -16036.6189 | -13559.6759 | -10470.4269 | -6126.6071 | -473.1435 | 5624.2543 | 13643.4244 | 24143.0789 | 37885.3664 | 55917.4565 | 79731.8863 | 111318.611 | 153399.5617 | 197410.2228 | 232498.3011 | 211430.604 | 166294.3507 | 167773.2678 | 144171.3052 | 115343.0111 | 114456.3631 | 113177.1864
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | 2005.6632 | 4651.6783 | 6985.5843 | 9462.5273 | 12551.7762 | 16895.596 | 22549.0597 | 28646.4574 | 36665.6276 | 47165.2821 | 60907.5695 | 78939.6597 | 102754.0895 | 134340.8142 | 176421.7648 | 220432.4259 | 255520.5043 | 234452.8072 | 189316.5538 | 190795.471 | 167193.5084 | 138365.2143 | 137478.5663 | 136199.3896
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | 1055.1194 | 3965.736 | 6533.0326 | 9257.6698 | 12655.8437 | 17434.0455 | 23652.8555 | 30359.993 | 39181.0802 | 50730.7001 | 65847.2163 | 85682.5155 | 111878.3883 | 146623.7855 | 192912.8311 | 241324.5584 | 279921.4446 | 256746.9778 | 207097.0991 | 208723.9079 | 182761.7491 | 151050.6255 | 150075.3127 | 148668.2184
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | -20065.9961 | -17684.5825 | -15584.0672 | -13354.8185 | -10574.4944 | -6665.0566 | -1576.9393 | 3910.7187 | 11127.9718 | 20577.6609 | 32945.7196 | 49174.6007 | 70607.5875 | 99035.6398 | 136908.4953 | 176518.0903 | 208097.3609 | 189136.4335 | 148513.8054 | 149844.8309 | 128603.0645 | 102657.5998 | 101859.6166 | 100708.3576
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | -31577.0977 | -29195.6841 | -27095.1687 | -24865.92 | -22085.596 | -18176.1582 | -13088.0409 | -7600.3829 | -383.1298 | 9066.5593 | 21434.618 | 37663.4991 | 59096.486 | 87524.5382 | 125397.3937 | 165006.9888 | 196586.2593 | 177625.3319 | 137002.7039 | 138333.7293 | 117091.9629 | 91146.4982 | 90348.515 | 89197.2561
sens | 0 | 0% | 0% | Option 2sens | 0 | -9505.4383 | -6859.4233 | -4525.5173 | -2048.5743 | 1040.6747 | 5384.4945 | 11037.9581 | 17135.3559 | 25154.526 | 35654.1805 | 49396.468 | 67428.5581 | 91242.9879 | 122829.7126 | 164910.6632 | 208921.3244 | 244009.4027 | 222941.7056 | 177805.4522 | 179284.3694 | 155682.4068 | 126854.1127 | 125967.4647 | 124688.288
sens | 0 | 0% | 0% | Option 2sens | 0 | -9505.4383 | -6859.4233 | -4525.5173 | -2048.5743 | 1040.6747 | 5384.4945 | 11037.9581 | 17135.3559 | 25154.526 | 35654.1805 | 49396.468 | 67428.5581 | 91242.9879 | 122829.7126 | 164910.6632 | 208921.3244 | 244009.4027 | 222941.7056 | 177805.4522 | 179284.3694 | 155682.4068 | 126854.1127 | 125967.4647 | 124688.288
sens | 0 | 0% | 0% | Option 2sens | 0 | -9505.4383 | -6859.4233 | -4525.5173 | -2048.5743 | 1040.6747 | 5384.4945 | 11037.9581 | 17135.3559 | 25154.526 | 35654.1805 | 49396.468 | 67428.5581 | 91242.9879 | 122829.7126 | 164910.6632 | 208921.3244 | 244009.4027 | 222941.7056 | 177805.4522 | 179284.3694 | 155682.4068 | 126854.1127 | 125967.4647 | 124688.288

## Option3
CitiPower
R switchboard and relay retirement
OPTION 3 | Decomission switchboard, direct connect transformers and connect VR Cremorne feeders to RTS
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Retire switchboard and direct connection |  | 50 | 2023-12-31 | 4400000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 4400000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 50104.8931 | 2023-12-31 | 62651.8352 | 5085.3419 | 5172.3784 | 5200.3187 | 5281.2056 | 5567.3497 | 5996.404 | 6601.951 | 7366.4994 | 8451.0602 | 9986.558 | 12171.6842 | 15308.6396 | 19781.7048 | 26176.844 | 35341.2774 | 48501.1143 | 67432.2691 | 94708.9723 | 134064.7997 | 141353.6595 | 141905.1705 | 142577.4021 | 142747.6088 | 142948.3086
| Safety risk | (after DF) |  | 2023-12-31 | 2031.4306 | 636.8635 | 644.8034 | 654.5713 | 670.0141 | 697.0377 | 776.514 | 921.2264 | 1116.8804 | 1382.8258 | 1746.1277 | 2244.9514 | 2933.781 | 3886.6898 | 5209.802 | 7053.1587 | 9629.2314 | 13239.3364 | 18360.4693 | 25599.8813 | 33646.2068 | 44509.925 | 57804.0125 | 58166.8679 | 58670.8604
| Unplanned replacement risk |  |  | 2023-12-31 | 11476.5693 | 1629.1879 | 1638.9287 | 1650.9121 | 1696.5786 | 1825.1929 | 2044.65 | 2383.7675 | 2851.8298 | 3501.1637 | 4406.1861 | 5674.582 | 7466.5551 | 9990.4315 | 13557.064 | 18612.4215 | 25797.1607 | 36032.6973 | 50736.8133 | 71819.3326 | 82383.5675 | 93352.719 | 106705.7759 | 107431.3611 | 108428.1978
| Unplanned fault risk |  |  | 2023-12-31 | 762 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
| Environmental risk |  |  | 2023-12-31 | 207.6826 | 80.1943 | 81.3126 | 82.6883 | 84.5719 | 87.3372 | 97.0818 | 115.4361 | 140.1436 | 173.5801 | 219.0556 | 281.2074 | 366.5868 | 484.1994 | 646.8155 | 872.4197 | 1186.381 | 1624.5381 | 2244.5088 | 3117.9417 | 4225.0648 | 5754.588 | 7626.3091 | 7676.8084 | 7747.0835
| Other risk |  |  | 2023-12-31 | 30000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 107129.5176 | 7507.7876 | 7613.6231 | 7664.6904 | 7808.5703 | 8253.1175 | 8990.8499 | 10098.581 | 11551.5532 | 13584.8298 | 16434.1274 | 20448.6251 | 26151.7625 | 34219.2255 | 45666.7255 | 61955.4773 | 85190.0875 | 118405.041 | 166126.9637 | 234678.1552 | 261684.6986 | 285598.6025 | 314789.6995 | 316098.8462 | 317870.6503
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex saving |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 108697.8123 | 111401.8333 | 113754.2183 | 116232.8406 | 119326.7574 | 123696.4897 | 129388.8456 | 135483.3426 | 143502.5128 | 154002.1673 | 167744.4547 | 185776.5448 | 209590.9747 | 241177.6994 | 283258.65 | 327269.3111 | 362357.3895 | 341289.6924 | 296153.439 | 297632.3562 | 274030.3936 | 245202.0995 | 244315.4514 | 243036.2748
Capital expenditure
| Retire switchboard and direct connection |  |  | 2023-12-31 | -4400000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Retire switchboard and direct connection |  |  | 2023-12-31 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000 | -4400000
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Retire switchboard and direct connection |  |  | 2023-12-31 | 0 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221
| Annualised capex |  |  | 2023-12-31 | 0 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 108697.8123 | 111401.8333 | 113754.2183 | 116232.8406 | 119326.7574 | 123696.4897 | 129388.8456 | 135483.3426 | 143502.5128 | 154002.1673 | 167744.4547 | 185776.5448 | 209590.9747 | 241177.6994 | 283258.65 | 327269.3111 | 362357.3895 | 341289.6924 | 296153.439 | 297632.3562 | 274030.3936 | 245202.0995 | 244315.4514 | 243036.2748
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | -78890.5098 | -76186.4888 | -73834.1038 | -71355.4815 | -68261.5647 | -63891.8324 | -58199.4765 | -52104.9795 | -44085.8093 | -33586.1548 | -19843.8674 | -1811.7773 | 22002.6526 | 53589.3773 | 95670.3279 | 139680.989 | 174769.0674 | 153701.3703 | 108565.1169 | 110044.0341 | 86442.0715 | 57613.7774 | 56727.1293 | 55447.9527
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | -78890.5098 | -76186.4888 | -73834.1038 | -71355.4815 | -68261.5647 | -63891.8324 | -58199.4765 | -52104.9795 | -44085.8093 | -33586.1548 | -19843.8674 | -1811.7773 | 22002.6526 | 53589.3773 | 95670.3279 | 139680.989 | 174769.0674 | 153701.3703 | 108565.1169 | 110044.0341 | 86442.0715 | 57613.7774 | 56727.1293 | 55447.9527
| Total annualised capex |  |  |  | 0 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221 | -187588.3221
| Total benefits |  |  |  | 0 | 108697.8123 | 111401.8333 | 113754.2183 | 116232.8406 | 119326.7574 | 123696.4897 | 129388.8456 | 135483.3426 | 143502.5128 | 154002.1673 | 167744.4547 | 185776.5448 | 209590.9747 | 241177.6994 | 283258.65 | 327269.3111 | 362357.3895 | 341289.6924 | 296153.439 | 297632.3562 | 274030.3936 | 245202.0995 | 244315.4514 | 243036.2748
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | -97649.342 | -94945.321 | -92592.936 | -90114.3137 | -87020.3969 | -82650.6646 | -76958.3087 | -70863.8117 | -62844.6415 | -52344.987 | -38602.6996 | -20570.6095 | 3243.8204 | 34830.5451 | 76911.4957 | 120922.1568 | 156010.2352 | 134942.5381 | 89806.2847 | 91285.2019 | 67683.2393 | 38854.9452 | 37968.2971 | 36689.1205
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | -60131.6775 | -57427.6566 | -55075.2716 | -52596.6493 | -49502.7325 | -45133.0002 | -39440.6443 | -33346.1473 | -25326.9771 | -14827.3226 | -1085.0352 | 16947.055 | 40761.4848 | 72348.2095 | 114429.1601 | 158439.8212 | 193527.8996 | 172460.2025 | 127323.9491 | 128802.8663 | 105200.9037 | 76372.6096 | 75485.9616 | 74206.7849
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | -68020.7285 | -65046.3055 | -62458.682 | -59732.1975 | -56328.8889 | -51522.1834 | -45260.592 | -38556.6452 | -29735.558 | -18185.9381 | -3069.4219 | 16765.8772 | 42961.7501 | 77707.1472 | 123996.1929 | 172407.9202 | 211004.8064 | 187830.3395 | 138180.4608 | 139807.2697 | 113845.1108 | 82133.9873 | 81158.6745 | 79751.5802
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | -89760.291 | -87326.6721 | -85209.5256 | -82978.7656 | -80194.2404 | -76261.4814 | -71138.3611 | -65653.3137 | -58436.0606 | -48986.3715 | -36618.3128 | -20389.4317 | 1043.5551 | 29471.6074 | 67344.4629 | 106954.0579 | 138533.3285 | 119572.401 | 78949.773 | 80280.7984 | 59039.0321 | 33093.5674 | 32295.5842 | 31144.3252
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | -108519.1232 | -106085.5044 | -103968.3578 | -101737.5978 | -98953.0726 | -95020.3136 | -89897.1933 | -84412.1459 | -77194.8928 | -67745.2037 | -55377.1451 | -39148.2639 | -17715.2771 | 10712.7752 | 48585.6307 | 88195.2257 | 119774.4962 | 100813.5688 | 60190.9408 | 61521.9662 | 40280.1999 | 14334.7352 | 13536.752 | 12385.493
sens | 0 | 0% | 0% | Option 3sens | 0 | -78890.5098 | -76186.4888 | -73834.1038 | -71355.4815 | -68261.5647 | -63891.8324 | -58199.4765 | -52104.9795 | -44085.8093 | -33586.1548 | -19843.8674 | -1811.7773 | 22002.6526 | 53589.3773 | 95670.3279 | 139680.989 | 174769.0674 | 153701.3703 | 108565.1169 | 110044.0341 | 86442.0715 | 57613.7774 | 56727.1293 | 55447.9527
sens | 0 | 0% | 0% | Option 3sens | 0 | -78890.5098 | -76186.4888 | -73834.1038 | -71355.4815 | -68261.5647 | -63891.8324 | -58199.4765 | -52104.9795 | -44085.8093 | -33586.1548 | -19843.8674 | -1811.7773 | 22002.6526 | 53589.3773 | 95670.3279 | 139680.989 | 174769.0674 | 153701.3703 | 108565.1169 | 110044.0341 | 86442.0715 | 57613.7774 | 56727.1293 | 55447.9527
sens | 0 | 0% | 0% | Option 3sens | 0 | -78890.5098 | -76186.4888 | -73834.1038 | -71355.4815 | -68261.5647 | -63891.8324 | -58199.4765 | -52104.9795 | -44085.8093 | -33586.1548 | -19843.8674 | -1811.7773 | 22002.6526 | 53589.3773 | 95670.3279 | 139680.989 | 174769.0674 | 153701.3703 | 108565.1169 | 110044.0341 | 86442.0715 | 57613.7774 | 56727.1293 | 55447.9527

## Option4
CitiPower
R switchboard and relay retirement
OPTION 4 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 50104.8931 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option5
CitiPower
R switchboard and relay retirement
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 50104.8931 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
CitiPower
R switchboard and relay retirement
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 2152429.1293 | 2026-06-30 |  | 69726.0197 | 78746.9894 | 80481.1738 | 81317.3068 | 81800.3801 | 82543.5445 | 84136.366 | 86449.2896 | 88078.7725 | 90514.4303 | 94010.4055 | 98994.6444 | 106119.6242 | 116328.6737 | 130986.9148 | 152071.5106 | 182440.4099 | 226239.8202 | 234351.4269 | 234964.8553 | 235712.4986 | 235901.2405 | 236123.6491 | 236385.9182 | 236695.4025
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 3373913.8156 | 2026-06-30 |  | 119225.795 | 129326.6817 | 132453.8065 | 135128.639 | 138047.2548 | 141985.2562 | 147669.4182 | 155237.3211 | 163636.9951 | 174824.4902 | 189680.7077 | 209442.4585 | 235857.6934 | 271339.4551 | 319232.788 | 384193.168 | 459031.2808 | 535046.5888 | 564710.4135 | 590769.1943 | 622471.0236 | 622818.1871 | 623221.955 | 623692.1591 | 624240.4104
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 820775.8277 | 2026-06-30 |  | 69726.0197 | 8728.4938 | 8889.9133 | 8941.574 | 9033.463 | 9357.1113 | 9863.4496 | 10580.6542 | 11428.3015 | 12635.3229 | 14344.1978 | 16776.0525 | 20267.2097 | 25245.3406 | 32362.5718 | 42561.7857 | 57207.5346 | 78276.2562 | 108632.8441 | 152432.4421 | 160544.3064 | 161158.09 | 161906.225 | 162095.6502 | 162319.0116
Option 2 | Capital expenditure | Option 2Capital expenditure | -2953620.3171 | 2026-06-30 |  | -3004864.1453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 740324.6901 | 2026-06-30 |  | 119225.795 | 11796.899 | 11979.2402 | 12056.6392 | 12218.6338 | 12718.571 | 13568.441 | 14844.5326 | 16458.3356 | 18721.1948 | 21892.2141 | 26359.9994 | 32707.0931 | 41685.4747 | 54425.5422 | 72553.5001 | 98411.5916 | 135376.9334 | 188487.2647 | 264778.7526 | 0 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -1726394.6984 | 2026-06-30 |  | 0 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | -128108.5053 | 0 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 2633589.1255 | 2026-06-30 |  | 0 | 117529.7827 | 120474.5663 | 123071.9998 | 125828.621 | 129266.6852 | 134100.9772 | 140392.7884 | 147178.6595 | 156103.2954 | 167788.4937 | 183082.4591 | 203150.6003 | 229653.9804 | 264807.2458 | 311639.6679 | 360619.6892 | 399669.6554 | 376223.1488 | 325990.4417 | 0 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | -10578.7225 | -7633.9389 | -5036.5054 | -2279.8843 | 1158.18 | 5992.472 | 12284.2832 | 19070.1542 | 27994.7901 | 39679.9884 | 54973.9539 | 75042.095 | 101545.4751 | 136698.7405 | 183531.1626 | 232511.184 | 271561.1501 | 248114.6436 | 197881.9364 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 907194.427 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -1726394.6984 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 2633589.1255 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 770250.2585 | 2026-06-30 |  | 69726.0197 | 5659.5413 | 5756.4053 | 5787.5004 | 5877.5205 | 6195.9739 | 6673.4739 | 7347.3948 | 8198.2703 | 9405.2918 | 11114.1667 | 13546.0213 | 17037.1786 | 22015.3095 | 29132.5407 | 39331.7545 | 53977.5035 | 75046.2251 | 105402.813 | 149202.411 | 157314.2753 | 157928.0588 | 158676.1939 | 158865.6191 | 159088.9805
Option 3 | Capital expenditure | Option 3Capital expenditure | -4813307.1834 | 2026-06-30 |  | -4896815.6442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 692236.6367 | 2026-06-30 |  | 119225.795 | 8355.5118 | 8473.2974 | 8530.1309 | 8690.2566 | 9184.9988 | 10006.0306 | 11238.8385 | 12855.8697 | 15118.7289 | 18289.7482 | 22757.5335 | 29104.6272 | 38083.0088 | 50823.0763 | 68951.0342 | 94809.1257 | 131774.4675 | 184884.7988 | 261176.2867 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -2813383.953 | 2026-06-30 |  | 0 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | -208769.416 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 2681677.1788 | 2026-06-30 |  | 0 | 120971.17 | 123980.5091 | 126598.5081 | 129356.9982 | 132800.2574 | 137663.3877 | 143998.4825 | 150781.1254 | 159705.7613 | 171390.9595 | 186684.925 | 206753.0662 | 233256.4463 | 268409.7117 | 315242.1338 | 364222.1551 | 403272.1213 | 379825.6147 | 329592.9076 | 0 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | -87798.246 | -84788.9069 | -82170.9079 | -79412.4178 | -75969.1586 | -71106.0283 | -64770.9334 | -57988.2906 | -49063.6547 | -37378.4564 | -22084.491 | -2016.3498 | 24487.0303 | 59640.2957 | 106472.7178 | 155452.7392 | 194502.7053 | 171056.1988 | 120823.4916 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | -131706.7742 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -2813383.953 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 2681677.1788 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 0 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | 0 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 0 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0.12811 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 0.11923 | 0.12933 | 0.13245 | 0.13513 | 0.13805 | 0.14199 | 0.14767 | 0.15524 | 0.16364 | 0.17482 | 0.18968 | 0.20944 | 0.23586 | 0.27134 | 0.31923 | 0.38419 | 0.45903 | 0.53505 | 0.56471 | 0.59077 | 0.62247 | 0.62282 | 0.62322 | 0.62369 | 0.62424
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 0 |  |  | Energy at risk energy at risk (weighted) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Energy at risk value | 0.21268 |  |  | Option 1 (base case) risk cost | 0.062652 | 0.070758 | 0.072316 | 0.073067 | 0.073501 | 0.074169 | 0.0756 | 0.077678 | 0.079143 | 0.081331 | 0.084472 | 0.088951 | 0.095353 | 0.10453 | 0.1177 | 0.13664 | 0.16393 | 0.20329 | 0.21057 | 0.21113 | 0.2118 | 0.21197 | 0.21217 | 0.2124 | 0.21268

## Sensitivity_calcs
CitiPower
R switchboard and relay retirement
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
[7 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 248114.6436 | 197881.9364 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 907194.427 |  | 0 | 0 | -10578.7225 | -7633.9389 | -5036.5054 | -2279.8843 | 1158.18 | 5992.472 | 12284.2832 | 19070.1542 | 27994.7901 | 39679.9884 | 54973.9539 | 75042.095 | 101545.4751 | 136698.7405 | 183531.1626 | 232511.184 | 271561.1501 | 248114.6436 | 197881.9364 | 0 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 734554.9572 |  | 0 | 0 | -23389.5731 | -20444.7894 | -17847.356 | -15090.7348 | -11652.6705 | -6818.3785 | -526.5674 | 6259.3037 | 15183.9396 | 26869.1379 | 42163.1033 | 62231.2445 | 88734.6246 | 123887.89 | 170720.3121 | 219700.3335 | 258750.2996 | 235303.7931 | 185071.0859 | 0 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 1079833.8969 |  | 0 | 0 | 2232.128 | 5176.9116 | 7774.3451 | 10530.9663 | 13969.0305 | 18803.3225 | 25095.1337 | 31881.0048 | 40805.6406 | 52490.8389 | 67784.8044 | 87852.9455 | 114356.3257 | 149509.5911 | 196342.0132 | 245322.0345 | 284372.0007 | 260925.4941 | 210692.7869 | 0 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 1170553.3396 |  | 0 | 0 | 1174.2557 | 4413.5177 | 7270.6946 | 10302.9778 | 14084.8485 | 19402.5697 | 26323.562 | 33788.0202 | 43605.1196 | 56458.8378 | 73282.1998 | 95357.155 | 124510.8732 | 163179.4651 | 214695.1294 | 268573.1529 | 311528.1157 | 285736.9585 | 230480.9806 | 0 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 643835.5145 |  | 0 | 0 | -22331.7008 | -19681.3956 | -17343.7054 | -14862.7464 | -11768.4885 | -7417.6257 | -1754.9957 | 4352.2883 | 12384.4606 | 22901.139 | 36665.708 | 54727.035 | 78580.0771 | 110218.016 | 152367.1959 | 196449.2151 | 231594.1846 | 210492.3287 | 165282.8922 | 0 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 471196.0446 |  | 0 | 0 | -35142.5513 | -32492.2461 | -30154.5559 | -27673.5969 | -24579.3391 | -20228.4763 | -14565.8462 | -8458.5622 | -426.39 | 10090.2885 | 23854.8574 | 41916.1845 | 65769.2266 | 97407.1654 | 139556.3453 | 183638.3645 | 218783.3341 | 197681.4782 | 152472.0417 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 907194.427 |  | 0 | 0 | -10578.7225 | -7633.9389 | -5036.5054 | -2279.8843 | 1158.18 | 5992.472 | 12284.2832 | 19070.1542 | 27994.7901 | 39679.9884 | 54973.9539 | 75042.095 | 101545.4751 | 136698.7405 | 183531.1626 | 232511.184 | 271561.1501 | 248114.6436 | 197881.9364 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 907194.427 |  | 0 | 0 | -10578.7225 | -7633.9389 | -5036.5054 | -2279.8843 | 1158.18 | 5992.472 | 12284.2832 | 19070.1542 | 27994.7901 | 39679.9884 | 54973.9539 | 75042.095 | 101545.4751 | 136698.7405 | 183531.1626 | 232511.184 | 271561.1501 | 248114.6436 | 197881.9364 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 907194.427 |  | 0 | 0 | -10578.7225 | -7633.9389 | -5036.5054 | -2279.8843 | 1158.18 | 5992.472 | 12284.2832 | 19070.1542 | 27994.7901 | 39679.9884 | 54973.9539 | 75042.095 | 101545.4751 | 136698.7405 | 183531.1626 | 232511.184 | 271561.1501 | 248114.6436 | 197881.9364 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | -87798.246 | -84788.9069 | -82170.9079 | -79412.4178 | -75969.1586 | -71106.0283 | -64770.9334 | -57988.2906 | -49063.6547 | -37378.4564 | -22084.491 | -2016.3498 | 24487.0303 | 59640.2957 | 106472.7178 | 155452.7392 | 194502.7053 | 171056.1988 | 120823.4916 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | -131706.7742 |  | 0 | 0 | -87798.246 | -84788.9069 | -82170.9079 | -79412.4178 | -75969.1586 | -71106.0283 | -64770.9334 | -57988.2906 | -49063.6547 | -37378.4564 | -22084.491 | -2016.3498 | 24487.0303 | 59640.2957 | 106472.7178 | 155452.7392 | 194502.7053 | 171056.1988 | 120823.4916 | 0 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | -413045.1695 |  | 0 | 0 | -108675.1876 | -105665.8485 | -103047.8495 | -100289.3594 | -96846.1002 | -91982.9699 | -85647.875 | -78865.2322 | -69940.5963 | -58255.398 | -42961.4326 | -22893.2914 | 3610.0887 | 38763.3541 | 85595.7762 | 134575.7976 | 173625.7637 | 150179.2572 | 99946.55 | 0 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 149631.6211 |  | 0 | 0 | -66921.3044 | -63911.9653 | -61293.9663 | -58535.4762 | -55092.217 | -50229.0867 | -43893.9918 | -37111.349 | -28186.7131 | -16501.5148 | -1207.5494 | 18860.5918 | 45363.9719 | 80517.2373 | 127349.6594 | 176329.6808 | 215379.6469 | 191933.1404 | 141700.4332 | 0 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 136460.9437 |  | 0 | 0 | -75701.129 | -72390.856 | -69511.0571 | -66476.7179 | -62689.1329 | -57339.6895 | -50371.0852 | -42910.178 | -33093.0786 | -20239.3605 | -3415.9984 | 18658.9568 | 47812.675 | 86481.2669 | 137996.9312 | 191874.9547 | 234829.9174 | 209038.7602 | 153782.7823 | 0 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | -399874.4921 |  | 0 | 0 | -99895.363 | -97186.9578 | -94830.7587 | -92348.1176 | -89249.1843 | -84872.3671 | -79170.7817 | -73066.4031 | -65034.2308 | -54517.5524 | -40752.9835 | -22691.6564 | 1161.3857 | 32799.3245 | 74948.5044 | 119030.5237 | 154175.4932 | 133073.6373 | 87864.2008 | 0 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | -681212.8874 |  | 0 | 0 | -120772.3046 | -118063.8994 | -115707.7003 | -113225.0592 | -110126.1259 | -105749.3087 | -100047.7233 | -93943.3447 | -85911.1724 | -75394.494 | -61629.9251 | -43568.598 | -19715.5559 | 11922.3829 | 54071.5628 | 98153.5821 | 133298.5516 | 112196.6957 | 66987.2592 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -131706.7742 |  | 0 | 0 | -87798.246 | -84788.9069 | -82170.9079 | -79412.4178 | -75969.1586 | -71106.0283 | -64770.9334 | -57988.2906 | -49063.6547 | -37378.4564 | -22084.491 | -2016.3498 | 24487.0303 | 59640.2957 | 106472.7178 | 155452.7392 | 194502.7053 | 171056.1988 | 120823.4916 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -131706.7742 |  | 0 | 0 | -87798.246 | -84788.9069 | -82170.9079 | -79412.4178 | -75969.1586 | -71106.0283 | -64770.9334 | -57988.2906 | -49063.6547 | -37378.4564 | -22084.491 | -2016.3498 | 24487.0303 | 59640.2957 | 106472.7178 | 155452.7392 | 194502.7053 | 171056.1988 | 120823.4916 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -131706.7742 |  | 0 | 0 | -87798.246 | -84788.9069 | -82170.9079 | -79412.4178 | -75969.1586 | -71106.0283 | -64770.9334 | -57988.2906 | -49063.6547 | -37378.4564 | -22084.491 | -2016.3498 | 24487.0303 | 59640.2957 | 106472.7178 | 155452.7392 | 194502.7053 | 171056.1988 | 120823.4916 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 1 | 1 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 0.90719 | -0.13171 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens1 | Capex 10% higher | 0 | 0.73455 | -0.41305 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens2 | Capex 10% lower | 0 | 1.0798 | 0.14963 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens3 | Total benefits 10% higher | 0 | 1.1706 | 0.13646 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens4 | Total benefits 10% lower | 0 | 0.64384 | -0.39987 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 0.4712 | -0.68121 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Workings_costs
CitiPower
R switchboard and relay retirement
WORKINGS - COSTS
Option 1 - continue existing maintenance with no proactive replacement cost
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
|  | SWBD online monitoring annual cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Relay annual maintenance cost ($)
|  | Total opex cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - Decomission switchboard and connect transformers and VR Cremorne feeders to RMU
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | SWBD capex profile ($) | 2700000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Relay capex profile ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total capex ($) | 2700000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
|  | SWBD online monitoring annual cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Relay annual maintenance cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total opex cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Opex saving | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Decomission switchboard, direct connect transformers and connect VR Cremorne feeders to RTS
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | SWBD capex profile ($) | 4400000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Relay capex profile ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total capex ($) | 4400000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
|  | SWBD online monitoring annual cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Relay annual maintenance cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total opex cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Opex saving | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Workings_risks
CitiPower
R switchboard and relay retirement
WORKINGS - RISKS
Option 1 - continue existing maintenance with no proactive replacement cost
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
SWBD risks
|  | Energy at Risk ($) | 61694.7483 | 69799.6576 | 71278.8541 | 71750.1541 | 71792.8784 | 71911.9601 | 72572.6012 | 73564.1675 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307
|  | Safety risk | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347
|  | Unplanned replacement risk | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100
|  | Unplanned fault risk | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762
|  | Other risk | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000
|  | Total SWBD risks | 101089.183 | 109194.0922 | 110673.2888 | 111144.5888 | 111187.3131 | 111306.3948 | 111967.0359 | 112958.6022 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654
Relay risks
|  | Environmental risk | 207.6826 | 247.5274 | 297.7007 | 361.1701 | 447.3266 | 561.9833 | 708.199 | 895.1078 | 1134.6152 | 1442.2967 | 1838.6265 | 2350.3397 | 3012.7895 | 3872.7345 | 4992.2159 | 6453.8222 | 7867.0608 | 8728.0577 | 9817.7703 | 11322.903 | 13160.4239 | 13162.9133 | 13165.7074 | 13168.8473 | 13172.3797
|  | Energy at Risk ($) | 957.0869 | 957.9079 | 1036.9507 | 1316.9523 | 1708.2902 | 2256.9738 | 3027.5515 | 4114.2468 | 5652.4442 | 7840.9877 | 10982.2722 | 15460.8258 | 21862.9273 | 31036.1985 | 44207.2602 | 63152.6786 | 90440.4441 | 129796.1029 | 137084.7313 | 137635.9231 | 138307.7128 | 138477.3056 | 138677.1493 | 138912.8094 | 139190.8944
|  | Safety risk | 1498.9959 | 1781.7596 | 2139.8891 | 2597.6995 | 3219.4325 | 4047.5542 | 5105.4914 | 6460.5519 | 8200.8015 | 10442.0259 | 13337.5152 | 17087.1582 | 21957.3402 | 28302.297 | 36594.7438 | 47467.7568 | 58218.3171 | 65369.478 | 73292.2505 | 83982.8846 | 97034.2748 | 97056.4346 | 97081.5594 | 97110.0866 | 97142.5237
|  | Unplanned replacement risk | 3376.5693 | 4024.3128 | 4867.6271 | 5998.4979 | 7479.0484 | 9406.9689 | 11879.0618 | 15058.9179 | 19162.4696 | 24477.4668 | 31393.3153 | 40410.1907 | 52210.6849 | 67714.4049 | 88165.6395 | 115255.3042 | 143049.0113 | 163984.2266 | 174337.3387 | 185005.318 | 197930.0779 | 198047.7773 | 198182.8175 | 198337.989 | 198516.5619
|  | Unplanned fault risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Other risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total relay risks | 6040.3346 | 7011.5077 | 8342.1676 | 10274.3199 | 12854.0977 | 16273.4801 | 20720.3037 | 26528.8244 | 34150.3305 | 44202.7772 | 57551.7292 | 75308.5144 | 99043.742 | 130925.6348 | 173959.8595 | 232329.5619 | 299574.8332 | 367877.8651 | 394532.0907 | 417947.0288 | 446432.4894 | 446744.4307 | 447107.2336 | 447529.7323 | 448022.3597
Total SWBD and relay risk
|  | Energy at Risk ($) | 62651.8352 | 70757.5654 | 72315.8049 | 73067.1064 | 73501.1686 | 74168.9339 | 75600.1527 | 77678.4143 | 79142.5749 | 81331.1185 | 84472.403 | 88950.9565 | 95353.0581 | 104526.3293 | 117697.3909 | 136642.8094 | 163930.5748 | 203286.2336 | 210574.862 | 211126.0538 | 211797.8436 | 211967.4363 | 212167.28 | 212402.9401 | 212681.0251
|  | Safety risk | 2031.4306 | 2314.1942 | 2672.3237 | 3130.1342 | 3751.8672 | 4579.9889 | 5637.9261 | 6992.9866 | 8733.2362 | 10974.4606 | 13869.9498 | 17619.5929 | 22489.7749 | 28834.7316 | 37127.1785 | 48000.1915 | 58750.7518 | 65901.9126 | 73824.6851 | 84515.3193 | 97566.7095 | 97588.8693 | 97613.9941 | 97642.5212 | 97674.9584
|  | Unplanned replacement risk | 11476.5693 | 12124.3128 | 12967.6271 | 14098.4979 | 15579.0484 | 17506.9689 | 19979.0618 | 23158.9179 | 27262.4696 | 32577.4668 | 39493.3153 | 48510.1907 | 60310.6849 | 75814.4049 | 96265.6395 | 123355.3042 | 151149.0113 | 172084.2266 | 182437.3387 | 193105.318 | 206030.0779 | 206147.7773 | 206282.8175 | 206437.989 | 206616.5619
|  | Unplanned fault risk | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762
|  | Environmental risk | 207.6826 | 247.5274 | 297.7007 | 361.1701 | 447.3266 | 561.9833 | 708.199 | 895.1078 | 1134.6152 | 1442.2967 | 1838.6265 | 2350.3397 | 3012.7895 | 3872.7345 | 4992.2159 | 6453.8222 | 7867.0608 | 8728.0577 | 9817.7703 | 11322.903 | 13160.4239 | 13162.9133 | 13165.7074 | 13168.8473 | 13172.3797
|  | Other risk | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000
|  | Total SWBD and relay risks | 107129.5176 | 116205.5999 | 119015.4564 | 121418.9087 | 124041.4108 | 127579.8749 | 132687.3396 | 139487.4266 | 147034.8959 | 157087.3426 | 170436.2946 | 188193.0798 | 211928.3074 | 243810.2002 | 286844.4249 | 345214.1273 | 412459.3986 | 480762.4305 | 507416.6561 | 530831.5942 | 559317.0548 | 559628.9961 | 559991.799 | 560414.2977 | 560906.9251
Option 2 - Decomission switchboard and connect transformers and VR Cremorne feeders to RMU
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
SWBD risks
|  | Energy at Risk ($) | 61694.7483 | 6887.8557 | 7032.6639 | 7078.7951 | 7082.9881 | 7094.6408 | 7159.3308 | 7256.4244 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835
|  | Safety risk | 532.4347 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435
|  | Unplanned replacement risk | 8100 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810
|  | Unplanned fault risk | 762 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
|  | Other risk | 30000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total SWBD risks | 101089.183 | 7827.2992 | 7972.1074 | 8018.2386 | 8022.4316 | 8034.0843 | 8098.7742 | 8195.8679 | 8188.6269 | 8188.6269 | 8188.6269 | 8188.6269 | 8188.6269 | 8188.6269 | 8188.6269 | 8188.6269 | 8188.6269 | 8188.6269 | 8188.6269 | 8188.6269 | 8188.6269 | 8188.6269 | 8188.6269 | 8188.6269 | 8188.6269
Relay risks
|  | Environmental risk | 207.6826 | 80.1943 | 81.3126 | 82.6883 | 84.5719 | 87.3372 | 97.0818 | 115.4361 | 140.1436 | 173.5801 | 219.0556 | 281.2074 | 366.5868 | 484.1994 | 646.8155 | 872.4197 | 1186.381 | 1624.5381 | 2244.5088 | 3117.9417 | 4225.0648 | 5754.588 | 7626.3091 | 7676.8084 | 7747.0835
|  | Energy at Risk ($) | 957.0869 | 955.0723 | 955.3065 | 955.5946 | 1033.9679 | 1313.1272 | 1703.404 | 2250.7495 | 3019.6382 | 4104.199 | 5639.6968 | 7824.823 | 10961.7784 | 15434.8436 | 21829.9827 | 30994.4162 | 44154.2531 | 63085.4079 | 90362.1111 | 129717.9385 | 137006.7983 | 137558.3093 | 138230.5409 | 138400.7476 | 138601.4474
|  | Safety risk | 1498.9959 | 594.2687 | 602.2086 | 611.9766 | 627.4193 | 654.4429 | 733.9192 | 878.6316 | 1074.2857 | 1340.2311 | 1703.533 | 2202.3566 | 2891.1863 | 3844.095 | 5167.2073 | 7010.5639 | 9586.6366 | 13196.7417 | 18317.8745 | 25557.2865 | 33603.612 | 44467.3302 | 57761.4177 | 58124.2731 | 58628.2656
|  | Unplanned replacement risk | 3376.5693 | 1143.1879 | 1152.9287 | 1164.9121 | 1210.5786 | 1339.1929 | 1558.65 | 1897.7675 | 2365.8298 | 3015.1637 | 3920.1861 | 5188.582 | 6980.5551 | 9504.4315 | 13071.064 | 18126.4215 | 25311.1607 | 35546.6973 | 50250.8133 | 71333.3326 | 81897.5675 | 92866.719 | 106219.7759 | 106945.3611 | 107942.1978
|  | Unplanned fault risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Other risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total relay risks | 6040.3346 | 2772.7233 | 2791.7565 | 2815.1716 | 2956.5377 | 3394.1002 | 4093.0551 | 5142.5848 | 6599.8972 | 8633.1738 | 11482.4714 | 15496.9691 | 21200.1065 | 29267.5695 | 40715.0695 | 57003.8213 | 80238.4315 | 113453.385 | 161175.3077 | 229726.4992 | 256733.0427 | 280646.9466 | 309838.0436 | 311147.1902 | 312918.9943
Total SWBD and relay risk
|  | Energy at Risk ($) | 62651.8352 | 7842.928 | 7987.9704 | 8034.3897 | 8116.956 | 8407.768 | 8862.7347 | 9507.174 | 10268.8216 | 11353.3825 | 12888.8802 | 15074.0065 | 18210.9618 | 22684.0271 | 29079.1662 | 38243.5996 | 51403.4366 | 70334.5914 | 97611.2945 | 136967.1219 | 144255.9818 | 144807.4928 | 145479.7243 | 145649.9311 | 145850.6309
|  | Safety risk | 2031.4306 | 647.5122 | 655.4521 | 665.22 | 680.6628 | 707.6864 | 787.1627 | 931.875 | 1127.5291 | 1393.4745 | 1756.7764 | 2255.6001 | 2944.4297 | 3897.3384 | 5220.4507 | 7063.8074 | 9639.8801 | 13249.9851 | 18371.118 | 25610.5299 | 33656.8555 | 44520.5737 | 57814.6612 | 58177.5166 | 58681.5091
|  | Unplanned replacement risk | 11476.5693 | 1953.1879 | 1962.9287 | 1974.9121 | 2020.5786 | 2149.1929 | 2368.65 | 2707.7675 | 3175.8298 | 3825.1637 | 4730.1861 | 5998.582 | 7790.5551 | 10314.4315 | 13881.064 | 18936.4215 | 26121.1607 | 36356.6973 | 51060.8133 | 72143.3326 | 82707.5675 | 93676.719 | 107029.7759 | 107755.3611 | 108752.1978
|  | Unplanned fault risk | 762 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
|  | Environmental risk | 207.6826 | 80.1943 | 81.3126 | 82.6883 | 84.5719 | 87.3372 | 97.0818 | 115.4361 | 140.1436 | 173.5801 | 219.0556 | 281.2074 | 366.5868 | 484.1994 | 646.8155 | 872.4197 | 1186.381 | 1624.5381 | 2244.5088 | 3117.9417 | 4225.0648 | 5754.588 | 7626.3091 | 7676.8084 | 7747.0835
|  | Other risk | 30000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total SWBD and relay risks | 107129.5176 | 10600.0224 | 10763.8638 | 10833.4102 | 10978.9693 | 11428.1844 | 12191.8293 | 13338.4527 | 14788.5242 | 16821.8008 | 19671.0983 | 23685.596 | 29388.7335 | 37456.1965 | 48903.6964 | 65192.4482 | 88427.0584 | 121642.0119 | 169363.9346 | 237915.1261 | 264921.6696 | 288835.5735 | 318026.6705 | 319335.8172 | 321107.6212
Option 3 - Decomission switchboard, direct connect transformers and connect VR Cremorne feeders to RTS
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
SWBD risks
|  | Energy at Risk ($) | 61694.7483 | 4130.2695 | 4217.0718 | 4244.7241 | 4247.2377 | 4254.2226 | 4293.0001 | 4351.2015 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612
|  | Safety risk | 532.4347 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948
|  | Unplanned replacement risk | 8100 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486
|  | Unplanned fault risk | 762 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
|  | Other risk | 30000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total SWBD risks | 101089.183 | 4735.0643 | 4821.8666 | 4849.5188 | 4852.0325 | 4859.0174 | 4897.7948 | 4955.9963 | 4951.656 | 4951.656 | 4951.656 | 4951.656 | 4951.656 | 4951.656 | 4951.656 | 4951.656 | 4951.656 | 4951.656 | 4951.656 | 4951.656 | 4951.656 | 4951.656 | 4951.656 | 4951.656 | 4951.656
Relay risks
|  | Environmental risk | 207.6826 | 80.1943 | 81.3126 | 82.6883 | 84.5719 | 87.3372 | 97.0818 | 115.4361 | 140.1436 | 173.5801 | 219.0556 | 281.2074 | 366.5868 | 484.1994 | 646.8155 | 872.4197 | 1186.381 | 1624.5381 | 2244.5088 | 3117.9417 | 4225.0648 | 5754.588 | 7626.3091 | 7676.8084 | 7747.0835
|  | Energy at Risk ($) | 957.0869 | 955.0723 | 955.3065 | 955.5946 | 1033.9679 | 1313.1272 | 1703.404 | 2250.7495 | 3019.6382 | 4104.199 | 5639.6968 | 7824.823 | 10961.7784 | 15434.8436 | 21829.9827 | 30994.4162 | 44154.2531 | 63085.4079 | 90362.1111 | 129717.9385 | 137006.7983 | 137558.3093 | 138230.5409 | 138400.7476 | 138601.4474
|  | Safety risk | 1498.9959 | 594.2687 | 602.2086 | 611.9766 | 627.4193 | 654.4429 | 733.9192 | 878.6316 | 1074.2857 | 1340.2311 | 1703.533 | 2202.3566 | 2891.1863 | 3844.095 | 5167.2073 | 7010.5639 | 9586.6366 | 13196.7417 | 18317.8745 | 25557.2865 | 33603.612 | 44467.3302 | 57761.4177 | 58124.2731 | 58628.2656
|  | Unplanned replacement risk | 3376.5693 | 1143.1879 | 1152.9287 | 1164.9121 | 1210.5786 | 1339.1929 | 1558.65 | 1897.7675 | 2365.8298 | 3015.1637 | 3920.1861 | 5188.582 | 6980.5551 | 9504.4315 | 13071.064 | 18126.4215 | 25311.1607 | 35546.6973 | 50250.8133 | 71333.3326 | 81897.5675 | 92866.719 | 106219.7759 | 106945.3611 | 107942.1978
|  | Unplanned fault risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Other risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total relay risks | 6040.3346 | 2772.7233 | 2791.7565 | 2815.1716 | 2956.5377 | 3394.1002 | 4093.0551 | 5142.5848 | 6599.8972 | 8633.1738 | 11482.4714 | 15496.9691 | 21200.1065 | 29267.5695 | 40715.0695 | 57003.8213 | 80238.4315 | 113453.385 | 161175.3077 | 229726.4992 | 256733.0427 | 280646.9466 | 309838.0436 | 311147.1902 | 312918.9943
Total SWBD and relay risk
|  | Energy at Risk ($) | 62651.8352 | 5085.3419 | 5172.3784 | 5200.3187 | 5281.2056 | 5567.3497 | 5996.404 | 6601.951 | 7366.4994 | 8451.0602 | 9986.558 | 12171.6842 | 15308.6396 | 19781.7048 | 26176.844 | 35341.2774 | 48501.1143 | 67432.2691 | 94708.9723 | 134064.7997 | 141353.6595 | 141905.1705 | 142577.4021 | 142747.6088 | 142948.3086
|  | Safety risk | 2031.4306 | 636.8635 | 644.8034 | 654.5713 | 670.0141 | 697.0377 | 776.514 | 921.2264 | 1116.8804 | 1382.8258 | 1746.1277 | 2244.9514 | 2933.781 | 3886.6898 | 5209.802 | 7053.1587 | 9629.2314 | 13239.3364 | 18360.4693 | 25599.8813 | 33646.2068 | 44509.925 | 57804.0125 | 58166.8679 | 58670.8604
|  | Unplanned replacement risk | 11476.5693 | 1629.1879 | 1638.9287 | 1650.9121 | 1696.5786 | 1825.1929 | 2044.65 | 2383.7675 | 2851.8298 | 3501.1637 | 4406.1861 | 5674.582 | 7466.5551 | 9990.4315 | 13557.064 | 18612.4215 | 25797.1607 | 36032.6973 | 50736.8133 | 71819.3326 | 82383.5675 | 93352.719 | 106705.7759 | 107431.3611 | 108428.1978
|  | Unplanned fault risk | 762 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
|  | Environmental risk | 207.6826 | 80.1943 | 81.3126 | 82.6883 | 84.5719 | 87.3372 | 97.0818 | 115.4361 | 140.1436 | 173.5801 | 219.0556 | 281.2074 | 366.5868 | 484.1994 | 646.8155 | 872.4197 | 1186.381 | 1624.5381 | 2244.5088 | 3117.9417 | 4225.0648 | 5754.588 | 7626.3091 | 7676.8084 | 7747.0835
|  | Other risk | 30000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total SWBD and relay risks | 107129.5176 | 7507.7876 | 7613.6231 | 7664.6904 | 7808.5703 | 8253.1175 | 8990.8499 | 10098.581 | 11551.5532 | 13584.8298 | 16434.1274 | 20448.6251 | 26151.7625 | 34219.2255 | 45666.7255 | 61955.4773 | 85190.0875 | 118405.041 | 166126.9637 | 234678.1552 | 261684.6986 | 285598.6025 | 314789.6995 | 316098.8462 | 317870.6503

## SWBD risks
CitiPower
R switchboard and relay retirement
Input Data - Station Configuration |  | Constants |  |  | POF METHOD | FIXED | Modifier (x) | Comment
Substation: | R | Major Failure CoC |  |  | PoF (#1) | 0.25% | 100%
Asset Type | Indoor CB | Minor Failure CoC |  |  | PoF (#2) | 0.25% | 100%
VCR | 50.105 | Major Failure CoC - used | 1080000 |  | PoF (#3) | 0.25% | 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 101600 |  | PoF (#4) | 0% | 100%
Scenario #1: R - Indoor CB | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 0% | 0 | Energy | 1002.7589 | 1215.4825 | 1369.8261 | 1396.133 | 1402.2936 | 1401.5265 | 1402.6576 | 1414.5925 | 1430.9391 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226
Online Monitoring | 0% | 50000 | Energy | 1037.5783 | 1268.2382 | 1447.298 | 1484.3219 | 1501.3011 | 1505.9334 | 1511.2164 | 1527.3188 | 1555.1425 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881 | 1558.881
Physical Separation | 0% | 300000 | Energy | 1002.7589 | 1215.4825 | 1369.8261 | 1396.133 | 1402.2936 | 1401.5265 | 1402.6576 | 1414.5925 | 1430.9391 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226 | 1427.226
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 50766.6223 | 61694.7483 | 69799.6576 | 71278.8541 | 71750.1541 | 71792.8784 | 71911.9601 | 72572.6012 | 73564.1675 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307 | 73490.1307
Replace 1 Asset | 0% | 900000 | Safety Risk | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347 | 532.4347
Replace 2 Assets | 0% | 1800000 | Unplanned Replacement Risk | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100 | 8100
Replace 3 Assets | 0% | 2700000 | Unplanned Fault Risk | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Total Life Cycle Cost | 90161.057 | 101089.183 | 109194.0922 | 110673.2888 | 111144.5888 | 111187.3131 | 111306.3948 | 111967.0359 | 112958.6022 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654 | 112884.5654
Input Data - Station Configuration |  | Constants |  | PoF (#4) 2026: POF METHOD; 0% 2027: FIXED; 100% 2028: Modifier (x); 100% 2029: Comment
Substation: | R | Major Failure CoC |  | PoF (#4) 2026: PoF (#1); 0% 2027: 0.25%; 100% 2028: 100%
Asset Type | Indoor CB | Minor Failure CoC |  | PoF (#4) 2026: PoF (#2); 0% 2027: 0.25%; 100% 2028: 100%
VCR | 50.105 | Major Failure CoC - used | 1080000 | PoF (#4) 2026: PoF (#3); 0% 2027: 0.25%; 100% 2028: 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 101600 | PoF (#4) 2026: PoF (#4); 0% 2027: 0%; 100% 2028: 100%
Scenario #2: R - Indoor CB | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 0% | 0 | Energy | 1002.7589 | 1215.4825 | 135.2833 | 137.859 | 138.4621 | 138.3873 | 138.4977 | 139.6666 | 141.2672 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037
Online Monitoring | 0% | 50000 | Energy | 1037.5783 | 1268.2382 | 142.567 | 146.1908 | 147.8526 | 148.3061 | 148.8236 | 150.3998 | 153.1244 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907 | 153.4907
Physical Separation | 0% | 300000 | Energy | 1002.7589 | 1215.4825 | 135.2833 | 137.859 | 138.4621 | 138.3873 | 138.4977 | 139.6666 | 141.2672 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037 | 140.9037
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.75% | 0.75% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 0.75% | 0.75% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 50766.6223 | 61694.7483 | 6887.8557 | 7032.6639 | 7078.7951 | 7082.9881 | 7094.6408 | 7159.3308 | 7256.4244 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835 | 7249.1835
Replace 1 Asset | 0% | 900000 | Safety Risk | 532.4347 | 532.4347 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435 | 53.2435
Replace 2 Assets | 0% | 1800000 | Unplanned Replacement Risk | 8100 | 8100 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810 | 810
Replace 3 Assets | 100% | 2700000 | Unplanned Fault Risk | 762 | 762 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 0 | 0 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158
|  |  | Total Life Cycle Cost | 60161.057 | 71089.183 | 122938.315 | 123083.1232 | 123129.2544 | 123133.4474 | 123145.1001 | 123209.7901 | 123306.8837 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428 | 123299.6428
Input Data - Station Configuration |  | Constants |  | PoF (#4) 2026: POF METHOD; 0% 2027: FIXED; 100% 2028: Modifier (x); 100% 2029: Comment
Substation: | R | Major Failure CoC |  | PoF (#4) 2026: PoF (#1); 0% 2027: 0.15%; 100% 2028: 60%
Asset Type | Indoor CB | Minor Failure CoC |  | PoF (#4) 2026: PoF (#2); 0% 2027: 0.15%; 100% 2028: 60%
VCR | 50.105 | Major Failure CoC - used | 1080000 | PoF (#4) 2026: PoF (#3); 0% 2027: 0.15%; 100% 2028: 60%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 101600 | PoF (#4) 2026: PoF (#4); 0% 2027: 0%; 100% 2028: 60%
Scenario #3: R - Indoor CB | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 0% | 0 | Energy | 599.1994 | 725.6302 | 81.1249 | 82.6688 | 83.0303 | 82.9855 | 83.0517 | 83.7524 | 84.7118 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494
Online Monitoring | 0% | 50000 | Energy | 619.2468 | 756.2199 | 85.4828 | 87.655 | 88.6511 | 88.923 | 89.2332 | 90.178 | 91.8112 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308 | 92.0308
Physical Separation | 0% | 300000 | Energy | 599.1994 | 725.6302 | 81.1249 | 82.6688 | 83.0303 | 82.9855 | 83.0517 | 83.7524 | 84.7118 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494 | 84.494
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.45% | 0.45% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045% | 0.045%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 0.75% | 0.75% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075% | 0.075%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 30324.228 | 36817.5104 | 4130.2695 | 4217.0718 | 4244.7241 | 4247.2377 | 4254.2226 | 4293.0001 | 4351.2015 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612 | 4346.8612
Replace 1 Asset | 0% | 900000 | Safety Risk | 425.9477 | 425.9477 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948 | 42.5948
Replace 2 Assets | 0% | 1800000 | Unplanned Replacement Risk | 4860 | 4860 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486
Replace 3 Assets | 100% | 2700000 | Unplanned Fault Risk | 762 | 762 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 0 | 0 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158 | 115111.0158
|  |  | Total Life Cycle Cost | 36372.1757 | 42865.4581 | 119846.0801 | 119932.8824 | 119960.5347 | 119963.0483 | 119970.0332 | 120008.8107 | 120067.0121 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718 | 120062.6718

## Misc_calcs
CitiPower
R switchboard and relay retirement
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 1 | TRUE
| Option 3 | 1 | TRUE
| Option 4 | Not used | FALSE
| Option 5 | Not used | FALSE
| First year | 1
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
CitiPower
R switchboard and relay retirement
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | TRUE | Not used |  | TRUE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
|  |  | CitiPower | Powercor | United Energy
| Reliability in worst-served areas | per MWh | 0 | 151432.8174 | 0
| Network resilience | per MWh | 0 | 24590 | 38560
| Enabling solar exports | per MWh | 4220.9954 | 88.3577 | 862.6028
| Aesthetics | per customer impacted | 0 | 0 | 0
| Customer value of time - residential | per minute customer time | 0.54769 | 0.35181 | 0.34751
| Customer value of time - business | per minute customer time | 0.54769 | 0.35181 | 0.34751
| Communication | per customer impacted | 0 | 0 | 0
| Information accessibility | per customer impacted | 0 | 0 | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020