## Cover
CitiPower
Regulatory proposal 2026-31
Relay replacement
| Model number: | 4.11
2025-01-31
15

## Summary
CitiPower
Relay replacements
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Replace all ageing relays at zone substations |  | -6.3926 | 18.7324 | 12.3399
| Option 3 | Defer investment to 2032-33 |  | -4.0919 | 15.5391 | 11.4472
| Option 4 | 0
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | Replace all ageing relays at zone substations |  | 12.3399
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 3.1798 | 5.5951 | 0 | 0 | 0 |  | 8.7749
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
Capex and risk ($M, 2026)
PREFERRED OPTION DATA
Select category for table:
Capital expenditure
|  | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Option 1 (base case) | No change to existing practices | 0 | 0 | 0 | 0 | 0 |  | 0
| Option 2 | Replace all ageing relays at zone substations | 3.1798 | 5.5951 | 0 | 0 | 0 |  | 8.7749
| Option 3 | Defer investment to 2032-33 | 0 | 0 | 0 | 0 | 0 |  | 0
| Option 4 | 0
| Option 5 | 0
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 12.3399 | 11.4472 |  |  |  | Option 2
| Capex 10% higher |  | 0 | 11.7006 | 11.038 |  |  |  | Option 2
| Capex 10% lower |  | 0 | 12.9791 | 11.8564 |  |  |  | Option 2
| Total benefits 10% higher |  | 0 | 14.2131 | 13.0011 |  |  |  | Option 2
| Total benefits 10% lower |  | 0 | 10.4666 | 9.8933 |  |  |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  | 0 | 9.8274 | 9.4841 |  |  |  | Option 2
0
| 0 | [6 empty] | 0
0
0

## Assumptions
CitiPower
Relay replacements
Project
|  | Business: | select > | CitiPower
|  | Descripton: |  | Relay replacements
|  | Date of cost inputs: | select > | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Replace all ageing relays at zone substations
|  | Option 3 |  | Defer investment to 2032-33
Option 4
Option 5
|  | Compliance project |  | No
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | Network average |  | Network average | 43815.4862 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 0 | 2023-12-31 | per MWh
|  | Network resilience |  |  |  | 0 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 4220.9954 | 2023-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
CitiPower
Relay replacements
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Relay replacement capex |  | 28 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety | (after DF) |  | 2023-12-31 |  | 9383.6998 | 10369.2056 | 11483.62 | 12748.7718 | 14199.5693 | 15930.9908 | 17960.9269 | 20384.6609 | 23281.5036 | 26751.4767 | 30956.5965 | 36118.8141 | 42545.8705 | 50669.2409 | 61100.0832 | 74712.073 | 91179.7547 | 112425.4667 | 133649.2318 | 146850.3256 | 160393.8761 | 174969.2593 | 191029.9066 | 206005.4004 | 215791.4086
| Environment |  |  | 2023-12-31 |  | 716.6175 | 788.6616 | 870.4699 | 963.9408 | 1072.6339 | 1208.359 | 1371.3224 | 1573.0169 | 1822.3333 | 2130.4801 | 2516.9236 | 3009.0125 | 3645.5192 | 4481.8671 | 5597.8707 | 7109.2379 | 9091.4653 | 11744.3821 | 14348.8155 | 15771.0148 | 17181.7916 | 18714.3008 | 20420.5825 | 21903.1277 | 22573.8647
| NP | (after DF) |  | 2023-12-31 |  | 149513.302 | 163065.1597 | 178016.851 | 194530.2945 | 212789.3697 | 233005.4425 | 255827.5608 | 281379.9061 | 309832.9615 | 341570.4619 | 377036.8343 | 416748.6183 | 461308.3773 | 511421.7197 | 567918.2283 | 631777.3339 | 701790.9 | 780449.6849 | 869864.2472 | 971252.9987 | 1087051.0433 | 1193334.6121 | 1293812.7533 | 1405384.7391 | 1529385.5898
| Financial |  |  | 2023-12-31 |  | 262811.1396 | 291623.2868 | 324017.289 | 360491.5031 | 401635.8889 | 448217.3767 | 501013.6204 | 560976.0535 | 629167.1287 | 706853.1489 | 795569.7086 | 897153.071 | 1013815.7644 | 1148247.148 | 1303749.1911 | 1484422.4914 | 1641380.8548 | 1805616.2795 | 1986417.7867 | 2173924.2772 | 2383222.7029 | 2609993.412 | 2858167.8479 | 3133587.2654 | 3434963.9124
| 0 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 422424.7589 | 465846.3138 | 514388.2298 | 568734.5102 | 629697.4617 | 698362.1691 | 776173.4306 | 864313.6374 | 964103.9271 | 1077305.5676 | 1206080.063 | 1353029.516 | 1521315.5314 | 1714819.9757 | 1938365.3733 | 2198021.1362 | 2443442.9748 | 2710235.8132 | 3004280.0812 | 3307798.6164 | 3647849.4139 | 3997011.5842 | 4363431.0903 | 4766880.5327 | 5202714.7755
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| Relay replacement capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Relay replacement capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Relay replacement capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
CitiPower
Relay replacements
OPTION 2 | Replace all ageing relays at zone substations
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Relay replacement capex |  | 28 | 2023-12-31 | 2857212 | 5027445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 2857212 | 5027445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety | (after DF) |  | 2023-12-31 | 9383.6998 | 8286.6632 | 3274.0225 | 3334.7709 | 3420.2361 | 3596.8761 | 3846.0385 | 4229.0016 | 4781.6953 | 5548.2396 | 6621.8172 | 8138.9794 | 10300.6988 | 13403.9358 | 17889.0767 | 24411.3649 | 34414.2468 | 48704.4029 | 65180.1459 | 73629.0558 | 82087.3686 | 92371.1 | 105479.5796 | 118414.6078 | 127712.536
| Environment |  |  | 2023-12-31 | 716.6175 | 689.6251 | 449.8148 | 457.5145 | 468.6264 | 492.5088 | 526.5259 | 579.3076 | 655.9087 | 762.537 | 912.3136 | 1124.4698 | 1427.3134 | 1862.6767 | 2492.6005 | 3409.3991 | 4816.4055 | 6827.2482 | 9145.7653 | 10333.1315 | 11521.5608 | 12966.8738 | 14809.8698 | 16627.8239 | 17932.4058
| NP | (after DF) |  | 2023-12-31 | 149513.302 | 14349.8207 | 1088.2463 | 1162.7956 | 1243.7368 | 1333.8187 | 1433.657 | 1543.7474 | 1665.9182 | 1802.6314 | 1957.2802 | 2134.6367 | 2341.5304 | 2587.8741 | 2888.2212 | 3264.1312 | 3767.3549 | 4445.3379 | 5262.4214 | 5695.8502 | 6104.9583 | 6575.252 | 7117.7581 | 7768.3536 | 8561.886
| Financial |  |  | 2023-12-31 | 262811.1396 | 212208.7566 | 11235.8208 | 11866.1527 | 12577.6973 | 13480.4897 | 14542.761 | 15857.5249 | 17484.6678 | 19499.2925 | 22047.5361 | 25341.6976 | 29692.3044 | 35556.2492 | 43609.2171 | 54854.8853 | 71345.6888 | 94466.2573 | 120338.9222 | 133865.4418 | 147031.1899 | 162552.7069 | 181122.2079 | 199608.6604 | 213701.6672
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 422424.7589 | 235534.8656 | 16047.9045 | 16821.2336 | 17710.2967 | 18903.6934 | 20348.9824 | 22209.5815 | 24588.19 | 27612.7006 | 31538.9472 | 36739.7836 | 43761.847 | 53410.7359 | 66879.1156 | 85939.7805 | 114343.6961 | 154443.2463 | 199927.2547 | 223523.4793 | 246745.0776 | 274465.9327 | 308529.4154 | 342419.4458 | 367908.495
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 230311.4482 | 498340.3252 | 551913.2766 | 611987.1651 | 679458.4757 | 755824.4482 | 842104.0559 | 939515.7371 | 1049692.867 | 1174541.1159 | 1316289.7324 | 1477553.6844 | 1661409.2398 | 1871486.2577 | 2112081.3557 | 2329099.2787 | 2555792.5668 | 2804352.8265 | 3084275.137 | 3401104.3363 | 3722545.6516 | 4054901.6749 | 4424461.0869 | 4834806.2804
Capital expenditure
| Relay replacement capex |  |  | 2023-12-31 | -2857212 | -5027445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Relay replacement capex |  |  | 2023-12-31 | -2857212 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Relay replacement capex |  |  | 2023-12-31 | 0 | -161725.7572 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -161725.7572 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429
| Annualised capex |  |  | 2023-12-31 | 0 | -161725.7572 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 230311.4482 | 498340.3252 | 551913.2766 | 611987.1651 | 679458.4757 | 755824.4482 | 842104.0559 | 939515.7371 | 1049692.867 | 1174541.1159 | 1316289.7324 | 1477553.6844 | 1661409.2398 | 1871486.2577 | 2112081.3557 | 2329099.2787 | 2555792.5668 | 2804352.8265 | 3084275.137 | 3401104.3363 | 3722545.6516 | 4054901.6749 | 4424461.0869 | 4834806.2804
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 68585.691 | 52047.8823 | 105620.8337 | 165694.7221 | 233166.0327 | 309532.0052 | 395811.613 | 493223.2942 | 603400.4241 | 728248.6729 | 869997.2894 | 1031261.2415 | 1215116.7969 | 1425193.8148 | 1665788.9128 | 1882806.8358 | 2109500.1239 | 2358060.3836 | 2637982.6941 | 2954811.8933 | 3276253.2086 | 3608609.232 | 3978168.644 | 4388513.8375
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | 68585.691 | 52047.8823 | 105620.8337 | 165694.7221 | 233166.0327 | 309532.0052 | 395811.613 | 493223.2942 | 603400.4241 | 728248.6729 | 869997.2894 | 1031261.2415 | 1215116.7969 | 1425193.8148 | 1665788.9128 | 1882806.8358 | 2109500.1239 | 2358060.3836 | 2637982.6941 | 2954811.8933 | 3276253.2086 | 3608609.232 | 3978168.644 | 4388513.8375
| Total annualised capex |  |  |  | 0 | -161725.7572 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429
| Total benefits |  |  |  | 0 | 230311.4482 | 498340.3252 | 551913.2766 | 611987.1651 | 679458.4757 | 755824.4482 | 842104.0559 | 939515.7371 | 1049692.867 | 1174541.1159 | 1316289.7324 | 1477553.6844 | 1661409.2398 | 1871486.2577 | 2112081.3557 | 2329099.2787 | 2555792.5668 | 2804352.8265 | 3084275.137 | 3401104.3363 | 3722545.6516 | 4054901.6749 | 4424461.0869 | 4834806.2804
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | 52413.1153 | 7418.638 | 60991.5894 | 121065.4778 | 188536.7884 | 264902.7609 | 351182.3687 | 448594.0499 | 558771.1798 | 683619.4286 | 825368.0452 | 986631.9972 | 1170487.5526 | 1380564.5705 | 1621159.6685 | 1838177.5915 | 2064870.8796 | 2313431.1393 | 2593353.4498 | 2910182.6491 | 3231623.9644 | 3563979.9877 | 3933539.3997 | 4343884.5932
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | 84758.2667 | 96677.1266 | 150250.078 | 210323.9664 | 277795.277 | 354161.2495 | 440440.8573 | 537852.5385 | 648029.6684 | 772877.9172 | 914626.5337 | 1075890.4858 | 1259746.0411 | 1469823.0591 | 1710418.1571 | 1927436.0801 | 2154129.3682 | 2402689.6279 | 2682611.9384 | 2999441.1376 | 3320882.4529 | 3653238.4763 | 4022797.8883 | 4433143.0818
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | 91616.8358 | 101881.9148 | 160812.1613 | 226893.4386 | 301111.8803 | 385114.4501 | 480022.0186 | 587174.8679 | 708369.7108 | 845702.7845 | 1001626.2627 | 1179016.6099 | 1381257.7208 | 1612342.4406 | 1876997.0483 | 2115716.7637 | 2365079.3806 | 2638495.6662 | 2946410.2078 | 3294922.327 | 3648507.7738 | 4014099.3995 | 4420614.7527 | 4871994.4656
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | 45554.5462 | 2213.8498 | 50429.506 | 104496.0056 | 165220.1852 | 233949.5604 | 311601.2074 | 399271.7205 | 498431.1374 | 610794.5614 | 738368.3162 | 883505.873 | 1048975.8729 | 1238045.189 | 1454580.7772 | 1649896.9079 | 1853920.8672 | 2077625.1009 | 2329555.1804 | 2614701.4597 | 2903998.6435 | 3203119.0645 | 3535722.5353 | 3905033.2095
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | 29381.9705 | -42415.3945 | 5800.2617 | 59866.7613 | 120590.9409 | 189320.3161 | 266971.9631 | 354642.4762 | 453801.8931 | 566165.3171 | 693739.0719 | 838876.6287 | 1004346.6286 | 1193415.9447 | 1409951.5329 | 1605267.6636 | 1809291.6229 | 2032995.8566 | 2284925.9361 | 2570072.2154 | 2859369.3992 | 3158489.8202 | 3491093.291 | 3860403.9652
sens | 0 | 0% | 0% | Option 2sens | 0 | 68585.691 | 52047.8823 | 105620.8337 | 165694.7221 | 233166.0327 | 309532.0052 | 395811.613 | 493223.2942 | 603400.4241 | 728248.6729 | 869997.2894 | 1031261.2415 | 1215116.7969 | 1425193.8148 | 1665788.9128 | 1882806.8358 | 2109500.1239 | 2358060.3836 | 2637982.6941 | 2954811.8933 | 3276253.2086 | 3608609.232 | 3978168.644 | 4388513.8375
sens | 0 | 0% | 0% | Option 2sens | 0 | 68585.691 | 52047.8823 | 105620.8337 | 165694.7221 | 233166.0327 | 309532.0052 | 395811.613 | 493223.2942 | 603400.4241 | 728248.6729 | 869997.2894 | 1031261.2415 | 1215116.7969 | 1425193.8148 | 1665788.9128 | 1882806.8358 | 2109500.1239 | 2358060.3836 | 2637982.6941 | 2954811.8933 | 3276253.2086 | 3608609.232 | 3978168.644 | 4388513.8375
sens | 0 | 0% | 0% | Option 2sens | 0 | 68585.691 | 52047.8823 | 105620.8337 | 165694.7221 | 233166.0327 | 309532.0052 | 395811.613 | 493223.2942 | 603400.4241 | 728248.6729 | 869997.2894 | 1031261.2415 | 1215116.7969 | 1425193.8148 | 1665788.9128 | 1882806.8358 | 2109500.1239 | 2358060.3836 | 2637982.6941 | 2954811.8933 | 3276253.2086 | 3608609.232 | 3978168.644 | 4388513.8375

## Option3
CitiPower
Relay replacements
OPTION 3 | Defer investment to 2032-33
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Relay replacement capex deferred tp FY33 |  | 28 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 7884657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 7884657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety | (after DF) |  | 2023-12-31 | 9383.6998 | 10369.2056 | 11483.62 | 12748.7718 | 14199.5693 | 15930.9908 | 20325.0499 | 4229.0016 | 4781.6953 | 5548.2396 | 6621.8172 | 8138.9794 | 10300.6988 | 13403.9358 | 17889.0767 | 24876.949 | 35335.4841 | 49968.9795 | 66923.8417 | 76043.2243 | 85442.1605 | 97048.5193 | 112020.5685 | 127586.1573 | 140603.3966
| Environment |  |  | 2023-12-31 | 716.6175 | 788.6616 | 870.4699 | 963.9408 | 1072.6339 | 1208.359 | 1704.2248 | 579.3076 | 655.9087 | 762.537 | 912.3136 | 1124.4698 | 1427.3134 | 1862.6767 | 2492.6005 | 3474.96 | 4946.1289 | 7005.3186 | 9391.3026 | 10673.081 | 11993.9634 | 13625.5213 | 15730.9346 | 17919.3092 | 19747.6233
| NP | (after DF) |  | 2023-12-31 | 149513.302 | 163065.1597 | 178016.851 | 194530.2945 | 212789.3697 | 233005.4425 | 255927.034 | 1543.7474 | 1665.9182 | 1802.6314 | 1957.2802 | 2134.6367 | 2341.5304 | 2587.8741 | 2888.2212 | 3283.7212 | 3806.117 | 4498.5465 | 5335.7894 | 5797.4291 | 6246.115 | 6772.0598 | 7392.9777 | 8154.2571 | 9104.2838
| Financial |  |  | 2023-12-31 | 262811.1396 | 291623.2868 | 324017.289 | 360491.5031 | 401635.8889 | 448217.3767 | 503835.8749 | 15857.5249 | 17484.6678 | 19499.2925 | 22047.5361 | 25341.6976 | 29692.3044 | 35556.2492 | 43609.2171 | 55410.6925 | 72445.4481 | 95975.8898 | 122420.5201 | 136747.4399 | 151036.0901 | 168136.5397 | 188930.7421 | 210557.5185 | 229090.5828
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 422424.7589 | 465846.3138 | 514388.2298 | 568734.5102 | 629697.4617 | 698362.1691 | 781792.1835 | 22209.5815 | 24588.19 | 27612.7006 | 31538.9472 | 36739.7836 | 43761.847 | 53410.7359 | 66879.1156 | 87046.3227 | 116533.1781 | 157448.7344 | 204071.4537 | 229261.1742 | 254718.329 | 285582.6402 | 324075.2229 | 364217.2422 | 398545.8864
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | -5618.7529 | 842104.0559 | 939515.7371 | 1049692.867 | 1174541.1159 | 1316289.7324 | 1477553.6844 | 1661409.2398 | 1871486.2577 | 2110974.8135 | 2326909.7967 | 2552787.0788 | 2800208.6275 | 3078537.4421 | 3393131.0849 | 3711428.9441 | 4039355.8674 | 4402663.2905 | 4804168.8891
Capital expenditure
| Relay replacement capex deferred tp FY33 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | -7884657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Relay replacement capex deferred tp FY33 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657 | -7884657
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Relay replacement capex deferred tp FY33 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | -5618.7529 | 842104.0559 | 939515.7371 | 1049692.867 | 1174541.1159 | 1316289.7324 | 1477553.6844 | 1661409.2398 | 1871486.2577 | 2110974.8135 | 2326909.7967 | 2552787.0788 | 2800208.6275 | 3078537.4421 | 3393131.0849 | 3711428.9441 | 4039355.8674 | 4402663.2905 | 4804168.8891
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | -5618.7529 | 395811.613 | 493223.2942 | 603400.4241 | 728248.6729 | 869997.2894 | 1031261.2415 | 1215116.7969 | 1425193.8148 | 1664682.3706 | 1880617.3538 | 2106494.6359 | 2353916.1846 | 2632244.9992 | 2946838.642 | 3265136.5011 | 3593063.4245 | 3956370.8476 | 4357876.4461
| First capex year |  |  | 7
| First year |  |  | 7
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | 0 | 0 | 0 | 0 | 0 | -5618.7529 | 395811.613 | 493223.2942 | 603400.4241 | 728248.6729 | 869997.2894 | 1031261.2415 | 1215116.7969 | 1425193.8148 | 1664682.3706 | 1880617.3538 | 2106494.6359 | 2353916.1846 | 2632244.9992 | 2946838.642 | 3265136.5011 | 3593063.4245 | 3956370.8476 | 4357876.4461
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429 | -446292.4429
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | -5618.7529 | 842104.0559 | 939515.7371 | 1049692.867 | 1174541.1159 | 1316289.7324 | 1477553.6844 | 1661409.2398 | 1871486.2577 | 2110974.8135 | 2326909.7967 | 2552787.0788 | 2800208.6275 | 3078537.4421 | 3393131.0849 | 3711428.9441 | 4039355.8674 | 4402663.2905 | 4804168.8891
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | 0 | 0 | 0 | 0 | 0 | -5618.7529 | 351182.3687 | 448594.0499 | 558771.1798 | 683619.4286 | 825368.0452 | 986631.9972 | 1170487.5526 | 1380564.5705 | 1620053.1263 | 1835988.1095 | 2061865.3916 | 2309286.9403 | 2587615.7549 | 2902209.3977 | 3220507.2569 | 3548434.1802 | 3911741.6033 | 4313247.2018
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | 0 | 0 | 0 | 0 | 0 | -5618.7529 | 440440.8573 | 537852.5385 | 648029.6684 | 772877.9172 | 914626.5337 | 1075890.4858 | 1259746.0411 | 1469823.0591 | 1709311.6149 | 1925246.5981 | 2151123.8802 | 2398545.4289 | 2676874.2435 | 2991467.8863 | 3309765.7454 | 3637692.6688 | 4001000.0919 | 4402505.6904
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | 0 | 0 | 0 | 0 | 0 | -6180.6282 | 480022.0186 | 587174.8679 | 708369.7108 | 845702.7845 | 1001626.2627 | 1179016.6099 | 1381257.7208 | 1612342.4406 | 1875779.852 | 2113308.3334 | 2361773.3438 | 2633937.0473 | 2940098.7434 | 3286151.7505 | 3636279.3956 | 3996999.0112 | 4396637.1767 | 4838293.335
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | 0 | 0 | 0 | 0 | 0 | -5056.8776 | 311601.2074 | 399271.7205 | 498431.1374 | 610794.5614 | 738368.3162 | 883505.873 | 1048975.8729 | 1238045.189 | 1453584.8892 | 1647926.3741 | 1851215.928 | 2073895.3218 | 2324391.255 | 2607525.5335 | 2893993.6067 | 3189127.8378 | 3516104.5185 | 3877459.5572
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | 0 | 0 | 0 | 0 | 0 | -5056.8776 | 266971.9631 | 354642.4762 | 453801.8931 | 566165.3171 | 693739.0719 | 838876.6287 | 1004346.6286 | 1193415.9447 | 1408955.645 | 1603297.1298 | 1806586.6837 | 2029266.0775 | 2279762.0107 | 2562896.2892 | 2849364.3624 | 3144498.5935 | 3471475.2743 | 3832830.3129
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 0 | 0 | 0 | -5618.7529 | 395811.613 | 493223.2942 | 603400.4241 | 728248.6729 | 869997.2894 | 1031261.2415 | 1215116.7969 | 1425193.8148 | 1664682.3706 | 1880617.3538 | 2106494.6359 | 2353916.1846 | 2632244.9992 | 2946838.642 | 3265136.5011 | 3593063.4245 | 3956370.8476 | 4357876.4461
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 0 | 0 | 0 | -5618.7529 | 395811.613 | 493223.2942 | 603400.4241 | 728248.6729 | 869997.2894 | 1031261.2415 | 1215116.7969 | 1425193.8148 | 1664682.3706 | 1880617.3538 | 2106494.6359 | 2353916.1846 | 2632244.9992 | 2946838.642 | 3265136.5011 | 3593063.4245 | 3956370.8476 | 4357876.4461
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 0 | 0 | 0 | -5618.7529 | 395811.613 | 493223.2942 | 603400.4241 | 728248.6729 | 869997.2894 | 1031261.2415 | 1215116.7969 | 1425193.8148 | 1664682.3706 | 1880617.3538 | 2106494.6359 | 2353916.1846 | 2632244.9992 | 2946838.642 | 3265136.5011 | 3593063.4245 | 3956370.8476 | 4357876.4461

## Option4
CitiPower
Relay replacements
OPTION 4 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety Risk | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned Replacement Risk |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Financial consequence |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NP consequence |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option5
CitiPower
Relay replacements
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
CitiPower
Relay replacements
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 20224111.8368 | 2026-06-30 |  | 470121.8563 | 518446.2539 | 572469.1661 | 632951.8289 | 700798.2686 | 777216.0897 | 863813.2267 | 961905.5775 | 1072963.453 | 1198946.9902 | 1342261.7547 | 1505803.6593 | 1693091.2941 | 1908444.8373 | 2157231.3373 | 2446205.5196 | 2719338.5875 | 3016255.7112 | 3343501.2958 | 3681290.912 | 4059737.7449 | 4448324.74 | 4856117.6422 | 5305121.6288 | 5790167.0693
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Capital expenditure | Option 2Capital expenditure | -8439310.1765 | 2026-06-30 |  | -3179827.3683 | -5595107.1197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 1491674.7831 | 2026-06-30 |  | 470121.8563 | 262129.7306 | 17859.9159 | 18720.5636 | 19710.0131 | 21038.1594 | 22646.6399 | 24717.3241 | 27364.5076 | 30730.5236 | 35100.0932 | 40888.1698 | 48703.113 | 59441.4834 | 74430.6135 | 95643.4686 | 127254.5454 | 171881.842 | 222501.5701 | 248762.1069 | 0 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -6392567.6835 | 2026-06-30 |  | 0 | -179986.6404 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | 0 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 18732437.0537 | 2026-06-30 |  | 0 | 256316.5233 | 554609.2502 | 614231.2653 | 681088.2554 | 756177.9303 | 841166.5868 | 937188.2534 | 1045598.9454 | 1168216.4666 | 1307161.6616 | 1464915.4895 | 1644388.1811 | 1849003.3538 | 2082800.7238 | 2350562.051 | 2592084.0421 | 2844373.8692 | 3120999.7256 | 3432528.805 | 0 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | 76329.8829 | 57924.7464 | 117546.7615 | 184403.7517 | 259493.4265 | 344482.0831 | 440503.7497 | 548914.4416 | 671531.9628 | 810477.1578 | 968230.9858 | 1147703.6774 | 1352318.8501 | 1586116.2201 | 1853877.5473 | 2095399.5383 | 2347689.3655 | 2624315.2219 | 2935844.3013 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 12339869.3702 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -6392567.6835 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 18732437.0537 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Capital expenditure | Option 3Capital expenditure | -7016679.0051 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | -8774934.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 4685050.8838 | 2026-06-30 |  | 470121.8563 | 518446.2539 | 572469.1661 | 632951.8289 | 700798.2686 | 777216.0897 | 870066.4078 | 24717.3241 | 27364.5076 | 30730.5236 | 35100.0932 | 40888.1698 | 48703.113 | 59441.4834 | 74430.6135 | 96874.9533 | 129691.2476 | 175226.6876 | 227113.7016 | 255147.6601 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -4091862.3267 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | -496684.5037 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 15539060.953 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | -6253.1811 | 937188.2534 | 1045598.9454 | 1168216.4666 | 1307161.6616 | 1464915.4895 | 1644388.1811 | 1849003.3538 | 2082800.7238 | 2349330.5662 | 2589647.3398 | 2841029.0236 | 3116387.5941 | 3426143.2518 | 0 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | -6253.1811 | 440503.7497 | 548914.4416 | 671531.9628 | 810477.1578 | 968230.9858 | 1147703.6774 | 1352318.8501 | 1586116.2201 | 1852646.0625 | 2092962.8361 | 2344344.5199 | 2619703.0904 | 2929458.7481 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | 11447198.6263 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -4091862.3267 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 15539060.953 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 0 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | 0 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 0 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0.49668 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 0.47012 | 0.51845 | 0.57247 | 0.63295 | 0.7008 | 0.77722 | 0.86381 | 0.96191 | 1.073 | 1.1989 | 1.3423 | 1.5058 | 1.6931 | 1.9084 | 2.1572 | 2.4462 | 2.7193 | 3.0163 | 3.3435 | 3.6813 | 4.0597 | 4.4483 | 4.8561 | 5.3051 | 5.7902
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 0 |  |  | Energy at risk energy at risk (weighted) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Energy at risk value | 0 |  |  | Option 1 (base case) risk cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Sensitivity_calcs
CitiPower
Relay replacements
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[7 empty] | 46203 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 2624315.2219 | 2935844.3013 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 12339869.3702 |  | 0 | 0 | 76329.8829 | 57924.7464 | 117546.7615 | 184403.7517 | 259493.4265 | 344482.0831 | 440503.7497 | 548914.4416 | 671531.9628 | 810477.1578 | 968230.9858 | 1147703.6774 | 1352318.8501 | 1586116.2201 | 1853877.5473 | 2095399.5383 | 2347689.3655 | 2624315.2219 | 2935844.3013 | 0 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 11700612.6019 |  | 0 | 0 | 58331.2189 | 8256.296 | 67878.3112 | 134735.3013 | 209824.9762 | 294813.6327 | 390835.2993 | 499245.9913 | 621863.5124 | 760808.7075 | 918562.5354 | 1098035.227 | 1302650.3997 | 1536447.7697 | 1804209.0969 | 2045731.088 | 2298020.9151 | 2574646.7715 | 2886175.8509 | 0 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 12979126.1386 |  | 0 | 0 | 94328.5469 | 107593.1968 | 167215.2119 | 234072.2021 | 309161.8769 | 394150.5335 | 490172.2001 | 598582.892 | 721200.4132 | 860145.6082 | 1017899.4361 | 1197372.1278 | 1401987.3005 | 1635784.6705 | 1903545.9976 | 2145067.9887 | 2397357.8159 | 2673983.6723 | 2985512.7517 | 0 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 14213113.0756 |  | 0 | 0 | 101961.5352 | 113385.6714 | 178969.8881 | 252512.5772 | 335111.2196 | 428598.7418 | 534222.575 | 653474.3362 | 788353.6095 | 941193.324 | 1114722.5347 | 1312142.4955 | 1537219.1855 | 1794396.2925 | 2088933.7524 | 2354607.9425 | 2632126.7524 | 2936415.1944 | 3279097.1818 | 0 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 10466625.6649 |  | 0 | 0 | 50698.2306 | 2463.8214 | 56123.635 | 116294.9262 | 183875.6335 | 260365.4244 | 346784.9243 | 444354.5471 | 554710.3162 | 679760.9917 | 821739.4368 | 983264.8593 | 1167418.5147 | 1377836.1477 | 1618821.3422 | 1836191.1341 | 2063251.9786 | 2312215.2493 | 2592591.4208 | 0 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 9827368.8965 |  | 0 | 0 | 32699.5665 | -47204.629 | 6455.1846 | 66626.4758 | 134207.1831 | 210696.974 | 297116.474 | 394686.0967 | 505041.8658 | 630092.5413 | 772070.9864 | 933596.4089 | 1117750.0643 | 1328167.6973 | 1569152.8918 | 1786522.6837 | 2013583.5282 | 2262546.7989 | 2542922.9704 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 12339869.3702 |  | 0 | 0 | 76329.8829 | 57924.7464 | 117546.7615 | 184403.7517 | 259493.4265 | 344482.0831 | 440503.7497 | 548914.4416 | 671531.9628 | 810477.1578 | 968230.9858 | 1147703.6774 | 1352318.8501 | 1586116.2201 | 1853877.5473 | 2095399.5383 | 2347689.3655 | 2624315.2219 | 2935844.3013 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 12339869.3702 |  | 0 | 0 | 76329.8829 | 57924.7464 | 117546.7615 | 184403.7517 | 259493.4265 | 344482.0831 | 440503.7497 | 548914.4416 | 671531.9628 | 810477.1578 | 968230.9858 | 1147703.6774 | 1352318.8501 | 1586116.2201 | 1853877.5473 | 2095399.5383 | 2347689.3655 | 2624315.2219 | 2935844.3013 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 12339869.3702 |  | 0 | 0 | 76329.8829 | 57924.7464 | 117546.7615 | 184403.7517 | 259493.4265 | 344482.0831 | 440503.7497 | 548914.4416 | 671531.9628 | 810477.1578 | 968230.9858 | 1147703.6774 | 1352318.8501 | 1586116.2201 | 1853877.5473 | 2095399.5383 | 2347689.3655 | 2624315.2219 | 2935844.3013 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6253.1811 | 440503.7497 | 548914.4416 | 671531.9628 | 810477.1578 | 968230.9858 | 1147703.6774 | 1352318.8501 | 1586116.2201 | 1852646.0625 | 2092962.8361 | 2344344.5199 | 2619703.0904 | 2929458.7481 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 11447198.6263 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6253.1811 | 440503.7497 | 548914.4416 | 671531.9628 | 810477.1578 | 968230.9858 | 1147703.6774 | 1352318.8501 | 1586116.2201 | 1852646.0625 | 2092962.8361 | 2344344.5199 | 2619703.0904 | 2929458.7481 | 0 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 11038012.3937 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6253.1811 | 390835.2993 | 499245.9913 | 621863.5124 | 760808.7075 | 918562.5354 | 1098035.227 | 1302650.3997 | 1536447.7697 | 1802977.6121 | 2043294.3857 | 2294676.0695 | 2570034.64 | 2879790.2977 | 0 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 11856384.859 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6253.1811 | 490172.2001 | 598582.892 | 721200.4132 | 860145.6082 | 1017899.4361 | 1197372.1278 | 1401987.3005 | 1635784.6705 | 1902314.5129 | 2142631.2865 | 2394012.9703 | 2669371.5408 | 2979127.1985 | 0 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 13001104.7216 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6878.4993 | 534222.575 | 653474.3362 | 788353.6095 | 941193.324 | 1114722.5347 | 1312142.4955 | 1537219.1855 | 1794396.2925 | 2087579.1191 | 2351927.5701 | 2628447.4222 | 2931341.8498 | 3272073.0733 | 0 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | 9893292.531 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5627.863 | 346784.9243 | 444354.5471 | 554710.3162 | 679760.9917 | 821739.4368 | 983264.8593 | 1167418.5147 | 1377836.1477 | 1617713.0059 | 1833998.1021 | 2060241.6175 | 2308064.331 | 2586844.4229 | 0 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | 9484106.2984 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5627.863 | 297116.474 | 394686.0967 | 505041.8658 | 630092.5413 | 772070.9864 | 933596.4089 | 1117750.0643 | 1328167.6973 | 1568044.5555 | 1784329.6517 | 2010573.1671 | 2258395.8806 | 2537175.9725 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 11447198.6263 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6253.1811 | 440503.7497 | 548914.4416 | 671531.9628 | 810477.1578 | 968230.9858 | 1147703.6774 | 1352318.8501 | 1586116.2201 | 1852646.0625 | 2092962.8361 | 2344344.5199 | 2619703.0904 | 2929458.7481 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 11447198.6263 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6253.1811 | 440503.7497 | 548914.4416 | 671531.9628 | 810477.1578 | 968230.9858 | 1147703.6774 | 1352318.8501 | 1586116.2201 | 1852646.0625 | 2092962.8361 | 2344344.5199 | 2619703.0904 | 2929458.7481 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 11447198.6263 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6253.1811 | 440503.7497 | 548914.4416 | 671531.9628 | 810477.1578 | 968230.9858 | 1147703.6774 | 1352318.8501 | 1586116.2201 | 1852646.0625 | 2092962.8361 | 2344344.5199 | 2619703.0904 | 2929458.7481 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | FALSE | FALSE | FALSE | TRUE | TRUE | 2028-29: FALSE
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 12.3399 | 11.4472 |  |  | 2026-27: 12.3399; 2028-29: Option 2
sens1 | Capex 10% higher | 0 | 11.7006 | 11.038 |  |  | 2026-27: 11.7006; 2028-29: Option 2
sens2 | Capex 10% lower | 0 | 12.9791 | 11.8564 |  |  | 2026-27: 12.9791; 2028-29: Option 2
sens3 | Total benefits 10% higher | 0 | 14.2131 | 13.0011 |  |  | 2026-27: 14.2131; 2028-29: Option 2
sens4 | Total benefits 10% lower | 0 | 10.4666 | 9.8933 |  |  | 2026-27: 10.4666; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 9.8274 | 9.4841 |  |  | 2026-27: 9.8274; 2028-29: Option 2
sens | 0 | [5 empty] | 2026-27: 0
sens | 0 | [5 empty] | 2026-27: 0
sens | 0 | [5 empty] | 2026-27: 0

## Workings_calcs
CitiPower
Relay replacements
WORKINGS - COSTS
[8 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Replacement year
|  | ZSS | Option 1 | Option 2 | Option 3
|  | BC | 2857212 | 27 | 32
|  | FB | 5027445 | 28 | 32
Option 1 capex profile
|  | ZSS | 27 | 28 | 29 | 30 | 31 | 2026-06-30: 32; 2026-27: 33; 2027-28: 34; 2028-29: 35
|  | BC | 2857212 | 0 | 0 | 0 | 0
|  | FB | 0 | 5027445 | 0 | 0 | 0
|  | Total | 2857212 | 5027445 | 0 | 0 | 0
Option 2 capex profile
|  | ZSS | 27 | 28 | 29 | 30 | 31 | 2026-06-30: 32; 2026-27: 33; 2027-28: 34; 2028-29: 35
|  | BC | 0 | 0 | 0 | 0 | 0 | 2026-06-30: 0; 2026-27: 2857212; 2027-28: 0; 2028-29: 0
|  | FB | 0 | 0 | 0 | 0 | 0 | 2026-06-30: 0; 2026-27: 5027445; 2027-28: 0; 2028-29: 0
|  | Total | 0 | 0 | 0 | 0 | 0 | 2026-06-30: 0; 2026-27: 7884657; 2027-28: 0; 2028-29: 0

## CBRM_data
CitiPower
Relay replacements
Flags and data for calcs
Future: future risk of current assets
New assets: risk associated with new assets
|  | Year | [147 empty] | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
|  | Flags | [147 empty] | TotalFuture1 | TotalFuture2 | TotalFuture3 | TotalFuture4 | TotalFuture5 | TotalFuture6 | TotalFuture7 | TotalFuture8 | TotalFuture9 | TotalFuture10 | TotalFuture11 | TotalFuture12 | TotalFuture13 | TotalFuture14 | TotalFuture15 | TotalFuture16 | TotalFuture17 | TotalFuture18 | TotalFuture19 | TotalFuture20 | TotalFuture21 | TotalFuture22 | TotalFuture23 | TotalFuture24 | TotalFuture25 | TotalFuture26 | TotalFuture27 | TotalFuture28 | TotalFuture29 | TotalFuture30 | #VALUE! | TotalNew1 | TotalNew2 | TotalNew3 | TotalNew4 | TotalNew5 | TotalNew6 | TotalNew7 | TotalNew8 | TotalNew9 | TotalNew10 | TotalNew11 | TotalNew12 | TotalNew13 | TotalNew14 | TotalNew15 | TotalNew16 | TotalNew17 | TotalNew18 | TotalNew19 | TotalNew20 | TotalNew21 | TotalNew22 | TotalNew23 | TotalNew24 | TotalNew25 | TotalNew26 | TotalNew27 | TotalNew28 | TotalNew29 | TotalNew30 | #VALUE! | OpexFuture1 | OpexFuture2 | OpexFuture3 | OpexFuture4 | OpexFuture5 | OpexFuture6 | OpexFuture7 | OpexFuture8 | OpexFuture9 | OpexFuture10 | OpexFuture11 | OpexFuture12 | OpexFuture13 | OpexFuture14 | OpexFuture15 | OpexFuture16 | OpexFuture17 | OpexFuture18 | OpexFuture19 | OpexFuture20 | OpexFuture21 | OpexFuture22 | OpexFuture23 | OpexFuture24 | OpexFuture25 | OpexFuture26 | OpexFuture27 | OpexFuture28 | OpexFuture29 | OpexFuture30 | #VALUE! | OpexNew1 | OpexNew2 | OpexNew3 | OpexNew4 | OpexNew5 | OpexNew6 | OpexNew7 | OpexNew8 | OpexNew9 | OpexNew10 | OpexNew11 | OpexNew12 | OpexNew13 | OpexNew14 | OpexNew15 | OpexNew16 | OpexNew17 | OpexNew18 | OpexNew19 | OpexNew20 | OpexNew21 | OpexNew22 | OpexNew23 | OpexNew24 | OpexNew25 | OpexNew26 | OpexNew27 | OpexNew28 | OpexNew29 | OpexNew30 | #VALUE! | OpexDelta1 | OpexDelta2 | OpexDelta3 | OpexDelta4 | OpexDelta5 | OpexDelta6 | OpexDelta7 | OpexDelta8 | OpexDelta9 | OpexDelta10 | OpexDelta11 | OpexDelta12 | OpexDelta13 | OpexDelta14 | OpexDelta15 | OpexDelta16 | OpexDelta17 | OpexDelta18 | OpexDelta19 | OpexDelta20 | OpexDelta21 | OpexDelta22 | OpexDelta23 | OpexDelta24 | OpexDelta25 | OpexDelta26 | OpexDelta27 | OpexDelta28 | OpexDelta29 | OpexDelta30 | #VALUE! | CapexFuture1 | CapexFuture2 | CapexFuture3 | CapexFuture4 | CapexFuture5 | CapexFuture6 | CapexFuture7 | CapexFuture8 | CapexFuture9 | CapexFuture10 | CapexFuture11 | CapexFuture12 | CapexFuture13 | CapexFuture14 | CapexFuture15 | CapexFuture16 | CapexFuture17 | CapexFuture18 | CapexFuture19 | CapexFuture20 | CapexFuture21 | CapexFuture22 | CapexFuture23 | CapexFuture24 | CapexFuture25 | CapexFuture26 | CapexFuture27 | CapexFuture28 | CapexFuture29 | CapexFuture30 | #VALUE! | CapexNew1 | CapexNew2 | CapexNew3 | CapexNew4 | CapexNew5 | CapexNew6 | CapexNew7 | CapexNew8 | CapexNew9 | CapexNew10 | CapexNew11 | CapexNew12 | CapexNew13 | CapexNew14 | CapexNew15 | CapexNew16 | CapexNew17 | CapexNew18 | CapexNew19 | CapexNew20 | CapexNew21 | CapexNew22 | CapexNew23 | CapexNew24 | CapexNew25 | CapexNew26 | CapexNew27 | CapexNew28 | CapexNew29 | CapexNew30 | #VALUE! | CapexDelta1 | CapexDelta2 | CapexDelta3 | CapexDelta4 | CapexDelta5 | CapexDelta6 | CapexDelta7 | CapexDelta8 | CapexDelta9 | CapexDelta10 | CapexDelta11 | CapexDelta12 | CapexDelta13 | CapexDelta14 | CapexDelta15 | CapexDelta16 | CapexDelta17 | CapexDelta18 | CapexDelta19 | CapexDelta20 | CapexDelta21 | CapexDelta22 | CapexDelta23 | CapexDelta24 | CapexDelta25 | CapexDelta26 | CapexDelta27 | CapexDelta28 | CapexDelta29 | CapexDelta30 | #VALUE! | TotexDelta1 | TotexDelta2 | TotexDelta3 | TotexDelta4 | TotexDelta5 | TotexDelta6 | TotexDelta7 | TotexDelta8 | TotexDelta9 | TotexDelta10 | TotexDelta11 | TotexDelta12 | TotexDelta13 | TotexDelta14 | TotexDelta15 | TotexDelta16 | TotexDelta17 | TotexDelta18 | TotexDelta19 | TotexDelta20 | TotexDelta21 | TotexDelta22 | TotexDelta23 | TotexDelta24 | TotexDelta25 | TotexDelta26 | TotexDelta27 | TotexDelta28 | TotexDelta29 | TotexDelta30 | #VALUE! | SafetyFuture1 | SafetyFuture2 | SafetyFuture3 | SafetyFuture4 | SafetyFuture5 | SafetyFuture6 | SafetyFuture7 | SafetyFuture8 | SafetyFuture9 | SafetyFuture10 | SafetyFuture11 | SafetyFuture12 | SafetyFuture13 | SafetyFuture14 | SafetyFuture15 | SafetyFuture16 | SafetyFuture17 | SafetyFuture18 | SafetyFuture19 | SafetyFuture20 | SafetyFuture21 | SafetyFuture22 | SafetyFuture23 | SafetyFuture24 | SafetyFuture25 | SafetyFuture26 | SafetyFuture27 | SafetyFuture28 | SafetyFuture29 | SafetyFuture30 | #VALUE! | SafetyNew1 | SafetyNew2 | SafetyNew3 | SafetyNew4 | SafetyNew5 | SafetyNew6 | SafetyNew7 | SafetyNew8 | SafetyNew9 | SafetyNew10 | SafetyNew11 | SafetyNew12 | SafetyNew13 | SafetyNew14 | SafetyNew15 | SafetyNew16 | SafetyNew17 | SafetyNew18 | SafetyNew19 | SafetyNew20 | SafetyNew21 | SafetyNew22 | SafetyNew23 | SafetyNew24 | SafetyNew25 | SafetyNew26 | SafetyNew27 | SafetyNew28 | SafetyNew29 | SafetyNew30 | #VALUE! | SafetyDelta1 | SafetyDelta2 | SafetyDelta3 | SafetyDelta4 | SafetyDelta5 | SafetyDelta6 | SafetyDelta7 | SafetyDelta8 | SafetyDelta9 | SafetyDelta10 | SafetyDelta11 | SafetyDelta12 | SafetyDelta13 | SafetyDelta14 | SafetyDelta15 | SafetyDelta16 | SafetyDelta17 | SafetyDelta18 | SafetyDelta19 | SafetyDelta20 | SafetyDelta21 | SafetyDelta22 | SafetyDelta23 | SafetyDelta24 | SafetyDelta25 | SafetyDelta26 | SafetyDelta27 | SafetyDelta28 | SafetyDelta29 | SafetyDelta30 | #VALUE! | EnvironmentFuture1 | EnvironmentFuture2 | EnvironmentFuture3 | EnvironmentFuture4 | EnvironmentFuture5 | EnvironmentFuture6 | EnvironmentFuture7 | EnvironmentFuture8 | EnvironmentFuture9 | EnvironmentFuture10 | EnvironmentFuture11 | EnvironmentFuture12 | EnvironmentFuture13 | EnvironmentFuture14 | EnvironmentFuture15 | EnvironmentFuture16 | EnvironmentFuture17 | EnvironmentFuture18 | EnvironmentFuture19 | EnvironmentFuture20 | EnvironmentFuture21 | EnvironmentFuture22 | EnvironmentFuture23 | EnvironmentFuture24 | EnvironmentFuture25 | EnvironmentFuture26 | EnvironmentFuture27 | EnvironmentFuture28 | EnvironmentFuture29 | EnvironmentFuture30 | #VALUE! | EnvironmentNew1 | EnvironmentNew2 | EnvironmentNew3 | EnvironmentNew4 | EnvironmentNew5 | EnvironmentNew6 | EnvironmentNew7 | EnvironmentNew8 | EnvironmentNew9 | EnvironmentNew10 | EnvironmentNew11 | EnvironmentNew12 | EnvironmentNew13 | EnvironmentNew14 | EnvironmentNew15 | EnvironmentNew16 | EnvironmentNew17 | EnvironmentNew18 | EnvironmentNew19 | EnvironmentNew20 | EnvironmentNew21 | EnvironmentNew22 | EnvironmentNew23 | EnvironmentNew24 | EnvironmentNew25 | EnvironmentNew26 | EnvironmentNew27 | EnvironmentNew28 | EnvironmentNew29 | EnvironmentNew30 | #VALUE! | EnvironmentDelta1 | EnvironmentDelta2 | EnvironmentDelta3 | EnvironmentDelta4 | EnvironmentDelta5 | EnvironmentDelta6 | EnvironmentDelta7 | EnvironmentDelta8 | EnvironmentDelta9 | EnvironmentDelta10 | EnvironmentDelta11 | EnvironmentDelta12 | EnvironmentDelta13 | EnvironmentDelta14 | EnvironmentDelta15 | EnvironmentDelta16 | EnvironmentDelta17 | EnvironmentDelta18 | EnvironmentDelta19 | EnvironmentDelta20 | EnvironmentDelta21 | EnvironmentDelta22 | EnvironmentDelta23 | EnvironmentDelta24 | EnvironmentDelta25 | EnvironmentDelta26 | EnvironmentDelta27 | EnvironmentDelta28 | EnvironmentDelta29 | EnvironmentDelta30 | #VALUE! | NPFuture1 | NPFuture2 | NPFuture3 | NPFuture4 | NPFuture5 | NPFuture6 | NPFuture7 | NPFuture8 | NPFuture9 | NPFuture10 | NPFuture11 | NPFuture12 | NPFuture13 | NPFuture14 | NPFuture15 | NPFuture16 | NPFuture17 | NPFuture18 | NPFuture19 | NPFuture20 | NPFuture21 | NPFuture22 | NPFuture23 | NPFuture24 | NPFuture25 | NPFuture26 | NPFuture27 | NPFuture28 | NPFuture29 | NPFuture30 | #VALUE! | NPNew1 | NPNew2 | NPNew3 | NPNew4 | NPNew5 | NPNew6 | NPNew7 | NPNew8 | NPNew9 | NPNew10 | NPNew11 | NPNew12 | NPNew13 | NPNew14 | NPNew15 | NPNew16 | NPNew17 | NPNew18 | NPNew19 | NPNew20 | NPNew21 | NPNew22 | NPNew23 | NPNew24 | NPNew25 | NPNew26 | NPNew27 | NPNew28 | NPNew29 | NPNew30 | #VALUE! | NPDelta1 | NPDelta2 | NPDelta3 | NPDelta4 | NPDelta5 | NPDelta6 | NPDelta7 | NPDelta8 | NPDelta9 | NPDelta10 | NPDelta11 | NPDelta12 | NPDelta13 | NPDelta14 | NPDelta15 | NPDelta16 | NPDelta17 | NPDelta18 | NPDelta19 | NPDelta20 | NPDelta21 | NPDelta22 | NPDelta23 | NPDelta24 | NPDelta25 | NPDelta26 | NPDelta27 | NPDelta28 | NPDelta29 | NPDelta30 | #VALUE! | Delta1 | Delta2 | Delta3 | Delta4 | Delta5 | Delta6 | Delta7 | Delta8 | Delta9 | Delta10 | Delta11 | Delta12 | Delta13 | Delta14 | Delta15 | Delta16 | Delta17 | Delta18 | Delta19 | Delta20 | Delta21 | Delta22 | Delta23 | Delta24 | Delta25 | Delta26 | Delta27 | Delta28 | Delta29 | Delta30
|  | Risk | [147 empty] | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | #VALUE! | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | #VALUE! | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | #VALUE! | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | #VALUE! | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | #VALUE! | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | #VALUE! | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | #VALUE! | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | #VALUE! | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | #VALUE! | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | #VALUE! | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | #VALUE! | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | #VALUE! | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | #VALUE! | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | #VALUE! | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | #VALUE! | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | #VALUE! | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | #VALUE! | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | #VALUE!
[150 empty] | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta
[150 empty] | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta
CBRM data extract
|  |  | Asset Description | [12 empty] | Essential Information |  |  | Current Condition Related Failure Risks (2024) | [10 empty] | Future Condition Related Failure Risks (2034) | [10 empty] | New Asset Condition Related Failure Risks | [9 empty] | Total Risk | [6 empty] | Future Health index | [30 empty] | Future PoF | [30 empty] | Future NP PoF | [29 empty] | 2025: Future Risk |  | New Asset Risk | [30 empty] | Future Opex Risk | [30 empty] | New Asset Future Opex Risk | [30 empty] | Delta Opex Risk | [30 empty] | Future Capex Risk | [30 empty] | New Asset Capex Risk | [30 empty] | Delta Capex Risk | [30 empty] | Delta Totex Risk | [30 empty] | Future Safety Risk | [30 empty] | New Asset Safety Risk | [30 empty] | Delta Safety Risk | [30 empty] | Future Environment Risk | [30 empty] | New Asset Environment Risk | [30 empty] | Delta Environment Risk | [30 empty] | Future NP Risk | [30 empty] | New Asset NP Risk | [30 empty] | Delta NP Risk | [30 empty] | Delta Risk
[58 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
| Replace | Asset Index | Asset ID | Substation ID | Feeder ID | Operating voltage | Asset Description | Protection Function | Relay Set | Manufacturer | Model | ManuModel | Class | Relay Type |  | Demand Distribution | Time Between Inspections Used |  | Current Health Index (2024) | Condition PoF (2024) | Condition PoF with NP Consequences | Condition PoF without NP Consequences | Financial Risk OPEX (2024) | Financial Risk CAPEX (2024) | Financial Risk TOTEX (2024) | Safety Risk (2024) | Envionmental Risk (2024) | Network Performance Risk (2024) |  | Future Health Index (2034) | Condition PoF (2034) | Condition PoF with NP Consequences | Condition PoF without NP Consequences | Financial Risk OPEX (2034) | Financial Risk CAPEX (2034) | Financial Risk TOTEX (2034) | Safety Risk (2034) | Envionmental Risk (2034) | Network Performance Risk (2034) |  | New Asset Condition PoF | Condition PoF with NP Consequences | Condition PoF without NP Consequences | New Asset Financial Risk OPEX | New Asset Financial Risk CAPEX | New Asset Financial Risk TOTEX | New Asset Safety Risk | New Asset Envionmental Risk | New Asset Network Performance Risk |  | Total Risk (2024) | Total Risk (2034) | New Asset Risk | Delta Risk |  | Forecast Ageing Constant (B2) |  | Health Index (2025) | Health Index (2026) | Health Index (2027) | Health Index (2028) | Health Index (2029) | Health Index (2030) | Health Index (2031) | Health Index (2032) | Health Index (2033) | Health Index (2034) | Health Index (2035) | Health Index (2036) | Health Index (2037) | Health Index (2038) | Health Index (2039) | Health Index (2040) | Health Index (2041) | Health Index (2042) | Health Index (2043) | Health Index (2044) | Health Index (2045) | Health Index (2046) | Health Index (2047) | Health Index (2048) | Health Index (2049) | Health Index (2050) | Health Index (2051) | Health Index (2052) | Health Index (2053) | Health Index (2054) |  | PoF (2025) | PoF (2026) | PoF (2027) | PoF (2028) | PoF (2029) | PoF (2030) | PoF (2031) | PoF (2032) | PoF (2033) | PoF (2034) | PoF (2035) | PoF (2036) | PoF (2037) | PoF (2038) | PoF (2039) | PoF (2040) | PoF (2041) | PoF (2042) | PoF (2043) | PoF (2044) | PoF (2045) | PoF (2046) | PoF (2047) | PoF (2048) | PoF (2049) | PoF (2050) | PoF (2051) | PoF (2052) | PoF (2053) | PoF (2054) |  | Future NP PoF (2025) | Future NP PoF (2026) | Future NP PoF (2027) | Future NP PoF (2028) | Future NP PoF (2029) | Future NP PoF (2030) | Future NP PoF (2031) | Future NP PoF (2032) | Future NP PoF (2033) | Future NP PoF (2034) | Future NP PoF (2035) | Future NP PoF (2036) | Future NP PoF (2037) | Future NP PoF (2038) | Future NP PoF (2039) | Future NP PoF (2040) | Future NP PoF (2041) | Future NP PoF (2042) | Future NP PoF (2043) | Future NP PoF (2044) | Future NP PoF (2045) | Future NP PoF (2046) | Future NP PoF (2047) | Future NP PoF (2048) | Future NP PoF (2049) | Future NP PoF (2050) | Future NP PoF (2051) | Future NP PoF (2052) | Future NP PoF (2053) | Future NP PoF (2054) | Future Total Risk (2025) | Future Total Risk (2026) | Future Total Risk (2027) | Future Total Risk (2028) | Future Total Risk (2029) | Future Total Risk (2030) | Future Total Risk (2031) | Future Total Risk (2032) | Future Total Risk (2033) | Future Total Risk (2034) | Future Total Risk (2035) | Future Total Risk (2036) | Future Total Risk (2037) | Future Total Risk (2038) | Future Total Risk (2039) | Future Total Risk (2040) | Future Total Risk (2041) | Future Total Risk (2042) | Future Total Risk (2043) | Future Total Risk (2044) | Future Total Risk (2045) | Future Total Risk (2046) | Future Total Risk (2047) | Future Total Risk (2048) | Future Total Risk (2049) | Future Total Risk (2050) | Future Total Risk (2051) | Future Total Risk (2052) | Future Total Risk (2053) | Future Total Risk (2054) |  | New Asset Total Risk (2025) | New Asset Total Risk (2026) | New Asset Total Risk (2027) | New Asset Total Risk (2028) | New Asset Total Risk (2029) | New Asset Total Risk (2030) | New Asset Total Risk (2031) | New Asset Total Risk (2032) | New Asset Total Risk (2033) | New Asset Total Risk (2034) | New Asset Total Risk (2035) | New Asset Total Risk (2036) | New Asset Total Risk (2037) | New Asset Total Risk (2038) | New Asset Total Risk (2039) | New Asset Total Risk (2040) | New Asset Total Risk (2041) | New Asset Total Risk (2042) | New Asset Total Risk (2043) | New Asset Total Risk (2044) | New Asset Total Risk (2045) | New Asset Total Risk (2046) | New Asset Total Risk (2047) | New Asset Total Risk (2048) | New Asset Total Risk (2049) | New Asset Total Risk (2050) | New Asset Total Risk (2051) | New Asset Total Risk (2052) | New Asset Total Risk (2053) | New Asset Total Risk (2054) |  | Future Opex Risk (2025) | Future Opex Risk (2026) | Future Opex Risk (2027) | Future Opex Risk (2028) | Future Opex Risk (2029) | Future Opex Risk (2030) | Future Opex Risk (2031) | Future Opex Risk (2032) | Future Opex Risk (2033) | Future Opex Risk (2034) | Future Opex Risk (2035) | Future Opex Risk (2036) | Future Opex Risk (2037) | Future Opex Risk (2038) | Future Opex Risk (2039) | Future Opex Risk (2040) | Future Opex Risk (2041) | Future Opex Risk (2042) | Future Opex Risk (2043) | Future Opex Risk (2044) | Future Opex Risk (2045) | Future Opex Risk (2046) | Future Opex Risk (2047) | Future Opex Risk (2048) | Future Opex Risk (2049) | Future Opex Risk (2050) | Future Opex Risk (2051) | Future Opex Risk (2052) | Future Opex Risk (2053) | Future Opex Risk (2054) |  | New Asset Opex Risk (2025) | New Asset Opex Risk (2026) | New Asset Opex Risk (2027) | New Asset Opex Risk (2028) | New Asset Opex Risk (2029) | New Asset Opex Risk (2030) | New Asset Opex Risk (2031) | New Asset Opex Risk (2032) | New Asset Opex Risk (2033) | New Asset Opex Risk (2034) | New Asset Opex Risk (2035) | New Asset Opex Risk (2036) | New Asset Opex Risk (2037) | New Asset Opex Risk (2038) | New Asset Opex Risk (2039) | New Asset Opex Risk (2040) | New Asset Opex Risk (2041) | New Asset Opex Risk (2042) | New Asset Opex Risk (2043) | New Asset Opex Risk (2044) | New Asset Opex Risk (2045) | New Asset Opex Risk (2046) | New Asset Opex Risk (2047) | New Asset Opex Risk (2048) | New Asset Opex Risk (2049) | New Asset Opex Risk (2050) | New Asset Opex Risk (2051) | New Asset Opex Risk (2052) | New Asset Opex Risk (2053) | New Asset Opex Risk (2054) |  | Delta Opex Risk (2025) | Delta Opex Risk (2026) | Delta Opex Risk (2027) | Delta Opex Risk (2028) | Delta Opex Risk (2029) | Delta Opex Risk (2030) | Delta Opex Risk (2031) | Delta Opex Risk (2032) | Delta Opex Risk (2033) | Delta Opex Risk (2034) | Delta Opex Risk (2035) | Delta Opex Risk (2036) | Delta Opex Risk (2037) | Delta Opex Risk (2038) | Delta Opex Risk (2039) | Delta Opex Risk (2040) | Delta Opex Risk (2041) | Delta Opex Risk (2042) | Delta Opex Risk (2043) | Delta Opex Risk (2044) | Delta Opex Risk (2045) | Delta Opex Risk (2046) | Delta Opex Risk (2047) | Delta Opex Risk (2048) | Delta Opex Risk (2049) | Delta Opex Risk (2050) | Delta Opex Risk (2051) | Delta Opex Risk (2052) | Delta Opex Risk (2053) | Delta Opex Risk (2054) |  | Future Capex Risk (2025) | Future Capex Risk (2026) | Future Capex Risk (2027) | Future Capex Risk (2028) | Future Capex Risk (2029) | Future Capex Risk (2030) | Future Capex Risk (2031) | Future Capex Risk (2032) | Future Capex Risk (2033) | Future Capex Risk (2034) | Future Capex Risk (2035) | Future Capex Risk (2036) | Future Capex Risk (2037) | Future Capex Risk (2038) | Future Capex Risk (2039) | Future Capex Risk (2040) | Future Capex Risk (2041) | Future Capex Risk (2042) | Future Capex Risk (2043) | Future Capex Risk (2044) | Future Capex Risk (2045) | Future Capex Risk (2046) | Future Capex Risk (2047) | Future Capex Risk (2048) | Future Capex Risk (2049) | Future Capex Risk (2050) | Future Capex Risk (2051) | Future Capex Risk (2052) | Future Capex Risk (2053) | Future Capex Risk (2054) |  | New Asset Capex Risk (2025) | New Asset Capex Risk (2026) | New Asset Capex Risk (2027) | New Asset Capex Risk (2028) | New Asset Capex Risk (2029) | New Asset Capex Risk (2030) | New Asset Capex Risk (2031) | New Asset Capex Risk (2032) | New Asset Capex Risk (2033) | New Asset Capex Risk (2034) | New Asset Capex Risk (2035) | New Asset Capex Risk (2036) | New Asset Capex Risk (2037) | New Asset Capex Risk (2038) | New Asset Capex Risk (2039) | New Asset Capex Risk (2040) | New Asset Capex Risk (2041) | New Asset Capex Risk (2042) | New Asset Capex Risk (2043) | New Asset Capex Risk (2044) | New Asset Capex Risk (2045) | New Asset Capex Risk (2046) | New Asset Capex Risk (2047) | New Asset Capex Risk (2048) | New Asset Capex Risk (2049) | New Asset Capex Risk (2050) | New Asset Capex Risk (2051) | New Asset Capex Risk (2052) | New Asset Capex Risk (2053) | New Asset Capex Risk (2054) |  | Delta Capex Risk (2025) | Delta Capex Risk (2026) | Delta Capex Risk (2027) | Delta Capex Risk (2028) | Delta Capex Risk (2029) | Delta Capex Risk (2030) | Delta Capex Risk (2031) | Delta Capex Risk (2032) | Delta Capex Risk (2033) | Delta Capex Risk (2034) | Delta Capex Risk (2035) | Delta Capex Risk (2036) | Delta Capex Risk (2037) | Delta Capex Risk (2038) | Delta Capex Risk (2039) | Delta Capex Risk (2040) | Delta Capex Risk (2041) | Delta Capex Risk (2042) | Delta Capex Risk (2043) | Delta Capex Risk (2044) | Delta Capex Risk (2045) | Delta Capex Risk (2046) | Delta Capex Risk (2047) | Delta Capex Risk (2048) | Delta Capex Risk (2049) | Delta Capex Risk (2050) | Delta Capex Risk (2051) | Delta Capex Risk (2052) | Delta Capex Risk (2053) | Delta Capex Risk (2054) |  | Delta Totex Risk (2025) | Delta Totex Risk (2026) | Delta Totex Risk (2027) | Delta Totex Risk (2028) | Delta Totex Risk (2029) | Delta Totex Risk (2030) | Delta Totex Risk (2031) | Delta Totex Risk (2032) | Delta Totex Risk (2033) | Delta Totex Risk (2034) | Delta Totex Risk (2035) | Delta Totex Risk (2036) | Delta Totex Risk (2037) | Delta Totex Risk (2038) | Delta Totex Risk (2039) | Delta Totex Risk (2040) | Delta Totex Risk (2041) | Delta Totex Risk (2042) | Delta Totex Risk (2043) | Delta Totex Risk (2044) | Delta Totex Risk (2045) | Delta Totex Risk (2046) | Delta Totex Risk (2047) | Delta Totex Risk (2048) | Delta Totex Risk (2049) | Delta Totex Risk (2050) | Delta Totex Risk (2051) | Delta Totex Risk (2052) | Delta Totex Risk (2053) | Delta Totex Risk (2054) |  | Future Safety Risk (2025) | Future Safety Risk (2026) | Future Safety Risk (2027) | Future Safety Risk (2028) | Future Safety Risk (2029) | Future Safety Risk (2030) | Future Safety Risk (2031) | Future Safety Risk (2032) | Future Safety Risk (2033) | Future Safety Risk (2034) | Future Safety Risk (2035) | Future Safety Risk (2036) | Future Safety Risk (2037) | Future Safety Risk (2038) | Future Safety Risk (2039) | Future Safety Risk (2040) | Future Safety Risk (2041) | Future Safety Risk (2042) | Future Safety Risk (2043) | Future Safety Risk (2044) | Future Safety Risk (2045) | Future Safety Risk (2046) | Future Safety Risk (2047) | Future Safety Risk (2048) | Future Safety Risk (2049) | Future Safety Risk (2050) | Future Safety Risk (2051) | Future Safety Risk (2052) | Future Safety Risk (2053) | Future Safety Risk (2054) |  | New Asset Safety Risk (2025) | New Asset Safety Risk (2026) | New Asset Safety Risk (2027) | New Asset Safety Risk (2028) | New Asset Safety Risk (2029) | New Asset Safety Risk (2030) | New Asset Safety Risk (2031) | New Asset Safety Risk (2032) | New Asset Safety Risk (2033) | New Asset Safety Risk (2034) | New Asset Safety Risk (2035) | New Asset Safety Risk (2036) | New Asset Safety Risk (2037) | New Asset Safety Risk (2038) | New Asset Safety Risk (2039) | New Asset Safety Risk (2040) | New Asset Safety Risk (2041) | New Asset Safety Risk (2042) | New Asset Safety Risk (2043) | New Asset Safety Risk (2044) | New Asset Safety Risk (2045) | New Asset Safety Risk (2046) | New Asset Safety Risk (2047) | New Asset Safety Risk (2048) | New Asset Safety Risk (2049) | New Asset Safety Risk (2050) | New Asset Safety Risk (2051) | New Asset Safety Risk (2052) | New Asset Safety Risk (2053) | New Asset Safety Risk (2054) |  | Delta Safety Risk (2025) | Delta Safety Risk (2026) | Delta Safety Risk (2027) | Delta Safety Risk (2028) | Delta Safety Risk (2029) | Delta Safety Risk (2030) | Delta Safety Risk (2031) | Delta Safety Risk (2032) | Delta Safety Risk (2033) | Delta Safety Risk (2034) | Delta Safety Risk (2035) | Delta Safety Risk (2036) | Delta Safety Risk (2037) | Delta Safety Risk (2038) | Delta Safety Risk (2039) | Delta Safety Risk (2040) | Delta Safety Risk (2041) | Delta Safety Risk (2042) | Delta Safety Risk (2043) | Delta Safety Risk (2044) | Delta Safety Risk (2045) | Delta Safety Risk (2046) | Delta Safety Risk (2047) | Delta Safety Risk (2048) | Delta Safety Risk (2049) | Delta Safety Risk (2050) | Delta Safety Risk (2051) | Delta Safety Risk (2052) | Delta Safety Risk (2053) | Delta Safety Risk (2054) |  | Future Environment Risk (2025) | Future Environment Risk (2026) | Future Environment Risk (2027) | Future Environment Risk (2028) | Future Environment Risk (2029) | Future Environment Risk (2030) | Future Environment Risk (2031) | Future Environment Risk (2032) | Future Environment Risk (2033) | Future Environment Risk (2034) | Future Environment Risk (2035) | Future Environment Risk (2036) | Future Environment Risk (2037) | Future Environment Risk (2038) | Future Environment Risk (2039) | Future Environment Risk (2040) | Future Environment Risk (2041) | Future Environment Risk (2042) | Future Environment Risk (2043) | Future Environment Risk (2044) | Future Environment Risk (2045) | Future Environment Risk (2046) | Future Environment Risk (2047) | Future Environment Risk (2048) | Future Environment Risk (2049) | Future Environment Risk (2050) | Future Environment Risk (2051) | Future Environment Risk (2052) | Future Environment Risk (2053) | Future Environment Risk (2054) |  | New Asset Environment Risk (2025) | New Asset Environment Risk (2026) | New Asset Environment Risk (2027) | New Asset Environment Risk (2028) | New Asset Environment Risk (2029) | New Asset Environment Risk (2030) | New Asset Environment Risk (2031) | New Asset Environment Risk (2032) | New Asset Environment Risk (2033) | New Asset Environment Risk (2034) | New Asset Environment Risk (2035) | New Asset Environment Risk (2036) | New Asset Environment Risk (2037) | New Asset Environment Risk (2038) | New Asset Environment Risk (2039) | New Asset Environment Risk (2040) | New Asset Environment Risk (2041) | New Asset Environment Risk (2042) | New Asset Environment Risk (2043) | New Asset Environment Risk (2044) | New Asset Environment Risk (2045) | New Asset Environment Risk (2046) | New Asset Environment Risk (2047) | New Asset Environment Risk (2048) | New Asset Environment Risk (2049) | New Asset Environment Risk (2050) | New Asset Environment Risk (2051) | New Asset Environment Risk (2052) | New Asset Environment Risk (2053) | New Asset Environment Risk (2054) |  | Delta Environment Risk (2025) | Delta Environment Risk (2026) | Delta Environment Risk (2027) | Delta Environment Risk (2028) | Delta Environment Risk (2029) | Delta Environment Risk (2030) | Delta Environment Risk (2031) | Delta Environment Risk (2032) | Delta Environment Risk (2033) | Delta Environment Risk (2034) | Delta Environment Risk (2035) | Delta Environment Risk (2036) | Delta Environment Risk (2037) | Delta Environment Risk (2038) | Delta Environment Risk (2039) | Delta Environment Risk (2040) | Delta Environment Risk (2041) | Delta Environment Risk (2042) | Delta Environment Risk (2043) | Delta Environment Risk (2044) | Delta Environment Risk (2045) | Delta Environment Risk (2046) | Delta Environment Risk (2047) | Delta Environment Risk (2048) | Delta Environment Risk (2049) | Delta Environment Risk (2050) | Delta Environment Risk (2051) | Delta Environment Risk (2052) | Delta Environment Risk (2053) | Delta Environment Risk (2054) |  | Future NP Risk (2025) | Future NP Risk (2026) | Future NP Risk (2027) | Future NP Risk (2028) | Future NP Risk (2029) | Future NP Risk (2030) | Future NP Risk (2031) | Future NP Risk (2032) | Future NP Risk (2033) | Future NP Risk (2034) | Future NP Risk (2035) | Future NP Risk (2036) | Future NP Risk (2037) | Future NP Risk (2038) | Future NP Risk (2039) | Future NP Risk (2040) | Future NP Risk (2041) | Future NP Risk (2042) | Future NP Risk (2043) | Future NP Risk (2044) | Future NP Risk (2045) | Future NP Risk (2046) | Future NP Risk (2047) | Future NP Risk (2048) | Future NP Risk (2049) | Future NP Risk (2050) | Future NP Risk (2051) | Future NP Risk (2052) | Future NP Risk (2053) | Future NP Risk (2054) |  | New Asset NP Risk (2025) | New Asset NP Risk (2026) | New Asset NP Risk (2027) | New Asset NP Risk (2028) | New Asset NP Risk (2029) | New Asset NP Risk (2030) | New Asset NP Risk (2031) | New Asset NP Risk (2032) | New Asset NP Risk (2033) | New Asset NP Risk (2034) | New Asset NP Risk (2035) | New Asset NP Risk (2036) | New Asset NP Risk (2037) | New Asset NP Risk (2038) | New Asset NP Risk (2039) | New Asset NP Risk (2040) | New Asset NP Risk (2041) | New Asset NP Risk (2042) | New Asset NP Risk (2043) | New Asset NP Risk (2044) | New Asset NP Risk (2045) | New Asset NP Risk (2046) | New Asset NP Risk (2047) | New Asset NP Risk (2048) | New Asset NP Risk (2049) | New Asset NP Risk (2050) | New Asset NP Risk (2051) | New Asset NP Risk (2052) | New Asset NP Risk (2053) | New Asset NP Risk (2054) |  | Delta NP Risk (2025) | Delta NP Risk (2026) | Delta NP Risk (2027) | Delta NP Risk (2028) | Delta NP Risk (2029) | Delta NP Risk (2030) | Delta NP Risk (2031) | Delta NP Risk (2032) | Delta NP Risk (2033) | Delta NP Risk (2034) | Delta NP Risk (2035) | Delta NP Risk (2036) | Delta NP Risk (2037) | Delta NP Risk (2038) | Delta NP Risk (2039) | Delta NP Risk (2040) | Delta NP Risk (2041) | Delta NP Risk (2042) | Delta NP Risk (2043) | Delta NP Risk (2044) | Delta NP Risk (2045) | Delta NP Risk (2046) | Delta NP Risk (2047) | Delta NP Risk (2048) | Delta NP Risk (2049) | Delta NP Risk (2050) | Delta NP Risk (2051) | Delta NP Risk (2052) | Delta NP Risk (2053) | Delta NP Risk (2054) |  | Delta Risk (2025) | Delta Risk (2026) | Delta Risk (2027) | Delta Risk (2028) | Delta Risk (2029) | Delta Risk (2030) | Delta Risk (2031) | Delta Risk (2032) | Delta Risk (2033) | Delta Risk (2034) | Delta Risk (2035) | Delta Risk (2036) | Delta Risk (2037) | Delta Risk (2038) | Delta Risk (2039) | Delta Risk (2040) | Delta Risk (2041) | Delta Risk (2042) | Delta Risk (2043) | Delta Risk (2044) | Delta Risk (2045) | Delta Risk (2046) | Delta Risk (2047) | Delta Risk (2048) | Delta Risk (2049) | Delta Risk (2050) | Delta Risk (2051) | Delta Risk (2052) | Delta Risk (2053) | Delta Risk (2054)
|  | Asset Index | Asset ID 1 | Asset ID 2 | Asset ID 3 | Asset Description 1 | Asset Description 2 | Asset Description 3 | Asset Description 4 | Asset Description 5 | Asset Description 6 | Asset Description 7 | Asset Description 8 | Relay Type | Blank 1 | Demand Dist | Time Between Inspections Used | Blank 2 | Current HI | Current PoF | Y0 POF Cons | Y0 POF No Cons | Current Financial Risk OPEX | Current Financial Risk CAPEX | Current Financial Risk TOTEX | Current Safety Risk | Current Environmental Risk | Current Network Performance Risk | Blank 22 | Future HI | Future PoF | YN POF Cons | YN POF No Cons | Future Financial Risk OPEX | Future Financial Risk CAPEX | Future Financial Risk TOTEX | Future Safety Risk | Future Environmental Risk | Future Network Performance Risk | Blank 3 | New PoF | NEW POF Cons | NEW POF No Cons | New Financial Risk OPEX | New Financial Risk CAPEX | New Financial Risk TOTEX | New Safety Risk | New Environmental Risk | New Network Performance Risk | Blank 4 | Current Total Risk | Future Total Risk | New Total Risk | Delta Risk | Column1 | Forecast Ageing Rate | Column3 | Health Index FY1 | Health Index FY2 | Health Index FY3 | Health Index FY4 | Health Index FY5 | Health Index FY6 | Health Index FY7 | Health Index FY8 | Health Index FY9 | Health Index FY10 | Health Index FY11 | Health Index FY12 | Health Index FY13 | Health Index FY14 | Health Index FY15 | Health Index FY16 | Health Index FY17 | Health Index FY18 | Health Index FY19 | Health Index FY20 | Health Index FY21 | Health Index FY22 | Health Index FY23 | Health Index FY24 | Health Index FY25 | Health Index FY26 | Health Index FY27 | Health Index FY28 | Health Index FY29 | Health Index FY30 | Delta Risk22 | PoF FY1 | PoF FY2 | PoF FY3 | PoF FY4 | PoF FY5 | PoF FY6 | PoF FY7 | PoF FY8 | PoF FY9 | PoF FY10 | PoF FY11 | PoF FY12 | PoF FY13 | PoF FY14 | PoF FY15 | PoF FY16 | PoF FY17 | PoF FY18 | PoF FY19 | PoF FY20 | PoF FY21 | PoF FY22 | PoF FY23 | PoF FY24 | PoF FY25 | PoF FY26 | PoF FY27 | PoF FY28 | PoF FY29 | PoF FY30 | Column2 | NP POF FY1 | NP POF FY2 | NP POF FY3 | NP POF FY4 | NP POF FY5 | NP POF FY6 | NP POF FY7 | NP POF FY8 | NP POF FY9 | NP POF FY10 | NP POF FY11 | NP POF FY12 | NP POF FY13 | NP POF FY14 | NP POF FY15 | NP POF FY16 | NP POF FY17 | NP POF FY18 | NP POF FY19 | NP POF FY20 | NP POF FY21 | NP POF FY22 | NP POF FY23 | NP POF FY24 | NP POF FY25 | NP POF FY26 | NP POF FY27 | NP POF FY28 | NP POF FY29 | NP POF FY30 | [63 empty] | Future Future Opex Risk (2026) | Future Future Opex Risk (2027) | Future Future Opex Risk (2028) | Future Future Opex Risk (2029) | Future Future Opex Risk (2030) | Future Future Opex Risk (2031) | Future Future Opex Risk (2032) | Future Future Opex Risk (2033) | Future Future Opex Risk (2034) | Future Future Opex Risk (2035) | Future Future Opex Risk (2036) | Future Future Opex Risk (2037) | Future Future Opex Risk (2038) | Future Future Opex Risk (2039) | Future Future Opex Risk (2040) | Future Future Opex Risk (2041) | Future Future Opex Risk (2042) | Future Future Opex Risk (2043) | Future Future Opex Risk (2044) | Future Future Opex Risk (2045) | Future Future Opex Risk (2046) | Future Future Opex Risk (2047) | Future Future Opex Risk (2048) | Future Future Opex Risk (2049) | Future Future Opex Risk (2050) | Future Future Opex Risk (2051) | Future Future Opex Risk (2052) | Future Future Opex Risk (2053) | Future Future Opex Risk (2054) | Delta Risk107 | New Asset Opex Risk FY1 | New Asset Opex Risk FY2 | New Asset Opex Risk FY3 | New Asset Opex Risk FY4 | New Asset Opex Risk FY5 | New Asset Opex Risk FY6 | New Asset Opex Risk FY7 | New Asset Opex Risk FY8 | New Asset Opex Risk FY9 | New Asset Opex Risk FY10 | New Asset Opex Risk FY11 | New Asset Opex Risk FY12 | New Asset Opex Risk FY13 | New Asset Opex Risk FY14 | New Asset Opex Risk FY15 | New Asset Opex Risk FY16 | New Asset Opex Risk FY17 | New Asset Opex Risk FY18 | New Asset Opex Risk FY19 | New Asset Opex Risk FY20 | New Asset Opex Risk FY21 | New Asset Opex Risk FY22 | New Asset Opex Risk FY23 | New Asset Opex Risk FY24 | New Asset Opex Risk FY25 | New Asset Opex Risk FY26 | New Asset Opex Risk FY27 | New Asset Opex Risk FY28 | New Asset Opex Risk FY29 | New Asset Opex Risk FY30 | Delta Risk126 | Delta Opex Risk FY1 | Delta Opex Risk FY2 | Delta Opex Risk FY3 | Delta Opex Risk FY4 | Delta Opex Risk FY5 | Delta Opex Risk FY6 | Delta Opex Risk FY7 | Delta Opex Risk FY8 | Delta Opex Risk FY9 | Delta Opex Risk FY10 | Delta Opex Risk FY11 | Delta Opex Risk FY12 | Delta Opex Risk FY13 | Delta Opex Risk FY14 | Delta Opex Risk FY15 | Delta Opex Risk FY16 | Delta Opex Risk FY17 | Delta Opex Risk FY18 | Delta Opex Risk FY19 | Delta Opex Risk FY20 | Delta Opex Risk FY21 | Delta Opex Risk FY22 | Delta Opex Risk FY23 | Delta Opex Risk FY24 | Delta Opex Risk FY25 | Delta Opex Risk FY26 | Delta Opex Risk FY27 | Delta Opex Risk FY28 | Delta Opex Risk FY29 | Delta Opex Risk FY30 | NewRisk FY21 | Future Capex Risk FY1 | Future Capex Risk FY2 | Future Capex Risk FY3 | Future Capex Risk FY4 | Future Capex Risk FY5 | Future Capex Risk FY6 | Future Capex Risk FY7 | Future Capex Risk FY8 | Future Capex Risk FY9 | Future Capex Risk FY10 | Future Capex Risk FY11 | Future Capex Risk FY12 | Future Capex Risk FY13 | Future Capex Risk FY14 | Future Capex Risk FY15 | Future Capex Risk FY16 | Future Capex Risk FY17 | Future Capex Risk FY18 | Future Capex Risk FY19 | Future Capex Risk FY20 | Future Capex Risk FY21 | Future Capex Risk FY22 | Future Capex Risk FY23 | Future Capex Risk FY24 | Future Capex Risk FY25 | Future Capex Risk FY26 | Future Capex Risk FY27 | Future Capex Risk FY28 | Future Capex Risk FY29 | Future Capex Risk FY30 | NewRisk FY2312 | New Asset Capex Risk FY1 | New Asset Capex Risk FY2 | New Asset Capex Risk FY3 | New Asset Capex Risk FY4 | New Asset Capex Risk FY5 | New Asset Capex Risk FY6 | New Asset Capex Risk FY7 | New Asset Capex Risk FY8 | New Asset Capex Risk FY9 | New Asset Capex Risk FY10 | New Asset Capex Risk FY11 | New Asset Capex Risk FY12 | New Asset Capex Risk FY13 | New Asset Capex Risk FY14 | New Asset Capex Risk FY15 | New Asset Capex Risk FY16 | New Asset Capex Risk FY17 | New Asset Capex Risk FY18 | New Asset Capex Risk FY19 | New Asset Capex Risk FY20 | New Asset Capex Risk FY21 | New Asset Capex Risk FY22 | New Asset Capex Risk FY23 | New Asset Capex Risk FY24 | New Asset Capex Risk FY25 | New Asset Capex Risk FY26 | New Asset Capex Risk FY27 | New Asset Capex Risk FY28 | New Asset Capex Risk FY29 | New Asset Capex Risk FY30 | NewRisk FY41 | Delta Capex Risk FY1 | Delta Capex Risk FY2 | Delta Capex Risk FY3 | Delta Capex Risk FY4 | Delta Capex Risk FY5 | Delta Capex Risk FY6 | Delta Capex Risk FY7 | Delta Capex Risk FY8 | Delta Capex Risk FY9 | Delta Capex Risk FY10 | Delta Capex Risk FY11 | Delta Capex Risk FY12 | Delta Capex Risk FY13 | Delta Capex Risk FY14 | Delta Capex Risk FY15 | Delta Capex Risk FY16 | Delta Capex Risk FY17 | Delta Capex Risk FY18 | Delta Capex Risk FY19 | Delta Capex Risk FY20 | Delta Capex Risk FY21 | Delta Capex Risk FY22 | Delta Capex Risk FY23 | Delta Capex Risk FY24 | Delta Capex Risk FY25 | Delta Capex Risk FY26 | Delta Capex Risk FY27 | Delta Capex Risk FY28 | Delta Capex Risk FY29 | Delta Capex Risk FY30 | Column8 | Delta Totex Risk FY1 | Delta Totex Risk FY2 | Delta Totex Risk FY3 | Delta Totex Risk FY4 | Delta Totex Risk FY5 | Delta Totex Risk FY6 | Delta Totex Risk FY7 | Delta Totex Risk FY8 | Delta Totex Risk FY9 | Delta Totex Risk FY10 | Delta Totex Risk FY11 | Delta Totex Risk FY12 | Delta Totex Risk FY13 | Delta Totex Risk FY14 | Delta Totex Risk FY15 | Delta Totex Risk FY16 | Delta Totex Risk FY17 | Delta Totex Risk FY18 | Delta Totex Risk FY19 | Delta Totex Risk FY20 | Delta Totex Risk FY21 | Delta Totex Risk FY22 | Delta Totex Risk FY23 | Delta Totex Risk FY24 | Delta Totex Risk FY25 | Delta Totex Risk FY26 | Delta Totex Risk FY27 | Delta Totex Risk FY28 | Delta Totex Risk FY29 | Delta Totex Risk FY30 | Delta Totex Risk FY212 | Future Safety Risk FY1 | Future Safety Risk FY2 | Future Safety Risk FY3 | Future Safety Risk FY4 | Future Safety Risk FY5 | Future Safety Risk FY6 | Future Safety Risk FY7 | Future Safety Risk FY8 | Future Safety Risk FY9 | Future Safety Risk FY10 | Future Safety Risk FY11 | Future Safety Risk FY12 | Future Safety Risk FY13 | Future Safety Risk FY14 | Future Safety Risk FY15 | Future Safety Risk FY16 | Future Safety Risk FY17 | Future Safety Risk FY18 | Future Safety Risk FY19 | Future Safety Risk FY20 | Future Safety Risk FY21 | Future Safety Risk FY22 | Future Safety Risk FY23 | Future Safety Risk FY24 | Future Safety Risk FY25 | Future Safety Risk FY26 | Future Safety Risk FY27 | Future Safety Risk FY28 | Future Safety Risk FY29 | Future Safety Risk FY30 | Column5 | New Asset Safety Risk FY1 | New Asset Safety Risk FY2 | New Asset Safety Risk FY3 | New Asset Safety Risk FY4 | New Asset Safety Risk FY5 | New Asset Safety Risk FY6 | New Asset Safety Risk FY7 | New Asset Safety Risk FY8 | New Asset Safety Risk FY9 | New Asset Safety Risk FY10 | New Asset Safety Risk FY11 | New Asset Safety Risk FY12 | New Asset Safety Risk FY13 | New Asset Safety Risk FY14 | New Asset Safety Risk FY15 | New Asset Safety Risk FY16 | New Asset Safety Risk FY17 | New Asset Safety Risk FY18 | New Asset Safety Risk FY19 | New Asset Safety Risk FY20 | New Asset Safety Risk FY21 | New Asset Safety Risk FY22 | New Asset Safety Risk FY23 | New Asset Safety Risk FY24 | New Asset Safety Risk FY25 | New Asset Safety Risk FY26 | New Asset Safety Risk FY27 | New Asset Safety Risk FY28 | New Asset Safety Risk FY29 | New Asset Safety Risk FY30 | Delta Risk FY42 | Delta Safety Risk FY1 | Delta Safety Risk FY2 | Delta Safety Risk FY3 | Delta Safety Risk FY4 | Delta Safety Risk FY5 | Delta Safety Risk FY6 | Delta Safety Risk FY7 | Delta Safety Risk FY8 | Delta Safety Risk FY9 | Delta Safety Risk FY10 | Delta Safety Risk FY11 | Delta Safety Risk FY12 | Delta Safety Risk FY13 | Delta Safety Risk FY14 | Delta Safety Risk FY15 | Delta Safety Risk FY16 | Delta Safety Risk FY17 | Delta Safety Risk FY18 | Delta Safety Risk FY19 | Delta Safety Risk FY20 | Delta Safety Risk FY21 | Delta Safety Risk FY22 | Delta Safety Risk FY23 | Delta Safety Risk FY24 | Delta Safety Risk FY25 | Delta Safety Risk FY26 | Delta Safety Risk FY27 | Delta Safety Risk FY28 | Delta Safety Risk FY29 | Delta Safety Risk FY30 | Delta Safety Risk FY2010 | Future Environment Risk FY1 | Future Environment Risk FY2 | Future Environment Risk FY3 | Future Environment Risk FY4 | Future Environment Risk FY5 | Future Environment Risk FY6 | Future Environment Risk FY7 | Future Environment Risk FY8 | Future Environment Risk FY9 | Future Environment Risk FY10 | Future Environment Risk FY11 | Future Environment Risk FY12 | Future Environment Risk FY13 | Future Environment Risk FY14 | Future Environment Risk FY15 | Future Environment Risk FY16 | Future Environment Risk FY17 | Future Environment Risk FY18 | Future Environment Risk FY19 | Future Environment Risk FY20 | Future Environment Risk FY21 | Future Environment Risk FY22 | Future Environment Risk FY23 | Future Environment Risk FY24 | Future Environment Risk FY25 | Future Environment Risk FY26 | Future Environment Risk FY27 | Future Environment Risk FY28 | Future Environment Risk FY29 | Future Environment Risk FY30 | Delta Safety Risk FY212 | New Asset Environment Risk FY1 | New Asset Environment Risk FY2 | New Asset Environment Risk FY3 | New Asset Environment Risk FY4 | New Asset Environment Risk FY5 | New Asset Environment Risk FY6 | New Asset Environment Risk FY7 | New Asset Environment Risk FY8 | New Asset Environment Risk FY9 | New Asset Environment Risk FY10 | New Asset Environment Risk FY11 | New Asset Environment Risk FY12 | New Asset Environment Risk FY13 | New Asset Environment Risk FY14 | New Asset Environment Risk FY15 | New Asset Environment Risk FY16 | New Asset Environment Risk FY17 | New Asset Environment Risk FY18 | New Asset Environment Risk FY19 | New Asset Environment Risk FY20 | New Asset Environment Risk FY21 | New Asset Environment Risk FY22 | New Asset Environment Risk FY23 | New Asset Environment Risk FY24 | New Asset Environment Risk FY25 | New Asset Environment Risk FY26 | New Asset Environment Risk FY27 | New Asset Environment Risk FY28 | New Asset Environment Risk FY29 | New Asset Environment Risk FY30 | Column4 | Delta Environment Risk FY1 | Delta Environment Risk FY2 | Delta Environment Risk FY3 | Delta Environment Risk FY4 | Delta Environment Risk FY5 | Delta Environment Risk FY6 | Delta Environment Risk FY7 | Delta Environment Risk FY8 | Delta Environment Risk FY9 | Delta Environment Risk FY10 | Delta Environment Risk FY11 | Delta Environment Risk FY12 | Delta Environment Risk FY13 | Delta Environment Risk FY14 | Delta Environment Risk FY15 | Delta Environment Risk FY16 | Delta Environment Risk FY17 | Delta Environment Risk FY18 | Delta Environment Risk FY19 | Delta Environment Risk FY20 | Delta Environment Risk FY21 | Delta Environment Risk FY22 | Delta Environment Risk FY23 | Delta Environment Risk FY24 | Delta Environment Risk FY25 | Delta Environment Risk FY26 | Delta Environment Risk FY27 | Delta Environment Risk FY28 | Delta Environment Risk FY29 | Delta Environment Risk FY30 | Delta Risk FY44 | Future NP Risk FY1 | Future NP Risk FY2 | Future NP Risk FY3 | Future NP Risk FY4 | Future NP Risk FY5 | Future NP Risk FY6 | Future NP Risk FY7 | Future NP Risk FY8 | Future NP Risk FY9 | Future NP Risk FY10 | Future NP Risk FY11 | Future NP Risk FY12 | Future NP Risk FY13 | Future NP Risk FY14 | Future NP Risk FY15 | Future NP Risk FY16 | Future NP Risk FY17 | Future NP Risk FY18 | Future NP Risk FY19 | Future NP Risk FY20 | Future NP Risk FY21 | Future NP Risk FY22 | Future NP Risk FY23 | Future NP Risk FY24 | Future NP Risk FY25 | Future NP Risk FY26 | Future NP Risk FY27 | Future NP Risk FY28 | Future NP Risk FY29 | Future NP Risk FY30 | Column6 | New Asset NP Risk FY1 | New Asset NP Risk FY2 | New Asset NP Risk FY3 | New Asset NP Risk FY4 | New Asset NP Risk FY5 | New Asset NP Risk FY6 | New Asset NP Risk FY7 | New Asset NP Risk FY8 | New Asset NP Risk FY9 | New Asset NP Risk FY10 | New Asset NP Risk FY11 | New Asset NP Risk FY12 | New Asset NP Risk FY13 | New Asset NP Risk FY14 | New Asset NP Risk FY15 | New Asset NP Risk FY16 | New Asset NP Risk FY17 | New Asset NP Risk FY18 | New Asset NP Risk FY19 | New Asset NP Risk FY20 | New Asset NP Risk FY21 | New Asset NP Risk FY22 | New Asset NP Risk FY23 | New Asset NP Risk FY24 | New Asset NP Risk FY25 | New Asset NP Risk FY26 | New Asset NP Risk FY27 | New Asset NP Risk FY28 | New Asset NP Risk FY29 | New Asset NP Risk FY30 | Delta Risk FY480 | Delta NP Risk FY1 | Delta NP Risk FY2 | Delta NP Risk FY3 | Delta NP Risk FY4 | Delta NP Risk FY5 | Delta NP Risk FY6 | Delta NP Risk FY7 | Delta NP Risk FY8 | Delta NP Risk FY9 | Delta NP Risk FY10 | Delta NP Risk FY11 | Delta NP Risk FY12 | Delta NP Risk FY13 | Delta NP Risk FY14 | Delta NP Risk FY15 | Delta NP Risk FY16 | Delta NP Risk FY17 | Delta NP Risk FY18 | Delta NP Risk FY19 | Delta NP Risk FY20 | Delta NP Risk FY21 | Delta NP Risk FY22 | Delta NP Risk FY23 | Delta NP Risk FY24 | Delta NP Risk FY25 | Delta NP Risk FY26 | Delta NP Risk FY27 | Delta NP Risk FY28 | Delta NP Risk FY29 | Delta NP Risk FY30 | Column7 | Delta Risk FY1 | Delta Risk FY2 | Delta Risk FY3 | Delta Risk FY4 | Delta Risk FY5 | Delta Risk FY6 | Delta Risk FY7 | Delta Risk FY8 | Delta Risk FY9 | Delta Risk FY10 | Delta Risk FY11 | Delta Risk FY12 | Delta Risk FY13 | Delta Risk FY14 | Delta Risk FY15 | Delta Risk FY16 | Delta Risk FY17 | Delta Risk FY18 | Delta Risk FY19 | Delta Risk FY20 | Delta Risk FY212 | Delta Risk FY22 | Delta Risk FY23 | Delta Risk FY24 | Delta Risk FY25 | Delta Risk FY26 | Delta Risk FY27 | Delta Risk FY28 | Delta Risk FY29 | Delta Risk FY30
| FALSE | 458 | 22013856 | BC | Blank | 11 | BUS ALL | VOLTAGE REGULATION | C | RMS | 2V162 | 2V162 | 2V162 | Electronic |  | 0 | 2190 |  | 5.8543 | 0.010886 | 0 | 0.010886 | 37.4211 | 0 | 37.4211 | 30.9016 | 4.3555 | 0 |  | 13.88 | 0.10835 | 0 | 0.10835 | 372.4584 | 0 | 372.4584 | 307.5684 | 43.3515 | 0 |  | 0.0051679 | 0 | 0.0051679 | 17.7648 | 0 | 17.7648 | 14.6698 | 2.0677 | 0 |  | 72.6782 | 723.3783 | 34.5023 | 688.8761 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.013522 | 0.016856 | 0.021081 | 0.026444 | 0.033262 | 0.041945 | 0.053017 | 0.067154 | 0.085226 | 0.10835 | 0.13798 | 0.17596 | 0.2247 | 0.2873 | 0.36776 | 0.47123 | 0.60438 | 0.77582 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2767 | 112.535 | 140.7402 | 176.5439 | 222.0673 | 280.0363 | 353.9559 | 448.3364 | 568.9842 | 723.3783 | 921.1568 | 1174.7453 | 1500.1697 | 1918.1069 | 2455.2434 | 3146.0333 | 4034.9713 | 5179.5341 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 46.4824 | 57.9429 | 72.4654 | 90.9003 | 114.3397 | 144.1872 | 182.2475 | 230.8428 | 292.9628 | 372.4584 | 474.2921 | 604.8617 | 772.4186 | 987.6092 | 1264.1741 | 1619.8531 | 2077.5562 | 2666.8772 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 32.2705 | 43.731 | 58.2535 | 76.6884 | 100.1279 | 129.9753 | 168.0356 | 216.631 | 278.751 | 358.2466 | 460.0803 | 590.6498 | 758.2068 | 973.3974 | 1249.9622 | 1605.6413 | 2063.3443 | 2649.8666 | 2731.8443 | 2724.2423 | 2713.7602 | 2699.2475 | 2679.0803 | 2650.9622 | 2611.6413 | 2556.507 | 2479.0141 | 2369.8626 | 2215.825 | 1998.073 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 32.2705 | 43.731 | 58.2535 | 76.6884 | 100.1279 | 129.9753 | 168.0356 | 216.631 | 278.751 | 358.2466 | 460.0803 | 590.6498 | 758.2068 | 973.3974 | 1249.9622 | 1605.6413 | 2063.3443 | 2649.8666 | 2731.8443 | 2724.2423 | 2713.7602 | 2699.2475 | 2679.0803 | 2650.9622 | 2611.6413 | 2556.507 | 2479.0141 | 2369.8626 | 2215.825 | 1998.073 |  | 38.3842 | 47.848 | 59.8404 | 75.0635 | 94.4193 | 119.0668 | 150.4962 | 190.6252 | 241.9226 | 307.5684 | 391.6606 | 499.4822 | 637.8472 | 815.5471 | 1043.9287 | 1337.641 | 1715.6027 | 2202.2518 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 23.7144 | 33.1782 | 45.1706 | 60.3938 | 79.7496 | 104.397 | 135.8264 | 175.9554 | 227.2528 | 292.8987 | 376.9908 | 484.8124 | 623.1774 | 800.8774 | 1029.2589 | 1322.9712 | 1700.9329 | 2184.693 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 5.4102 | 6.7441 | 8.4344 | 10.5801 | 13.3083 | 16.7823 | 21.2123 | 26.8684 | 34.0987 | 43.3515 | 55.2042 | 70.4015 | 89.9039 | 114.9505 | 147.1407 | 188.5391 | 241.8124 | 310.4051 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 3.3425 | 4.6764 | 6.3667 | 8.5124 | 11.2406 | 14.7146 | 19.1446 | 24.8007 | 32.0311 | 41.2838 | 53.1365 | 68.3338 | 87.8362 | 112.8828 | 145.073 | 186.4714 | 239.7447 | 307.9302 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 59.3274 | 81.5857 | 109.7909 | 145.5946 | 191.118 | 249.087 | 323.0066 | 417.3871 | 538.0349 | 692.429 | 890.2075 | 1143.796 | 1469.2204 | 1887.1576 | 2424.2941 | 3115.084 | 4004.022 | 5142.4897 | 5300.4001 | 5283.8453 | 5261.0181 | 5229.4137 | 5185.4953 | 5124.262 | 5038.6324 | 4918.5654 | 4749.8081 | 4512.1072 | 4176.6572 | 3702.4555
| FALSE | 459 | 22013375 | BC | Blank | 11 | BUS ALL | POWER QUALITY | I | Schneider | ION_7650 | ION 7650 | ION 7000s | Digital |  | 0.033587 | 1 |  | 1.5657 | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.019022 | 14.2309 | 14.6711 | 2.0677 | 0.11017 |  | 6.522 | 0.016792 | 7.7259e-07 | 0.016791 | 46.1779 | 0.061808 | 46.2397 | 47.6701 | 6.7184 | 0.35796 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.019022 | 14.2309 | 14.6711 | 2.0677 | 0.11017 |  | 31.0799 | 100.9862 | 31.0799 | 69.9063 |  | 0.14268 |  | 1.8058 | 2.0828 | 2.4022 | 2.7706 | 3.1955 | 3.6856 | 4.2509 | 4.9028 | 5.6548 | 6.522 | 7.5223 | 8.6759 | 10.0065 | 11.5412 | 13.3112 | 15.3527 | 17.7073 | 20.423 | 23.5552 | 27.1678 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0059365 | 0.0082972 | 0.01174 | 0.016792 | 0.024247 | 0.035303 | 0.051771 | 0.076395 | 0.11334 | 0.16892 | 0.25277 | 0.37953 | 0.57156 | 0.86294 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.7314e-07 | 3.8176e-07 | 5.4015e-07 | 7.7259e-07 | 1.1156e-06 | 1.6243e-06 | 2.382e-06 | 3.5149e-06 | 5.2146e-06 | 7.772e-06 | 1.163e-05 | 1.7462e-05 | 2.6297e-05 | 3.9704e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 35.7021 | 49.8995 | 70.6036 | 100.9862 | 145.8218 | 212.3137 | 311.3531 | 459.4381 | 681.6011 | 1015.8782 | 1520.1363 | 2282.5099 | 3437.3604 | 5189.6935 | 5663.7344 | 5663.7344 | 5663.7344 | 5663.7344 | 5663.7344 | 5663.7344 | 5663.7344 | 5663.7344 | 5663.7344 | 5663.7344 |  | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 31.0799 | 37.2007 | 49.3117 | 65.9365 | 88.8599 | 120.5978 | 164.7015 | 226.1931 | 312.1841 | 432.7578 | 602.2273 | 840.9313 | 1177.7969 | 1653.9997 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 16.3255 | 22.8175 | 32.2849 | 46.1779 | 66.6799 | 97.0846 | 142.3722 | 210.087 | 311.6753 | 464.5299 | 695.1117 | 1043.7218 | 1571.7995 | 2373.0878 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1136 | 8.6056 | 18.073 | 31.966 | 52.468 | 82.8727 | 128.1603 | 195.8751 | 297.4634 | 450.318 | 680.8998 | 1026.7111 | 1549.2508 | 2342.937 | 2549.2192 | 2534.7064 | 2514.5392 | 2486.4209 | 2447.0999 | 2391.9652 | 2314.472 | 2205.32 | 2051.2817 | 1833.5287 |  | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.021851 | 0.03054 | 0.043212 | 0.061808 | 0.089249 | 0.12994 | 0.19056 | 0.28119 | 0.41717 | 0.62176 | 0.93038 | 1.397 | 2.1038 | 3.1763 | 3.4664 | 3.4664 | 3.4664 | 3.4664 | 3.4664 | 3.4664 | 3.4664 | 3.4664 | 3.4664 | 3.4664 |  | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.019022 | 0.022768 | 0.030181 | 0.040356 | 0.054386 | 0.073811 | 0.1008 | 0.13844 | 0.19107 | 0.26486 | 0.36859 | 0.51468 | 0.72086 | 1.0123 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.0028289 | 0.011518 | 0.02419 | 0.042785 | 0.070227 | 0.11092 | 0.17154 | 0.26217 | 0.39814 | 0.60273 | 0.91136 | 1.3742 | 2.0736 | 3.1359 | 3.412 | 3.3926 | 3.3656 | 3.328 | 3.2754 | 3.2016 | 3.0978 | 2.9517 | 2.7456 | 2.4541 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1164 | 8.6172 | 18.0972 | 32.0088 | 52.5382 | 82.9836 | 128.3319 | 196.1372 | 297.8616 | 450.9208 | 681.8112 | 1028.0853 | 1551.3244 | 2346.073 | 2552.6312 | 2538.0991 | 2517.9048 | 2489.7489 | 2450.3752 | 2395.1668 | 2317.5699 | 2208.2717 | 2054.0273 | 1835.9829 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 16.853 | 23.5549 | 33.3281 | 47.6701 | 68.8346 | 100.2218 | 146.9729 | 216.8758 | 321.7469 | 479.5409 | 717.5737 | 1077.4489 | 1622.5911 | 2449.7723 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1819 | 8.8837 | 18.657 | 32.999 | 54.1634 | 85.5506 | 132.3017 | 202.2046 | 307.0757 | 464.8697 | 702.9026 | 1059.8885 | 1599.3137 | 2418.6473 | 2631.5953 | 2616.6136 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.3752 | 3.3197 | 4.6971 | 6.7184 | 9.7013 | 14.1249 | 20.7138 | 30.5656 | 45.3458 | 67.5846 | 101.1321 | 151.8515 | 228.6818 | 345.2615 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.3075 | 1.252 | 2.6294 | 4.6507 | 7.6336 | 12.0572 | 18.6461 | 28.4979 | 43.2781 | 65.517 | 99.0644 | 149.3766 | 225.4011 | 340.8749 | 370.8869 | 368.7755 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.12655 | 0.17688 | 0.25027 | 0.35796 | 0.51689 | 0.75258 | 1.1036 | 1.6286 | 2.416 | 3.6009 | 5.3884 | 8.0907 | 12.1843 | 18.3957 | 20.076 | 20.076 | 20.076 | 20.076 | 20.076 | 20.076 | 20.076 | 20.076 | 20.076 | 20.076 |  | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.13186 | 0.17479 | 0.23372 | 0.31498 | 0.42748 | 0.58381 | 0.80178 | 1.1066 | 1.534 | 2.1347 | 2.9808 | 4.1749 | 5.8629 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.016384 | 0.066709 | 0.1401 | 0.24779 | 0.40672 | 0.64241 | 0.99347 | 1.5184 | 2.3059 | 3.4908 | 5.2782 | 7.9589 | 12.0095 | 18.162 | 19.761 | 19.6485 | 19.4922 | 19.2742 | 18.9694 | 18.542 | 17.9413 | 17.0952 | 15.9011 | 14.2131 |  | 0 | 0 | 0 | 0 | 0 | 0 | 4.6222 | 18.8196 | 39.5237 | 69.9063 | 114.7419 | 181.2338 | 280.2732 | 428.3582 | 650.5212 | 984.7982 | 1489.0564 | 2245.3092 | 3388.0487 | 5123.7571 | 5574.8744 | 5543.1366 | 5499.0329 | 5437.5413 | 5351.5503 | 5230.9766 | 5061.5071 | 4822.8031 | 4485.9375 | 4009.7347
| FALSE | 460 | 22005297 | BC | Blank | 11 | BUS ALL | STRUCTURE LEAKAGE | Blank | EMAIL | RC3_170 | RC3_170 | RC3 | Electromechanical |  | 0 | 2190 |  | 5.5 | 0.0019187 | 0 | 0.0019187 | 10.5531 | 0 | 10.5531 | 5.4466 | 0.76769 | 0 |  | 7.1791 | 0.0037591 | 0 | 0.0037591 | 20.6752 | 0 | 20.6752 | 10.6707 | 1.504 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 16.7674 | 32.8499 | 45.1611 | -12.3112 |  | 0.026643 |  | 5.6485 | 5.801 | 5.9577 | 6.1185 | 6.2837 | 6.4534 | 6.6277 | 6.8066 | 6.9904 | 7.1791 | 7.373 | 7.5721 | 7.7765 | 7.9865 | 8.2022 | 8.4236 | 8.6511 | 8.8847 | 9.1246 | 9.3709 | 9.624 | 9.8838 | 10.1507 | 10.4248 | 10.7063 | 10.9954 | 11.2923 | 11.5972 | 11.9103 | 12.2319 |  | 0.002049 | 0.0021888 | 0.0023391 | 0.0025006 | 0.0026742 | 0.0028608 | 0.0030615 | 0.0032773 | 0.0035094 | 0.0037591 | 0.0040278 | 0.004317 | 0.0046283 | 0.0049635 | 0.0053243 | 0.0057129 | 0.0061314 | 0.0065822 | 0.0070679 | 0.0075912 | 0.0081552 | 0.0087631 | 0.0094183 | 0.010125 | 0.010886 | 0.011708 | 0.012593 | 0.013548 | 0.014579 | 0.015691 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.9052 | 19.1275 | 20.4407 | 21.852 | 23.3689 | 24.9997 | 26.7532 | 28.639 | 30.6675 | 32.8499 | 35.1982 | 37.7254 | 40.4457 | 43.3742 | 46.5274 | 49.9231 | 53.5804 | 57.52 | 61.7644 | 66.3377 | 71.2662 | 76.578 | 82.3038 | 88.4766 | 95.132 | 102.3088 | 110.0485 | 118.3964 | 127.4012 | 137.1157 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 11.2692 | 12.0385 | 12.865 | 13.7533 | 14.708 | 15.7344 | 16.838 | 18.0249 | 19.3016 | 20.6752 | 22.1531 | 23.7437 | 25.4558 | 27.299 | 29.2836 | 31.4207 | 33.7226 | 36.2021 | 38.8734 | 41.7518 | 44.8537 | 48.1969 | 51.8006 | 55.6856 | 59.8745 | 64.3914 | 69.2627 | 74.5167 | 80.1842 | 86.2983 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | -2.9426 | -2.1733 | -1.3468 | -0.45857 | 0.49615 | 1.5225 | 2.6262 | 3.8131 | 5.0898 | 6.4633 | 7.9413 | 9.5319 | 11.244 | 13.0872 | 15.0717 | 17.2089 | 19.5107 | 19.1914 | 16.3248 | 11.6012 | 4.221 | -6.9485 | -23.512 | -47.7451 | -82.8771 | -133.4946 | -206.1161 | -310.0136 | -458.3838 | -670.0216 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -2.9426 | -2.1733 | -1.3468 | -0.45857 | 0.49615 | 1.5225 | 2.6262 | 3.8131 | 5.0898 | 6.4633 | 7.9413 | 9.5319 | 11.244 | 13.0872 | 15.0717 | 17.2089 | 19.5107 | 19.1914 | 16.3248 | 11.6012 | 4.221 | -6.9485 | -23.512 | -47.7451 | -82.8771 | -133.4946 | -206.1161 | -310.0136 | -458.3838 | -670.0216 |  | 5.8162 | 6.2132 | 6.6398 | 7.0982 | 7.591 | 8.1207 | 8.6903 | 9.3029 | 9.9618 | 10.6707 | 11.4335 | 12.2544 | 13.1381 | 14.0893 | 15.1136 | 16.2166 | 17.4046 | 18.6843 | 20.0631 | 21.5486 | 23.1495 | 24.875 | 26.7349 | 28.74 | 30.9019 | 33.2332 | 35.7473 | 38.459 | 41.384 | 44.5396 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | -8.8536 | -8.4566 | -8.03 | -7.5716 | -7.0788 | -6.5491 | -5.9795 | -5.3669 | -4.708 | -3.9991 | -3.2363 | -2.4154 | -1.5317 | -0.58045 | 0.44382 | 1.5468 | 2.7348 | 1.1255 | -3.2122 | -9.5735 | -18.7926 | -32.0474 | -51.0046 | -78.0236 | -116.4497 | -171.0295 | -248.5053 | -358.4625 | -514.5387 | -736.152 |  | 0.81979 | 0.87575 | 0.93587 | 1.0005 | 1.0699 | 1.1446 | 1.2249 | 1.3112 | 1.4041 | 1.504 | 1.6115 | 1.7272 | 1.8518 | 1.9859 | 2.1302 | 2.2857 | 2.4532 | 2.6335 | 2.8279 | 3.0373 | 3.2629 | 3.5061 | 3.7683 | 4.0509 | 4.3556 | 4.6842 | 5.0385 | 5.4208 | 5.833 | 6.2778 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | -1.2479 | -1.1919 | -1.1318 | -1.0672 | -0.99775 | -0.92309 | -0.8428 | -0.75646 | -0.66359 | -0.56367 | -0.45615 | -0.34044 | -0.2159 | -0.081814 | 0.062556 | 0.21802 | 0.38547 | 0.15864 | -0.45276 | -1.3494 | -2.6488 | -4.5171 | -7.189 | -10.9973 | -16.4135 | -24.1064 | -35.0266 | -50.5249 | -72.5237 | -103.7599 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -13.0441 | -11.8218 | -10.5086 | -9.0973 | -7.5804 | -5.9496 | -4.1961 | -2.3103 | -0.28178 | 1.9006 | 4.2489 | 6.7761 | 9.4964 | 12.4249 | 15.5781 | 18.9738 | 22.6311 | 20.4756 | 12.6598 | 0.67831 | -17.2204 | -43.513 | -81.7056 | -136.766 | -215.7402 | -328.6304 | -489.648 | -719.001 | -1045.4462 | -1509.9335
| TRUE | 461 | 22005288 | BC | Blank | 11 | BUS NO.1 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.033587 | 2190 |  | 9.9 | 0.0088019 | 0.00083024 | 0.0079716 | 48.8669 | 265.6753 | 314.5422 | 29.6986 | 3.5299 | 384.6683 |  | 13.7946 | 0.021906 | 0.0020663 | 0.01984 | 121.622 | 661.2238 | 782.8458 | 73.915 | 8.7854 | 957.3786 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.11017 |  | 732.439 | 1822.9249 | 45.3489 | 1777.576 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.00090827 | 0.00099396 | 0.0010881 | 0.0011915 | 0.0013051 | 0.00143 | 0.0015672 | 0.0017181 | 0.0018839 | 0.0020663 | 0.0022669 | 0.0024876 | 0.0027303 | 0.0029974 | 0.0032913 | 0.0036147 | 0.0039707 | 0.0043626 | 0.0047941 | 0.0052691 | 0.0057922 | 0.0063682 | 0.0070027 | 0.0077015 | 0.0084713 | 0.0093195 | 0.010254 | 0.011284 | 0.012418 | 0.013669 | 801.2813 | 876.8814 | 959.9183 | 1051.1401 | 1151.3713 | 1261.5204 | 1382.5889 | 1515.6806 | 1662.0121 | 1822.9249 | 1999.8975 | 2194.5605 | 2408.7114 | 2644.3325 | 2903.6094 | 3188.9526 | 3503.0206 | 3848.7453 | 4229.3604 | 4648.4329 | 5109.8972 | 5618.0937 | 6177.8103 | 6794.3293 | 7473.4781 | 8221.6865 | 9046.0484 | 9954.3915 | 10955.3527 | 12058.4627 |  | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 37.2699 | 49.4034 | 66.0591 | 89.0252 | 120.822 | 165.0077 | 226.6137 | 312.7646 | 433.5624 | 603.347 | 842.4948 | 1179.9867 | 1657.0749 |  | 53.4599 | 58.5038 | 64.0439 | 70.13 | 76.8172 | 84.1662 | 92.2436 | 101.1232 | 110.8862 | 121.622 | 133.4292 | 146.4168 | 160.7045 | 176.4247 | 193.7231 | 212.7607 | 233.7147 | 256.7807 | 282.1746 | 310.1343 | 340.9223 | 374.8282 | 412.1714 | 453.3043 | 498.6158 | 548.5348 | 603.5346 | 664.1375 | 730.9196 | 804.517 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 39.248 | 44.2919 | 49.832 | 55.9181 | 62.6053 | 69.9543 | 78.0317 | 86.9113 | 96.6743 | 107.4101 | 119.2174 | 132.2049 | 146.4926 | 162.2128 | 179.5112 | 198.5488 | 219.5028 | 239.77 | 259.6259 | 279.9836 | 300.2894 | 319.6825 | 336.8584 | 349.8731 | 355.8636 | 350.6479 | 328.1545 | 279.6054 | 192.3492 | 48.1936 |  | 290.6463 | 318.0685 | 348.1882 | 381.2768 | 417.6333 | 457.5874 | 501.5022 | 549.7781 | 602.8565 | 661.2238 | 725.4166 | 796.0261 | 873.7044 | 959.1704 | 1053.2172 | 1156.7188 | 1270.6397 | 1396.0434 | 1534.1027 | 1686.1115 | 1853.4971 | 2037.8336 | 2240.8578 | 2464.4858 | 2710.8314 | 2982.2266 | 3281.2449 | 3610.7253 | 3973.8008 | 4373.9285 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 290.5702 | 317.9924 | 348.1121 | 381.2007 | 417.5572 | 457.5113 | 501.4261 | 549.702 | 602.7804 | 661.1477 | 725.3405 | 795.95 | 873.6283 | 959.0944 | 1053.1411 | 1156.6427 | 1270.5636 | 1395.9523 | 1533.982 | 1685.9501 | 1853.2795 | 2037.5383 | 2240.4546 | 2463.9321 | 2710.0671 | 2981.1672 | 3279.7705 | 3608.6666 | 3970.9174 | 4369.8793 |  | 329.8182 | 362.2843 | 397.9441 | 437.1188 | 480.1626 | 527.4656 | 579.4578 | 636.6133 | 699.4547 | 768.5578 | 844.5578 | 928.1549 | 1020.1209 | 1121.3071 | 1232.6523 | 1355.1915 | 1490.0664 | 1635.7223 | 1793.6078 | 1965.9337 | 2153.5689 | 2357.2209 | 2577.3131 | 2813.8052 | 3065.9306 | 3331.8151 | 3607.925 | 3888.2719 | 4163.2666 | 4418.0729 |  | 32.4899 | 35.5553 | 38.9223 | 42.6211 | 46.6852 | 51.1515 | 56.0605 | 61.457 | 67.3904 | 73.915 | 81.0908 | 88.9839 | 97.6672 | 107.221 | 117.734 | 129.304 | 142.0387 | 156.0569 | 171.4899 | 188.4822 | 207.1935 | 227.7996 | 250.4946 | 275.4929 | 303.0307 | 333.3687 | 366.7945 | 403.6255 | 444.212 | 488.9403 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 17.8188 | 20.8842 | 24.2511 | 27.9499 | 32.0141 | 36.4803 | 41.3894 | 46.7859 | 52.7193 | 59.2439 | 66.4197 | 74.3128 | 82.996 | 92.5499 | 103.0629 | 114.6329 | 127.3675 | 138.4965 | 148.2125 | 157.3572 | 165.2475 | 170.8719 | 172.748 | 168.7195 | 155.6655 | 129.0872 | 82.5157 | 6.6675 | -111.7619 | -291.8231 |  | 3.8617 | 4.2261 | 4.6262 | 5.0659 | 5.5489 | 6.0798 | 6.6633 | 7.3047 | 8.0099 | 8.7854 | 9.6383 | 10.5765 | 11.6086 | 12.7441 | 13.9937 | 15.3689 | 16.8825 | 18.5487 | 20.3831 | 22.4027 | 24.6267 | 27.0759 | 29.7734 | 32.7447 | 36.0178 | 39.6237 | 43.5967 | 47.9744 | 52.7984 | 58.1148 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 1.794 | 2.1584 | 2.5586 | 2.9982 | 3.4812 | 4.0121 | 4.5956 | 5.237 | 5.9422 | 6.7177 | 7.5706 | 8.5088 | 9.5409 | 10.6764 | 11.926 | 13.3012 | 14.8148 | 16.0738 | 17.1024 | 18.0161 | 18.715 | 19.0528 | 18.8161 | 17.6965 | 15.2487 | 10.8331 | 3.5315 | -7.9714 | -25.5584 | -51.923 |  | 420.8235 | 460.5278 | 504.1378 | 552.0464 | 604.6866 | 662.5356 | 726.1194 | 796.0175 | 872.8691 | 957.3786 | 1050.3226 | 1152.5573 | 1265.0268 | 1388.7722 | 1524.9413 | 1674.8003 | 1839.7451 | 2021.3156 | 2221.2101 | 2441.302 | 2683.6577 | 2950.5565 | 3244.513 | 3568.3015 | 3924.9824 | 4317.9326 | 4750.8778 | 5227.9288 | 5753.6218 | 6332.9622 |  | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.13186 | 0.17479 | 0.23372 | 0.31498 | 0.42748 | 0.58381 | 0.80178 | 1.1066 | 1.534 | 2.1347 | 2.9808 | 4.1749 | 5.8629 |  | 420.7133 | 460.4176 | 504.0276 | 551.9362 | 604.5764 | 662.4255 | 726.0092 | 795.9074 | 872.759 | 957.2684 | 1050.2124 | 1152.4471 | 1264.9166 | 1388.662 | 1524.8312 | 1674.6901 | 1839.6349 | 2021.1837 | 2221.0353 | 2441.0683 | 2683.3427 | 2950.129 | 3243.9292 | 3567.4997 | 3923.8758 | 4316.3986 | 4748.7431 | 5224.948 | 5749.4469 | 6327.0993 |  | 770.1443 | 845.7444 | 928.7813 | 1020.0032 | 1120.2343 | 1230.3835 | 1351.452 | 1484.5436 | 1630.8751 | 1791.7879 | 1968.7606 | 2163.4236 | 2377.5745 | 2613.1955 | 2872.4724 | 3157.8157 | 3471.8837 | 3811.4763 | 4179.9581 | 4582.3753 | 5020.8741 | 5497.2745 | 6012.8064 | 6567.7208 | 7160.7208 | 7788.1341 | 8442.7154 | 9111.9161 | 9775.3932 | 10401.4261
| TRUE | 462 | 22005287 | BC | Blank | 11 | BUS NO.1 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.033587 | 2190 |  | 9.9 | 0.0088019 | 0.00083024 | 0.0079716 | 48.8669 | 265.6753 | 314.5422 | 29.6986 | 3.5299 | 384.6683 |  | 13.7946 | 0.021906 | 0.0020663 | 0.01984 | 121.622 | 661.2238 | 782.8458 | 73.915 | 8.7854 | 957.3786 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.11017 |  | 732.439 | 1822.9249 | 45.3489 | 1777.576 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.00090827 | 0.00099396 | 0.0010881 | 0.0011915 | 0.0013051 | 0.00143 | 0.0015672 | 0.0017181 | 0.0018839 | 0.0020663 | 0.0022669 | 0.0024876 | 0.0027303 | 0.0029974 | 0.0032913 | 0.0036147 | 0.0039707 | 0.0043626 | 0.0047941 | 0.0052691 | 0.0057922 | 0.0063682 | 0.0070027 | 0.0077015 | 0.0084713 | 0.0093195 | 0.010254 | 0.011284 | 0.012418 | 0.013669 | 801.2813 | 876.8814 | 959.9183 | 1051.1401 | 1151.3713 | 1261.5204 | 1382.5889 | 1515.6806 | 1662.0121 | 1822.9249 | 1999.8975 | 2194.5605 | 2408.7114 | 2644.3325 | 2903.6094 | 3188.9526 | 3503.0206 | 3848.7453 | 4229.3604 | 4648.4329 | 5109.8972 | 5618.0937 | 6177.8103 | 6794.3293 | 7473.4781 | 8221.6865 | 9046.0484 | 9954.3915 | 10955.3527 | 12058.4627 |  | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 37.2699 | 49.4034 | 66.0591 | 89.0252 | 120.822 | 165.0077 | 226.6137 | 312.7646 | 433.5624 | 603.347 | 842.4948 | 1179.9867 | 1657.0749 |  | 53.4599 | 58.5038 | 64.0439 | 70.13 | 76.8172 | 84.1662 | 92.2436 | 101.1232 | 110.8862 | 121.622 | 133.4292 | 146.4168 | 160.7045 | 176.4247 | 193.7231 | 212.7607 | 233.7147 | 256.7807 | 282.1746 | 310.1343 | 340.9223 | 374.8282 | 412.1714 | 453.3043 | 498.6158 | 548.5348 | 603.5346 | 664.1375 | 730.9196 | 804.517 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 39.248 | 44.2919 | 49.832 | 55.9181 | 62.6053 | 69.9543 | 78.0317 | 86.9113 | 96.6743 | 107.4101 | 119.2174 | 132.2049 | 146.4926 | 162.2128 | 179.5112 | 198.5488 | 219.5028 | 239.77 | 259.6259 | 279.9836 | 300.2894 | 319.6825 | 336.8584 | 349.8731 | 355.8636 | 350.6479 | 328.1545 | 279.6054 | 192.3492 | 48.1936 |  | 290.6463 | 318.0685 | 348.1882 | 381.2768 | 417.6333 | 457.5874 | 501.5022 | 549.7781 | 602.8565 | 661.2238 | 725.4166 | 796.0261 | 873.7044 | 959.1704 | 1053.2172 | 1156.7188 | 1270.6397 | 1396.0434 | 1534.1027 | 1686.1115 | 1853.4971 | 2037.8336 | 2240.8578 | 2464.4858 | 2710.8314 | 2982.2266 | 3281.2449 | 3610.7253 | 3973.8008 | 4373.9285 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 290.5702 | 317.9924 | 348.1121 | 381.2007 | 417.5572 | 457.5113 | 501.4261 | 549.702 | 602.7804 | 661.1477 | 725.3405 | 795.95 | 873.6283 | 959.0944 | 1053.1411 | 1156.6427 | 1270.5636 | 1395.9523 | 1533.982 | 1685.9501 | 1853.2795 | 2037.5383 | 2240.4546 | 2463.9321 | 2710.0671 | 2981.1672 | 3279.7705 | 3608.6666 | 3970.9174 | 4369.8793 |  | 329.8182 | 362.2843 | 397.9441 | 437.1188 | 480.1626 | 527.4656 | 579.4578 | 636.6133 | 699.4547 | 768.5578 | 844.5578 | 928.1549 | 1020.1209 | 1121.3071 | 1232.6523 | 1355.1915 | 1490.0664 | 1635.7223 | 1793.6078 | 1965.9337 | 2153.5689 | 2357.2209 | 2577.3131 | 2813.8052 | 3065.9306 | 3331.8151 | 3607.925 | 3888.2719 | 4163.2666 | 4418.0729 |  | 32.4899 | 35.5553 | 38.9223 | 42.6211 | 46.6852 | 51.1515 | 56.0605 | 61.457 | 67.3904 | 73.915 | 81.0908 | 88.9839 | 97.6672 | 107.221 | 117.734 | 129.304 | 142.0387 | 156.0569 | 171.4899 | 188.4822 | 207.1935 | 227.7996 | 250.4946 | 275.4929 | 303.0307 | 333.3687 | 366.7945 | 403.6255 | 444.212 | 488.9403 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 17.8188 | 20.8842 | 24.2511 | 27.9499 | 32.0141 | 36.4803 | 41.3894 | 46.7859 | 52.7193 | 59.2439 | 66.4197 | 74.3128 | 82.996 | 92.5499 | 103.0629 | 114.6329 | 127.3675 | 138.4965 | 148.2125 | 157.3572 | 165.2475 | 170.8719 | 172.748 | 168.7195 | 155.6655 | 129.0872 | 82.5157 | 6.6675 | -111.7619 | -291.8231 |  | 3.8617 | 4.2261 | 4.6262 | 5.0659 | 5.5489 | 6.0798 | 6.6633 | 7.3047 | 8.0099 | 8.7854 | 9.6383 | 10.5765 | 11.6086 | 12.7441 | 13.9937 | 15.3689 | 16.8825 | 18.5487 | 20.3831 | 22.4027 | 24.6267 | 27.0759 | 29.7734 | 32.7447 | 36.0178 | 39.6237 | 43.5967 | 47.9744 | 52.7984 | 58.1148 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 1.794 | 2.1584 | 2.5586 | 2.9982 | 3.4812 | 4.0121 | 4.5956 | 5.237 | 5.9422 | 6.7177 | 7.5706 | 8.5088 | 9.5409 | 10.6764 | 11.926 | 13.3012 | 14.8148 | 16.0738 | 17.1024 | 18.0161 | 18.715 | 19.0528 | 18.8161 | 17.6965 | 15.2487 | 10.8331 | 3.5315 | -7.9714 | -25.5584 | -51.923 |  | 420.8235 | 460.5278 | 504.1378 | 552.0464 | 604.6866 | 662.5356 | 726.1194 | 796.0175 | 872.8691 | 957.3786 | 1050.3226 | 1152.5573 | 1265.0268 | 1388.7722 | 1524.9413 | 1674.8003 | 1839.7451 | 2021.3156 | 2221.2101 | 2441.302 | 2683.6577 | 2950.5565 | 3244.513 | 3568.3015 | 3924.9824 | 4317.9326 | 4750.8778 | 5227.9288 | 5753.6218 | 6332.9622 |  | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.13186 | 0.17479 | 0.23372 | 0.31498 | 0.42748 | 0.58381 | 0.80178 | 1.1066 | 1.534 | 2.1347 | 2.9808 | 4.1749 | 5.8629 |  | 420.7133 | 460.4176 | 504.0276 | 551.9362 | 604.5764 | 662.4255 | 726.0092 | 795.9074 | 872.759 | 957.2684 | 1050.2124 | 1152.4471 | 1264.9166 | 1388.662 | 1524.8312 | 1674.6901 | 1839.6349 | 2021.1837 | 2221.0353 | 2441.0683 | 2683.3427 | 2950.129 | 3243.9292 | 3567.4997 | 3923.8758 | 4316.3986 | 4748.7431 | 5224.948 | 5749.4469 | 6327.0993 |  | 770.1443 | 845.7444 | 928.7813 | 1020.0032 | 1120.2343 | 1230.3835 | 1351.452 | 1484.5436 | 1630.8751 | 1791.7879 | 1968.7606 | 2163.4236 | 2377.5745 | 2613.1955 | 2872.4724 | 3157.8157 | 3471.8837 | 3811.4763 | 4179.9581 | 4582.3753 | 5020.8741 | 5497.2745 | 6012.8064 | 6567.7208 | 7160.7208 | 7788.1341 | 8442.7154 | 9111.9161 | 9775.3932 | 10401.4261
| TRUE | 463 | 22005286 | BC | Blank | 11 | BUS NO.1 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.033587 | 2190 |  | 9.9 | 0.0088019 | 0.00083024 | 0.0079716 | 48.8669 | 265.6753 | 314.5422 | 29.6986 | 3.5299 | 384.6683 |  | 13.7946 | 0.021906 | 0.0020663 | 0.01984 | 121.622 | 661.2238 | 782.8458 | 73.915 | 8.7854 | 957.3786 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.11017 |  | 732.439 | 1822.9249 | 45.3489 | 1777.576 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.00090827 | 0.00099396 | 0.0010881 | 0.0011915 | 0.0013051 | 0.00143 | 0.0015672 | 0.0017181 | 0.0018839 | 0.0020663 | 0.0022669 | 0.0024876 | 0.0027303 | 0.0029974 | 0.0032913 | 0.0036147 | 0.0039707 | 0.0043626 | 0.0047941 | 0.0052691 | 0.0057922 | 0.0063682 | 0.0070027 | 0.0077015 | 0.0084713 | 0.0093195 | 0.010254 | 0.011284 | 0.012418 | 0.013669 | 801.2813 | 876.8814 | 959.9183 | 1051.1401 | 1151.3713 | 1261.5204 | 1382.5889 | 1515.6806 | 1662.0121 | 1822.9249 | 1999.8975 | 2194.5605 | 2408.7114 | 2644.3325 | 2903.6094 | 3188.9526 | 3503.0206 | 3848.7453 | 4229.3604 | 4648.4329 | 5109.8972 | 5618.0937 | 6177.8103 | 6794.3293 | 7473.4781 | 8221.6865 | 9046.0484 | 9954.3915 | 10955.3527 | 12058.4627 |  | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 37.2699 | 49.4034 | 66.0591 | 89.0252 | 120.822 | 165.0077 | 226.6137 | 312.7646 | 433.5624 | 603.347 | 842.4948 | 1179.9867 | 1657.0749 |  | 53.4599 | 58.5038 | 64.0439 | 70.13 | 76.8172 | 84.1662 | 92.2436 | 101.1232 | 110.8862 | 121.622 | 133.4292 | 146.4168 | 160.7045 | 176.4247 | 193.7231 | 212.7607 | 233.7147 | 256.7807 | 282.1746 | 310.1343 | 340.9223 | 374.8282 | 412.1714 | 453.3043 | 498.6158 | 548.5348 | 603.5346 | 664.1375 | 730.9196 | 804.517 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 39.248 | 44.2919 | 49.832 | 55.9181 | 62.6053 | 69.9543 | 78.0317 | 86.9113 | 96.6743 | 107.4101 | 119.2174 | 132.2049 | 146.4926 | 162.2128 | 179.5112 | 198.5488 | 219.5028 | 239.77 | 259.6259 | 279.9836 | 300.2894 | 319.6825 | 336.8584 | 349.8731 | 355.8636 | 350.6479 | 328.1545 | 279.6054 | 192.3492 | 48.1936 |  | 290.6463 | 318.0685 | 348.1882 | 381.2768 | 417.6333 | 457.5874 | 501.5022 | 549.7781 | 602.8565 | 661.2238 | 725.4166 | 796.0261 | 873.7044 | 959.1704 | 1053.2172 | 1156.7188 | 1270.6397 | 1396.0434 | 1534.1027 | 1686.1115 | 1853.4971 | 2037.8336 | 2240.8578 | 2464.4858 | 2710.8314 | 2982.2266 | 3281.2449 | 3610.7253 | 3973.8008 | 4373.9285 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 290.5702 | 317.9924 | 348.1121 | 381.2007 | 417.5572 | 457.5113 | 501.4261 | 549.702 | 602.7804 | 661.1477 | 725.3405 | 795.95 | 873.6283 | 959.0944 | 1053.1411 | 1156.6427 | 1270.5636 | 1395.9523 | 1533.982 | 1685.9501 | 1853.2795 | 2037.5383 | 2240.4546 | 2463.9321 | 2710.0671 | 2981.1672 | 3279.7705 | 3608.6666 | 3970.9174 | 4369.8793 |  | 329.8182 | 362.2843 | 397.9441 | 437.1188 | 480.1626 | 527.4656 | 579.4578 | 636.6133 | 699.4547 | 768.5578 | 844.5578 | 928.1549 | 1020.1209 | 1121.3071 | 1232.6523 | 1355.1915 | 1490.0664 | 1635.7223 | 1793.6078 | 1965.9337 | 2153.5689 | 2357.2209 | 2577.3131 | 2813.8052 | 3065.9306 | 3331.8151 | 3607.925 | 3888.2719 | 4163.2666 | 4418.0729 |  | 32.4899 | 35.5553 | 38.9223 | 42.6211 | 46.6852 | 51.1515 | 56.0605 | 61.457 | 67.3904 | 73.915 | 81.0908 | 88.9839 | 97.6672 | 107.221 | 117.734 | 129.304 | 142.0387 | 156.0569 | 171.4899 | 188.4822 | 207.1935 | 227.7996 | 250.4946 | 275.4929 | 303.0307 | 333.3687 | 366.7945 | 403.6255 | 444.212 | 488.9403 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 17.8188 | 20.8842 | 24.2511 | 27.9499 | 32.0141 | 36.4803 | 41.3894 | 46.7859 | 52.7193 | 59.2439 | 66.4197 | 74.3128 | 82.996 | 92.5499 | 103.0629 | 114.6329 | 127.3675 | 138.4965 | 148.2125 | 157.3572 | 165.2475 | 170.8719 | 172.748 | 168.7195 | 155.6655 | 129.0872 | 82.5157 | 6.6675 | -111.7619 | -291.8231 |  | 3.8617 | 4.2261 | 4.6262 | 5.0659 | 5.5489 | 6.0798 | 6.6633 | 7.3047 | 8.0099 | 8.7854 | 9.6383 | 10.5765 | 11.6086 | 12.7441 | 13.9937 | 15.3689 | 16.8825 | 18.5487 | 20.3831 | 22.4027 | 24.6267 | 27.0759 | 29.7734 | 32.7447 | 36.0178 | 39.6237 | 43.5967 | 47.9744 | 52.7984 | 58.1148 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 1.794 | 2.1584 | 2.5586 | 2.9982 | 3.4812 | 4.0121 | 4.5956 | 5.237 | 5.9422 | 6.7177 | 7.5706 | 8.5088 | 9.5409 | 10.6764 | 11.926 | 13.3012 | 14.8148 | 16.0738 | 17.1024 | 18.0161 | 18.715 | 19.0528 | 18.8161 | 17.6965 | 15.2487 | 10.8331 | 3.5315 | -7.9714 | -25.5584 | -51.923 |  | 420.8235 | 460.5278 | 504.1378 | 552.0464 | 604.6866 | 662.5356 | 726.1194 | 796.0175 | 872.8691 | 957.3786 | 1050.3226 | 1152.5573 | 1265.0268 | 1388.7722 | 1524.9413 | 1674.8003 | 1839.7451 | 2021.3156 | 2221.2101 | 2441.302 | 2683.6577 | 2950.5565 | 3244.513 | 3568.3015 | 3924.9824 | 4317.9326 | 4750.8778 | 5227.9288 | 5753.6218 | 6332.9622 |  | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.13186 | 0.17479 | 0.23372 | 0.31498 | 0.42748 | 0.58381 | 0.80178 | 1.1066 | 1.534 | 2.1347 | 2.9808 | 4.1749 | 5.8629 |  | 420.7133 | 460.4176 | 504.0276 | 551.9362 | 604.5764 | 662.4255 | 726.0092 | 795.9074 | 872.759 | 957.2684 | 1050.2124 | 1152.4471 | 1264.9166 | 1388.662 | 1524.8312 | 1674.6901 | 1839.6349 | 2021.1837 | 2221.0353 | 2441.0683 | 2683.3427 | 2950.129 | 3243.9292 | 3567.4997 | 3923.8758 | 4316.3986 | 4748.7431 | 5224.948 | 5749.4469 | 6327.0993 |  | 770.1443 | 845.7444 | 928.7813 | 1020.0032 | 1120.2343 | 1230.3835 | 1351.452 | 1484.5436 | 1630.8751 | 1791.7879 | 1968.7606 | 2163.4236 | 2377.5745 | 2613.1955 | 2872.4724 | 3157.8157 | 3471.8837 | 3811.4763 | 4179.9581 | 4582.3753 | 5020.8741 | 5497.2745 | 6012.8064 | 6567.7208 | 7160.7208 | 7788.1341 | 8442.7154 | 9111.9161 | 9775.3932 | 10401.4261
| TRUE | 464 | 22013837 | BC | Blank | 11 | BUS NO.1 | RESIDUAL BUS PROT | Blank | GEC | CDG14_548 | CDG14 548 | CDG14 | Electromechanical |  | 0.033587 | 2190 |  | 8.25 | 0.0054067 | 0.00050998 | 0.0048967 | 30.0172 | 163.1947 | 193.2118 | 18.2427 | 2.1683 | 236.2878 |  | 11.265 | 0.01251 | 0.00118 | 0.01133 | 69.4541 | 377.6018 | 447.0559 | 42.2103 | 5.0171 | 546.7255 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.11017 |  | 449.9107 | 1041.0087 | 45.3489 | 995.6598 |  | 0.031148 |  | 8.511 | 8.7803 | 9.0581 | 9.3447 | 9.6403 | 9.9453 | 10.26 | 10.5846 | 10.9195 | 11.265 | 11.6214 | 11.9891 | 12.3684 | 12.7597 | 13.1634 | 13.5799 | 14.0095 | 14.4528 | 14.91 | 15.3818 | 15.8684 | 16.3705 | 16.8884 | 17.4227 | 17.974 | 18.5426 | 19.1293 | 19.7345 | 20.3589 | 21.003 |  | 0.0058713 | 0.0063781 | 0.006931 | 0.0075342 | 0.0081926 | 0.0089113 | 0.0096958 | 0.010553 | 0.011488 | 0.01251 | 0.013626 | 0.014846 | 0.016179 | 0.017636 | 0.019228 | 0.020969 | 0.022872 | 0.024954 | 0.02723 | 0.02972 | 0.032443 | 0.035422 | 0.038682 | 0.042249 | 0.046153 | 0.050426 | 0.055102 | 0.060222 | 0.065826 | 0.071963 |  | 0.00055381 | 0.00060161 | 0.00065376 | 0.00071067 | 0.00077277 | 0.00084055 | 0.00091456 | 0.00099537 | 0.0010836 | 0.00118 | 0.0012853 | 0.0014004 | 0.0015261 | 0.0016635 | 0.0018137 | 0.0019779 | 0.0021574 | 0.0023538 | 0.0025685 | 0.0028033 | 0.0030602 | 0.0033412 | 0.0036487 | 0.0039852 | 0.0043534 | 0.0047564 | 0.0051975 | 0.0056804 | 0.0062091 | 0.0067879 | 488.5753 | 530.7476 | 576.7549 | 626.9554 | 681.7415 | 741.5428 | 806.8298 | 878.1179 | 955.9714 | 1041.0087 | 1133.907 | 1235.4085 | 1346.3261 | 1467.5505 | 1600.058 | 1744.918 | 1903.3028 | 2076.497 | 2265.9087 | 2473.0809 | 2699.7053 | 2947.6362 | 3218.9063 | 3515.7439 | 3840.5922 | 4196.1296 | 4585.2931 | 5011.3027 | 5477.6893 | 5988.325 |  | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 37.2699 | 49.4034 | 66.0591 | 89.0252 | 120.822 | 165.0077 | 226.6137 | 312.7646 | 433.5624 | 603.347 | 842.4948 | 1179.9867 | 1657.0749 |  | 32.5968 | 35.4104 | 38.48 | 41.8292 | 45.4845 | 49.4743 | 53.8301 | 58.5863 | 63.7805 | 69.4541 | 75.6521 | 82.424 | 89.8242 | 97.9121 | 106.7527 | 116.4175 | 126.9846 | 138.5398 | 151.177 | 164.9991 | 180.119 | 196.6605 | 214.7591 | 234.5635 | 256.2368 | 279.9575 | 305.9218 | 334.3443 | 365.4607 | 399.5293 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 18.3849 | 21.1985 | 24.2681 | 27.6173 | 31.2726 | 35.2624 | 39.6182 | 44.3744 | 49.5686 | 55.2422 | 61.4402 | 68.2121 | 75.6123 | 83.7002 | 92.5408 | 102.2056 | 112.7727 | 121.5291 | 128.6282 | 134.8484 | 139.4861 | 141.5148 | 139.4462 | 131.1324 | 113.4845 | 82.0707 | 30.5417 | -50.1878 | -173.1097 | -356.7941 |  | 177.2194 | 192.5164 | 209.2045 | 227.4136 | 247.286 | 268.9775 | 292.6589 | 318.517 | 346.7565 | 377.6018 | 411.2985 | 448.1159 | 488.3486 | 532.32 | 580.384 | 632.9287 | 690.3791 | 753.2013 | 821.906 | 897.0529 | 979.2557 | 1069.1869 | 1167.5838 | 1275.2548 | 1393.086 | 1522.049 | 1663.209 | 1817.7342 | 1986.9051 | 2172.1264 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 177.1433 | 192.4403 | 209.1284 | 227.3375 | 247.2099 | 268.9014 | 292.5828 | 318.4409 | 346.6804 | 377.5257 | 411.2225 | 448.0398 | 488.2726 | 532.2439 | 580.3079 | 632.8526 | 690.303 | 753.1102 | 821.7852 | 896.8915 | 979.0381 | 1068.8916 | 1167.1806 | 1274.701 | 1392.3217 | 1520.9895 | 1661.7347 | 1815.6754 | 1984.0217 | 2168.0772 |  | 195.5282 | 213.6389 | 233.3965 | 254.9548 | 278.4825 | 304.1638 | 332.201 | 362.8153 | 396.2491 | 432.7679 | 472.6626 | 516.2519 | 563.8849 | 615.9441 | 672.8488 | 735.0582 | 803.0757 | 874.6393 | 950.4135 | 1031.7399 | 1118.5242 | 1210.4065 | 1306.6268 | 1405.8334 | 1505.8063 | 1603.0602 | 1692.2764 | 1765.4876 | 1810.912 | 1811.2831 |  | 19.8105 | 21.5205 | 23.386 | 25.4215 | 27.6429 | 30.0677 | 32.7149 | 35.6055 | 38.7622 | 42.2103 | 45.9771 | 50.0927 | 54.5901 | 59.5055 | 64.8783 | 70.752 | 77.1741 | 84.1967 | 91.8769 | 100.2772 | 109.4663 | 119.5192 | 130.5185 | 142.5546 | 155.7263 | 170.1425 | 185.9221 | 203.1957 | 222.1065 | 242.8115 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 5.1394 | 6.8493 | 8.7148 | 10.7503 | 12.9718 | 15.3966 | 18.0438 | 20.9343 | 24.0911 | 27.5391 | 31.3059 | 35.4216 | 39.919 | 44.8343 | 50.2072 | 56.0809 | 62.503 | 66.6363 | 68.5995 | 69.1522 | 67.5203 | 62.5916 | 52.7719 | 35.7811 | 8.3612 | -34.1389 | -98.3567 | -193.7623 | -333.8674 | -537.9519 |  | 2.3546 | 2.5579 | 2.7796 | 3.0216 | 3.2856 | 3.5738 | 3.8884 | 4.232 | 4.6072 | 5.0171 | 5.4648 | 5.9539 | 6.4885 | 7.0727 | 7.7113 | 8.4095 | 9.1728 | 10.0075 | 10.9204 | 11.9188 | 13.011 | 14.2059 | 15.5133 | 16.9438 | 18.5094 | 20.2229 | 22.0984 | 24.1516 | 26.3993 | 28.8602 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0.28695 | 0.4902 | 0.71193 | 0.95387 | 1.2179 | 1.5061 | 1.8208 | 2.1643 | 2.5395 | 2.9494 | 3.3971 | 3.8863 | 4.4208 | 5.005 | 5.6437 | 6.3418 | 7.1051 | 7.5326 | 7.6397 | 7.5322 | 7.0993 | 6.1827 | 4.5559 | 1.8956 | -2.2597 | -8.5677 | -17.9667 | -31.7942 | -51.9576 | -81.1776 |  | 256.594 | 278.7424 | 302.9049 | 329.2696 | 358.0426 | 389.4495 | 423.7375 | 461.1771 | 502.0649 | 546.7255 | 595.5146 | 648.8219 | 707.0745 | 770.7402 | 840.3315 | 916.4103 | 999.5922 | 1090.5517 | 1190.0285 | 1298.8329 | 1417.8534 | 1548.0637 | 1690.5316 | 1846.4272 | 2017.0337 | 2203.7577 | 2408.1418 | 2631.877 | 2876.8177 | 3144.9975 |  | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.13186 | 0.17479 | 0.23372 | 0.31498 | 0.42748 | 0.58381 | 0.80178 | 1.1066 | 1.534 | 2.1347 | 2.9808 | 4.1749 | 5.8629 |  | 256.4838 | 278.6322 | 302.7947 | 329.1594 | 357.9324 | 389.3394 | 423.6273 | 461.067 | 501.9547 | 546.6153 | 595.4044 | 648.7118 | 706.9644 | 770.63 | 840.2214 | 916.3002 | 999.482 | 1090.4199 | 1189.8537 | 1298.5991 | 1417.5384 | 1547.6363 | 1689.9478 | 1845.6254 | 2015.9271 | 2202.2237 | 2406.0071 | 2628.8962 | 2872.6428 | 3139.1347 |  | 457.4383 | 499.6106 | 545.6179 | 595.8184 | 650.6046 | 710.4059 | 775.6929 | 846.9809 | 924.8344 | 1009.8717 | 1102.77 | 1204.2715 | 1315.1891 | 1436.4135 | 1568.921 | 1713.781 | 1872.1658 | 2039.228 | 2216.5064 | 2407.0233 | 2610.6822 | 2826.817 | 3053.9024 | 3289.1355 | 3527.8348 | 3762.5773 | 3981.96 | 4168.8273 | 4297.7299 | 4331.2883
| TRUE | 465 | 22005291 | BC | Blank | 11 | BUS NO.2 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.033587 | 2190 |  | 9.9 | 0.0088019 | 0.00083024 | 0.0079716 | 48.8669 | 265.6753 | 314.5422 | 29.6986 | 3.5299 | 384.6683 |  | 13.7946 | 0.021906 | 0.0020663 | 0.01984 | 121.622 | 661.2238 | 782.8458 | 73.915 | 8.7854 | 957.3786 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.11017 |  | 732.439 | 1822.9249 | 45.3489 | 1777.576 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.00090827 | 0.00099396 | 0.0010881 | 0.0011915 | 0.0013051 | 0.00143 | 0.0015672 | 0.0017181 | 0.0018839 | 0.0020663 | 0.0022669 | 0.0024876 | 0.0027303 | 0.0029974 | 0.0032913 | 0.0036147 | 0.0039707 | 0.0043626 | 0.0047941 | 0.0052691 | 0.0057922 | 0.0063682 | 0.0070027 | 0.0077015 | 0.0084713 | 0.0093195 | 0.010254 | 0.011284 | 0.012418 | 0.013669 | 801.2813 | 876.8814 | 959.9183 | 1051.1401 | 1151.3713 | 1261.5204 | 1382.5889 | 1515.6806 | 1662.0121 | 1822.9249 | 1999.8975 | 2194.5605 | 2408.7114 | 2644.3325 | 2903.6094 | 3188.9526 | 3503.0206 | 3848.7453 | 4229.3604 | 4648.4329 | 5109.8972 | 5618.0937 | 6177.8103 | 6794.3293 | 7473.4781 | 8221.6865 | 9046.0484 | 9954.3915 | 10955.3527 | 12058.4627 |  | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 37.2699 | 49.4034 | 66.0591 | 89.0252 | 120.822 | 165.0077 | 226.6137 | 312.7646 | 433.5624 | 603.347 | 842.4948 | 1179.9867 | 1657.0749 |  | 53.4599 | 58.5038 | 64.0439 | 70.13 | 76.8172 | 84.1662 | 92.2436 | 101.1232 | 110.8862 | 121.622 | 133.4292 | 146.4168 | 160.7045 | 176.4247 | 193.7231 | 212.7607 | 233.7147 | 256.7807 | 282.1746 | 310.1343 | 340.9223 | 374.8282 | 412.1714 | 453.3043 | 498.6158 | 548.5348 | 603.5346 | 664.1375 | 730.9196 | 804.517 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 39.248 | 44.2919 | 49.832 | 55.9181 | 62.6053 | 69.9543 | 78.0317 | 86.9113 | 96.6743 | 107.4101 | 119.2174 | 132.2049 | 146.4926 | 162.2128 | 179.5112 | 198.5488 | 219.5028 | 239.77 | 259.6259 | 279.9836 | 300.2894 | 319.6825 | 336.8584 | 349.8731 | 355.8636 | 350.6479 | 328.1545 | 279.6054 | 192.3492 | 48.1936 |  | 290.6463 | 318.0685 | 348.1882 | 381.2768 | 417.6333 | 457.5874 | 501.5022 | 549.7781 | 602.8565 | 661.2238 | 725.4166 | 796.0261 | 873.7044 | 959.1704 | 1053.2172 | 1156.7188 | 1270.6397 | 1396.0434 | 1534.1027 | 1686.1115 | 1853.4971 | 2037.8336 | 2240.8578 | 2464.4858 | 2710.8314 | 2982.2266 | 3281.2449 | 3610.7253 | 3973.8008 | 4373.9285 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 290.5702 | 317.9924 | 348.1121 | 381.2007 | 417.5572 | 457.5113 | 501.4261 | 549.702 | 602.7804 | 661.1477 | 725.3405 | 795.95 | 873.6283 | 959.0944 | 1053.1411 | 1156.6427 | 1270.5636 | 1395.9523 | 1533.982 | 1685.9501 | 1853.2795 | 2037.5383 | 2240.4546 | 2463.9321 | 2710.0671 | 2981.1672 | 3279.7705 | 3608.6666 | 3970.9174 | 4369.8793 |  | 329.8182 | 362.2843 | 397.9441 | 437.1188 | 480.1626 | 527.4656 | 579.4578 | 636.6133 | 699.4547 | 768.5578 | 844.5578 | 928.1549 | 1020.1209 | 1121.3071 | 1232.6523 | 1355.1915 | 1490.0664 | 1635.7223 | 1793.6078 | 1965.9337 | 2153.5689 | 2357.2209 | 2577.3131 | 2813.8052 | 3065.9306 | 3331.8151 | 3607.925 | 3888.2719 | 4163.2666 | 4418.0729 |  | 32.4899 | 35.5553 | 38.9223 | 42.6211 | 46.6852 | 51.1515 | 56.0605 | 61.457 | 67.3904 | 73.915 | 81.0908 | 88.9839 | 97.6672 | 107.221 | 117.734 | 129.304 | 142.0387 | 156.0569 | 171.4899 | 188.4822 | 207.1935 | 227.7996 | 250.4946 | 275.4929 | 303.0307 | 333.3687 | 366.7945 | 403.6255 | 444.212 | 488.9403 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 17.8188 | 20.8842 | 24.2511 | 27.9499 | 32.0141 | 36.4803 | 41.3894 | 46.7859 | 52.7193 | 59.2439 | 66.4197 | 74.3128 | 82.996 | 92.5499 | 103.0629 | 114.6329 | 127.3675 | 138.4965 | 148.2125 | 157.3572 | 165.2475 | 170.8719 | 172.748 | 168.7195 | 155.6655 | 129.0872 | 82.5157 | 6.6675 | -111.7619 | -291.8231 |  | 3.8617 | 4.2261 | 4.6262 | 5.0659 | 5.5489 | 6.0798 | 6.6633 | 7.3047 | 8.0099 | 8.7854 | 9.6383 | 10.5765 | 11.6086 | 12.7441 | 13.9937 | 15.3689 | 16.8825 | 18.5487 | 20.3831 | 22.4027 | 24.6267 | 27.0759 | 29.7734 | 32.7447 | 36.0178 | 39.6237 | 43.5967 | 47.9744 | 52.7984 | 58.1148 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 1.794 | 2.1584 | 2.5586 | 2.9982 | 3.4812 | 4.0121 | 4.5956 | 5.237 | 5.9422 | 6.7177 | 7.5706 | 8.5088 | 9.5409 | 10.6764 | 11.926 | 13.3012 | 14.8148 | 16.0738 | 17.1024 | 18.0161 | 18.715 | 19.0528 | 18.8161 | 17.6965 | 15.2487 | 10.8331 | 3.5315 | -7.9714 | -25.5584 | -51.923 |  | 420.8235 | 460.5278 | 504.1378 | 552.0464 | 604.6866 | 662.5356 | 726.1194 | 796.0175 | 872.8691 | 957.3786 | 1050.3226 | 1152.5573 | 1265.0268 | 1388.7722 | 1524.9413 | 1674.8003 | 1839.7451 | 2021.3156 | 2221.2101 | 2441.302 | 2683.6577 | 2950.5565 | 3244.513 | 3568.3015 | 3924.9824 | 4317.9326 | 4750.8778 | 5227.9288 | 5753.6218 | 6332.9622 |  | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.13186 | 0.17479 | 0.23372 | 0.31498 | 0.42748 | 0.58381 | 0.80178 | 1.1066 | 1.534 | 2.1347 | 2.9808 | 4.1749 | 5.8629 |  | 420.7133 | 460.4176 | 504.0276 | 551.9362 | 604.5764 | 662.4255 | 726.0092 | 795.9074 | 872.759 | 957.2684 | 1050.2124 | 1152.4471 | 1264.9166 | 1388.662 | 1524.8312 | 1674.6901 | 1839.6349 | 2021.1837 | 2221.0353 | 2441.0683 | 2683.3427 | 2950.129 | 3243.9292 | 3567.4997 | 3923.8758 | 4316.3986 | 4748.7431 | 5224.948 | 5749.4469 | 6327.0993 |  | 770.1443 | 845.7444 | 928.7813 | 1020.0032 | 1120.2343 | 1230.3835 | 1351.452 | 1484.5436 | 1630.8751 | 1791.7879 | 1968.7606 | 2163.4236 | 2377.5745 | 2613.1955 | 2872.4724 | 3157.8157 | 3471.8837 | 3811.4763 | 4179.9581 | 4582.3753 | 5020.8741 | 5497.2745 | 6012.8064 | 6567.7208 | 7160.7208 | 7788.1341 | 8442.7154 | 9111.9161 | 9775.3932 | 10401.4261
| TRUE | 466 | 22005290 | BC | Blank | 11 | BUS NO.2 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.033587 | 2190 |  | 9.9 | 0.0088019 | 0.00083024 | 0.0079716 | 48.8669 | 265.6753 | 314.5422 | 29.6986 | 3.5299 | 384.6683 |  | 13.7946 | 0.021906 | 0.0020663 | 0.01984 | 121.622 | 661.2238 | 782.8458 | 73.915 | 8.7854 | 957.3786 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.11017 |  | 732.439 | 1822.9249 | 45.3489 | 1777.576 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.00090827 | 0.00099396 | 0.0010881 | 0.0011915 | 0.0013051 | 0.00143 | 0.0015672 | 0.0017181 | 0.0018839 | 0.0020663 | 0.0022669 | 0.0024876 | 0.0027303 | 0.0029974 | 0.0032913 | 0.0036147 | 0.0039707 | 0.0043626 | 0.0047941 | 0.0052691 | 0.0057922 | 0.0063682 | 0.0070027 | 0.0077015 | 0.0084713 | 0.0093195 | 0.010254 | 0.011284 | 0.012418 | 0.013669 | 801.2813 | 876.8814 | 959.9183 | 1051.1401 | 1151.3713 | 1261.5204 | 1382.5889 | 1515.6806 | 1662.0121 | 1822.9249 | 1999.8975 | 2194.5605 | 2408.7114 | 2644.3325 | 2903.6094 | 3188.9526 | 3503.0206 | 3848.7453 | 4229.3604 | 4648.4329 | 5109.8972 | 5618.0937 | 6177.8103 | 6794.3293 | 7473.4781 | 8221.6865 | 9046.0484 | 9954.3915 | 10955.3527 | 12058.4627 |  | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 37.2699 | 49.4034 | 66.0591 | 89.0252 | 120.822 | 165.0077 | 226.6137 | 312.7646 | 433.5624 | 603.347 | 842.4948 | 1179.9867 | 1657.0749 |  | 53.4599 | 58.5038 | 64.0439 | 70.13 | 76.8172 | 84.1662 | 92.2436 | 101.1232 | 110.8862 | 121.622 | 133.4292 | 146.4168 | 160.7045 | 176.4247 | 193.7231 | 212.7607 | 233.7147 | 256.7807 | 282.1746 | 310.1343 | 340.9223 | 374.8282 | 412.1714 | 453.3043 | 498.6158 | 548.5348 | 603.5346 | 664.1375 | 730.9196 | 804.517 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 39.248 | 44.2919 | 49.832 | 55.9181 | 62.6053 | 69.9543 | 78.0317 | 86.9113 | 96.6743 | 107.4101 | 119.2174 | 132.2049 | 146.4926 | 162.2128 | 179.5112 | 198.5488 | 219.5028 | 239.77 | 259.6259 | 279.9836 | 300.2894 | 319.6825 | 336.8584 | 349.8731 | 355.8636 | 350.6479 | 328.1545 | 279.6054 | 192.3492 | 48.1936 |  | 290.6463 | 318.0685 | 348.1882 | 381.2768 | 417.6333 | 457.5874 | 501.5022 | 549.7781 | 602.8565 | 661.2238 | 725.4166 | 796.0261 | 873.7044 | 959.1704 | 1053.2172 | 1156.7188 | 1270.6397 | 1396.0434 | 1534.1027 | 1686.1115 | 1853.4971 | 2037.8336 | 2240.8578 | 2464.4858 | 2710.8314 | 2982.2266 | 3281.2449 | 3610.7253 | 3973.8008 | 4373.9285 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 290.5702 | 317.9924 | 348.1121 | 381.2007 | 417.5572 | 457.5113 | 501.4261 | 549.702 | 602.7804 | 661.1477 | 725.3405 | 795.95 | 873.6283 | 959.0944 | 1053.1411 | 1156.6427 | 1270.5636 | 1395.9523 | 1533.982 | 1685.9501 | 1853.2795 | 2037.5383 | 2240.4546 | 2463.9321 | 2710.0671 | 2981.1672 | 3279.7705 | 3608.6666 | 3970.9174 | 4369.8793 |  | 329.8182 | 362.2843 | 397.9441 | 437.1188 | 480.1626 | 527.4656 | 579.4578 | 636.6133 | 699.4547 | 768.5578 | 844.5578 | 928.1549 | 1020.1209 | 1121.3071 | 1232.6523 | 1355.1915 | 1490.0664 | 1635.7223 | 1793.6078 | 1965.9337 | 2153.5689 | 2357.2209 | 2577.3131 | 2813.8052 | 3065.9306 | 3331.8151 | 3607.925 | 3888.2719 | 4163.2666 | 4418.0729 |  | 32.4899 | 35.5553 | 38.9223 | 42.6211 | 46.6852 | 51.1515 | 56.0605 | 61.457 | 67.3904 | 73.915 | 81.0908 | 88.9839 | 97.6672 | 107.221 | 117.734 | 129.304 | 142.0387 | 156.0569 | 171.4899 | 188.4822 | 207.1935 | 227.7996 | 250.4946 | 275.4929 | 303.0307 | 333.3687 | 366.7945 | 403.6255 | 444.212 | 488.9403 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 17.8188 | 20.8842 | 24.2511 | 27.9499 | 32.0141 | 36.4803 | 41.3894 | 46.7859 | 52.7193 | 59.2439 | 66.4197 | 74.3128 | 82.996 | 92.5499 | 103.0629 | 114.6329 | 127.3675 | 138.4965 | 148.2125 | 157.3572 | 165.2475 | 170.8719 | 172.748 | 168.7195 | 155.6655 | 129.0872 | 82.5157 | 6.6675 | -111.7619 | -291.8231 |  | 3.8617 | 4.2261 | 4.6262 | 5.0659 | 5.5489 | 6.0798 | 6.6633 | 7.3047 | 8.0099 | 8.7854 | 9.6383 | 10.5765 | 11.6086 | 12.7441 | 13.9937 | 15.3689 | 16.8825 | 18.5487 | 20.3831 | 22.4027 | 24.6267 | 27.0759 | 29.7734 | 32.7447 | 36.0178 | 39.6237 | 43.5967 | 47.9744 | 52.7984 | 58.1148 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 1.794 | 2.1584 | 2.5586 | 2.9982 | 3.4812 | 4.0121 | 4.5956 | 5.237 | 5.9422 | 6.7177 | 7.5706 | 8.5088 | 9.5409 | 10.6764 | 11.926 | 13.3012 | 14.8148 | 16.0738 | 17.1024 | 18.0161 | 18.715 | 19.0528 | 18.8161 | 17.6965 | 15.2487 | 10.8331 | 3.5315 | -7.9714 | -25.5584 | -51.923 |  | 420.8235 | 460.5278 | 504.1378 | 552.0464 | 604.6866 | 662.5356 | 726.1194 | 796.0175 | 872.8691 | 957.3786 | 1050.3226 | 1152.5573 | 1265.0268 | 1388.7722 | 1524.9413 | 1674.8003 | 1839.7451 | 2021.3156 | 2221.2101 | 2441.302 | 2683.6577 | 2950.5565 | 3244.513 | 3568.3015 | 3924.9824 | 4317.9326 | 4750.8778 | 5227.9288 | 5753.6218 | 6332.9622 |  | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.13186 | 0.17479 | 0.23372 | 0.31498 | 0.42748 | 0.58381 | 0.80178 | 1.1066 | 1.534 | 2.1347 | 2.9808 | 4.1749 | 5.8629 |  | 420.7133 | 460.4176 | 504.0276 | 551.9362 | 604.5764 | 662.4255 | 726.0092 | 795.9074 | 872.759 | 957.2684 | 1050.2124 | 1152.4471 | 1264.9166 | 1388.662 | 1524.8312 | 1674.6901 | 1839.6349 | 2021.1837 | 2221.0353 | 2441.0683 | 2683.3427 | 2950.129 | 3243.9292 | 3567.4997 | 3923.8758 | 4316.3986 | 4748.7431 | 5224.948 | 5749.4469 | 6327.0993 |  | 770.1443 | 845.7444 | 928.7813 | 1020.0032 | 1120.2343 | 1230.3835 | 1351.452 | 1484.5436 | 1630.8751 | 1791.7879 | 1968.7606 | 2163.4236 | 2377.5745 | 2613.1955 | 2872.4724 | 3157.8157 | 3471.8837 | 3811.4763 | 4179.9581 | 4582.3753 | 5020.8741 | 5497.2745 | 6012.8064 | 6567.7208 | 7160.7208 | 7788.1341 | 8442.7154 | 9111.9161 | 9775.3932 | 10401.4261
| TRUE | 467 | 22005289 | BC | Blank | 11 | BUS NO.2 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.033587 | 2190 |  | 9.9 | 0.0088019 | 0.00083024 | 0.0079716 | 48.8669 | 265.6753 | 314.5422 | 29.6986 | 3.5299 | 384.6683 |  | 13.7946 | 0.021906 | 0.0020663 | 0.01984 | 121.622 | 661.2238 | 782.8458 | 73.915 | 8.7854 | 957.3786 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.11017 |  | 732.439 | 1822.9249 | 45.3489 | 1777.576 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.00090827 | 0.00099396 | 0.0010881 | 0.0011915 | 0.0013051 | 0.00143 | 0.0015672 | 0.0017181 | 0.0018839 | 0.0020663 | 0.0022669 | 0.0024876 | 0.0027303 | 0.0029974 | 0.0032913 | 0.0036147 | 0.0039707 | 0.0043626 | 0.0047941 | 0.0052691 | 0.0057922 | 0.0063682 | 0.0070027 | 0.0077015 | 0.0084713 | 0.0093195 | 0.010254 | 0.011284 | 0.012418 | 0.013669 | 801.2813 | 876.8814 | 959.9183 | 1051.1401 | 1151.3713 | 1261.5204 | 1382.5889 | 1515.6806 | 1662.0121 | 1822.9249 | 1999.8975 | 2194.5605 | 2408.7114 | 2644.3325 | 2903.6094 | 3188.9526 | 3503.0206 | 3848.7453 | 4229.3604 | 4648.4329 | 5109.8972 | 5618.0937 | 6177.8103 | 6794.3293 | 7473.4781 | 8221.6865 | 9046.0484 | 9954.3915 | 10955.3527 | 12058.4627 |  | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 37.2699 | 49.4034 | 66.0591 | 89.0252 | 120.822 | 165.0077 | 226.6137 | 312.7646 | 433.5624 | 603.347 | 842.4948 | 1179.9867 | 1657.0749 |  | 53.4599 | 58.5038 | 64.0439 | 70.13 | 76.8172 | 84.1662 | 92.2436 | 101.1232 | 110.8862 | 121.622 | 133.4292 | 146.4168 | 160.7045 | 176.4247 | 193.7231 | 212.7607 | 233.7147 | 256.7807 | 282.1746 | 310.1343 | 340.9223 | 374.8282 | 412.1714 | 453.3043 | 498.6158 | 548.5348 | 603.5346 | 664.1375 | 730.9196 | 804.517 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 39.248 | 44.2919 | 49.832 | 55.9181 | 62.6053 | 69.9543 | 78.0317 | 86.9113 | 96.6743 | 107.4101 | 119.2174 | 132.2049 | 146.4926 | 162.2128 | 179.5112 | 198.5488 | 219.5028 | 239.77 | 259.6259 | 279.9836 | 300.2894 | 319.6825 | 336.8584 | 349.8731 | 355.8636 | 350.6479 | 328.1545 | 279.6054 | 192.3492 | 48.1936 |  | 290.6463 | 318.0685 | 348.1882 | 381.2768 | 417.6333 | 457.5874 | 501.5022 | 549.7781 | 602.8565 | 661.2238 | 725.4166 | 796.0261 | 873.7044 | 959.1704 | 1053.2172 | 1156.7188 | 1270.6397 | 1396.0434 | 1534.1027 | 1686.1115 | 1853.4971 | 2037.8336 | 2240.8578 | 2464.4858 | 2710.8314 | 2982.2266 | 3281.2449 | 3610.7253 | 3973.8008 | 4373.9285 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 290.5702 | 317.9924 | 348.1121 | 381.2007 | 417.5572 | 457.5113 | 501.4261 | 549.702 | 602.7804 | 661.1477 | 725.3405 | 795.95 | 873.6283 | 959.0944 | 1053.1411 | 1156.6427 | 1270.5636 | 1395.9523 | 1533.982 | 1685.9501 | 1853.2795 | 2037.5383 | 2240.4546 | 2463.9321 | 2710.0671 | 2981.1672 | 3279.7705 | 3608.6666 | 3970.9174 | 4369.8793 |  | 329.8182 | 362.2843 | 397.9441 | 437.1188 | 480.1626 | 527.4656 | 579.4578 | 636.6133 | 699.4547 | 768.5578 | 844.5578 | 928.1549 | 1020.1209 | 1121.3071 | 1232.6523 | 1355.1915 | 1490.0664 | 1635.7223 | 1793.6078 | 1965.9337 | 2153.5689 | 2357.2209 | 2577.3131 | 2813.8052 | 3065.9306 | 3331.8151 | 3607.925 | 3888.2719 | 4163.2666 | 4418.0729 |  | 32.4899 | 35.5553 | 38.9223 | 42.6211 | 46.6852 | 51.1515 | 56.0605 | 61.457 | 67.3904 | 73.915 | 81.0908 | 88.9839 | 97.6672 | 107.221 | 117.734 | 129.304 | 142.0387 | 156.0569 | 171.4899 | 188.4822 | 207.1935 | 227.7996 | 250.4946 | 275.4929 | 303.0307 | 333.3687 | 366.7945 | 403.6255 | 444.212 | 488.9403 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 17.8188 | 20.8842 | 24.2511 | 27.9499 | 32.0141 | 36.4803 | 41.3894 | 46.7859 | 52.7193 | 59.2439 | 66.4197 | 74.3128 | 82.996 | 92.5499 | 103.0629 | 114.6329 | 127.3675 | 138.4965 | 148.2125 | 157.3572 | 165.2475 | 170.8719 | 172.748 | 168.7195 | 155.6655 | 129.0872 | 82.5157 | 6.6675 | -111.7619 | -291.8231 |  | 3.8617 | 4.2261 | 4.6262 | 5.0659 | 5.5489 | 6.0798 | 6.6633 | 7.3047 | 8.0099 | 8.7854 | 9.6383 | 10.5765 | 11.6086 | 12.7441 | 13.9937 | 15.3689 | 16.8825 | 18.5487 | 20.3831 | 22.4027 | 24.6267 | 27.0759 | 29.7734 | 32.7447 | 36.0178 | 39.6237 | 43.5967 | 47.9744 | 52.7984 | 58.1148 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 1.794 | 2.1584 | 2.5586 | 2.9982 | 3.4812 | 4.0121 | 4.5956 | 5.237 | 5.9422 | 6.7177 | 7.5706 | 8.5088 | 9.5409 | 10.6764 | 11.926 | 13.3012 | 14.8148 | 16.0738 | 17.1024 | 18.0161 | 18.715 | 19.0528 | 18.8161 | 17.6965 | 15.2487 | 10.8331 | 3.5315 | -7.9714 | -25.5584 | -51.923 |  | 420.8235 | 460.5278 | 504.1378 | 552.0464 | 604.6866 | 662.5356 | 726.1194 | 796.0175 | 872.8691 | 957.3786 | 1050.3226 | 1152.5573 | 1265.0268 | 1388.7722 | 1524.9413 | 1674.8003 | 1839.7451 | 2021.3156 | 2221.2101 | 2441.302 | 2683.6577 | 2950.5565 | 3244.513 | 3568.3015 | 3924.9824 | 4317.9326 | 4750.8778 | 5227.9288 | 5753.6218 | 6332.9622 |  | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.13186 | 0.17479 | 0.23372 | 0.31498 | 0.42748 | 0.58381 | 0.80178 | 1.1066 | 1.534 | 2.1347 | 2.9808 | 4.1749 | 5.8629 |  | 420.7133 | 460.4176 | 504.0276 | 551.9362 | 604.5764 | 662.4255 | 726.0092 | 795.9074 | 872.759 | 957.2684 | 1050.2124 | 1152.4471 | 1264.9166 | 1388.662 | 1524.8312 | 1674.6901 | 1839.6349 | 2021.1837 | 2221.0353 | 2441.0683 | 2683.3427 | 2950.129 | 3243.9292 | 3567.4997 | 3923.8758 | 4316.3986 | 4748.7431 | 5224.948 | 5749.4469 | 6327.0993 |  | 770.1443 | 845.7444 | 928.7813 | 1020.0032 | 1120.2343 | 1230.3835 | 1351.452 | 1484.5436 | 1630.8751 | 1791.7879 | 1968.7606 | 2163.4236 | 2377.5745 | 2613.1955 | 2872.4724 | 3157.8157 | 3471.8837 | 3811.4763 | 4179.9581 | 4582.3753 | 5020.8741 | 5497.2745 | 6012.8064 | 6567.7208 | 7160.7208 | 7788.1341 | 8442.7154 | 9111.9161 | 9775.3932 | 10401.4261
| TRUE | 468 | 22013838 | BC | Blank | 11 | BUS NO.2 | RESIDUAL BUS PROT | Blank | GEC | CDG14_548 | CDG14 548 | CDG14 | Electromechanical |  | 0.033587 | 2190 |  | 8.25 | 0.0054067 | 0.00050998 | 0.0048967 | 30.0172 | 163.1947 | 193.2118 | 18.2427 | 2.1683 | 236.2878 |  | 11.265 | 0.01251 | 0.00118 | 0.01133 | 69.4541 | 377.6018 | 447.0559 | 42.2103 | 5.0171 | 546.7255 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.11017 |  | 449.9107 | 1041.0087 | 45.3489 | 995.6598 |  | 0.031148 |  | 8.511 | 8.7803 | 9.0581 | 9.3447 | 9.6403 | 9.9453 | 10.26 | 10.5846 | 10.9195 | 11.265 | 11.6214 | 11.9891 | 12.3684 | 12.7597 | 13.1634 | 13.5799 | 14.0095 | 14.4528 | 14.91 | 15.3818 | 15.8684 | 16.3705 | 16.8884 | 17.4227 | 17.974 | 18.5426 | 19.1293 | 19.7345 | 20.3589 | 21.003 |  | 0.0058713 | 0.0063781 | 0.006931 | 0.0075342 | 0.0081926 | 0.0089113 | 0.0096958 | 0.010553 | 0.011488 | 0.01251 | 0.013626 | 0.014846 | 0.016179 | 0.017636 | 0.019228 | 0.020969 | 0.022872 | 0.024954 | 0.02723 | 0.02972 | 0.032443 | 0.035422 | 0.038682 | 0.042249 | 0.046153 | 0.050426 | 0.055102 | 0.060222 | 0.065826 | 0.071963 |  | 0.00055381 | 0.00060161 | 0.00065376 | 0.00071067 | 0.00077277 | 0.00084055 | 0.00091456 | 0.00099537 | 0.0010836 | 0.00118 | 0.0012853 | 0.0014004 | 0.0015261 | 0.0016635 | 0.0018137 | 0.0019779 | 0.0021574 | 0.0023538 | 0.0025685 | 0.0028033 | 0.0030602 | 0.0033412 | 0.0036487 | 0.0039852 | 0.0043534 | 0.0047564 | 0.0051975 | 0.0056804 | 0.0062091 | 0.0067879 | 488.5753 | 530.7476 | 576.7549 | 626.9554 | 681.7415 | 741.5428 | 806.8298 | 878.1179 | 955.9714 | 1041.0087 | 1133.907 | 1235.4085 | 1346.3261 | 1467.5505 | 1600.058 | 1744.918 | 1903.3028 | 2076.497 | 2265.9087 | 2473.0809 | 2699.7053 | 2947.6362 | 3218.9063 | 3515.7439 | 3840.5922 | 4196.1296 | 4585.2931 | 5011.3027 | 5477.6893 | 5988.325 |  | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 37.2699 | 49.4034 | 66.0591 | 89.0252 | 120.822 | 165.0077 | 226.6137 | 312.7646 | 433.5624 | 603.347 | 842.4948 | 1179.9867 | 1657.0749 |  | 32.5968 | 35.4104 | 38.48 | 41.8292 | 45.4845 | 49.4743 | 53.8301 | 58.5863 | 63.7805 | 69.4541 | 75.6521 | 82.424 | 89.8242 | 97.9121 | 106.7527 | 116.4175 | 126.9846 | 138.5398 | 151.177 | 164.9991 | 180.119 | 196.6605 | 214.7591 | 234.5635 | 256.2368 | 279.9575 | 305.9218 | 334.3443 | 365.4607 | 399.5293 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 18.3849 | 21.1985 | 24.2681 | 27.6173 | 31.2726 | 35.2624 | 39.6182 | 44.3744 | 49.5686 | 55.2422 | 61.4402 | 68.2121 | 75.6123 | 83.7002 | 92.5408 | 102.2056 | 112.7727 | 121.5291 | 128.6282 | 134.8484 | 139.4861 | 141.5148 | 139.4462 | 131.1324 | 113.4845 | 82.0707 | 30.5417 | -50.1878 | -173.1097 | -356.7941 |  | 177.2194 | 192.5164 | 209.2045 | 227.4136 | 247.286 | 268.9775 | 292.6589 | 318.517 | 346.7565 | 377.6018 | 411.2985 | 448.1159 | 488.3486 | 532.32 | 580.384 | 632.9287 | 690.3791 | 753.2013 | 821.906 | 897.0529 | 979.2557 | 1069.1869 | 1167.5838 | 1275.2548 | 1393.086 | 1522.049 | 1663.209 | 1817.7342 | 1986.9051 | 2172.1264 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 177.1433 | 192.4403 | 209.1284 | 227.3375 | 247.2099 | 268.9014 | 292.5828 | 318.4409 | 346.6804 | 377.5257 | 411.2225 | 448.0398 | 488.2726 | 532.2439 | 580.3079 | 632.8526 | 690.303 | 753.1102 | 821.7852 | 896.8915 | 979.0381 | 1068.8916 | 1167.1806 | 1274.701 | 1392.3217 | 1520.9895 | 1661.7347 | 1815.6754 | 1984.0217 | 2168.0772 |  | 195.5282 | 213.6389 | 233.3965 | 254.9548 | 278.4825 | 304.1638 | 332.201 | 362.8153 | 396.2491 | 432.7679 | 472.6626 | 516.2519 | 563.8849 | 615.9441 | 672.8488 | 735.0582 | 803.0757 | 874.6393 | 950.4135 | 1031.7399 | 1118.5242 | 1210.4065 | 1306.6268 | 1405.8334 | 1505.8063 | 1603.0602 | 1692.2764 | 1765.4876 | 1810.912 | 1811.2831 |  | 19.8105 | 21.5205 | 23.386 | 25.4215 | 27.6429 | 30.0677 | 32.7149 | 35.6055 | 38.7622 | 42.2103 | 45.9771 | 50.0927 | 54.5901 | 59.5055 | 64.8783 | 70.752 | 77.1741 | 84.1967 | 91.8769 | 100.2772 | 109.4663 | 119.5192 | 130.5185 | 142.5546 | 155.7263 | 170.1425 | 185.9221 | 203.1957 | 222.1065 | 242.8115 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 5.1394 | 6.8493 | 8.7148 | 10.7503 | 12.9718 | 15.3966 | 18.0438 | 20.9343 | 24.0911 | 27.5391 | 31.3059 | 35.4216 | 39.919 | 44.8343 | 50.2072 | 56.0809 | 62.503 | 66.6363 | 68.5995 | 69.1522 | 67.5203 | 62.5916 | 52.7719 | 35.7811 | 8.3612 | -34.1389 | -98.3567 | -193.7623 | -333.8674 | -537.9519 |  | 2.3546 | 2.5579 | 2.7796 | 3.0216 | 3.2856 | 3.5738 | 3.8884 | 4.232 | 4.6072 | 5.0171 | 5.4648 | 5.9539 | 6.4885 | 7.0727 | 7.7113 | 8.4095 | 9.1728 | 10.0075 | 10.9204 | 11.9188 | 13.011 | 14.2059 | 15.5133 | 16.9438 | 18.5094 | 20.2229 | 22.0984 | 24.1516 | 26.3993 | 28.8602 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0.28695 | 0.4902 | 0.71193 | 0.95387 | 1.2179 | 1.5061 | 1.8208 | 2.1643 | 2.5395 | 2.9494 | 3.3971 | 3.8863 | 4.4208 | 5.005 | 5.6437 | 6.3418 | 7.1051 | 7.5326 | 7.6397 | 7.5322 | 7.0993 | 6.1827 | 4.5559 | 1.8956 | -2.2597 | -8.5677 | -17.9667 | -31.7942 | -51.9576 | -81.1776 |  | 256.594 | 278.7424 | 302.9049 | 329.2696 | 358.0426 | 389.4495 | 423.7375 | 461.1771 | 502.0649 | 546.7255 | 595.5146 | 648.8219 | 707.0745 | 770.7402 | 840.3315 | 916.4103 | 999.5922 | 1090.5517 | 1190.0285 | 1298.8329 | 1417.8534 | 1548.0637 | 1690.5316 | 1846.4272 | 2017.0337 | 2203.7577 | 2408.1418 | 2631.877 | 2876.8177 | 3144.9975 |  | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.13186 | 0.17479 | 0.23372 | 0.31498 | 0.42748 | 0.58381 | 0.80178 | 1.1066 | 1.534 | 2.1347 | 2.9808 | 4.1749 | 5.8629 |  | 256.4838 | 278.6322 | 302.7947 | 329.1594 | 357.9324 | 389.3394 | 423.6273 | 461.067 | 501.9547 | 546.6153 | 595.4044 | 648.7118 | 706.9644 | 770.63 | 840.2214 | 916.3002 | 999.482 | 1090.4199 | 1189.8537 | 1298.5991 | 1417.5384 | 1547.6363 | 1689.9478 | 1845.6254 | 2015.9271 | 2202.2237 | 2406.0071 | 2628.8962 | 2872.6428 | 3139.1347 |  | 457.4383 | 499.6106 | 545.6179 | 595.8184 | 650.6046 | 710.4059 | 775.6929 | 846.9809 | 924.8344 | 1009.8717 | 1102.77 | 1204.2715 | 1315.1891 | 1436.4135 | 1568.921 | 1713.781 | 1872.1658 | 2039.228 | 2216.5064 | 2407.0233 | 2610.6822 | 2826.817 | 3053.9024 | 3289.1355 | 3527.8348 | 3762.5773 | 3981.96 | 4168.8273 | 4297.7299 | 4331.2883
| TRUE | 469 | 22005285 | BC | Blank | 11 | BUS NO.3 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.033587 | 2190 |  | 9.9 | 0.0088019 | 0.00083024 | 0.0079716 | 48.8669 | 265.6753 | 314.5422 | 29.6986 | 3.5299 | 384.6683 |  | 13.7946 | 0.021906 | 0.0020663 | 0.01984 | 121.622 | 661.2238 | 782.8458 | 73.915 | 8.7854 | 957.3786 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.11017 |  | 732.439 | 1822.9249 | 45.3489 | 1777.576 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.00090827 | 0.00099396 | 0.0010881 | 0.0011915 | 0.0013051 | 0.00143 | 0.0015672 | 0.0017181 | 0.0018839 | 0.0020663 | 0.0022669 | 0.0024876 | 0.0027303 | 0.0029974 | 0.0032913 | 0.0036147 | 0.0039707 | 0.0043626 | 0.0047941 | 0.0052691 | 0.0057922 | 0.0063682 | 0.0070027 | 0.0077015 | 0.0084713 | 0.0093195 | 0.010254 | 0.011284 | 0.012418 | 0.013669 | 801.2813 | 876.8814 | 959.9183 | 1051.1401 | 1151.3713 | 1261.5204 | 1382.5889 | 1515.6806 | 1662.0121 | 1822.9249 | 1999.8975 | 2194.5605 | 2408.7114 | 2644.3325 | 2903.6094 | 3188.9526 | 3503.0206 | 3848.7453 | 4229.3604 | 4648.4329 | 5109.8972 | 5618.0937 | 6177.8103 | 6794.3293 | 7473.4781 | 8221.6865 | 9046.0484 | 9954.3915 | 10955.3527 | 12058.4627 |  | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 37.2699 | 49.4034 | 66.0591 | 89.0252 | 120.822 | 165.0077 | 226.6137 | 312.7646 | 433.5624 | 603.347 | 842.4948 | 1179.9867 | 1657.0749 |  | 53.4599 | 58.5038 | 64.0439 | 70.13 | 76.8172 | 84.1662 | 92.2436 | 101.1232 | 110.8862 | 121.622 | 133.4292 | 146.4168 | 160.7045 | 176.4247 | 193.7231 | 212.7607 | 233.7147 | 256.7807 | 282.1746 | 310.1343 | 340.9223 | 374.8282 | 412.1714 | 453.3043 | 498.6158 | 548.5348 | 603.5346 | 664.1375 | 730.9196 | 804.517 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 39.248 | 44.2919 | 49.832 | 55.9181 | 62.6053 | 69.9543 | 78.0317 | 86.9113 | 96.6743 | 107.4101 | 119.2174 | 132.2049 | 146.4926 | 162.2128 | 179.5112 | 198.5488 | 219.5028 | 239.77 | 259.6259 | 279.9836 | 300.2894 | 319.6825 | 336.8584 | 349.8731 | 355.8636 | 350.6479 | 328.1545 | 279.6054 | 192.3492 | 48.1936 |  | 290.6463 | 318.0685 | 348.1882 | 381.2768 | 417.6333 | 457.5874 | 501.5022 | 549.7781 | 602.8565 | 661.2238 | 725.4166 | 796.0261 | 873.7044 | 959.1704 | 1053.2172 | 1156.7188 | 1270.6397 | 1396.0434 | 1534.1027 | 1686.1115 | 1853.4971 | 2037.8336 | 2240.8578 | 2464.4858 | 2710.8314 | 2982.2266 | 3281.2449 | 3610.7253 | 3973.8008 | 4373.9285 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 290.5702 | 317.9924 | 348.1121 | 381.2007 | 417.5572 | 457.5113 | 501.4261 | 549.702 | 602.7804 | 661.1477 | 725.3405 | 795.95 | 873.6283 | 959.0944 | 1053.1411 | 1156.6427 | 1270.5636 | 1395.9523 | 1533.982 | 1685.9501 | 1853.2795 | 2037.5383 | 2240.4546 | 2463.9321 | 2710.0671 | 2981.1672 | 3279.7705 | 3608.6666 | 3970.9174 | 4369.8793 |  | 329.8182 | 362.2843 | 397.9441 | 437.1188 | 480.1626 | 527.4656 | 579.4578 | 636.6133 | 699.4547 | 768.5578 | 844.5578 | 928.1549 | 1020.1209 | 1121.3071 | 1232.6523 | 1355.1915 | 1490.0664 | 1635.7223 | 1793.6078 | 1965.9337 | 2153.5689 | 2357.2209 | 2577.3131 | 2813.8052 | 3065.9306 | 3331.8151 | 3607.925 | 3888.2719 | 4163.2666 | 4418.0729 |  | 32.4899 | 35.5553 | 38.9223 | 42.6211 | 46.6852 | 51.1515 | 56.0605 | 61.457 | 67.3904 | 73.915 | 81.0908 | 88.9839 | 97.6672 | 107.221 | 117.734 | 129.304 | 142.0387 | 156.0569 | 171.4899 | 188.4822 | 207.1935 | 227.7996 | 250.4946 | 275.4929 | 303.0307 | 333.3687 | 366.7945 | 403.6255 | 444.212 | 488.9403 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 17.8188 | 20.8842 | 24.2511 | 27.9499 | 32.0141 | 36.4803 | 41.3894 | 46.7859 | 52.7193 | 59.2439 | 66.4197 | 74.3128 | 82.996 | 92.5499 | 103.0629 | 114.6329 | 127.3675 | 138.4965 | 148.2125 | 157.3572 | 165.2475 | 170.8719 | 172.748 | 168.7195 | 155.6655 | 129.0872 | 82.5157 | 6.6675 | -111.7619 | -291.8231 |  | 3.8617 | 4.2261 | 4.6262 | 5.0659 | 5.5489 | 6.0798 | 6.6633 | 7.3047 | 8.0099 | 8.7854 | 9.6383 | 10.5765 | 11.6086 | 12.7441 | 13.9937 | 15.3689 | 16.8825 | 18.5487 | 20.3831 | 22.4027 | 24.6267 | 27.0759 | 29.7734 | 32.7447 | 36.0178 | 39.6237 | 43.5967 | 47.9744 | 52.7984 | 58.1148 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 1.794 | 2.1584 | 2.5586 | 2.9982 | 3.4812 | 4.0121 | 4.5956 | 5.237 | 5.9422 | 6.7177 | 7.5706 | 8.5088 | 9.5409 | 10.6764 | 11.926 | 13.3012 | 14.8148 | 16.0738 | 17.1024 | 18.0161 | 18.715 | 19.0528 | 18.8161 | 17.6965 | 15.2487 | 10.8331 | 3.5315 | -7.9714 | -25.5584 | -51.923 |  | 420.8235 | 460.5278 | 504.1378 | 552.0464 | 604.6866 | 662.5356 | 726.1194 | 796.0175 | 872.8691 | 957.3786 | 1050.3226 | 1152.5573 | 1265.0268 | 1388.7722 | 1524.9413 | 1674.8003 | 1839.7451 | 2021.3156 | 2221.2101 | 2441.302 | 2683.6577 | 2950.5565 | 3244.513 | 3568.3015 | 3924.9824 | 4317.9326 | 4750.8778 | 5227.9288 | 5753.6218 | 6332.9622 |  | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.13186 | 0.17479 | 0.23372 | 0.31498 | 0.42748 | 0.58381 | 0.80178 | 1.1066 | 1.534 | 2.1347 | 2.9808 | 4.1749 | 5.8629 |  | 420.7133 | 460.4176 | 504.0276 | 551.9362 | 604.5764 | 662.4255 | 726.0092 | 795.9074 | 872.759 | 957.2684 | 1050.2124 | 1152.4471 | 1264.9166 | 1388.662 | 1524.8312 | 1674.6901 | 1839.6349 | 2021.1837 | 2221.0353 | 2441.0683 | 2683.3427 | 2950.129 | 3243.9292 | 3567.4997 | 3923.8758 | 4316.3986 | 4748.7431 | 5224.948 | 5749.4469 | 6327.0993 |  | 770.1443 | 845.7444 | 928.7813 | 1020.0032 | 1120.2343 | 1230.3835 | 1351.452 | 1484.5436 | 1630.8751 | 1791.7879 | 1968.7606 | 2163.4236 | 2377.5745 | 2613.1955 | 2872.4724 | 3157.8157 | 3471.8837 | 3811.4763 | 4179.9581 | 4582.3753 | 5020.8741 | 5497.2745 | 6012.8064 | 6567.7208 | 7160.7208 | 7788.1341 | 8442.7154 | 9111.9161 | 9775.3932 | 10401.4261
| TRUE | 470 | 22005284 | BC | Blank | 11 | BUS NO.3 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.033587 | 2190 |  | 9.9 | 0.0088019 | 0.00083024 | 0.0079716 | 48.8669 | 265.6753 | 314.5422 | 29.6986 | 3.5299 | 384.6683 |  | 13.7946 | 0.021906 | 0.0020663 | 0.01984 | 121.622 | 661.2238 | 782.8458 | 73.915 | 8.7854 | 957.3786 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.11017 |  | 732.439 | 1822.9249 | 45.3489 | 1777.576 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.00090827 | 0.00099396 | 0.0010881 | 0.0011915 | 0.0013051 | 0.00143 | 0.0015672 | 0.0017181 | 0.0018839 | 0.0020663 | 0.0022669 | 0.0024876 | 0.0027303 | 0.0029974 | 0.0032913 | 0.0036147 | 0.0039707 | 0.0043626 | 0.0047941 | 0.0052691 | 0.0057922 | 0.0063682 | 0.0070027 | 0.0077015 | 0.0084713 | 0.0093195 | 0.010254 | 0.011284 | 0.012418 | 0.013669 | 801.2813 | 876.8814 | 959.9183 | 1051.1401 | 1151.3713 | 1261.5204 | 1382.5889 | 1515.6806 | 1662.0121 | 1822.9249 | 1999.8975 | 2194.5605 | 2408.7114 | 2644.3325 | 2903.6094 | 3188.9526 | 3503.0206 | 3848.7453 | 4229.3604 | 4648.4329 | 5109.8972 | 5618.0937 | 6177.8103 | 6794.3293 | 7473.4781 | 8221.6865 | 9046.0484 | 9954.3915 | 10955.3527 | 12058.4627 |  | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 37.2699 | 49.4034 | 66.0591 | 89.0252 | 120.822 | 165.0077 | 226.6137 | 312.7646 | 433.5624 | 603.347 | 842.4948 | 1179.9867 | 1657.0749 |  | 53.4599 | 58.5038 | 64.0439 | 70.13 | 76.8172 | 84.1662 | 92.2436 | 101.1232 | 110.8862 | 121.622 | 133.4292 | 146.4168 | 160.7045 | 176.4247 | 193.7231 | 212.7607 | 233.7147 | 256.7807 | 282.1746 | 310.1343 | 340.9223 | 374.8282 | 412.1714 | 453.3043 | 498.6158 | 548.5348 | 603.5346 | 664.1375 | 730.9196 | 804.517 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 39.248 | 44.2919 | 49.832 | 55.9181 | 62.6053 | 69.9543 | 78.0317 | 86.9113 | 96.6743 | 107.4101 | 119.2174 | 132.2049 | 146.4926 | 162.2128 | 179.5112 | 198.5488 | 219.5028 | 239.77 | 259.6259 | 279.9836 | 300.2894 | 319.6825 | 336.8584 | 349.8731 | 355.8636 | 350.6479 | 328.1545 | 279.6054 | 192.3492 | 48.1936 |  | 290.6463 | 318.0685 | 348.1882 | 381.2768 | 417.6333 | 457.5874 | 501.5022 | 549.7781 | 602.8565 | 661.2238 | 725.4166 | 796.0261 | 873.7044 | 959.1704 | 1053.2172 | 1156.7188 | 1270.6397 | 1396.0434 | 1534.1027 | 1686.1115 | 1853.4971 | 2037.8336 | 2240.8578 | 2464.4858 | 2710.8314 | 2982.2266 | 3281.2449 | 3610.7253 | 3973.8008 | 4373.9285 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 290.5702 | 317.9924 | 348.1121 | 381.2007 | 417.5572 | 457.5113 | 501.4261 | 549.702 | 602.7804 | 661.1477 | 725.3405 | 795.95 | 873.6283 | 959.0944 | 1053.1411 | 1156.6427 | 1270.5636 | 1395.9523 | 1533.982 | 1685.9501 | 1853.2795 | 2037.5383 | 2240.4546 | 2463.9321 | 2710.0671 | 2981.1672 | 3279.7705 | 3608.6666 | 3970.9174 | 4369.8793 |  | 329.8182 | 362.2843 | 397.9441 | 437.1188 | 480.1626 | 527.4656 | 579.4578 | 636.6133 | 699.4547 | 768.5578 | 844.5578 | 928.1549 | 1020.1209 | 1121.3071 | 1232.6523 | 1355.1915 | 1490.0664 | 1635.7223 | 1793.6078 | 1965.9337 | 2153.5689 | 2357.2209 | 2577.3131 | 2813.8052 | 3065.9306 | 3331.8151 | 3607.925 | 3888.2719 | 4163.2666 | 4418.0729 |  | 32.4899 | 35.5553 | 38.9223 | 42.6211 | 46.6852 | 51.1515 | 56.0605 | 61.457 | 67.3904 | 73.915 | 81.0908 | 88.9839 | 97.6672 | 107.221 | 117.734 | 129.304 | 142.0387 | 156.0569 | 171.4899 | 188.4822 | 207.1935 | 227.7996 | 250.4946 | 275.4929 | 303.0307 | 333.3687 | 366.7945 | 403.6255 | 444.212 | 488.9403 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 17.8188 | 20.8842 | 24.2511 | 27.9499 | 32.0141 | 36.4803 | 41.3894 | 46.7859 | 52.7193 | 59.2439 | 66.4197 | 74.3128 | 82.996 | 92.5499 | 103.0629 | 114.6329 | 127.3675 | 138.4965 | 148.2125 | 157.3572 | 165.2475 | 170.8719 | 172.748 | 168.7195 | 155.6655 | 129.0872 | 82.5157 | 6.6675 | -111.7619 | -291.8231 |  | 3.8617 | 4.2261 | 4.6262 | 5.0659 | 5.5489 | 6.0798 | 6.6633 | 7.3047 | 8.0099 | 8.7854 | 9.6383 | 10.5765 | 11.6086 | 12.7441 | 13.9937 | 15.3689 | 16.8825 | 18.5487 | 20.3831 | 22.4027 | 24.6267 | 27.0759 | 29.7734 | 32.7447 | 36.0178 | 39.6237 | 43.5967 | 47.9744 | 52.7984 | 58.1148 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 1.794 | 2.1584 | 2.5586 | 2.9982 | 3.4812 | 4.0121 | 4.5956 | 5.237 | 5.9422 | 6.7177 | 7.5706 | 8.5088 | 9.5409 | 10.6764 | 11.926 | 13.3012 | 14.8148 | 16.0738 | 17.1024 | 18.0161 | 18.715 | 19.0528 | 18.8161 | 17.6965 | 15.2487 | 10.8331 | 3.5315 | -7.9714 | -25.5584 | -51.923 |  | 420.8235 | 460.5278 | 504.1378 | 552.0464 | 604.6866 | 662.5356 | 726.1194 | 796.0175 | 872.8691 | 957.3786 | 1050.3226 | 1152.5573 | 1265.0268 | 1388.7722 | 1524.9413 | 1674.8003 | 1839.7451 | 2021.3156 | 2221.2101 | 2441.302 | 2683.6577 | 2950.5565 | 3244.513 | 3568.3015 | 3924.9824 | 4317.9326 | 4750.8778 | 5227.9288 | 5753.6218 | 6332.9622 |  | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.13186 | 0.17479 | 0.23372 | 0.31498 | 0.42748 | 0.58381 | 0.80178 | 1.1066 | 1.534 | 2.1347 | 2.9808 | 4.1749 | 5.8629 |  | 420.7133 | 460.4176 | 504.0276 | 551.9362 | 604.5764 | 662.4255 | 726.0092 | 795.9074 | 872.759 | 957.2684 | 1050.2124 | 1152.4471 | 1264.9166 | 1388.662 | 1524.8312 | 1674.6901 | 1839.6349 | 2021.1837 | 2221.0353 | 2441.0683 | 2683.3427 | 2950.129 | 3243.9292 | 3567.4997 | 3923.8758 | 4316.3986 | 4748.7431 | 5224.948 | 5749.4469 | 6327.0993 |  | 770.1443 | 845.7444 | 928.7813 | 1020.0032 | 1120.2343 | 1230.3835 | 1351.452 | 1484.5436 | 1630.8751 | 1791.7879 | 1968.7606 | 2163.4236 | 2377.5745 | 2613.1955 | 2872.4724 | 3157.8157 | 3471.8837 | 3811.4763 | 4179.9581 | 4582.3753 | 5020.8741 | 5497.2745 | 6012.8064 | 6567.7208 | 7160.7208 | 7788.1341 | 8442.7154 | 9111.9161 | 9775.3932 | 10401.4261
| TRUE | 471 | 22005283 | BC | Blank | 11 | BUS NO.3 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.033587 | 2190 |  | 9.9 | 0.0088019 | 0.00083024 | 0.0079716 | 48.8669 | 265.6753 | 314.5422 | 29.6986 | 3.5299 | 384.6683 |  | 13.7946 | 0.021906 | 0.0020663 | 0.01984 | 121.622 | 661.2238 | 782.8458 | 73.915 | 8.7854 | 957.3786 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.11017 |  | 732.439 | 1822.9249 | 45.3489 | 1777.576 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.00090827 | 0.00099396 | 0.0010881 | 0.0011915 | 0.0013051 | 0.00143 | 0.0015672 | 0.0017181 | 0.0018839 | 0.0020663 | 0.0022669 | 0.0024876 | 0.0027303 | 0.0029974 | 0.0032913 | 0.0036147 | 0.0039707 | 0.0043626 | 0.0047941 | 0.0052691 | 0.0057922 | 0.0063682 | 0.0070027 | 0.0077015 | 0.0084713 | 0.0093195 | 0.010254 | 0.011284 | 0.012418 | 0.013669 | 801.2813 | 876.8814 | 959.9183 | 1051.1401 | 1151.3713 | 1261.5204 | 1382.5889 | 1515.6806 | 1662.0121 | 1822.9249 | 1999.8975 | 2194.5605 | 2408.7114 | 2644.3325 | 2903.6094 | 3188.9526 | 3503.0206 | 3848.7453 | 4229.3604 | 4648.4329 | 5109.8972 | 5618.0937 | 6177.8103 | 6794.3293 | 7473.4781 | 8221.6865 | 9046.0484 | 9954.3915 | 10955.3527 | 12058.4627 |  | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 37.2699 | 49.4034 | 66.0591 | 89.0252 | 120.822 | 165.0077 | 226.6137 | 312.7646 | 433.5624 | 603.347 | 842.4948 | 1179.9867 | 1657.0749 |  | 53.4599 | 58.5038 | 64.0439 | 70.13 | 76.8172 | 84.1662 | 92.2436 | 101.1232 | 110.8862 | 121.622 | 133.4292 | 146.4168 | 160.7045 | 176.4247 | 193.7231 | 212.7607 | 233.7147 | 256.7807 | 282.1746 | 310.1343 | 340.9223 | 374.8282 | 412.1714 | 453.3043 | 498.6158 | 548.5348 | 603.5346 | 664.1375 | 730.9196 | 804.517 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 39.248 | 44.2919 | 49.832 | 55.9181 | 62.6053 | 69.9543 | 78.0317 | 86.9113 | 96.6743 | 107.4101 | 119.2174 | 132.2049 | 146.4926 | 162.2128 | 179.5112 | 198.5488 | 219.5028 | 239.77 | 259.6259 | 279.9836 | 300.2894 | 319.6825 | 336.8584 | 349.8731 | 355.8636 | 350.6479 | 328.1545 | 279.6054 | 192.3492 | 48.1936 |  | 290.6463 | 318.0685 | 348.1882 | 381.2768 | 417.6333 | 457.5874 | 501.5022 | 549.7781 | 602.8565 | 661.2238 | 725.4166 | 796.0261 | 873.7044 | 959.1704 | 1053.2172 | 1156.7188 | 1270.6397 | 1396.0434 | 1534.1027 | 1686.1115 | 1853.4971 | 2037.8336 | 2240.8578 | 2464.4858 | 2710.8314 | 2982.2266 | 3281.2449 | 3610.7253 | 3973.8008 | 4373.9285 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 290.5702 | 317.9924 | 348.1121 | 381.2007 | 417.5572 | 457.5113 | 501.4261 | 549.702 | 602.7804 | 661.1477 | 725.3405 | 795.95 | 873.6283 | 959.0944 | 1053.1411 | 1156.6427 | 1270.5636 | 1395.9523 | 1533.982 | 1685.9501 | 1853.2795 | 2037.5383 | 2240.4546 | 2463.9321 | 2710.0671 | 2981.1672 | 3279.7705 | 3608.6666 | 3970.9174 | 4369.8793 |  | 329.8182 | 362.2843 | 397.9441 | 437.1188 | 480.1626 | 527.4656 | 579.4578 | 636.6133 | 699.4547 | 768.5578 | 844.5578 | 928.1549 | 1020.1209 | 1121.3071 | 1232.6523 | 1355.1915 | 1490.0664 | 1635.7223 | 1793.6078 | 1965.9337 | 2153.5689 | 2357.2209 | 2577.3131 | 2813.8052 | 3065.9306 | 3331.8151 | 3607.925 | 3888.2719 | 4163.2666 | 4418.0729 |  | 32.4899 | 35.5553 | 38.9223 | 42.6211 | 46.6852 | 51.1515 | 56.0605 | 61.457 | 67.3904 | 73.915 | 81.0908 | 88.9839 | 97.6672 | 107.221 | 117.734 | 129.304 | 142.0387 | 156.0569 | 171.4899 | 188.4822 | 207.1935 | 227.7996 | 250.4946 | 275.4929 | 303.0307 | 333.3687 | 366.7945 | 403.6255 | 444.212 | 488.9403 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 17.8188 | 20.8842 | 24.2511 | 27.9499 | 32.0141 | 36.4803 | 41.3894 | 46.7859 | 52.7193 | 59.2439 | 66.4197 | 74.3128 | 82.996 | 92.5499 | 103.0629 | 114.6329 | 127.3675 | 138.4965 | 148.2125 | 157.3572 | 165.2475 | 170.8719 | 172.748 | 168.7195 | 155.6655 | 129.0872 | 82.5157 | 6.6675 | -111.7619 | -291.8231 |  | 3.8617 | 4.2261 | 4.6262 | 5.0659 | 5.5489 | 6.0798 | 6.6633 | 7.3047 | 8.0099 | 8.7854 | 9.6383 | 10.5765 | 11.6086 | 12.7441 | 13.9937 | 15.3689 | 16.8825 | 18.5487 | 20.3831 | 22.4027 | 24.6267 | 27.0759 | 29.7734 | 32.7447 | 36.0178 | 39.6237 | 43.5967 | 47.9744 | 52.7984 | 58.1148 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 1.794 | 2.1584 | 2.5586 | 2.9982 | 3.4812 | 4.0121 | 4.5956 | 5.237 | 5.9422 | 6.7177 | 7.5706 | 8.5088 | 9.5409 | 10.6764 | 11.926 | 13.3012 | 14.8148 | 16.0738 | 17.1024 | 18.0161 | 18.715 | 19.0528 | 18.8161 | 17.6965 | 15.2487 | 10.8331 | 3.5315 | -7.9714 | -25.5584 | -51.923 |  | 420.8235 | 460.5278 | 504.1378 | 552.0464 | 604.6866 | 662.5356 | 726.1194 | 796.0175 | 872.8691 | 957.3786 | 1050.3226 | 1152.5573 | 1265.0268 | 1388.7722 | 1524.9413 | 1674.8003 | 1839.7451 | 2021.3156 | 2221.2101 | 2441.302 | 2683.6577 | 2950.5565 | 3244.513 | 3568.3015 | 3924.9824 | 4317.9326 | 4750.8778 | 5227.9288 | 5753.6218 | 6332.9622 |  | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.13186 | 0.17479 | 0.23372 | 0.31498 | 0.42748 | 0.58381 | 0.80178 | 1.1066 | 1.534 | 2.1347 | 2.9808 | 4.1749 | 5.8629 |  | 420.7133 | 460.4176 | 504.0276 | 551.9362 | 604.5764 | 662.4255 | 726.0092 | 795.9074 | 872.759 | 957.2684 | 1050.2124 | 1152.4471 | 1264.9166 | 1388.662 | 1524.8312 | 1674.6901 | 1839.6349 | 2021.1837 | 2221.0353 | 2441.0683 | 2683.3427 | 2950.129 | 3243.9292 | 3567.4997 | 3923.8758 | 4316.3986 | 4748.7431 | 5224.948 | 5749.4469 | 6327.0993 |  | 770.1443 | 845.7444 | 928.7813 | 1020.0032 | 1120.2343 | 1230.3835 | 1351.452 | 1484.5436 | 1630.8751 | 1791.7879 | 1968.7606 | 2163.4236 | 2377.5745 | 2613.1955 | 2872.4724 | 3157.8157 | 3471.8837 | 3811.4763 | 4179.9581 | 4582.3753 | 5020.8741 | 5497.2745 | 6012.8064 | 6567.7208 | 7160.7208 | 7788.1341 | 8442.7154 | 9111.9161 | 9775.3932 | 10401.4261
| TRUE | 472 | 22013839 | BC | Blank | 11 | BUS NO.3 | RESIDUAL BUS PROT | Blank | GEC | CDG14_548 | CDG14 548 | CDG14 | Electromechanical |  | 0.033587 | 2190 |  | 8.25 | 0.0054067 | 0.00050998 | 0.0048967 | 30.0172 | 163.1947 | 193.2118 | 18.2427 | 2.1683 | 236.2878 |  | 11.265 | 0.01251 | 0.00118 | 0.01133 | 69.4541 | 377.6018 | 447.0559 | 42.2103 | 5.0171 | 546.7255 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.11017 |  | 449.9107 | 1041.0087 | 45.3489 | 995.6598 |  | 0.031148 |  | 8.511 | 8.7803 | 9.0581 | 9.3447 | 9.6403 | 9.9453 | 10.26 | 10.5846 | 10.9195 | 11.265 | 11.6214 | 11.9891 | 12.3684 | 12.7597 | 13.1634 | 13.5799 | 14.0095 | 14.4528 | 14.91 | 15.3818 | 15.8684 | 16.3705 | 16.8884 | 17.4227 | 17.974 | 18.5426 | 19.1293 | 19.7345 | 20.3589 | 21.003 |  | 0.0058713 | 0.0063781 | 0.006931 | 0.0075342 | 0.0081926 | 0.0089113 | 0.0096958 | 0.010553 | 0.011488 | 0.01251 | 0.013626 | 0.014846 | 0.016179 | 0.017636 | 0.019228 | 0.020969 | 0.022872 | 0.024954 | 0.02723 | 0.02972 | 0.032443 | 0.035422 | 0.038682 | 0.042249 | 0.046153 | 0.050426 | 0.055102 | 0.060222 | 0.065826 | 0.071963 |  | 0.00055381 | 0.00060161 | 0.00065376 | 0.00071067 | 0.00077277 | 0.00084055 | 0.00091456 | 0.00099537 | 0.0010836 | 0.00118 | 0.0012853 | 0.0014004 | 0.0015261 | 0.0016635 | 0.0018137 | 0.0019779 | 0.0021574 | 0.0023538 | 0.0025685 | 0.0028033 | 0.0030602 | 0.0033412 | 0.0036487 | 0.0039852 | 0.0043534 | 0.0047564 | 0.0051975 | 0.0056804 | 0.0062091 | 0.0067879 | 488.5753 | 530.7476 | 576.7549 | 626.9554 | 681.7415 | 741.5428 | 806.8298 | 878.1179 | 955.9714 | 1041.0087 | 1133.907 | 1235.4085 | 1346.3261 | 1467.5505 | 1600.058 | 1744.918 | 1903.3028 | 2076.497 | 2265.9087 | 2473.0809 | 2699.7053 | 2947.6362 | 3218.9063 | 3515.7439 | 3840.5922 | 4196.1296 | 4585.2931 | 5011.3027 | 5477.6893 | 5988.325 |  | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 31.1377 | 37.2699 | 49.4034 | 66.0591 | 89.0252 | 120.822 | 165.0077 | 226.6137 | 312.7646 | 433.5624 | 603.347 | 842.4948 | 1179.9867 | 1657.0749 |  | 32.5968 | 35.4104 | 38.48 | 41.8292 | 45.4845 | 49.4743 | 53.8301 | 58.5863 | 63.7805 | 69.4541 | 75.6521 | 82.424 | 89.8242 | 97.9121 | 106.7527 | 116.4175 | 126.9846 | 138.5398 | 151.177 | 164.9991 | 180.119 | 196.6605 | 214.7591 | 234.5635 | 256.2368 | 279.9575 | 305.9218 | 334.3443 | 365.4607 | 399.5293 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 18.3849 | 21.1985 | 24.2681 | 27.6173 | 31.2726 | 35.2624 | 39.6182 | 44.3744 | 49.5686 | 55.2422 | 61.4402 | 68.2121 | 75.6123 | 83.7002 | 92.5408 | 102.2056 | 112.7727 | 121.5291 | 128.6282 | 134.8484 | 139.4861 | 141.5148 | 139.4462 | 131.1324 | 113.4845 | 82.0707 | 30.5417 | -50.1878 | -173.1097 | -356.7941 |  | 177.2194 | 192.5164 | 209.2045 | 227.4136 | 247.286 | 268.9775 | 292.6589 | 318.517 | 346.7565 | 377.6018 | 411.2985 | 448.1159 | 488.3486 | 532.32 | 580.384 | 632.9287 | 690.3791 | 753.2013 | 821.906 | 897.0529 | 979.2557 | 1069.1869 | 1167.5838 | 1275.2548 | 1393.086 | 1522.049 | 1663.209 | 1817.7342 | 1986.9051 | 2172.1264 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 177.1433 | 192.4403 | 209.1284 | 227.3375 | 247.2099 | 268.9014 | 292.5828 | 318.4409 | 346.6804 | 377.5257 | 411.2225 | 448.0398 | 488.2726 | 532.2439 | 580.3079 | 632.8526 | 690.303 | 753.1102 | 821.7852 | 896.8915 | 979.0381 | 1068.8916 | 1167.1806 | 1274.701 | 1392.3217 | 1520.9895 | 1661.7347 | 1815.6754 | 1984.0217 | 2168.0772 |  | 195.5282 | 213.6389 | 233.3965 | 254.9548 | 278.4825 | 304.1638 | 332.201 | 362.8153 | 396.2491 | 432.7679 | 472.6626 | 516.2519 | 563.8849 | 615.9441 | 672.8488 | 735.0582 | 803.0757 | 874.6393 | 950.4135 | 1031.7399 | 1118.5242 | 1210.4065 | 1306.6268 | 1405.8334 | 1505.8063 | 1603.0602 | 1692.2764 | 1765.4876 | 1810.912 | 1811.2831 |  | 19.8105 | 21.5205 | 23.386 | 25.4215 | 27.6429 | 30.0677 | 32.7149 | 35.6055 | 38.7622 | 42.2103 | 45.9771 | 50.0927 | 54.5901 | 59.5055 | 64.8783 | 70.752 | 77.1741 | 84.1967 | 91.8769 | 100.2772 | 109.4663 | 119.5192 | 130.5185 | 142.5546 | 155.7263 | 170.1425 | 185.9221 | 203.1957 | 222.1065 | 242.8115 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 5.1394 | 6.8493 | 8.7148 | 10.7503 | 12.9718 | 15.3966 | 18.0438 | 20.9343 | 24.0911 | 27.5391 | 31.3059 | 35.4216 | 39.919 | 44.8343 | 50.2072 | 56.0809 | 62.503 | 66.6363 | 68.5995 | 69.1522 | 67.5203 | 62.5916 | 52.7719 | 35.7811 | 8.3612 | -34.1389 | -98.3567 | -193.7623 | -333.8674 | -537.9519 |  | 2.3546 | 2.5579 | 2.7796 | 3.0216 | 3.2856 | 3.5738 | 3.8884 | 4.232 | 4.6072 | 5.0171 | 5.4648 | 5.9539 | 6.4885 | 7.0727 | 7.7113 | 8.4095 | 9.1728 | 10.0075 | 10.9204 | 11.9188 | 13.011 | 14.2059 | 15.5133 | 16.9438 | 18.5094 | 20.2229 | 22.0984 | 24.1516 | 26.3993 | 28.8602 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0.28695 | 0.4902 | 0.71193 | 0.95387 | 1.2179 | 1.5061 | 1.8208 | 2.1643 | 2.5395 | 2.9494 | 3.3971 | 3.8863 | 4.4208 | 5.005 | 5.6437 | 6.3418 | 7.1051 | 7.5326 | 7.6397 | 7.5322 | 7.0993 | 6.1827 | 4.5559 | 1.8956 | -2.2597 | -8.5677 | -17.9667 | -31.7942 | -51.9576 | -81.1776 |  | 256.594 | 278.7424 | 302.9049 | 329.2696 | 358.0426 | 389.4495 | 423.7375 | 461.1771 | 502.0649 | 546.7255 | 595.5146 | 648.8219 | 707.0745 | 770.7402 | 840.3315 | 916.4103 | 999.5922 | 1090.5517 | 1190.0285 | 1298.8329 | 1417.8534 | 1548.0637 | 1690.5316 | 1846.4272 | 2017.0337 | 2203.7577 | 2408.1418 | 2631.877 | 2876.8177 | 3144.9975 |  | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.11017 | 0.13186 | 0.17479 | 0.23372 | 0.31498 | 0.42748 | 0.58381 | 0.80178 | 1.1066 | 1.534 | 2.1347 | 2.9808 | 4.1749 | 5.8629 |  | 256.4838 | 278.6322 | 302.7947 | 329.1594 | 357.9324 | 389.3394 | 423.6273 | 461.067 | 501.9547 | 546.6153 | 595.4044 | 648.7118 | 706.9644 | 770.63 | 840.2214 | 916.3002 | 999.482 | 1090.4199 | 1189.8537 | 1298.5991 | 1417.5384 | 1547.6363 | 1689.9478 | 1845.6254 | 2015.9271 | 2202.2237 | 2406.0071 | 2628.8962 | 2872.6428 | 3139.1347 |  | 457.4383 | 499.6106 | 545.6179 | 595.8184 | 650.6046 | 710.4059 | 775.6929 | 846.9809 | 924.8344 | 1009.8717 | 1102.77 | 1204.2715 | 1315.1891 | 1436.4135 | 1568.921 | 1713.781 | 1872.1658 | 2039.228 | 2216.5064 | 2407.0233 | 2610.6822 | 2826.817 | 3053.9024 | 3289.1355 | 3527.8348 | 3762.5773 | 3981.96 | 4168.8273 | 4297.7299 | 4331.2883
| TRUE | 473 | 22013841 | BC | Blank | 11 | CAP NO.1 | OVERCURRENT | Blank | GEC | CDG14_984 | CDG14 984 | CDG14 | Electromechanical |  | 0.2894 | 2190 |  | 8.25 | 0.0054067 | 0.0028421 | 0.0025646 | 31.2998 | 909.4607 | 940.7605 | 31.4825 | 2.1916 | 1316.7979 |  | 11.265 | 0.01251 | 0.006576 | 0.005934 | 72.4219 | 2104.321 | 2176.7428 | 72.8446 | 5.071 | 3046.8228 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.94924 |  | 2291.2325 | 5301.4812 | 46.7787 | 5254.7025 |  | 0.031148 |  | 8.511 | 8.7803 | 9.0581 | 9.3447 | 9.6403 | 9.9453 | 10.26 | 10.5846 | 10.9195 | 11.265 | 11.6214 | 11.9891 | 12.3684 | 12.7597 | 13.1634 | 13.5799 | 14.0095 | 14.4528 | 14.91 | 15.3818 | 15.8684 | 16.3705 | 16.8884 | 17.4227 | 17.974 | 18.5426 | 19.1293 | 19.7345 | 20.3589 | 21.003 |  | 0.0058713 | 0.0063781 | 0.006931 | 0.0075342 | 0.0081926 | 0.0089113 | 0.0096958 | 0.010553 | 0.011488 | 0.01251 | 0.013626 | 0.014846 | 0.016179 | 0.017636 | 0.019228 | 0.020969 | 0.022872 | 0.024954 | 0.02723 | 0.02972 | 0.032443 | 0.035422 | 0.038682 | 0.042249 | 0.046153 | 0.050426 | 0.055102 | 0.060222 | 0.065826 | 0.071963 |  | 0.0030863 | 0.0033527 | 0.0036433 | 0.0039604 | 0.0043065 | 0.0046843 | 0.0050967 | 0.005547 | 0.0060388 | 0.006576 | 0.0071628 | 0.007804 | 0.0085047 | 0.0092704 | 0.010107 | 0.011023 | 0.012023 | 0.013117 | 0.014314 | 0.015622 | 0.017054 | 0.01862 | 0.020334 | 0.022209 | 0.024261 | 0.026507 | 0.028965 | 0.031656 | 0.034602 | 0.037828 | 2488.1374 | 2702.9059 | 2937.2044 | 3192.8575 | 3471.8634 | 3776.4099 | 4108.8931 | 4471.9373 | 4868.4171 | 5301.4812 | 5774.579 | 6291.4893 | 6856.3524 | 7473.7049 | 8148.5174 | 8886.2373 | 9692.834 | 10574.8496 | 11539.4545 | 12594.5079 | 13748.6244 | 15011.2469 | 16392.7274 | 17904.4142 | 19558.7491 | 21369.373 | 23351.2419 | 25520.7548 | 27895.8937 | 30496.3767 |  | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 38.9873 | 51.68 | 69.1031 | 93.1275 | 126.3896 | 172.6115 | 237.0563 | 327.1771 | 453.5414 | 631.1499 | 881.3179 | 1234.3617 | 1733.4347 |  | 33.9897 | 36.9235 | 40.1242 | 43.6166 | 47.428 | 51.5883 | 56.1303 | 61.0897 | 66.5059 | 72.4219 | 78.8847 | 85.946 | 93.6625 | 102.0959 | 111.3143 | 121.3921 | 132.4107 | 144.4597 | 157.6368 | 172.0496 | 187.8156 | 205.0639 | 223.9359 | 244.5865 | 267.1859 | 291.9202 | 318.9939 | 348.6309 | 381.077 | 416.6013 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 19.7773 | 22.7112 | 25.9118 | 29.4042 | 33.2156 | 37.376 | 41.9179 | 46.8773 | 52.2935 | 58.2095 | 64.6723 | 71.7337 | 79.4501 | 87.8835 | 97.1019 | 107.1797 | 118.1983 | 127.4483 | 135.0873 | 141.8978 | 147.1812 | 149.9163 | 148.6203 | 141.1517 | 124.4286 | 94.0264 | 43.6042 | -35.9146 | -157.5123 | -339.7485 |  | 987.6183 | 1072.8665 | 1165.8668 | 1267.3434 | 1378.0894 | 1498.9732 | 1630.946 | 1775.0495 | 1932.4245 | 2104.321 | 2292.108 | 2497.2856 | 2721.4972 | 2966.5433 | 3234.3972 | 3527.2209 | 3847.3839 | 4197.483 | 4580.3644 | 4999.1476 | 5457.2519 | 5958.4256 | 6506.7777 | 7106.8127 | 7763.4691 | 8482.1614 | 9268.8261 | 10129.9725 | 11072.7382 | 12104.9499 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 986.9627 | 1072.2109 | 1165.2111 | 1266.6878 | 1377.4338 | 1498.3176 | 1630.2904 | 1774.3939 | 1931.7689 | 2103.6654 | 2291.4524 | 2496.63 | 2720.8416 | 2965.8877 | 3233.7416 | 3526.5653 | 3846.7283 | 4196.6983 | 4579.3242 | 4997.7567 | 5455.3775 | 5955.8817 | 6503.3035 | 7102.0414 | 7756.8839 | 8473.0328 | 9256.1227 | 10112.2339 | 11047.8937 | 12070.0603 |  | 1006.7399 | 1094.922 | 1191.123 | 1296.092 | 1410.6494 | 1535.6936 | 1672.2083 | 1821.2712 | 1984.0624 | 2161.8748 | 2356.1247 | 2568.3637 | 2800.2916 | 3053.7713 | 3330.8435 | 3633.745 | 3964.9267 | 4324.1467 | 4714.4115 | 5139.6545 | 5602.5587 | 6105.798 | 6651.9237 | 7243.1931 | 7881.3125 | 8567.0592 | 9299.7269 | 10076.3193 | 10890.3814 | 11730.3118 |  | 34.1881 | 37.1391 | 40.3584 | 43.8712 | 47.7049 | 51.8895 | 56.4579 | 61.4463 | 66.8941 | 72.8446 | 79.3452 | 86.4477 | 94.2092 | 102.6919 | 111.9641 | 122.1007 | 133.1837 | 145.3029 | 158.557 | 173.0539 | 188.9119 | 206.2609 | 225.2431 | 246.0143 | 268.7455 | 293.6243 | 320.856 | 350.666 | 383.3015 | 419.0332 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 19.5067 | 22.4577 | 25.677 | 29.1898 | 33.0235 | 37.2081 | 41.7765 | 46.7649 | 52.2127 | 58.1632 | 64.6638 | 71.7663 | 79.5278 | 88.0105 | 97.2827 | 107.4193 | 118.5022 | 127.7302 | 135.2633 | 141.9071 | 146.9366 | 149.2934 | 147.4419 | 139.166 | 121.2771 | 89.1997 | 36.378 | -46.5701 | -173.0621 | -362.2773 |  | 2.38 | 2.5854 | 2.8095 | 3.0541 | 3.3209 | 3.6122 | 3.9303 | 4.2775 | 4.6568 | 5.071 | 5.5235 | 6.018 | 6.5583 | 7.1488 | 7.7943 | 8.4999 | 9.2715 | 10.1151 | 11.0378 | 12.047 | 13.1509 | 14.3587 | 15.6801 | 17.1261 | 18.7085 | 20.4404 | 22.3361 | 24.4113 | 26.6832 | 29.1706 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0.31226 | 0.51769 | 0.74181 | 0.98635 | 1.2532 | 1.5445 | 1.8626 | 2.2098 | 2.5891 | 3.0033 | 3.4558 | 3.9503 | 4.4906 | 5.0811 | 5.7266 | 6.4322 | 7.2038 | 7.6402 | 7.7572 | 7.6603 | 7.2392 | 6.3354 | 4.7227 | 2.0777 | -2.0608 | -8.3505 | -17.7294 | -31.5349 | -51.6743 | -80.8681 |  | 1429.9615 | 1553.3914 | 1688.0454 | 1834.9723 | 1995.3202 | 2170.3466 | 2361.4285 | 2570.0743 | 2797.9358 | 3046.8228 | 3318.7176 | 3615.7919 | 3940.4253 | 4295.2249 | 4683.0475 | 5107.0237 | 5570.5842 | 6077.4888 | 6631.8585 | 7238.2099 | 7901.494 | 8627.1378 | 9421.0907 | 10289.8747 | 11240.6401 | 12281.2267 | 13420.2297 | 14667.074 | 16032.0939 | 17526.6216 |  | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 1.1362 | 1.5061 | 2.0138 | 2.7139 | 3.6833 | 5.0303 | 6.9084 | 9.5347 | 13.2172 | 18.3931 | 25.6836 | 35.9721 | 50.5162 |  | 1429.0122 | 1552.4421 | 1687.0962 | 1834.0231 | 1994.371 | 2169.3973 | 2360.4793 | 2569.125 | 2796.9866 | 3045.8736 | 3317.7683 | 3614.8427 | 3939.4761 | 4294.2757 | 4682.0983 | 5106.0745 | 5569.6349 | 6076.3526 | 6630.3524 | 7236.1961 | 7898.78 | 8623.4545 | 9416.0604 | 10282.9663 | 11231.1055 | 12268.0095 | 13401.8366 | 14641.3904 | 15996.1218 | 17476.1054 |  | 2455.5711 | 2670.3395 | 2904.638 | 3160.2912 | 3439.2971 | 3743.8435 | 4076.3267 | 4439.3709 | 4835.8508 | 5268.9149 | 5742.0126 | 6258.9229 | 6823.7861 | 7441.1385 | 8115.9511 | 8853.671 | 9660.2676 | 10535.8697 | 11487.7844 | 12525.4179 | 13655.5145 | 14884.8813 | 16220.1487 | 17667.403 | 19231.6343 | 20915.9179 | 22720.2121 | 24639.6047 | 26661.7669 | 28763.2717
| TRUE | 474 | 22013843 | BC | Blank | 11 | CAP NO.1 | OVERCURRENT | Blank | GEC | CDG14_984 | CDG14 984 | CDG14 | Electromechanical |  | 0.2894 | 2190 |  | 8.25 | 0.0054067 | 0.0028421 | 0.0025646 | 31.2998 | 909.4607 | 940.7605 | 31.4825 | 2.1916 | 1316.7979 |  | 11.265 | 0.01251 | 0.006576 | 0.005934 | 72.4219 | 2104.321 | 2176.7428 | 72.8446 | 5.071 | 3046.8228 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.94924 |  | 2291.2325 | 5301.4812 | 46.7787 | 5254.7025 |  | 0.031148 |  | 8.511 | 8.7803 | 9.0581 | 9.3447 | 9.6403 | 9.9453 | 10.26 | 10.5846 | 10.9195 | 11.265 | 11.6214 | 11.9891 | 12.3684 | 12.7597 | 13.1634 | 13.5799 | 14.0095 | 14.4528 | 14.91 | 15.3818 | 15.8684 | 16.3705 | 16.8884 | 17.4227 | 17.974 | 18.5426 | 19.1293 | 19.7345 | 20.3589 | 21.003 |  | 0.0058713 | 0.0063781 | 0.006931 | 0.0075342 | 0.0081926 | 0.0089113 | 0.0096958 | 0.010553 | 0.011488 | 0.01251 | 0.013626 | 0.014846 | 0.016179 | 0.017636 | 0.019228 | 0.020969 | 0.022872 | 0.024954 | 0.02723 | 0.02972 | 0.032443 | 0.035422 | 0.038682 | 0.042249 | 0.046153 | 0.050426 | 0.055102 | 0.060222 | 0.065826 | 0.071963 |  | 0.0030863 | 0.0033527 | 0.0036433 | 0.0039604 | 0.0043065 | 0.0046843 | 0.0050967 | 0.005547 | 0.0060388 | 0.006576 | 0.0071628 | 0.007804 | 0.0085047 | 0.0092704 | 0.010107 | 0.011023 | 0.012023 | 0.013117 | 0.014314 | 0.015622 | 0.017054 | 0.01862 | 0.020334 | 0.022209 | 0.024261 | 0.026507 | 0.028965 | 0.031656 | 0.034602 | 0.037828 | 2488.1374 | 2702.9059 | 2937.2044 | 3192.8575 | 3471.8634 | 3776.4099 | 4108.8931 | 4471.9373 | 4868.4171 | 5301.4812 | 5774.579 | 6291.4893 | 6856.3524 | 7473.7049 | 8148.5174 | 8886.2373 | 9692.834 | 10574.8496 | 11539.4545 | 12594.5079 | 13748.6244 | 15011.2469 | 16392.7274 | 17904.4142 | 19558.7491 | 21369.373 | 23351.2419 | 25520.7548 | 27895.8937 | 30496.3767 |  | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 38.9873 | 51.68 | 69.1031 | 93.1275 | 126.3896 | 172.6115 | 237.0563 | 327.1771 | 453.5414 | 631.1499 | 881.3179 | 1234.3617 | 1733.4347 |  | 33.9897 | 36.9235 | 40.1242 | 43.6166 | 47.428 | 51.5883 | 56.1303 | 61.0897 | 66.5059 | 72.4219 | 78.8847 | 85.946 | 93.6625 | 102.0959 | 111.3143 | 121.3921 | 132.4107 | 144.4597 | 157.6368 | 172.0496 | 187.8156 | 205.0639 | 223.9359 | 244.5865 | 267.1859 | 291.9202 | 318.9939 | 348.6309 | 381.077 | 416.6013 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 19.7773 | 22.7112 | 25.9118 | 29.4042 | 33.2156 | 37.376 | 41.9179 | 46.8773 | 52.2935 | 58.2095 | 64.6723 | 71.7337 | 79.4501 | 87.8835 | 97.1019 | 107.1797 | 118.1983 | 127.4483 | 135.0873 | 141.8978 | 147.1812 | 149.9163 | 148.6203 | 141.1517 | 124.4286 | 94.0264 | 43.6042 | -35.9146 | -157.5123 | -339.7485 |  | 987.6183 | 1072.8665 | 1165.8668 | 1267.3434 | 1378.0894 | 1498.9732 | 1630.946 | 1775.0495 | 1932.4245 | 2104.321 | 2292.108 | 2497.2856 | 2721.4972 | 2966.5433 | 3234.3972 | 3527.2209 | 3847.3839 | 4197.483 | 4580.3644 | 4999.1476 | 5457.2519 | 5958.4256 | 6506.7777 | 7106.8127 | 7763.4691 | 8482.1614 | 9268.8261 | 10129.9725 | 11072.7382 | 12104.9499 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 986.9627 | 1072.2109 | 1165.2111 | 1266.6878 | 1377.4338 | 1498.3176 | 1630.2904 | 1774.3939 | 1931.7689 | 2103.6654 | 2291.4524 | 2496.63 | 2720.8416 | 2965.8877 | 3233.7416 | 3526.5653 | 3846.7283 | 4196.6983 | 4579.3242 | 4997.7567 | 5455.3775 | 5955.8817 | 6503.3035 | 7102.0414 | 7756.8839 | 8473.0328 | 9256.1227 | 10112.2339 | 11047.8937 | 12070.0603 |  | 1006.7399 | 1094.922 | 1191.123 | 1296.092 | 1410.6494 | 1535.6936 | 1672.2083 | 1821.2712 | 1984.0624 | 2161.8748 | 2356.1247 | 2568.3637 | 2800.2916 | 3053.7713 | 3330.8435 | 3633.745 | 3964.9267 | 4324.1467 | 4714.4115 | 5139.6545 | 5602.5587 | 6105.798 | 6651.9237 | 7243.1931 | 7881.3125 | 8567.0592 | 9299.7269 | 10076.3193 | 10890.3814 | 11730.3118 |  | 34.1881 | 37.1391 | 40.3584 | 43.8712 | 47.7049 | 51.8895 | 56.4579 | 61.4463 | 66.8941 | 72.8446 | 79.3452 | 86.4477 | 94.2092 | 102.6919 | 111.9641 | 122.1007 | 133.1837 | 145.3029 | 158.557 | 173.0539 | 188.9119 | 206.2609 | 225.2431 | 246.0143 | 268.7455 | 293.6243 | 320.856 | 350.666 | 383.3015 | 419.0332 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 19.5067 | 22.4577 | 25.677 | 29.1898 | 33.0235 | 37.2081 | 41.7765 | 46.7649 | 52.2127 | 58.1632 | 64.6638 | 71.7663 | 79.5278 | 88.0105 | 97.2827 | 107.4193 | 118.5022 | 127.7302 | 135.2633 | 141.9071 | 146.9366 | 149.2934 | 147.4419 | 139.166 | 121.2771 | 89.1997 | 36.378 | -46.5701 | -173.0621 | -362.2773 |  | 2.38 | 2.5854 | 2.8095 | 3.0541 | 3.3209 | 3.6122 | 3.9303 | 4.2775 | 4.6568 | 5.071 | 5.5235 | 6.018 | 6.5583 | 7.1488 | 7.7943 | 8.4999 | 9.2715 | 10.1151 | 11.0378 | 12.047 | 13.1509 | 14.3587 | 15.6801 | 17.1261 | 18.7085 | 20.4404 | 22.3361 | 24.4113 | 26.6832 | 29.1706 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0.31226 | 0.51769 | 0.74181 | 0.98635 | 1.2532 | 1.5445 | 1.8626 | 2.2098 | 2.5891 | 3.0033 | 3.4558 | 3.9503 | 4.4906 | 5.0811 | 5.7266 | 6.4322 | 7.2038 | 7.6402 | 7.7572 | 7.6603 | 7.2392 | 6.3354 | 4.7227 | 2.0777 | -2.0608 | -8.3505 | -17.7294 | -31.5349 | -51.6743 | -80.8681 |  | 1429.9615 | 1553.3914 | 1688.0454 | 1834.9723 | 1995.3202 | 2170.3466 | 2361.4285 | 2570.0743 | 2797.9358 | 3046.8228 | 3318.7176 | 3615.7919 | 3940.4253 | 4295.2249 | 4683.0475 | 5107.0237 | 5570.5842 | 6077.4888 | 6631.8585 | 7238.2099 | 7901.494 | 8627.1378 | 9421.0907 | 10289.8747 | 11240.6401 | 12281.2267 | 13420.2297 | 14667.074 | 16032.0939 | 17526.6216 |  | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 1.1362 | 1.5061 | 2.0138 | 2.7139 | 3.6833 | 5.0303 | 6.9084 | 9.5347 | 13.2172 | 18.3931 | 25.6836 | 35.9721 | 50.5162 |  | 1429.0122 | 1552.4421 | 1687.0962 | 1834.0231 | 1994.371 | 2169.3973 | 2360.4793 | 2569.125 | 2796.9866 | 3045.8736 | 3317.7683 | 3614.8427 | 3939.4761 | 4294.2757 | 4682.0983 | 5106.0745 | 5569.6349 | 6076.3526 | 6630.3524 | 7236.1961 | 7898.78 | 8623.4545 | 9416.0604 | 10282.9663 | 11231.1055 | 12268.0095 | 13401.8366 | 14641.3904 | 15996.1218 | 17476.1054 |  | 2455.5711 | 2670.3395 | 2904.638 | 3160.2912 | 3439.2971 | 3743.8435 | 4076.3267 | 4439.3709 | 4835.8508 | 5268.9149 | 5742.0126 | 6258.9229 | 6823.7861 | 7441.1385 | 8115.9511 | 8853.671 | 9660.2676 | 10535.8697 | 11487.7844 | 12525.4179 | 13655.5145 | 14884.8813 | 16220.1487 | 17667.403 | 19231.6343 | 20915.9179 | 22720.2121 | 24639.6047 | 26661.7669 | 28763.2717
| TRUE | 475 | 22013842 | BC | Blank | 11 | CAP NO.1 | OVERCURRENT | Blank | GEC | CDG14_984 | CDG14 984 | CDG14 | Electromechanical |  | 0.2894 | 2190 |  | 8.25 | 0.0054067 | 0.0028421 | 0.0025646 | 31.2998 | 909.4607 | 940.7605 | 31.4825 | 2.1916 | 1316.7979 |  | 11.265 | 0.01251 | 0.006576 | 0.005934 | 72.4219 | 2104.321 | 2176.7428 | 72.8446 | 5.071 | 3046.8228 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.94924 |  | 2291.2325 | 5301.4812 | 46.7787 | 5254.7025 |  | 0.031148 |  | 8.511 | 8.7803 | 9.0581 | 9.3447 | 9.6403 | 9.9453 | 10.26 | 10.5846 | 10.9195 | 11.265 | 11.6214 | 11.9891 | 12.3684 | 12.7597 | 13.1634 | 13.5799 | 14.0095 | 14.4528 | 14.91 | 15.3818 | 15.8684 | 16.3705 | 16.8884 | 17.4227 | 17.974 | 18.5426 | 19.1293 | 19.7345 | 20.3589 | 21.003 |  | 0.0058713 | 0.0063781 | 0.006931 | 0.0075342 | 0.0081926 | 0.0089113 | 0.0096958 | 0.010553 | 0.011488 | 0.01251 | 0.013626 | 0.014846 | 0.016179 | 0.017636 | 0.019228 | 0.020969 | 0.022872 | 0.024954 | 0.02723 | 0.02972 | 0.032443 | 0.035422 | 0.038682 | 0.042249 | 0.046153 | 0.050426 | 0.055102 | 0.060222 | 0.065826 | 0.071963 |  | 0.0030863 | 0.0033527 | 0.0036433 | 0.0039604 | 0.0043065 | 0.0046843 | 0.0050967 | 0.005547 | 0.0060388 | 0.006576 | 0.0071628 | 0.007804 | 0.0085047 | 0.0092704 | 0.010107 | 0.011023 | 0.012023 | 0.013117 | 0.014314 | 0.015622 | 0.017054 | 0.01862 | 0.020334 | 0.022209 | 0.024261 | 0.026507 | 0.028965 | 0.031656 | 0.034602 | 0.037828 | 2488.1374 | 2702.9059 | 2937.2044 | 3192.8575 | 3471.8634 | 3776.4099 | 4108.8931 | 4471.9373 | 4868.4171 | 5301.4812 | 5774.579 | 6291.4893 | 6856.3524 | 7473.7049 | 8148.5174 | 8886.2373 | 9692.834 | 10574.8496 | 11539.4545 | 12594.5079 | 13748.6244 | 15011.2469 | 16392.7274 | 17904.4142 | 19558.7491 | 21369.373 | 23351.2419 | 25520.7548 | 27895.8937 | 30496.3767 |  | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 32.5726 | 38.9873 | 51.68 | 69.1031 | 93.1275 | 126.3896 | 172.6115 | 237.0563 | 327.1771 | 453.5414 | 631.1499 | 881.3179 | 1234.3617 | 1733.4347 |  | 33.9897 | 36.9235 | 40.1242 | 43.6166 | 47.428 | 51.5883 | 56.1303 | 61.0897 | 66.5059 | 72.4219 | 78.8847 | 85.946 | 93.6625 | 102.0959 | 111.3143 | 121.3921 | 132.4107 | 144.4597 | 157.6368 | 172.0496 | 187.8156 | 205.0639 | 223.9359 | 244.5865 | 267.1859 | 291.9202 | 318.9939 | 348.6309 | 381.077 | 416.6013 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 19.7773 | 22.7112 | 25.9118 | 29.4042 | 33.2156 | 37.376 | 41.9179 | 46.8773 | 52.2935 | 58.2095 | 64.6723 | 71.7337 | 79.4501 | 87.8835 | 97.1019 | 107.1797 | 118.1983 | 127.4483 | 135.0873 | 141.8978 | 147.1812 | 149.9163 | 148.6203 | 141.1517 | 124.4286 | 94.0264 | 43.6042 | -35.9146 | -157.5123 | -339.7485 |  | 987.6183 | 1072.8665 | 1165.8668 | 1267.3434 | 1378.0894 | 1498.9732 | 1630.946 | 1775.0495 | 1932.4245 | 2104.321 | 2292.108 | 2497.2856 | 2721.4972 | 2966.5433 | 3234.3972 | 3527.2209 | 3847.3839 | 4197.483 | 4580.3644 | 4999.1476 | 5457.2519 | 5958.4256 | 6506.7777 | 7106.8127 | 7763.4691 | 8482.1614 | 9268.8261 | 10129.9725 | 11072.7382 | 12104.9499 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 986.9627 | 1072.2109 | 1165.2111 | 1266.6878 | 1377.4338 | 1498.3176 | 1630.2904 | 1774.3939 | 1931.7689 | 2103.6654 | 2291.4524 | 2496.63 | 2720.8416 | 2965.8877 | 3233.7416 | 3526.5653 | 3846.7283 | 4196.6983 | 4579.3242 | 4997.7567 | 5455.3775 | 5955.8817 | 6503.3035 | 7102.0414 | 7756.8839 | 8473.0328 | 9256.1227 | 10112.2339 | 11047.8937 | 12070.0603 |  | 1006.7399 | 1094.922 | 1191.123 | 1296.092 | 1410.6494 | 1535.6936 | 1672.2083 | 1821.2712 | 1984.0624 | 2161.8748 | 2356.1247 | 2568.3637 | 2800.2916 | 3053.7713 | 3330.8435 | 3633.745 | 3964.9267 | 4324.1467 | 4714.4115 | 5139.6545 | 5602.5587 | 6105.798 | 6651.9237 | 7243.1931 | 7881.3125 | 8567.0592 | 9299.7269 | 10076.3193 | 10890.3814 | 11730.3118 |  | 34.1881 | 37.1391 | 40.3584 | 43.8712 | 47.7049 | 51.8895 | 56.4579 | 61.4463 | 66.8941 | 72.8446 | 79.3452 | 86.4477 | 94.2092 | 102.6919 | 111.9641 | 122.1007 | 133.1837 | 145.3029 | 158.557 | 173.0539 | 188.9119 | 206.2609 | 225.2431 | 246.0143 | 268.7455 | 293.6243 | 320.856 | 350.666 | 383.3015 | 419.0332 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 19.5067 | 22.4577 | 25.677 | 29.1898 | 33.0235 | 37.2081 | 41.7765 | 46.7649 | 52.2127 | 58.1632 | 64.6638 | 71.7663 | 79.5278 | 88.0105 | 97.2827 | 107.4193 | 118.5022 | 127.7302 | 135.2633 | 141.9071 | 146.9366 | 149.2934 | 147.4419 | 139.166 | 121.2771 | 89.1997 | 36.378 | -46.5701 | -173.0621 | -362.2773 |  | 2.38 | 2.5854 | 2.8095 | 3.0541 | 3.3209 | 3.6122 | 3.9303 | 4.2775 | 4.6568 | 5.071 | 5.5235 | 6.018 | 6.5583 | 7.1488 | 7.7943 | 8.4999 | 9.2715 | 10.1151 | 11.0378 | 12.047 | 13.1509 | 14.3587 | 15.6801 | 17.1261 | 18.7085 | 20.4404 | 22.3361 | 24.4113 | 26.6832 | 29.1706 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0.31226 | 0.51769 | 0.74181 | 0.98635 | 1.2532 | 1.5445 | 1.8626 | 2.2098 | 2.5891 | 3.0033 | 3.4558 | 3.9503 | 4.4906 | 5.0811 | 5.7266 | 6.4322 | 7.2038 | 7.6402 | 7.7572 | 7.6603 | 7.2392 | 6.3354 | 4.7227 | 2.0777 | -2.0608 | -8.3505 | -17.7294 | -31.5349 | -51.6743 | -80.8681 |  | 1429.9615 | 1553.3914 | 1688.0454 | 1834.9723 | 1995.3202 | 2170.3466 | 2361.4285 | 2570.0743 | 2797.9358 | 3046.8228 | 3318.7176 | 3615.7919 | 3940.4253 | 4295.2249 | 4683.0475 | 5107.0237 | 5570.5842 | 6077.4888 | 6631.8585 | 7238.2099 | 7901.494 | 8627.1378 | 9421.0907 | 10289.8747 | 11240.6401 | 12281.2267 | 13420.2297 | 14667.074 | 16032.0939 | 17526.6216 |  | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 1.1362 | 1.5061 | 2.0138 | 2.7139 | 3.6833 | 5.0303 | 6.9084 | 9.5347 | 13.2172 | 18.3931 | 25.6836 | 35.9721 | 50.5162 |  | 1429.0122 | 1552.4421 | 1687.0962 | 1834.0231 | 1994.371 | 2169.3973 | 2360.4793 | 2569.125 | 2796.9866 | 3045.8736 | 3317.7683 | 3614.8427 | 3939.4761 | 4294.2757 | 4682.0983 | 5106.0745 | 5569.6349 | 6076.3526 | 6630.3524 | 7236.1961 | 7898.78 | 8623.4545 | 9416.0604 | 10282.9663 | 11231.1055 | 12268.0095 | 13401.8366 | 14641.3904 | 15996.1218 | 17476.1054 |  | 2455.5711 | 2670.3395 | 2904.638 | 3160.2912 | 3439.2971 | 3743.8435 | 4076.3267 | 4439.3709 | 4835.8508 | 5268.9149 | 5742.0126 | 6258.9229 | 6823.7861 | 7441.1385 | 8115.9511 | 8853.671 | 9660.2676 | 10535.8697 | 11487.7844 | 12525.4179 | 13655.5145 | 14884.8813 | 16220.1487 | 17667.403 | 19231.6343 | 20915.9179 | 22720.2121 | 24639.6047 | 26661.7669 | 28763.2717
| TRUE | 476 | 22005268 | BC | Blank | 11 | CAP NO.1 | VOLTAGE BALANCE | Blank | RPL | GROUP_653 | GROUP 653 | GROUP 000s | Electronic |  | 0.2894 | 2190 |  | 5.5 | 0.0093284 | 0.0049035 | 0.0044248 | 40.5023 | 784.5676 | 825.0699 | 54.3183 | 3.7813 | 2271.9333 |  | 11.3746 | 0.062456 | 0.032831 | 0.029626 | 271.1756 | 5252.9309 | 5524.1065 | 363.6781 | 25.3171 | 15211.3198 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 21.3186 | 0.3278 | 21.6464 | 14.6814 | 2.0677 | 0.94924 |  | 3155.1027 | 21124.4214 | 39.3447 | 21085.0767 |  | 0.072663 |  | 5.9145 | 6.3603 | 6.8397 | 7.3552 | 7.9095 | 8.5056 | 9.1467 | 9.8361 | 10.5774 | 11.3746 | 12.2319 | 13.1538 | 14.1452 | 15.2113 | 16.3577 | 17.5906 | 18.9164 | 20.3421 | 21.8752 | 23.5239 | 25.2969 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.011168 | 0.013405 | 0.016132 | 0.019459 | 0.023524 | 0.028497 | 0.034586 | 0.04205 | 0.051208 | 0.062456 | 0.076283 | 0.093293 | 0.11423 | 0.14003 | 0.17183 | 0.21106 | 0.25948 | 0.31927 | 0.39314 | 0.48444 | 0.59735 | 0.73701 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0058703 | 0.0070466 | 0.00848 | 0.010229 | 0.012366 | 0.01498 | 0.01818 | 0.022104 | 0.026918 | 0.032831 | 0.040099 | 0.04904 | 0.060048 | 0.073609 | 0.090327 | 0.11095 | 0.1364 | 0.16783 | 0.20666 | 0.25465 | 0.314 | 0.38742 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 3777.1442 | 4534.0312 | 5456.3221 | 6581.6851 | 7956.5793 | 9638.3383 | 11697.752 | 14222.2663 | 17319.9512 | 21124.4214 | 25800.9392 | 31553.9853 | 38636.6538 | 47362.3089 | 58119.0543 | 71387.6932 | 87764.0256 | 107986.532 | 132970.7501 | 163851.9667 | 202038.2394 | 249276.2556 | 271013.3414 | 271013.3414 | 271013.3414 | 271013.3414 | 271013.3414 | 271013.3414 | 271013.3414 | 271013.3414 |  | 32.2417 | 32.2417 | 32.2417 | 32.2417 | 32.2417 | 32.2417 | 32.2417 | 32.2417 | 32.2417 | 32.2417 | 32.2417 | 32.2417 | 32.2417 | 32.2417 | 32.2417 | 32.2417 | 32.2417 | 38.5912 | 51.155 | 68.4011 | 92.1815 | 125.1056 | 170.8579 | 234.6481 | 323.8534 | 448.934 | 624.7381 | 872.3647 | 1221.8221 | 1715.825 |  | 48.4874 | 58.2037 | 70.0432 | 84.4895 | 102.1391 | 123.728 | 150.1648 | 182.5722 | 222.3374 | 271.1756 | 331.2084 | 405.0606 | 495.9813 | 607.9931 | 746.0781 | 916.4085 | 1126.6326 | 1386.2303 | 1706.9543 | 2103.3785 | 2593.5782 | 3199.9758 | 3479.0162 | 3479.0162 | 3479.0162 | 3479.0162 | 3479.0162 | 3479.0162 | 3479.0162 | 3479.0162 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 34.2751 | 43.9913 | 55.8308 | 70.2771 | 87.9267 | 109.5156 | 135.9524 | 168.3598 | 208.125 | 256.9632 | 316.996 | 390.8482 | 481.7689 | 593.7807 | 731.8658 | 902.1962 | 1112.4202 | 1369.2189 | 1684.4048 | 2073.2268 | 2552.9439 | 3144.8282 | 3403.7006 | 3375.5814 | 3336.2589 | 3281.1224 | 3203.6265 | 3094.4706 | 2940.4269 | 2722.6663 |  | 939.2483 | 1127.4606 | 1356.8032 | 1636.643 | 1978.5328 | 2396.7295 | 2908.8362 | 3536.5978 | 4306.8875 | 5252.9309 | 6415.823 | 7846.4115 | 9607.6322 | 11777.4082 | 14452.2478 | 17751.7107 | 21823.952 | 26852.607 | 33065.3391 | 40744.4557 | 50240.0933 | 61986.5941 | 67391.8739 | 67391.8739 | 67391.8739 | 67391.8739 | 67391.8739 | 67391.8739 | 67391.8739 | 67391.8739 |  | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.39236 | 0.52009 | 0.69543 | 0.93721 | 1.2719 | 1.7371 | 2.3857 | 3.2926 | 4.5643 | 6.3517 | 8.8693 | 12.4223 | 17.4448 |  | 938.9205 | 1127.1328 | 1356.4754 | 1636.3152 | 1978.205 | 2396.4017 | 2908.5084 | 3536.27 | 4306.5597 | 5252.6031 | 6415.4952 | 7846.0837 | 9607.3044 | 11777.0804 | 14451.92 | 17751.3829 | 21823.6242 | 26852.2146 | 33064.819 | 40743.7603 | 50239.1561 | 61985.3221 | 67390.1368 | 67389.4882 | 67388.5813 | 67387.3096 | 67385.5222 | 67383.0046 | 67379.4516 | 67374.4291 |  | 973.1956 | 1171.124 | 1412.3062 | 1706.5923 | 2066.1317 | 2505.9173 | 3044.4609 | 3704.6297 | 4514.6847 | 5509.5663 | 6732.4912 | 8236.9319 | 10089.0733 | 12370.8611 | 15183.7858 | 18653.579 | 22936.0444 | 28221.4335 | 34749.2238 | 42816.987 | 52792.1 | 65130.1503 | 70793.8374 | 70765.0696 | 70724.8402 | 70668.432 | 70589.1486 | 70477.4752 | 70319.8786 | 70097.0954 |  | 65.0273 | 78.0579 | 93.936 | 113.3103 | 136.9805 | 165.9336 | 201.3885 | 244.8506 | 298.1803 | 363.6781 | 444.189 | 543.2335 | 665.1687 | 815.3896 | 1000.5777 | 1229.0106 | 1510.9456 | 1859.0963 | 2289.2246 | 2820.8757 | 3478.2906 | 4291.5404 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 50.3459 | 63.3765 | 79.2546 | 98.6289 | 122.2991 | 151.2522 | 186.7071 | 230.1691 | 283.4989 | 348.9967 | 429.5076 | 528.552 | 650.4873 | 800.7082 | 985.8963 | 1214.3292 | 1496.2642 | 1841.5236 | 2265.9309 | 2789.7289 | 3436.3153 | 4234.5728 | 4587.965 | 4558.9178 | 4518.2976 | 4461.3415 | 4381.2881 | 4268.5299 | 4109.4026 | 3884.4555 |  | 4.5268 | 5.4339 | 6.5393 | 7.888 | 9.5358 | 11.5513 | 14.0195 | 17.0451 | 20.7576 | 25.3171 | 30.9218 | 37.8167 | 46.3051 | 56.7626 | 69.6544 | 85.5565 | 105.1832 | 129.4194 | 159.3624 | 196.3728 | 242.1382 | 298.7519 | 324.8033 | 324.8033 | 324.8033 | 324.8033 | 324.8033 | 324.8033 | 324.8033 | 324.8033 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 2.4591 | 3.3662 | 4.4716 | 5.8203 | 7.4681 | 9.4836 | 11.9518 | 14.9773 | 18.6899 | 23.2494 | 28.8541 | 35.749 | 44.2374 | 54.6949 | 67.5866 | 83.4888 | 103.1155 | 126.9445 | 156.0818 | 191.9862 | 236.2265 | 290.7287 | 313.8459 | 309.7549 | 304.034 | 296.0124 | 284.7378 | 268.8571 | 246.4458 | 214.7645 |  | 2719.8543 | 3264.8751 | 3929.0004 | 4739.3542 | 5729.3911 | 6940.3958 | 8423.343 | 10241.2007 | 12471.7885 | 15211.3198 | 18578.7969 | 22721.463 | 27821.5665 | 34104.7554 | 41850.4962 | 51405.0069 | 63197.3123 | 77759.179 | 95749.8697 | 117986.884 | 145484.1391 | 179499.3935 | 195151.8819 | 195151.8819 | 195151.8819 | 195151.8819 | 195151.8819 | 195151.8819 | 195151.8819 | 195151.8819 |  | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 0.94924 | 1.1362 | 1.5061 | 2.0138 | 2.7139 | 3.6833 | 5.0303 | 6.9084 | 9.5347 | 13.2172 | 18.3931 | 25.6836 | 35.9721 | 50.5162 |  | 2718.905 | 3263.9259 | 3928.0512 | 4738.405 | 5728.4418 | 6939.4466 | 8422.3937 | 10240.2515 | 12470.8393 | 15210.3705 | 18577.8477 | 22720.5138 | 27820.6173 | 34103.8061 | 41849.547 | 51404.0577 | 63196.363 | 77758.0429 | 95748.3636 | 117984.8702 | 145481.4251 | 179495.7102 | 195146.8516 | 195144.9736 | 195142.3473 | 195138.6647 | 195133.4888 | 195126.1983 | 195115.9098 | 195101.3657 |  | 3744.9056 | 4501.7926 | 5424.0836 | 6549.4465 | 7924.3407 | 9606.0998 | 11665.5135 | 14190.0277 | 17287.7127 | 21092.1829 | 25768.7006 | 31521.7468 | 38604.4152 | 47330.0703 | 58086.8157 | 71355.4547 | 87731.7871 | 107947.9444 | 132919.6001 | 163783.5722 | 201946.0668 | 249151.162 | 270842.4999 | 270778.7159 | 270689.5191 | 270564.4506 | 270388.6633 | 270141.0605 | 269791.6367 | 269297.6812
| FALSE | 477 | 22013376 | BC | Blank | 11 | CAP NO.1 | METER (DIGITAL MULTI FN.) | I | Schneider | ION_6200 | ION 6200 | ION 6000s | Digital |  | 0 | 1 |  | 2.3762 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 7.4134 | 0.023345 | 0 | 0.023345 | 64.1976 | 0 | 64.1976 | 66.2663 | 9.3402 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 139.804 | 30.9493 | 108.8547 |  | 0.11378 |  | 2.6625 | 2.9833 | 3.3429 | 3.7457 | 4.1971 | 4.7028 | 5.2696 | 5.9046 | 6.6161 | 7.4134 | 8.3068 | 9.3078 | 10.4294 | 11.6862 | 13.0945 | 14.6725 | 16.4406 | 18.4218 | 20.6417 | 23.1292 | 25.9164 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0057654 | 0.0075148 | 0.0098744 | 0.01307 | 0.017416 | 0.023345 | 0.031459 | 0.042597 | 0.057923 | 0.079063 | 0.10828 | 0.14874 | 0.20486 | 0.28283 | 0.39128 | 0.54232 | 0.7529 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 34.5273 | 45.004 | 59.1351 | 78.2752 | 104.2986 | 139.804 | 188.399 | 255.0991 | 346.8851 | 473.4848 | 648.4667 | 890.774 | 1226.8737 | 1693.7728 | 2343.2483 | 3247.7848 | 4508.9083 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 15.8548 | 20.6657 | 27.1547 | 35.9437 | 47.8936 | 64.1976 | 86.5123 | 117.1407 | 159.2886 | 217.4227 | 297.7739 | 409.0407 | 563.3766 | 777.7753 | 1076.0124 | 1491.3728 | 2070.4768 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 1.643 | 6.4539 | 12.9429 | 21.7319 | 33.6818 | 49.9858 | 72.3004 | 102.9289 | 145.0767 | 203.2109 | 283.5621 | 394.8288 | 549.1648 | 760.7646 | 1053.4638 | 1461.2222 | 2029.8441 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 1.643 | 6.4539 | 12.9429 | 21.7319 | 33.6818 | 49.9858 | 72.3004 | 102.9289 | 145.0767 | 203.2109 | 283.5621 | 394.8288 | 549.1648 | 760.7646 | 1053.4638 | 1461.2222 | 2029.8441 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 16.3657 | 21.3316 | 28.0297 | 37.102 | 49.4369 | 66.2663 | 89.3 | 120.9154 | 164.4215 | 224.429 | 307.3694 | 422.2216 | 581.5309 | 802.8383 | 1110.6859 | 1539.4308 | 2137.1959 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 1.696 | 6.6619 | 13.3599 | 22.4322 | 34.7671 | 51.5965 | 74.6302 | 106.2457 | 149.7517 | 209.7592 | 292.6996 | 407.5518 | 566.8611 | 785.2795 | 1087.4106 | 1508.3087 | 2095.2538 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.3067 | 3.0067 | 3.9508 | 5.2295 | 6.9681 | 9.3402 | 12.5867 | 17.0429 | 23.175 | 31.633 | 43.3234 | 59.5117 | 81.9662 | 113.1592 | 156.55 | 216.9812 | 301.2356 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0.23904 | 0.93898 | 1.8831 | 3.1618 | 4.9004 | 7.2725 | 10.5191 | 14.9752 | 21.1073 | 29.5653 | 41.2557 | 57.444 | 79.8985 | 110.6843 | 153.2694 | 212.5945 | 295.3239 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 3.578 | 14.0547 | 28.1858 | 47.3259 | 73.3493 | 108.8547 | 157.4497 | 224.1498 | 315.9358 | 442.5355 | 617.5174 | 859.8247 | 1195.9244 | 1656.7284 | 2294.1438 | 3182.1254 | 4420.4218 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 478 | 22013377 | BC | Blank | 11 | CAP NO.3 | METER (DIGITAL MULTI FN.) | I | Schneider | ION_6200 | ION 6200 | ION 6000s | Digital |  | 0 | 1 |  | 1.4709 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 4.8786 | 0.0081995 | 0 | 0.0081995 | 22.5486 | 0 | 22.5486 | 23.2752 | 3.2806 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 49.1045 | 30.9493 | 18.1552 |  | 0.11989 |  | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 132.6818 | 189.5929 | 266.6938 | 373.6462 | 524.8006 | 738.7495 | 1041.9903 | 1472.3087 | 2083.6164 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.7014 | 26.7229 | 37.5902 | 52.665 | 73.9701 | 104.126 | 146.8675 | 207.5204 | 293.6836 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 133.0601 | 194.2933 | 279.9229 | 399.9899 | 562.6522 | 788.2929 | 1107.188 | 1558.5626 | 2198.3191 | 3106.1752 | 4395.87 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 479 | 22013367 | BC | Blank | 11 | CB BT 1-2 | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 1.4709 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 4.8786 | 0.0081995 | 0 | 0.0081995 | 22.5486 | 0 | 22.5486 | 23.2752 | 3.2806 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 49.1045 | 30.9493 | 18.1552 |  | 0.11989 |  | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 132.6818 | 189.5929 | 266.6938 | 373.6462 | 524.8006 | 738.7495 | 1041.9903 | 1472.3087 | 2083.6164 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.7014 | 26.7229 | 37.5902 | 52.665 | 73.9701 | 104.126 | 146.8675 | 207.5204 | 293.6836 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 133.0601 | 194.2933 | 279.9229 | 399.9899 | 562.6522 | 788.2929 | 1107.188 | 1558.5626 | 2198.3191 | 3106.1752 | 4395.87 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 480 | 22013369 | BC | Blank | 11 | CB BT 2-3 | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 1.4709 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 4.8786 | 0.0081995 | 0 | 0.0081995 | 22.5486 | 0 | 22.5486 | 23.2752 | 3.2806 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 49.1045 | 30.9493 | 18.1552 |  | 0.11989 |  | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 132.6818 | 189.5929 | 266.6938 | 373.6462 | 524.8006 | 738.7495 | 1041.9903 | 1472.3087 | 2083.6164 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.7014 | 26.7229 | 37.5902 | 52.665 | 73.9701 | 104.126 | 146.8675 | 207.5204 | 293.6836 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 133.0601 | 194.2933 | 279.9229 | 399.9899 | 562.6522 | 788.2929 | 1107.188 | 1558.5626 | 2198.3191 | 3106.1752 | 4395.87 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 481 | 22013359 | BC | Blank | 11 | CB TR1 NO.1 11kV Bus | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 1.4709 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 4.8786 | 0.0081995 | 0 | 0.0081995 | 22.5486 | 0 | 22.5486 | 23.2752 | 3.2806 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 49.1045 | 30.9493 | 18.1552 |  | 0.11989 |  | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 132.6818 | 189.5929 | 266.6938 | 373.6462 | 524.8006 | 738.7495 | 1041.9903 | 1472.3087 | 2083.6164 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.7014 | 26.7229 | 37.5902 | 52.665 | 73.9701 | 104.126 | 146.8675 | 207.5204 | 293.6836 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 133.0601 | 194.2933 | 279.9229 | 399.9899 | 562.6522 | 788.2929 | 1107.188 | 1558.5626 | 2198.3191 | 3106.1752 | 4395.87 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 482 | 22013361 | BC | Blank | 11 | CB TR1 NO.2 11kV Bus | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 1.4709 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 4.8786 | 0.0081995 | 0 | 0.0081995 | 22.5486 | 0 | 22.5486 | 23.2752 | 3.2806 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 49.1045 | 30.9493 | 18.1552 |  | 0.11989 |  | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 132.6818 | 189.5929 | 266.6938 | 373.6462 | 524.8006 | 738.7495 | 1041.9903 | 1472.3087 | 2083.6164 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.7014 | 26.7229 | 37.5902 | 52.665 | 73.9701 | 104.126 | 146.8675 | 207.5204 | 293.6836 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 133.0601 | 194.2933 | 279.9229 | 399.9899 | 562.6522 | 788.2929 | 1107.188 | 1558.5626 | 2198.3191 | 3106.1752 | 4395.87 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 483 | 22013363 | BC | Blank | 11 | CB TR2 NO.2 11kV Bus | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 1.4709 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 4.8786 | 0.0081995 | 0 | 0.0081995 | 22.5486 | 0 | 22.5486 | 23.2752 | 3.2806 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 49.1045 | 30.9493 | 18.1552 |  | 0.11989 |  | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 132.6818 | 189.5929 | 266.6938 | 373.6462 | 524.8006 | 738.7495 | 1041.9903 | 1472.3087 | 2083.6164 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.7014 | 26.7229 | 37.5902 | 52.665 | 73.9701 | 104.126 | 146.8675 | 207.5204 | 293.6836 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 133.0601 | 194.2933 | 279.9229 | 399.9899 | 562.6522 | 788.2929 | 1107.188 | 1558.5626 | 2198.3191 | 3106.1752 | 4395.87 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 484 | 22013365 | BC | Blank | 11 | CB TR2 NO.3 11kV Bus | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 1.4709 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 4.8786 | 0.0081995 | 0 | 0.0081995 | 22.5486 | 0 | 22.5486 | 23.2752 | 3.2806 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 49.1045 | 30.9493 | 18.1552 |  | 0.11989 |  | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 132.6818 | 189.5929 | 266.6938 | 373.6462 | 524.8006 | 738.7495 | 1041.9903 | 1472.3087 | 2083.6164 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.7014 | 26.7229 | 37.5902 | 52.665 | 73.9701 | 104.126 | 146.8675 | 207.5204 | 293.6836 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 133.0601 | 194.2933 | 279.9229 | 399.9899 | 562.6522 | 788.2929 | 1107.188 | 1558.5626 | 2198.3191 | 3106.1752 | 4395.87 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 485 | 22013355 | BC | Blank | 11 | CB TR3 NO.1 11kV Bus | CB MGMT & CB FAIL | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0 | 1 |  | 1.7651 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 7.1689 | 0.021401 | 0 | 0.021401 | 58.8522 | 0 | 58.8522 | 60.7487 | 8.5625 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 128.1633 | 30.9493 | 97.214 |  | 0.14015 |  | 2.0307 | 2.3362 | 2.6877 | 3.0921 | 3.5573 | 4.0924 | 4.7082 | 5.4165 | 6.2314 | 7.1689 | 8.2475 | 9.4883 | 10.9158 | 12.5581 | 14.4475 | 16.6211 | 19.1217 | 21.9985 | 25.3082 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054426 | 0.0075349 | 0.01056 | 0.014961 | 0.021401 | 0.030869 | 0.044852 | 0.065583 | 0.096424 | 0.14244 | 0.21128 | 0.3145 | 0.46958 | 0.70298 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 32.5939 | 45.1243 | 63.2411 | 89.5993 | 128.1633 | 184.8664 | 268.6078 | 392.7608 | 577.4555 | 853.0362 | 1265.3035 | 1883.464 | 2812.1949 | 4209.9593 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.967 | 20.7209 | 29.0401 | 41.1437 | 58.8522 | 84.8901 | 123.3439 | 180.3546 | 265.1658 | 391.7116 | 581.0235 | 864.8809 | 1291.3513 | 1933.2004 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0.75521 | 6.5091 | 14.8283 | 26.9319 | 44.6404 | 70.6782 | 109.132 | 166.1427 | 250.954 | 377.4998 | 566.8116 | 850.669 | 1274.3406 | 1910.6517 | 2559.6896 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.75521 | 6.5091 | 14.8283 | 26.9319 | 44.6404 | 70.6782 | 109.132 | 166.1427 | 250.954 | 377.4998 | 566.8116 | 850.669 | 1274.3406 | 1910.6517 | 2559.6896 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 15.4493 | 21.3887 | 29.9759 | 42.4695 | 60.7487 | 87.6256 | 127.3185 | 186.1663 | 273.7105 | 404.3341 | 599.7464 | 892.7508 | 1332.9638 | 1995.4958 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0.77955 | 6.7189 | 15.3061 | 27.7998 | 46.0789 | 72.9558 | 112.6487 | 171.4965 | 259.0407 | 389.6643 | 585.0766 | 878.081 | 1315.405 | 1972.2206 | 2642.1731 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1776 | 3.0147 | 4.2251 | 5.986 | 8.5625 | 12.3507 | 17.9454 | 26.24 | 38.5792 | 56.9905 | 84.5336 | 125.8323 | 187.8799 | 281.2631 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0.10988 | 0.94702 | 2.1574 | 3.9183 | 6.4948 | 10.283 | 15.8777 | 24.1723 | 36.5115 | 54.9228 | 82.4659 | 123.7646 | 185.405 | 277.9825 | 372.4116 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1.6446 | 14.175 | 32.2918 | 58.65 | 97.214 | 153.9171 | 237.6585 | 361.8115 | 546.5062 | 822.0869 | 1234.3542 | 1852.5147 | 2775.1505 | 4160.8548 | 5574.2742 | 5551.4471 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 486 | 22013357 | BC | Blank | 11 | CB TR3 NO.3 11kV Bus | CB MGMT & CB FAIL | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0 | 1 |  | 1.7651 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 7.1689 | 0.021401 | 0 | 0.021401 | 58.8522 | 0 | 58.8522 | 60.7487 | 8.5625 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 128.1633 | 30.9493 | 97.214 |  | 0.14015 |  | 2.0307 | 2.3362 | 2.6877 | 3.0921 | 3.5573 | 4.0924 | 4.7082 | 5.4165 | 6.2314 | 7.1689 | 8.2475 | 9.4883 | 10.9158 | 12.5581 | 14.4475 | 16.6211 | 19.1217 | 21.9985 | 25.3082 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054426 | 0.0075349 | 0.01056 | 0.014961 | 0.021401 | 0.030869 | 0.044852 | 0.065583 | 0.096424 | 0.14244 | 0.21128 | 0.3145 | 0.46958 | 0.70298 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 32.5939 | 45.1243 | 63.2411 | 89.5993 | 128.1633 | 184.8664 | 268.6078 | 392.7608 | 577.4555 | 853.0362 | 1265.3035 | 1883.464 | 2812.1949 | 4209.9593 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.967 | 20.7209 | 29.0401 | 41.1437 | 58.8522 | 84.8901 | 123.3439 | 180.3546 | 265.1658 | 391.7116 | 581.0235 | 864.8809 | 1291.3513 | 1933.2004 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0.75521 | 6.5091 | 14.8283 | 26.9319 | 44.6404 | 70.6782 | 109.132 | 166.1427 | 250.954 | 377.4998 | 566.8116 | 850.669 | 1274.3406 | 1910.6517 | 2559.6896 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.75521 | 6.5091 | 14.8283 | 26.9319 | 44.6404 | 70.6782 | 109.132 | 166.1427 | 250.954 | 377.4998 | 566.8116 | 850.669 | 1274.3406 | 1910.6517 | 2559.6896 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 15.4493 | 21.3887 | 29.9759 | 42.4695 | 60.7487 | 87.6256 | 127.3185 | 186.1663 | 273.7105 | 404.3341 | 599.7464 | 892.7508 | 1332.9638 | 1995.4958 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0.77955 | 6.7189 | 15.3061 | 27.7998 | 46.0789 | 72.9558 | 112.6487 | 171.4965 | 259.0407 | 389.6643 | 585.0766 | 878.081 | 1315.405 | 1972.2206 | 2642.1731 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1776 | 3.0147 | 4.2251 | 5.986 | 8.5625 | 12.3507 | 17.9454 | 26.24 | 38.5792 | 56.9905 | 84.5336 | 125.8323 | 187.8799 | 281.2631 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0.10988 | 0.94702 | 2.1574 | 3.9183 | 6.4948 | 10.283 | 15.8777 | 24.1723 | 36.5115 | 54.9228 | 82.4659 | 123.7646 | 185.405 | 277.9825 | 372.4116 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1.6446 | 14.175 | 32.2918 | 58.65 | 97.214 | 153.9171 | 237.6585 | 361.8115 | 546.5062 | 822.0869 | 1234.3542 | 1852.5147 | 2775.1505 | 4160.8548 | 5574.2742 | 5551.4471 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 487 | 22013840 | BC | Blank | 11 | ALLFDRS | MASTER EARTH FAULT | Blank | English Electric | CMU_590B | CMU 590B | CMU | Electromechanical |  | 0.81881 | 2190 |  | 8.25 | 0.0054067 | 0.0043154 | 0.0010912 | 32.1101 | 1380.9353 | 1413.0455 | 39.8471 | 2.2064 | 1999.4408 |  | 11.265 | 0.01251 | 0.0099851 | 0.0025249 | 74.2968 | 3195.2247 | 3269.5215 | 92.1987 | 5.1051 | 4626.3301 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 28.4268 | 1.8549 | 30.2818 | 14.7027 | 2.0677 | 2.6857 |  | 3454.5397 | 7993.1554 | 49.7379 | 7943.4175 |  | 0.031148 |  | 8.511 | 8.7803 | 9.0581 | 9.3447 | 9.6403 | 9.9453 | 10.26 | 10.5846 | 10.9195 | 11.265 | 11.6214 | 11.9891 | 12.3684 | 12.7597 | 13.1634 | 13.5799 | 14.0095 | 14.4528 | 14.91 | 15.3818 | 15.8684 | 16.3705 | 16.8884 | 17.4227 | 17.974 | 18.5426 | 19.1293 | 19.7345 | 20.3589 | 21.003 |  | 0.0058713 | 0.0063781 | 0.006931 | 0.0075342 | 0.0081926 | 0.0089113 | 0.0096958 | 0.010553 | 0.011488 | 0.01251 | 0.013626 | 0.014846 | 0.016179 | 0.017636 | 0.019228 | 0.020969 | 0.022872 | 0.024954 | 0.02723 | 0.02972 | 0.032443 | 0.035422 | 0.038682 | 0.042249 | 0.046153 | 0.050426 | 0.055102 | 0.060222 | 0.065826 | 0.071963 |  | 0.0046863 | 0.0050908 | 0.0055321 | 0.0060136 | 0.0065391 | 0.0071127 | 0.0077389 | 0.0084227 | 0.0091694 | 0.0099851 | 0.010876 | 0.01185 | 0.012914 | 0.014076 | 0.015347 | 0.016737 | 0.018256 | 0.019917 | 0.021734 | 0.023721 | 0.025895 | 0.028273 | 0.030875 | 0.033722 | 0.036838 | 0.040248 | 0.043981 | 0.048067 | 0.052541 | 0.057438 | 3751.4174 | 4075.2284 | 4428.4852 | 4813.9389 | 5234.6019 | 5693.7731 | 6195.065 | 6742.4345 | 7340.2155 | 7993.1554 | 8706.4549 | 9485.8115 | 10337.4676 | 11268.263 | 12285.6922 | 13397.968 | 14614.0908 | 15943.9245 | 17398.2798 | 18989.0061 | 20729.0919 | 22632.7746 | 24715.6619 | 26994.8642 | 29489.1399 | 32219.0558 | 35207.1615 | 38478.1821 | 42059.2293 | 45980.0324 |  | 35.5421 | 35.5421 | 35.5421 | 35.5421 | 35.5421 | 35.5421 | 35.5421 | 35.5421 | 35.5421 | 35.5421 | 35.5421 | 35.5421 | 35.5421 | 35.5421 | 35.5421 | 35.5421 | 35.5421 | 42.5416 | 56.3914 | 75.403 | 101.6176 | 137.912 | 188.3478 | 258.6678 | 357.0045 | 494.889 | 688.6893 | 961.6641 | 1346.8936 | 1891.4651 |  | 34.8696 | 37.8795 | 41.163 | 44.7458 | 48.6559 | 52.924 | 57.5835 | 62.6713 | 68.2277 | 74.2968 | 80.927 | 88.1712 | 96.0874 | 104.7392 | 114.1962 | 124.5349 | 135.8388 | 148.1997 | 161.718 | 176.5039 | 192.6781 | 210.373 | 229.7335 | 250.9188 | 274.1033 | 299.478 | 327.2526 | 357.6569 | 390.943 | 427.3871 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 20.6562 | 23.6661 | 26.9496 | 30.5324 | 34.4425 | 38.7105 | 43.3701 | 48.4579 | 54.0143 | 60.0834 | 66.7136 | 73.9578 | 81.8739 | 90.5257 | 99.9828 | 110.3215 | 121.6254 | 131.1871 | 139.1669 | 146.3499 | 152.0408 | 155.2214 | 154.4125 | 147.4765 | 131.3357 | 101.5698 | 51.8429 | -26.9165 | -147.6853 | -329.0177 |  | 1499.6107 | 1629.0526 | 1770.2652 | 1924.3485 | 2092.5064 | 2276.0579 | 2476.4468 | 2695.2551 | 2934.2151 | 3195.2247 | 3480.3626 | 3791.9066 | 4132.352 | 4504.4328 | 4911.1452 | 5355.772 | 5841.9111 | 6373.5056 | 6954.877 | 7590.762 | 8286.3528 | 9047.3406 | 9879.9646 | 10791.0645 | 11788.139 | 12879.4095 | 14073.8901 | 15381.4645 | 16812.9706 | 18380.2924 |  | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 2.2202 | 2.9431 | 3.9353 | 5.3034 | 7.1976 | 9.8298 | 13.4998 | 18.632 | 25.8281 | 35.9425 | 50.189 | 70.294 | 98.7151 |  | 1497.7558 | 1627.1976 | 1768.4103 | 1922.4935 | 2090.6515 | 2274.2029 | 2474.5919 | 2693.4002 | 2932.3602 | 3193.3697 | 3478.5077 | 3790.0517 | 4130.497 | 4502.5779 | 4909.2902 | 5353.9171 | 5840.0562 | 6371.2854 | 6951.9339 | 7586.8268 | 8281.0494 | 9040.143 | 9870.1348 | 10777.5647 | 11769.5071 | 12853.5814 | 14037.9476 | 15331.2755 | 16742.6765 | 18281.5773 |  | 1518.412 | 1650.8637 | 1795.3599 | 1953.0259 | 2125.094 | 2312.9135 | 2517.962 | 2741.8581 | 2986.3745 | 3253.4532 | 3545.2213 | 3864.0094 | 4212.371 | 4593.1037 | 5009.2731 | 5464.2385 | 5961.6816 | 6502.4725 | 7091.1008 | 7733.1767 | 8433.0902 | 9195.3644 | 10024.5473 | 10925.0413 | 11900.8427 | 12955.1512 | 14089.7905 | 15304.359 | 16594.9912 | 17952.5597 |  | 43.2715 | 47.0066 | 51.0813 | 55.5274 | 60.3796 | 65.676 | 71.4583 | 77.772 | 84.6672 | 92.1987 | 100.4264 | 109.4161 | 119.2397 | 129.9761 | 141.7119 | 154.5416 | 168.5693 | 183.9085 | 200.6841 | 219.0326 | 239.104 | 261.0624 | 285.0879 | 311.3779 | 340.1486 | 371.6374 | 406.1043 | 443.8346 | 485.1409 | 530.3662 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 28.5688 | 32.3039 | 36.3786 | 40.8247 | 45.6769 | 50.9733 | 56.7556 | 63.0693 | 69.9645 | 77.496 | 85.7237 | 94.7134 | 104.537 | 115.2734 | 127.0092 | 139.839 | 153.8666 | 166.3103 | 177.3566 | 187.8407 | 197.0678 | 204.0123 | 207.1741 | 204.3747 | 192.4665 | 166.9165 | 121.214 | 46.0227 | -72.0289 | -252.0766 |  | 2.396 | 2.6028 | 2.8284 | 3.0746 | 3.3433 | 3.6365 | 3.9567 | 4.3063 | 4.6881 | 5.1051 | 5.5607 | 6.0584 | 6.6024 | 7.1969 | 7.8467 | 8.5571 | 9.3338 | 10.1831 | 11.112 | 12.128 | 13.2394 | 14.4552 | 15.7855 | 17.2412 | 18.8343 | 20.5778 | 22.4863 | 24.5754 | 26.8626 | 29.3667 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 0.32822 | 0.53504 | 0.76066 | 1.0068 | 1.2755 | 1.5688 | 1.8889 | 2.2385 | 2.6203 | 3.0374 | 3.4929 | 3.9907 | 4.5346 | 5.1291 | 5.7789 | 6.4893 | 7.266 | 7.7082 | 7.8313 | 7.7412 | 7.3275 | 6.4318 | 4.8279 | 2.1926 | -1.9354 | -8.2136 | -17.58 | -31.3718 | -51.4963 | -80.674 |  | 2171.2696 | 2358.687 | 2563.1472 | 2786.2426 | 3029.7167 | 3295.4787 | 3585.6197 | 3902.4298 | 4248.4173 | 4626.3301 | 5039.1782 | 5490.2592 | 5983.1862 | 6521.918 | 7110.7922 | 7754.5624 | 8458.4378 | 9228.1275 | 10069.8887 | 10990.5795 | 11997.7176 | 13099.5434 | 14305.0903 | 15624.2617 | 17067.9148 | 18647.9531 | 20377.4282 | 22270.6506 | 24343.3122 | 26612.6199 |  | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 3.2147 | 4.2612 | 5.6978 | 7.6787 | 10.4213 | 14.2325 | 19.5462 | 26.977 | 37.3963 | 52.0408 | 72.6681 | 101.7779 | 142.9285 |  | 2168.5839 | 2356.0012 | 2560.4615 | 2783.5569 | 3027.031 | 3292.793 | 3582.934 | 3899.744 | 4245.7316 | 4623.6444 | 5036.4924 | 5487.5735 | 5980.5005 | 6519.2322 | 7108.1065 | 7751.8767 | 8455.7521 | 9224.9129 | 10065.6274 | 10984.8817 | 11990.0389 | 13089.122 | 14290.8578 | 15604.7155 | 17040.9377 | 18610.5568 | 20325.3874 | 22197.9825 | 24241.5342 | 26469.6915 |  | 3715.8929 | 4039.7038 | 4392.9606 | 4778.4144 | 5199.0774 | 5658.2485 | 6159.5405 | 6706.91 | 7304.691 | 7957.6309 | 8670.9304 | 9450.287 | 10301.9431 | 11232.7384 | 12250.1676 | 13362.4435 | 14578.5663 | 15901.4038 | 17341.9162 | 18913.6403 | 20627.5244 | 22494.9306 | 24527.4071 | 26736.324 | 29132.3115 | 31724.411 | 34518.812 | 37516.9924 | 40713.0002 | 44089.5005
| TRUE | 488 | 22013848 | BC | BC011 | 11 | BC11 | SENSITIVE EF | Blank | RPL | ARTC_650 | ARTC 650 | AVE | Electromechanical |  | 0.57434 | 2190 |  | 2.5292 | 0.00090442 | 0.00065051 | 0.00025391 | 2.6661 | 52.0408 | 54.7069 | 6.2604 | 0.36836 | 360.9407 |  | 4.7392 | 0.0013394 | 0.00096335 | 0.00037602 | 3.9482 | 77.0677 | 81.0159 | 9.2711 | 0.54551 | 534.52 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 2.256 |  | 422.2764 | 625.3525 | 33.5548 | 591.7977 |  | 0.062797 |  | 2.6931 | 2.8677 | 3.0535 | 3.2514 | 3.4622 | 3.6865 | 3.9255 | 4.1799 | 4.4508 | 4.7392 | 5.0464 | 5.3734 | 5.7217 | 6.0925 | 6.4874 | 6.9078 | 7.3555 | 7.8322 | 8.3398 | 8.8804 | 9.4559 | 10.0687 | 10.7213 | 11.4161 | 12.156 | 12.9438 | 13.7827 | 14.676 | 15.6272 | 16.64 |  | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00099954 | 0.0011556 | 0.0013394 | 0.0015562 | 0.0018123 | 0.0021153 | 0.002474 | 0.0028992 | 0.0034038 | 0.0040031 | 0.0047157 | 0.0055637 | 0.0065737 | 0.0077776 | 0.0092136 | 0.010928 | 0.012976 | 0.015423 | 0.018351 | 0.021854 | 0.026048 | 0.031073 | 0.037095 |  | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00071893 | 0.00083114 | 0.00096335 | 0.0011193 | 0.0013035 | 0.0015214 | 0.0017794 | 0.0020853 | 0.0024482 | 0.0028793 | 0.0033918 | 0.0040017 | 0.0047282 | 0.005594 | 0.006627 | 0.00786 | 0.0093328 | 0.011093 | 0.013199 | 0.015719 | 0.018735 | 0.022349 | 0.02668 | 422.2764 | 422.2764 | 422.2764 | 422.2764 | 422.2764 | 422.2764 | 422.2764 | 466.6888 | 539.533 | 625.3525 | 726.5956 | 846.1886 | 987.631 | 1155.1104 | 1353.6399 | 1589.2241 | 1869.0582 | 2201.7681 | 2597.6989 | 3069.2624 | 3631.3555 | 4301.8637 | 5102.2678 | 6058.3747 | 7201.1974 | 8568.0152 | 10203.6519 | 12162.0155 | 14507.9536 | 17319.4909 |  | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 40.163 | 53.2385 | 71.1871 | 95.936 | 130.2011 | 177.8169 | 244.2051 | 337.0437 | 467.2188 | 650.1833 | 907.8956 | 1271.5861 | 1785.7096 |  | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.9465 | 3.4064 | 3.9482 | 4.5874 | 5.3424 | 6.2354 | 7.2928 | 8.5462 | 10.0336 | 11.8003 | 13.9009 | 16.4006 | 19.3779 | 22.9267 | 27.1599 | 32.2133 | 38.2497 | 45.4649 | 54.0944 | 64.421 | 76.7852 | 91.5963 | 109.347 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.2665 | -10.8066 | -10.2648 | -9.6256 | -8.8705 | -7.9775 | -6.9201 | -5.6667 | -4.1793 | -2.4126 | -3.1111 | -6.1498 | -10.7751 | -17.7093 | -27.9898 | -43.1052 | -65.1891 | -97.2979 | -143.8071 | -210.9795 | -307.7754 | -447.014 | -647.0324 |  | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 57.5142 | 66.4914 | 77.0677 | 89.5448 | 104.2833 | 121.7144 | 142.3544 | 166.8209 | 195.854 | 230.3405 | 271.3432 | 320.1373 | 378.2522 | 447.5238 | 530.1564 | 628.7973 | 746.6267 | 887.4668 | 1055.9118 | 1257.4856 | 1498.832 | 1787.9425 | 2134.433 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.38933 | 0.51609 | 0.69008 | 0.92999 | 1.2621 | 1.7237 | 2.3673 | 3.2672 | 4.5291 | 6.3028 | 8.801 | 12.3265 | 17.3104 |  | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 57.1889 | 66.1661 | 76.7424 | 89.2195 | 103.958 | 121.3892 | 142.0291 | 166.4957 | 195.5288 | 230.0152 | 270.9539 | 319.6212 | 377.5621 | 446.5938 | 528.8943 | 627.0735 | 744.2594 | 884.1996 | 1051.3826 | 1251.1829 | 1490.031 | 1775.616 | 2117.1226 |  | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 45.9224 | 55.3595 | 66.4776 | 79.5939 | 95.0875 | 113.4117 | 135.109 | 160.829 | 191.3494 | 227.6026 | 267.8428 | 313.4714 | 366.787 | 428.8846 | 500.9045 | 583.9683 | 679.0703 | 786.9017 | 907.5755 | 1040.2034 | 1182.2556 | 1328.602 | 1470.0902 |  | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.9188 | 7.9988 | 9.2711 | 10.7721 | 12.5451 | 14.642 | 17.1249 | 20.0682 | 23.5608 | 27.7095 | 32.642 | 38.5119 | 45.503 | 53.8362 | 63.7768 | 75.643 | 89.8177 | 106.7605 | 127.0241 | 151.273 | 180.3065 | 215.0859 | 256.768 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -7.774 | -6.6941 | -5.4218 | -3.9208 | -2.1478 | -0.050867 | 2.4321 | 5.3754 | 8.868 | 13.0166 | 15.0556 | 15.2 | 14.3318 | 11.8281 | 6.7648 | -2.2188 | -17.114 | -40.823 | -77.56 | -133.4269 | -217.2395 | -341.7116 | -525.152 |  | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.40711 | 0.47065 | 0.54551 | 0.63383 | 0.73816 | 0.86154 | 1.0076 | 1.1808 | 1.3863 | 1.6304 | 1.9207 | 2.2661 | 2.6774 | 3.1677 | 3.7526 | 4.4509 | 5.2849 | 6.2818 | 7.4741 | 8.901 | 10.6093 | 12.6557 | 15.1083 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6606 | -1.5971 | -1.5222 | -1.4339 | -1.3296 | -1.2062 | -1.0601 | -0.88691 | -0.6814 | -0.4373 | -0.55428 | -1.0146 | -1.7093 | -2.7441 | -4.2707 | -6.5066 | -9.7636 | -14.4876 | -21.317 | -31.1649 | -45.3375 | -65.7025 | -94.9315 |  | 360.9407 | 360.9407 | 360.9407 | 360.9407 | 360.9407 | 360.9407 | 360.9407 | 398.9022 | 461.1658 | 534.52 | 621.0576 | 723.2797 | 844.1776 | 987.3306 | 1157.0237 | 1358.3893 | 1597.5775 | 1881.9612 | 2220.3831 | 2623.452 | 3103.9011 | 3677.0179 | 4361.1633 | 5178.3957 | 6155.2233 | 7323.5108 | 8721.5713 | 10395.4825 | 12400.6731 | 14803.8346 |  | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.7003 | 3.5794 | 4.7862 | 6.4501 | 8.7539 | 11.9553 | 16.4188 | 22.6607 | 31.4129 | 43.7143 | 61.0412 | 85.4935 | 120.06 |  | 358.6847 | 358.6847 | 358.6847 | 358.6847 | 358.6847 | 358.6847 | 358.6847 | 396.6462 | 458.9098 | 532.264 | 618.8016 | 721.0237 | 841.9216 | 985.0746 | 1154.7677 | 1356.1332 | 1595.3214 | 1879.2609 | 2216.8037 | 2618.6658 | 3097.4509 | 3668.264 | 4349.208 | 5161.9769 | 6132.5626 | 7292.098 | 8677.8571 | 10334.4413 | 12315.1796 | 14683.7746 |  | 388.7216 | 388.7216 | 388.7216 | 388.7216 | 388.7216 | 388.7216 | 388.7216 | 433.1339 | 505.9782 | 591.7977 | 693.0408 | 812.6337 | 954.0762 | 1121.5556 | 1320.0851 | 1555.6692 | 1835.5033 | 2161.6051 | 2544.4604 | 2998.0754 | 3535.4196 | 4171.6626 | 4924.451 | 5814.1696 | 6864.1537 | 8100.7964 | 9553.4686 | 11254.1199 | 13236.3675 | 15533.7814
| TRUE | 489 | 22005269 | BC | BC011 | 11 | BC11 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 3512.6854 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 8742.518 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 2.256 |  | 5654.9402 | 14074.2512 | 48.7436 | 14025.5076 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 6186.4504 | 6770.1359 | 7411.2387 | 8115.5348 | 8889.3894 | 9739.8175 | 10674.5507 | 11702.1111 | 12831.8926 | 14074.2512 | 15440.6037 | 16943.5377 | 18596.9321 | 20416.0906 | 22417.8892 | 24620.9383 | 27045.7623 | 29714.9978 | 32653.6119 | 35889.1435 | 39451.9701 | 43375.6014 | 47697.0041 | 52456.9602 | 57700.4629 | 63477.1532 | 69841.8023 | 76854.844 | 84582.9625 | 93099.7417 |  | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 41.3458 | 54.8063 | 73.2834 | 98.7611 | 134.0353 | 183.0532 | 251.3965 | 346.969 | 480.9775 | 669.33 | 934.6314 | 1309.0319 | 1838.2953 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 3842.8442 | 4205.4127 | 4603.6473 | 5041.1357 | 5521.8318 | 6050.0931 | 6630.7224 | 7269.0132 | 7970.8008 | 8742.518 | 9591.2567 | 10524.8359 | 11551.8767 | 12681.8854 | 13925.3448 | 15293.8152 | 16800.0458 | 18458.0977 | 20283.4798 | 22293.2986 | 24506.4235 | 26943.6699 | 29628.0003 | 32584.7474 | 35841.8597 | 39430.1728 | 43383.7088 | 47740.0076 | 52540.4914 | 57830.8685 |  | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.7003 | 3.5794 | 4.7862 | 6.4501 | 8.7539 | 11.9553 | 16.4188 | 22.6607 | 31.4129 | 43.7143 | 61.0412 | 85.4935 | 120.06 |  | 3840.5881 | 4203.1567 | 4601.3913 | 5038.8796 | 5519.5758 | 6047.8371 | 6628.4663 | 7266.7571 | 7968.5448 | 8740.262 | 9589.0007 | 10522.5799 | 11549.6207 | 12679.6294 | 13923.0888 | 15291.5592 | 16797.7898 | 18455.3974 | 20279.9004 | 22288.5124 | 24499.9734 | 26934.9159 | 29616.045 | 32568.3286 | 35819.199 | 39398.7599 | 43339.9945 | 47678.9664 | 52454.9979 | 57710.8085 |  | 6151.9197 | 6735.6053 | 7376.7081 | 8081.0042 | 8854.8588 | 9705.2869 | 10640.0201 | 11667.5804 | 12797.3619 | 14039.7205 | 15406.0731 | 16909.007 | 18562.4014 | 20381.56 | 22383.3586 | 24586.4076 | 27011.2317 | 29673.6668 | 32598.8251 | 35815.8862 | 39353.2442 | 43241.6139 | 47514.016 | 52205.6532 | 57353.6174 | 62996.347 | 69172.7106 | 75920.5454 | 83274.3967 | 91262.101
| TRUE | 490 | 22005270 | BC | BC011 | 11 | BC11 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 3512.6854 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 8742.518 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 2.256 |  | 5654.9402 | 14074.2512 | 48.7436 | 14025.5076 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 6186.4504 | 6770.1359 | 7411.2387 | 8115.5348 | 8889.3894 | 9739.8175 | 10674.5507 | 11702.1111 | 12831.8926 | 14074.2512 | 15440.6037 | 16943.5377 | 18596.9321 | 20416.0906 | 22417.8892 | 24620.9383 | 27045.7623 | 29714.9978 | 32653.6119 | 35889.1435 | 39451.9701 | 43375.6014 | 47697.0041 | 52456.9602 | 57700.4629 | 63477.1532 | 69841.8023 | 76854.844 | 84582.9625 | 93099.7417 |  | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 41.3458 | 54.8063 | 73.2834 | 98.7611 | 134.0353 | 183.0532 | 251.3965 | 346.969 | 480.9775 | 669.33 | 934.6314 | 1309.0319 | 1838.2953 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 3842.8442 | 4205.4127 | 4603.6473 | 5041.1357 | 5521.8318 | 6050.0931 | 6630.7224 | 7269.0132 | 7970.8008 | 8742.518 | 9591.2567 | 10524.8359 | 11551.8767 | 12681.8854 | 13925.3448 | 15293.8152 | 16800.0458 | 18458.0977 | 20283.4798 | 22293.2986 | 24506.4235 | 26943.6699 | 29628.0003 | 32584.7474 | 35841.8597 | 39430.1728 | 43383.7088 | 47740.0076 | 52540.4914 | 57830.8685 |  | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.7003 | 3.5794 | 4.7862 | 6.4501 | 8.7539 | 11.9553 | 16.4188 | 22.6607 | 31.4129 | 43.7143 | 61.0412 | 85.4935 | 120.06 |  | 3840.5881 | 4203.1567 | 4601.3913 | 5038.8796 | 5519.5758 | 6047.8371 | 6628.4663 | 7266.7571 | 7968.5448 | 8740.262 | 9589.0007 | 10522.5799 | 11549.6207 | 12679.6294 | 13923.0888 | 15291.5592 | 16797.7898 | 18455.3974 | 20279.9004 | 22288.5124 | 24499.9734 | 26934.9159 | 29616.045 | 32568.3286 | 35819.199 | 39398.7599 | 43339.9945 | 47678.9664 | 52454.9979 | 57710.8085 |  | 6151.9197 | 6735.6053 | 7376.7081 | 8081.0042 | 8854.8588 | 9705.2869 | 10640.0201 | 11667.5804 | 12797.3619 | 14039.7205 | 15406.0731 | 16909.007 | 18562.4014 | 20381.56 | 22383.3586 | 24586.4076 | 27011.2317 | 29673.6668 | 32598.8251 | 35815.8862 | 39353.2442 | 43241.6139 | 47514.016 | 52205.6532 | 57353.6174 | 62996.347 | 69172.7106 | 75920.5454 | 83274.3967 | 91262.101
| TRUE | 491 | 22015698 | BC | BC011 | 11 | BC11 | AUTO RECLOSE | Blank | English Electric | GROUP_624 | GROUP 624 | GROUP 000s | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 53.114 | 1051.8847 | 1104.9987 | 45.1415 | 3.7652 | 1823.895 |  | 7.1791 | 0.018276 | 0.00644 | 0.011836 | 104.0585 | 2060.8049 | 2164.8634 | 88.4392 | 7.3765 | 3573.2926 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 28.4243 | 0.35573 | 28.78 | 14.6761 | 2.0677 | 0.61681 |  | 2977.8004 | 5833.9718 | 46.1406 | 5787.8312 |  | 0.026643 |  | 5.6485 | 5.801 | 5.9577 | 6.1185 | 6.2837 | 6.4534 | 6.6277 | 6.8066 | 6.9904 | 7.1791 | 7.373 | 7.5721 | 7.7765 | 7.9865 | 8.2022 | 8.4236 | 8.6511 | 8.8847 | 9.1246 | 9.3709 | 9.624 | 9.8838 | 10.1507 | 10.4248 | 10.7063 | 10.9954 | 11.2923 | 11.5972 | 11.9103 | 12.2319 |  | 0.0099614 | 0.010641 | 0.011372 | 0.012157 | 0.013001 | 0.013908 | 0.014884 | 0.015933 | 0.017062 | 0.018276 | 0.019582 | 0.020988 | 0.022502 | 0.024131 | 0.025885 | 0.027774 | 0.029809 | 0.032001 | 0.034362 | 0.036906 | 0.039648 | 0.042603 | 0.045789 | 0.049223 | 0.052926 | 0.056919 | 0.061224 | 0.065869 | 0.070879 | 0.076283 |  | 0.0035102 | 0.0037498 | 0.0040073 | 0.0042839 | 0.0045813 | 0.004901 | 0.0052448 | 0.0056145 | 0.0060122 | 0.00644 | 0.0069004 | 0.0073958 | 0.0079291 | 0.0085032 | 0.0091214 | 0.0097871 | 0.010504 | 0.011276 | 0.012109 | 0.013005 | 0.013971 | 0.015013 | 0.016135 | 0.017345 | 0.01865 | 0.020057 | 0.021574 | 0.023211 | 0.024976 | 0.026881 | 3179.8724 | 3396.9403 | 3630.1647 | 3880.7985 | 4150.194 | 4439.8112 | 4751.2265 | 5086.142 | 5446.3954 | 5833.9718 | 6251.0147 | 6699.8395 | 7182.9469 | 7703.0388 | 8263.0335 | 8866.0844 | 9515.5983 | 10215.2564 | 10969.0368 | 11781.2382 | 12656.5065 | 13599.8628 | 14616.7344 | 15712.9874 | 16894.9632 | 18169.5167 | 19544.0589 | 21026.6019 | 22625.8083 | 24351.0446 |  | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 38.2204 | 50.6634 | 67.7438 | 91.2957 | 123.9035 | 169.2161 | 232.3933 | 320.7414 | 444.62 | 618.7348 | 863.9819 | 1210.0812 | 1699.3372 |  | 56.7183 | 60.59 | 64.75 | 69.2205 | 74.0256 | 79.1914 | 84.746 | 90.7197 | 97.1455 | 104.0585 | 111.4972 | 119.5027 | 128.1197 | 137.3964 | 147.3849 | 158.1413 | 169.7264 | 182.206 | 195.6509 | 210.1379 | 225.7497 | 242.576 | 260.7136 | 280.2671 | 301.3496 | 324.0834 | 348.6006 | 375.0442 | 403.5687 | 434.3411 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 42.5062 | 46.3779 | 50.5379 | 55.0083 | 59.8134 | 64.9792 | 70.5338 | 76.5076 | 82.9333 | 89.8464 | 97.2851 | 105.2906 | 113.9076 | 123.1843 | 133.1727 | 143.9291 | 155.5143 | 165.195 | 173.1018 | 179.9866 | 185.1161 | 187.4294 | 185.3994 | 176.8342 | 158.5949 | 126.1931 | 73.2159 | -9.4944 | -135.0108 | -321.995 |  | 1123.265 | 1199.9426 | 1282.3273 | 1370.8617 | 1466.0235 | 1568.3286 | 1678.3336 | 1796.6398 | 1923.8966 | 2060.8049 | 2208.122 | 2366.6659 | 2537.3198 | 2721.0382 | 2918.8519 | 3131.8749 | 3361.3106 | 3608.4594 | 3874.7264 | 4161.6302 | 4470.8119 | 4804.0451 | 5163.247 | 5550.4898 | 5968.0135 | 6418.2396 | 6903.7858 | 7427.4825 | 7992.3897 | 8601.8159 |  | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.42579 | 0.56441 | 0.75469 | 1.0171 | 1.3803 | 1.8851 | 2.5889 | 3.5732 | 4.9532 | 6.8929 | 9.625 | 13.4807 | 18.9311 |  | 1122.9093 | 1199.5868 | 1281.9715 | 1370.506 | 1465.6678 | 1567.9728 | 1677.9779 | 1796.2841 | 1923.5408 | 2060.4492 | 2207.7663 | 2366.3101 | 2536.9641 | 2720.6824 | 2918.4962 | 3131.5192 | 3360.9549 | 3608.0336 | 3874.162 | 4160.8755 | 4469.7948 | 4802.6648 | 5161.3619 | 5547.9009 | 5964.4404 | 6413.2864 | 6896.8929 | 7417.8575 | 7978.909 | 8582.8848 |  | 1165.4155 | 1245.9648 | 1332.5094 | 1425.5143 | 1525.4813 | 1632.9521 | 1748.5117 | 1872.7917 | 2006.4742 | 2150.2956 | 2305.0513 | 2471.6007 | 2650.8717 | 2843.8667 | 3051.6689 | 3275.4483 | 3516.4692 | 3773.2285 | 4047.2638 | 4340.8621 | 4654.9109 | 4990.0942 | 5346.7613 | 5724.7351 | 6123.0353 | 6539.4795 | 6970.1088 | 7408.3631 | 7843.8982 | 8260.8898 |  | 48.2048 | 51.4954 | 55.031 | 58.8304 | 62.9143 | 67.3047 | 72.0255 | 77.1026 | 82.5638 | 88.4392 | 94.7613 | 101.5652 | 108.8888 | 116.7731 | 125.2623 | 134.4041 | 144.2503 | 154.8567 | 166.2835 | 178.596 | 191.8645 | 206.1651 | 221.5803 | 238.1987 | 256.1167 | 275.4381 | 296.2753 | 318.7497 | 342.9926 | 369.1461 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 33.5287 | 36.8193 | 40.3549 | 44.1543 | 48.2382 | 52.6286 | 57.3494 | 62.4265 | 67.8877 | 73.7631 | 80.0852 | 86.8891 | 94.2127 | 102.097 | 110.5862 | 119.728 | 129.5742 | 137.2903 | 142.9983 | 147.4604 | 149.9043 | 149.2182 | 143.8073 | 131.3892 | 108.7017 | 71.0876 | 11.9004 | -78.3425 | -213.1693 | -411.8813 |  | 4.0207 | 4.2951 | 4.59 | 4.9069 | 5.2475 | 5.6137 | 6.0075 | 6.431 | 6.8865 | 7.3765 | 7.9038 | 8.4713 | 9.0822 | 9.7398 | 10.4478 | 11.2103 | 12.0316 | 12.9163 | 13.8693 | 14.8963 | 16.003 | 17.1958 | 18.4815 | 19.8676 | 21.3621 | 22.9737 | 24.7117 | 26.5862 | 28.6083 | 30.7897 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 1.953 | 2.2274 | 2.5223 | 2.8392 | 3.1798 | 3.546 | 3.9398 | 4.3633 | 4.8188 | 5.3088 | 5.8361 | 6.4036 | 7.0145 | 7.6721 | 8.3801 | 9.1426 | 9.9639 | 10.4413 | 10.5887 | 10.5096 | 10.0913 | 9.1726 | 7.5242 | 4.8193 | 0.59296 | -5.8171 | -15.3537 | -29.3598 | -49.7489 | -79.2486 |  | 1947.6636 | 2080.6171 | 2223.4665 | 2376.979 | 2541.9831 | 2719.3729 | 2910.114 | 3115.2488 | 3335.9031 | 3573.2926 | 3828.7303 | 4103.6343 | 4399.5364 | 4718.0913 | 5061.0866 | 5430.4537 | 5828.2793 | 6256.8181 | 6718.5066 | 7215.9779 | 7752.0775 | 8329.8808 | 8952.712 | 9624.1641 | 10348.1212 | 11128.782 | 11970.6855 | 12878.7392 | 13858.249 | 14914.9518 |  | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.73828 | 0.97864 | 1.3086 | 1.7635 | 2.3934 | 3.2687 | 4.489 | 6.1956 | 8.5885 | 11.9518 | 16.6891 | 23.3746 | 32.8253 |  | 1947.0468 | 2080.0003 | 2222.8497 | 2376.3622 | 2541.3663 | 2718.7561 | 2909.4971 | 3114.632 | 3335.2863 | 3572.6758 | 3828.1135 | 4103.0175 | 4398.9196 | 4717.4745 | 5060.4698 | 5429.8369 | 5827.6625 | 6256.0798 | 6717.528 | 7214.6693 | 7750.3139 | 8327.4874 | 8949.4433 | 9619.6751 | 10341.9256 | 11120.1934 | 11958.7337 | 12862.0501 | 13834.8745 | 14882.1265 |  | 3147.944 | 3365.0118 | 3598.2363 | 3848.87 | 4118.2655 | 4407.8828 | 4719.2981 | 5054.2135 | 5414.467 | 5802.0434 | 6219.0863 | 6667.911 | 7151.0185 | 7671.1103 | 8231.1051 | 8834.1559 | 9483.6698 | 10177.04 | 10918.3787 | 11713.5015 | 12565.2204 | 13475.9724 | 14447.5361 | 15480.6186 | 16574.2556 | 17724.9435 | 18925.3892 | 20162.7109 | 21415.8545 | 22651.8863
| TRUE | 492 | 22013849 | BC | BC012 | 11 | BC12 | SENSITIVE EF | Blank | RPL | ARTC_650 | ARTC 650 | AVE | Electromechanical |  | 0.57434 | 2190 |  | 2.5292 | 0.00090442 | 0.00065051 | 0.00025391 | 2.6661 | 52.0408 | 54.7069 | 6.2604 | 0.36836 | 721.8815 |  | 4.7392 | 0.0013394 | 0.00096335 | 0.00037602 | 3.9482 | 77.0677 | 81.0159 | 9.2711 | 0.54551 | 1069.0401 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 4.512 |  | 783.2171 | 1159.8726 | 35.8109 | 1124.0617 |  | 0.062797 |  | 2.6931 | 2.8677 | 3.0535 | 3.2514 | 3.4622 | 3.6865 | 3.9255 | 4.1799 | 4.4508 | 4.7392 | 5.0464 | 5.3734 | 5.7217 | 6.0925 | 6.4874 | 6.9078 | 7.3555 | 7.8322 | 8.3398 | 8.8804 | 9.4559 | 10.0687 | 10.7213 | 11.4161 | 12.156 | 12.9438 | 13.7827 | 14.676 | 15.6272 | 16.64 |  | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00099954 | 0.0011556 | 0.0013394 | 0.0015562 | 0.0018123 | 0.0021153 | 0.002474 | 0.0028992 | 0.0034038 | 0.0040031 | 0.0047157 | 0.0055637 | 0.0065737 | 0.0077776 | 0.0092136 | 0.010928 | 0.012976 | 0.015423 | 0.018351 | 0.021854 | 0.026048 | 0.031073 | 0.037095 |  | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00071893 | 0.00083114 | 0.00096335 | 0.0011193 | 0.0013035 | 0.0015214 | 0.0017794 | 0.0020853 | 0.0024482 | 0.0028793 | 0.0033918 | 0.0040017 | 0.0047282 | 0.005594 | 0.006627 | 0.00786 | 0.0093328 | 0.011093 | 0.013199 | 0.015719 | 0.018735 | 0.022349 | 0.02668 | 783.2171 | 783.2171 | 783.2171 | 783.2171 | 783.2171 | 783.2171 | 783.2171 | 865.591 | 1000.6988 | 1159.8726 | 1347.6532 | 1569.4683 | 1831.8086 | 2142.441 | 2510.6636 | 2947.6133 | 3466.6356 | 4083.7293 | 4818.082 | 5692.7145 | 6735.2566 | 7978.8816 | 9463.4312 | 11236.7705 | 13356.4207 | 15891.526 | 18925.2233 | 22557.498 | 26908.6267 | 32123.3255 |  | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 42.8633 | 56.8179 | 75.9732 | 102.3861 | 138.955 | 189.7722 | 260.624 | 359.7044 | 498.6316 | 693.8976 | 968.9368 | 1357.0797 | 1905.7696 |  | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.9465 | 3.4064 | 3.9482 | 4.5874 | 5.3424 | 6.2354 | 7.2928 | 8.5462 | 10.0336 | 11.8003 | 13.9009 | 16.4006 | 19.3779 | 22.9267 | 27.1599 | 32.2133 | 38.2497 | 45.4649 | 54.0944 | 64.421 | 76.7852 | 91.5963 | 109.347 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.2665 | -10.8066 | -10.2648 | -9.6256 | -8.8705 | -7.9775 | -6.9201 | -5.6667 | -4.1793 | -2.4126 | -3.1111 | -6.1498 | -10.7751 | -17.7093 | -27.9898 | -43.1052 | -65.1891 | -97.2979 | -143.8071 | -210.9795 | -307.7754 | -447.014 | -647.0324 |  | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 57.5142 | 66.4914 | 77.0677 | 89.5448 | 104.2833 | 121.7144 | 142.3544 | 166.8209 | 195.854 | 230.3405 | 271.3432 | 320.1373 | 378.2522 | 447.5238 | 530.1564 | 628.7973 | 746.6267 | 887.4668 | 1055.9118 | 1257.4856 | 1498.832 | 1787.9425 | 2134.433 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.38933 | 0.51609 | 0.69008 | 0.92999 | 1.2621 | 1.7237 | 2.3673 | 3.2672 | 4.5291 | 6.3028 | 8.801 | 12.3265 | 17.3104 |  | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 57.1889 | 66.1661 | 76.7424 | 89.2195 | 103.958 | 121.3892 | 142.0291 | 166.4957 | 195.5288 | 230.0152 | 270.9539 | 319.6212 | 377.5621 | 446.5938 | 528.8943 | 627.0735 | 744.2594 | 884.1996 | 1051.3826 | 1251.1829 | 1490.031 | 1775.616 | 2117.1226 |  | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 45.9224 | 55.3595 | 66.4776 | 79.5939 | 95.0875 | 113.4117 | 135.109 | 160.829 | 191.3494 | 227.6026 | 267.8428 | 313.4714 | 366.787 | 428.8846 | 500.9045 | 583.9683 | 679.0703 | 786.9017 | 907.5755 | 1040.2034 | 1182.2556 | 1328.602 | 1470.0902 |  | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.9188 | 7.9988 | 9.2711 | 10.7721 | 12.5451 | 14.642 | 17.1249 | 20.0682 | 23.5608 | 27.7095 | 32.642 | 38.5119 | 45.503 | 53.8362 | 63.7768 | 75.643 | 89.8177 | 106.7605 | 127.0241 | 151.273 | 180.3065 | 215.0859 | 256.768 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -7.774 | -6.6941 | -5.4218 | -3.9208 | -2.1478 | -0.050867 | 2.4321 | 5.3754 | 8.868 | 13.0166 | 15.0556 | 15.2 | 14.3318 | 11.8281 | 6.7648 | -2.2188 | -17.114 | -40.823 | -77.56 | -133.4269 | -217.2395 | -341.7116 | -525.152 |  | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.40711 | 0.47065 | 0.54551 | 0.63383 | 0.73816 | 0.86154 | 1.0076 | 1.1808 | 1.3863 | 1.6304 | 1.9207 | 2.2661 | 2.6774 | 3.1677 | 3.7526 | 4.4509 | 5.2849 | 6.2818 | 7.4741 | 8.901 | 10.6093 | 12.6557 | 15.1083 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6606 | -1.5971 | -1.5222 | -1.4339 | -1.3296 | -1.2062 | -1.0601 | -0.88691 | -0.6814 | -0.4373 | -0.55428 | -1.0146 | -1.7093 | -2.7441 | -4.2707 | -6.5066 | -9.7636 | -14.4876 | -21.317 | -31.1649 | -45.3375 | -65.7025 | -94.9315 |  | 721.8815 | 721.8815 | 721.8815 | 721.8815 | 721.8815 | 721.8815 | 721.8815 | 797.8044 | 922.3316 | 1069.0401 | 1242.1152 | 1446.5594 | 1688.3552 | 1974.6612 | 2314.0474 | 2716.7785 | 3195.1549 | 3763.9225 | 4440.7662 | 5246.904 | 6207.8021 | 7354.0358 | 8722.3267 | 10356.7914 | 12310.4467 | 14647.0217 | 17443.1427 | 20790.9651 | 24801.3462 | 29607.6692 |  | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 5.4006 | 7.1588 | 9.5723 | 12.9003 | 17.5078 | 23.9106 | 32.8377 | 45.3214 | 62.8258 | 87.4285 | 122.0825 | 170.987 | 240.12 |  | 717.3694 | 717.3694 | 717.3694 | 717.3694 | 717.3694 | 717.3694 | 717.3694 | 793.2924 | 917.8196 | 1064.5281 | 1237.6031 | 1442.0473 | 1683.8432 | 1970.1492 | 2309.5353 | 2712.2665 | 3190.6429 | 3758.5219 | 4433.6074 | 5237.3317 | 6194.9019 | 7336.528 | 8698.4161 | 10323.9538 | 12265.1252 | 14584.1959 | 17355.7141 | 20668.8826 | 24630.3592 | 29367.5492 |  | 747.4063 | 747.4063 | 747.4063 | 747.4063 | 747.4063 | 747.4063 | 747.4063 | 829.7801 | 964.8879 | 1124.0617 | 1311.8423 | 1533.6574 | 1795.9978 | 2106.6301 | 2474.8527 | 2911.8025 | 3430.8248 | 4040.866 | 4761.2641 | 5616.7412 | 6632.8705 | 7839.9266 | 9273.659 | 10976.1465 | 12996.7163 | 15392.8944 | 18231.3257 | 21588.5612 | 25551.5471 | 30217.556
| TRUE | 493 | 22005271 | BC | BC012 | 11 | BC12 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 7025.3708 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 17485.036 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 4.512 |  | 9167.6256 | 22816.7692 | 50.9996 | 22765.7696 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 10029.2945 | 10975.5487 | 12014.886 | 13156.6705 | 14411.2212 | 15789.9107 | 17305.2731 | 18971.1242 | 20802.6934 | 22816.7692 | 25031.8604 | 27468.3736 | 30148.8088 | 33097.976 | 36343.234 | 39914.7535 | 43845.8081 | 48173.0955 | 52937.0917 | 58182.4421 | 63958.3937 | 70319.2713 | 77325.0043 | 85041.7076 | 93542.3226 | 102907.3259 | 113225.5111 | 124594.8516 | 137123.4539 | 150930.6102 |  | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 44.0461 | 58.3857 | 78.0696 | 105.2112 | 142.7892 | 195.0085 | 267.8153 | 369.6297 | 512.3903 | 713.0442 | 995.6726 | 1394.5254 | 1958.3552 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 7685.6883 | 8410.8255 | 9207.2945 | 10082.2713 | 11043.6635 | 12100.1863 | 13261.4447 | 14538.0263 | 15941.6016 | 17485.036 | 19182.5134 | 21049.6718 | 23103.7534 | 25363.7708 | 27850.6896 | 30587.6304 | 33600.0916 | 36916.1955 | 40566.9597 | 44586.5972 | 49012.847 | 53887.3397 | 59256.0005 | 65169.4948 | 71683.7194 | 78860.3455 | 86767.4176 | 95480.0152 | 105080.9829 | 115661.737 |  | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 5.4006 | 7.1588 | 9.5723 | 12.9003 | 17.5078 | 23.9106 | 32.8377 | 45.3214 | 62.8258 | 87.4285 | 122.0825 | 170.987 | 240.12 |  | 7681.1763 | 8406.3135 | 9202.7825 | 10077.7593 | 11039.1515 | 12095.6742 | 13256.9327 | 14533.5143 | 15937.0895 | 17480.524 | 19178.0014 | 21045.1597 | 23099.2413 | 25359.2587 | 27846.1776 | 30583.1184 | 33595.5796 | 36910.7948 | 40559.8008 | 44577.0248 | 48999.9468 | 53869.8319 | 59232.0899 | 65136.6572 | 71638.398 | 78797.5198 | 86679.9891 | 95357.9327 | 104909.9959 | 115421.6171 |  | 9992.5079 | 10938.762 | 11978.0993 | 13119.8838 | 14374.4345 | 15753.124 | 17268.4864 | 18934.3375 | 20765.9067 | 22779.9825 | 24995.0738 | 27431.5869 | 30112.0221 | 33061.1894 | 36306.4473 | 39877.9668 | 43809.0214 | 48129.0642 | 52878.7255 | 58104.3987 | 63853.2176 | 70176.5298 | 77130.061 | 84773.9818 | 93172.8164 | 102395.1069 | 112512.7052 | 123599.5117 | 135729.3946 | 148972.9095
| TRUE | 494 | 22005272 | BC | BC012 | 11 | BC12 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 7025.3708 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 17485.036 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 4.512 |  | 9167.6256 | 22816.7692 | 50.9996 | 22765.7696 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 10029.2945 | 10975.5487 | 12014.886 | 13156.6705 | 14411.2212 | 15789.9107 | 17305.2731 | 18971.1242 | 20802.6934 | 22816.7692 | 25031.8604 | 27468.3736 | 30148.8088 | 33097.976 | 36343.234 | 39914.7535 | 43845.8081 | 48173.0955 | 52937.0917 | 58182.4421 | 63958.3937 | 70319.2713 | 77325.0043 | 85041.7076 | 93542.3226 | 102907.3259 | 113225.5111 | 124594.8516 | 137123.4539 | 150930.6102 |  | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 44.0461 | 58.3857 | 78.0696 | 105.2112 | 142.7892 | 195.0085 | 267.8153 | 369.6297 | 512.3903 | 713.0442 | 995.6726 | 1394.5254 | 1958.3552 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 7685.6883 | 8410.8255 | 9207.2945 | 10082.2713 | 11043.6635 | 12100.1863 | 13261.4447 | 14538.0263 | 15941.6016 | 17485.036 | 19182.5134 | 21049.6718 | 23103.7534 | 25363.7708 | 27850.6896 | 30587.6304 | 33600.0916 | 36916.1955 | 40566.9597 | 44586.5972 | 49012.847 | 53887.3397 | 59256.0005 | 65169.4948 | 71683.7194 | 78860.3455 | 86767.4176 | 95480.0152 | 105080.9829 | 115661.737 |  | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 5.4006 | 7.1588 | 9.5723 | 12.9003 | 17.5078 | 23.9106 | 32.8377 | 45.3214 | 62.8258 | 87.4285 | 122.0825 | 170.987 | 240.12 |  | 7681.1763 | 8406.3135 | 9202.7825 | 10077.7593 | 11039.1515 | 12095.6742 | 13256.9327 | 14533.5143 | 15937.0895 | 17480.524 | 19178.0014 | 21045.1597 | 23099.2413 | 25359.2587 | 27846.1776 | 30583.1184 | 33595.5796 | 36910.7948 | 40559.8008 | 44577.0248 | 48999.9468 | 53869.8319 | 59232.0899 | 65136.6572 | 71638.398 | 78797.5198 | 86679.9891 | 95357.9327 | 104909.9959 | 115421.6171 |  | 9992.5079 | 10938.762 | 11978.0993 | 13119.8838 | 14374.4345 | 15753.124 | 17268.4864 | 18934.3375 | 20765.9067 | 22779.9825 | 24995.0738 | 27431.5869 | 30112.0221 | 33061.1894 | 36306.4473 | 39877.9668 | 43809.0214 | 48129.0642 | 52878.7255 | 58104.3987 | 63853.2176 | 70176.5298 | 77130.061 | 84773.9818 | 93172.8164 | 102395.1069 | 112512.7052 | 123599.5117 | 135729.3946 | 148972.9095
| TRUE | 495 | 22015699 | BC | BC012 | 11 | BC12 | AUTO RECLOSE | Blank | English Electric | GROUP_624 | GROUP 624 | GROUP 000s | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 53.114 | 1051.8847 | 1104.9987 | 45.1415 | 3.7652 | 3647.7901 |  | 7.1791 | 0.018276 | 0.00644 | 0.011836 | 104.0585 | 2060.8049 | 2164.8634 | 88.4392 | 7.3765 | 7146.5853 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 28.4243 | 0.35573 | 28.78 | 14.6761 | 2.0677 | 1.2336 |  | 4801.6954 | 9407.2645 | 46.7574 | 9360.5071 |  | 0.026643 |  | 5.6485 | 5.801 | 5.9577 | 6.1185 | 6.2837 | 6.4534 | 6.6277 | 6.8066 | 6.9904 | 7.1791 | 7.373 | 7.5721 | 7.7765 | 7.9865 | 8.2022 | 8.4236 | 8.6511 | 8.8847 | 9.1246 | 9.3709 | 9.624 | 9.8838 | 10.1507 | 10.4248 | 10.7063 | 10.9954 | 11.2923 | 11.5972 | 11.9103 | 12.2319 |  | 0.0099614 | 0.010641 | 0.011372 | 0.012157 | 0.013001 | 0.013908 | 0.014884 | 0.015933 | 0.017062 | 0.018276 | 0.019582 | 0.020988 | 0.022502 | 0.024131 | 0.025885 | 0.027774 | 0.029809 | 0.032001 | 0.034362 | 0.036906 | 0.039648 | 0.042603 | 0.045789 | 0.049223 | 0.052926 | 0.056919 | 0.061224 | 0.065869 | 0.070879 | 0.076283 |  | 0.0035102 | 0.0037498 | 0.0040073 | 0.0042839 | 0.0045813 | 0.004901 | 0.0052448 | 0.0056145 | 0.0060122 | 0.00644 | 0.0069004 | 0.0073958 | 0.0079291 | 0.0085032 | 0.0091214 | 0.0097871 | 0.010504 | 0.011276 | 0.012109 | 0.013005 | 0.013971 | 0.015013 | 0.016135 | 0.017345 | 0.01865 | 0.020057 | 0.021574 | 0.023211 | 0.024976 | 0.026881 | 5127.536 | 5477.5575 | 5853.6312 | 6257.7775 | 6692.1771 | 7159.1841 | 7661.3405 | 8201.3908 | 8782.2986 | 9407.2645 | 10079.7451 | 10803.4738 | 11582.4833 | 12421.1301 | 13324.1202 | 14296.5381 | 15343.8776 | 16472.0745 | 17687.5434 | 18997.2161 | 20408.5839 | 21929.7436 | 23569.4463 | 25337.1515 | 27243.0844 | 29298.2987 | 31514.7444 | 33905.3411 | 36484.0573 | 39265.9964 |  | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 38.9587 | 51.642 | 69.0524 | 93.0592 | 126.2968 | 172.4848 | 236.8823 | 326.937 | 453.2085 | 630.6866 | 880.671 | 1233.4558 | 1732.1625 |  | 56.7183 | 60.59 | 64.75 | 69.2205 | 74.0256 | 79.1914 | 84.746 | 90.7197 | 97.1455 | 104.0585 | 111.4972 | 119.5027 | 128.1197 | 137.3964 | 147.3849 | 158.1413 | 169.7264 | 182.206 | 195.6509 | 210.1379 | 225.7497 | 242.576 | 260.7136 | 280.2671 | 301.3496 | 324.0834 | 348.6006 | 375.0442 | 403.5687 | 434.3411 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 42.5062 | 46.3779 | 50.5379 | 55.0083 | 59.8134 | 64.9792 | 70.5338 | 76.5076 | 82.9333 | 89.8464 | 97.2851 | 105.2906 | 113.9076 | 123.1843 | 133.1727 | 143.9291 | 155.5143 | 165.195 | 173.1018 | 179.9866 | 185.1161 | 187.4294 | 185.3994 | 176.8342 | 158.5949 | 126.1931 | 73.2159 | -9.4944 | -135.0108 | -321.995 |  | 1123.265 | 1199.9426 | 1282.3273 | 1370.8617 | 1466.0235 | 1568.3286 | 1678.3336 | 1796.6398 | 1923.8966 | 2060.8049 | 2208.122 | 2366.6659 | 2537.3198 | 2721.0382 | 2918.8519 | 3131.8749 | 3361.3106 | 3608.4594 | 3874.7264 | 4161.6302 | 4470.8119 | 4804.0451 | 5163.247 | 5550.4898 | 5968.0135 | 6418.2396 | 6903.7858 | 7427.4825 | 7992.3897 | 8601.8159 |  | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.42579 | 0.56441 | 0.75469 | 1.0171 | 1.3803 | 1.8851 | 2.5889 | 3.5732 | 4.9532 | 6.8929 | 9.625 | 13.4807 | 18.9311 |  | 1122.9093 | 1199.5868 | 1281.9715 | 1370.506 | 1465.6678 | 1567.9728 | 1677.9779 | 1796.2841 | 1923.5408 | 2060.4492 | 2207.7663 | 2366.3101 | 2536.9641 | 2720.6824 | 2918.4962 | 3131.5192 | 3360.9549 | 3608.0336 | 3874.162 | 4160.8755 | 4469.7948 | 4802.6648 | 5161.3619 | 5547.9009 | 5964.4404 | 6413.2864 | 6896.8929 | 7417.8575 | 7978.909 | 8582.8848 |  | 1165.4155 | 1245.9648 | 1332.5094 | 1425.5143 | 1525.4813 | 1632.9521 | 1748.5117 | 1872.7917 | 2006.4742 | 2150.2956 | 2305.0513 | 2471.6007 | 2650.8717 | 2843.8667 | 3051.6689 | 3275.4483 | 3516.4692 | 3773.2285 | 4047.2638 | 4340.8621 | 4654.9109 | 4990.0942 | 5346.7613 | 5724.7351 | 6123.0353 | 6539.4795 | 6970.1088 | 7408.3631 | 7843.8982 | 8260.8898 |  | 48.2048 | 51.4954 | 55.031 | 58.8304 | 62.9143 | 67.3047 | 72.0255 | 77.1026 | 82.5638 | 88.4392 | 94.7613 | 101.5652 | 108.8888 | 116.7731 | 125.2623 | 134.4041 | 144.2503 | 154.8567 | 166.2835 | 178.596 | 191.8645 | 206.1651 | 221.5803 | 238.1987 | 256.1167 | 275.4381 | 296.2753 | 318.7497 | 342.9926 | 369.1461 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 33.5287 | 36.8193 | 40.3549 | 44.1543 | 48.2382 | 52.6286 | 57.3494 | 62.4265 | 67.8877 | 73.7631 | 80.0852 | 86.8891 | 94.2127 | 102.097 | 110.5862 | 119.728 | 129.5742 | 137.2903 | 142.9983 | 147.4604 | 149.9043 | 149.2182 | 143.8073 | 131.3892 | 108.7017 | 71.0876 | 11.9004 | -78.3425 | -213.1693 | -411.8813 |  | 4.0207 | 4.2951 | 4.59 | 4.9069 | 5.2475 | 5.6137 | 6.0075 | 6.431 | 6.8865 | 7.3765 | 7.9038 | 8.4713 | 9.0822 | 9.7398 | 10.4478 | 11.2103 | 12.0316 | 12.9163 | 13.8693 | 14.8963 | 16.003 | 17.1958 | 18.4815 | 19.8676 | 21.3621 | 22.9737 | 24.7117 | 26.5862 | 28.6083 | 30.7897 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 1.953 | 2.2274 | 2.5223 | 2.8392 | 3.1798 | 3.546 | 3.9398 | 4.3633 | 4.8188 | 5.3088 | 5.8361 | 6.4036 | 7.0145 | 7.6721 | 8.3801 | 9.1426 | 9.9639 | 10.4413 | 10.5887 | 10.5096 | 10.0913 | 9.1726 | 7.5242 | 4.8193 | 0.59296 | -5.8171 | -15.3537 | -29.3598 | -49.7489 | -79.2486 |  | 3895.3273 | 4161.2343 | 4446.933 | 4753.9581 | 5083.9661 | 5438.7458 | 5820.2279 | 6230.4976 | 6671.8062 | 7146.5853 | 7657.4607 | 8207.2686 | 8799.0728 | 9436.1826 | 10122.1733 | 10860.9075 | 11656.5586 | 12513.6362 | 13437.0133 | 14431.9558 | 15504.1549 | 16659.7615 | 17905.4239 | 19248.3282 | 20696.2424 | 22257.5639 | 23941.371 | 25757.4784 | 27716.498 | 29829.9036 |  | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.4766 | 1.9573 | 2.6171 | 3.527 | 4.7868 | 6.5373 | 8.9781 | 12.3912 | 17.177 | 23.9036 | 33.3782 | 46.7491 | 65.6505 |  | 3894.0936 | 4160.0007 | 4445.6994 | 4752.7244 | 5082.7325 | 5437.5121 | 5818.9943 | 6229.264 | 6670.5726 | 7145.3517 | 7656.2271 | 8206.035 | 8797.8392 | 9434.949 | 10120.9397 | 10859.6739 | 11655.325 | 12512.1597 | 13435.056 | 14429.3386 | 15500.6279 | 16654.9748 | 17898.8866 | 19239.3502 | 20683.8512 | 22240.3869 | 23917.4674 | 25724.1002 | 27669.7489 | 29764.253 |  | 5094.9908 | 5445.0122 | 5821.0859 | 6225.2322 | 6659.6318 | 7126.6388 | 7628.7952 | 8168.8455 | 8749.7533 | 9374.7192 | 10047.1998 | 10770.9285 | 11549.9381 | 12388.5848 | 13291.5749 | 14263.9928 | 15311.3323 | 16433.1199 | 17635.9067 | 18928.1708 | 20315.5344 | 21803.4598 | 23396.9794 | 25100.2937 | 26916.1812 | 28845.1369 | 30884.1229 | 33024.761 | 35250.729 | 37534.0129
| TRUE | 496 | 22013850 | BC | BC013 | 11 | BC13 | SENSITIVE EF | Blank | RPL | ARTC_650 | ARTC 650 | AVE | Electromechanical |  | 0.57434 | 2190 |  | 2.5292 | 0.00090442 | 0.00065051 | 0.00025391 | 2.6661 | 52.0408 | 54.7069 | 6.2604 | 0.36836 | 360.9407 |  | 4.7392 | 0.0013394 | 0.00096335 | 0.00037602 | 3.9482 | 77.0677 | 81.0159 | 9.2711 | 0.54551 | 534.52 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 2.256 |  | 422.2764 | 625.3525 | 33.5548 | 591.7977 |  | 0.062797 |  | 2.6931 | 2.8677 | 3.0535 | 3.2514 | 3.4622 | 3.6865 | 3.9255 | 4.1799 | 4.4508 | 4.7392 | 5.0464 | 5.3734 | 5.7217 | 6.0925 | 6.4874 | 6.9078 | 7.3555 | 7.8322 | 8.3398 | 8.8804 | 9.4559 | 10.0687 | 10.7213 | 11.4161 | 12.156 | 12.9438 | 13.7827 | 14.676 | 15.6272 | 16.64 |  | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00099954 | 0.0011556 | 0.0013394 | 0.0015562 | 0.0018123 | 0.0021153 | 0.002474 | 0.0028992 | 0.0034038 | 0.0040031 | 0.0047157 | 0.0055637 | 0.0065737 | 0.0077776 | 0.0092136 | 0.010928 | 0.012976 | 0.015423 | 0.018351 | 0.021854 | 0.026048 | 0.031073 | 0.037095 |  | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00071893 | 0.00083114 | 0.00096335 | 0.0011193 | 0.0013035 | 0.0015214 | 0.0017794 | 0.0020853 | 0.0024482 | 0.0028793 | 0.0033918 | 0.0040017 | 0.0047282 | 0.005594 | 0.006627 | 0.00786 | 0.0093328 | 0.011093 | 0.013199 | 0.015719 | 0.018735 | 0.022349 | 0.02668 | 422.2764 | 422.2764 | 422.2764 | 422.2764 | 422.2764 | 422.2764 | 422.2764 | 466.6888 | 539.533 | 625.3525 | 726.5956 | 846.1886 | 987.631 | 1155.1104 | 1353.6399 | 1589.2241 | 1869.0582 | 2201.7681 | 2597.6989 | 3069.2624 | 3631.3555 | 4301.8637 | 5102.2678 | 6058.3747 | 7201.1974 | 8568.0152 | 10203.6519 | 12162.0155 | 14507.9536 | 17319.4909 |  | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 40.163 | 53.2385 | 71.1871 | 95.936 | 130.2011 | 177.8169 | 244.2051 | 337.0437 | 467.2188 | 650.1833 | 907.8956 | 1271.5861 | 1785.7096 |  | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.9465 | 3.4064 | 3.9482 | 4.5874 | 5.3424 | 6.2354 | 7.2928 | 8.5462 | 10.0336 | 11.8003 | 13.9009 | 16.4006 | 19.3779 | 22.9267 | 27.1599 | 32.2133 | 38.2497 | 45.4649 | 54.0944 | 64.421 | 76.7852 | 91.5963 | 109.347 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.2665 | -10.8066 | -10.2648 | -9.6256 | -8.8705 | -7.9775 | -6.9201 | -5.6667 | -4.1793 | -2.4126 | -3.1111 | -6.1498 | -10.7751 | -17.7093 | -27.9898 | -43.1052 | -65.1891 | -97.2979 | -143.8071 | -210.9795 | -307.7754 | -447.014 | -647.0324 |  | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 57.5142 | 66.4914 | 77.0677 | 89.5448 | 104.2833 | 121.7144 | 142.3544 | 166.8209 | 195.854 | 230.3405 | 271.3432 | 320.1373 | 378.2522 | 447.5238 | 530.1564 | 628.7973 | 746.6267 | 887.4668 | 1055.9118 | 1257.4856 | 1498.832 | 1787.9425 | 2134.433 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.38933 | 0.51609 | 0.69008 | 0.92999 | 1.2621 | 1.7237 | 2.3673 | 3.2672 | 4.5291 | 6.3028 | 8.801 | 12.3265 | 17.3104 |  | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 57.1889 | 66.1661 | 76.7424 | 89.2195 | 103.958 | 121.3892 | 142.0291 | 166.4957 | 195.5288 | 230.0152 | 270.9539 | 319.6212 | 377.5621 | 446.5938 | 528.8943 | 627.0735 | 744.2594 | 884.1996 | 1051.3826 | 1251.1829 | 1490.031 | 1775.616 | 2117.1226 |  | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 45.9224 | 55.3595 | 66.4776 | 79.5939 | 95.0875 | 113.4117 | 135.109 | 160.829 | 191.3494 | 227.6026 | 267.8428 | 313.4714 | 366.787 | 428.8846 | 500.9045 | 583.9683 | 679.0703 | 786.9017 | 907.5755 | 1040.2034 | 1182.2556 | 1328.602 | 1470.0902 |  | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.9188 | 7.9988 | 9.2711 | 10.7721 | 12.5451 | 14.642 | 17.1249 | 20.0682 | 23.5608 | 27.7095 | 32.642 | 38.5119 | 45.503 | 53.8362 | 63.7768 | 75.643 | 89.8177 | 106.7605 | 127.0241 | 151.273 | 180.3065 | 215.0859 | 256.768 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -7.774 | -6.6941 | -5.4218 | -3.9208 | -2.1478 | -0.050867 | 2.4321 | 5.3754 | 8.868 | 13.0166 | 15.0556 | 15.2 | 14.3318 | 11.8281 | 6.7648 | -2.2188 | -17.114 | -40.823 | -77.56 | -133.4269 | -217.2395 | -341.7116 | -525.152 |  | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.40711 | 0.47065 | 0.54551 | 0.63383 | 0.73816 | 0.86154 | 1.0076 | 1.1808 | 1.3863 | 1.6304 | 1.9207 | 2.2661 | 2.6774 | 3.1677 | 3.7526 | 4.4509 | 5.2849 | 6.2818 | 7.4741 | 8.901 | 10.6093 | 12.6557 | 15.1083 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6606 | -1.5971 | -1.5222 | -1.4339 | -1.3296 | -1.2062 | -1.0601 | -0.88691 | -0.6814 | -0.4373 | -0.55428 | -1.0146 | -1.7093 | -2.7441 | -4.2707 | -6.5066 | -9.7636 | -14.4876 | -21.317 | -31.1649 | -45.3375 | -65.7025 | -94.9315 |  | 360.9407 | 360.9407 | 360.9407 | 360.9407 | 360.9407 | 360.9407 | 360.9407 | 398.9022 | 461.1658 | 534.52 | 621.0576 | 723.2797 | 844.1776 | 987.3306 | 1157.0237 | 1358.3893 | 1597.5775 | 1881.9612 | 2220.3831 | 2623.452 | 3103.9011 | 3677.0179 | 4361.1633 | 5178.3957 | 6155.2233 | 7323.5108 | 8721.5713 | 10395.4825 | 12400.6731 | 14803.8346 |  | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.7003 | 3.5794 | 4.7862 | 6.4501 | 8.7539 | 11.9553 | 16.4188 | 22.6607 | 31.4129 | 43.7143 | 61.0412 | 85.4935 | 120.06 |  | 358.6847 | 358.6847 | 358.6847 | 358.6847 | 358.6847 | 358.6847 | 358.6847 | 396.6462 | 458.9098 | 532.264 | 618.8016 | 721.0237 | 841.9216 | 985.0746 | 1154.7677 | 1356.1332 | 1595.3214 | 1879.2609 | 2216.8037 | 2618.6658 | 3097.4509 | 3668.264 | 4349.208 | 5161.9769 | 6132.5626 | 7292.098 | 8677.8571 | 10334.4413 | 12315.1796 | 14683.7746 |  | 388.7216 | 388.7216 | 388.7216 | 388.7216 | 388.7216 | 388.7216 | 388.7216 | 433.1339 | 505.9782 | 591.7977 | 693.0408 | 812.6337 | 954.0762 | 1121.5556 | 1320.0851 | 1555.6692 | 1835.5033 | 2161.6051 | 2544.4604 | 2998.0754 | 3535.4196 | 4171.6626 | 4924.451 | 5814.1696 | 6864.1537 | 8100.7964 | 9553.4686 | 11254.1199 | 13236.3675 | 15533.7814
| TRUE | 497 | 22005274 | BC | BC013 | 11 | BC13 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 3512.6854 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 8742.518 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 2.256 |  | 5654.9402 | 14074.2512 | 48.7436 | 14025.5076 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 6186.4504 | 6770.1359 | 7411.2387 | 8115.5348 | 8889.3894 | 9739.8175 | 10674.5507 | 11702.1111 | 12831.8926 | 14074.2512 | 15440.6037 | 16943.5377 | 18596.9321 | 20416.0906 | 22417.8892 | 24620.9383 | 27045.7623 | 29714.9978 | 32653.6119 | 35889.1435 | 39451.9701 | 43375.6014 | 47697.0041 | 52456.9602 | 57700.4629 | 63477.1532 | 69841.8023 | 76854.844 | 84582.9625 | 93099.7417 |  | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 41.3458 | 54.8063 | 73.2834 | 98.7611 | 134.0353 | 183.0532 | 251.3965 | 346.969 | 480.9775 | 669.33 | 934.6314 | 1309.0319 | 1838.2953 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 3842.8442 | 4205.4127 | 4603.6473 | 5041.1357 | 5521.8318 | 6050.0931 | 6630.7224 | 7269.0132 | 7970.8008 | 8742.518 | 9591.2567 | 10524.8359 | 11551.8767 | 12681.8854 | 13925.3448 | 15293.8152 | 16800.0458 | 18458.0977 | 20283.4798 | 22293.2986 | 24506.4235 | 26943.6699 | 29628.0003 | 32584.7474 | 35841.8597 | 39430.1728 | 43383.7088 | 47740.0076 | 52540.4914 | 57830.8685 |  | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.7003 | 3.5794 | 4.7862 | 6.4501 | 8.7539 | 11.9553 | 16.4188 | 22.6607 | 31.4129 | 43.7143 | 61.0412 | 85.4935 | 120.06 |  | 3840.5881 | 4203.1567 | 4601.3913 | 5038.8796 | 5519.5758 | 6047.8371 | 6628.4663 | 7266.7571 | 7968.5448 | 8740.262 | 9589.0007 | 10522.5799 | 11549.6207 | 12679.6294 | 13923.0888 | 15291.5592 | 16797.7898 | 18455.3974 | 20279.9004 | 22288.5124 | 24499.9734 | 26934.9159 | 29616.045 | 32568.3286 | 35819.199 | 39398.7599 | 43339.9945 | 47678.9664 | 52454.9979 | 57710.8085 |  | 6151.9197 | 6735.6053 | 7376.7081 | 8081.0042 | 8854.8588 | 9705.2869 | 10640.0201 | 11667.5804 | 12797.3619 | 14039.7205 | 15406.0731 | 16909.007 | 18562.4014 | 20381.56 | 22383.3586 | 24586.4076 | 27011.2317 | 29673.6668 | 32598.8251 | 35815.8862 | 39353.2442 | 43241.6139 | 47514.016 | 52205.6532 | 57353.6174 | 62996.347 | 69172.7106 | 75920.5454 | 83274.3967 | 91262.101
| TRUE | 498 | 22005273 | BC | BC013 | 11 | BC13 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 3512.6854 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 8742.518 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 2.256 |  | 5654.9402 | 14074.2512 | 48.7436 | 14025.5076 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 6186.4504 | 6770.1359 | 7411.2387 | 8115.5348 | 8889.3894 | 9739.8175 | 10674.5507 | 11702.1111 | 12831.8926 | 14074.2512 | 15440.6037 | 16943.5377 | 18596.9321 | 20416.0906 | 22417.8892 | 24620.9383 | 27045.7623 | 29714.9978 | 32653.6119 | 35889.1435 | 39451.9701 | 43375.6014 | 47697.0041 | 52456.9602 | 57700.4629 | 63477.1532 | 69841.8023 | 76854.844 | 84582.9625 | 93099.7417 |  | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 41.3458 | 54.8063 | 73.2834 | 98.7611 | 134.0353 | 183.0532 | 251.3965 | 346.969 | 480.9775 | 669.33 | 934.6314 | 1309.0319 | 1838.2953 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 3842.8442 | 4205.4127 | 4603.6473 | 5041.1357 | 5521.8318 | 6050.0931 | 6630.7224 | 7269.0132 | 7970.8008 | 8742.518 | 9591.2567 | 10524.8359 | 11551.8767 | 12681.8854 | 13925.3448 | 15293.8152 | 16800.0458 | 18458.0977 | 20283.4798 | 22293.2986 | 24506.4235 | 26943.6699 | 29628.0003 | 32584.7474 | 35841.8597 | 39430.1728 | 43383.7088 | 47740.0076 | 52540.4914 | 57830.8685 |  | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.7003 | 3.5794 | 4.7862 | 6.4501 | 8.7539 | 11.9553 | 16.4188 | 22.6607 | 31.4129 | 43.7143 | 61.0412 | 85.4935 | 120.06 |  | 3840.5881 | 4203.1567 | 4601.3913 | 5038.8796 | 5519.5758 | 6047.8371 | 6628.4663 | 7266.7571 | 7968.5448 | 8740.262 | 9589.0007 | 10522.5799 | 11549.6207 | 12679.6294 | 13923.0888 | 15291.5592 | 16797.7898 | 18455.3974 | 20279.9004 | 22288.5124 | 24499.9734 | 26934.9159 | 29616.045 | 32568.3286 | 35819.199 | 39398.7599 | 43339.9945 | 47678.9664 | 52454.9979 | 57710.8085 |  | 6151.9197 | 6735.6053 | 7376.7081 | 8081.0042 | 8854.8588 | 9705.2869 | 10640.0201 | 11667.5804 | 12797.3619 | 14039.7205 | 15406.0731 | 16909.007 | 18562.4014 | 20381.56 | 22383.3586 | 24586.4076 | 27011.2317 | 29673.6668 | 32598.8251 | 35815.8862 | 39353.2442 | 43241.6139 | 47514.016 | 52205.6532 | 57353.6174 | 62996.347 | 69172.7106 | 75920.5454 | 83274.3967 | 91262.101
| TRUE | 499 | 22015700 | BC | BC013 | 11 | BC13 | AUTO RECLOSE | Blank | English Electric | GROUP_624 | GROUP 624 | GROUP 000s | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 53.114 | 1051.8847 | 1104.9987 | 45.1415 | 3.7652 | 1823.895 |  | 7.1791 | 0.018276 | 0.00644 | 0.011836 | 104.0585 | 2060.8049 | 2164.8634 | 88.4392 | 7.3765 | 3573.2926 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 28.4243 | 0.35573 | 28.78 | 14.6761 | 2.0677 | 0.61681 |  | 2977.8004 | 5833.9718 | 46.1406 | 5787.8312 |  | 0.026643 |  | 5.6485 | 5.801 | 5.9577 | 6.1185 | 6.2837 | 6.4534 | 6.6277 | 6.8066 | 6.9904 | 7.1791 | 7.373 | 7.5721 | 7.7765 | 7.9865 | 8.2022 | 8.4236 | 8.6511 | 8.8847 | 9.1246 | 9.3709 | 9.624 | 9.8838 | 10.1507 | 10.4248 | 10.7063 | 10.9954 | 11.2923 | 11.5972 | 11.9103 | 12.2319 |  | 0.0099614 | 0.010641 | 0.011372 | 0.012157 | 0.013001 | 0.013908 | 0.014884 | 0.015933 | 0.017062 | 0.018276 | 0.019582 | 0.020988 | 0.022502 | 0.024131 | 0.025885 | 0.027774 | 0.029809 | 0.032001 | 0.034362 | 0.036906 | 0.039648 | 0.042603 | 0.045789 | 0.049223 | 0.052926 | 0.056919 | 0.061224 | 0.065869 | 0.070879 | 0.076283 |  | 0.0035102 | 0.0037498 | 0.0040073 | 0.0042839 | 0.0045813 | 0.004901 | 0.0052448 | 0.0056145 | 0.0060122 | 0.00644 | 0.0069004 | 0.0073958 | 0.0079291 | 0.0085032 | 0.0091214 | 0.0097871 | 0.010504 | 0.011276 | 0.012109 | 0.013005 | 0.013971 | 0.015013 | 0.016135 | 0.017345 | 0.01865 | 0.020057 | 0.021574 | 0.023211 | 0.024976 | 0.026881 | 3179.8724 | 3396.9403 | 3630.1647 | 3880.7985 | 4150.194 | 4439.8112 | 4751.2265 | 5086.142 | 5446.3954 | 5833.9718 | 6251.0147 | 6699.8395 | 7182.9469 | 7703.0388 | 8263.0335 | 8866.0844 | 9515.5983 | 10215.2564 | 10969.0368 | 11781.2382 | 12656.5065 | 13599.8628 | 14616.7344 | 15712.9874 | 16894.9632 | 18169.5167 | 19544.0589 | 21026.6019 | 22625.8083 | 24351.0446 |  | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 38.2204 | 50.6634 | 67.7438 | 91.2957 | 123.9035 | 169.2161 | 232.3933 | 320.7414 | 444.62 | 618.7348 | 863.9819 | 1210.0812 | 1699.3372 |  | 56.7183 | 60.59 | 64.75 | 69.2205 | 74.0256 | 79.1914 | 84.746 | 90.7197 | 97.1455 | 104.0585 | 111.4972 | 119.5027 | 128.1197 | 137.3964 | 147.3849 | 158.1413 | 169.7264 | 182.206 | 195.6509 | 210.1379 | 225.7497 | 242.576 | 260.7136 | 280.2671 | 301.3496 | 324.0834 | 348.6006 | 375.0442 | 403.5687 | 434.3411 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 42.5062 | 46.3779 | 50.5379 | 55.0083 | 59.8134 | 64.9792 | 70.5338 | 76.5076 | 82.9333 | 89.8464 | 97.2851 | 105.2906 | 113.9076 | 123.1843 | 133.1727 | 143.9291 | 155.5143 | 165.195 | 173.1018 | 179.9866 | 185.1161 | 187.4294 | 185.3994 | 176.8342 | 158.5949 | 126.1931 | 73.2159 | -9.4944 | -135.0108 | -321.995 |  | 1123.265 | 1199.9426 | 1282.3273 | 1370.8617 | 1466.0235 | 1568.3286 | 1678.3336 | 1796.6398 | 1923.8966 | 2060.8049 | 2208.122 | 2366.6659 | 2537.3198 | 2721.0382 | 2918.8519 | 3131.8749 | 3361.3106 | 3608.4594 | 3874.7264 | 4161.6302 | 4470.8119 | 4804.0451 | 5163.247 | 5550.4898 | 5968.0135 | 6418.2396 | 6903.7858 | 7427.4825 | 7992.3897 | 8601.8159 |  | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.42579 | 0.56441 | 0.75469 | 1.0171 | 1.3803 | 1.8851 | 2.5889 | 3.5732 | 4.9532 | 6.8929 | 9.625 | 13.4807 | 18.9311 |  | 1122.9093 | 1199.5868 | 1281.9715 | 1370.506 | 1465.6678 | 1567.9728 | 1677.9779 | 1796.2841 | 1923.5408 | 2060.4492 | 2207.7663 | 2366.3101 | 2536.9641 | 2720.6824 | 2918.4962 | 3131.5192 | 3360.9549 | 3608.0336 | 3874.162 | 4160.8755 | 4469.7948 | 4802.6648 | 5161.3619 | 5547.9009 | 5964.4404 | 6413.2864 | 6896.8929 | 7417.8575 | 7978.909 | 8582.8848 |  | 1165.4155 | 1245.9648 | 1332.5094 | 1425.5143 | 1525.4813 | 1632.9521 | 1748.5117 | 1872.7917 | 2006.4742 | 2150.2956 | 2305.0513 | 2471.6007 | 2650.8717 | 2843.8667 | 3051.6689 | 3275.4483 | 3516.4692 | 3773.2285 | 4047.2638 | 4340.8621 | 4654.9109 | 4990.0942 | 5346.7613 | 5724.7351 | 6123.0353 | 6539.4795 | 6970.1088 | 7408.3631 | 7843.8982 | 8260.8898 |  | 48.2048 | 51.4954 | 55.031 | 58.8304 | 62.9143 | 67.3047 | 72.0255 | 77.1026 | 82.5638 | 88.4392 | 94.7613 | 101.5652 | 108.8888 | 116.7731 | 125.2623 | 134.4041 | 144.2503 | 154.8567 | 166.2835 | 178.596 | 191.8645 | 206.1651 | 221.5803 | 238.1987 | 256.1167 | 275.4381 | 296.2753 | 318.7497 | 342.9926 | 369.1461 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 33.5287 | 36.8193 | 40.3549 | 44.1543 | 48.2382 | 52.6286 | 57.3494 | 62.4265 | 67.8877 | 73.7631 | 80.0852 | 86.8891 | 94.2127 | 102.097 | 110.5862 | 119.728 | 129.5742 | 137.2903 | 142.9983 | 147.4604 | 149.9043 | 149.2182 | 143.8073 | 131.3892 | 108.7017 | 71.0876 | 11.9004 | -78.3425 | -213.1693 | -411.8813 |  | 4.0207 | 4.2951 | 4.59 | 4.9069 | 5.2475 | 5.6137 | 6.0075 | 6.431 | 6.8865 | 7.3765 | 7.9038 | 8.4713 | 9.0822 | 9.7398 | 10.4478 | 11.2103 | 12.0316 | 12.9163 | 13.8693 | 14.8963 | 16.003 | 17.1958 | 18.4815 | 19.8676 | 21.3621 | 22.9737 | 24.7117 | 26.5862 | 28.6083 | 30.7897 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 1.953 | 2.2274 | 2.5223 | 2.8392 | 3.1798 | 3.546 | 3.9398 | 4.3633 | 4.8188 | 5.3088 | 5.8361 | 6.4036 | 7.0145 | 7.6721 | 8.3801 | 9.1426 | 9.9639 | 10.4413 | 10.5887 | 10.5096 | 10.0913 | 9.1726 | 7.5242 | 4.8193 | 0.59296 | -5.8171 | -15.3537 | -29.3598 | -49.7489 | -79.2486 |  | 1947.6636 | 2080.6171 | 2223.4665 | 2376.979 | 2541.9831 | 2719.3729 | 2910.114 | 3115.2488 | 3335.9031 | 3573.2926 | 3828.7303 | 4103.6343 | 4399.5364 | 4718.0913 | 5061.0866 | 5430.4537 | 5828.2793 | 6256.8181 | 6718.5066 | 7215.9779 | 7752.0775 | 8329.8808 | 8952.712 | 9624.1641 | 10348.1212 | 11128.782 | 11970.6855 | 12878.7392 | 13858.249 | 14914.9518 |  | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.73828 | 0.97864 | 1.3086 | 1.7635 | 2.3934 | 3.2687 | 4.489 | 6.1956 | 8.5885 | 11.9518 | 16.6891 | 23.3746 | 32.8253 |  | 1947.0468 | 2080.0003 | 2222.8497 | 2376.3622 | 2541.3663 | 2718.7561 | 2909.4971 | 3114.632 | 3335.2863 | 3572.6758 | 3828.1135 | 4103.0175 | 4398.9196 | 4717.4745 | 5060.4698 | 5429.8369 | 5827.6625 | 6256.0798 | 6717.528 | 7214.6693 | 7750.3139 | 8327.4874 | 8949.4433 | 9619.6751 | 10341.9256 | 11120.1934 | 11958.7337 | 12862.0501 | 13834.8745 | 14882.1265 |  | 3147.944 | 3365.0118 | 3598.2363 | 3848.87 | 4118.2655 | 4407.8828 | 4719.2981 | 5054.2135 | 5414.467 | 5802.0434 | 6219.0863 | 6667.911 | 7151.0185 | 7671.1103 | 8231.1051 | 8834.1559 | 9483.6698 | 10177.04 | 10918.3787 | 11713.5015 | 12565.2204 | 13475.9724 | 14447.5361 | 15480.6186 | 16574.2556 | 17724.9435 | 18925.3892 | 20162.7109 | 21415.8545 | 22651.8863
| TRUE | 500 | 22013851 | BC | BC014 | 11 | BC14 | SENSITIVE EF | Blank | RPL | ARTC_650 | ARTC 650 | AVE | Electromechanical |  | 0.57434 | 2190 |  | 2.5292 | 0.00090442 | 0.00065051 | 0.00025391 | 2.6661 | 52.0408 | 54.7069 | 6.2604 | 0.36836 | 721.8815 |  | 4.7392 | 0.0013394 | 0.00096335 | 0.00037602 | 3.9482 | 77.0677 | 81.0159 | 9.2711 | 0.54551 | 1069.0401 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 4.512 |  | 783.2171 | 1159.8726 | 35.8109 | 1124.0617 |  | 0.062797 |  | 2.6931 | 2.8677 | 3.0535 | 3.2514 | 3.4622 | 3.6865 | 3.9255 | 4.1799 | 4.4508 | 4.7392 | 5.0464 | 5.3734 | 5.7217 | 6.0925 | 6.4874 | 6.9078 | 7.3555 | 7.8322 | 8.3398 | 8.8804 | 9.4559 | 10.0687 | 10.7213 | 11.4161 | 12.156 | 12.9438 | 13.7827 | 14.676 | 15.6272 | 16.64 |  | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00099954 | 0.0011556 | 0.0013394 | 0.0015562 | 0.0018123 | 0.0021153 | 0.002474 | 0.0028992 | 0.0034038 | 0.0040031 | 0.0047157 | 0.0055637 | 0.0065737 | 0.0077776 | 0.0092136 | 0.010928 | 0.012976 | 0.015423 | 0.018351 | 0.021854 | 0.026048 | 0.031073 | 0.037095 |  | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00071893 | 0.00083114 | 0.00096335 | 0.0011193 | 0.0013035 | 0.0015214 | 0.0017794 | 0.0020853 | 0.0024482 | 0.0028793 | 0.0033918 | 0.0040017 | 0.0047282 | 0.005594 | 0.006627 | 0.00786 | 0.0093328 | 0.011093 | 0.013199 | 0.015719 | 0.018735 | 0.022349 | 0.02668 | 783.2171 | 783.2171 | 783.2171 | 783.2171 | 783.2171 | 783.2171 | 783.2171 | 865.591 | 1000.6988 | 1159.8726 | 1347.6532 | 1569.4683 | 1831.8086 | 2142.441 | 2510.6636 | 2947.6133 | 3466.6356 | 4083.7293 | 4818.082 | 5692.7145 | 6735.2566 | 7978.8816 | 9463.4312 | 11236.7705 | 13356.4207 | 15891.526 | 18925.2233 | 22557.498 | 26908.6267 | 32123.3255 |  | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 42.8633 | 56.8179 | 75.9732 | 102.3861 | 138.955 | 189.7722 | 260.624 | 359.7044 | 498.6316 | 693.8976 | 968.9368 | 1357.0797 | 1905.7696 |  | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.9465 | 3.4064 | 3.9482 | 4.5874 | 5.3424 | 6.2354 | 7.2928 | 8.5462 | 10.0336 | 11.8003 | 13.9009 | 16.4006 | 19.3779 | 22.9267 | 27.1599 | 32.2133 | 38.2497 | 45.4649 | 54.0944 | 64.421 | 76.7852 | 91.5963 | 109.347 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.2665 | -10.8066 | -10.2648 | -9.6256 | -8.8705 | -7.9775 | -6.9201 | -5.6667 | -4.1793 | -2.4126 | -3.1111 | -6.1498 | -10.7751 | -17.7093 | -27.9898 | -43.1052 | -65.1891 | -97.2979 | -143.8071 | -210.9795 | -307.7754 | -447.014 | -647.0324 |  | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 57.5142 | 66.4914 | 77.0677 | 89.5448 | 104.2833 | 121.7144 | 142.3544 | 166.8209 | 195.854 | 230.3405 | 271.3432 | 320.1373 | 378.2522 | 447.5238 | 530.1564 | 628.7973 | 746.6267 | 887.4668 | 1055.9118 | 1257.4856 | 1498.832 | 1787.9425 | 2134.433 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.38933 | 0.51609 | 0.69008 | 0.92999 | 1.2621 | 1.7237 | 2.3673 | 3.2672 | 4.5291 | 6.3028 | 8.801 | 12.3265 | 17.3104 |  | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 57.1889 | 66.1661 | 76.7424 | 89.2195 | 103.958 | 121.3892 | 142.0291 | 166.4957 | 195.5288 | 230.0152 | 270.9539 | 319.6212 | 377.5621 | 446.5938 | 528.8943 | 627.0735 | 744.2594 | 884.1996 | 1051.3826 | 1251.1829 | 1490.031 | 1775.616 | 2117.1226 |  | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 45.9224 | 55.3595 | 66.4776 | 79.5939 | 95.0875 | 113.4117 | 135.109 | 160.829 | 191.3494 | 227.6026 | 267.8428 | 313.4714 | 366.787 | 428.8846 | 500.9045 | 583.9683 | 679.0703 | 786.9017 | 907.5755 | 1040.2034 | 1182.2556 | 1328.602 | 1470.0902 |  | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.9188 | 7.9988 | 9.2711 | 10.7721 | 12.5451 | 14.642 | 17.1249 | 20.0682 | 23.5608 | 27.7095 | 32.642 | 38.5119 | 45.503 | 53.8362 | 63.7768 | 75.643 | 89.8177 | 106.7605 | 127.0241 | 151.273 | 180.3065 | 215.0859 | 256.768 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -7.774 | -6.6941 | -5.4218 | -3.9208 | -2.1478 | -0.050867 | 2.4321 | 5.3754 | 8.868 | 13.0166 | 15.0556 | 15.2 | 14.3318 | 11.8281 | 6.7648 | -2.2188 | -17.114 | -40.823 | -77.56 | -133.4269 | -217.2395 | -341.7116 | -525.152 |  | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.40711 | 0.47065 | 0.54551 | 0.63383 | 0.73816 | 0.86154 | 1.0076 | 1.1808 | 1.3863 | 1.6304 | 1.9207 | 2.2661 | 2.6774 | 3.1677 | 3.7526 | 4.4509 | 5.2849 | 6.2818 | 7.4741 | 8.901 | 10.6093 | 12.6557 | 15.1083 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6606 | -1.5971 | -1.5222 | -1.4339 | -1.3296 | -1.2062 | -1.0601 | -0.88691 | -0.6814 | -0.4373 | -0.55428 | -1.0146 | -1.7093 | -2.7441 | -4.2707 | -6.5066 | -9.7636 | -14.4876 | -21.317 | -31.1649 | -45.3375 | -65.7025 | -94.9315 |  | 721.8815 | 721.8815 | 721.8815 | 721.8815 | 721.8815 | 721.8815 | 721.8815 | 797.8044 | 922.3316 | 1069.0401 | 1242.1152 | 1446.5594 | 1688.3552 | 1974.6612 | 2314.0474 | 2716.7785 | 3195.1549 | 3763.9225 | 4440.7662 | 5246.904 | 6207.8021 | 7354.0358 | 8722.3267 | 10356.7914 | 12310.4467 | 14647.0217 | 17443.1427 | 20790.9651 | 24801.3462 | 29607.6692 |  | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 5.4006 | 7.1588 | 9.5723 | 12.9003 | 17.5078 | 23.9106 | 32.8377 | 45.3214 | 62.8258 | 87.4285 | 122.0825 | 170.987 | 240.12 |  | 717.3694 | 717.3694 | 717.3694 | 717.3694 | 717.3694 | 717.3694 | 717.3694 | 793.2924 | 917.8196 | 1064.5281 | 1237.6031 | 1442.0473 | 1683.8432 | 1970.1492 | 2309.5353 | 2712.2665 | 3190.6429 | 3758.5219 | 4433.6074 | 5237.3317 | 6194.9019 | 7336.528 | 8698.4161 | 10323.9538 | 12265.1252 | 14584.1959 | 17355.7141 | 20668.8826 | 24630.3592 | 29367.5492 |  | 747.4063 | 747.4063 | 747.4063 | 747.4063 | 747.4063 | 747.4063 | 747.4063 | 829.7801 | 964.8879 | 1124.0617 | 1311.8423 | 1533.6574 | 1795.9978 | 2106.6301 | 2474.8527 | 2911.8025 | 3430.8248 | 4040.866 | 4761.2641 | 5616.7412 | 6632.8705 | 7839.9266 | 9273.659 | 10976.1465 | 12996.7163 | 15392.8944 | 18231.3257 | 21588.5612 | 25551.5471 | 30217.556
| TRUE | 501 | 22005276 | BC | BC014 | 11 | BC14 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 7025.3708 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 17485.036 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 4.512 |  | 9167.6256 | 22816.7692 | 50.9996 | 22765.7696 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 10029.2945 | 10975.5487 | 12014.886 | 13156.6705 | 14411.2212 | 15789.9107 | 17305.2731 | 18971.1242 | 20802.6934 | 22816.7692 | 25031.8604 | 27468.3736 | 30148.8088 | 33097.976 | 36343.234 | 39914.7535 | 43845.8081 | 48173.0955 | 52937.0917 | 58182.4421 | 63958.3937 | 70319.2713 | 77325.0043 | 85041.7076 | 93542.3226 | 102907.3259 | 113225.5111 | 124594.8516 | 137123.4539 | 150930.6102 |  | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 44.0461 | 58.3857 | 78.0696 | 105.2112 | 142.7892 | 195.0085 | 267.8153 | 369.6297 | 512.3903 | 713.0442 | 995.6726 | 1394.5254 | 1958.3552 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 7685.6883 | 8410.8255 | 9207.2945 | 10082.2713 | 11043.6635 | 12100.1863 | 13261.4447 | 14538.0263 | 15941.6016 | 17485.036 | 19182.5134 | 21049.6718 | 23103.7534 | 25363.7708 | 27850.6896 | 30587.6304 | 33600.0916 | 36916.1955 | 40566.9597 | 44586.5972 | 49012.847 | 53887.3397 | 59256.0005 | 65169.4948 | 71683.7194 | 78860.3455 | 86767.4176 | 95480.0152 | 105080.9829 | 115661.737 |  | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 5.4006 | 7.1588 | 9.5723 | 12.9003 | 17.5078 | 23.9106 | 32.8377 | 45.3214 | 62.8258 | 87.4285 | 122.0825 | 170.987 | 240.12 |  | 7681.1763 | 8406.3135 | 9202.7825 | 10077.7593 | 11039.1515 | 12095.6742 | 13256.9327 | 14533.5143 | 15937.0895 | 17480.524 | 19178.0014 | 21045.1597 | 23099.2413 | 25359.2587 | 27846.1776 | 30583.1184 | 33595.5796 | 36910.7948 | 40559.8008 | 44577.0248 | 48999.9468 | 53869.8319 | 59232.0899 | 65136.6572 | 71638.398 | 78797.5198 | 86679.9891 | 95357.9327 | 104909.9959 | 115421.6171 |  | 9992.5079 | 10938.762 | 11978.0993 | 13119.8838 | 14374.4345 | 15753.124 | 17268.4864 | 18934.3375 | 20765.9067 | 22779.9825 | 24995.0738 | 27431.5869 | 30112.0221 | 33061.1894 | 36306.4473 | 39877.9668 | 43809.0214 | 48129.0642 | 52878.7255 | 58104.3987 | 63853.2176 | 70176.5298 | 77130.061 | 84773.9818 | 93172.8164 | 102395.1069 | 112512.7052 | 123599.5117 | 135729.3946 | 148972.9095
| TRUE | 502 | 22005275 | BC | BC014 | 11 | BC14 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 7025.3708 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 17485.036 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 4.512 |  | 9167.6256 | 22816.7692 | 50.9996 | 22765.7696 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 10029.2945 | 10975.5487 | 12014.886 | 13156.6705 | 14411.2212 | 15789.9107 | 17305.2731 | 18971.1242 | 20802.6934 | 22816.7692 | 25031.8604 | 27468.3736 | 30148.8088 | 33097.976 | 36343.234 | 39914.7535 | 43845.8081 | 48173.0955 | 52937.0917 | 58182.4421 | 63958.3937 | 70319.2713 | 77325.0043 | 85041.7076 | 93542.3226 | 102907.3259 | 113225.5111 | 124594.8516 | 137123.4539 | 150930.6102 |  | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 36.799 | 44.0461 | 58.3857 | 78.0696 | 105.2112 | 142.7892 | 195.0085 | 267.8153 | 369.6297 | 512.3903 | 713.0442 | 995.6726 | 1394.5254 | 1958.3552 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 7685.6883 | 8410.8255 | 9207.2945 | 10082.2713 | 11043.6635 | 12100.1863 | 13261.4447 | 14538.0263 | 15941.6016 | 17485.036 | 19182.5134 | 21049.6718 | 23103.7534 | 25363.7708 | 27850.6896 | 30587.6304 | 33600.0916 | 36916.1955 | 40566.9597 | 44586.5972 | 49012.847 | 53887.3397 | 59256.0005 | 65169.4948 | 71683.7194 | 78860.3455 | 86767.4176 | 95480.0152 | 105080.9829 | 115661.737 |  | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 5.4006 | 7.1588 | 9.5723 | 12.9003 | 17.5078 | 23.9106 | 32.8377 | 45.3214 | 62.8258 | 87.4285 | 122.0825 | 170.987 | 240.12 |  | 7681.1763 | 8406.3135 | 9202.7825 | 10077.7593 | 11039.1515 | 12095.6742 | 13256.9327 | 14533.5143 | 15937.0895 | 17480.524 | 19178.0014 | 21045.1597 | 23099.2413 | 25359.2587 | 27846.1776 | 30583.1184 | 33595.5796 | 36910.7948 | 40559.8008 | 44577.0248 | 48999.9468 | 53869.8319 | 59232.0899 | 65136.6572 | 71638.398 | 78797.5198 | 86679.9891 | 95357.9327 | 104909.9959 | 115421.6171 |  | 9992.5079 | 10938.762 | 11978.0993 | 13119.8838 | 14374.4345 | 15753.124 | 17268.4864 | 18934.3375 | 20765.9067 | 22779.9825 | 24995.0738 | 27431.5869 | 30112.0221 | 33061.1894 | 36306.4473 | 39877.9668 | 43809.0214 | 48129.0642 | 52878.7255 | 58104.3987 | 63853.2176 | 70176.5298 | 77130.061 | 84773.9818 | 93172.8164 | 102395.1069 | 112512.7052 | 123599.5117 | 135729.3946 | 148972.9095
| TRUE | 503 | 22015701 | BC | BC014 | 11 | BC14 | AUTO RECLOSE | Blank | English Electric | GROUP_624 | GROUP 624 | GROUP 000s | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 53.114 | 1051.8847 | 1104.9987 | 45.1415 | 3.7652 | 3647.7901 |  | 7.1791 | 0.018276 | 0.00644 | 0.011836 | 104.0585 | 2060.8049 | 2164.8634 | 88.4392 | 7.3765 | 7146.5853 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 28.4243 | 0.35573 | 28.78 | 14.6761 | 2.0677 | 1.2336 |  | 4801.6954 | 9407.2645 | 46.7574 | 9360.5071 |  | 0.026643 |  | 5.6485 | 5.801 | 5.9577 | 6.1185 | 6.2837 | 6.4534 | 6.6277 | 6.8066 | 6.9904 | 7.1791 | 7.373 | 7.5721 | 7.7765 | 7.9865 | 8.2022 | 8.4236 | 8.6511 | 8.8847 | 9.1246 | 9.3709 | 9.624 | 9.8838 | 10.1507 | 10.4248 | 10.7063 | 10.9954 | 11.2923 | 11.5972 | 11.9103 | 12.2319 |  | 0.0099614 | 0.010641 | 0.011372 | 0.012157 | 0.013001 | 0.013908 | 0.014884 | 0.015933 | 0.017062 | 0.018276 | 0.019582 | 0.020988 | 0.022502 | 0.024131 | 0.025885 | 0.027774 | 0.029809 | 0.032001 | 0.034362 | 0.036906 | 0.039648 | 0.042603 | 0.045789 | 0.049223 | 0.052926 | 0.056919 | 0.061224 | 0.065869 | 0.070879 | 0.076283 |  | 0.0035102 | 0.0037498 | 0.0040073 | 0.0042839 | 0.0045813 | 0.004901 | 0.0052448 | 0.0056145 | 0.0060122 | 0.00644 | 0.0069004 | 0.0073958 | 0.0079291 | 0.0085032 | 0.0091214 | 0.0097871 | 0.010504 | 0.011276 | 0.012109 | 0.013005 | 0.013971 | 0.015013 | 0.016135 | 0.017345 | 0.01865 | 0.020057 | 0.021574 | 0.023211 | 0.024976 | 0.026881 | 5127.536 | 5477.5575 | 5853.6312 | 6257.7775 | 6692.1771 | 7159.1841 | 7661.3405 | 8201.3908 | 8782.2986 | 9407.2645 | 10079.7451 | 10803.4738 | 11582.4833 | 12421.1301 | 13324.1202 | 14296.5381 | 15343.8776 | 16472.0745 | 17687.5434 | 18997.2161 | 20408.5839 | 21929.7436 | 23569.4463 | 25337.1515 | 27243.0844 | 29298.2987 | 31514.7444 | 33905.3411 | 36484.0573 | 39265.9964 |  | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 32.5486 | 38.9587 | 51.642 | 69.0524 | 93.0592 | 126.2968 | 172.4848 | 236.8823 | 326.937 | 453.2085 | 630.6866 | 880.671 | 1233.4558 | 1732.1625 |  | 56.7183 | 60.59 | 64.75 | 69.2205 | 74.0256 | 79.1914 | 84.746 | 90.7197 | 97.1455 | 104.0585 | 111.4972 | 119.5027 | 128.1197 | 137.3964 | 147.3849 | 158.1413 | 169.7264 | 182.206 | 195.6509 | 210.1379 | 225.7497 | 242.576 | 260.7136 | 280.2671 | 301.3496 | 324.0834 | 348.6006 | 375.0442 | 403.5687 | 434.3411 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 42.5062 | 46.3779 | 50.5379 | 55.0083 | 59.8134 | 64.9792 | 70.5338 | 76.5076 | 82.9333 | 89.8464 | 97.2851 | 105.2906 | 113.9076 | 123.1843 | 133.1727 | 143.9291 | 155.5143 | 165.195 | 173.1018 | 179.9866 | 185.1161 | 187.4294 | 185.3994 | 176.8342 | 158.5949 | 126.1931 | 73.2159 | -9.4944 | -135.0108 | -321.995 |  | 1123.265 | 1199.9426 | 1282.3273 | 1370.8617 | 1466.0235 | 1568.3286 | 1678.3336 | 1796.6398 | 1923.8966 | 2060.8049 | 2208.122 | 2366.6659 | 2537.3198 | 2721.0382 | 2918.8519 | 3131.8749 | 3361.3106 | 3608.4594 | 3874.7264 | 4161.6302 | 4470.8119 | 4804.0451 | 5163.247 | 5550.4898 | 5968.0135 | 6418.2396 | 6903.7858 | 7427.4825 | 7992.3897 | 8601.8159 |  | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.42579 | 0.56441 | 0.75469 | 1.0171 | 1.3803 | 1.8851 | 2.5889 | 3.5732 | 4.9532 | 6.8929 | 9.625 | 13.4807 | 18.9311 |  | 1122.9093 | 1199.5868 | 1281.9715 | 1370.506 | 1465.6678 | 1567.9728 | 1677.9779 | 1796.2841 | 1923.5408 | 2060.4492 | 2207.7663 | 2366.3101 | 2536.9641 | 2720.6824 | 2918.4962 | 3131.5192 | 3360.9549 | 3608.0336 | 3874.162 | 4160.8755 | 4469.7948 | 4802.6648 | 5161.3619 | 5547.9009 | 5964.4404 | 6413.2864 | 6896.8929 | 7417.8575 | 7978.909 | 8582.8848 |  | 1165.4155 | 1245.9648 | 1332.5094 | 1425.5143 | 1525.4813 | 1632.9521 | 1748.5117 | 1872.7917 | 2006.4742 | 2150.2956 | 2305.0513 | 2471.6007 | 2650.8717 | 2843.8667 | 3051.6689 | 3275.4483 | 3516.4692 | 3773.2285 | 4047.2638 | 4340.8621 | 4654.9109 | 4990.0942 | 5346.7613 | 5724.7351 | 6123.0353 | 6539.4795 | 6970.1088 | 7408.3631 | 7843.8982 | 8260.8898 |  | 48.2048 | 51.4954 | 55.031 | 58.8304 | 62.9143 | 67.3047 | 72.0255 | 77.1026 | 82.5638 | 88.4392 | 94.7613 | 101.5652 | 108.8888 | 116.7731 | 125.2623 | 134.4041 | 144.2503 | 154.8567 | 166.2835 | 178.596 | 191.8645 | 206.1651 | 221.5803 | 238.1987 | 256.1167 | 275.4381 | 296.2753 | 318.7497 | 342.9926 | 369.1461 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 33.5287 | 36.8193 | 40.3549 | 44.1543 | 48.2382 | 52.6286 | 57.3494 | 62.4265 | 67.8877 | 73.7631 | 80.0852 | 86.8891 | 94.2127 | 102.097 | 110.5862 | 119.728 | 129.5742 | 137.2903 | 142.9983 | 147.4604 | 149.9043 | 149.2182 | 143.8073 | 131.3892 | 108.7017 | 71.0876 | 11.9004 | -78.3425 | -213.1693 | -411.8813 |  | 4.0207 | 4.2951 | 4.59 | 4.9069 | 5.2475 | 5.6137 | 6.0075 | 6.431 | 6.8865 | 7.3765 | 7.9038 | 8.4713 | 9.0822 | 9.7398 | 10.4478 | 11.2103 | 12.0316 | 12.9163 | 13.8693 | 14.8963 | 16.003 | 17.1958 | 18.4815 | 19.8676 | 21.3621 | 22.9737 | 24.7117 | 26.5862 | 28.6083 | 30.7897 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 1.953 | 2.2274 | 2.5223 | 2.8392 | 3.1798 | 3.546 | 3.9398 | 4.3633 | 4.8188 | 5.3088 | 5.8361 | 6.4036 | 7.0145 | 7.6721 | 8.3801 | 9.1426 | 9.9639 | 10.4413 | 10.5887 | 10.5096 | 10.0913 | 9.1726 | 7.5242 | 4.8193 | 0.59296 | -5.8171 | -15.3537 | -29.3598 | -49.7489 | -79.2486 |  | 3895.3273 | 4161.2343 | 4446.933 | 4753.9581 | 5083.9661 | 5438.7458 | 5820.2279 | 6230.4976 | 6671.8062 | 7146.5853 | 7657.4607 | 8207.2686 | 8799.0728 | 9436.1826 | 10122.1733 | 10860.9075 | 11656.5586 | 12513.6362 | 13437.0133 | 14431.9558 | 15504.1549 | 16659.7615 | 17905.4239 | 19248.3282 | 20696.2424 | 22257.5639 | 23941.371 | 25757.4784 | 27716.498 | 29829.9036 |  | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.2336 | 1.4766 | 1.9573 | 2.6171 | 3.527 | 4.7868 | 6.5373 | 8.9781 | 12.3912 | 17.177 | 23.9036 | 33.3782 | 46.7491 | 65.6505 |  | 3894.0936 | 4160.0007 | 4445.6994 | 4752.7244 | 5082.7325 | 5437.5121 | 5818.9943 | 6229.264 | 6670.5726 | 7145.3517 | 7656.2271 | 8206.035 | 8797.8392 | 9434.949 | 10120.9397 | 10859.6739 | 11655.325 | 12512.1597 | 13435.056 | 14429.3386 | 15500.6279 | 16654.9748 | 17898.8866 | 19239.3502 | 20683.8512 | 22240.3869 | 23917.4674 | 25724.1002 | 27669.7489 | 29764.253 |  | 5094.9908 | 5445.0122 | 5821.0859 | 6225.2322 | 6659.6318 | 7126.6388 | 7628.7952 | 8168.8455 | 8749.7533 | 9374.7192 | 10047.1998 | 10770.9285 | 11549.9381 | 12388.5848 | 13291.5749 | 14263.9928 | 15311.3323 | 16433.1199 | 17635.9067 | 18928.1708 | 20315.5344 | 21803.4598 | 23396.9794 | 25100.2937 | 26916.1812 | 28845.1369 | 30884.1229 | 33024.761 | 35250.729 | 37534.0129
| TRUE | 504 | 22013852 | BC | BC015 | 11 | BC15 | SENSITIVE EF | Blank | RPL | ARTC_650 | ARTC 650 | AVE | Electromechanical |  | 0.57434 | 2190 |  | 2.5292 | 0.00090442 | 0.00065051 | 0.00025391 | 2.6661 | 52.0408 | 54.7069 | 6.2604 | 0.36836 | 360.9407 |  | 4.7392 | 0.0013394 | 0.00096335 | 0.00037602 | 3.9482 | 77.0677 | 81.0159 | 9.2711 | 0.54551 | 534.52 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 2.256 |  | 422.2764 | 625.3525 | 33.5548 | 591.7977 |  | 0.062797 |  | 2.6931 | 2.8677 | 3.0535 | 3.2514 | 3.4622 | 3.6865 | 3.9255 | 4.1799 | 4.4508 | 4.7392 | 5.0464 | 5.3734 | 5.7217 | 6.0925 | 6.4874 | 6.9078 | 7.3555 | 7.8322 | 8.3398 | 8.8804 | 9.4559 | 10.0687 | 10.7213 | 11.4161 | 12.156 | 12.9438 | 13.7827 | 14.676 | 15.6272 | 16.64 |  | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00099954 | 0.0011556 | 0.0013394 | 0.0015562 | 0.0018123 | 0.0021153 | 0.002474 | 0.0028992 | 0.0034038 | 0.0040031 | 0.0047157 | 0.0055637 | 0.0065737 | 0.0077776 | 0.0092136 | 0.010928 | 0.012976 | 0.015423 | 0.018351 | 0.021854 | 0.026048 | 0.031073 | 0.037095 |  | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00071893 | 0.00083114 | 0.00096335 | 0.0011193 | 0.0013035 | 0.0015214 | 0.0017794 | 0.0020853 | 0.0024482 | 0.0028793 | 0.0033918 | 0.0040017 | 0.0047282 | 0.005594 | 0.006627 | 0.00786 | 0.0093328 | 0.011093 | 0.013199 | 0.015719 | 0.018735 | 0.022349 | 0.02668 | 422.2764 | 422.2764 | 422.2764 | 422.2764 | 422.2764 | 422.2764 | 422.2764 | 466.6888 | 539.533 | 625.3525 | 726.5956 | 846.1886 | 987.631 | 1155.1104 | 1353.6399 | 1589.2241 | 1869.0582 | 2201.7681 | 2597.6989 | 3069.2624 | 3631.3555 | 4301.8637 | 5102.2678 | 6058.3747 | 7201.1974 | 8568.0152 | 10203.6519 | 12162.0155 | 14507.9536 | 17319.4909 |  | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 33.5548 | 40.163 | 53.2385 | 71.1871 | 95.936 | 130.2011 | 177.8169 | 244.2051 | 337.0437 | 467.2188 | 650.1833 | 907.8956 | 1271.5861 | 1785.7096 |  | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.9465 | 3.4064 | 3.9482 | 4.5874 | 5.3424 | 6.2354 | 7.2928 | 8.5462 | 10.0336 | 11.8003 | 13.9009 | 16.4006 | 19.3779 | 22.9267 | 27.1599 | 32.2133 | 38.2497 | 45.4649 | 54.0944 | 64.421 | 76.7852 | 91.5963 | 109.347 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.2665 | -10.8066 | -10.2648 | -9.6256 | -8.8705 | -7.9775 | -6.9201 | -5.6667 | -4.1793 | -2.4126 | -3.1111 | -6.1498 | -10.7751 | -17.7093 | -27.9898 | -43.1052 | -65.1891 | -97.2979 | -143.8071 | -210.9795 | -307.7754 | -447.014 | -647.0324 |  | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 57.5142 | 66.4914 | 77.0677 | 89.5448 | 104.2833 | 121.7144 | 142.3544 | 166.8209 | 195.854 | 230.3405 | 271.3432 | 320.1373 | 378.2522 | 447.5238 | 530.1564 | 628.7973 | 746.6267 | 887.4668 | 1055.9118 | 1257.4856 | 1498.832 | 1787.9425 | 2134.433 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.38933 | 0.51609 | 0.69008 | 0.92999 | 1.2621 | 1.7237 | 2.3673 | 3.2672 | 4.5291 | 6.3028 | 8.801 | 12.3265 | 17.3104 |  | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 57.1889 | 66.1661 | 76.7424 | 89.2195 | 103.958 | 121.3892 | 142.0291 | 166.4957 | 195.5288 | 230.0152 | 270.9539 | 319.6212 | 377.5621 | 446.5938 | 528.8943 | 627.0735 | 744.2594 | 884.1996 | 1051.3826 | 1251.1829 | 1490.031 | 1775.616 | 2117.1226 |  | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 45.9224 | 55.3595 | 66.4776 | 79.5939 | 95.0875 | 113.4117 | 135.109 | 160.829 | 191.3494 | 227.6026 | 267.8428 | 313.4714 | 366.787 | 428.8846 | 500.9045 | 583.9683 | 679.0703 | 786.9017 | 907.5755 | 1040.2034 | 1182.2556 | 1328.602 | 1470.0902 |  | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.9188 | 7.9988 | 9.2711 | 10.7721 | 12.5451 | 14.642 | 17.1249 | 20.0682 | 23.5608 | 27.7095 | 32.642 | 38.5119 | 45.503 | 53.8362 | 63.7768 | 75.643 | 89.8177 | 106.7605 | 127.0241 | 151.273 | 180.3065 | 215.0859 | 256.768 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -7.774 | -6.6941 | -5.4218 | -3.9208 | -2.1478 | -0.050867 | 2.4321 | 5.3754 | 8.868 | 13.0166 | 15.0556 | 15.2 | 14.3318 | 11.8281 | 6.7648 | -2.2188 | -17.114 | -40.823 | -77.56 | -133.4269 | -217.2395 | -341.7116 | -525.152 |  | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.40711 | 0.47065 | 0.54551 | 0.63383 | 0.73816 | 0.86154 | 1.0076 | 1.1808 | 1.3863 | 1.6304 | 1.9207 | 2.2661 | 2.6774 | 3.1677 | 3.7526 | 4.4509 | 5.2849 | 6.2818 | 7.4741 | 8.901 | 10.6093 | 12.6557 | 15.1083 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6606 | -1.5971 | -1.5222 | -1.4339 | -1.3296 | -1.2062 | -1.0601 | -0.88691 | -0.6814 | -0.4373 | -0.55428 | -1.0146 | -1.7093 | -2.7441 | -4.2707 | -6.5066 | -9.7636 | -14.4876 | -21.317 | -31.1649 | -45.3375 | -65.7025 | -94.9315 |  | 360.9407 | 360.9407 | 360.9407 | 360.9407 | 360.9407 | 360.9407 | 360.9407 | 398.9022 | 461.1658 | 534.52 | 621.0576 | 723.2797 | 844.1776 | 987.3306 | 1157.0237 | 1358.3893 | 1597.5775 | 1881.9612 | 2220.3831 | 2623.452 | 3103.9011 | 3677.0179 | 4361.1633 | 5178.3957 | 6155.2233 | 7323.5108 | 8721.5713 | 10395.4825 | 12400.6731 | 14803.8346 |  | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.7003 | 3.5794 | 4.7862 | 6.4501 | 8.7539 | 11.9553 | 16.4188 | 22.6607 | 31.4129 | 43.7143 | 61.0412 | 85.4935 | 120.06 |  | 358.6847 | 358.6847 | 358.6847 | 358.6847 | 358.6847 | 358.6847 | 358.6847 | 396.6462 | 458.9098 | 532.264 | 618.8016 | 721.0237 | 841.9216 | 985.0746 | 1154.7677 | 1356.1332 | 1595.3214 | 1879.2609 | 2216.8037 | 2618.6658 | 3097.4509 | 3668.264 | 4349.208 | 5161.9769 | 6132.5626 | 7292.098 | 8677.8571 | 10334.4413 | 12315.1796 | 14683.7746 |  | 388.7216 | 388.7216 | 388.7216 | 388.7216 | 388.7216 | 388.7216 | 388.7216 | 433.1339 | 505.9782 | 591.7977 | 693.0408 | 812.6337 | 954.0762 | 1121.5556 | 1320.0851 | 1555.6692 | 1835.5033 | 2161.6051 | 2544.4604 | 2998.0754 | 3535.4196 | 4171.6626 | 4924.451 | 5814.1696 | 6864.1537 | 8100.7964 | 9553.4686 | 11254.1199 | 13236.3675 | 15533.7814
| TRUE | 505 | 22005278 | BC | BC015 | 11 | BC15 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 3512.6854 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 8742.518 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 2.256 |  | 5654.9402 | 14074.2512 | 48.7436 | 14025.5076 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 6186.4504 | 6770.1359 | 7411.2387 | 8115.5348 | 8889.3894 | 9739.8175 | 10674.5507 | 11702.1111 | 12831.8926 | 14074.2512 | 15440.6037 | 16943.5377 | 18596.9321 | 20416.0906 | 22417.8892 | 24620.9383 | 27045.7623 | 29714.9978 | 32653.6119 | 35889.1435 | 39451.9701 | 43375.6014 | 47697.0041 | 52456.9602 | 57700.4629 | 63477.1532 | 69841.8023 | 76854.844 | 84582.9625 | 93099.7417 |  | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 41.3458 | 54.8063 | 73.2834 | 98.7611 | 134.0353 | 183.0532 | 251.3965 | 346.969 | 480.9775 | 669.33 | 934.6314 | 1309.0319 | 1838.2953 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 3842.8442 | 4205.4127 | 4603.6473 | 5041.1357 | 5521.8318 | 6050.0931 | 6630.7224 | 7269.0132 | 7970.8008 | 8742.518 | 9591.2567 | 10524.8359 | 11551.8767 | 12681.8854 | 13925.3448 | 15293.8152 | 16800.0458 | 18458.0977 | 20283.4798 | 22293.2986 | 24506.4235 | 26943.6699 | 29628.0003 | 32584.7474 | 35841.8597 | 39430.1728 | 43383.7088 | 47740.0076 | 52540.4914 | 57830.8685 |  | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.7003 | 3.5794 | 4.7862 | 6.4501 | 8.7539 | 11.9553 | 16.4188 | 22.6607 | 31.4129 | 43.7143 | 61.0412 | 85.4935 | 120.06 |  | 3840.5881 | 4203.1567 | 4601.3913 | 5038.8796 | 5519.5758 | 6047.8371 | 6628.4663 | 7266.7571 | 7968.5448 | 8740.262 | 9589.0007 | 10522.5799 | 11549.6207 | 12679.6294 | 13923.0888 | 15291.5592 | 16797.7898 | 18455.3974 | 20279.9004 | 22288.5124 | 24499.9734 | 26934.9159 | 29616.045 | 32568.3286 | 35819.199 | 39398.7599 | 43339.9945 | 47678.9664 | 52454.9979 | 57710.8085 |  | 6151.9197 | 6735.6053 | 7376.7081 | 8081.0042 | 8854.8588 | 9705.2869 | 10640.0201 | 11667.5804 | 12797.3619 | 14039.7205 | 15406.0731 | 16909.007 | 18562.4014 | 20381.56 | 22383.3586 | 24586.4076 | 27011.2317 | 29673.6668 | 32598.8251 | 35815.8862 | 39353.2442 | 43241.6139 | 47514.016 | 52205.6532 | 57353.6174 | 62996.347 | 69172.7106 | 75920.5454 | 83274.3967 | 91262.101
| TRUE | 506 | 22005277 | BC | BC015 | 11 | BC15 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 3512.6854 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 8742.518 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 2.256 |  | 5654.9402 | 14074.2512 | 48.7436 | 14025.5076 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 6186.4504 | 6770.1359 | 7411.2387 | 8115.5348 | 8889.3894 | 9739.8175 | 10674.5507 | 11702.1111 | 12831.8926 | 14074.2512 | 15440.6037 | 16943.5377 | 18596.9321 | 20416.0906 | 22417.8892 | 24620.9383 | 27045.7623 | 29714.9978 | 32653.6119 | 35889.1435 | 39451.9701 | 43375.6014 | 47697.0041 | 52456.9602 | 57700.4629 | 63477.1532 | 69841.8023 | 76854.844 | 84582.9625 | 93099.7417 |  | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 34.543 | 41.3458 | 54.8063 | 73.2834 | 98.7611 | 134.0353 | 183.0532 | 251.3965 | 346.969 | 480.9775 | 669.33 | 934.6314 | 1309.0319 | 1838.2953 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 3842.8442 | 4205.4127 | 4603.6473 | 5041.1357 | 5521.8318 | 6050.0931 | 6630.7224 | 7269.0132 | 7970.8008 | 8742.518 | 9591.2567 | 10524.8359 | 11551.8767 | 12681.8854 | 13925.3448 | 15293.8152 | 16800.0458 | 18458.0977 | 20283.4798 | 22293.2986 | 24506.4235 | 26943.6699 | 29628.0003 | 32584.7474 | 35841.8597 | 39430.1728 | 43383.7088 | 47740.0076 | 52540.4914 | 57830.8685 |  | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.256 | 2.7003 | 3.5794 | 4.7862 | 6.4501 | 8.7539 | 11.9553 | 16.4188 | 22.6607 | 31.4129 | 43.7143 | 61.0412 | 85.4935 | 120.06 |  | 3840.5881 | 4203.1567 | 4601.3913 | 5038.8796 | 5519.5758 | 6047.8371 | 6628.4663 | 7266.7571 | 7968.5448 | 8740.262 | 9589.0007 | 10522.5799 | 11549.6207 | 12679.6294 | 13923.0888 | 15291.5592 | 16797.7898 | 18455.3974 | 20279.9004 | 22288.5124 | 24499.9734 | 26934.9159 | 29616.045 | 32568.3286 | 35819.199 | 39398.7599 | 43339.9945 | 47678.9664 | 52454.9979 | 57710.8085 |  | 6151.9197 | 6735.6053 | 7376.7081 | 8081.0042 | 8854.8588 | 9705.2869 | 10640.0201 | 11667.5804 | 12797.3619 | 14039.7205 | 15406.0731 | 16909.007 | 18562.4014 | 20381.56 | 22383.3586 | 24586.4076 | 27011.2317 | 29673.6668 | 32598.8251 | 35815.8862 | 39353.2442 | 43241.6139 | 47514.016 | 52205.6532 | 57353.6174 | 62996.347 | 69172.7106 | 75920.5454 | 83274.3967 | 91262.101
| TRUE | 507 | 22015702 | BC | BC015 | 11 | BC15 | AUTO RECLOSE | Blank | English Electric | GROUP_624 | GROUP 624 | GROUP 000s | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 53.114 | 1051.8847 | 1104.9987 | 45.1415 | 3.7652 | 1823.895 |  | 7.1791 | 0.018276 | 0.00644 | 0.011836 | 104.0585 | 2060.8049 | 2164.8634 | 88.4392 | 7.3765 | 3573.2926 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 28.4243 | 0.35573 | 28.78 | 14.6761 | 2.0677 | 0.61681 |  | 2977.8004 | 5833.9718 | 46.1406 | 5787.8312 |  | 0.026643 |  | 5.6485 | 5.801 | 5.9577 | 6.1185 | 6.2837 | 6.4534 | 6.6277 | 6.8066 | 6.9904 | 7.1791 | 7.373 | 7.5721 | 7.7765 | 7.9865 | 8.2022 | 8.4236 | 8.6511 | 8.8847 | 9.1246 | 9.3709 | 9.624 | 9.8838 | 10.1507 | 10.4248 | 10.7063 | 10.9954 | 11.2923 | 11.5972 | 11.9103 | 12.2319 |  | 0.0099614 | 0.010641 | 0.011372 | 0.012157 | 0.013001 | 0.013908 | 0.014884 | 0.015933 | 0.017062 | 0.018276 | 0.019582 | 0.020988 | 0.022502 | 0.024131 | 0.025885 | 0.027774 | 0.029809 | 0.032001 | 0.034362 | 0.036906 | 0.039648 | 0.042603 | 0.045789 | 0.049223 | 0.052926 | 0.056919 | 0.061224 | 0.065869 | 0.070879 | 0.076283 |  | 0.0035102 | 0.0037498 | 0.0040073 | 0.0042839 | 0.0045813 | 0.004901 | 0.0052448 | 0.0056145 | 0.0060122 | 0.00644 | 0.0069004 | 0.0073958 | 0.0079291 | 0.0085032 | 0.0091214 | 0.0097871 | 0.010504 | 0.011276 | 0.012109 | 0.013005 | 0.013971 | 0.015013 | 0.016135 | 0.017345 | 0.01865 | 0.020057 | 0.021574 | 0.023211 | 0.024976 | 0.026881 | 3179.8724 | 3396.9403 | 3630.1647 | 3880.7985 | 4150.194 | 4439.8112 | 4751.2265 | 5086.142 | 5446.3954 | 5833.9718 | 6251.0147 | 6699.8395 | 7182.9469 | 7703.0388 | 8263.0335 | 8866.0844 | 9515.5983 | 10215.2564 | 10969.0368 | 11781.2382 | 12656.5065 | 13599.8628 | 14616.7344 | 15712.9874 | 16894.9632 | 18169.5167 | 19544.0589 | 21026.6019 | 22625.8083 | 24351.0446 |  | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 31.9318 | 38.2204 | 50.6634 | 67.7438 | 91.2957 | 123.9035 | 169.2161 | 232.3933 | 320.7414 | 444.62 | 618.7348 | 863.9819 | 1210.0812 | 1699.3372 |  | 56.7183 | 60.59 | 64.75 | 69.2205 | 74.0256 | 79.1914 | 84.746 | 90.7197 | 97.1455 | 104.0585 | 111.4972 | 119.5027 | 128.1197 | 137.3964 | 147.3849 | 158.1413 | 169.7264 | 182.206 | 195.6509 | 210.1379 | 225.7497 | 242.576 | 260.7136 | 280.2671 | 301.3496 | 324.0834 | 348.6006 | 375.0442 | 403.5687 | 434.3411 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 42.5062 | 46.3779 | 50.5379 | 55.0083 | 59.8134 | 64.9792 | 70.5338 | 76.5076 | 82.9333 | 89.8464 | 97.2851 | 105.2906 | 113.9076 | 123.1843 | 133.1727 | 143.9291 | 155.5143 | 165.195 | 173.1018 | 179.9866 | 185.1161 | 187.4294 | 185.3994 | 176.8342 | 158.5949 | 126.1931 | 73.2159 | -9.4944 | -135.0108 | -321.995 |  | 1123.265 | 1199.9426 | 1282.3273 | 1370.8617 | 1466.0235 | 1568.3286 | 1678.3336 | 1796.6398 | 1923.8966 | 2060.8049 | 2208.122 | 2366.6659 | 2537.3198 | 2721.0382 | 2918.8519 | 3131.8749 | 3361.3106 | 3608.4594 | 3874.7264 | 4161.6302 | 4470.8119 | 4804.0451 | 5163.247 | 5550.4898 | 5968.0135 | 6418.2396 | 6903.7858 | 7427.4825 | 7992.3897 | 8601.8159 |  | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.42579 | 0.56441 | 0.75469 | 1.0171 | 1.3803 | 1.8851 | 2.5889 | 3.5732 | 4.9532 | 6.8929 | 9.625 | 13.4807 | 18.9311 |  | 1122.9093 | 1199.5868 | 1281.9715 | 1370.506 | 1465.6678 | 1567.9728 | 1677.9779 | 1796.2841 | 1923.5408 | 2060.4492 | 2207.7663 | 2366.3101 | 2536.9641 | 2720.6824 | 2918.4962 | 3131.5192 | 3360.9549 | 3608.0336 | 3874.162 | 4160.8755 | 4469.7948 | 4802.6648 | 5161.3619 | 5547.9009 | 5964.4404 | 6413.2864 | 6896.8929 | 7417.8575 | 7978.909 | 8582.8848 |  | 1165.4155 | 1245.9648 | 1332.5094 | 1425.5143 | 1525.4813 | 1632.9521 | 1748.5117 | 1872.7917 | 2006.4742 | 2150.2956 | 2305.0513 | 2471.6007 | 2650.8717 | 2843.8667 | 3051.6689 | 3275.4483 | 3516.4692 | 3773.2285 | 4047.2638 | 4340.8621 | 4654.9109 | 4990.0942 | 5346.7613 | 5724.7351 | 6123.0353 | 6539.4795 | 6970.1088 | 7408.3631 | 7843.8982 | 8260.8898 |  | 48.2048 | 51.4954 | 55.031 | 58.8304 | 62.9143 | 67.3047 | 72.0255 | 77.1026 | 82.5638 | 88.4392 | 94.7613 | 101.5652 | 108.8888 | 116.7731 | 125.2623 | 134.4041 | 144.2503 | 154.8567 | 166.2835 | 178.596 | 191.8645 | 206.1651 | 221.5803 | 238.1987 | 256.1167 | 275.4381 | 296.2753 | 318.7497 | 342.9926 | 369.1461 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 33.5287 | 36.8193 | 40.3549 | 44.1543 | 48.2382 | 52.6286 | 57.3494 | 62.4265 | 67.8877 | 73.7631 | 80.0852 | 86.8891 | 94.2127 | 102.097 | 110.5862 | 119.728 | 129.5742 | 137.2903 | 142.9983 | 147.4604 | 149.9043 | 149.2182 | 143.8073 | 131.3892 | 108.7017 | 71.0876 | 11.9004 | -78.3425 | -213.1693 | -411.8813 |  | 4.0207 | 4.2951 | 4.59 | 4.9069 | 5.2475 | 5.6137 | 6.0075 | 6.431 | 6.8865 | 7.3765 | 7.9038 | 8.4713 | 9.0822 | 9.7398 | 10.4478 | 11.2103 | 12.0316 | 12.9163 | 13.8693 | 14.8963 | 16.003 | 17.1958 | 18.4815 | 19.8676 | 21.3621 | 22.9737 | 24.7117 | 26.5862 | 28.6083 | 30.7897 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 1.953 | 2.2274 | 2.5223 | 2.8392 | 3.1798 | 3.546 | 3.9398 | 4.3633 | 4.8188 | 5.3088 | 5.8361 | 6.4036 | 7.0145 | 7.6721 | 8.3801 | 9.1426 | 9.9639 | 10.4413 | 10.5887 | 10.5096 | 10.0913 | 9.1726 | 7.5242 | 4.8193 | 0.59296 | -5.8171 | -15.3537 | -29.3598 | -49.7489 | -79.2486 |  | 1947.6636 | 2080.6171 | 2223.4665 | 2376.979 | 2541.9831 | 2719.3729 | 2910.114 | 3115.2488 | 3335.9031 | 3573.2926 | 3828.7303 | 4103.6343 | 4399.5364 | 4718.0913 | 5061.0866 | 5430.4537 | 5828.2793 | 6256.8181 | 6718.5066 | 7215.9779 | 7752.0775 | 8329.8808 | 8952.712 | 9624.1641 | 10348.1212 | 11128.782 | 11970.6855 | 12878.7392 | 13858.249 | 14914.9518 |  | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.61681 | 0.73828 | 0.97864 | 1.3086 | 1.7635 | 2.3934 | 3.2687 | 4.489 | 6.1956 | 8.5885 | 11.9518 | 16.6891 | 23.3746 | 32.8253 |  | 1947.0468 | 2080.0003 | 2222.8497 | 2376.3622 | 2541.3663 | 2718.7561 | 2909.4971 | 3114.632 | 3335.2863 | 3572.6758 | 3828.1135 | 4103.0175 | 4398.9196 | 4717.4745 | 5060.4698 | 5429.8369 | 5827.6625 | 6256.0798 | 6717.528 | 7214.6693 | 7750.3139 | 8327.4874 | 8949.4433 | 9619.6751 | 10341.9256 | 11120.1934 | 11958.7337 | 12862.0501 | 13834.8745 | 14882.1265 |  | 3147.944 | 3365.0118 | 3598.2363 | 3848.87 | 4118.2655 | 4407.8828 | 4719.2981 | 5054.2135 | 5414.467 | 5802.0434 | 6219.0863 | 6667.911 | 7151.0185 | 7671.1103 | 8231.1051 | 8834.1559 | 9483.6698 | 10177.04 | 10918.3787 | 11713.5015 | 12565.2204 | 13475.9724 | 14447.5361 | 15480.6186 | 16574.2556 | 17724.9435 | 18925.3892 | 20162.7109 | 21415.8545 | 22651.8863
| TRUE | 508 | 22015703 | BC | BC019 | 11 | BC19 | AUTO RECLOSE | Blank | English Electric | GROUP_624 | GROUP 624 | GROUP 000s | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 53.114 | 1051.8847 | 1104.9987 | 45.1415 | 3.7652 | 1360.5504 |  | 7.1791 | 0.018276 | 0.00644 | 0.011836 | 104.0585 | 2060.8049 | 2164.8634 | 88.4392 | 7.3765 | 2665.5288 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 28.4243 | 0.35573 | 28.78 | 14.6761 | 2.0677 | 0.46012 |  | 2514.4558 | 4926.208 | 45.9839 | 4880.2241 |  | 0.026643 |  | 5.6485 | 5.801 | 5.9577 | 6.1185 | 6.2837 | 6.4534 | 6.6277 | 6.8066 | 6.9904 | 7.1791 | 7.373 | 7.5721 | 7.7765 | 7.9865 | 8.2022 | 8.4236 | 8.6511 | 8.8847 | 9.1246 | 9.3709 | 9.624 | 9.8838 | 10.1507 | 10.4248 | 10.7063 | 10.9954 | 11.2923 | 11.5972 | 11.9103 | 12.2319 |  | 0.0099614 | 0.010641 | 0.011372 | 0.012157 | 0.013001 | 0.013908 | 0.014884 | 0.015933 | 0.017062 | 0.018276 | 0.019582 | 0.020988 | 0.022502 | 0.024131 | 0.025885 | 0.027774 | 0.029809 | 0.032001 | 0.034362 | 0.036906 | 0.039648 | 0.042603 | 0.045789 | 0.049223 | 0.052926 | 0.056919 | 0.061224 | 0.065869 | 0.070879 | 0.076283 |  | 0.0035102 | 0.0037498 | 0.0040073 | 0.0042839 | 0.0045813 | 0.004901 | 0.0052448 | 0.0056145 | 0.0060122 | 0.00644 | 0.0069004 | 0.0073958 | 0.0079291 | 0.0085032 | 0.0091214 | 0.0097871 | 0.010504 | 0.011276 | 0.012109 | 0.013005 | 0.013971 | 0.015013 | 0.016135 | 0.017345 | 0.01865 | 0.020057 | 0.021574 | 0.023211 | 0.024976 | 0.026881 | 2685.0855 | 2868.3777 | 3065.3124 | 3276.9477 | 3504.4253 | 3748.9782 | 4011.9375 | 4294.7402 | 4598.9383 | 4926.208 | 5278.3592 | 5657.3469 | 6065.2831 | 6504.4488 | 6977.3086 | 7486.525 | 8034.9747 | 8625.7663 | 9262.2587 | 9948.0819 | 10687.1588 | 11483.7292 | 12342.3759 | 13268.0524 | 14266.1132 | 15342.3467 | 16503.0106 | 17754.8704 | 19105.2409 | 20562.0311 |  | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 38.0328 | 50.4148 | 67.4114 | 90.8477 | 123.2954 | 168.3857 | 231.2529 | 319.1674 | 442.4382 | 615.6986 | 859.7422 | 1204.1431 | 1690.9982 |  | 56.7183 | 60.59 | 64.75 | 69.2205 | 74.0256 | 79.1914 | 84.746 | 90.7197 | 97.1455 | 104.0585 | 111.4972 | 119.5027 | 128.1197 | 137.3964 | 147.3849 | 158.1413 | 169.7264 | 182.206 | 195.6509 | 210.1379 | 225.7497 | 242.576 | 260.7136 | 280.2671 | 301.3496 | 324.0834 | 348.6006 | 375.0442 | 403.5687 | 434.3411 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 42.5062 | 46.3779 | 50.5379 | 55.0083 | 59.8134 | 64.9792 | 70.5338 | 76.5076 | 82.9333 | 89.8464 | 97.2851 | 105.2906 | 113.9076 | 123.1843 | 133.1727 | 143.9291 | 155.5143 | 165.195 | 173.1018 | 179.9866 | 185.1161 | 187.4294 | 185.3994 | 176.8342 | 158.5949 | 126.1931 | 73.2159 | -9.4944 | -135.0108 | -321.995 |  | 1123.265 | 1199.9426 | 1282.3273 | 1370.8617 | 1466.0235 | 1568.3286 | 1678.3336 | 1796.6398 | 1923.8966 | 2060.8049 | 2208.122 | 2366.6659 | 2537.3198 | 2721.0382 | 2918.8519 | 3131.8749 | 3361.3106 | 3608.4594 | 3874.7264 | 4161.6302 | 4470.8119 | 4804.0451 | 5163.247 | 5550.4898 | 5968.0135 | 6418.2396 | 6903.7858 | 7427.4825 | 7992.3897 | 8601.8159 |  | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.42579 | 0.56441 | 0.75469 | 1.0171 | 1.3803 | 1.8851 | 2.5889 | 3.5732 | 4.9532 | 6.8929 | 9.625 | 13.4807 | 18.9311 |  | 1122.9093 | 1199.5868 | 1281.9715 | 1370.506 | 1465.6678 | 1567.9728 | 1677.9779 | 1796.2841 | 1923.5408 | 2060.4492 | 2207.7663 | 2366.3101 | 2536.9641 | 2720.6824 | 2918.4962 | 3131.5192 | 3360.9549 | 3608.0336 | 3874.162 | 4160.8755 | 4469.7948 | 4802.6648 | 5161.3619 | 5547.9009 | 5964.4404 | 6413.2864 | 6896.8929 | 7417.8575 | 7978.909 | 8582.8848 |  | 1165.4155 | 1245.9648 | 1332.5094 | 1425.5143 | 1525.4813 | 1632.9521 | 1748.5117 | 1872.7917 | 2006.4742 | 2150.2956 | 2305.0513 | 2471.6007 | 2650.8717 | 2843.8667 | 3051.6689 | 3275.4483 | 3516.4692 | 3773.2285 | 4047.2638 | 4340.8621 | 4654.9109 | 4990.0942 | 5346.7613 | 5724.7351 | 6123.0353 | 6539.4795 | 6970.1088 | 7408.3631 | 7843.8982 | 8260.8898 |  | 48.2048 | 51.4954 | 55.031 | 58.8304 | 62.9143 | 67.3047 | 72.0255 | 77.1026 | 82.5638 | 88.4392 | 94.7613 | 101.5652 | 108.8888 | 116.7731 | 125.2623 | 134.4041 | 144.2503 | 154.8567 | 166.2835 | 178.596 | 191.8645 | 206.1651 | 221.5803 | 238.1987 | 256.1167 | 275.4381 | 296.2753 | 318.7497 | 342.9926 | 369.1461 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 33.5287 | 36.8193 | 40.3549 | 44.1543 | 48.2382 | 52.6286 | 57.3494 | 62.4265 | 67.8877 | 73.7631 | 80.0852 | 86.8891 | 94.2127 | 102.097 | 110.5862 | 119.728 | 129.5742 | 137.2903 | 142.9983 | 147.4604 | 149.9043 | 149.2182 | 143.8073 | 131.3892 | 108.7017 | 71.0876 | 11.9004 | -78.3425 | -213.1693 | -411.8813 |  | 4.0207 | 4.2951 | 4.59 | 4.9069 | 5.2475 | 5.6137 | 6.0075 | 6.431 | 6.8865 | 7.3765 | 7.9038 | 8.4713 | 9.0822 | 9.7398 | 10.4478 | 11.2103 | 12.0316 | 12.9163 | 13.8693 | 14.8963 | 16.003 | 17.1958 | 18.4815 | 19.8676 | 21.3621 | 22.9737 | 24.7117 | 26.5862 | 28.6083 | 30.7897 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 1.953 | 2.2274 | 2.5223 | 2.8392 | 3.1798 | 3.546 | 3.9398 | 4.3633 | 4.8188 | 5.3088 | 5.8361 | 6.4036 | 7.0145 | 7.6721 | 8.3801 | 9.1426 | 9.9639 | 10.4413 | 10.5887 | 10.5096 | 10.0913 | 9.1726 | 7.5242 | 4.8193 | 0.59296 | -5.8171 | -15.3537 | -29.3598 | -49.7489 | -79.2486 |  | 1452.8767 | 1552.0545 | 1658.6142 | 1773.1282 | 1896.2144 | 2028.5399 | 2170.8249 | 2323.847 | 2488.446 | 2665.5288 | 2856.0748 | 3061.1418 | 3281.8725 | 3519.5013 | 3775.3617 | 4050.8943 | 4347.6558 | 4667.328 | 5011.7286 | 5382.8216 | 5782.7297 | 6213.7472 | 6678.3535 | 7179.2291 | 7719.2712 | 8301.6119 | 8929.6372 | 9607.0078 | 10337.6817 | 11125.9383 |  | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.55073 | 0.73003 | 0.97614 | 1.3155 | 1.7854 | 2.4383 | 3.3486 | 4.6217 | 6.4067 | 8.9155 | 12.4494 | 17.4364 | 24.4863 |  | 1452.4165 | 1551.5944 | 1658.1541 | 1772.6681 | 1895.7543 | 2028.0798 | 2170.3648 | 2323.3869 | 2487.9859 | 2665.0687 | 2855.6147 | 3060.6817 | 3281.4124 | 3519.0412 | 3774.9016 | 4050.4342 | 4347.1956 | 4666.7773 | 5010.9986 | 5381.8455 | 5781.4142 | 6211.9618 | 6675.9152 | 7175.8805 | 7714.6496 | 8295.2052 | 8920.7216 | 9594.5584 | 10320.2452 | 11101.452 |  | 2653.3137 | 2836.6059 | 3033.5407 | 3245.1759 | 3472.6536 | 3717.2065 | 3980.1657 | 4262.9684 | 4567.1666 | 4894.4362 | 5246.5874 | 5625.5751 | 6033.5113 | 6472.677 | 6945.5368 | 7454.7532 | 8003.2029 | 8587.7375 | 9211.8493 | 9880.6776 | 10596.3207 | 11360.4468 | 12174.008 | 13036.824 | 13946.9795 | 14899.9553 | 15887.3772 | 16895.2192 | 17901.2252 | 18871.2118
| FALSE | 509 | 22013371 | BC | BC012 | 11 | BC2 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 1.7651 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 4.512 |  | 7.1689 | 0.021401 | 1.6837e-05 | 0.021384 | 58.8568 | 1.347 | 60.2038 | 60.8442 | 8.5626 | 18.6847 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 4.512 |  | 35.8109 | 148.2954 | 35.8109 | 112.4845 |  | 0.14015 |  | 2.0307 | 2.3362 | 2.6877 | 3.0921 | 3.5573 | 4.0924 | 4.7082 | 5.4165 | 6.2314 | 7.1689 | 8.2475 | 9.4883 | 10.9158 | 12.5581 | 14.4475 | 16.6211 | 19.1217 | 21.9985 | 25.3082 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054426 | 0.0075349 | 0.01056 | 0.014961 | 0.021401 | 0.030869 | 0.044852 | 0.065583 | 0.096424 | 0.14244 | 0.21128 | 0.3145 | 0.46958 | 0.70298 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.282e-06 | 5.9282e-06 | 8.3082e-06 | 1.1771e-05 | 1.6837e-05 | 2.4287e-05 | 3.5288e-05 | 5.1599e-05 | 7.5863e-05 | 0.00011207 | 0.00016623 | 0.00024744 | 0.00036945 | 0.00055308 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 37.7138 | 52.2125 | 73.175 | 103.6737 | 148.2954 | 213.9054 | 310.801 | 454.4562 | 668.1629 | 987.0322 | 1464.0589 | 2179.3207 | 3253.9378 | 4871.2647 | 6525.8611 | 6525.8611 | 6525.8611 | 6525.8611 | 6525.8611 | 6525.8611 | 6525.8611 | 6525.8611 | 6525.8611 | 6525.8611 | 6525.8611 |  | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 35.8109 | 42.8633 | 56.8179 | 75.9732 | 102.3861 | 138.955 | 189.7722 | 260.624 | 359.7044 | 498.6316 | 693.8976 | 968.9368 | 1357.0797 | 1905.7696 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.9682 | 20.7226 | 29.0424 | 41.147 | 58.8568 | 84.8967 | 123.3536 | 180.3688 | 265.1867 | 391.7424 | 581.0692 | 864.9489 | 1291.4529 | 1933.3525 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0.75527 | 6.5096 | 14.8294 | 26.934 | 44.6439 | 70.6838 | 109.1406 | 166.1558 | 250.9737 | 377.5295 | 566.8562 | 850.736 | 1274.4409 | 1910.8021 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.34256 | 0.47425 | 0.66466 | 0.94168 | 1.347 | 1.9429 | 2.8231 | 4.1279 | 6.069 | 8.9654 | 13.2983 | 19.7951 | 29.556 | 44.2464 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.38933 | 0.51609 | 0.69008 | 0.92999 | 1.2621 | 1.7237 | 2.3673 | 3.2672 | 4.5291 | 6.3028 | 8.801 | 12.3265 | 17.3104 |  | 0 | 0 | 0 | 0 | 0 | 0.017285 | 0.14898 | 0.33938 | 0.61641 | 1.0217 | 1.6177 | 2.4978 | 3.8026 | 5.7437 | 8.6401 | 12.973 | 19.4698 | 29.1667 | 43.7303 | 58.5853 | 58.3453 | 58.0132 | 57.5516 | 56.908 | 56.0081 | 54.7462 | 52.9726 | 50.4743 | 46.9488 | 41.965 |  | 0 | 0 | 0 | 0 | 0 | 0.77256 | 6.6586 | 15.1688 | 27.5504 | 45.6656 | 72.3015 | 111.6384 | 169.9584 | 256.7175 | 386.1696 | 579.8292 | 870.2058 | 1303.6075 | 1954.5324 | 2618.4762 | 2607.7534 | 2592.9074 | 2572.277 | 2543.5132 | 2503.2892 | 2446.8886 | 2367.616 | 2255.9577 | 2098.3824 | 1875.6295 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 15.4736 | 21.4223 | 30.0231 | 42.5364 | 60.8442 | 87.7634 | 127.5188 | 186.4593 | 274.1412 | 404.9704 | 600.6901 | 894.1556 | 1335.0612 | 1998.6358 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0.78078 | 6.7294 | 15.3302 | 27.8435 | 46.1514 | 73.0706 | 112.826 | 171.7664 | 259.4483 | 390.2775 | 585.9972 | 879.4627 | 1317.4748 | 1975.3239 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1776 | 3.0148 | 4.2252 | 5.9862 | 8.5626 | 12.351 | 17.9458 | 26.2405 | 38.58 | 56.9916 | 84.5353 | 125.8348 | 187.8836 | 281.2686 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0.10988 | 0.94704 | 2.1574 | 3.9184 | 6.4949 | 10.2832 | 15.878 | 24.1727 | 36.5122 | 54.9239 | 82.4676 | 123.767 | 185.4086 | 277.9879 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.7518 | 6.5786 | 9.2198 | 13.0625 | 18.6847 | 26.9513 | 39.1598 | 57.2598 | 84.1861 | 124.3624 | 184.466 | 274.5864 | 409.9842 | 613.7614 | 822.2345 | 822.2345 | 822.2345 | 822.2345 | 822.2345 | 822.2345 | 822.2345 | 822.2345 | 822.2345 | 822.2345 | 822.2345 |  | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 4.512 | 5.4006 | 7.1588 | 9.5723 | 12.9003 | 17.5078 | 23.9106 | 32.8377 | 45.3214 | 62.8258 | 87.4285 | 122.0825 | 170.987 | 240.12 |  | 0 | 0 | 0 | 0 | 0 | 0.23977 | 2.0665 | 4.7077 | 8.5505 | 14.1726 | 22.4393 | 34.6477 | 52.7478 | 79.674 | 119.8504 | 179.954 | 270.0744 | 404.5836 | 606.6026 | 812.6622 | 809.3342 | 804.7267 | 798.3239 | 789.3968 | 776.9131 | 759.4088 | 734.806 | 700.152 | 651.2475 | 582.1146 |  | 0 | 0 | 0 | 0 | 0 | 1.903 | 16.4016 | 37.3642 | 67.8628 | 112.4845 | 178.0945 | 274.9901 | 418.6453 | 632.3521 | 951.2213 | 1428.248 | 2143.5099 | 3211.0745 | 4814.4468 | 6449.8879 | 6423.475 | 6386.9061 | 6336.089 | 6265.2372 | 6166.1567 | 6027.2295 | 5831.9635 | 5556.9243 | 5168.7815 | 4620.0916
| TRUE | 510 | 22013853 | BC | BC020 | 11 | BC20 | SENSITIVE EF | Blank | RPL | ARTC_650 | ARTC 650 | AVE | Electromechanical |  | 0.57434 | 2190 |  | 2.5292 | 0.00090442 | 0.00065051 | 0.00025391 | 2.6661 | 52.0408 | 54.7069 | 6.2604 | 0.36836 | 538.4938 |  | 4.7392 | 0.0013394 | 0.00096335 | 0.00037602 | 3.9482 | 77.0677 | 81.0159 | 9.2711 | 0.54551 | 797.4598 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 3.3658 |  | 599.8294 | 888.2922 | 34.6646 | 853.6276 |  | 0.062797 |  | 2.6931 | 2.8677 | 3.0535 | 3.2514 | 3.4622 | 3.6865 | 3.9255 | 4.1799 | 4.4508 | 4.7392 | 5.0464 | 5.3734 | 5.7217 | 6.0925 | 6.4874 | 6.9078 | 7.3555 | 7.8322 | 8.3398 | 8.8804 | 9.4559 | 10.0687 | 10.7213 | 11.4161 | 12.156 | 12.9438 | 13.7827 | 14.676 | 15.6272 | 16.64 |  | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00099954 | 0.0011556 | 0.0013394 | 0.0015562 | 0.0018123 | 0.0021153 | 0.002474 | 0.0028992 | 0.0034038 | 0.0040031 | 0.0047157 | 0.0055637 | 0.0065737 | 0.0077776 | 0.0092136 | 0.010928 | 0.012976 | 0.015423 | 0.018351 | 0.021854 | 0.026048 | 0.031073 | 0.037095 |  | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00071893 | 0.00083114 | 0.00096335 | 0.0011193 | 0.0013035 | 0.0015214 | 0.0017794 | 0.0020853 | 0.0024482 | 0.0028793 | 0.0033918 | 0.0040017 | 0.0047282 | 0.005594 | 0.006627 | 0.00786 | 0.0093328 | 0.011093 | 0.013199 | 0.015719 | 0.018735 | 0.022349 | 0.02668 | 599.8294 | 599.8294 | 599.8294 | 599.8294 | 599.8294 | 599.8294 | 599.8294 | 662.9157 | 766.3885 | 888.2922 | 1032.1047 | 1201.9825 | 1402.8967 | 1640.7955 | 1922.8 | 2257.4394 | 2654.9344 | 3127.5376 | 3689.9441 | 4359.7842 | 5158.2186 | 6110.6529 | 7247.6001 | 8605.7179 | 10229.059 | 12170.5778 | 14493.9449 | 17275.7346 | 20608.0609 | 24601.7552 |  | 34.6646 | 34.6646 | 34.6646 | 34.6646 | 34.6646 | 34.6646 | 34.6646 | 34.6646 | 34.6646 | 34.6646 | 34.6646 | 34.6646 | 34.6646 | 34.6646 | 34.6646 | 34.6646 | 34.6646 | 41.4914 | 54.9993 | 73.5415 | 99.1089 | 134.5073 | 183.6979 | 252.2818 | 348.1909 | 482.6713 | 671.6871 | 937.9229 | 1313.6419 | 1844.7692 |  | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.9465 | 3.4064 | 3.9482 | 4.5874 | 5.3424 | 6.2354 | 7.2928 | 8.5462 | 10.0336 | 11.8003 | 13.9009 | 16.4006 | 19.3779 | 22.9267 | 27.1599 | 32.2133 | 38.2497 | 45.4649 | 54.0944 | 64.421 | 76.7852 | 91.5963 | 109.347 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.2665 | -10.8066 | -10.2648 | -9.6256 | -8.8705 | -7.9775 | -6.9201 | -5.6667 | -4.1793 | -2.4126 | -3.1111 | -6.1498 | -10.7751 | -17.7093 | -27.9898 | -43.1052 | -65.1891 | -97.2979 | -143.8071 | -210.9795 | -307.7754 | -447.014 | -647.0324 |  | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 57.5142 | 66.4914 | 77.0677 | 89.5448 | 104.2833 | 121.7144 | 142.3544 | 166.8209 | 195.854 | 230.3405 | 271.3432 | 320.1373 | 378.2522 | 447.5238 | 530.1564 | 628.7973 | 746.6267 | 887.4668 | 1055.9118 | 1257.4856 | 1498.832 | 1787.9425 | 2134.433 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.38933 | 0.51609 | 0.69008 | 0.92999 | 1.2621 | 1.7237 | 2.3673 | 3.2672 | 4.5291 | 6.3028 | 8.801 | 12.3265 | 17.3104 |  | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 57.1889 | 66.1661 | 76.7424 | 89.2195 | 103.958 | 121.3892 | 142.0291 | 166.4957 | 195.5288 | 230.0152 | 270.9539 | 319.6212 | 377.5621 | 446.5938 | 528.8943 | 627.0735 | 744.2594 | 884.1996 | 1051.3826 | 1251.1829 | 1490.031 | 1775.616 | 2117.1226 |  | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 45.9224 | 55.3595 | 66.4776 | 79.5939 | 95.0875 | 113.4117 | 135.109 | 160.829 | 191.3494 | 227.6026 | 267.8428 | 313.4714 | 366.787 | 428.8846 | 500.9045 | 583.9683 | 679.0703 | 786.9017 | 907.5755 | 1040.2034 | 1182.2556 | 1328.602 | 1470.0902 |  | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.9188 | 7.9988 | 9.2711 | 10.7721 | 12.5451 | 14.642 | 17.1249 | 20.0682 | 23.5608 | 27.7095 | 32.642 | 38.5119 | 45.503 | 53.8362 | 63.7768 | 75.643 | 89.8177 | 106.7605 | 127.0241 | 151.273 | 180.3065 | 215.0859 | 256.768 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -7.774 | -6.6941 | -5.4218 | -3.9208 | -2.1478 | -0.050867 | 2.4321 | 5.3754 | 8.868 | 13.0166 | 15.0556 | 15.2 | 14.3318 | 11.8281 | 6.7648 | -2.2188 | -17.114 | -40.823 | -77.56 | -133.4269 | -217.2395 | -341.7116 | -525.152 |  | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.40711 | 0.47065 | 0.54551 | 0.63383 | 0.73816 | 0.86154 | 1.0076 | 1.1808 | 1.3863 | 1.6304 | 1.9207 | 2.2661 | 2.6774 | 3.1677 | 3.7526 | 4.4509 | 5.2849 | 6.2818 | 7.4741 | 8.901 | 10.6093 | 12.6557 | 15.1083 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6606 | -1.5971 | -1.5222 | -1.4339 | -1.3296 | -1.2062 | -1.0601 | -0.88691 | -0.6814 | -0.4373 | -0.55428 | -1.0146 | -1.7093 | -2.7441 | -4.2707 | -6.5066 | -9.7636 | -14.4876 | -21.317 | -31.1649 | -45.3375 | -65.7025 | -94.9315 |  | 538.4938 | 538.4938 | 538.4938 | 538.4938 | 538.4938 | 538.4938 | 538.4938 | 595.1292 | 688.0213 | 797.4598 | 926.5666 | 1079.0736 | 1259.4433 | 1473.0157 | 1726.1838 | 2026.6046 | 2383.4537 | 2807.7308 | 3312.6283 | 3913.9738 | 4630.7641 | 5485.8071 | 6506.4956 | 7725.7388 | 9183.085 | 10926.0735 | 13011.8643 | 15509.2016 | 18500.7804 | 22086.0989 |  | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 4.0286 | 5.3402 | 7.1406 | 9.6231 | 13.0601 | 17.8363 | 24.4955 | 33.8079 | 46.8654 | 65.2181 | 91.0685 | 127.5493 | 179.1196 |  | 535.128 | 535.128 | 535.128 | 535.128 | 535.128 | 535.128 | 535.128 | 591.7634 | 684.6555 | 794.094 | 923.2008 | 1075.7078 | 1256.0775 | 1469.6499 | 1722.818 | 2023.2388 | 2380.0879 | 2803.7021 | 3307.2881 | 3906.8332 | 4621.1411 | 5472.747 | 6488.6593 | 7701.2433 | 9149.2771 | 10879.2081 | 12946.6462 | 15418.1331 | 18373.2311 | 21906.9793 |  | 565.1648 | 565.1648 | 565.1648 | 565.1648 | 565.1648 | 565.1648 | 565.1648 | 628.2511 | 731.7239 | 853.6276 | 997.4401 | 1167.3179 | 1368.2321 | 1606.1309 | 1888.1354 | 2222.7748 | 2620.2698 | 3086.0463 | 3634.9448 | 4286.2428 | 5059.1097 | 5976.1456 | 7063.9022 | 8353.436 | 9880.8681 | 11687.9065 | 13822.2578 | 16337.8117 | 19294.419 | 22756.9861
| TRUE | 511 | 22005262 | BC | BC020 | 11 | BC20 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 5240.6366 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 13043.115 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 3.3658 |  | 7382.8914 | 18374.8482 | 49.8534 | 18324.9948 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 8076.8124 | 8838.8518 | 9675.8531 | 10595.3573 | 11605.6748 | 12715.9638 | 13936.3186 | 15277.8654 | 16752.8685 | 18374.8482 | 20158.7101 | 22120.888 | 24279.5016 | 26654.5312 | 29268.0091 | 32144.2326 | 35309.9977 | 38794.8579 | 42631.4092 | 46855.6058 | 51507.1071 | 56629.6624 | 62271.5339 | 68485.9655 | 75331.6985 | 82873.5426 | 91183.005 | 100338.986 | 110428.5462 | 121547.7541 |  | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 42.6741 | 56.567 | 75.6378 | 101.934 | 138.3415 | 188.9342 | 259.4732 | 358.1162 | 496.43 | 690.8338 | 964.6586 | 1351.0876 | 1897.3549 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 5733.2062 | 6274.1286 | 6868.2616 | 7520.9582 | 8238.1171 | 9026.2394 | 9892.4903 | 10844.7674 | 11891.7766 | 13043.115 | 14309.3631 | 15702.1861 | 17234.4462 | 18920.3259 | 20775.4647 | 22817.1095 | 25064.2812 | 27537.9578 | 30261.2772 | 33259.7608 | 36561.5605 | 40197.7308 | 44202.5301 | 48613.7527 | 53473.0954 | 58826.5622 | 64724.9115 | 71224.1496 | 78386.0752 | 86278.8809 |  | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 4.0286 | 5.3402 | 7.1406 | 9.6231 | 13.0601 | 17.8363 | 24.4955 | 33.8079 | 46.8654 | 65.2181 | 91.0685 | 127.5493 | 179.1196 |  | 5729.8404 | 6270.7628 | 6864.8958 | 7517.5924 | 8234.7513 | 9022.8736 | 9889.1245 | 10841.4017 | 11888.4109 | 13039.7493 | 14305.9973 | 15698.8203 | 17231.0804 | 18916.9601 | 20772.0989 | 22813.7437 | 25060.9154 | 27533.9292 | 30255.937 | 33252.6202 | 36551.9374 | 40184.6707 | 44184.6938 | 48589.2572 | 53439.2874 | 58779.6967 | 64659.6934 | 71133.0811 | 78258.5259 | 86099.7614 |  | 8041.172 | 8803.2113 | 9640.2126 | 10559.7169 | 11570.0343 | 12680.3234 | 13900.6782 | 15242.2249 | 16717.228 | 18339.2078 | 20123.0697 | 22085.2475 | 24243.8612 | 26618.8907 | 29232.3687 | 32108.5922 | 35274.3573 | 38752.1985 | 42574.8617 | 46779.9941 | 51405.2082 | 56491.3686 | 62082.6649 | 68226.5818 | 74973.7059 | 82377.2838 | 90492.4095 | 99374.6601 | 109077.9246 | 119651.0538
| TRUE | 512 | 22005263 | BC | BC020 | 11 | BC20 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 5240.6366 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 13043.115 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 3.3658 |  | 7382.8914 | 18374.8482 | 49.8534 | 18324.9948 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 8076.8124 | 8838.8518 | 9675.8531 | 10595.3573 | 11605.6748 | 12715.9638 | 13936.3186 | 15277.8654 | 16752.8685 | 18374.8482 | 20158.7101 | 22120.888 | 24279.5016 | 26654.5312 | 29268.0091 | 32144.2326 | 35309.9977 | 38794.8579 | 42631.4092 | 46855.6058 | 51507.1071 | 56629.6624 | 62271.5339 | 68485.9655 | 75331.6985 | 82873.5426 | 91183.005 | 100338.986 | 110428.5462 | 121547.7541 |  | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 35.6527 | 42.6741 | 56.567 | 75.6378 | 101.934 | 138.3415 | 188.9342 | 259.4732 | 358.1162 | 496.43 | 690.8338 | 964.6586 | 1351.0876 | 1897.3549 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 5733.2062 | 6274.1286 | 6868.2616 | 7520.9582 | 8238.1171 | 9026.2394 | 9892.4903 | 10844.7674 | 11891.7766 | 13043.115 | 14309.3631 | 15702.1861 | 17234.4462 | 18920.3259 | 20775.4647 | 22817.1095 | 25064.2812 | 27537.9578 | 30261.2772 | 33259.7608 | 36561.5605 | 40197.7308 | 44202.5301 | 48613.7527 | 53473.0954 | 58826.5622 | 64724.9115 | 71224.1496 | 78386.0752 | 86278.8809 |  | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 3.3658 | 4.0286 | 5.3402 | 7.1406 | 9.6231 | 13.0601 | 17.8363 | 24.4955 | 33.8079 | 46.8654 | 65.2181 | 91.0685 | 127.5493 | 179.1196 |  | 5729.8404 | 6270.7628 | 6864.8958 | 7517.5924 | 8234.7513 | 9022.8736 | 9889.1245 | 10841.4017 | 11888.4109 | 13039.7493 | 14305.9973 | 15698.8203 | 17231.0804 | 18916.9601 | 20772.0989 | 22813.7437 | 25060.9154 | 27533.9292 | 30255.937 | 33252.6202 | 36551.9374 | 40184.6707 | 44184.6938 | 48589.2572 | 53439.2874 | 58779.6967 | 64659.6934 | 71133.0811 | 78258.5259 | 86099.7614 |  | 8041.172 | 8803.2113 | 9640.2126 | 10559.7169 | 11570.0343 | 12680.3234 | 13900.6782 | 15242.2249 | 16717.228 | 18339.2078 | 20123.0697 | 22085.2475 | 24243.8612 | 26618.8907 | 29232.3687 | 32108.5922 | 35274.3573 | 38752.1985 | 42574.8617 | 46779.9941 | 51405.2082 | 56491.3686 | 62082.6649 | 68226.5818 | 74973.7059 | 82377.2838 | 90492.4095 | 99374.6601 | 109077.9246 | 119651.0538
| TRUE | 513 | 22015704 | BC | BC020 | 11 | BC20 | AUTO RECLOSE | Blank | English Electric | GROUP_624 | GROUP 624 | GROUP 000s | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 53.114 | 1051.8847 | 1104.9987 | 45.1415 | 3.7652 | 2721.1008 |  | 7.1791 | 0.018276 | 0.00644 | 0.011836 | 104.0585 | 2060.8049 | 2164.8634 | 88.4392 | 7.3765 | 5331.0576 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 28.4243 | 0.35573 | 28.78 | 14.6761 | 2.0677 | 0.92023 |  | 3875.0062 | 7591.7368 | 46.444 | 7545.2927 |  | 0.026643 |  | 5.6485 | 5.801 | 5.9577 | 6.1185 | 6.2837 | 6.4534 | 6.6277 | 6.8066 | 6.9904 | 7.1791 | 7.373 | 7.5721 | 7.7765 | 7.9865 | 8.2022 | 8.4236 | 8.6511 | 8.8847 | 9.1246 | 9.3709 | 9.624 | 9.8838 | 10.1507 | 10.4248 | 10.7063 | 10.9954 | 11.2923 | 11.5972 | 11.9103 | 12.2319 |  | 0.0099614 | 0.010641 | 0.011372 | 0.012157 | 0.013001 | 0.013908 | 0.014884 | 0.015933 | 0.017062 | 0.018276 | 0.019582 | 0.020988 | 0.022502 | 0.024131 | 0.025885 | 0.027774 | 0.029809 | 0.032001 | 0.034362 | 0.036906 | 0.039648 | 0.042603 | 0.045789 | 0.049223 | 0.052926 | 0.056919 | 0.061224 | 0.065869 | 0.070879 | 0.076283 |  | 0.0035102 | 0.0037498 | 0.0040073 | 0.0042839 | 0.0045813 | 0.004901 | 0.0052448 | 0.0056145 | 0.0060122 | 0.00644 | 0.0069004 | 0.0073958 | 0.0079291 | 0.0085032 | 0.0091214 | 0.0097871 | 0.010504 | 0.011276 | 0.012109 | 0.013005 | 0.013971 | 0.015013 | 0.016135 | 0.017345 | 0.01865 | 0.020057 | 0.021574 | 0.023211 | 0.024976 | 0.026881 | 4137.9621 | 4420.4322 | 4723.9267 | 5050.0759 | 5400.6398 | 5777.5181 | 6182.7623 | 6618.5872 | 7087.3843 | 7591.7368 | 8134.4339 | 8718.4887 | 9347.1556 | 10023.9501 | 10752.6703 | 11537.4193 | 12382.6305 | 13293.0943 | 14273.9873 | 15330.9035 | 16469.8885 | 17697.4764 | 19020.7295 | 20447.2815 | 21985.3844 | 23643.9586 | 25432.6478 | 27361.8782 | 29442.9226 | 31687.9694 |  | 32.2353 | 32.2353 | 32.2353 | 32.2353 | 32.2353 | 32.2353 | 32.2353 | 32.2353 | 32.2353 | 32.2353 | 32.2353 | 32.2353 | 32.2353 | 32.2353 | 32.2353 | 32.2353 | 32.2353 | 38.5836 | 51.1448 | 68.3876 | 92.1632 | 125.0808 | 170.824 | 234.6015 | 323.7891 | 448.8449 | 624.6141 | 872.1916 | 1221.5796 | 1715.4845 |  | 56.7183 | 60.59 | 64.75 | 69.2205 | 74.0256 | 79.1914 | 84.746 | 90.7197 | 97.1455 | 104.0585 | 111.4972 | 119.5027 | 128.1197 | 137.3964 | 147.3849 | 158.1413 | 169.7264 | 182.206 | 195.6509 | 210.1379 | 225.7497 | 242.576 | 260.7136 | 280.2671 | 301.3496 | 324.0834 | 348.6006 | 375.0442 | 403.5687 | 434.3411 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 42.5062 | 46.3779 | 50.5379 | 55.0083 | 59.8134 | 64.9792 | 70.5338 | 76.5076 | 82.9333 | 89.8464 | 97.2851 | 105.2906 | 113.9076 | 123.1843 | 133.1727 | 143.9291 | 155.5143 | 165.195 | 173.1018 | 179.9866 | 185.1161 | 187.4294 | 185.3994 | 176.8342 | 158.5949 | 126.1931 | 73.2159 | -9.4944 | -135.0108 | -321.995 |  | 1123.265 | 1199.9426 | 1282.3273 | 1370.8617 | 1466.0235 | 1568.3286 | 1678.3336 | 1796.6398 | 1923.8966 | 2060.8049 | 2208.122 | 2366.6659 | 2537.3198 | 2721.0382 | 2918.8519 | 3131.8749 | 3361.3106 | 3608.4594 | 3874.7264 | 4161.6302 | 4470.8119 | 4804.0451 | 5163.247 | 5550.4898 | 5968.0135 | 6418.2396 | 6903.7858 | 7427.4825 | 7992.3897 | 8601.8159 |  | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.42579 | 0.56441 | 0.75469 | 1.0171 | 1.3803 | 1.8851 | 2.5889 | 3.5732 | 4.9532 | 6.8929 | 9.625 | 13.4807 | 18.9311 |  | 1122.9093 | 1199.5868 | 1281.9715 | 1370.506 | 1465.6678 | 1567.9728 | 1677.9779 | 1796.2841 | 1923.5408 | 2060.4492 | 2207.7663 | 2366.3101 | 2536.9641 | 2720.6824 | 2918.4962 | 3131.5192 | 3360.9549 | 3608.0336 | 3874.162 | 4160.8755 | 4469.7948 | 4802.6648 | 5161.3619 | 5547.9009 | 5964.4404 | 6413.2864 | 6896.8929 | 7417.8575 | 7978.909 | 8582.8848 |  | 1165.4155 | 1245.9648 | 1332.5094 | 1425.5143 | 1525.4813 | 1632.9521 | 1748.5117 | 1872.7917 | 2006.4742 | 2150.2956 | 2305.0513 | 2471.6007 | 2650.8717 | 2843.8667 | 3051.6689 | 3275.4483 | 3516.4692 | 3773.2285 | 4047.2638 | 4340.8621 | 4654.9109 | 4990.0942 | 5346.7613 | 5724.7351 | 6123.0353 | 6539.4795 | 6970.1088 | 7408.3631 | 7843.8982 | 8260.8898 |  | 48.2048 | 51.4954 | 55.031 | 58.8304 | 62.9143 | 67.3047 | 72.0255 | 77.1026 | 82.5638 | 88.4392 | 94.7613 | 101.5652 | 108.8888 | 116.7731 | 125.2623 | 134.4041 | 144.2503 | 154.8567 | 166.2835 | 178.596 | 191.8645 | 206.1651 | 221.5803 | 238.1987 | 256.1167 | 275.4381 | 296.2753 | 318.7497 | 342.9926 | 369.1461 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 33.5287 | 36.8193 | 40.3549 | 44.1543 | 48.2382 | 52.6286 | 57.3494 | 62.4265 | 67.8877 | 73.7631 | 80.0852 | 86.8891 | 94.2127 | 102.097 | 110.5862 | 119.728 | 129.5742 | 137.2903 | 142.9983 | 147.4604 | 149.9043 | 149.2182 | 143.8073 | 131.3892 | 108.7017 | 71.0876 | 11.9004 | -78.3425 | -213.1693 | -411.8813 |  | 4.0207 | 4.2951 | 4.59 | 4.9069 | 5.2475 | 5.6137 | 6.0075 | 6.431 | 6.8865 | 7.3765 | 7.9038 | 8.4713 | 9.0822 | 9.7398 | 10.4478 | 11.2103 | 12.0316 | 12.9163 | 13.8693 | 14.8963 | 16.003 | 17.1958 | 18.4815 | 19.8676 | 21.3621 | 22.9737 | 24.7117 | 26.5862 | 28.6083 | 30.7897 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 1.953 | 2.2274 | 2.5223 | 2.8392 | 3.1798 | 3.546 | 3.9398 | 4.3633 | 4.8188 | 5.3088 | 5.8361 | 6.4036 | 7.0145 | 7.6721 | 8.3801 | 9.1426 | 9.9639 | 10.4413 | 10.5887 | 10.5096 | 10.0913 | 9.1726 | 7.5242 | 4.8193 | 0.59296 | -5.8171 | -15.3537 | -29.3598 | -49.7489 | -79.2486 |  | 2905.7533 | 3104.109 | 3317.2284 | 3546.2565 | 3792.4289 | 4057.0798 | 4341.6497 | 4647.694 | 4976.892 | 5331.0576 | 5712.1495 | 6122.2836 | 6563.7451 | 7039.0027 | 7550.7234 | 8101.7886 | 8695.3115 | 9334.656 | 10023.4572 | 10765.6432 | 11565.4595 | 12427.4943 | 13356.7071 | 14358.4582 | 15438.5424 | 16603.2238 | 17859.2744 | 19214.0156 | 20675.3633 | 22251.8766 |  | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 0.92023 | 1.1015 | 1.4601 | 1.9523 | 2.631 | 3.5707 | 4.8766 | 6.6973 | 9.2433 | 12.8133 | 17.8311 | 24.8988 | 34.8729 | 48.9726 |  | 2904.8331 | 3103.1888 | 3316.3082 | 3545.3362 | 3791.5086 | 4056.1596 | 4340.7295 | 4646.7737 | 4975.9718 | 5330.1374 | 5711.2293 | 6121.3634 | 6562.8248 | 7038.0824 | 7549.8032 | 8100.8684 | 8694.3913 | 9333.5546 | 10021.9971 | 10763.6909 | 11562.8285 | 12423.9236 | 13351.8305 | 14351.761 | 15429.2991 | 16590.4105 | 17841.4433 | 19189.1168 | 20640.4904 | 22202.904 |  | 4105.7302 | 4388.2003 | 4691.6948 | 5017.844 | 5368.4079 | 5745.2863 | 6150.5304 | 6586.3553 | 7055.1525 | 7559.5049 | 8102.202 | 8686.2568 | 9314.9237 | 9991.7182 | 10720.4384 | 11505.1874 | 12350.3986 | 13254.5148 | 14222.8479 | 15262.5231 | 16377.735 | 17572.4086 | 18849.9233 | 20212.7045 | 21661.6291 | 23195.1605 | 24808.0988 | 26489.7776 | 28221.4705 | 29972.6638
| TRUE | 514 | 22013854 | BC | BC022 | 11 | BC22 | SENSITIVE EF | Blank | RPL | ARTC_650 | ARTC 650 | AVE | Electromechanical |  | 0.57434 | 2190 |  | 2.5292 | 0.00090442 | 0.00065051 | 0.00025391 | 2.6661 | 52.0408 | 54.7069 | 6.2604 | 0.36836 | 269.2469 |  | 4.7392 | 0.0013394 | 0.00096335 | 0.00037602 | 3.9482 | 77.0677 | 81.0159 | 9.2711 | 0.54551 | 398.7299 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 1.6829 |  | 330.5825 | 489.5623 | 32.9817 | 456.5806 |  | 0.062797 |  | 2.6931 | 2.8677 | 3.0535 | 3.2514 | 3.4622 | 3.6865 | 3.9255 | 4.1799 | 4.4508 | 4.7392 | 5.0464 | 5.3734 | 5.7217 | 6.0925 | 6.4874 | 6.9078 | 7.3555 | 7.8322 | 8.3398 | 8.8804 | 9.4559 | 10.0687 | 10.7213 | 11.4161 | 12.156 | 12.9438 | 13.7827 | 14.676 | 15.6272 | 16.64 |  | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00099954 | 0.0011556 | 0.0013394 | 0.0015562 | 0.0018123 | 0.0021153 | 0.002474 | 0.0028992 | 0.0034038 | 0.0040031 | 0.0047157 | 0.0055637 | 0.0065737 | 0.0077776 | 0.0092136 | 0.010928 | 0.012976 | 0.015423 | 0.018351 | 0.021854 | 0.026048 | 0.031073 | 0.037095 |  | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00071893 | 0.00083114 | 0.00096335 | 0.0011193 | 0.0013035 | 0.0015214 | 0.0017794 | 0.0020853 | 0.0024482 | 0.0028793 | 0.0033918 | 0.0040017 | 0.0047282 | 0.005594 | 0.006627 | 0.00786 | 0.0093328 | 0.011093 | 0.013199 | 0.015719 | 0.018735 | 0.022349 | 0.02668 | 330.5825 | 330.5825 | 330.5825 | 330.5825 | 330.5825 | 330.5825 | 330.5825 | 365.3511 | 422.3778 | 489.5623 | 568.8213 | 662.4457 | 773.1751 | 904.2877 | 1059.7081 | 1244.1371 | 1463.2076 | 1723.6722 | 2033.6299 | 2402.7973 | 2842.8365 | 3367.7493 | 3994.3523 | 4742.8485 | 5637.5165 | 6707.5411 | 7988.0128 | 9521.1338 | 11357.6707 | 13558.7058 |  | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 39.477 | 52.3292 | 69.9712 | 94.2974 | 127.9773 | 174.7797 | 240.0341 | 331.287 | 459.2386 | 639.0781 | 892.3886 | 1249.8673 | 1755.2094 |  | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.9465 | 3.4064 | 3.9482 | 4.5874 | 5.3424 | 6.2354 | 7.2928 | 8.5462 | 10.0336 | 11.8003 | 13.9009 | 16.4006 | 19.3779 | 22.9267 | 27.1599 | 32.2133 | 38.2497 | 45.4649 | 54.0944 | 64.421 | 76.7852 | 91.5963 | 109.347 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.2665 | -10.8066 | -10.2648 | -9.6256 | -8.8705 | -7.9775 | -6.9201 | -5.6667 | -4.1793 | -2.4126 | -3.1111 | -6.1498 | -10.7751 | -17.7093 | -27.9898 | -43.1052 | -65.1891 | -97.2979 | -143.8071 | -210.9795 | -307.7754 | -447.014 | -647.0324 |  | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 57.5142 | 66.4914 | 77.0677 | 89.5448 | 104.2833 | 121.7144 | 142.3544 | 166.8209 | 195.854 | 230.3405 | 271.3432 | 320.1373 | 378.2522 | 447.5238 | 530.1564 | 628.7973 | 746.6267 | 887.4668 | 1055.9118 | 1257.4856 | 1498.832 | 1787.9425 | 2134.433 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.38933 | 0.51609 | 0.69008 | 0.92999 | 1.2621 | 1.7237 | 2.3673 | 3.2672 | 4.5291 | 6.3028 | 8.801 | 12.3265 | 17.3104 |  | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 57.1889 | 66.1661 | 76.7424 | 89.2195 | 103.958 | 121.3892 | 142.0291 | 166.4957 | 195.5288 | 230.0152 | 270.9539 | 319.6212 | 377.5621 | 446.5938 | 528.8943 | 627.0735 | 744.2594 | 884.1996 | 1051.3826 | 1251.1829 | 1490.031 | 1775.616 | 2117.1226 |  | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 45.9224 | 55.3595 | 66.4776 | 79.5939 | 95.0875 | 113.4117 | 135.109 | 160.829 | 191.3494 | 227.6026 | 267.8428 | 313.4714 | 366.787 | 428.8846 | 500.9045 | 583.9683 | 679.0703 | 786.9017 | 907.5755 | 1040.2034 | 1182.2556 | 1328.602 | 1470.0902 |  | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.9188 | 7.9988 | 9.2711 | 10.7721 | 12.5451 | 14.642 | 17.1249 | 20.0682 | 23.5608 | 27.7095 | 32.642 | 38.5119 | 45.503 | 53.8362 | 63.7768 | 75.643 | 89.8177 | 106.7605 | 127.0241 | 151.273 | 180.3065 | 215.0859 | 256.768 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -7.774 | -6.6941 | -5.4218 | -3.9208 | -2.1478 | -0.050867 | 2.4321 | 5.3754 | 8.868 | 13.0166 | 15.0556 | 15.2 | 14.3318 | 11.8281 | 6.7648 | -2.2188 | -17.114 | -40.823 | -77.56 | -133.4269 | -217.2395 | -341.7116 | -525.152 |  | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.40711 | 0.47065 | 0.54551 | 0.63383 | 0.73816 | 0.86154 | 1.0076 | 1.1808 | 1.3863 | 1.6304 | 1.9207 | 2.2661 | 2.6774 | 3.1677 | 3.7526 | 4.4509 | 5.2849 | 6.2818 | 7.4741 | 8.901 | 10.6093 | 12.6557 | 15.1083 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6606 | -1.5971 | -1.5222 | -1.4339 | -1.3296 | -1.2062 | -1.0601 | -0.88691 | -0.6814 | -0.4373 | -0.55428 | -1.0146 | -1.7093 | -2.7441 | -4.2707 | -6.5066 | -9.7636 | -14.4876 | -21.317 | -31.1649 | -45.3375 | -65.7025 | -94.9315 |  | 269.2469 | 269.2469 | 269.2469 | 269.2469 | 269.2469 | 269.2469 | 269.2469 | 297.5646 | 344.0107 | 398.7299 | 463.2833 | 539.5368 | 629.7216 | 736.5079 | 863.0919 | 1013.3023 | 1191.7268 | 1403.8654 | 1656.3141 | 1956.9869 | 2315.3821 | 2742.9036 | 3253.2478 | 3862.8694 | 4591.5425 | 5463.0368 | 6505.9322 | 7754.6008 | 9250.3902 | 11043.0495 |  | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 2.0143 | 2.6701 | 3.5703 | 4.8115 | 6.5301 | 8.9182 | 12.2478 | 16.904 | 23.4327 | 32.609 | 45.5342 | 63.7746 | 89.5598 |  | 267.564 | 267.564 | 267.564 | 267.564 | 267.564 | 267.564 | 267.564 | 295.8817 | 342.3278 | 397.047 | 461.6004 | 537.8539 | 628.0387 | 734.825 | 861.409 | 1011.6194 | 1190.0439 | 1401.8511 | 1653.644 | 1953.4166 | 2310.5705 | 2736.3735 | 3244.3297 | 3850.6217 | 4574.6385 | 5439.604 | 6473.3231 | 7709.0666 | 9186.6156 | 10953.4897 |  | 297.6008 | 297.6008 | 297.6008 | 297.6008 | 297.6008 | 297.6008 | 297.6008 | 332.3694 | 389.3961 | 456.5806 | 535.8396 | 629.464 | 740.1933 | 871.306 | 1026.7264 | 1211.1554 | 1430.2258 | 1684.1952 | 1981.3008 | 2332.8261 | 2748.5391 | 3239.7721 | 3819.5726 | 4502.8144 | 5306.2296 | 6248.3025 | 7348.9347 | 8628.7451 | 10107.8034 | 11803.4964
| TRUE | 515 | 22005265 | BC | BC022 | 11 | BC22 | OVERCURRENT | Blank | English Electric | CDG11_1054 | CDG11 1054 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 2620.3183 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 6521.5575 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 1.6829 |  | 4762.5731 | 11853.2907 | 48.1705 | 11805.1202 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 5210.2093 | 5701.7875 | 6241.7223 | 6834.8782 | 7486.6162 | 8202.8441 | 8990.0735 | 9855.4816 | 10806.9801 | 11853.2907 | 13004.0285 | 14269.7949 | 15662.2785 | 17194.3682 | 18880.2768 | 20735.6779 | 22777.8571 | 25025.879 | 27500.7706 | 30225.7253 | 33226.3269 | 36530.797 | 40170.2689 | 44179.0891 | 48595.1508 | 53460.2615 | 58820.5492 | 64726.9112 | 71235.5086 | 78408.3136 |  | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 40.6598 | 53.8969 | 72.0675 | 97.1225 | 131.8114 | 180.0161 | 247.2254 | 341.2122 | 472.9973 | 658.2247 | 919.1244 | 1287.313 | 1807.7951 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 2866.6031 | 3137.0643 | 3434.1308 | 3760.4791 | 4119.0585 | 4513.1197 | 4946.2451 | 5422.3837 | 5945.8883 | 6521.5575 | 7154.6816 | 7851.0931 | 8617.2231 | 9460.1629 | 10387.7323 | 11408.5548 | 12532.1406 | 13768.9789 | 15130.6386 | 16629.8804 | 18280.7802 | 20098.8654 | 22101.2651 | 24306.8764 | 26736.5477 | 29413.2811 | 32362.4558 | 35612.0748 | 39193.0376 | 43139.4405 |  | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 2.0143 | 2.6701 | 3.5703 | 4.8115 | 6.5301 | 8.9182 | 12.2478 | 16.904 | 23.4327 | 32.609 | 45.5342 | 63.7746 | 89.5598 |  | 2864.9202 | 3135.3814 | 3432.4479 | 3758.7962 | 4117.3756 | 4511.4368 | 4944.5622 | 5420.7008 | 5944.2054 | 6519.8746 | 7152.9987 | 7849.4102 | 8615.5402 | 9458.4801 | 10386.0494 | 11406.8719 | 12530.4577 | 13766.9646 | 15127.9685 | 16626.3101 | 18275.9687 | 20092.3353 | 22092.3469 | 24294.6286 | 26719.6437 | 29389.8484 | 32329.8467 | 35566.5406 | 39129.2629 | 43049.8807 |  | 5176.2518 | 5667.8299 | 6207.7647 | 6800.9207 | 7452.6587 | 8168.8866 | 8956.116 | 9821.5241 | 10773.0226 | 11819.3331 | 12970.071 | 14235.8374 | 15628.321 | 17160.4107 | 18846.3192 | 20701.7203 | 22743.8996 | 24985.2339 | 27446.8932 | 30153.6839 | 33129.2395 | 36399.0333 | 39990.318 | 43931.9532 | 48254.0621 | 52987.4355 | 58162.5628 | 63808.1196 | 69948.6617 | 76601.1731
| TRUE | 516 | 22005264 | BC | BC022 | 11 | BC22 | OVERCURRENT | Blank | English Electric | CDG11_1054 | CDG11 1054 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 2620.3183 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 6521.5575 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 1.6829 |  | 4762.5731 | 11853.2907 | 48.1705 | 11805.1202 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 5210.2093 | 5701.7875 | 6241.7223 | 6834.8782 | 7486.6162 | 8202.8441 | 8990.0735 | 9855.4816 | 10806.9801 | 11853.2907 | 13004.0285 | 14269.7949 | 15662.2785 | 17194.3682 | 18880.2768 | 20735.6779 | 22777.8571 | 25025.879 | 27500.7706 | 30225.7253 | 33226.3269 | 36530.797 | 40170.2689 | 44179.0891 | 48595.1508 | 53460.2615 | 58820.5492 | 64726.9112 | 71235.5086 | 78408.3136 |  | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 33.9698 | 40.6598 | 53.8969 | 72.0675 | 97.1225 | 131.8114 | 180.0161 | 247.2254 | 341.2122 | 472.9973 | 658.2247 | 919.1244 | 1287.313 | 1807.7951 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 2866.6031 | 3137.0643 | 3434.1308 | 3760.4791 | 4119.0585 | 4513.1197 | 4946.2451 | 5422.3837 | 5945.8883 | 6521.5575 | 7154.6816 | 7851.0931 | 8617.2231 | 9460.1629 | 10387.7323 | 11408.5548 | 12532.1406 | 13768.9789 | 15130.6386 | 16629.8804 | 18280.7802 | 20098.8654 | 22101.2651 | 24306.8764 | 26736.5477 | 29413.2811 | 32362.4558 | 35612.0748 | 39193.0376 | 43139.4405 |  | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 2.0143 | 2.6701 | 3.5703 | 4.8115 | 6.5301 | 8.9182 | 12.2478 | 16.904 | 23.4327 | 32.609 | 45.5342 | 63.7746 | 89.5598 |  | 2864.9202 | 3135.3814 | 3432.4479 | 3758.7962 | 4117.3756 | 4511.4368 | 4944.5622 | 5420.7008 | 5944.2054 | 6519.8746 | 7152.9987 | 7849.4102 | 8615.5402 | 9458.4801 | 10386.0494 | 11406.8719 | 12530.4577 | 13766.9646 | 15127.9685 | 16626.3101 | 18275.9687 | 20092.3353 | 22092.3469 | 24294.6286 | 26719.6437 | 29389.8484 | 32329.8467 | 35566.5406 | 39129.2629 | 43049.8807 |  | 5176.2518 | 5667.8299 | 6207.7647 | 6800.9207 | 7452.6587 | 8168.8866 | 8956.116 | 9821.5241 | 10773.0226 | 11819.3331 | 12970.071 | 14235.8374 | 15628.321 | 17160.4107 | 18846.3192 | 20701.7203 | 22743.8996 | 24985.2339 | 27446.8932 | 30153.6839 | 33129.2395 | 36399.0333 | 39990.318 | 43931.9532 | 48254.0621 | 52987.4355 | 58162.5628 | 63808.1196 | 69948.6617 | 76601.1731
| TRUE | 517 | 22015705 | BC | BC022 | 11 | BC22 | AUTO RECLOSE | Blank | English Electric | GROUP_624 | GROUP 624 | GROUP 000s | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 53.114 | 1051.8847 | 1104.9987 | 45.1415 | 3.7652 | 1360.5504 |  | 7.1791 | 0.018276 | 0.00644 | 0.011836 | 104.0585 | 2060.8049 | 2164.8634 | 88.4392 | 7.3765 | 2665.5288 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 28.4243 | 0.35573 | 28.78 | 14.6761 | 2.0677 | 0.46012 |  | 2514.4558 | 4926.208 | 45.9839 | 4880.2241 |  | 0.026643 |  | 5.6485 | 5.801 | 5.9577 | 6.1185 | 6.2837 | 6.4534 | 6.6277 | 6.8066 | 6.9904 | 7.1791 | 7.373 | 7.5721 | 7.7765 | 7.9865 | 8.2022 | 8.4236 | 8.6511 | 8.8847 | 9.1246 | 9.3709 | 9.624 | 9.8838 | 10.1507 | 10.4248 | 10.7063 | 10.9954 | 11.2923 | 11.5972 | 11.9103 | 12.2319 |  | 0.0099614 | 0.010641 | 0.011372 | 0.012157 | 0.013001 | 0.013908 | 0.014884 | 0.015933 | 0.017062 | 0.018276 | 0.019582 | 0.020988 | 0.022502 | 0.024131 | 0.025885 | 0.027774 | 0.029809 | 0.032001 | 0.034362 | 0.036906 | 0.039648 | 0.042603 | 0.045789 | 0.049223 | 0.052926 | 0.056919 | 0.061224 | 0.065869 | 0.070879 | 0.076283 |  | 0.0035102 | 0.0037498 | 0.0040073 | 0.0042839 | 0.0045813 | 0.004901 | 0.0052448 | 0.0056145 | 0.0060122 | 0.00644 | 0.0069004 | 0.0073958 | 0.0079291 | 0.0085032 | 0.0091214 | 0.0097871 | 0.010504 | 0.011276 | 0.012109 | 0.013005 | 0.013971 | 0.015013 | 0.016135 | 0.017345 | 0.01865 | 0.020057 | 0.021574 | 0.023211 | 0.024976 | 0.026881 | 2685.0855 | 2868.3777 | 3065.3124 | 3276.9477 | 3504.4253 | 3748.9782 | 4011.9375 | 4294.7402 | 4598.9383 | 4926.208 | 5278.3592 | 5657.3469 | 6065.2831 | 6504.4488 | 6977.3086 | 7486.525 | 8034.9747 | 8625.7663 | 9262.2587 | 9948.0819 | 10687.1588 | 11483.7292 | 12342.3759 | 13268.0524 | 14266.1132 | 15342.3467 | 16503.0106 | 17754.8704 | 19105.2409 | 20562.0311 |  | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 31.7751 | 38.0328 | 50.4148 | 67.4114 | 90.8477 | 123.2954 | 168.3857 | 231.2529 | 319.1674 | 442.4382 | 615.6986 | 859.7422 | 1204.1431 | 1690.9982 |  | 56.7183 | 60.59 | 64.75 | 69.2205 | 74.0256 | 79.1914 | 84.746 | 90.7197 | 97.1455 | 104.0585 | 111.4972 | 119.5027 | 128.1197 | 137.3964 | 147.3849 | 158.1413 | 169.7264 | 182.206 | 195.6509 | 210.1379 | 225.7497 | 242.576 | 260.7136 | 280.2671 | 301.3496 | 324.0834 | 348.6006 | 375.0442 | 403.5687 | 434.3411 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 42.5062 | 46.3779 | 50.5379 | 55.0083 | 59.8134 | 64.9792 | 70.5338 | 76.5076 | 82.9333 | 89.8464 | 97.2851 | 105.2906 | 113.9076 | 123.1843 | 133.1727 | 143.9291 | 155.5143 | 165.195 | 173.1018 | 179.9866 | 185.1161 | 187.4294 | 185.3994 | 176.8342 | 158.5949 | 126.1931 | 73.2159 | -9.4944 | -135.0108 | -321.995 |  | 1123.265 | 1199.9426 | 1282.3273 | 1370.8617 | 1466.0235 | 1568.3286 | 1678.3336 | 1796.6398 | 1923.8966 | 2060.8049 | 2208.122 | 2366.6659 | 2537.3198 | 2721.0382 | 2918.8519 | 3131.8749 | 3361.3106 | 3608.4594 | 3874.7264 | 4161.6302 | 4470.8119 | 4804.0451 | 5163.247 | 5550.4898 | 5968.0135 | 6418.2396 | 6903.7858 | 7427.4825 | 7992.3897 | 8601.8159 |  | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.42579 | 0.56441 | 0.75469 | 1.0171 | 1.3803 | 1.8851 | 2.5889 | 3.5732 | 4.9532 | 6.8929 | 9.625 | 13.4807 | 18.9311 |  | 1122.9093 | 1199.5868 | 1281.9715 | 1370.506 | 1465.6678 | 1567.9728 | 1677.9779 | 1796.2841 | 1923.5408 | 2060.4492 | 2207.7663 | 2366.3101 | 2536.9641 | 2720.6824 | 2918.4962 | 3131.5192 | 3360.9549 | 3608.0336 | 3874.162 | 4160.8755 | 4469.7948 | 4802.6648 | 5161.3619 | 5547.9009 | 5964.4404 | 6413.2864 | 6896.8929 | 7417.8575 | 7978.909 | 8582.8848 |  | 1165.4155 | 1245.9648 | 1332.5094 | 1425.5143 | 1525.4813 | 1632.9521 | 1748.5117 | 1872.7917 | 2006.4742 | 2150.2956 | 2305.0513 | 2471.6007 | 2650.8717 | 2843.8667 | 3051.6689 | 3275.4483 | 3516.4692 | 3773.2285 | 4047.2638 | 4340.8621 | 4654.9109 | 4990.0942 | 5346.7613 | 5724.7351 | 6123.0353 | 6539.4795 | 6970.1088 | 7408.3631 | 7843.8982 | 8260.8898 |  | 48.2048 | 51.4954 | 55.031 | 58.8304 | 62.9143 | 67.3047 | 72.0255 | 77.1026 | 82.5638 | 88.4392 | 94.7613 | 101.5652 | 108.8888 | 116.7731 | 125.2623 | 134.4041 | 144.2503 | 154.8567 | 166.2835 | 178.596 | 191.8645 | 206.1651 | 221.5803 | 238.1987 | 256.1167 | 275.4381 | 296.2753 | 318.7497 | 342.9926 | 369.1461 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 33.5287 | 36.8193 | 40.3549 | 44.1543 | 48.2382 | 52.6286 | 57.3494 | 62.4265 | 67.8877 | 73.7631 | 80.0852 | 86.8891 | 94.2127 | 102.097 | 110.5862 | 119.728 | 129.5742 | 137.2903 | 142.9983 | 147.4604 | 149.9043 | 149.2182 | 143.8073 | 131.3892 | 108.7017 | 71.0876 | 11.9004 | -78.3425 | -213.1693 | -411.8813 |  | 4.0207 | 4.2951 | 4.59 | 4.9069 | 5.2475 | 5.6137 | 6.0075 | 6.431 | 6.8865 | 7.3765 | 7.9038 | 8.4713 | 9.0822 | 9.7398 | 10.4478 | 11.2103 | 12.0316 | 12.9163 | 13.8693 | 14.8963 | 16.003 | 17.1958 | 18.4815 | 19.8676 | 21.3621 | 22.9737 | 24.7117 | 26.5862 | 28.6083 | 30.7897 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 1.953 | 2.2274 | 2.5223 | 2.8392 | 3.1798 | 3.546 | 3.9398 | 4.3633 | 4.8188 | 5.3088 | 5.8361 | 6.4036 | 7.0145 | 7.6721 | 8.3801 | 9.1426 | 9.9639 | 10.4413 | 10.5887 | 10.5096 | 10.0913 | 9.1726 | 7.5242 | 4.8193 | 0.59296 | -5.8171 | -15.3537 | -29.3598 | -49.7489 | -79.2486 |  | 1452.8767 | 1552.0545 | 1658.6142 | 1773.1282 | 1896.2144 | 2028.5399 | 2170.8249 | 2323.847 | 2488.446 | 2665.5288 | 2856.0748 | 3061.1418 | 3281.8725 | 3519.5013 | 3775.3617 | 4050.8943 | 4347.6558 | 4667.328 | 5011.7286 | 5382.8216 | 5782.7297 | 6213.7472 | 6678.3535 | 7179.2291 | 7719.2712 | 8301.6119 | 8929.6372 | 9607.0078 | 10337.6817 | 11125.9383 |  | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.46012 | 0.55073 | 0.73003 | 0.97614 | 1.3155 | 1.7854 | 2.4383 | 3.3486 | 4.6217 | 6.4067 | 8.9155 | 12.4494 | 17.4364 | 24.4863 |  | 1452.4165 | 1551.5944 | 1658.1541 | 1772.6681 | 1895.7543 | 2028.0798 | 2170.3648 | 2323.3869 | 2487.9859 | 2665.0687 | 2855.6147 | 3060.6817 | 3281.4124 | 3519.0412 | 3774.9016 | 4050.4342 | 4347.1956 | 4666.7773 | 5010.9986 | 5381.8455 | 5781.4142 | 6211.9618 | 6675.9152 | 7175.8805 | 7714.6496 | 8295.2052 | 8920.7216 | 9594.5584 | 10320.2452 | 11101.452 |  | 2653.3137 | 2836.6059 | 3033.5407 | 3245.1759 | 3472.6536 | 3717.2065 | 3980.1657 | 4262.9684 | 4567.1666 | 4894.4362 | 5246.5874 | 5625.5751 | 6033.5113 | 6472.677 | 6945.5368 | 7454.7532 | 8003.2029 | 8587.7375 | 9211.8493 | 9880.6776 | 10596.3207 | 11360.4468 | 12174.008 | 13036.824 | 13946.9795 | 14899.9553 | 15887.3772 | 16895.2192 | 17901.2252 | 18871.2118
| TRUE | 518 | 22013855 | BC | BC023 | 11 | BC23 | SENSITIVE EF | Blank | RPL | ARTC_650 | ARTC 650 | AVE | Electromechanical |  | 0.81881 | 2190 |  | 2.5292 | 0.00090442 | 0.00072188 | 0.00018254 | 2.6857 | 57.7504 | 60.4361 | 6.6656 | 0.36908 | 298.787 |  | 4.7392 | 0.0013394 | 0.001069 | 0.00027033 | 3.9772 | 85.5231 | 89.5003 | 9.8711 | 0.54657 | 442.4761 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.46373 | 14.6772 | 14.7027 | 2.0677 | 2.3992 |  | 366.2578 | 542.3941 | 33.8468 | 508.5472 |  | 0.062797 |  | 2.6931 | 2.8677 | 3.0535 | 3.2514 | 3.4622 | 3.6865 | 3.9255 | 4.1799 | 4.4508 | 4.7392 | 5.0464 | 5.3734 | 5.7217 | 6.0925 | 6.4874 | 6.9078 | 7.3555 | 7.8322 | 8.3398 | 8.8804 | 9.4559 | 10.0687 | 10.7213 | 11.4161 | 12.156 | 12.9438 | 13.7827 | 14.676 | 15.6272 | 16.64 |  | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00099954 | 0.0011556 | 0.0013394 | 0.0015562 | 0.0018123 | 0.0021153 | 0.002474 | 0.0028992 | 0.0034038 | 0.0040031 | 0.0047157 | 0.0055637 | 0.0065737 | 0.0077776 | 0.0092136 | 0.010928 | 0.012976 | 0.015423 | 0.018351 | 0.021854 | 0.026048 | 0.031073 | 0.037095 |  | 0.00072188 | 0.00072188 | 0.00072188 | 0.00072188 | 0.00072188 | 0.00072188 | 0.00072188 | 0.0007978 | 0.00092233 | 0.001069 | 0.0012421 | 0.0014466 | 0.0016884 | 0.0019747 | 0.002314 | 0.0027168 | 0.0031951 | 0.0037639 | 0.0044408 | 0.0052469 | 0.0062078 | 0.007354 | 0.0087223 | 0.010357 | 0.01231 | 0.014647 | 0.017443 | 0.020791 | 0.024801 | 0.029608 | 366.2578 | 366.2578 | 366.2578 | 366.2578 | 366.2578 | 366.2578 | 366.2578 | 404.7785 | 467.9593 | 542.3941 | 630.2064 | 733.9343 | 856.6132 | 1001.875 | 1174.0679 | 1378.3997 | 1621.1114 | 1909.6845 | 2253.0917 | 2662.0982 | 3149.6248 | 3731.1842 | 4425.4078 | 5254.6789 | 6245.8962 | 7431.3938 | 8850.0492 | 10548.6188 | 12583.3479 | 15021.9105 |  | 33.8468 | 33.8468 | 33.8468 | 33.8468 | 33.8468 | 33.8468 | 33.8468 | 33.8468 | 33.8468 | 33.8468 | 33.8468 | 33.8468 | 33.8468 | 33.8468 | 33.8468 | 33.8468 | 33.8468 | 40.5125 | 53.7018 | 71.8066 | 96.7708 | 131.3342 | 179.3643 | 246.3303 | 339.9767 | 471.2846 | 655.8414 | 915.7963 | 1282.6518 | 1801.2492 |  | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.6857 | 2.9681 | 3.4314 | 3.9772 | 4.6212 | 5.3818 | 6.2813 | 7.3465 | 8.6092 | 10.1075 | 11.8872 | 14.0033 | 16.5214 | 19.5205 | 23.0954 | 27.3599 | 32.4504 | 38.5313 | 45.7996 | 54.4926 | 64.8953 | 77.3505 | 92.2706 | 110.152 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | -11.5277 | -11.5277 | -11.5277 | -11.5277 | -11.5277 | -11.5277 | -11.5277 | -11.2453 | -10.782 | -10.2362 | -9.5923 | -8.8317 | -7.9321 | -6.8669 | -5.6043 | -4.1059 | -2.3262 | -3.0093 | -6.0298 | -10.6335 | -17.5419 | -27.7917 | -42.8706 | -64.911 | -96.968 | -143.4155 | -210.5144 | -307.223 | -446.3577 | -646.2527 |  | 57.7504 | 57.7504 | 57.7504 | 57.7504 | 57.7504 | 57.7504 | 57.7504 | 63.8243 | 73.7864 | 85.5231 | 99.3691 | 115.7246 | 135.0682 | 157.9726 | 185.1235 | 217.3419 | 255.612 | 301.1133 | 355.2607 | 419.7517 | 496.6234 | 588.3219 | 697.785 | 828.542 | 984.8342 | 1171.7599 | 1395.4492 | 1663.2746 | 1984.1046 | 2368.6098 |  | 0.46373 | 0.46373 | 0.46373 | 0.46373 | 0.46373 | 0.46373 | 0.46373 | 0.46373 | 0.46373 | 0.46373 | 0.46373 | 0.46373 | 0.46373 | 0.46373 | 0.46373 | 0.46373 | 0.46373 | 0.55506 | 0.73576 | 0.98382 | 1.3258 | 1.7994 | 2.4575 | 3.375 | 4.658 | 6.457 | 8.9856 | 12.5473 | 17.5735 | 24.6788 |  | 57.2867 | 57.2867 | 57.2867 | 57.2867 | 57.2867 | 57.2867 | 57.2867 | 63.3605 | 73.3227 | 85.0593 | 98.9053 | 115.2608 | 134.6045 | 157.5089 | 184.6598 | 216.8782 | 255.1483 | 300.5583 | 354.525 | 418.7678 | 495.2975 | 586.5225 | 695.3276 | 825.1671 | 980.1762 | 1165.3028 | 1386.4636 | 1650.7273 | 1966.5311 | 2343.931 |  | 45.759 | 45.759 | 45.759 | 45.759 | 45.759 | 45.759 | 45.759 | 52.1152 | 62.5407 | 74.8232 | 89.3131 | 106.4292 | 126.6724 | 150.642 | 179.0555 | 212.7723 | 252.8221 | 297.5489 | 348.4952 | 408.1344 | 477.7557 | 558.7308 | 652.457 | 760.256 | 883.2082 | 1021.8873 | 1175.9491 | 1343.5043 | 1520.1734 | 1697.6783 |  | 6.6656 | 6.6656 | 6.6656 | 6.6656 | 6.6656 | 6.6656 | 6.6656 | 7.3666 | 8.5165 | 9.8711 | 11.4692 | 13.357 | 15.5897 | 18.2333 | 21.3671 | 25.0857 | 29.5029 | 34.7547 | 41.0044 | 48.448 | 57.3206 | 67.9045 | 80.5388 | 95.6308 | 113.6702 | 135.2453 | 161.0636 | 191.9762 | 229.0066 | 273.3864 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | -8.0371 | -8.0371 | -8.0371 | -8.0371 | -8.0371 | -8.0371 | -8.0371 | -7.3361 | -6.1862 | -4.8316 | -3.2335 | -1.3457 | 0.88696 | 3.5306 | 6.6644 | 10.383 | 14.8002 | 17.1565 | 17.677 | 17.256 | 15.2844 | 10.8544 | 2.6249 | -11.3723 | -34.012 | -69.4756 | -123.8267 | -205.8357 | -328.1632 | -509.0565 |  | 0.36908 | 0.36908 | 0.36908 | 0.36908 | 0.36908 | 0.36908 | 0.36908 | 0.4079 | 0.47156 | 0.54657 | 0.63506 | 0.73959 | 0.86321 | 1.0096 | 1.1831 | 1.389 | 1.6336 | 1.9244 | 2.2704 | 2.6826 | 3.1739 | 3.7599 | 4.4595 | 5.2951 | 6.294 | 7.4886 | 8.9182 | 10.6299 | 12.6803 | 15.1376 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | -1.6987 | -1.6987 | -1.6987 | -1.6987 | -1.6987 | -1.6987 | -1.6987 | -1.6599 | -1.5962 | -1.5212 | -1.4327 | -1.3282 | -1.2045 | -1.0582 | -0.88464 | -0.67873 | -0.43415 | -0.55058 | -1.0103 | -1.7042 | -2.738 | -4.2635 | -6.4981 | -9.7535 | -14.4756 | -21.3028 | -31.148 | -45.3174 | -65.6787 | -94.9032 |  | 298.787 | 298.787 | 298.787 | 298.787 | 298.787 | 298.787 | 298.787 | 330.2115 | 381.7534 | 442.4761 | 514.1119 | 598.7314 | 698.8108 | 817.313 | 957.785 | 1124.4756 | 1322.4757 | 1557.8888 | 1838.0347 | 2171.6954 | 2569.4115 | 3043.838 | 3610.1741 | 4286.6796 | 5095.2982 | 6062.4074 | 7219.7229 | 8605.3877 | 10265.2859 | 12254.6247 |  | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.8717 | 3.8067 | 5.09 | 6.8596 | 9.3097 | 12.7143 | 17.4612 | 24.0994 | 33.4072 | 46.4895 | 64.9165 | 90.9212 | 127.6821 |  | 296.3878 | 296.3878 | 296.3878 | 296.3878 | 296.3878 | 296.3878 | 296.3878 | 327.8123 | 379.3541 | 440.0768 | 511.7127 | 596.3322 | 696.4116 | 814.9137 | 955.3858 | 1122.0763 | 1320.0765 | 1555.0171 | 1834.228 | 2166.6054 | 2562.5519 | 3034.5284 | 3597.4598 | 4269.2184 | 5071.1988 | 6029.0003 | 7173.2333 | 8540.4712 | 10174.3647 | 12126.9426 |  | 332.4109 | 332.4109 | 332.4109 | 332.4109 | 332.4109 | 332.4109 | 332.4109 | 370.9316 | 434.1124 | 508.5472 | 596.3596 | 700.0875 | 822.7664 | 968.0282 | 1140.221 | 1344.5529 | 1587.2646 | 1869.172 | 2199.3899 | 2590.2917 | 3052.854 | 3599.8501 | 4246.0436 | 5008.3486 | 5905.9195 | 6960.1092 | 8194.2078 | 9632.8225 | 11300.6962 | 13220.6613
| TRUE | 519 | 22005266 | BC | BC023 | 11 | BC23 | OVERCURRENT | Blank | English Electric | CDG11_1054 | CDG11 1054 | CDG11 | Electromechanical |  | 0.81881 | 2190 |  | 9.9 | 0.0088019 | 0.0070254 | 0.0017765 | 52.2742 | 2248.1151 | 2300.3893 | 64.8697 | 3.5919 | 2907.8034 |  | 13.7946 | 0.021906 | 0.017485 | 0.0044214 | 130.1022 | 5595.2027 | 5725.3049 | 161.4505 | 8.9396 | 7237.0625 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 28.4268 | 1.8549 | 30.2818 | 14.7027 | 2.0677 | 2.3992 |  | 5276.6543 | 13132.7576 | 49.4515 | 13083.3061 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0076857 | 0.0084108 | 0.0092073 | 0.010082 | 0.011044 | 0.0121 | 0.013261 | 0.014538 | 0.015942 | 0.017485 | 0.019182 | 0.02105 | 0.023104 | 0.025364 | 0.027851 | 0.030588 | 0.0336 | 0.036916 | 0.040567 | 0.044587 | 0.049013 | 0.053887 | 0.059256 | 0.065169 | 0.071684 | 0.07886 | 0.086767 | 0.09548 | 0.10508 | 0.11566 | 5772.6093 | 6317.2493 | 6915.4657 | 7572.6481 | 8294.7359 | 9088.2748 | 9960.4792 | 10919.3012 | 11973.5063 | 13132.7576 | 14407.7083 | 15810.1039 | 17352.8948 | 19050.3612 | 20918.25 | 22973.9266 | 25236.5426 | 27727.2202 | 30469.2564 | 33488.348 | 36812.8402 | 40474.0011 | 44506.3246 | 48947.8645 | 53840.6044 | 59230.8644 | 65169.7518 | 71713.6578 | 78924.8057 | 86871.857 |  | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 42.1987 | 55.9369 | 74.7952 | 100.7985 | 136.8004 | 186.8296 | 256.5827 | 354.1269 | 490.8999 | 683.138 | 953.9125 | 1336.0368 | 1876.2187 |  | 57.1875 | 62.5831 | 68.5094 | 75.0199 | 82.1734 | 90.0348 | 98.6754 | 108.1742 | 118.6179 | 130.1022 | 142.7328 | 156.6259 | 171.9099 | 188.7262 | 207.2308 | 227.5957 | 250.0108 | 274.6852 | 301.8497 | 331.7589 | 364.6936 | 400.9637 | 440.9107 | 484.9116 | 533.3825 | 586.7822 | 645.617 | 710.4455 | 781.8841 | 860.6131 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 42.9741 | 48.3697 | 54.296 | 60.8065 | 67.96 | 75.8214 | 84.462 | 93.9608 | 104.4045 | 115.8888 | 128.5194 | 142.4125 | 157.6964 | 174.5127 | 193.0173 | 213.3823 | 235.7974 | 257.6726 | 279.2985 | 301.6049 | 324.0563 | 345.8121 | 365.5896 | 381.4693 | 390.6149 | 388.8741 | 370.2073 | 325.872 | 243.2558 | 104.2084 |  | 2459.4164 | 2691.4599 | 2946.3296 | 3226.3217 | 3533.9667 | 3872.0535 | 4243.6556 | 4652.1611 | 5101.3044 | 5595.2027 | 6138.3946 | 6735.8843 | 7393.1894 | 8116.3938 | 8912.2066 | 9788.0263 | 10752.0123 | 11813.1639 | 12981.4066 | 14267.6885 | 15684.0862 | 17243.9214 | 18961.8902 | 20854.2054 | 22938.7539 | 25235.2707 | 27765.5297 | 30553.5566 | 33625.8614 | 37011.6973 |  | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 2.2202 | 2.9431 | 3.9353 | 5.3034 | 7.1976 | 9.8298 | 13.4998 | 18.632 | 25.8281 | 35.9425 | 50.189 | 70.294 | 98.7151 |  | 2457.5614 | 2689.605 | 2944.4747 | 3224.4668 | 3532.1118 | 3870.1985 | 4241.8007 | 4650.3061 | 5099.4495 | 5593.3478 | 6136.5397 | 6734.0294 | 7391.3345 | 8114.5389 | 8910.3517 | 9786.1713 | 10750.1574 | 11810.9436 | 12978.4635 | 14263.7533 | 15678.7829 | 17236.7238 | 18952.0604 | 20840.7056 | 22920.122 | 25209.4425 | 27729.5872 | 30503.3675 | 33555.5673 | 36912.9822 |  | 2500.5355 | 2737.9746 | 2998.7707 | 3285.2733 | 3600.0718 | 3946.0199 | 4326.2627 | 4744.2669 | 5203.854 | 5709.2366 | 6265.059 | 6876.4419 | 7549.0309 | 8289.0516 | 9103.369 | 9999.5536 | 10985.9547 | 12068.6162 | 13257.762 | 14565.3582 | 16002.8392 | 17582.5359 | 19317.65 | 21222.1749 | 23310.7369 | 25598.3166 | 28099.7945 | 30829.2395 | 33798.8231 | 37017.1907 |  | 70.9668 | 77.6625 | 85.0168 | 93.096 | 101.9732 | 111.7287 | 122.4514 | 134.2388 | 147.1989 | 161.4505 | 177.1243 | 194.365 | 213.3316 | 234.1998 | 257.1631 | 282.435 | 310.251 | 340.8707 | 374.5805 | 411.6964 | 452.5668 | 497.5761 | 547.1483 | 601.7514 | 661.9014 | 728.1677 | 801.1788 | 881.6277 | 970.2795 | 1067.9784 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 56.2642 | 62.9598 | 70.3141 | 78.3933 | 87.2705 | 97.026 | 107.7487 | 119.5361 | 132.4963 | 146.7478 | 162.4217 | 179.6623 | 198.629 | 219.4971 | 242.4604 | 267.7324 | 295.5483 | 323.2725 | 351.2531 | 380.5044 | 410.5306 | 440.526 | 469.2345 | 494.7482 | 514.2192 | 523.4469 | 516.2885 | 483.8158 | 413.1097 | 285.5355 |  | 3.9295 | 4.3002 | 4.7074 | 5.1548 | 5.6463 | 6.1865 | 6.7802 | 7.4329 | 8.1505 | 8.9396 | 9.8075 | 10.7621 | 11.8123 | 12.9678 | 14.2393 | 15.6386 | 17.1788 | 18.8742 | 20.7408 | 22.7959 | 25.0589 | 27.5511 | 30.296 | 33.3194 | 36.6499 | 40.3191 | 44.3618 | 48.8163 | 53.725 | 59.1347 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 1.8617 | 2.2325 | 2.6397 | 3.087 | 3.5786 | 4.1187 | 4.7125 | 5.3651 | 6.0828 | 6.8719 | 7.7397 | 8.6944 | 9.7446 | 10.9001 | 12.1715 | 13.5709 | 15.1111 | 16.3993 | 17.4601 | 18.4092 | 19.1471 | 19.5277 | 19.3384 | 18.2707 | 15.8803 | 11.5277 | 4.2956 | -7.1309 | -24.6339 | -50.9061 |  | 3181.1091 | 3481.2436 | 3810.9024 | 4173.0556 | 4570.9762 | 5008.2713 | 5488.9166 | 6017.2942 | 6598.2345 | 7237.0625 | 7939.649 | 8712.4665 | 9562.6516 | 10498.0736 | 11527.4102 | 12660.231 | 13907.0897 | 15279.6262 | 16790.6788 | 18454.4082 | 20286.4346 | 22303.9888 | 24526.0794 | 26973.6767 | 29669.9166 | 32640.3247 | 35913.0646 | 39519.2118 | 43493.0557 | 47872.4335 |  | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.8717 | 3.8067 | 5.09 | 6.8596 | 9.3097 | 12.7143 | 17.4612 | 24.0994 | 33.4072 | 46.4895 | 64.9165 | 90.9212 | 127.6821 |  | 3178.7098 | 3478.8444 | 3808.5032 | 4170.6564 | 4568.577 | 5005.8721 | 5486.5174 | 6014.8949 | 6595.8352 | 7234.6633 | 7937.2498 | 8710.0673 | 9560.2524 | 10495.6744 | 11525.0109 | 12657.8317 | 13904.6905 | 15276.7545 | 16786.8722 | 18449.3182 | 20279.5749 | 22294.6791 | 24513.3651 | 26956.2156 | 29645.8172 | 32606.9175 | 35866.5751 | 39454.2953 | 43402.1345 | 47744.7514 |  | 5737.3712 | 6282.0113 | 6880.2277 | 7537.41 | 8259.4979 | 9053.0368 | 9925.2412 | 10884.0632 | 11938.2682 | 13097.5195 | 14372.4702 | 15774.8658 | 17317.6568 | 19015.1232 | 20883.0119 | 22938.6886 | 25201.3046 | 27685.0425 | 30413.3473 | 33413.59 | 36712.0918 | 40337.2687 | 44319.5879 | 48691.4094 | 53486.6537 | 58740.2087 | 64486.9536 | 70760.2197 | 77589.4334 | 84996.5715
| TRUE | 520 | 22005267 | BC | BC023 | 11 | BC23 | OVERCURRENT | Blank | English Electric | CDG11_1054 | CDG11 1054 | CDG11 | Electromechanical |  | 0.81881 | 2190 |  | 9.9 | 0.0088019 | 0.0070254 | 0.0017765 | 52.2742 | 2248.1151 | 2300.3893 | 64.8697 | 3.5919 | 2907.8034 |  | 13.7946 | 0.021906 | 0.017485 | 0.0044214 | 130.1022 | 5595.2027 | 5725.3049 | 161.4505 | 8.9396 | 7237.0625 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 28.4268 | 1.8549 | 30.2818 | 14.7027 | 2.0677 | 2.3992 |  | 5276.6543 | 13132.7576 | 49.4515 | 13083.3061 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0076857 | 0.0084108 | 0.0092073 | 0.010082 | 0.011044 | 0.0121 | 0.013261 | 0.014538 | 0.015942 | 0.017485 | 0.019182 | 0.02105 | 0.023104 | 0.025364 | 0.027851 | 0.030588 | 0.0336 | 0.036916 | 0.040567 | 0.044587 | 0.049013 | 0.053887 | 0.059256 | 0.065169 | 0.071684 | 0.07886 | 0.086767 | 0.09548 | 0.10508 | 0.11566 | 5772.6093 | 6317.2493 | 6915.4657 | 7572.6481 | 8294.7359 | 9088.2748 | 9960.4792 | 10919.3012 | 11973.5063 | 13132.7576 | 14407.7083 | 15810.1039 | 17352.8948 | 19050.3612 | 20918.25 | 22973.9266 | 25236.5426 | 27727.2202 | 30469.2564 | 33488.348 | 36812.8402 | 40474.0011 | 44506.3246 | 48947.8645 | 53840.6044 | 59230.8644 | 65169.7518 | 71713.6578 | 78924.8057 | 86871.857 |  | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 35.2556 | 42.1987 | 55.9369 | 74.7952 | 100.7985 | 136.8004 | 186.8296 | 256.5827 | 354.1269 | 490.8999 | 683.138 | 953.9125 | 1336.0368 | 1876.2187 |  | 57.1875 | 62.5831 | 68.5094 | 75.0199 | 82.1734 | 90.0348 | 98.6754 | 108.1742 | 118.6179 | 130.1022 | 142.7328 | 156.6259 | 171.9099 | 188.7262 | 207.2308 | 227.5957 | 250.0108 | 274.6852 | 301.8497 | 331.7589 | 364.6936 | 400.9637 | 440.9107 | 484.9116 | 533.3825 | 586.7822 | 645.617 | 710.4455 | 781.8841 | 860.6131 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 42.9741 | 48.3697 | 54.296 | 60.8065 | 67.96 | 75.8214 | 84.462 | 93.9608 | 104.4045 | 115.8888 | 128.5194 | 142.4125 | 157.6964 | 174.5127 | 193.0173 | 213.3823 | 235.7974 | 257.6726 | 279.2985 | 301.6049 | 324.0563 | 345.8121 | 365.5896 | 381.4693 | 390.6149 | 388.8741 | 370.2073 | 325.872 | 243.2558 | 104.2084 |  | 2459.4164 | 2691.4599 | 2946.3296 | 3226.3217 | 3533.9667 | 3872.0535 | 4243.6556 | 4652.1611 | 5101.3044 | 5595.2027 | 6138.3946 | 6735.8843 | 7393.1894 | 8116.3938 | 8912.2066 | 9788.0263 | 10752.0123 | 11813.1639 | 12981.4066 | 14267.6885 | 15684.0862 | 17243.9214 | 18961.8902 | 20854.2054 | 22938.7539 | 25235.2707 | 27765.5297 | 30553.5566 | 33625.8614 | 37011.6973 |  | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 2.2202 | 2.9431 | 3.9353 | 5.3034 | 7.1976 | 9.8298 | 13.4998 | 18.632 | 25.8281 | 35.9425 | 50.189 | 70.294 | 98.7151 |  | 2457.5614 | 2689.605 | 2944.4747 | 3224.4668 | 3532.1118 | 3870.1985 | 4241.8007 | 4650.3061 | 5099.4495 | 5593.3478 | 6136.5397 | 6734.0294 | 7391.3345 | 8114.5389 | 8910.3517 | 9786.1713 | 10750.1574 | 11810.9436 | 12978.4635 | 14263.7533 | 15678.7829 | 17236.7238 | 18952.0604 | 20840.7056 | 22920.122 | 25209.4425 | 27729.5872 | 30503.3675 | 33555.5673 | 36912.9822 |  | 2500.5355 | 2737.9746 | 2998.7707 | 3285.2733 | 3600.0718 | 3946.0199 | 4326.2627 | 4744.2669 | 5203.854 | 5709.2366 | 6265.059 | 6876.4419 | 7549.0309 | 8289.0516 | 9103.369 | 9999.5536 | 10985.9547 | 12068.6162 | 13257.762 | 14565.3582 | 16002.8392 | 17582.5359 | 19317.65 | 21222.1749 | 23310.7369 | 25598.3166 | 28099.7945 | 30829.2395 | 33798.8231 | 37017.1907 |  | 70.9668 | 77.6625 | 85.0168 | 93.096 | 101.9732 | 111.7287 | 122.4514 | 134.2388 | 147.1989 | 161.4505 | 177.1243 | 194.365 | 213.3316 | 234.1998 | 257.1631 | 282.435 | 310.251 | 340.8707 | 374.5805 | 411.6964 | 452.5668 | 497.5761 | 547.1483 | 601.7514 | 661.9014 | 728.1677 | 801.1788 | 881.6277 | 970.2795 | 1067.9784 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 56.2642 | 62.9598 | 70.3141 | 78.3933 | 87.2705 | 97.026 | 107.7487 | 119.5361 | 132.4963 | 146.7478 | 162.4217 | 179.6623 | 198.629 | 219.4971 | 242.4604 | 267.7324 | 295.5483 | 323.2725 | 351.2531 | 380.5044 | 410.5306 | 440.526 | 469.2345 | 494.7482 | 514.2192 | 523.4469 | 516.2885 | 483.8158 | 413.1097 | 285.5355 |  | 3.9295 | 4.3002 | 4.7074 | 5.1548 | 5.6463 | 6.1865 | 6.7802 | 7.4329 | 8.1505 | 8.9396 | 9.8075 | 10.7621 | 11.8123 | 12.9678 | 14.2393 | 15.6386 | 17.1788 | 18.8742 | 20.7408 | 22.7959 | 25.0589 | 27.5511 | 30.296 | 33.3194 | 36.6499 | 40.3191 | 44.3618 | 48.8163 | 53.725 | 59.1347 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 1.8617 | 2.2325 | 2.6397 | 3.087 | 3.5786 | 4.1187 | 4.7125 | 5.3651 | 6.0828 | 6.8719 | 7.7397 | 8.6944 | 9.7446 | 10.9001 | 12.1715 | 13.5709 | 15.1111 | 16.3993 | 17.4601 | 18.4092 | 19.1471 | 19.5277 | 19.3384 | 18.2707 | 15.8803 | 11.5277 | 4.2956 | -7.1309 | -24.6339 | -50.9061 |  | 3181.1091 | 3481.2436 | 3810.9024 | 4173.0556 | 4570.9762 | 5008.2713 | 5488.9166 | 6017.2942 | 6598.2345 | 7237.0625 | 7939.649 | 8712.4665 | 9562.6516 | 10498.0736 | 11527.4102 | 12660.231 | 13907.0897 | 15279.6262 | 16790.6788 | 18454.4082 | 20286.4346 | 22303.9888 | 24526.0794 | 26973.6767 | 29669.9166 | 32640.3247 | 35913.0646 | 39519.2118 | 43493.0557 | 47872.4335 |  | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.3992 | 2.8717 | 3.8067 | 5.09 | 6.8596 | 9.3097 | 12.7143 | 17.4612 | 24.0994 | 33.4072 | 46.4895 | 64.9165 | 90.9212 | 127.6821 |  | 3178.7098 | 3478.8444 | 3808.5032 | 4170.6564 | 4568.577 | 5005.8721 | 5486.5174 | 6014.8949 | 6595.8352 | 7234.6633 | 7937.2498 | 8710.0673 | 9560.2524 | 10495.6744 | 11525.0109 | 12657.8317 | 13904.6905 | 15276.7545 | 16786.8722 | 18449.3182 | 20279.5749 | 22294.6791 | 24513.3651 | 26956.2156 | 29645.8172 | 32606.9175 | 35866.5751 | 39454.2953 | 43402.1345 | 47744.7514 |  | 5737.3712 | 6282.0113 | 6880.2277 | 7537.41 | 8259.4979 | 9053.0368 | 9925.2412 | 10884.0632 | 11938.2682 | 13097.5195 | 14372.4702 | 15774.8658 | 17317.6568 | 19015.1232 | 20883.0119 | 22938.6886 | 25201.3046 | 27685.0425 | 30413.3473 | 33413.59 | 36712.0918 | 40337.2687 | 44319.5879 | 48691.4094 | 53486.6537 | 58740.2087 | 64486.9536 | 70760.2197 | 77589.4334 | 84996.5715
| TRUE | 521 | 22015706 | BC | BC023 | 11 | BC23 | AUTO RECLOSE | Blank | English Electric | GROUP_624 | GROUP 624 | GROUP 000s | Electronic |  | 0.2894 | 2190 |  | 5.5 | 0.0093284 | 0.0049035 | 0.0044248 | 54.003 | 1569.1352 | 1623.1382 | 54.3183 | 3.7813 | 2029.5832 |  | 7.1791 | 0.018276 | 0.0096068 | 0.0086689 | 105.8003 | 3074.1787 | 3179.9789 | 106.4179 | 7.4082 | 3976.2676 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.84798 |  | 3710.821 | 7270.0726 | 46.6775 | 7223.3951 |  | 0.026643 |  | 5.6485 | 5.801 | 5.9577 | 6.1185 | 6.2837 | 6.4534 | 6.6277 | 6.8066 | 6.9904 | 7.1791 | 7.373 | 7.5721 | 7.7765 | 7.9865 | 8.2022 | 8.4236 | 8.6511 | 8.8847 | 9.1246 | 9.3709 | 9.624 | 9.8838 | 10.1507 | 10.4248 | 10.7063 | 10.9954 | 11.2923 | 11.5972 | 11.9103 | 12.2319 |  | 0.0099614 | 0.010641 | 0.011372 | 0.012157 | 0.013001 | 0.013908 | 0.014884 | 0.015933 | 0.017062 | 0.018276 | 0.019582 | 0.020988 | 0.022502 | 0.024131 | 0.025885 | 0.027774 | 0.029809 | 0.032001 | 0.034362 | 0.036906 | 0.039648 | 0.042603 | 0.045789 | 0.049223 | 0.052926 | 0.056919 | 0.061224 | 0.065869 | 0.070879 | 0.076283 |  | 0.0052363 | 0.0055937 | 0.0059778 | 0.0063905 | 0.0068341 | 0.007311 | 0.0078239 | 0.0083754 | 0.0089686 | 0.0096068 | 0.010294 | 0.011033 | 0.011828 | 0.012685 | 0.013607 | 0.0146 | 0.015669 | 0.016821 | 0.018063 | 0.0194 | 0.020841 | 0.022395 | 0.024069 | 0.025875 | 0.027821 | 0.02992 | 0.032183 | 0.034625 | 0.037258 | 0.040099 | 3962.6354 | 4233.1371 | 4523.7725 | 4836.1027 | 5171.813 | 5532.723 | 5920.7968 | 6338.1556 | 6787.0897 | 7270.0726 | 7789.7755 | 8349.0837 | 8951.1138 | 9599.2323 | 10297.0764 | 11048.5753 | 11857.9747 | 12729.8619 | 13669.1942 | 14681.3285 | 15772.0544 | 16947.629 | 18214.8154 | 19580.924 | 21053.857 | 22642.1569 | 24355.0588 | 26202.5472 | 28195.4171 | 30345.3406 |  | 32.4713 | 32.4713 | 32.4713 | 32.4713 | 32.4713 | 32.4713 | 32.4713 | 32.4713 | 32.4713 | 32.4713 | 32.4713 | 32.4713 | 32.4713 | 32.4713 | 32.4713 | 32.4713 | 32.4713 | 38.8661 | 51.5193 | 68.8883 | 92.838 | 125.9967 | 172.0749 | 236.3194 | 326.16 | 452.1315 | 629.1878 | 878.5782 | 1230.5245 | 1728.0461 |  | 57.6676 | 61.6042 | 65.8338 | 70.3791 | 75.2646 | 80.5169 | 86.1645 | 92.2382 | 98.7715 | 105.8003 | 113.3634 | 121.503 | 130.2642 | 139.6962 | 149.8518 | 160.7882 | 172.5673 | 185.2558 | 198.9257 | 213.6552 | 229.5283 | 246.6363 | 265.0775 | 284.9582 | 306.3936 | 329.5079 | 354.4355 | 381.3217 | 410.3236 | 441.6111 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 43.4552 | 47.3918 | 51.6214 | 56.1667 | 61.0522 | 66.3045 | 71.9521 | 78.0258 | 84.5591 | 91.5879 | 99.151 | 107.2906 | 116.0518 | 125.4838 | 135.6394 | 146.5759 | 158.3549 | 168.2444 | 176.3762 | 183.5034 | 188.894 | 191.4887 | 189.7619 | 181.5234 | 163.6364 | 131.6141 | 79.0458 | -3.2239 | -128.2656 | -314.7387 |  | 1675.6159 | 1789.9986 | 1912.8949 | 2044.9649 | 2186.9214 | 2339.5336 | 2503.6321 | 2680.1139 | 2869.9475 | 3074.1787 | 3293.9371 | 3530.4427 | 3785.0135 | 4059.073 | 4354.1591 | 4671.9333 | 5014.191 | 5382.872 | 5780.0723 | 6208.0572 | 6669.2749 | 7166.3713 | 7702.206 | 8279.8704 | 8902.7059 | 9574.3247 | 10298.632 | 11079.8497 | 11922.5425 | 12831.6461 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 1674.9603 | 1789.343 | 1912.2393 | 2044.3093 | 2186.2658 | 2338.878 | 2502.9765 | 2679.4583 | 2869.2919 | 3073.5231 | 3293.2815 | 3529.7871 | 3784.3579 | 4058.4174 | 4353.5035 | 4671.2777 | 5013.5354 | 5382.0872 | 5779.0321 | 6206.6664 | 6667.4005 | 7163.8274 | 7698.7318 | 8275.0991 | 8896.1206 | 9565.1961 | 10285.9286 | 11062.111 | 11897.698 | 12796.7565 |  | 1718.4155 | 1836.7348 | 1963.8607 | 2100.476 | 2247.318 | 2405.1825 | 2574.9286 | 2757.4842 | 2953.851 | 3165.1109 | 3392.4325 | 3637.0777 | 3900.4097 | 4183.9012 | 4489.1429 | 4817.8536 | 5171.8903 | 5550.3317 | 5955.4083 | 6390.1697 | 6856.2945 | 7355.3161 | 7888.4937 | 8456.6225 | 9059.757 | 9696.8102 | 10364.9743 | 11058.8871 | 11769.4324 | 12482.0178 |  | 58.0043 | 61.9638 | 66.2181 | 70.7899 | 75.704 | 80.9869 | 86.6674 | 92.7766 | 99.3481 | 106.4179 | 114.0252 | 122.2122 | 131.0246 | 140.5116 | 150.7265 | 161.7268 | 173.5747 | 186.3372 | 200.0869 | 214.9023 | 230.8682 | 248.076 | 266.6248 | 286.6216 | 308.1821 | 331.4313 | 356.5045 | 383.5476 | 412.7189 | 444.189 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 43.3228 | 47.2824 | 51.5367 | 56.1085 | 61.0225 | 66.3055 | 71.986 | 78.0952 | 84.6666 | 91.7364 | 99.3438 | 107.5308 | 116.3432 | 125.8302 | 136.0451 | 147.0454 | 158.8932 | 168.7644 | 176.7932 | 183.7555 | 188.8928 | 191.1084 | 188.8237 | 179.7733 | 160.7137 | 127.0068 | 72.0265 | -13.6885 | -143.6447 | -337.1215 |  | 4.0379 | 4.3136 | 4.6097 | 4.928 | 5.2701 | 5.6378 | 6.0333 | 6.4586 | 6.916 | 7.4082 | 7.9378 | 8.5077 | 9.1212 | 9.7816 | 10.4927 | 11.2585 | 12.0833 | 12.9717 | 13.9289 | 14.9602 | 16.0717 | 17.2696 | 18.5609 | 19.9529 | 21.4538 | 23.0723 | 24.8178 | 26.7003 | 28.7311 | 30.9218 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.9702 | 2.2458 | 2.542 | 2.8603 | 3.2024 | 3.5701 | 3.9656 | 4.3909 | 4.8483 | 5.3405 | 5.8701 | 6.44 | 7.0535 | 7.7139 | 8.425 | 9.1908 | 10.0155 | 10.4968 | 10.6482 | 10.5736 | 10.1599 | 9.2464 | 7.6035 | 4.9045 | 0.68457 | -5.7186 | -15.2478 | -29.2459 | -49.6264 | -79.1169 |  | 2167.3097 | 2315.2569 | 2474.216 | 2645.0408 | 2828.653 | 3026.0478 | 3238.2995 | 3466.5683 | 3712.1067 | 3976.2676 | 4260.5121 | 4566.4181 | 4895.6903 | 5250.17 | 5631.8463 | 6042.8684 | 6485.5584 | 6962.4253 | 7476.1804 | 8029.7535 | 8626.3113 | 9269.2758 | 9962.3463 | 10709.5209 | 11515.1216 | 12383.8207 | 13320.6691 | 14331.1278 | 15421.101 | 16596.9725 |  | 0.84798 | 0.84798 | 0.84798 | 0.84798 | 0.84798 | 0.84798 | 0.84798 | 0.84798 | 0.84798 | 0.84798 | 0.84798 | 0.84798 | 0.84798 | 0.84798 | 0.84798 | 0.84798 | 0.84798 | 1.015 | 1.3454 | 1.799 | 2.4244 | 3.2904 | 4.4937 | 6.1714 | 8.5176 | 11.8073 | 16.4311 | 22.9439 | 32.1349 | 45.1276 |  | 2166.4617 | 2314.409 | 2473.368 | 2644.1928 | 2827.805 | 3025.1998 | 3237.4515 | 3465.7203 | 3711.2587 | 3975.4196 | 4259.6641 | 4565.5701 | 4894.8423 | 5249.322 | 5630.9983 | 6042.0205 | 6484.7105 | 6961.4104 | 7474.835 | 8027.9545 | 8623.8868 | 9265.9855 | 9957.8526 | 10703.3494 | 11506.604 | 12372.0133 | 13304.238 | 14308.184 | 15388.9661 | 16551.8449 |  | 3930.1703 | 4200.672 | 4491.3074 | 4803.6376 | 5139.3479 | 5500.2579 | 5888.3317 | 6305.6905 | 6754.6246 | 7237.6075 | 7757.3104 | 8316.6186 | 8918.6487 | 9566.7672 | 10264.6113 | 11016.1102 | 11825.5096 | 12691.0032 | 13617.6847 | 14612.4533 | 15679.2341 | 16821.6563 | 18042.7734 | 19344.6498 | 20727.7593 | 22190.1117 | 23725.991 | 25324.1367 | 26965.1274 | 28617.6243
| FALSE | 522 | 22013374 | BC | BC024 | 11 | BC24 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 1.5657 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 1.6829 |  | 6.522 | 0.016792 | 1.3211e-05 | 0.016779 | 46.1813 | 1.0569 | 47.2382 | 47.7407 | 6.7186 | 5.4681 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 1.6829 |  | 32.9817 | 107.1657 | 32.9817 | 74.184 |  | 0.14268 |  | 1.8058 | 2.0828 | 2.4022 | 2.7706 | 3.1955 | 3.6856 | 4.2509 | 4.9028 | 5.6548 | 6.522 | 7.5223 | 8.6759 | 10.0065 | 11.5412 | 13.3112 | 15.3527 | 17.7073 | 20.423 | 23.5552 | 27.1678 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0059365 | 0.0082972 | 0.01174 | 0.016792 | 0.024247 | 0.035303 | 0.051771 | 0.076395 | 0.11334 | 0.16892 | 0.25277 | 0.37953 | 0.57156 | 0.86294 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.6706e-06 | 6.528e-06 | 9.2365e-06 | 1.3211e-05 | 1.9077e-05 | 2.7775e-05 | 4.0732e-05 | 6.0105e-05 | 8.9168e-05 | 0.0001329 | 0.00019887 | 0.0002986 | 0.00044968 | 0.00067893 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 37.8867 | 52.9529 | 74.9239 | 107.1657 | 154.7448 | 225.3054 | 330.4051 | 487.5515 | 723.3089 | 1078.0406 | 1613.1547 | 2422.1787 | 3647.6954 | 5507.2553 | 6010.3031 | 6010.3031 | 6010.3031 | 6010.3031 | 6010.3031 | 6010.3031 | 6010.3031 | 6010.3031 | 6010.3031 | 6010.3031 |  | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 32.9817 | 39.477 | 52.3292 | 69.9712 | 94.2974 | 127.9773 | 174.7797 | 240.0341 | 331.287 | 459.2386 | 639.0781 | 892.3886 | 1249.8673 | 1755.2094 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.3267 | 22.8192 | 32.2872 | 46.1813 | 66.6848 | 97.0917 | 142.3828 | 210.1025 | 311.6984 | 464.5643 | 695.1632 | 1043.7991 | 1571.916 | 2373.2635 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1137 | 8.6063 | 18.0743 | 31.9684 | 52.4719 | 82.8788 | 128.1698 | 195.8896 | 297.4854 | 450.3514 | 680.9503 | 1026.7871 | 1549.3656 | 2343.1106 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.37365 | 0.52224 | 0.73892 | 1.0569 | 1.5261 | 2.222 | 3.2585 | 4.8084 | 7.1335 | 10.6319 | 15.9094 | 23.8882 | 35.9746 | 54.3141 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.38933 | 0.51609 | 0.69008 | 0.92999 | 1.2621 | 1.7237 | 2.3673 | 3.2672 | 4.5291 | 6.3028 | 8.801 | 12.3265 | 17.3104 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.048374 | 0.19696 | 0.41365 | 0.73162 | 1.2009 | 1.8968 | 2.9333 | 4.4831 | 6.8082 | 10.3067 | 15.5841 | 23.4989 | 35.4585 | 53.6241 | 58.3453 | 58.0132 | 57.5516 | 56.908 | 56.0081 | 54.7462 | 52.9726 | 50.4743 | 46.9488 | 41.965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1621 | 8.8032 | 18.488 | 32.7 | 53.6727 | 84.7756 | 131.1031 | 200.3727 | 304.2936 | 460.6581 | 696.5344 | 1050.286 | 1584.8241 | 2396.7346 | 2607.7534 | 2592.9074 | 2572.277 | 2543.5132 | 2503.2892 | 2446.8886 | 2367.616 | 2255.9577 | 2098.3824 | 1875.6295 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 16.878 | 23.5898 | 33.3775 | 47.7407 | 68.9365 | 100.3702 | 147.1906 | 217.197 | 322.2235 | 480.2512 | 718.6367 | 1079.045 | 1624.9947 | 2453.4013 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1851 | 8.8969 | 18.6846 | 33.0479 | 54.2437 | 85.6774 | 132.4977 | 202.5042 | 307.5306 | 465.5584 | 703.9439 | 1061.4586 | 1601.6828 | 2422.2302 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.3752 | 3.3198 | 4.6972 | 6.7186 | 9.7015 | 14.1251 | 20.7142 | 30.5662 | 45.3466 | 67.5859 | 101.134 | 151.8543 | 228.686 | 345.2679 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.30751 | 1.2521 | 2.6295 | 4.6508 | 7.6337 | 12.0574 | 18.6464 | 28.4985 | 43.2789 | 65.5182 | 99.0662 | 149.3794 | 225.4053 | 340.8812 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.9332 | 2.7019 | 3.823 | 5.4681 | 7.8959 | 11.4962 | 16.859 | 24.8774 | 36.9069 | 55.0072 | 82.3114 | 123.592 | 186.1241 | 281.0084 | 306.6765 | 306.6765 | 306.6765 | 306.6765 | 306.6765 | 306.6765 | 306.6765 | 306.6765 | 306.6765 | 306.6765 |  | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 1.6829 | 2.0143 | 2.6701 | 3.5703 | 4.8115 | 6.5301 | 8.9182 | 12.2478 | 16.904 | 23.4327 | 32.609 | 45.5342 | 63.7746 | 89.5598 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.25028 | 1.019 | 2.1401 | 3.7852 | 6.213 | 9.8133 | 15.1761 | 23.1945 | 35.224 | 53.3243 | 80.6285 | 121.5777 | 183.454 | 277.4381 | 301.865 | 300.1464 | 297.7583 | 294.4287 | 289.7725 | 283.2438 | 274.0675 | 261.1423 | 242.9019 | 217.1167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 4.905 | 19.9712 | 41.9422 | 74.184 | 121.7631 | 192.3237 | 297.4233 | 454.5698 | 690.3272 | 1045.0589 | 1580.173 | 2382.7016 | 3595.3663 | 5437.2841 | 5916.0058 | 5882.3259 | 5835.5234 | 5770.269 | 5679.0162 | 5551.0645 | 5371.225 | 5117.9145 | 4760.4359 | 4255.0937
| FALSE | 523 | 22013372 | BC | BC003 | 11 | BC3 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 1.5657 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 3.4253 |  | 6.522 | 0.016792 | 1.3211e-05 | 0.016779 | 46.1813 | 1.0569 | 47.2382 | 47.7407 | 6.7186 | 11.1295 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 3.4253 |  | 34.7241 | 112.8271 | 34.7241 | 78.103 |  | 0.14268 |  | 1.8058 | 2.0828 | 2.4022 | 2.7706 | 3.1955 | 3.6856 | 4.2509 | 4.9028 | 5.6548 | 6.522 | 7.5223 | 8.6759 | 10.0065 | 11.5412 | 13.3112 | 15.3527 | 17.7073 | 20.423 | 23.5552 | 27.1678 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0059365 | 0.0082972 | 0.01174 | 0.016792 | 0.024247 | 0.035303 | 0.051771 | 0.076395 | 0.11334 | 0.16892 | 0.25277 | 0.37953 | 0.57156 | 0.86294 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.6706e-06 | 6.528e-06 | 9.2365e-06 | 1.3211e-05 | 1.9077e-05 | 2.7775e-05 | 4.0732e-05 | 6.0105e-05 | 8.9168e-05 | 0.0001329 | 0.00019887 | 0.0002986 | 0.00044968 | 0.00067893 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 39.8882 | 55.7504 | 78.882 | 112.8271 | 162.9197 | 237.2079 | 347.8598 | 513.308 | 761.5201 | 1134.9917 | 1698.375 | 2550.1383 | 3840.3971 | 5798.1943 | 6327.8173 | 6327.8173 | 6327.8173 | 6327.8173 | 6327.8173 | 6327.8173 | 6327.8173 | 6327.8173 | 6327.8173 | 6327.8173 |  | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 34.7241 | 41.5626 | 55.0936 | 73.6676 | 99.2789 | 134.7381 | 184.013 | 252.7147 | 348.7883 | 483.4994 | 672.8395 | 939.532 | 1315.8956 | 1847.9341 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.3267 | 22.8192 | 32.2872 | 46.1813 | 66.6848 | 97.0917 | 142.3828 | 210.1025 | 311.6984 | 464.5643 | 695.1632 | 1043.7991 | 1571.916 | 2373.2635 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1137 | 8.6063 | 18.0743 | 31.9684 | 52.4719 | 82.8788 | 128.1698 | 195.8896 | 297.4854 | 450.3514 | 680.9503 | 1026.7871 | 1549.3656 | 2343.1106 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.37365 | 0.52224 | 0.73892 | 1.0569 | 1.5261 | 2.222 | 3.2585 | 4.8084 | 7.1335 | 10.6319 | 15.9094 | 23.8882 | 35.9746 | 54.3141 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.38933 | 0.51609 | 0.69008 | 0.92999 | 1.2621 | 1.7237 | 2.3673 | 3.2672 | 4.5291 | 6.3028 | 8.801 | 12.3265 | 17.3104 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.048374 | 0.19696 | 0.41365 | 0.73162 | 1.2009 | 1.8968 | 2.9333 | 4.4831 | 6.8082 | 10.3067 | 15.5841 | 23.4989 | 35.4585 | 53.6241 | 58.3453 | 58.0132 | 57.5516 | 56.908 | 56.0081 | 54.7462 | 52.9726 | 50.4743 | 46.9488 | 41.965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1621 | 8.8032 | 18.488 | 32.7 | 53.6727 | 84.7756 | 131.1031 | 200.3727 | 304.2936 | 460.6581 | 696.5344 | 1050.286 | 1584.8241 | 2396.7346 | 2607.7534 | 2592.9074 | 2572.277 | 2543.5132 | 2503.2892 | 2446.8886 | 2367.616 | 2255.9577 | 2098.3824 | 1875.6295 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 16.878 | 23.5898 | 33.3775 | 47.7407 | 68.9365 | 100.3702 | 147.1906 | 217.197 | 322.2235 | 480.2512 | 718.6367 | 1079.045 | 1624.9947 | 2453.4013 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.1851 | 8.8969 | 18.6846 | 33.0479 | 54.2437 | 85.6774 | 132.4977 | 202.5042 | 307.5306 | 465.5584 | 703.9439 | 1061.4586 | 1601.6828 | 2422.2302 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.3752 | 3.3198 | 4.6972 | 6.7186 | 9.7015 | 14.1251 | 20.7142 | 30.5662 | 45.3466 | 67.5859 | 101.134 | 151.8543 | 228.686 | 345.2679 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.30751 | 1.2521 | 2.6295 | 4.6508 | 7.6337 | 12.0574 | 18.6464 | 28.4985 | 43.2789 | 65.5182 | 99.0662 | 149.3794 | 225.4053 | 340.8812 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.9347 | 5.4993 | 7.7811 | 11.1295 | 16.0708 | 23.3987 | 34.3137 | 50.6339 | 75.1181 | 111.9582 | 167.5317 | 251.5516 | 378.8258 | 571.9475 | 624.1907 | 624.1907 | 624.1907 | 624.1907 | 624.1907 | 624.1907 | 624.1907 | 624.1907 | 624.1907 | 624.1907 |  | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 3.4253 | 4.0998 | 5.4346 | 7.2667 | 9.7931 | 13.2909 | 18.1515 | 24.9284 | 34.4053 | 47.6935 | 66.3705 | 92.6776 | 129.803 | 182.2845 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.5094 | 2.0741 | 4.3558 | 7.7043 | 12.6455 | 19.9735 | 30.8884 | 47.2086 | 71.6929 | 108.533 | 164.1064 | 247.4518 | 373.3912 | 564.6807 | 614.3976 | 610.8998 | 606.0392 | 599.2623 | 589.7854 | 576.4972 | 557.8202 | 531.5131 | 494.3877 | 441.9062 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5.1641 | 21.0263 | 44.1579 | 78.103 | 128.1956 | 202.4838 | 313.1357 | 478.584 | 726.796 | 1100.2676 | 1663.6509 | 2508.5757 | 3785.3034 | 5724.5267 | 6228.5384 | 6193.0792 | 6143.8043 | 6075.1027 | 5979.029 | 5844.3179 | 5654.9778 | 5388.2853 | 5011.9217 | 4479.8832
| TRUE | 524 | 22013847 | BC | BC006 | 11 | BC6 | SENSITIVE EF | Blank | RPL | ARTC_650 | ARTC 650 | AVE | Electromechanical |  | 0.57434 | 2190 |  | 2.5292 | 0.00090442 | 0.00065051 | 0.00025391 | 2.6661 | 52.0408 | 54.7069 | 6.2604 | 0.36836 | 274.0044 |  | 4.7392 | 0.0013394 | 0.00096335 | 0.00037602 | 3.9482 | 77.0677 | 81.0159 | 9.2711 | 0.54551 | 405.7753 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 1.7126 |  | 335.34 | 496.6078 | 33.0115 | 463.5963 |  | 0.062797 |  | 2.6931 | 2.8677 | 3.0535 | 3.2514 | 3.4622 | 3.6865 | 3.9255 | 4.1799 | 4.4508 | 4.7392 | 5.0464 | 5.3734 | 5.7217 | 6.0925 | 6.4874 | 6.9078 | 7.3555 | 7.8322 | 8.3398 | 8.8804 | 9.4559 | 10.0687 | 10.7213 | 11.4161 | 12.156 | 12.9438 | 13.7827 | 14.676 | 15.6272 | 16.64 |  | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00090442 | 0.00099954 | 0.0011556 | 0.0013394 | 0.0015562 | 0.0018123 | 0.0021153 | 0.002474 | 0.0028992 | 0.0034038 | 0.0040031 | 0.0047157 | 0.0055637 | 0.0065737 | 0.0077776 | 0.0092136 | 0.010928 | 0.012976 | 0.015423 | 0.018351 | 0.021854 | 0.026048 | 0.031073 | 0.037095 |  | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00065051 | 0.00071893 | 0.00083114 | 0.00096335 | 0.0011193 | 0.0013035 | 0.0015214 | 0.0017794 | 0.0020853 | 0.0024482 | 0.0028793 | 0.0033918 | 0.0040017 | 0.0047282 | 0.005594 | 0.006627 | 0.00786 | 0.0093328 | 0.011093 | 0.013199 | 0.015719 | 0.018735 | 0.022349 | 0.02668 | 335.34 | 335.34 | 335.34 | 335.34 | 335.34 | 335.34 | 335.34 | 370.609 | 428.4564 | 496.6078 | 577.0074 | 671.9791 | 784.302 | 917.3015 | 1074.9586 | 1262.0418 | 1484.2649 | 1748.478 | 2062.8964 | 2437.3765 | 2883.7484 | 3416.2154 | 4051.8359 | 4811.1039 | 5718.6473 | 6804.0708 | 8102.9701 | 9658.1545 | 11521.1215 | 13753.8322 |  | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 39.5126 | 52.3763 | 70.0343 | 94.3824 | 128.0926 | 174.9373 | 240.2505 | 331.5856 | 459.6526 | 639.6543 | 893.1932 | 1250.9941 | 1756.7919 |  | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.6661 | 2.9465 | 3.4064 | 3.9482 | 4.5874 | 5.3424 | 6.2354 | 7.2928 | 8.5462 | 10.0336 | 11.8003 | 13.9009 | 16.4006 | 19.3779 | 22.9267 | 27.1599 | 32.2133 | 38.2497 | 45.4649 | 54.0944 | 64.421 | 76.7852 | 91.5963 | 109.347 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.5469 | -11.2665 | -10.8066 | -10.2648 | -9.6256 | -8.8705 | -7.9775 | -6.9201 | -5.6667 | -4.1793 | -2.4126 | -3.1111 | -6.1498 | -10.7751 | -17.7093 | -27.9898 | -43.1052 | -65.1891 | -97.2979 | -143.8071 | -210.9795 | -307.7754 | -447.014 | -647.0324 |  | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 52.0408 | 57.5142 | 66.4914 | 77.0677 | 89.5448 | 104.2833 | 121.7144 | 142.3544 | 166.8209 | 195.854 | 230.3405 | 271.3432 | 320.1373 | 378.2522 | 447.5238 | 530.1564 | 628.7973 | 746.6267 | 887.4668 | 1055.9118 | 1257.4856 | 1498.832 | 1787.9425 | 2134.433 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.38933 | 0.51609 | 0.69008 | 0.92999 | 1.2621 | 1.7237 | 2.3673 | 3.2672 | 4.5291 | 6.3028 | 8.801 | 12.3265 | 17.3104 |  | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 51.7156 | 57.1889 | 66.1661 | 76.7424 | 89.2195 | 103.958 | 121.3892 | 142.0291 | 166.4957 | 195.5288 | 230.0152 | 270.9539 | 319.6212 | 377.5621 | 446.5938 | 528.8943 | 627.0735 | 744.2594 | 884.1996 | 1051.3826 | 1251.1829 | 1490.031 | 1775.616 | 2117.1226 |  | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 40.1687 | 45.9224 | 55.3595 | 66.4776 | 79.5939 | 95.0875 | 113.4117 | 135.109 | 160.829 | 191.3494 | 227.6026 | 267.8428 | 313.4714 | 366.787 | 428.8846 | 500.9045 | 583.9683 | 679.0703 | 786.9017 | 907.5755 | 1040.2034 | 1182.2556 | 1328.602 | 1470.0902 |  | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.2604 | 6.9188 | 7.9988 | 9.2711 | 10.7721 | 12.5451 | 14.642 | 17.1249 | 20.0682 | 23.5608 | 27.7095 | 32.642 | 38.5119 | 45.503 | 53.8362 | 63.7768 | 75.643 | 89.8177 | 106.7605 | 127.0241 | 151.273 | 180.3065 | 215.0859 | 256.768 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -8.4325 | -7.774 | -6.6941 | -5.4218 | -3.9208 | -2.1478 | -0.050867 | 2.4321 | 5.3754 | 8.868 | 13.0166 | 15.0556 | 15.2 | 14.3318 | 11.8281 | 6.7648 | -2.2188 | -17.114 | -40.823 | -77.56 | -133.4269 | -217.2395 | -341.7116 | -525.152 |  | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.36836 | 0.40711 | 0.47065 | 0.54551 | 0.63383 | 0.73816 | 0.86154 | 1.0076 | 1.1808 | 1.3863 | 1.6304 | 1.9207 | 2.2661 | 2.6774 | 3.1677 | 3.7526 | 4.4509 | 5.2849 | 6.2818 | 7.4741 | 8.901 | 10.6093 | 12.6557 | 15.1083 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6994 | -1.6606 | -1.5971 | -1.5222 | -1.4339 | -1.3296 | -1.2062 | -1.0601 | -0.88691 | -0.6814 | -0.4373 | -0.55428 | -1.0146 | -1.7093 | -2.7441 | -4.2707 | -6.5066 | -9.7636 | -14.4876 | -21.317 | -31.1649 | -45.3375 | -65.7025 | -94.9315 |  | 274.0044 | 274.0044 | 274.0044 | 274.0044 | 274.0044 | 274.0044 | 274.0044 | 302.8224 | 350.0892 | 405.7753 | 471.4694 | 549.0702 | 640.8486 | 749.5217 | 878.3424 | 1031.207 | 1212.7842 | 1428.6712 | 1685.5806 | 1991.5661 | 2356.294 | 2791.3696 | 3310.7314 | 3931.1248 | 4672.6733 | 5559.5665 | 6620.8895 | 7891.6216 | 9413.841 | 11238.1759 |  | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 2.0499 | 2.7173 | 3.6334 | 4.8966 | 6.6454 | 9.0757 | 12.4642 | 17.2026 | 23.8468 | 33.1852 | 46.3388 | 64.9015 | 91.1423 |  | 272.2917 | 272.2917 | 272.2917 | 272.2917 | 272.2917 | 272.2917 | 272.2917 | 301.1098 | 348.3766 | 404.0627 | 469.7567 | 547.3576 | 639.1359 | 747.809 | 876.6298 | 1029.4943 | 1211.0715 | 1426.6212 | 1682.8633 | 1987.9327 | 2351.3974 | 2784.7242 | 3301.6557 | 3918.6606 | 4655.4706 | 5535.7197 | 6587.7042 | 7845.2828 | 9348.9395 | 11147.0336 |  | 302.3286 | 302.3286 | 302.3286 | 302.3286 | 302.3286 | 302.3286 | 302.3286 | 337.5975 | 395.4449 | 463.5963 | 543.9959 | 638.9676 | 751.2905 | 884.29 | 1041.9472 | 1229.0303 | 1451.2535 | 1708.9654 | 2010.52 | 2367.3423 | 2789.366 | 3288.1227 | 3876.8986 | 4570.8534 | 5387.0617 | 6344.4182 | 7463.3158 | 8764.9614 | 10270.1274 | 11997.0403
| TRUE | 525 | 22005280 | BC | BC006 | 11 | BC6 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 2666.6183 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 6636.7909 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 1.7126 |  | 4808.8731 | 11968.5241 | 48.2002 | 11920.3239 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 5260.8611 | 5757.2182 | 6302.402 | 6901.3245 | 7559.3984 | 8282.5892 | 9077.4717 | 9951.2931 | 10912.0417 | 11968.5241 | 13130.449 | 14408.5207 | 15814.5415 | 17361.5256 | 19063.824 | 20937.2626 | 22999.2952 | 25269.1715 | 27768.1231 | 30519.5689 | 33549.3412 | 36885.9361 | 40560.7896 | 44608.5822 | 49067.5752 | 53979.9827 | 59392.3812 | 65356.1627 | 71928.0344 | 79170.5708 |  | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 40.6954 | 53.9441 | 72.1306 | 97.2075 | 131.9268 | 180.1737 | 247.4419 | 341.5109 | 473.4113 | 658.8009 | 919.929 | 1288.4399 | 1809.3776 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 2917.2549 | 3192.495 | 3494.8106 | 3826.9253 | 4191.8407 | 4592.8648 | 5033.6434 | 5518.1951 | 6050.9499 | 6636.7909 | 7281.102 | 7989.8188 | 8769.4861 | 9627.3204 | 10571.2795 | 11610.1395 | 12753.5787 | 14012.2714 | 15397.9911 | 16923.7239 | 18603.7945 | 20454.0045 | 22491.7858 | 24736.3694 | 27208.9721 | 29933.0023 | 32934.2878 | 36241.3263 | 39885.5633 | 43901.6976 |  | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 2.0499 | 2.7173 | 3.6334 | 4.8966 | 6.6454 | 9.0757 | 12.4642 | 17.2026 | 23.8468 | 33.1852 | 46.3388 | 64.9015 | 91.1423 |  | 2915.5422 | 3190.7824 | 3493.0979 | 3825.2127 | 4190.1281 | 4591.1521 | 5031.9307 | 5516.4825 | 6049.2372 | 6635.0783 | 7279.3894 | 7988.1062 | 8767.7735 | 9625.6077 | 10569.5669 | 11608.4269 | 12751.866 | 14010.2215 | 15395.2738 | 16920.0906 | 18598.898 | 20447.3591 | 22482.7101 | 24723.9052 | 27191.7694 | 29909.1556 | 32901.1026 | 36194.9875 | 39820.6618 | 43810.5553 |  | 5226.8738 | 5723.2309 | 6268.4147 | 6867.3372 | 7525.4111 | 8248.6019 | 9043.4845 | 9917.3058 | 10878.0544 | 11934.5368 | 13096.4617 | 14374.5334 | 15780.5542 | 17327.5383 | 19029.8367 | 20903.2753 | 22965.3079 | 25228.4908 | 27714.1985 | 30447.4644 | 33452.1688 | 36754.057 | 40380.6811 | 44361.2298 | 48726.1879 | 53506.7427 | 58733.8186 | 64436.5665 | 70640.0606 | 77361.8478
| TRUE | 526 | 22005279 | BC | BC006 | 11 | BC6 | OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 2666.6183 |  | 13.7946 | 0.021906 | 0.015756 | 0.0061501 | 129.1515 | 5042.023 | 5171.1745 | 151.6363 | 8.9223 | 6636.7909 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 1.7126 |  | 4808.8731 | 11968.5241 | 48.2002 | 11920.3239 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0069258 | 0.0075793 | 0.008297 | 0.0090855 | 0.0099518 | 0.010904 | 0.01195 | 0.013101 | 0.014365 | 0.015756 | 0.017286 | 0.018969 | 0.02082 | 0.022856 | 0.025097 | 0.027563 | 0.030278 | 0.033266 | 0.036556 | 0.040178 | 0.044167 | 0.04856 | 0.053397 | 0.058726 | 0.064596 | 0.071064 | 0.078189 | 0.08604 | 0.094692 | 0.10423 | 5260.8611 | 5757.2182 | 6302.402 | 6901.3245 | 7559.3984 | 8282.5892 | 9077.4717 | 9951.2931 | 10912.0417 | 11968.5241 | 13130.449 | 14408.5207 | 15814.5415 | 17361.5256 | 19063.824 | 20937.2626 | 22999.2952 | 25269.1715 | 27768.1231 | 30519.5689 | 33549.3412 | 36885.9361 | 40560.7896 | 44608.5822 | 49067.5752 | 53979.9827 | 59392.3812 | 65356.1627 | 71928.0344 | 79170.5708 |  | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 33.9996 | 40.6954 | 53.9441 | 72.1306 | 97.2075 | 131.9268 | 180.1737 | 247.4419 | 341.5109 | 473.4113 | 658.8009 | 919.929 | 1288.4399 | 1809.3776 |  | 56.7696 | 62.1257 | 68.0088 | 74.4717 | 81.5729 | 89.3768 | 97.9543 | 107.3837 | 117.751 | 129.1515 | 141.6897 | 155.4813 | 170.6536 | 187.347 | 205.7163 | 225.9325 | 248.1837 | 272.6778 | 299.6438 | 329.3344 | 362.0285 | 398.0334 | 437.6885 | 481.3679 | 529.4846 | 582.494 | 640.8988 | 705.2536 | 776.1702 | 854.3238 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 42.5566 | 47.9128 | 53.7958 | 60.2587 | 67.36 | 75.1639 | 83.7414 | 93.1707 | 103.5381 | 114.9385 | 127.4768 | 141.2684 | 156.4406 | 173.134 | 191.5034 | 211.7195 | 233.9708 | 255.6658 | 277.0934 | 299.1815 | 321.3925 | 342.8837 | 362.37 | 377.9291 | 386.7218 | 384.5925 | 365.4984 | 320.693 | 237.5599 | 97.9444 |  | 2216.2618 | 2425.3639 | 2655.0355 | 2907.3457 | 3184.5749 | 3489.236 | 3824.0991 | 4192.2169 | 4596.9549 | 5042.023 | 5531.5113 | 6069.9292 | 6662.2486 | 7313.9521 | 8031.0855 | 8820.3157 | 9688.9955 | 10645.2345 | 11697.9768 | 12857.0882 | 14133.4512 | 15539.0706 | 17087.1893 | 18792.4174 | 20670.8734 | 22740.3409 | 25020.4414 | 27532.825 | 30301.3809 | 33352.4702 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2214.9607 | 2424.0628 | 2653.7344 | 2906.0446 | 3183.2738 | 3487.9349 | 3822.798 | 4190.9158 | 4595.6538 | 5040.7219 | 5530.2102 | 6068.6281 | 6660.9475 | 7312.651 | 8029.7844 | 8819.0146 | 9687.6944 | 10643.6771 | 11695.9125 | 12854.3279 | 14129.7313 | 15534.022 | 17080.2944 | 18782.9482 | 20657.8044 | 22722.2243 | 24995.2303 | 27497.621 | 30252.0747 | 33283.2287 |  | 2257.5173 | 2471.9756 | 2707.5302 | 2966.3033 | 3250.6337 | 3563.0988 | 3906.5394 | 4284.0865 | 4699.1919 | 5155.6605 | 5657.687 | 6209.8964 | 6817.3881 | 7485.7851 | 8221.2878 | 9030.7341 | 9921.6652 | 10899.3429 | 11973.0058 | 13153.5094 | 14451.1238 | 15876.9057 | 17442.6644 | 19160.8773 | 21044.5262 | 23106.8168 | 25360.7287 | 27818.314 | 30489.6346 | 33381.1732 |  | 66.653 | 72.9416 | 79.8489 | 87.437 | 95.7745 | 104.937 | 115.0079 | 126.0788 | 138.2511 | 151.6363 | 166.3574 | 182.5501 | 200.3638 | 219.9634 | 241.5309 | 265.2666 | 291.3917 | 320.1501 | 351.8108 | 386.6705 | 425.0564 | 467.3297 | 513.8886 | 565.1725 | 621.6661 | 683.9043 | 752.4772 | 828.0358 | 911.2988 | 1003.0587 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 51.9601 | 58.2487 | 65.156 | 72.7441 | 81.0816 | 90.2441 | 100.315 | 111.3859 | 123.5582 | 136.9434 | 151.6645 | 167.8572 | 185.6709 | 205.2706 | 226.838 | 250.5737 | 276.6988 | 302.5636 | 328.4989 | 355.4993 | 383.0483 | 410.3177 | 436.0268 | 458.2408 | 474.0826 | 479.3203 | 467.7773 | 430.4898 | 354.5013 | 221.1388 |  | 3.9219 | 4.2919 | 4.6983 | 5.1448 | 5.6354 | 6.1745 | 6.7671 | 7.4185 | 8.1347 | 8.9223 | 9.7885 | 10.7413 | 11.7895 | 12.9427 | 14.2118 | 15.6084 | 17.1456 | 18.8377 | 20.7007 | 22.7518 | 25.0105 | 27.4979 | 30.2374 | 33.255 | 36.5791 | 40.2412 | 44.276 | 48.7219 | 53.6211 | 59.0203 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8542 | 2.2242 | 2.6306 | 3.0771 | 3.5677 | 4.1068 | 4.6994 | 5.3508 | 6.067 | 6.8546 | 7.7208 | 8.6736 | 9.7217 | 10.875 | 12.144 | 13.5406 | 15.0779 | 16.3628 | 17.42 | 18.3651 | 19.0987 | 19.4745 | 19.2799 | 18.2064 | 15.8096 | 11.45 | 4.2101 | -7.2248 | -24.7371 | -51.0195 |  | 2917.2549 | 3192.495 | 3494.8106 | 3826.9253 | 4191.8407 | 4592.8648 | 5033.6434 | 5518.1951 | 6050.9499 | 6636.7909 | 7281.102 | 7989.8188 | 8769.4861 | 9627.3204 | 10571.2795 | 11610.1395 | 12753.5787 | 14012.2714 | 15397.9911 | 16923.7239 | 18603.7945 | 20454.0045 | 22491.7858 | 24736.3694 | 27208.9721 | 29933.0023 | 32934.2878 | 36241.3263 | 39885.5633 | 43901.6976 |  | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 2.0499 | 2.7173 | 3.6334 | 4.8966 | 6.6454 | 9.0757 | 12.4642 | 17.2026 | 23.8468 | 33.1852 | 46.3388 | 64.9015 | 91.1423 |  | 2915.5422 | 3190.7824 | 3493.0979 | 3825.2127 | 4190.1281 | 4591.1521 | 5031.9307 | 5516.4825 | 6049.2372 | 6635.0783 | 7279.3894 | 7988.1062 | 8767.7735 | 9625.6077 | 10569.5669 | 11608.4269 | 12751.866 | 14010.2215 | 15395.2738 | 16920.0906 | 18598.898 | 20447.3591 | 22482.7101 | 24723.9052 | 27191.7694 | 29909.1556 | 32901.1026 | 36194.9875 | 39820.6618 | 43810.5553 |  | 5226.8738 | 5723.2309 | 6268.4147 | 6867.3372 | 7525.4111 | 8248.6019 | 9043.4845 | 9917.3058 | 10878.0544 | 11934.5368 | 13096.4617 | 14374.5334 | 15780.5542 | 17327.5383 | 19029.8367 | 20903.2753 | 22965.3079 | 25228.4908 | 27714.1985 | 30447.4644 | 33452.1688 | 36754.057 | 40380.6811 | 44361.2298 | 48726.1879 | 53506.7427 | 58733.8186 | 64436.5665 | 70640.0606 | 77361.8478
| TRUE | 527 | 22015696 | BC | BC006 | 11 | BC6 | AUTO RECLOSE | Blank | English Electric | GROUP_624 | GROUP 624 | GROUP 000s | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 53.114 | 1051.8847 | 1104.9987 | 45.1415 | 3.7652 | 1384.5908 |  | 7.1791 | 0.018276 | 0.00644 | 0.011836 | 104.0585 | 2060.8049 | 2164.8634 | 88.4392 | 7.3765 | 2712.6277 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 28.4243 | 0.35573 | 28.78 | 14.6761 | 2.0677 | 0.46825 |  | 2538.4962 | 4973.3068 | 45.992 | 4927.3148 |  | 0.026643 |  | 5.6485 | 5.801 | 5.9577 | 6.1185 | 6.2837 | 6.4534 | 6.6277 | 6.8066 | 6.9904 | 7.1791 | 7.373 | 7.5721 | 7.7765 | 7.9865 | 8.2022 | 8.4236 | 8.6511 | 8.8847 | 9.1246 | 9.3709 | 9.624 | 9.8838 | 10.1507 | 10.4248 | 10.7063 | 10.9954 | 11.2923 | 11.5972 | 11.9103 | 12.2319 |  | 0.0099614 | 0.010641 | 0.011372 | 0.012157 | 0.013001 | 0.013908 | 0.014884 | 0.015933 | 0.017062 | 0.018276 | 0.019582 | 0.020988 | 0.022502 | 0.024131 | 0.025885 | 0.027774 | 0.029809 | 0.032001 | 0.034362 | 0.036906 | 0.039648 | 0.042603 | 0.045789 | 0.049223 | 0.052926 | 0.056919 | 0.061224 | 0.065869 | 0.070879 | 0.076283 |  | 0.0035102 | 0.0037498 | 0.0040073 | 0.0042839 | 0.0045813 | 0.004901 | 0.0052448 | 0.0056145 | 0.0060122 | 0.00644 | 0.0069004 | 0.0073958 | 0.0079291 | 0.0085032 | 0.0091214 | 0.0097871 | 0.010504 | 0.011276 | 0.012109 | 0.013005 | 0.013971 | 0.015013 | 0.016135 | 0.017345 | 0.01865 | 0.020057 | 0.021574 | 0.023211 | 0.024976 | 0.026881 | 2710.7572 | 2895.8019 | 3094.6195 | 3308.2782 | 3537.9307 | 3784.8218 | 4050.2951 | 4335.8016 | 4642.9082 | 4973.3068 | 5328.8249 | 5711.4361 | 6123.2725 | 6566.637 | 7044.0178 | 7558.1027 | 8111.7961 | 8708.2362 | 9350.814 | 10043.1943 | 10789.3374 | 11593.5237 | 12460.3798 | 13394.9066 | 14402.5097 | 15489.0329 | 16660.7938 | 17924.6225 | 19287.9038 | 20758.6221 |  | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 38.0426 | 50.4277 | 67.4287 | 90.8709 | 123.327 | 168.4288 | 231.312 | 319.2491 | 442.5514 | 615.8561 | 859.9622 | 1204.4512 | 1691.4309 |  | 56.7183 | 60.59 | 64.75 | 69.2205 | 74.0256 | 79.1914 | 84.746 | 90.7197 | 97.1455 | 104.0585 | 111.4972 | 119.5027 | 128.1197 | 137.3964 | 147.3849 | 158.1413 | 169.7264 | 182.206 | 195.6509 | 210.1379 | 225.7497 | 242.576 | 260.7136 | 280.2671 | 301.3496 | 324.0834 | 348.6006 | 375.0442 | 403.5687 | 434.3411 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 42.5062 | 46.3779 | 50.5379 | 55.0083 | 59.8134 | 64.9792 | 70.5338 | 76.5076 | 82.9333 | 89.8464 | 97.2851 | 105.2906 | 113.9076 | 123.1843 | 133.1727 | 143.9291 | 155.5143 | 165.195 | 173.1018 | 179.9866 | 185.1161 | 187.4294 | 185.3994 | 176.8342 | 158.5949 | 126.1931 | 73.2159 | -9.4944 | -135.0108 | -321.995 |  | 1123.265 | 1199.9426 | 1282.3273 | 1370.8617 | 1466.0235 | 1568.3286 | 1678.3336 | 1796.6398 | 1923.8966 | 2060.8049 | 2208.122 | 2366.6659 | 2537.3198 | 2721.0382 | 2918.8519 | 3131.8749 | 3361.3106 | 3608.4594 | 3874.7264 | 4161.6302 | 4470.8119 | 4804.0451 | 5163.247 | 5550.4898 | 5968.0135 | 6418.2396 | 6903.7858 | 7427.4825 | 7992.3897 | 8601.8159 |  | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.42579 | 0.56441 | 0.75469 | 1.0171 | 1.3803 | 1.8851 | 2.5889 | 3.5732 | 4.9532 | 6.8929 | 9.625 | 13.4807 | 18.9311 |  | 1122.9093 | 1199.5868 | 1281.9715 | 1370.506 | 1465.6678 | 1567.9728 | 1677.9779 | 1796.2841 | 1923.5408 | 2060.4492 | 2207.7663 | 2366.3101 | 2536.9641 | 2720.6824 | 2918.4962 | 3131.5192 | 3360.9549 | 3608.0336 | 3874.162 | 4160.8755 | 4469.7948 | 4802.6648 | 5161.3619 | 5547.9009 | 5964.4404 | 6413.2864 | 6896.8929 | 7417.8575 | 7978.909 | 8582.8848 |  | 1165.4155 | 1245.9648 | 1332.5094 | 1425.5143 | 1525.4813 | 1632.9521 | 1748.5117 | 1872.7917 | 2006.4742 | 2150.2956 | 2305.0513 | 2471.6007 | 2650.8717 | 2843.8667 | 3051.6689 | 3275.4483 | 3516.4692 | 3773.2285 | 4047.2638 | 4340.8621 | 4654.9109 | 4990.0942 | 5346.7613 | 5724.7351 | 6123.0353 | 6539.4795 | 6970.1088 | 7408.3631 | 7843.8982 | 8260.8898 |  | 48.2048 | 51.4954 | 55.031 | 58.8304 | 62.9143 | 67.3047 | 72.0255 | 77.1026 | 82.5638 | 88.4392 | 94.7613 | 101.5652 | 108.8888 | 116.7731 | 125.2623 | 134.4041 | 144.2503 | 154.8567 | 166.2835 | 178.596 | 191.8645 | 206.1651 | 221.5803 | 238.1987 | 256.1167 | 275.4381 | 296.2753 | 318.7497 | 342.9926 | 369.1461 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 33.5287 | 36.8193 | 40.3549 | 44.1543 | 48.2382 | 52.6286 | 57.3494 | 62.4265 | 67.8877 | 73.7631 | 80.0852 | 86.8891 | 94.2127 | 102.097 | 110.5862 | 119.728 | 129.5742 | 137.2903 | 142.9983 | 147.4604 | 149.9043 | 149.2182 | 143.8073 | 131.3892 | 108.7017 | 71.0876 | 11.9004 | -78.3425 | -213.1693 | -411.8813 |  | 4.0207 | 4.2951 | 4.59 | 4.9069 | 5.2475 | 5.6137 | 6.0075 | 6.431 | 6.8865 | 7.3765 | 7.9038 | 8.4713 | 9.0822 | 9.7398 | 10.4478 | 11.2103 | 12.0316 | 12.9163 | 13.8693 | 14.8963 | 16.003 | 17.1958 | 18.4815 | 19.8676 | 21.3621 | 22.9737 | 24.7117 | 26.5862 | 28.6083 | 30.7897 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 1.953 | 2.2274 | 2.5223 | 2.8392 | 3.1798 | 3.546 | 3.9398 | 4.3633 | 4.8188 | 5.3088 | 5.8361 | 6.4036 | 7.0145 | 7.6721 | 8.3801 | 9.1426 | 9.9639 | 10.4413 | 10.5887 | 10.5096 | 10.0913 | 9.1726 | 7.5242 | 4.8193 | 0.59296 | -5.8171 | -15.3537 | -29.3598 | -49.7489 | -79.2486 |  | 1478.5484 | 1579.4787 | 1687.9213 | 1804.4587 | 1929.7198 | 2064.3834 | 2209.1825 | 2364.9085 | 2532.4159 | 2712.6277 | 2906.5405 | 3115.231 | 3339.8619 | 3581.6896 | 3842.0709 | 4122.472 | 4424.4771 | 4749.7979 | 5100.2839 | 5477.934 | 5884.9083 | 6323.5417 | 6796.3574 | 7306.0833 | 7855.6677 | 8448.2982 | 9087.4204 | 9776.7599 | 10520.3445 | 11322.5293 |  | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.56046 | 0.74292 | 0.99339 | 1.3388 | 1.8169 | 2.4814 | 3.4078 | 4.7033 | 6.5199 | 9.0731 | 12.6694 | 17.7445 | 24.919 |  | 1478.0802 | 1579.0105 | 1687.453 | 1803.9905 | 1929.2516 | 2063.9152 | 2208.7143 | 2364.4402 | 2531.9476 | 2712.1594 | 2906.0723 | 3114.7627 | 3339.3937 | 3581.2213 | 3841.6026 | 4122.0038 | 4424.0089 | 4749.2374 | 5099.541 | 5476.9406 | 5883.5696 | 6321.7248 | 6793.8761 | 7302.6755 | 7850.9644 | 8441.7783 | 9078.3473 | 9764.0905 | 10502.5999 | 11297.6103 |  | 2678.9773 | 2864.022 | 3062.8396 | 3276.4983 | 3506.1508 | 3753.0419 | 4018.5152 | 4304.0217 | 4611.1283 | 4941.5269 | 5297.045 | 5679.6562 | 6091.4926 | 6534.8571 | 7012.2378 | 7526.3228 | 8080.0162 | 8670.1976 | 9300.3917 | 9975.7727 | 10698.4761 | 11470.2098 | 12291.9689 | 13163.619 | 14083.2944 | 15046.5283 | 16045.0028 | 17064.7513 | 18083.58 | 19067.3702
| TRUE | 528 | 22013845 | BC | BC007 | 11 | BC7 | OC & EF | X | Siemens | 7SR11 | 7SR11 | SIEMENS 7SR11 | Digital |  | 0.57434 | 1 |  | 1.8695 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 1.7126 |  | 6.2006 | 0.014776 | 1.1625e-05 | 0.014764 | 40.6359 | 0.92999 | 41.5659 | 42.0081 | 5.9118 | 4.8966 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.32528 | 14.5382 | 14.6929 | 2.0677 | 1.7126 |  | 33.0115 | 94.3824 | 33.0115 | 61.3709 |  | 0.11989 |  | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.8667e-06 | 6.4511e-06 | 8.6259e-06 | 1.1625e-05 | 1.5777e-05 | 2.1547e-05 | 2.9591e-05 | 4.0841e-05 | 5.6614e-05 | 7.8785e-05 | 0.00011001 | 0.00015408 | 0.00021638 | 0.00030458 | 0.00042962 | 0.00060709 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 39.5126 | 52.3763 | 70.0343 | 94.3824 | 128.0926 | 174.9373 | 240.2505 | 331.5856 | 459.6526 | 639.6543 | 893.1932 | 1250.9941 | 1756.7919 | 2472.8856 | 3488.0767 | 4929.017 | 6015.722 | 6015.722 | 6015.722 | 6015.722 | 6015.722 | 6015.722 | 6015.722 | 6015.722 |  | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 33.0115 | 39.5126 | 52.3763 | 70.0343 | 94.3824 | 128.0926 | 174.9373 | 240.2505 | 331.5856 | 459.6526 | 639.6543 | 893.1932 | 1250.9941 | 1756.7919 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 | 1064.6905 | 1501.7768 | 2122.1676 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.7991 | 8.3375 | 15.94 | 26.423 | 40.9368 | 61.1056 | 89.2259 | 128.5499 | 183.6886 | 261.1875 | 370.3477 | 521.5983 | 733.829 | 1034.5376 | 1461.1409 | 2067.0179 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.38933 | 0.51609 | 0.69008 | 0.92999 | 1.2621 | 1.7237 | 2.3673 | 3.2672 | 4.5291 | 6.3028 | 8.801 | 12.3265 | 17.3104 | 24.3663 | 34.3694 | 48.5676 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 | 59.2753 |  | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.32528 | 0.38933 | 0.51609 | 0.69008 | 0.92999 | 1.2621 | 1.7237 | 2.3673 | 3.2672 | 4.5291 | 6.3028 | 8.801 | 12.3265 | 17.3104 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.064059 | 0.19081 | 0.3648 | 0.60471 | 0.93687 | 1.3985 | 2.042 | 2.942 | 4.2039 | 5.9775 | 8.4757 | 11.9372 | 16.7943 | 23.6763 | 33.4394 | 47.3054 | 57.5516 | 56.908 | 56.0081 | 54.7462 | 52.9726 | 50.4743 | 46.9488 | 41.965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.8631 | 8.5283 | 16.3048 | 27.0277 | 41.8737 | 62.504 | 91.2679 | 131.4918 | 187.8925 | 267.165 | 378.8234 | 533.5355 | 750.6233 | 1058.2138 | 1494.5803 | 2114.3233 | 2572.277 | 2543.5132 | 2503.2892 | 2446.8886 | 2367.616 | 2255.9577 | 2098.3824 | 1875.6295 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 | 1100.6418 | 1552.4872 | 2193.8267 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.8936 | 8.619 | 16.4783 | 27.3152 | 42.3191 | 63.1689 | 92.2388 | 132.8906 | 189.8912 | 270.007 | 382.8531 | 539.2111 | 758.6081 | 1069.4707 | 1510.4791 | 2136.8147 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 | 154.8937 | 218.482 | 308.7379 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.213 | 2.319 | 3.8441 | 5.9556 | 8.8898 | 12.9808 | 18.7017 | 26.7234 | 37.9982 | 53.879 | 75.8833 | 106.7591 | 150.5069 | 212.5702 | 300.7146 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 2.0499 | 2.7173 | 3.6334 | 4.8966 | 6.6454 | 9.0757 | 12.4642 | 17.2026 | 23.8468 | 33.1852 | 46.3388 | 64.9015 | 91.1423 | 128.2932 | 180.9612 | 255.7172 | 312.0954 | 312.0954 | 312.0954 | 312.0954 | 312.0954 | 312.0954 | 312.0954 | 312.0954 |  | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 1.7126 | 2.0499 | 2.7173 | 3.6334 | 4.8966 | 6.6454 | 9.0757 | 12.4642 | 17.2026 | 23.8468 | 33.1852 | 46.3388 | 64.9015 | 91.1423 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.33728 | 1.0046 | 1.9207 | 3.1839 | 4.9328 | 7.3631 | 10.7516 | 15.49 | 22.1341 | 31.4726 | 44.6262 | 62.8516 | 88.425 | 124.6598 | 176.0647 | 249.0717 | 303.0196 | 299.6312 | 294.8927 | 288.2486 | 278.9101 | 265.7565 | 247.1938 | 220.9531 |  | 0 | 0 | 0 | 0 | 0 | 0 | 6.5012 | 19.3649 | 37.0228 | 61.3709 | 95.0812 | 141.9259 | 207.239 | 298.5742 | 426.6412 | 606.6428 | 860.1817 | 1211.4815 | 1704.4155 | 2402.8513 | 3393.6943 | 4800.9243 | 5840.7847 | 5775.4715 | 5684.1363 | 5556.0693 | 5376.0677 | 5122.5288 | 4764.7278 | 4258.9301
| TRUE | 529 | 22015697 | BC | BC007 | 11 | BC7 | AUTO RECLOSE | Blank | English Electric | GROUP_624 | GROUP 624 | GROUP 000s | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 53.114 | 1051.8847 | 1104.9987 | 45.1415 | 3.7652 | 1384.5908 |  | 7.1791 | 0.018276 | 0.00644 | 0.011836 | 104.0585 | 2060.8049 | 2164.8634 | 88.4392 | 7.3765 | 2712.6277 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 28.4243 | 0.35573 | 28.78 | 14.6761 | 2.0677 | 0.46825 |  | 2538.4962 | 4973.3068 | 45.992 | 4927.3148 |  | 0.026643 |  | 5.6485 | 5.801 | 5.9577 | 6.1185 | 6.2837 | 6.4534 | 6.6277 | 6.8066 | 6.9904 | 7.1791 | 7.373 | 7.5721 | 7.7765 | 7.9865 | 8.2022 | 8.4236 | 8.6511 | 8.8847 | 9.1246 | 9.3709 | 9.624 | 9.8838 | 10.1507 | 10.4248 | 10.7063 | 10.9954 | 11.2923 | 11.5972 | 11.9103 | 12.2319 |  | 0.0099614 | 0.010641 | 0.011372 | 0.012157 | 0.013001 | 0.013908 | 0.014884 | 0.015933 | 0.017062 | 0.018276 | 0.019582 | 0.020988 | 0.022502 | 0.024131 | 0.025885 | 0.027774 | 0.029809 | 0.032001 | 0.034362 | 0.036906 | 0.039648 | 0.042603 | 0.045789 | 0.049223 | 0.052926 | 0.056919 | 0.061224 | 0.065869 | 0.070879 | 0.076283 |  | 0.0035102 | 0.0037498 | 0.0040073 | 0.0042839 | 0.0045813 | 0.004901 | 0.0052448 | 0.0056145 | 0.0060122 | 0.00644 | 0.0069004 | 0.0073958 | 0.0079291 | 0.0085032 | 0.0091214 | 0.0097871 | 0.010504 | 0.011276 | 0.012109 | 0.013005 | 0.013971 | 0.015013 | 0.016135 | 0.017345 | 0.01865 | 0.020057 | 0.021574 | 0.023211 | 0.024976 | 0.026881 | 2710.7572 | 2895.8019 | 3094.6195 | 3308.2782 | 3537.9307 | 3784.8218 | 4050.2951 | 4335.8016 | 4642.9082 | 4973.3068 | 5328.8249 | 5711.4361 | 6123.2725 | 6566.637 | 7044.0178 | 7558.1027 | 8111.7961 | 8708.2362 | 9350.814 | 10043.1943 | 10789.3374 | 11593.5237 | 12460.3798 | 13394.9066 | 14402.5097 | 15489.0329 | 16660.7938 | 17924.6225 | 19287.9038 | 20758.6221 |  | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 31.7833 | 38.0426 | 50.4277 | 67.4287 | 90.8709 | 123.327 | 168.4288 | 231.312 | 319.2491 | 442.5514 | 615.8561 | 859.9622 | 1204.4512 | 1691.4309 |  | 56.7183 | 60.59 | 64.75 | 69.2205 | 74.0256 | 79.1914 | 84.746 | 90.7197 | 97.1455 | 104.0585 | 111.4972 | 119.5027 | 128.1197 | 137.3964 | 147.3849 | 158.1413 | 169.7264 | 182.206 | 195.6509 | 210.1379 | 225.7497 | 242.576 | 260.7136 | 280.2671 | 301.3496 | 324.0834 | 348.6006 | 375.0442 | 403.5687 | 434.3411 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 42.5062 | 46.3779 | 50.5379 | 55.0083 | 59.8134 | 64.9792 | 70.5338 | 76.5076 | 82.9333 | 89.8464 | 97.2851 | 105.2906 | 113.9076 | 123.1843 | 133.1727 | 143.9291 | 155.5143 | 165.195 | 173.1018 | 179.9866 | 185.1161 | 187.4294 | 185.3994 | 176.8342 | 158.5949 | 126.1931 | 73.2159 | -9.4944 | -135.0108 | -321.995 |  | 1123.265 | 1199.9426 | 1282.3273 | 1370.8617 | 1466.0235 | 1568.3286 | 1678.3336 | 1796.6398 | 1923.8966 | 2060.8049 | 2208.122 | 2366.6659 | 2537.3198 | 2721.0382 | 2918.8519 | 3131.8749 | 3361.3106 | 3608.4594 | 3874.7264 | 4161.6302 | 4470.8119 | 4804.0451 | 5163.247 | 5550.4898 | 5968.0135 | 6418.2396 | 6903.7858 | 7427.4825 | 7992.3897 | 8601.8159 |  | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.35573 | 0.42579 | 0.56441 | 0.75469 | 1.0171 | 1.3803 | 1.8851 | 2.5889 | 3.5732 | 4.9532 | 6.8929 | 9.625 | 13.4807 | 18.9311 |  | 1122.9093 | 1199.5868 | 1281.9715 | 1370.506 | 1465.6678 | 1567.9728 | 1677.9779 | 1796.2841 | 1923.5408 | 2060.4492 | 2207.7663 | 2366.3101 | 2536.9641 | 2720.6824 | 2918.4962 | 3131.5192 | 3360.9549 | 3608.0336 | 3874.162 | 4160.8755 | 4469.7948 | 4802.6648 | 5161.3619 | 5547.9009 | 5964.4404 | 6413.2864 | 6896.8929 | 7417.8575 | 7978.909 | 8582.8848 |  | 1165.4155 | 1245.9648 | 1332.5094 | 1425.5143 | 1525.4813 | 1632.9521 | 1748.5117 | 1872.7917 | 2006.4742 | 2150.2956 | 2305.0513 | 2471.6007 | 2650.8717 | 2843.8667 | 3051.6689 | 3275.4483 | 3516.4692 | 3773.2285 | 4047.2638 | 4340.8621 | 4654.9109 | 4990.0942 | 5346.7613 | 5724.7351 | 6123.0353 | 6539.4795 | 6970.1088 | 7408.3631 | 7843.8982 | 8260.8898 |  | 48.2048 | 51.4954 | 55.031 | 58.8304 | 62.9143 | 67.3047 | 72.0255 | 77.1026 | 82.5638 | 88.4392 | 94.7613 | 101.5652 | 108.8888 | 116.7731 | 125.2623 | 134.4041 | 144.2503 | 154.8567 | 166.2835 | 178.596 | 191.8645 | 206.1651 | 221.5803 | 238.1987 | 256.1167 | 275.4381 | 296.2753 | 318.7497 | 342.9926 | 369.1461 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 33.5287 | 36.8193 | 40.3549 | 44.1543 | 48.2382 | 52.6286 | 57.3494 | 62.4265 | 67.8877 | 73.7631 | 80.0852 | 86.8891 | 94.2127 | 102.097 | 110.5862 | 119.728 | 129.5742 | 137.2903 | 142.9983 | 147.4604 | 149.9043 | 149.2182 | 143.8073 | 131.3892 | 108.7017 | 71.0876 | 11.9004 | -78.3425 | -213.1693 | -411.8813 |  | 4.0207 | 4.2951 | 4.59 | 4.9069 | 5.2475 | 5.6137 | 6.0075 | 6.431 | 6.8865 | 7.3765 | 7.9038 | 8.4713 | 9.0822 | 9.7398 | 10.4478 | 11.2103 | 12.0316 | 12.9163 | 13.8693 | 14.8963 | 16.003 | 17.1958 | 18.4815 | 19.8676 | 21.3621 | 22.9737 | 24.7117 | 26.5862 | 28.6083 | 30.7897 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 1.953 | 2.2274 | 2.5223 | 2.8392 | 3.1798 | 3.546 | 3.9398 | 4.3633 | 4.8188 | 5.3088 | 5.8361 | 6.4036 | 7.0145 | 7.6721 | 8.3801 | 9.1426 | 9.9639 | 10.4413 | 10.5887 | 10.5096 | 10.0913 | 9.1726 | 7.5242 | 4.8193 | 0.59296 | -5.8171 | -15.3537 | -29.3598 | -49.7489 | -79.2486 |  | 1478.5484 | 1579.4787 | 1687.9213 | 1804.4587 | 1929.7198 | 2064.3834 | 2209.1825 | 2364.9085 | 2532.4159 | 2712.6277 | 2906.5405 | 3115.231 | 3339.8619 | 3581.6896 | 3842.0709 | 4122.472 | 4424.4771 | 4749.7979 | 5100.2839 | 5477.934 | 5884.9083 | 6323.5417 | 6796.3574 | 7306.0833 | 7855.6677 | 8448.2982 | 9087.4204 | 9776.7599 | 10520.3445 | 11322.5293 |  | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.46825 | 0.56046 | 0.74292 | 0.99339 | 1.3388 | 1.8169 | 2.4814 | 3.4078 | 4.7033 | 6.5199 | 9.0731 | 12.6694 | 17.7445 | 24.919 |  | 1478.0802 | 1579.0105 | 1687.453 | 1803.9905 | 1929.2516 | 2063.9152 | 2208.7143 | 2364.4402 | 2531.9476 | 2712.1594 | 2906.0723 | 3114.7627 | 3339.3937 | 3581.2213 | 3841.6026 | 4122.0038 | 4424.0089 | 4749.2374 | 5099.541 | 5476.9406 | 5883.5696 | 6321.7248 | 6793.8761 | 7302.6755 | 7850.9644 | 8441.7783 | 9078.3473 | 9764.0905 | 10502.5999 | 11297.6103 |  | 2678.9773 | 2864.022 | 3062.8396 | 3276.4983 | 3506.1508 | 3753.0419 | 4018.5152 | 4304.0217 | 4611.1283 | 4941.5269 | 5297.045 | 5679.6562 | 6091.4926 | 6534.8571 | 7012.2378 | 7526.3228 | 8080.0162 | 8670.1976 | 9300.3917 | 9975.7727 | 10698.4761 | 11470.2098 | 12291.9689 | 13163.619 | 14083.2944 | 15046.5283 | 16045.0028 | 17064.7513 | 18083.58 | 19067.3702
| FALSE | 530 | 22013378 | BC | Blank | 11 | TRANS NO.1 | METER (DIGITAL MULTI FN.) | I | Schneider | ION_6200 | ION 6200 | ION 6000s | Digital |  | 0 | 1 |  | 1.4709 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 4.8786 | 0.0081995 | 0 | 0.0081995 | 43.0474 | 0 | 43.0474 | 23.2752 | 3.2806 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 69.6033 | 43.8691 | 25.7341 |  | 0.11989 |  | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 | 3286.2344 | 4635.3288 | 6550.2041 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 | 2032.4311 | 2866.803 | 4051.0922 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 116.6469 | 170.327 | 245.3941 | 350.6506 | 493.2483 | 691.056 | 970.6149 | 1366.3118 | 1927.1535 | 2723.0244 | 3853.6336 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 116.6469 | 170.327 | 245.3941 | 350.6506 | 493.2483 | 691.056 | 970.6149 | 1366.3118 | 1927.1535 | 2723.0244 | 3853.6336 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 132.6818 | 189.5929 | 266.6938 | 373.6462 | 524.8006 | 738.7495 | 1041.9903 | 1472.3087 | 2083.6164 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.7014 | 26.7229 | 37.5902 | 52.665 | 73.9701 | 104.126 | 146.8675 | 207.5204 | 293.6836 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6395 | 25.7341 | 49.1999 | 81.5562 | 126.354 | 188.6062 | 275.4014 | 396.7773 | 566.9664 | 797.5323 | 1117.3672 | 1569.3856 | 2209.1873 | 3116.0112 | 4402.8535 | 6230.9336 | 7553.6874 | 7383.4983 | 7144.2929 | 6807.3633 | 6331.8792 | 5659.7211
| FALSE | 531 | 22013379 | BC | Blank | 11 | TRANS NO.2 | METER (DIGITAL MULTI FN.) | I | Schneider | ION_6200 | ION 6200 | ION 6000s | Digital |  | 0 | 1 |  | 1.4709 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 4.8786 | 0.0081995 | 0 | 0.0081995 | 43.0474 | 0 | 43.0474 | 23.2752 | 3.2806 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 69.6033 | 43.8691 | 25.7341 |  | 0.11989 |  | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 | 3286.2344 | 4635.3288 | 6550.2041 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 | 2032.4311 | 2866.803 | 4051.0922 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 116.6469 | 170.327 | 245.3941 | 350.6506 | 493.2483 | 691.056 | 970.6149 | 1366.3118 | 1927.1535 | 2723.0244 | 3853.6336 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 116.6469 | 170.327 | 245.3941 | 350.6506 | 493.2483 | 691.056 | 970.6149 | 1366.3118 | 1927.1535 | 2723.0244 | 3853.6336 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 132.6818 | 189.5929 | 266.6938 | 373.6462 | 524.8006 | 738.7495 | 1041.9903 | 1472.3087 | 2083.6164 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.7014 | 26.7229 | 37.5902 | 52.665 | 73.9701 | 104.126 | 146.8675 | 207.5204 | 293.6836 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6395 | 25.7341 | 49.1999 | 81.5562 | 126.354 | 188.6062 | 275.4014 | 396.7773 | 566.9664 | 797.5323 | 1117.3672 | 1569.3856 | 2209.1873 | 3116.0112 | 4402.8535 | 6230.9336 | 7553.6874 | 7383.4983 | 7144.2929 | 6807.3633 | 6331.8792 | 5659.7211
| FALSE | 532 | 22013380 | BC | Blank | 11 | TRANS NO.3 | METER (DIGITAL MULTI FN.) | I | Schneider | ION_6200 | ION 6200 | ION 6000s | Digital |  | 0 | 1 |  | 1.4709 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 4.8786 | 0.0081995 | 0 | 0.0081995 | 43.0474 | 0 | 43.0474 | 23.2752 | 3.2806 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 69.6033 | 43.8691 | 25.7341 |  | 0.11989 |  | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 | 3286.2344 | 4635.3288 | 6550.2041 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 | 2032.4311 | 2866.803 | 4051.0922 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 116.6469 | 170.327 | 245.3941 | 350.6506 | 493.2483 | 691.056 | 970.6149 | 1366.3118 | 1927.1535 | 2723.0244 | 3853.6336 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 116.6469 | 170.327 | 245.3941 | 350.6506 | 493.2483 | 691.056 | 970.6149 | 1366.3118 | 1927.1535 | 2723.0244 | 3853.6336 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 132.6818 | 189.5929 | 266.6938 | 373.6462 | 524.8006 | 738.7495 | 1041.9903 | 1472.3087 | 2083.6164 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.7014 | 26.7229 | 37.5902 | 52.665 | 73.9701 | 104.126 | 146.8675 | 207.5204 | 293.6836 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6395 | 25.7341 | 49.1999 | 81.5562 | 126.354 | 188.6062 | 275.4014 | 396.7773 | 566.9664 | 797.5323 | 1117.3672 | 1569.3856 | 2209.1873 | 3116.0112 | 4402.8535 | 6230.9336 | 7553.6874 | 7383.4983 | 7144.2929 | 6807.3633 | 6331.8792 | 5659.7211
| FALSE | 533 | 22013340 | BC | Blank | 66 | BUS NO.2 | LOW IMP BUS PROT | Y | Schweitzer | SEL_351A | SEL 351 | SEL 300s | Digital |  | 0.0034106 | 1 |  | 1.7651 | 0.0051679 | 2.4145e-08 | 0.0051679 | 27.1317 | 0.0028974 | 27.1346 | 14.6699 | 2.0677 | 0.013536 |  | 7.1689 | 0.021401 | 9.9986e-08 | 0.021401 | 112.3543 | 0.011998 | 112.3663 | 60.7492 | 8.5625 | 0.056052 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 27.1317 | 0.0028974 | 27.1346 | 14.6699 | 2.0677 | 0.013536 |  | 43.8857 | 181.734 | 43.8857 | 137.8483 |  | 0.14015 |  | 2.0307 | 2.3362 | 2.6877 | 3.0921 | 3.5573 | 4.0924 | 4.7082 | 5.4165 | 6.2314 | 7.1689 | 8.2475 | 9.4883 | 10.9158 | 12.5581 | 14.4475 | 16.6211 | 19.1217 | 21.9985 | 25.3082 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054426 | 0.0075349 | 0.01056 | 0.014961 | 0.021401 | 0.030869 | 0.044852 | 0.065583 | 0.096424 | 0.14244 | 0.21128 | 0.3145 | 0.46958 | 0.70298 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.5428e-08 | 3.5203e-08 | 4.9337e-08 | 6.99e-08 | 9.9986e-08 | 1.4422e-07 | 2.0955e-07 | 3.0641e-07 | 4.505e-07 | 6.6549e-07 | 9.8712e-07 | 1.4694e-06 | 2.1939e-06 | 3.2844e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 46.2178 | 63.9857 | 89.675 | 127.0507 | 181.734 | 262.1382 | 380.8825 | 556.93 | 818.8248 | 1209.5948 | 1794.1846 | 2670.7285 | 3987.6574 | 5969.67 | 7997.3558 | 7997.3558 | 7997.3558 | 7997.3558 | 7997.3558 | 7997.3558 | 7997.3558 | 7997.3558 | 7997.3558 | 7997.3558 | 7997.3558 |  | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 43.8857 | 52.5285 | 69.6296 | 93.1042 | 125.4728 | 170.2875 | 232.5633 | 319.3912 | 440.813 | 611.0664 | 850.3623 | 1187.4192 | 1663.083 | 2335.4952 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 28.5734 | 39.5582 | 55.4402 | 78.5472 | 112.3543 | 162.0629 | 235.4748 | 344.3134 | 506.2259 | 747.8134 | 1109.2271 | 1651.137 | 2465.3081 | 3690.657 | 4944.2427 | 4944.2427 | 4944.2427 | 4944.2427 | 4944.2427 | 4944.2427 | 4944.2427 | 4944.2427 | 4944.2427 | 4944.2427 | 4944.2427 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2777 | 143.7787 | 197.4587 | 272.5259 | 377.7825 | 525.7234 | 734.1037 | 1028.1756 | 1443.8841 |  | 0 | 0 | 0 | 0 | 0 | 1.4418 | 12.4265 | 28.3085 | 51.4155 | 85.2226 | 134.9313 | 208.3431 | 317.1818 | 479.0942 | 720.6818 | 1082.0955 | 1624.0053 | 2432.8332 | 3647.6096 | 4886.6824 | 4866.671 | 4838.965 | 4800.464 | 4746.784 | 4671.7168 | 4566.4602 | 4418.5192 | 4210.139 | 3916.0671 | 3500.3586 |  | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.0030513 | 0.0042244 | 0.0059204 | 0.008388 | 0.011998 | 0.017307 | 0.025146 | 0.036769 | 0.05406 | 0.079859 | 0.11845 | 0.17632 | 0.26327 | 0.39412 | 0.52799 | 0.52799 | 0.52799 | 0.52799 | 0.52799 | 0.52799 | 0.52799 | 0.52799 | 0.52799 | 0.52799 | 0.52799 |  | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.0028974 | 0.003468 | 0.004597 | 0.0061468 | 0.0082839 | 0.011243 | 0.015354 | 0.021087 | 0.029103 | 0.040343 | 0.056142 | 0.078395 | 0.1098 | 0.15419 |  | 0 | 0 | 0 | 0 | 0 | 0.00015397 | 0.001327 | 0.0030231 | 0.0054906 | 0.0091009 | 0.014409 | 0.022249 | 0.033872 | 0.051162 | 0.076961 | 0.11556 | 0.17343 | 0.2598 | 0.38953 | 0.52185 | 0.51971 | 0.51675 | 0.51264 | 0.50691 | 0.49889 | 0.48765 | 0.47185 | 0.4496 | 0.4182 | 0.3738 |  | 0 | 0 | 0 | 0 | 0 | 1.4419 | 12.4278 | 28.3116 | 51.421 | 85.2317 | 134.9457 | 208.3653 | 317.2156 | 479.1453 | 720.7587 | 1082.211 | 1624.1787 | 2433.093 | 3647.9991 | 4887.2043 | 4867.1908 | 4839.4818 | 4800.9767 | 4747.2909 | 4672.2157 | 4566.9479 | 4418.9911 | 4210.5886 | 3916.4853 | 3500.7324 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 15.4495 | 21.3889 | 29.9762 | 42.4699 | 60.7492 | 87.6264 | 127.3197 | 186.1681 | 273.7131 | 404.3379 | 599.752 | 892.7591 | 1332.9762 | 1995.5145 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 0 | 0 | 0 | 0 | 0 | 0.77956 | 6.7189 | 15.3062 | 27.8 | 46.0793 | 72.9565 | 112.6498 | 171.4981 | 259.0431 | 389.668 | 585.0821 | 878.0892 | 1315.4173 | 1972.239 | 2642.1978 | 2631.3777 | 2616.3973 | 2595.58 | 2566.5555 | 2525.9672 | 2469.0557 | 2389.0649 | 2276.395 | 2117.3923 | 1892.6214 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1776 | 3.0147 | 4.2251 | 5.986 | 8.5625 | 12.3507 | 17.9454 | 26.24 | 38.5792 | 56.9905 | 84.5336 | 125.8323 | 187.8799 | 281.2631 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0.10988 | 0.94702 | 2.1574 | 3.9183 | 6.4948 | 10.283 | 15.8777 | 24.1723 | 36.5115 | 54.9228 | 82.466 | 123.7646 | 185.405 | 277.9825 | 372.4116 | 370.8866 | 368.7751 | 365.8409 | 361.75 | 356.0292 | 348.0076 | 336.7331 | 320.8526 | 298.4415 | 266.7606 |  | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.014255 | 0.019735 | 0.027659 | 0.039186 | 0.056052 | 0.080851 | 0.11748 | 0.17177 | 0.25255 | 0.37308 | 0.55338 | 0.82373 | 1.2299 | 1.8412 | 2.4666 | 2.4666 | 2.4666 | 2.4666 | 2.4666 | 2.4666 | 2.4666 | 2.4666 | 2.4666 | 2.4666 | 2.4666 |  | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.013536 | 0.016201 | 0.021476 | 0.028716 | 0.0387 | 0.052522 | 0.07173 | 0.09851 | 0.13596 | 0.18847 | 0.26228 | 0.36624 | 0.51295 | 0.72034 |  | 0 | 0 | 0 | 0 | 0 | 0.00071929 | 0.0061995 | 0.014123 | 0.025651 | 0.042517 | 0.067316 | 0.10394 | 0.15824 | 0.23902 | 0.35954 | 0.53985 | 0.8102 | 1.2137 | 1.8198 | 2.4379 | 2.4279 | 2.4141 | 2.3949 | 2.3681 | 2.3307 | 2.2782 | 2.2044 | 2.1004 | 1.9537 | 1.7463 |  | 0 | 0 | 0 | 0 | 0 | 2.3321 | 20.1 | 45.7893 | 83.165 | 137.8483 | 218.2525 | 336.9967 | 513.0443 | 774.939 | 1165.709 | 1750.2989 | 2626.8428 | 3935.129 | 5900.0404 | 7904.2516 | 7871.883 | 7827.0682 | 7764.7925 | 7677.9646 | 7556.5428 | 7386.2893 | 7146.9935 | 6809.9366 | 6334.2727 | 5661.8606
| FALSE | 534 | 22013342 | BC | Blank | 66 | CB A | CB MGMT & CB FAIL | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0 | 1 |  | 1.7651 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 7.1689 | 0.021401 | 0 | 0.021401 | 112.3542 | 0 | 112.3542 | 60.7487 | 8.5625 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 181.6653 | 43.8691 | 137.7962 |  | 0.14015 |  | 2.0307 | 2.3362 | 2.6877 | 3.0921 | 3.5573 | 4.0924 | 4.7082 | 5.4165 | 6.2314 | 7.1689 | 8.2475 | 9.4883 | 10.9158 | 12.5581 | 14.4475 | 16.6211 | 19.1217 | 21.9985 | 25.3082 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054426 | 0.0075349 | 0.01056 | 0.014961 | 0.021401 | 0.030869 | 0.044852 | 0.065583 | 0.096424 | 0.14244 | 0.21128 | 0.3145 | 0.46958 | 0.70298 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 46.2003 | 63.9615 | 89.6411 | 127.0027 | 181.6653 | 262.0391 | 380.7385 | 556.7195 | 818.5153 | 1209.1377 | 1793.5066 | 2669.7193 | 3986.1506 | 5967.4142 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 28.5734 | 39.5582 | 55.4402 | 78.5471 | 112.3542 | 162.0629 | 235.4746 | 344.3133 | 506.2256 | 747.8131 | 1109.2266 | 1651.1362 | 2465.307 | 3690.6553 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 1.4418 | 12.4265 | 28.3085 | 51.4155 | 85.2225 | 134.9312 | 208.343 | 317.1816 | 479.094 | 720.6814 | 1082.095 | 1624.0045 | 2432.8321 | 3647.6079 | 4886.6802 | 4866.6688 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1.4418 | 12.4265 | 28.3085 | 51.4155 | 85.2225 | 134.9312 | 208.343 | 317.1816 | 479.094 | 720.6814 | 1082.095 | 1624.0045 | 2432.8321 | 3647.6079 | 4886.6802 | 4866.6688 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 15.4493 | 21.3887 | 29.9759 | 42.4695 | 60.7487 | 87.6256 | 127.3185 | 186.1663 | 273.7105 | 404.3341 | 599.7464 | 892.7508 | 1332.9638 | 1995.4958 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0.77955 | 6.7189 | 15.3061 | 27.7998 | 46.0789 | 72.9558 | 112.6487 | 171.4965 | 259.0407 | 389.6643 | 585.0766 | 878.081 | 1315.405 | 1972.2206 | 2642.1731 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1776 | 3.0147 | 4.2251 | 5.986 | 8.5625 | 12.3507 | 17.9454 | 26.24 | 38.5792 | 56.9905 | 84.5336 | 125.8323 | 187.8799 | 281.2631 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0.10988 | 0.94702 | 2.1574 | 3.9183 | 6.4948 | 10.283 | 15.8777 | 24.1723 | 36.5115 | 54.9228 | 82.4659 | 123.7646 | 185.405 | 277.9825 | 372.4116 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2.3312 | 20.0924 | 45.772 | 83.1336 | 137.7962 | 218.17 | 336.8694 | 512.8504 | 774.6462 | 1165.2686 | 1749.6375 | 2625.8502 | 3933.642 | 5897.8109 | 7901.2648 | 7868.9084 | 7824.1106 | 7761.8584 | 7675.0633 | 7553.6874 | 7383.4983 | 7144.2929 | 6807.3633 | 6331.8792 | 5659.7211
| FALSE | 535 | 22013344 | BC | Blank | 66 | CB B | CB MGMT & CB FAIL | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0 | 1 |  | 1.7651 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 7.1689 | 0.021401 | 0 | 0.021401 | 112.3542 | 0 | 112.3542 | 60.7487 | 8.5625 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 181.6653 | 43.8691 | 137.7962 |  | 0.14015 |  | 2.0307 | 2.3362 | 2.6877 | 3.0921 | 3.5573 | 4.0924 | 4.7082 | 5.4165 | 6.2314 | 7.1689 | 8.2475 | 9.4883 | 10.9158 | 12.5581 | 14.4475 | 16.6211 | 19.1217 | 21.9985 | 25.3082 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054426 | 0.0075349 | 0.01056 | 0.014961 | 0.021401 | 0.030869 | 0.044852 | 0.065583 | 0.096424 | 0.14244 | 0.21128 | 0.3145 | 0.46958 | 0.70298 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 46.2003 | 63.9615 | 89.6411 | 127.0027 | 181.6653 | 262.0391 | 380.7385 | 556.7195 | 818.5153 | 1209.1377 | 1793.5066 | 2669.7193 | 3986.1506 | 5967.4142 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 28.5734 | 39.5582 | 55.4402 | 78.5471 | 112.3542 | 162.0629 | 235.4746 | 344.3133 | 506.2256 | 747.8131 | 1109.2266 | 1651.1362 | 2465.307 | 3690.6553 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 1.4418 | 12.4265 | 28.3085 | 51.4155 | 85.2225 | 134.9312 | 208.343 | 317.1816 | 479.094 | 720.6814 | 1082.095 | 1624.0045 | 2432.8321 | 3647.6079 | 4886.6802 | 4866.6688 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1.4418 | 12.4265 | 28.3085 | 51.4155 | 85.2225 | 134.9312 | 208.343 | 317.1816 | 479.094 | 720.6814 | 1082.095 | 1624.0045 | 2432.8321 | 3647.6079 | 4886.6802 | 4866.6688 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 15.4493 | 21.3887 | 29.9759 | 42.4695 | 60.7487 | 87.6256 | 127.3185 | 186.1663 | 273.7105 | 404.3341 | 599.7464 | 892.7508 | 1332.9638 | 1995.4958 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0.77955 | 6.7189 | 15.3061 | 27.7998 | 46.0789 | 72.9558 | 112.6487 | 171.4965 | 259.0407 | 389.6643 | 585.0766 | 878.081 | 1315.405 | 1972.2206 | 2642.1731 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1776 | 3.0147 | 4.2251 | 5.986 | 8.5625 | 12.3507 | 17.9454 | 26.24 | 38.5792 | 56.9905 | 84.5336 | 125.8323 | 187.8799 | 281.2631 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0.10988 | 0.94702 | 2.1574 | 3.9183 | 6.4948 | 10.283 | 15.8777 | 24.1723 | 36.5115 | 54.9228 | 82.4659 | 123.7646 | 185.405 | 277.9825 | 372.4116 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2.3312 | 20.0924 | 45.772 | 83.1336 | 137.7962 | 218.17 | 336.8694 | 512.8504 | 774.6462 | 1165.2686 | 1749.6375 | 2625.8502 | 3933.642 | 5897.8109 | 7901.2648 | 7868.9084 | 7824.1106 | 7761.8584 | 7675.0633 | 7553.6874 | 7383.4983 | 7144.2929 | 6807.3633 | 6331.8792 | 5659.7211
| FALSE | 536 | 22016053 | BC | BC-AR | 66 | AR LINE | CURRENT DIFF & DEF | Y | GE | GE_L90 | GE L90 | GE RELAYS | Digital |  | 0.016937 | 1 |  | 1.0927 | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.014388 | 27.1461 | 14.6705 | 2.0677 | 0.0033609 |  | 5.2187 | 0.0096441 | 2.2376e-07 | 0.0096439 | 50.6318 | 0.026851 | 50.6586 | 27.3772 | 3.8586 | 0.006272 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.014388 | 27.1461 | 14.6705 | 2.0677 | 0.0033609 |  | 43.8876 | 81.9007 | 43.8876 | 38.0131 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.542e-07 | 2.2376e-07 | 3.2926e-07 | 4.9041e-07 | 7.3813e-07 | 1.121e-06 | 1.7156e-06 | 2.6427e-06 | 4.0934e-06 | 6.3704e-06 | 9.9538e-06 | 1.5606e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 56.4415 | 81.9007 | 120.5155 | 179.5027 | 270.1752 | 410.3155 | 627.9397 | 967.2772 | 1498.2756 | 2331.7221 | 3643.3178 | 5712.0253 | 7997.704 | 7997.704 | 7997.704 | 7997.704 | 7997.704 | 7997.704 | 7997.704 | 7997.704 | 7997.704 | 7997.704 |  | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 52.5307 | 69.6326 | 93.1082 | 125.4783 | 170.2949 | 232.5734 | 319.4051 | 440.8322 | 611.093 | 850.3993 | 1187.4709 | 1663.1554 | 2335.5969 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 34.8926 | 50.6318 | 74.5038 | 110.9702 | 167.0247 | 253.6607 | 388.1979 | 597.9794 | 926.2473 | 1441.4914 | 2252.3315 | 3531.2249 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7609 | 23.5 | 47.3721 | 83.8384 | 139.893 | 226.529 | 361.0662 | 570.8477 | 899.1156 | 1409.0164 | 2209.284 | 3473.6645 | 4866.6801 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.018504 | 0.026851 | 0.039511 | 0.058849 | 0.088576 | 0.13452 | 0.20587 | 0.31712 | 0.49121 | 0.76445 | 1.1945 | 1.8727 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 |  | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.017222 | 0.022829 | 0.030525 | 0.041138 | 0.055831 | 0.076249 | 0.10472 | 0.14453 | 0.20035 | 0.2788 | 0.38931 | 0.54526 | 0.76572 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0041157 | 0.012462 | 0.025122 | 0.044461 | 0.074188 | 0.12013 | 0.19148 | 0.30273 | 0.47682 | 0.74723 | 1.1716 | 1.8421 | 2.5809 | 2.5662 | 2.5458 | 2.5173 | 2.4775 | 2.4217 | 2.3432 | 2.2327 | 2.0768 | 1.8563 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.765 | 23.5125 | 47.3972 | 83.8829 | 139.9672 | 226.6491 | 361.2577 | 571.1504 | 899.5924 | 1409.7636 | 2210.4556 | 3475.5067 | 4869.261 | 4841.5402 | 4803.0187 | 4749.3101 | 4674.203 | 4568.8904 | 4420.8707 | 4212.3795 | 3918.1511 | 3502.2214 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 18.8669 | 27.3772 | 40.2851 | 60.003 | 90.3124 | 137.1575 | 209.9035 | 323.335 | 500.8336 | 779.4325 | 1217.864 | 1909.3778 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1964 | 12.7068 | 25.6147 | 45.3325 | 75.6419 | 122.4871 | 195.233 | 308.6645 | 486.1631 | 761.8729 | 1194.5877 | 1878.2542 | 2631.4752 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6591 | 3.8586 | 5.6779 | 8.457 | 12.7289 | 19.3313 | 29.5843 | 45.5716 | 70.5887 | 109.8552 | 171.6488 | 269.1125 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59145 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2636 | 27.5166 | 43.504 | 68.5211 | 107.3803 | 168.3682 | 264.7259 | 370.8867 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0043223 | 0.006272 | 0.0092291 | 0.013746 | 0.02069 | 0.031422 | 0.048088 | 0.074074 | 0.11474 | 0.17856 | 0.27901 | 0.43743 | 0.61247 | 0.61247 | 0.61247 | 0.61247 | 0.61247 | 0.61247 | 0.61247 | 0.61247 | 0.61247 | 0.61247 |  | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0040228 | 0.0053325 | 0.0071302 | 0.0096091 | 0.013041 | 0.017811 | 0.02446 | 0.033759 | 0.046798 | 0.065124 | 0.090937 | 0.12736 | 0.17886 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00096137 | 0.002911 | 0.0058682 | 0.010385 | 0.017329 | 0.028061 | 0.044727 | 0.070713 | 0.11138 | 0.17454 | 0.27367 | 0.4303 | 0.60286 | 0.59942 | 0.59466 | 0.58801 | 0.57871 | 0.56567 | 0.54734 | 0.52153 | 0.4851 | 0.43361 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5538 | 38.0131 | 76.6279 | 135.6151 | 226.2876 | 366.4279 | 584.0521 | 923.3896 | 1454.3879 | 2279.1914 | 3573.6852 | 5618.917 | 7872.2258 | 7827.4091 | 7765.1306 | 7678.2989 | 7556.8719 | 7386.611 | 7147.3047 | 6810.2331 | 6334.5486 | 5662.1072
| FALSE | 537 | 22013337 | BC | BC-TK/RTS | 66 | TK/RTS LINE | CURRENT DIFF & DEF | Y | GE | GE_L90 | GE L90 | GE RELAYS | Digital |  | 0.016937 | 1 |  | 1.7651 | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.014388 | 27.1461 | 14.6705 | 2.0677 | 0.0033609 |  | 7.1689 | 0.021401 | 4.9653e-07 | 0.0214 | 112.3545 | 0.059584 | 112.414 | 60.7515 | 8.5625 | 0.013918 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.014388 | 27.1461 | 14.6705 | 2.0677 | 0.0033609 |  | 43.8876 | 181.7419 | 43.8876 | 137.8543 |  | 0.14015 |  | 2.0307 | 2.3362 | 2.6877 | 3.0921 | 3.5573 | 4.0924 | 4.7082 | 5.4165 | 6.2314 | 7.1689 | 8.2475 | 9.4883 | 10.9158 | 12.5581 | 14.4475 | 16.6211 | 19.1217 | 21.9985 | 25.3082 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054426 | 0.0075349 | 0.01056 | 0.014961 | 0.021401 | 0.030869 | 0.044852 | 0.065583 | 0.096424 | 0.14244 | 0.21128 | 0.3145 | 0.46958 | 0.70298 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.2628e-07 | 1.7482e-07 | 2.4501e-07 | 3.4713e-07 | 4.9653e-07 | 7.1621e-07 | 1.0406e-06 | 1.5216e-06 | 2.2372e-06 | 3.3048e-06 | 4.902e-06 | 7.2969e-06 | 1.0895e-05 | 1.631e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 46.2198 | 63.9885 | 89.6789 | 127.0562 | 181.7419 | 262.1496 | 380.8991 | 556.9542 | 818.8604 | 1209.6474 | 1794.2627 | 2670.8448 | 3987.8311 | 5969.9299 | 7997.704 | 7997.704 | 7997.704 | 7997.704 | 7997.704 | 7997.704 | 7997.704 | 7997.704 | 7997.704 | 7997.704 | 7997.704 |  | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 43.8876 | 52.5307 | 69.6326 | 93.1082 | 125.4783 | 170.2949 | 232.5734 | 319.4051 | 440.8322 | 611.093 | 850.3993 | 1187.4709 | 1663.1554 | 2335.5969 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 28.5735 | 39.5583 | 55.4403 | 78.5473 | 112.3545 | 162.0632 | 235.4752 | 344.3141 | 506.2268 | 747.8148 | 1109.2292 | 1651.14 | 2465.3127 | 3690.6638 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 0 | 0 | 0 | 0 | 0 | 1.4418 | 12.4265 | 28.3086 | 51.4156 | 85.2227 | 134.9315 | 208.3435 | 317.1823 | 479.0951 | 720.6831 | 1082.0975 | 1624.0083 | 2432.8377 | 3647.6163 | 4886.6915 | 4866.6801 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.015153 | 0.020978 | 0.029401 | 0.041655 | 0.059584 | 0.085945 | 0.12488 | 0.1826 | 0.26846 | 0.39658 | 0.58824 | 0.87563 | 1.3074 | 1.9572 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 |  | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.017222 | 0.022829 | 0.030525 | 0.041138 | 0.055831 | 0.076249 | 0.10472 | 0.14453 | 0.20035 | 0.2788 | 0.38931 | 0.54526 | 0.76572 |  | 0 | 0 | 0 | 0 | 0 | 0.0007646 | 0.00659 | 0.015013 | 0.027267 | 0.045195 | 0.071557 | 0.11049 | 0.16821 | 0.25407 | 0.38219 | 0.57386 | 0.86124 | 1.2902 | 1.9344 | 2.5915 | 2.5809 | 2.5662 | 2.5458 | 2.5173 | 2.4775 | 2.4217 | 2.3432 | 2.2327 | 2.0768 | 1.8563 |  | 0 | 0 | 0 | 0 | 0 | 1.4425 | 12.4331 | 28.3236 | 51.4428 | 85.2679 | 135.0031 | 208.4539 | 317.3506 | 479.3491 | 721.0653 | 1082.6713 | 1624.8695 | 2434.1279 | 3649.5507 | 4889.283 | 4869.261 | 4841.5402 | 4803.0187 | 4749.3101 | 4674.203 | 4568.8904 | 4420.8707 | 4212.3795 | 3918.1511 | 3502.2214 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 15.4501 | 21.3896 | 29.9773 | 42.4715 | 60.7515 | 87.6296 | 127.3244 | 186.175 | 273.7232 | 404.3529 | 599.7742 | 892.7922 | 1333.0256 | 1995.5884 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 0 | 0 | 0 | 0 | 0 | 0.77959 | 6.7192 | 15.3068 | 27.801 | 46.081 | 72.9592 | 112.6539 | 171.5045 | 259.0527 | 389.6824 | 585.1037 | 878.1218 | 1315.466 | 1972.3121 | 2642.2957 | 2631.4752 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1776 | 3.0147 | 4.2251 | 5.986 | 8.5625 | 12.3507 | 17.9454 | 26.24 | 38.5792 | 56.9905 | 84.5337 | 125.8324 | 187.88 | 281.2632 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0.10988 | 0.94702 | 2.1574 | 3.9183 | 6.4948 | 10.283 | 15.8777 | 24.1723 | 36.5115 | 54.9228 | 82.466 | 123.7647 | 185.4051 | 277.9826 | 372.4118 | 370.8867 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0035395 | 0.0049003 | 0.0068676 | 0.00973 | 0.013918 | 0.020075 | 0.029169 | 0.042652 | 0.062708 | 0.092635 | 0.1374 | 0.20453 | 0.30539 | 0.45718 | 0.61247 | 0.61247 | 0.61247 | 0.61247 | 0.61247 | 0.61247 | 0.61247 | 0.61247 | 0.61247 | 0.61247 | 0.61247 |  | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0033609 | 0.0040228 | 0.0053325 | 0.0071302 | 0.0096091 | 0.013041 | 0.017811 | 0.02446 | 0.033759 | 0.046798 | 0.065124 | 0.090937 | 0.12736 | 0.17886 |  | 0 | 0 | 0 | 0 | 0 | 0.0001786 | 0.0015393 | 0.0035067 | 0.0063691 | 0.010557 | 0.016715 | 0.025808 | 0.039291 | 0.059348 | 0.089274 | 0.13404 | 0.20117 | 0.30137 | 0.45185 | 0.60534 | 0.60286 | 0.59942 | 0.59466 | 0.58801 | 0.57871 | 0.56567 | 0.54734 | 0.52153 | 0.4851 | 0.43361 |  | 0 | 0 | 0 | 0 | 0 | 2.3322 | 20.1009 | 45.7913 | 83.1686 | 137.8543 | 218.262 | 337.0114 | 513.0666 | 774.9728 | 1165.7598 | 1750.3751 | 2626.9572 | 3935.3003 | 5900.2973 | 7904.5958 | 7872.2258 | 7827.4091 | 7765.1306 | 7678.2989 | 7556.8719 | 7386.611 | 7147.3047 | 6810.2331 | 6334.5486 | 5662.1072
| FALSE | 538 | 22013332 | BC | BC-TK/RTS | 66 | TK/RTS LINE | CURRENT DIFF & DEF | X | Schweitzer | SEL_311L | SEL 311L | SEL 300s | Digital |  | 0.15703 | 1 |  | 1.7651 | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.1334 | 27.2656 | 14.6761 | 2.0677 | 0.03116 |  | 7.1689 | 0.021401 | 4.6035e-06 | 0.021396 | 112.3566 | 0.55241 | 112.909 | 60.7748 | 8.5625 | 0.12904 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.1334 | 27.2656 | 14.6761 | 2.0677 | 0.03116 |  | 44.0406 | 182.3754 | 44.0406 | 138.3348 |  | 0.14015 |  | 2.0307 | 2.3362 | 2.6877 | 3.0921 | 3.5573 | 4.0924 | 4.7082 | 5.4165 | 6.2314 | 7.1689 | 8.2475 | 9.4883 | 10.9158 | 12.5581 | 14.4475 | 16.6211 | 19.1217 | 21.9985 | 25.3082 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054426 | 0.0075349 | 0.01056 | 0.014961 | 0.021401 | 0.030869 | 0.044852 | 0.065583 | 0.096424 | 0.14244 | 0.21128 | 0.3145 | 0.46958 | 0.70298 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1707e-06 | 1.6208e-06 | 2.2715e-06 | 3.2183e-06 | 4.6035e-06 | 6.6402e-06 | 9.648e-06 | 1.4107e-05 | 2.0741e-05 | 3.064e-05 | 4.5448e-05 | 6.7651e-05 | 0.00010101 | 0.00015122 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 46.3809 | 64.2115 | 89.9915 | 127.4991 | 182.3754 | 263.0633 | 382.2267 | 558.8955 | 821.7146 | 1213.8637 | 1800.5166 | 2680.154 | 4001.7307 | 5990.7381 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 |  | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 52.7138 | 69.8753 | 93.4328 | 125.9156 | 170.8885 | 233.384 | 320.5184 | 442.3687 | 613.223 | 853.3634 | 1191.6098 | 1668.9524 | 2343.7376 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 28.574 | 39.559 | 55.4414 | 78.5488 | 112.3566 | 162.0663 | 235.4797 | 344.3207 | 506.2365 | 747.8292 | 1109.2505 | 1651.1717 | 2465.36 | 3690.7347 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 0 | 0 | 0 | 0 | 0 | 1.4418 | 12.4268 | 28.3091 | 51.4166 | 85.2244 | 134.9341 | 208.3475 | 317.1884 | 479.1043 | 720.6969 | 1082.1182 | 1624.0395 | 2432.8844 | 3647.6863 | 4886.7853 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.14049 | 0.1945 | 0.27258 | 0.38619 | 0.55241 | 0.79682 | 1.1578 | 1.6929 | 2.489 | 3.6768 | 5.4538 | 8.1182 | 12.1212 | 18.1459 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 |  | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.15967 | 0.21165 | 0.28301 | 0.3814 | 0.51762 | 0.70692 | 0.97085 | 1.3399 | 1.8575 | 2.5848 | 3.6094 | 5.0553 | 7.0992 |  | 0 | 0 | 0 | 0 | 0 | 0.0070888 | 0.061098 | 0.13919 | 0.2528 | 0.41902 | 0.66342 | 1.0244 | 1.5595 | 2.3556 | 3.5434 | 5.3204 | 7.9848 | 11.9616 | 17.9343 | 24.0265 | 23.9281 | 23.7918 | 23.6025 | 23.3386 | 22.9695 | 22.452 | 21.7246 | 20.7001 | 19.2542 | 17.2103 |  | 0 | 0 | 0 | 0 | 0 | 1.4489 | 12.4879 | 28.4483 | 51.6694 | 85.6434 | 135.5975 | 209.3718 | 318.7479 | 481.4598 | 724.2403 | 1087.4386 | 1632.0243 | 2444.8459 | 3665.6206 | 4910.8117 | 4890.7015 | 4862.8587 | 4824.1676 | 4770.2225 | 4694.7846 | 4589.0083 | 4440.3368 | 4230.9276 | 3935.4037 | 3517.6425 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 15.456 | 21.3979 | 29.9888 | 42.4878 | 60.7748 | 87.6633 | 127.3733 | 186.2464 | 273.8283 | 404.5081 | 600.0044 | 893.1349 | 1333.5372 | 1996.3543 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0 | 0 | 0 | 0 | 0.77989 | 6.7218 | 15.3127 | 27.8117 | 46.0987 | 72.9872 | 112.6972 | 171.5703 | 259.1522 | 389.832 | 585.3283 | 878.4588 | 1315.9709 | 1973.0691 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1776 | 3.0147 | 4.2251 | 5.9861 | 8.5625 | 12.3508 | 17.9455 | 26.2401 | 38.5794 | 56.9908 | 84.5341 | 125.833 | 187.8809 | 281.2646 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0 | 0 | 0 | 0 | 0.10988 | 0.94702 | 2.1574 | 3.9184 | 6.4948 | 10.2831 | 15.8778 | 24.1724 | 36.5117 | 54.9231 | 82.4664 | 123.7653 | 185.406 | 277.984 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.032816 | 0.045431 | 0.063672 | 0.090209 | 0.12904 | 0.18612 | 0.27044 | 0.39543 | 0.58139 | 0.85884 | 1.2739 | 1.8963 | 2.8313 | 4.2386 | 5.6783 | 5.6783 | 5.6783 | 5.6783 | 5.6783 | 5.6783 | 5.6783 | 5.6783 | 5.6783 | 5.6783 | 5.6783 |  | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.037297 | 0.049439 | 0.066106 | 0.089089 | 0.12091 | 0.16513 | 0.22678 | 0.31299 | 0.43387 | 0.60378 | 0.8431 | 1.1808 | 1.6583 |  | 0 | 0 | 0 | 0 | 0 | 0.0016558 | 0.014272 | 0.032512 | 0.059049 | 0.097876 | 0.15496 | 0.23928 | 0.36427 | 0.55023 | 0.82768 | 1.2428 | 1.8651 | 2.794 | 4.1892 | 5.6122 | 5.5892 | 5.5574 | 5.5132 | 5.4516 | 5.3653 | 5.2445 | 5.0745 | 4.8352 | 4.4975 | 4.0201 |  | 0 | 0 | 0 | 0 | 0 | 2.3403 | 20.1709 | 45.9509 | 83.4585 | 138.3348 | 219.0227 | 338.1861 | 514.8549 | 777.6739 | 1169.8231 | 1756.476 | 2636.1134 | 3949.0168 | 5920.8628 | 7932.1473 | 7899.6644 | 7854.6915 | 7792.196 | 7705.0617 | 7583.2114 | 7412.357 | 7172.2167 | 6833.9702 | 6356.6277 | 5681.8424
| FALSE | 539 | 22013334 | BC | BC-TK/RTS | 66 | TK/RTS LINE | NEUT DISP & AUTO RECL | X | Schweitzer | SEL_351A | SEL 351 | SEL 300s | Digital |  | 0.15703 | 1 |  | 1.7651 | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.1334 | 27.2656 | 14.6761 | 2.0677 | 0.03116 |  | 7.1689 | 0.021401 | 4.6035e-06 | 0.021396 | 112.3566 | 0.55241 | 112.909 | 60.7748 | 8.5625 | 0.12904 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.1334 | 27.2656 | 14.6761 | 2.0677 | 0.03116 |  | 44.0406 | 182.3754 | 44.0406 | 138.3348 |  | 0.14015 |  | 2.0307 | 2.3362 | 2.6877 | 3.0921 | 3.5573 | 4.0924 | 4.7082 | 5.4165 | 6.2314 | 7.1689 | 8.2475 | 9.4883 | 10.9158 | 12.5581 | 14.4475 | 16.6211 | 19.1217 | 21.9985 | 25.3082 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054426 | 0.0075349 | 0.01056 | 0.014961 | 0.021401 | 0.030869 | 0.044852 | 0.065583 | 0.096424 | 0.14244 | 0.21128 | 0.3145 | 0.46958 | 0.70298 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1707e-06 | 1.6208e-06 | 2.2715e-06 | 3.2183e-06 | 4.6035e-06 | 6.6402e-06 | 9.648e-06 | 1.4107e-05 | 2.0741e-05 | 3.064e-05 | 4.5448e-05 | 6.7651e-05 | 0.00010101 | 0.00015122 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 46.3809 | 64.2115 | 89.9915 | 127.4991 | 182.3754 | 263.0633 | 382.2267 | 558.8955 | 821.7146 | 1213.8637 | 1800.5166 | 2680.154 | 4001.7307 | 5990.7381 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 | 8025.5801 |  | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 44.0406 | 52.7138 | 69.8753 | 93.4328 | 125.9156 | 170.8885 | 233.384 | 320.5184 | 442.3687 | 613.223 | 853.3634 | 1191.6098 | 1668.9524 | 2343.7376 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 28.574 | 39.559 | 55.4414 | 78.5488 | 112.3566 | 162.0663 | 235.4797 | 344.3207 | 506.2365 | 747.8292 | 1109.2505 | 1651.1717 | 2465.36 | 3690.7347 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 0 | 0 | 0 | 0 | 0 | 1.4418 | 12.4268 | 28.3091 | 51.4166 | 85.2244 | 134.9341 | 208.3475 | 317.1884 | 479.1043 | 720.6969 | 1082.1182 | 1624.0395 | 2432.8844 | 3647.6863 | 4886.7853 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.14049 | 0.1945 | 0.27258 | 0.38619 | 0.55241 | 0.79682 | 1.1578 | 1.6929 | 2.489 | 3.6768 | 5.4538 | 8.1182 | 12.1212 | 18.1459 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 |  | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.15967 | 0.21165 | 0.28301 | 0.3814 | 0.51762 | 0.70692 | 0.97085 | 1.3399 | 1.8575 | 2.5848 | 3.6094 | 5.0553 | 7.0992 |  | 0 | 0 | 0 | 0 | 0 | 0.0070888 | 0.061098 | 0.13919 | 0.2528 | 0.41902 | 0.66342 | 1.0244 | 1.5595 | 2.3556 | 3.5434 | 5.3204 | 7.9848 | 11.9616 | 17.9343 | 24.0265 | 23.9281 | 23.7918 | 23.6025 | 23.3386 | 22.9695 | 22.452 | 21.7246 | 20.7001 | 19.2542 | 17.2103 |  | 0 | 0 | 0 | 0 | 0 | 1.4489 | 12.4879 | 28.4483 | 51.6694 | 85.6434 | 135.5975 | 209.3718 | 318.7479 | 481.4598 | 724.2403 | 1087.4386 | 1632.0243 | 2444.8459 | 3665.6206 | 4910.8117 | 4890.7015 | 4862.8587 | 4824.1676 | 4770.2225 | 4694.7846 | 4589.0083 | 4440.3368 | 4230.9276 | 3935.4037 | 3517.6425 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 15.456 | 21.3979 | 29.9888 | 42.4878 | 60.7748 | 87.6633 | 127.3733 | 186.2464 | 273.8283 | 404.5081 | 600.0044 | 893.1349 | 1333.5372 | 1996.3543 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0 | 0 | 0 | 0 | 0.77989 | 6.7218 | 15.3127 | 27.8117 | 46.0987 | 72.9872 | 112.6972 | 171.5703 | 259.1522 | 389.832 | 585.3283 | 878.4588 | 1315.9709 | 1973.0691 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1776 | 3.0147 | 4.2251 | 5.9861 | 8.5625 | 12.3508 | 17.9455 | 26.2401 | 38.5794 | 56.9908 | 84.5341 | 125.833 | 187.8809 | 281.2646 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0 | 0 | 0 | 0 | 0.10988 | 0.94702 | 2.1574 | 3.9184 | 6.4948 | 10.2831 | 15.8778 | 24.1724 | 36.5117 | 54.9231 | 82.4664 | 123.7653 | 185.406 | 277.984 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.032816 | 0.045431 | 0.063672 | 0.090209 | 0.12904 | 0.18612 | 0.27044 | 0.39543 | 0.58139 | 0.85884 | 1.2739 | 1.8963 | 2.8313 | 4.2386 | 5.6783 | 5.6783 | 5.6783 | 5.6783 | 5.6783 | 5.6783 | 5.6783 | 5.6783 | 5.6783 | 5.6783 | 5.6783 |  | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.03116 | 0.037297 | 0.049439 | 0.066106 | 0.089089 | 0.12091 | 0.16513 | 0.22678 | 0.31299 | 0.43387 | 0.60378 | 0.8431 | 1.1808 | 1.6583 |  | 0 | 0 | 0 | 0 | 0 | 0.0016558 | 0.014272 | 0.032512 | 0.059049 | 0.097876 | 0.15496 | 0.23928 | 0.36427 | 0.55023 | 0.82768 | 1.2428 | 1.8651 | 2.794 | 4.1892 | 5.6122 | 5.5892 | 5.5574 | 5.5132 | 5.4516 | 5.3653 | 5.2445 | 5.0745 | 4.8352 | 4.4975 | 4.0201 |  | 0 | 0 | 0 | 0 | 0 | 2.3403 | 20.1709 | 45.9509 | 83.4585 | 138.3348 | 219.0227 | 338.1861 | 514.8549 | 777.6739 | 1169.8231 | 1756.476 | 2636.1134 | 3949.0168 | 5920.8628 | 7932.1473 | 7899.6644 | 7854.6915 | 7792.196 | 7705.0617 | 7583.2114 | 7412.357 | 7172.2167 | 6833.9702 | 6356.6277 | 5681.8424
| TRUE | 540 | 22005311 | BC | Blank | 66 | TRANS NO.1 | DIFFERENTIAL | Blank | AEI | DT2_577 | DT2 577 | DT2 | Electromechanical |  | 0.066046 | 2190 |  | 5.5 | 0.0019187 | 0.00033459 | 0.0015842 | 20.4982 | 160.6041 | 181.1023 | 7.3461 | 0.77104 | 9.3787 |  | 7.1791 | 0.0037591 | 0.00065552 | 0.0031036 | 40.1591 | 314.6483 | 354.8074 | 14.3922 | 1.5106 | 18.3743 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.013106 |  | 198.5981 | 389.0845 | 71.2415 | 317.843 |  | 0.026643 |  | 5.6485 | 5.801 | 5.9577 | 6.1185 | 6.2837 | 6.4534 | 6.6277 | 6.8066 | 6.9904 | 7.1791 | 7.373 | 7.5721 | 7.7765 | 7.9865 | 8.2022 | 8.4236 | 8.6511 | 8.8847 | 9.1246 | 9.3709 | 9.624 | 9.8838 | 10.1507 | 10.4248 | 10.7063 | 10.9954 | 11.2923 | 11.5972 | 11.9103 | 12.2319 |  | 0.002049 | 0.0021888 | 0.0023391 | 0.0025006 | 0.0026742 | 0.0028608 | 0.0030615 | 0.0032773 | 0.0035094 | 0.0037591 | 0.0040278 | 0.004317 | 0.0046283 | 0.0049635 | 0.0053243 | 0.0057129 | 0.0061314 | 0.0065822 | 0.0070679 | 0.0075912 | 0.0081552 | 0.0087631 | 0.0094183 | 0.010125 | 0.010886 | 0.011708 | 0.012593 | 0.013548 | 0.014579 | 0.015691 |  | 0.0003573 | 0.00038169 | 0.00040789 | 0.00043605 | 0.00046632 | 0.00049887 | 0.00053386 | 0.00057149 | 0.00061197 | 0.00065552 | 0.00070238 | 0.00075281 | 0.00080709 | 0.00086553 | 0.00092845 | 0.00099621 | 0.0010692 | 0.0011478 | 0.0012325 | 0.0013238 | 0.0014221 | 0.0015281 | 0.0016424 | 0.0017655 | 0.0018984 | 0.0020416 | 0.002196 | 0.0023626 | 0.0025423 | 0.0027361 | 212.0749 | 226.5518 | 242.1062 | 258.8217 | 276.7885 | 296.1039 | 316.8731 | 339.2095 | 363.2359 | 389.0845 | 416.8983 | 446.8317 | 479.0515 | 513.738 | 551.0856 | 591.3048 | 634.6228 | 681.285 | 731.5568 | 785.7249 | 844.0991 | 907.0142 | 974.8323 | 1047.9446 | 1126.774 | 1211.7777 | 1303.4499 | 1402.325 | 1508.9807 | 1624.0417 |  | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 52.7996 | 69.989 | 93.5848 | 126.1205 | 171.1666 | 233.7639 | 321.04 | 443.0887 | 614.2211 | 854.7522 | 1193.5492 | 1671.6687 | 2347.5521 |  | 21.8891 | 23.3834 | 24.9888 | 26.7141 | 28.5685 | 30.5621 | 32.7058 | 35.0112 | 37.4911 | 40.1591 | 43.0298 | 46.1194 | 49.4449 | 53.0251 | 56.8799 | 61.0311 | 65.5021 | 70.3183 | 75.5071 | 81.098 | 87.123 | 93.6168 | 100.6166 | 108.1628 | 116.2991 | 125.0727 | 134.5346 | 144.7399 | 155.7483 | 167.6242 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | -5.2428 | -3.7485 | -2.1431 | -0.41783 | 1.4366 | 3.4302 | 5.5739 | 7.8793 | 10.3592 | 13.0271 | 15.8979 | 18.9875 | 22.313 | 25.8932 | 29.748 | 33.8992 | 38.3702 | 37.8431 | 32.4593 | 23.5372 | 9.5507 | -11.6618 | -43.1633 | -89.2976 | -156.2291 | -252.713 | -391.1934 | -589.3701 | -872.4362 | -1276.2723 |  | 171.5026 | 183.2099 | 195.7886 | 209.3063 | 223.8358 | 239.4559 | 256.2518 | 274.315 | 293.7449 | 314.6483 | 337.141 | 361.3479 | 387.4037 | 415.4542 | 445.6569 | 478.1817 | 513.2125 | 550.9477 | 591.602 | 635.4071 | 682.6136 | 733.4924 | 788.3362 | 847.4613 | 911.2098 | 979.9513 | 1054.0856 | 1134.0448 | 1220.2961 | 1313.3446 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 171.2782 | 182.9855 | 195.5642 | 209.0818 | 223.6113 | 239.2315 | 256.0273 | 274.0906 | 293.5204 | 314.4239 | 336.9166 | 361.1234 | 387.1793 | 415.2298 | 445.4325 | 477.9573 | 512.988 | 550.6791 | 591.2459 | 634.9309 | 681.972 | 732.6216 | 787.1469 | 845.8279 | 908.9554 | 976.8263 | 1049.7368 | 1127.9723 | 1211.7911 | 1301.4009 |  | 166.0354 | 179.237 | 193.4211 | 208.664 | 225.0479 | 242.6617 | 261.6012 | 281.9699 | 303.8796 | 327.451 | 352.8145 | 380.1109 | 409.4923 | 441.123 | 475.1804 | 511.8564 | 551.3582 | 588.5222 | 623.7051 | 658.4682 | 691.5227 | 720.9598 | 743.9835 | 756.5303 | 752.7263 | 724.1133 | 658.5434 | 538.6022 | 339.3549 | 25.1286 |  | 7.8446 | 8.3801 | 8.9555 | 9.5738 | 10.2384 | 10.9529 | 11.7211 | 12.5473 | 13.4361 | 14.3922 | 15.4211 | 16.5283 | 17.7201 | 19.0032 | 20.3846 | 21.8723 | 23.4747 | 25.2007 | 27.0603 | 29.0639 | 31.2232 | 33.5504 | 36.059 | 38.7634 | 41.6793 | 44.8236 | 48.2146 | 51.872 | 55.8171 | 60.0732 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | -6.8278 | -6.2923 | -5.7169 | -5.0986 | -4.434 | -3.7196 | -2.9513 | -2.1251 | -1.2364 | -0.28022 | 0.74861 | 1.8558 | 3.0477 | 4.3307 | 5.7122 | 7.1999 | 8.8022 | 7.6387 | 3.7808 | -2.0639 | -10.7265 | -23.3823 | -41.6945 | -68.0195 | -105.6989 | -159.476 | -236.0895 | -345.1213 | -500.2062 | -720.7596 |  | 0.82336 | 0.87956 | 0.93995 | 1.0048 | 1.0746 | 1.1496 | 1.2302 | 1.3169 | 1.4102 | 1.5106 | 1.6186 | 1.7348 | 1.8599 | 1.9945 | 2.1395 | 2.2957 | 2.4639 | 2.645 | 2.8402 | 3.0505 | 3.2771 | 3.5214 | 3.7847 | 4.0685 | 4.3746 | 4.7046 | 5.0605 | 5.4444 | 5.8585 | 6.3052 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | -1.2443 | -1.1881 | -1.1277 | -1.0628 | -0.99309 | -0.9181 | -0.83747 | -0.75075 | -0.65747 | -0.55712 | -0.44913 | -0.33292 | -0.20783 | -0.073163 | 0.071835 | 0.22798 | 0.39616 | 0.17011 | -0.44044 | -1.3362 | -2.6346 | -4.5018 | -7.1726 | -10.9797 | -16.3945 | -24.0861 | -35.0047 | -50.5014 | -72.4985 | -103.7327 |  | 10.0151 | 10.6988 | 11.4333 | 12.2227 | 13.0712 | 13.9833 | 14.9641 | 16.019 | 17.1536 | 18.3743 | 19.6878 | 21.1014 | 22.6229 | 24.261 | 26.0247 | 27.924 | 29.9697 | 32.1733 | 34.5473 | 37.1054 | 39.8621 | 42.8332 | 46.0359 | 49.4886 | 53.2112 | 57.2255 | 61.5547 | 66.224 | 71.2607 | 76.6944 |  | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.015687 | 0.020794 | 0.027805 | 0.037471 | 0.050854 | 0.069452 | 0.095383 | 0.13164 | 0.18249 | 0.25395 | 0.35461 | 0.49666 | 0.69747 |  | 10.002 | 10.6857 | 11.4202 | 12.2096 | 13.0581 | 13.9702 | 14.951 | 16.0059 | 17.1405 | 18.3612 | 19.6747 | 21.0883 | 22.6098 | 24.2479 | 26.0116 | 27.9109 | 29.9566 | 32.1576 | 34.5265 | 37.0776 | 39.8246 | 42.7824 | 45.9664 | 49.3932 | 53.0796 | 57.043 | 61.3007 | 65.8694 | 70.7641 | 75.9969 |  | 167.9653 | 182.4422 | 197.9966 | 214.7121 | 232.6789 | 251.9943 | 272.7635 | 295.1 | 319.1263 | 344.9749 | 372.7887 | 402.7221 | 434.9419 | 469.6284 | 506.976 | 547.1953 | 590.5132 | 628.4886 | 661.5721 | 692.1458 | 717.9862 | 735.8581 | 741.0828 | 726.9242 | 683.7125 | 597.5942 | 448.75 | 208.8488 | -162.5857 | -723.3668
| FALSE | 541 | 22015694 | BC | Blank | 66 | TRANS NO.1 | HT OVERCURRENT | Y | Schweitzer | SEL_351A | SEL 351 | SEL 300s | Digital |  | 0.0068096 | 1 |  | 1.0927 | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0057849 | 27.1375 | 14.6701 | 2.0677 | 0.0013513 |  | 5.2187 | 0.0096441 | 8.9962e-08 | 0.009644 | 50.6317 | 0.010795 | 50.6425 | 27.3765 | 3.8586 | 0.0025217 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0057849 | 27.1375 | 14.6701 | 2.0677 | 0.0013513 |  | 43.8766 | 81.8801 | 43.8766 | 38.0035 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 6.1997e-08 | 8.9962e-08 | 1.3238e-07 | 1.9717e-07 | 2.9677e-07 | 4.507e-07 | 6.8975e-07 | 1.0625e-06 | 1.6457e-06 | 2.5612e-06 | 4.0019e-06 | 6.2742e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 56.4272 | 81.8801 | 120.4852 | 179.4575 | 270.1072 | 410.2121 | 627.7815 | 967.0335 | 1497.898 | 2331.1346 | 3642.3998 | 5710.586 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 |  | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 52.5175 | 69.6151 | 93.0848 | 125.4466 | 170.252 | 232.5148 | 319.3246 | 440.7211 | 610.9391 | 850.185 | 1187.1717 | 1662.7364 | 2335.0084 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 34.8926 | 50.6317 | 74.5037 | 110.97 | 167.0245 | 253.6603 | 388.1974 | 597.9786 | 926.246 | 1441.4894 | 2252.3284 | 3531.22 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7609 | 23.5 | 47.372 | 83.8383 | 139.8928 | 226.5287 | 361.0657 | 570.8469 | 899.1143 | 1409.0144 | 2209.281 | 3473.6597 | 4866.6733 | 4838.9673 | 4800.4662 | 4746.7862 | 4671.719 | 4566.4623 | 4418.5213 | 4210.1409 | 3916.0689 | 3500.3602 |  | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0074396 | 0.010795 | 0.015885 | 0.02366 | 0.035612 | 0.054084 | 0.08277 | 0.1275 | 0.19749 | 0.30735 | 0.48023 | 0.75291 | 1.0542 | 1.0542 | 1.0542 | 1.0542 | 1.0542 | 1.0542 | 1.0542 | 1.0542 | 1.0542 | 1.0542 |  | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0069241 | 0.0091784 | 0.012273 | 0.016539 | 0.022447 | 0.030656 | 0.042101 | 0.058107 | 0.080549 | 0.11209 | 0.15652 | 0.21922 | 0.30786 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016547 | 0.0050106 | 0.0101 | 0.017876 | 0.029827 | 0.048299 | 0.076985 | 0.12171 | 0.1917 | 0.30042 | 0.47105 | 0.74064 | 1.0376 | 1.0317 | 1.0235 | 1.0121 | 0.99608 | 0.97364 | 0.9421 | 0.89767 | 0.83496 | 0.74633 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7625 | 23.505 | 47.3821 | 83.8562 | 139.9226 | 226.577 | 361.1427 | 570.9686 | 899.306 | 1409.3149 | 2209.752 | 3474.4004 | 4867.711 | 4839.999 | 4801.4898 | 4747.7983 | 4672.7151 | 4567.436 | 4419.4634 | 4211.0386 | 3916.9039 | 3501.1065 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 18.8664 | 27.3765 | 40.284 | 60.0013 | 90.3099 | 137.1537 | 209.8977 | 323.326 | 500.8197 | 779.4109 | 1217.8302 | 1909.3248 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1963 | 12.7064 | 25.614 | 45.3312 | 75.6398 | 122.4837 | 195.2276 | 308.656 | 486.1496 | 761.8518 | 1194.5546 | 1878.2021 | 2631.4022 | 2616.4216 | 2595.6042 | 2566.5794 | 2525.9907 | 2469.0787 | 2389.0872 | 2276.4162 | 2117.412 | 1892.639 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6591 | 3.8586 | 5.6779 | 8.457 | 12.7288 | 19.3313 | 29.5843 | 45.5716 | 70.5887 | 109.8551 | 171.6488 | 269.1124 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59145 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2636 | 27.5166 | 43.5039 | 68.521 | 107.3802 | 168.3681 | 264.7258 | 370.8866 | 368.7751 | 365.841 | 361.7501 | 356.0292 | 348.0077 | 336.7332 | 320.8526 | 298.4415 | 266.7606 |  | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0017378 | 0.0025217 | 0.0037106 | 0.0055267 | 0.0083185 | 0.012633 | 0.019334 | 0.029782 | 0.046131 | 0.071792 | 0.11217 | 0.17587 | 0.24624 | 0.24624 | 0.24624 | 0.24624 | 0.24624 | 0.24624 | 0.24624 | 0.24624 | 0.24624 | 0.24624 |  | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0016174 | 0.0021439 | 0.0028667 | 0.0038634 | 0.0052432 | 0.0071607 | 0.0098342 | 0.013573 | 0.018815 | 0.026183 | 0.036561 | 0.051207 | 0.071911 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00038652 | 0.0011704 | 0.0023593 | 0.0041755 | 0.0069672 | 0.011282 | 0.017982 | 0.02843 | 0.044779 | 0.070174 | 0.11003 | 0.173 | 0.24238 | 0.241 | 0.23908 | 0.23641 | 0.23267 | 0.22743 | 0.22006 | 0.20968 | 0.19504 | 0.17433 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5507 | 38.0035 | 76.6086 | 135.5809 | 226.2306 | 366.3355 | 583.9049 | 923.1569 | 1454.0215 | 2278.6171 | 3572.7847 | 5617.5012 | 7870.2422 | 7825.4368 | 7763.174 | 7676.3642 | 7554.9677 | 7384.7497 | 7145.5038 | 6808.5171 | 6332.9524 | 5660.6804
| TRUE | 542 | 22005304 | BC | Blank | 66 | TRANS NO.2 | HT OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 43.0228 |  | 13.7946 | 0.021906 | 0.0038201 | 0.018086 | 234.0288 | 1833.6285 | 2067.6573 | 83.8714 | 8.803 | 107.077 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.013106 |  | 911.0297 | 2267.4087 | 71.2415 | 2196.1672 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0016791 | 0.0018376 | 0.0020116 | 0.0022027 | 0.0024128 | 0.0026436 | 0.0028973 | 0.0031762 | 0.0034829 | 0.0038201 | 0.0041909 | 0.0045988 | 0.0050476 | 0.0055414 | 0.0060847 | 0.0066827 | 0.0073408 | 0.0080653 | 0.0088629 | 0.0097411 | 0.010708 | 0.011773 | 0.012946 | 0.014238 | 0.015661 | 0.017229 | 0.018957 | 0.02086 | 0.022958 | 0.025269 | 996.6577 | 1090.6914 | 1193.9752 | 1307.4396 | 1432.1102 | 1569.117 | 1719.7056 | 1885.249 | 2067.2606 | 2267.4087 | 2487.5326 | 2729.6603 | 2996.0276 | 3289.1001 | 3611.5965 | 3966.515 | 4357.1622 | 4787.1849 | 5260.6054 | 5781.8604 | 6355.8436 | 6987.9536 | 7684.1459 | 8450.9907 | 9295.7364 | 10226.3804 | 11251.7466 | 12381.5709 | 13626.5965 | 14998.6779 |  | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 52.7996 | 69.989 | 93.5848 | 126.1205 | 171.1666 | 233.7639 | 321.04 | 443.0887 | 614.2211 | 854.7522 | 1193.5492 | 1671.6687 | 2347.5521 |  | 102.8693 | 112.5749 | 123.2352 | 134.9464 | 147.8141 | 161.9552 | 177.4981 | 194.5845 | 213.3707 | 234.0288 | 256.7487 | 281.7398 | 309.2327 | 339.4819 | 372.7681 | 409.4008 | 449.7211 | 494.1056 | 542.9693 | 596.7702 | 656.0134 | 721.2562 | 793.1131 | 872.2624 | 959.4522 | 1055.5079 | 1161.3403 | 1277.9542 | 1406.4585 | 1548.0769 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 75.7373 | 85.443 | 96.1033 | 107.8145 | 120.6822 | 134.8233 | 150.3662 | 167.4526 | 186.2388 | 206.8969 | 229.6168 | 254.6078 | 282.1007 | 312.35 | 345.6362 | 382.2688 | 422.5892 | 461.6304 | 499.9215 | 539.2095 | 578.4411 | 615.9776 | 649.3332 | 674.802 | 686.924 | 677.7222 | 635.6123 | 543.8442 | 378.2741 | 104.1804 |  | 805.9861 | 882.0302 | 965.5546 | 1057.3121 | 1158.1318 | 1268.9277 | 1390.707 | 1524.5801 | 1671.7709 | 1833.6285 | 2011.6403 | 2207.4462 | 2422.8546 | 2659.8591 | 2920.6584 | 3207.6771 | 3523.5892 | 3871.3438 | 4254.1938 | 4675.7269 | 5139.9008 | 5651.0813 | 6214.0844 | 6834.2233 | 7517.3599 | 8269.9614 | 9099.1638 | 10012.8403 | 11019.6788 | 12129.266 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 805.7617 | 881.8057 | 965.3302 | 1057.0876 | 1157.9073 | 1268.7032 | 1390.4826 | 1524.3557 | 1671.5465 | 1833.404 | 2011.4158 | 2207.2218 | 2422.6301 | 2659.6347 | 2920.434 | 3207.4527 | 3523.3648 | 3871.0752 | 4253.8377 | 4675.2508 | 5139.2592 | 5650.2104 | 6212.895 | 6832.5899 | 7515.1055 | 8266.8364 | 9094.815 | 10006.7678 | 11011.1738 | 12117.3222 |  | 881.4991 | 967.2487 | 1061.4335 | 1164.9021 | 1278.5896 | 1403.5265 | 1540.8488 | 1691.8083 | 1857.7852 | 2040.3009 | 2241.0327 | 2461.8297 | 2704.7309 | 2971.9846 | 3266.0702 | 3589.7215 | 3945.954 | 4332.7056 | 4753.7592 | 5214.4602 | 5717.7003 | 6266.188 | 6862.2283 | 7507.3919 | 8202.0295 | 8944.5586 | 9730.4273 | 10550.612 | 11389.4479 | 12221.5026 |  | 36.8663 | 40.3446 | 44.1651 | 48.3621 | 52.9737 | 58.0416 | 63.6119 | 69.7353 | 76.4679 | 83.8714 | 92.0137 | 100.97 | 110.823 | 121.6637 | 133.5928 | 146.7213 | 161.1713 | 177.0778 | 194.5896 | 213.8708 | 235.1024 | 258.4842 | 284.2363 | 312.6019 | 343.849 | 378.2735 | 416.2017 | 457.9939 | 504.0474 | 554.8006 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.1939 | 25.6722 | 29.4927 | 33.6897 | 38.3013 | 43.3691 | 48.9394 | 55.0629 | 61.7955 | 69.1989 | 77.3413 | 86.2976 | 96.1505 | 106.9913 | 118.9204 | 132.0488 | 146.4988 | 159.5158 | 171.3102 | 182.743 | 193.1528 | 201.5515 | 206.4828 | 205.8189 | 196.4707 | 173.9739 | 131.8977 | 61.0006 | -51.976 | -226.0322 |  | 3.8694 | 4.2345 | 4.6355 | 5.076 | 5.56 | 6.0919 | 6.6766 | 7.3193 | 8.0259 | 8.803 | 9.6576 | 10.5976 | 11.6318 | 12.7696 | 14.0216 | 15.3996 | 16.9162 | 18.5857 | 20.4237 | 22.4475 | 24.6759 | 27.13 | 29.8329 | 32.8101 | 36.0897 | 39.7028 | 43.6837 | 48.0701 | 52.9038 | 58.2308 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8017 | 2.1668 | 2.5678 | 3.0083 | 3.4923 | 4.0242 | 4.6089 | 5.2516 | 5.9582 | 6.7353 | 7.5899 | 8.5299 | 9.5641 | 10.7019 | 11.9539 | 13.3319 | 14.8485 | 16.1108 | 17.1431 | 18.0608 | 18.7642 | 19.1068 | 18.8756 | 17.7618 | 15.3206 | 10.9122 | 3.6185 | -7.8757 | -25.4531 | -51.8071 |  | 47.0666 | 51.5073 | 56.3848 | 61.7431 | 67.6306 | 74.1006 | 81.2121 | 89.0298 | 97.6252 | 107.077 | 117.4723 | 128.9066 | 141.4856 | 155.3258 | 170.5555 | 187.3163 | 205.7644 | 226.072 | 248.429 | 273.045 | 300.151 | 330.002 | 362.8793 | 399.0931 | 438.9857 | 482.9348 | 531.3571 | 584.7124 | 643.508 | 708.3037 |  | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.015687 | 0.020794 | 0.027805 | 0.037471 | 0.050854 | 0.069452 | 0.095383 | 0.13164 | 0.18249 | 0.25395 | 0.35461 | 0.49666 | 0.69747 |  | 47.0535 | 51.4942 | 56.3717 | 61.73 | 67.6175 | 74.0875 | 81.199 | 89.0167 | 97.6121 | 107.0639 | 117.4592 | 128.8935 | 141.4725 | 155.3127 | 170.5424 | 187.3032 | 205.7513 | 226.0563 | 248.4082 | 273.0171 | 300.1135 | 329.9511 | 362.8098 | 398.9977 | 438.854 | 482.7523 | 531.1032 | 584.3578 | 643.0113 | 707.6063 |  | 952.5481 | 1046.5818 | 1149.8656 | 1263.3301 | 1388.0006 | 1525.0074 | 1675.596 | 1841.1394 | 2023.151 | 2223.2991 | 2443.423 | 2685.5507 | 2951.918 | 3244.9905 | 3567.4869 | 3922.4054 | 4313.0527 | 4734.3885 | 5190.6207 | 5688.2812 | 6229.7307 | 6816.7975 | 7450.3964 | 8129.9703 | 8852.6749 | 9612.197 | 10397.0466 | 11188.0947 | 11955.0301 | 12651.2695
| TRUE | 543 | 22005303 | BC | Blank | 66 | TRANS NO.2 | HT OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 43.0228 |  | 13.7946 | 0.021906 | 0.0038201 | 0.018086 | 234.0288 | 1833.6285 | 2067.6573 | 83.8714 | 8.803 | 107.077 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.013106 |  | 911.0297 | 2267.4087 | 71.2415 | 2196.1672 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0016791 | 0.0018376 | 0.0020116 | 0.0022027 | 0.0024128 | 0.0026436 | 0.0028973 | 0.0031762 | 0.0034829 | 0.0038201 | 0.0041909 | 0.0045988 | 0.0050476 | 0.0055414 | 0.0060847 | 0.0066827 | 0.0073408 | 0.0080653 | 0.0088629 | 0.0097411 | 0.010708 | 0.011773 | 0.012946 | 0.014238 | 0.015661 | 0.017229 | 0.018957 | 0.02086 | 0.022958 | 0.025269 | 996.6577 | 1090.6914 | 1193.9752 | 1307.4396 | 1432.1102 | 1569.117 | 1719.7056 | 1885.249 | 2067.2606 | 2267.4087 | 2487.5326 | 2729.6603 | 2996.0276 | 3289.1001 | 3611.5965 | 3966.515 | 4357.1622 | 4787.1849 | 5260.6054 | 5781.8604 | 6355.8436 | 6987.9536 | 7684.1459 | 8450.9907 | 9295.7364 | 10226.3804 | 11251.7466 | 12381.5709 | 13626.5965 | 14998.6779 |  | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 52.7996 | 69.989 | 93.5848 | 126.1205 | 171.1666 | 233.7639 | 321.04 | 443.0887 | 614.2211 | 854.7522 | 1193.5492 | 1671.6687 | 2347.5521 |  | 102.8693 | 112.5749 | 123.2352 | 134.9464 | 147.8141 | 161.9552 | 177.4981 | 194.5845 | 213.3707 | 234.0288 | 256.7487 | 281.7398 | 309.2327 | 339.4819 | 372.7681 | 409.4008 | 449.7211 | 494.1056 | 542.9693 | 596.7702 | 656.0134 | 721.2562 | 793.1131 | 872.2624 | 959.4522 | 1055.5079 | 1161.3403 | 1277.9542 | 1406.4585 | 1548.0769 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 75.7373 | 85.443 | 96.1033 | 107.8145 | 120.6822 | 134.8233 | 150.3662 | 167.4526 | 186.2388 | 206.8969 | 229.6168 | 254.6078 | 282.1007 | 312.35 | 345.6362 | 382.2688 | 422.5892 | 461.6304 | 499.9215 | 539.2095 | 578.4411 | 615.9776 | 649.3332 | 674.802 | 686.924 | 677.7222 | 635.6123 | 543.8442 | 378.2741 | 104.1804 |  | 805.9861 | 882.0302 | 965.5546 | 1057.3121 | 1158.1318 | 1268.9277 | 1390.707 | 1524.5801 | 1671.7709 | 1833.6285 | 2011.6403 | 2207.4462 | 2422.8546 | 2659.8591 | 2920.6584 | 3207.6771 | 3523.5892 | 3871.3438 | 4254.1938 | 4675.7269 | 5139.9008 | 5651.0813 | 6214.0844 | 6834.2233 | 7517.3599 | 8269.9614 | 9099.1638 | 10012.8403 | 11019.6788 | 12129.266 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 805.7617 | 881.8057 | 965.3302 | 1057.0876 | 1157.9073 | 1268.7032 | 1390.4826 | 1524.3557 | 1671.5465 | 1833.404 | 2011.4158 | 2207.2218 | 2422.6301 | 2659.6347 | 2920.434 | 3207.4527 | 3523.3648 | 3871.0752 | 4253.8377 | 4675.2508 | 5139.2592 | 5650.2104 | 6212.895 | 6832.5899 | 7515.1055 | 8266.8364 | 9094.815 | 10006.7678 | 11011.1738 | 12117.3222 |  | 881.4991 | 967.2487 | 1061.4335 | 1164.9021 | 1278.5896 | 1403.5265 | 1540.8488 | 1691.8083 | 1857.7852 | 2040.3009 | 2241.0327 | 2461.8297 | 2704.7309 | 2971.9846 | 3266.0702 | 3589.7215 | 3945.954 | 4332.7056 | 4753.7592 | 5214.4602 | 5717.7003 | 6266.188 | 6862.2283 | 7507.3919 | 8202.0295 | 8944.5586 | 9730.4273 | 10550.612 | 11389.4479 | 12221.5026 |  | 36.8663 | 40.3446 | 44.1651 | 48.3621 | 52.9737 | 58.0416 | 63.6119 | 69.7353 | 76.4679 | 83.8714 | 92.0137 | 100.97 | 110.823 | 121.6637 | 133.5928 | 146.7213 | 161.1713 | 177.0778 | 194.5896 | 213.8708 | 235.1024 | 258.4842 | 284.2363 | 312.6019 | 343.849 | 378.2735 | 416.2017 | 457.9939 | 504.0474 | 554.8006 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.1939 | 25.6722 | 29.4927 | 33.6897 | 38.3013 | 43.3691 | 48.9394 | 55.0629 | 61.7955 | 69.1989 | 77.3413 | 86.2976 | 96.1505 | 106.9913 | 118.9204 | 132.0488 | 146.4988 | 159.5158 | 171.3102 | 182.743 | 193.1528 | 201.5515 | 206.4828 | 205.8189 | 196.4707 | 173.9739 | 131.8977 | 61.0006 | -51.976 | -226.0322 |  | 3.8694 | 4.2345 | 4.6355 | 5.076 | 5.56 | 6.0919 | 6.6766 | 7.3193 | 8.0259 | 8.803 | 9.6576 | 10.5976 | 11.6318 | 12.7696 | 14.0216 | 15.3996 | 16.9162 | 18.5857 | 20.4237 | 22.4475 | 24.6759 | 27.13 | 29.8329 | 32.8101 | 36.0897 | 39.7028 | 43.6837 | 48.0701 | 52.9038 | 58.2308 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8017 | 2.1668 | 2.5678 | 3.0083 | 3.4923 | 4.0242 | 4.6089 | 5.2516 | 5.9582 | 6.7353 | 7.5899 | 8.5299 | 9.5641 | 10.7019 | 11.9539 | 13.3319 | 14.8485 | 16.1108 | 17.1431 | 18.0608 | 18.7642 | 19.1068 | 18.8756 | 17.7618 | 15.3206 | 10.9122 | 3.6185 | -7.8757 | -25.4531 | -51.8071 |  | 47.0666 | 51.5073 | 56.3848 | 61.7431 | 67.6306 | 74.1006 | 81.2121 | 89.0298 | 97.6252 | 107.077 | 117.4723 | 128.9066 | 141.4856 | 155.3258 | 170.5555 | 187.3163 | 205.7644 | 226.072 | 248.429 | 273.045 | 300.151 | 330.002 | 362.8793 | 399.0931 | 438.9857 | 482.9348 | 531.3571 | 584.7124 | 643.508 | 708.3037 |  | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.015687 | 0.020794 | 0.027805 | 0.037471 | 0.050854 | 0.069452 | 0.095383 | 0.13164 | 0.18249 | 0.25395 | 0.35461 | 0.49666 | 0.69747 |  | 47.0535 | 51.4942 | 56.3717 | 61.73 | 67.6175 | 74.0875 | 81.199 | 89.0167 | 97.6121 | 107.0639 | 117.4592 | 128.8935 | 141.4725 | 155.3127 | 170.5424 | 187.3032 | 205.7513 | 226.0563 | 248.4082 | 273.0171 | 300.1135 | 329.9511 | 362.8098 | 398.9977 | 438.854 | 482.7523 | 531.1032 | 584.3578 | 643.0113 | 707.6063 |  | 952.5481 | 1046.5818 | 1149.8656 | 1263.3301 | 1388.0006 | 1525.0074 | 1675.596 | 1841.1394 | 2023.151 | 2223.2991 | 2443.423 | 2685.5507 | 2951.918 | 3244.9905 | 3567.4869 | 3922.4054 | 4313.0527 | 4734.3885 | 5190.6207 | 5688.2812 | 6229.7307 | 6816.7975 | 7450.3964 | 8129.9703 | 8852.6749 | 9612.197 | 10397.0466 | 11188.0947 | 11955.0301 | 12651.2695
| TRUE | 544 | 22005302 | BC | Blank | 66 | TRANS NO.2 | HT OVERCURRENT | Blank | English Electric | CDG11_520 | CDG11 520 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 43.0228 |  | 13.7946 | 0.021906 | 0.0038201 | 0.018086 | 234.0288 | 1833.6285 | 2067.6573 | 83.8714 | 8.803 | 107.077 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.013106 |  | 911.0297 | 2267.4087 | 71.2415 | 2196.1672 |  | 0.033174 |  | 10.2339 | 10.5791 | 10.936 | 11.3048 | 11.6862 | 12.0804 | 12.4878 | 12.9091 | 13.3445 | 13.7946 | 14.2599 | 14.7409 | 15.2381 | 15.7521 | 16.2834 | 16.8327 | 17.4005 | 17.9874 | 18.5941 | 19.2213 | 19.8697 | 20.5399 | 21.2327 | 21.9489 | 22.6892 | 23.4546 | 24.2457 | 25.0635 | 25.9089 | 26.7829 |  | 0.0096292 | 0.010538 | 0.011536 | 0.012632 | 0.013836 | 0.01516 | 0.016615 | 0.018214 | 0.019973 | 0.021906 | 0.024033 | 0.026372 | 0.028946 | 0.031777 | 0.034893 | 0.038322 | 0.042097 | 0.046251 | 0.050825 | 0.055861 | 0.061407 | 0.067514 | 0.07424 | 0.081649 | 0.08981 | 0.098802 | 0.10871 | 0.11962 | 0.13165 | 0.14491 |  | 0.0016791 | 0.0018376 | 0.0020116 | 0.0022027 | 0.0024128 | 0.0026436 | 0.0028973 | 0.0031762 | 0.0034829 | 0.0038201 | 0.0041909 | 0.0045988 | 0.0050476 | 0.0055414 | 0.0060847 | 0.0066827 | 0.0073408 | 0.0080653 | 0.0088629 | 0.0097411 | 0.010708 | 0.011773 | 0.012946 | 0.014238 | 0.015661 | 0.017229 | 0.018957 | 0.02086 | 0.022958 | 0.025269 | 996.6577 | 1090.6914 | 1193.9752 | 1307.4396 | 1432.1102 | 1569.117 | 1719.7056 | 1885.249 | 2067.2606 | 2267.4087 | 2487.5326 | 2729.6603 | 2996.0276 | 3289.1001 | 3611.5965 | 3966.515 | 4357.1622 | 4787.1849 | 5260.6054 | 5781.8604 | 6355.8436 | 6987.9536 | 7684.1459 | 8450.9907 | 9295.7364 | 10226.3804 | 11251.7466 | 12381.5709 | 13626.5965 | 14998.6779 |  | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 44.1123 | 52.7996 | 69.989 | 93.5848 | 126.1205 | 171.1666 | 233.7639 | 321.04 | 443.0887 | 614.2211 | 854.7522 | 1193.5492 | 1671.6687 | 2347.5521 |  | 102.8693 | 112.5749 | 123.2352 | 134.9464 | 147.8141 | 161.9552 | 177.4981 | 194.5845 | 213.3707 | 234.0288 | 256.7487 | 281.7398 | 309.2327 | 339.4819 | 372.7681 | 409.4008 | 449.7211 | 494.1056 | 542.9693 | 596.7702 | 656.0134 | 721.2562 | 793.1131 | 872.2624 | 959.4522 | 1055.5079 | 1161.3403 | 1277.9542 | 1406.4585 | 1548.0769 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 75.7373 | 85.443 | 96.1033 | 107.8145 | 120.6822 | 134.8233 | 150.3662 | 167.4526 | 186.2388 | 206.8969 | 229.6168 | 254.6078 | 282.1007 | 312.35 | 345.6362 | 382.2688 | 422.5892 | 461.6304 | 499.9215 | 539.2095 | 578.4411 | 615.9776 | 649.3332 | 674.802 | 686.924 | 677.7222 | 635.6123 | 543.8442 | 378.2741 | 104.1804 |  | 805.9861 | 882.0302 | 965.5546 | 1057.3121 | 1158.1318 | 1268.9277 | 1390.707 | 1524.5801 | 1671.7709 | 1833.6285 | 2011.6403 | 2207.4462 | 2422.8546 | 2659.8591 | 2920.6584 | 3207.6771 | 3523.5892 | 3871.3438 | 4254.1938 | 4675.7269 | 5139.9008 | 5651.0813 | 6214.0844 | 6834.2233 | 7517.3599 | 8269.9614 | 9099.1638 | 10012.8403 | 11019.6788 | 12129.266 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 805.7617 | 881.8057 | 965.3302 | 1057.0876 | 1157.9073 | 1268.7032 | 1390.4826 | 1524.3557 | 1671.5465 | 1833.404 | 2011.4158 | 2207.2218 | 2422.6301 | 2659.6347 | 2920.434 | 3207.4527 | 3523.3648 | 3871.0752 | 4253.8377 | 4675.2508 | 5139.2592 | 5650.2104 | 6212.895 | 6832.5899 | 7515.1055 | 8266.8364 | 9094.815 | 10006.7678 | 11011.1738 | 12117.3222 |  | 881.4991 | 967.2487 | 1061.4335 | 1164.9021 | 1278.5896 | 1403.5265 | 1540.8488 | 1691.8083 | 1857.7852 | 2040.3009 | 2241.0327 | 2461.8297 | 2704.7309 | 2971.9846 | 3266.0702 | 3589.7215 | 3945.954 | 4332.7056 | 4753.7592 | 5214.4602 | 5717.7003 | 6266.188 | 6862.2283 | 7507.3919 | 8202.0295 | 8944.5586 | 9730.4273 | 10550.612 | 11389.4479 | 12221.5026 |  | 36.8663 | 40.3446 | 44.1651 | 48.3621 | 52.9737 | 58.0416 | 63.6119 | 69.7353 | 76.4679 | 83.8714 | 92.0137 | 100.97 | 110.823 | 121.6637 | 133.5928 | 146.7213 | 161.1713 | 177.0778 | 194.5896 | 213.8708 | 235.1024 | 258.4842 | 284.2363 | 312.6019 | 343.849 | 378.2735 | 416.2017 | 457.9939 | 504.0474 | 554.8006 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.1939 | 25.6722 | 29.4927 | 33.6897 | 38.3013 | 43.3691 | 48.9394 | 55.0629 | 61.7955 | 69.1989 | 77.3413 | 86.2976 | 96.1505 | 106.9913 | 118.9204 | 132.0488 | 146.4988 | 159.5158 | 171.3102 | 182.743 | 193.1528 | 201.5515 | 206.4828 | 205.8189 | 196.4707 | 173.9739 | 131.8977 | 61.0006 | -51.976 | -226.0322 |  | 3.8694 | 4.2345 | 4.6355 | 5.076 | 5.56 | 6.0919 | 6.6766 | 7.3193 | 8.0259 | 8.803 | 9.6576 | 10.5976 | 11.6318 | 12.7696 | 14.0216 | 15.3996 | 16.9162 | 18.5857 | 20.4237 | 22.4475 | 24.6759 | 27.13 | 29.8329 | 32.8101 | 36.0897 | 39.7028 | 43.6837 | 48.0701 | 52.9038 | 58.2308 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8017 | 2.1668 | 2.5678 | 3.0083 | 3.4923 | 4.0242 | 4.6089 | 5.2516 | 5.9582 | 6.7353 | 7.5899 | 8.5299 | 9.5641 | 10.7019 | 11.9539 | 13.3319 | 14.8485 | 16.1108 | 17.1431 | 18.0608 | 18.7642 | 19.1068 | 18.8756 | 17.7618 | 15.3206 | 10.9122 | 3.6185 | -7.8757 | -25.4531 | -51.8071 |  | 47.0666 | 51.5073 | 56.3848 | 61.7431 | 67.6306 | 74.1006 | 81.2121 | 89.0298 | 97.6252 | 107.077 | 117.4723 | 128.9066 | 141.4856 | 155.3258 | 170.5555 | 187.3163 | 205.7644 | 226.072 | 248.429 | 273.045 | 300.151 | 330.002 | 362.8793 | 399.0931 | 438.9857 | 482.9348 | 531.3571 | 584.7124 | 643.508 | 708.3037 |  | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.015687 | 0.020794 | 0.027805 | 0.037471 | 0.050854 | 0.069452 | 0.095383 | 0.13164 | 0.18249 | 0.25395 | 0.35461 | 0.49666 | 0.69747 |  | 47.0535 | 51.4942 | 56.3717 | 61.73 | 67.6175 | 74.0875 | 81.199 | 89.0167 | 97.6121 | 107.0639 | 117.4592 | 128.8935 | 141.4725 | 155.3127 | 170.5424 | 187.3032 | 205.7513 | 226.0563 | 248.4082 | 273.0171 | 300.1135 | 329.9511 | 362.8098 | 398.9977 | 438.854 | 482.7523 | 531.1032 | 584.3578 | 643.0113 | 707.6063 |  | 952.5481 | 1046.5818 | 1149.8656 | 1263.3301 | 1388.0006 | 1525.0074 | 1675.596 | 1841.1394 | 2023.151 | 2223.2991 | 2443.423 | 2685.5507 | 2951.918 | 3244.9905 | 3567.4869 | 3922.4054 | 4313.0527 | 4734.3885 | 5190.6207 | 5688.2812 | 6229.7307 | 6816.7975 | 7450.3964 | 8129.9703 | 8852.6749 | 9612.197 | 10397.0466 | 11188.0947 | 11955.0301 | 12651.2695
| FALSE | 545 | 22013346 | BC | Blank | 66 | TRANS NO.2 | DIFFERENTIAL | X | Schweitzer | SEL_387E | SEL 387E | SEL 300s | Digital |  | 0.066046 | 1 |  | 1.7651 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.056108 | 27.188 | 14.6724 | 2.0677 | 0.013106 |  | 7.1689 | 0.021401 | 1.9362e-06 | 0.021399 | 112.3552 | 0.23235 | 112.5876 | 60.7596 | 8.5625 | 0.054273 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.056108 | 27.188 | 14.6724 | 2.0677 | 0.013106 |  | 43.9413 | 181.964 | 43.9413 | 138.0227 |  | 0.14015 |  | 2.0307 | 2.3362 | 2.6877 | 3.0921 | 3.5573 | 4.0924 | 4.7082 | 5.4165 | 6.2314 | 7.1689 | 8.2475 | 9.4883 | 10.9158 | 12.5581 | 14.4475 | 16.6211 | 19.1217 | 21.9985 | 25.3082 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054426 | 0.0075349 | 0.01056 | 0.014961 | 0.021401 | 0.030869 | 0.044852 | 0.065583 | 0.096424 | 0.14244 | 0.21128 | 0.3145 | 0.46958 | 0.70298 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.9241e-07 | 6.8172e-07 | 9.5541e-07 | 1.3536e-06 | 1.9362e-06 | 2.7929e-06 | 4.058e-06 | 5.9336e-06 | 8.7239e-06 | 1.2887e-05 | 1.9116e-05 | 2.8454e-05 | 4.2485e-05 | 6.3602e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 46.2763 | 64.0667 | 89.7885 | 127.2115 | 181.964 | 262.4699 | 381.3645 | 557.6348 | 819.8609 | 1211.1255 | 1796.4551 | 2674.1082 | 3992.7036 | 5977.2243 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 |  | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 52.5949 | 69.7177 | 93.222 | 125.6316 | 170.503 | 232.8575 | 319.7954 | 441.3708 | 611.8397 | 851.4384 | 1188.9218 | 1665.1876 | 2338.4506 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 28.5737 | 39.5585 | 55.4407 | 78.5478 | 112.3552 | 162.0643 | 235.4768 | 344.3164 | 506.2302 | 747.8199 | 1109.2367 | 1651.1511 | 2465.3293 | 3690.6887 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 1.4418 | 12.4266 | 28.3088 | 51.4159 | 85.2233 | 134.9324 | 208.3449 | 317.1845 | 479.0983 | 720.6879 | 1082.1047 | 1624.0192 | 2432.8541 | 3647.6409 | 4886.7244 | 4866.7128 | 4839.0065 | 4800.5052 | 4746.8247 | 4671.7569 | 4566.4994 | 4418.5572 | 4210.1751 | 3916.1007 | 3500.3886 |  | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.05909 | 0.081806 | 0.11465 | 0.16243 | 0.23235 | 0.33514 | 0.48696 | 0.71204 | 1.0469 | 1.5465 | 2.2939 | 3.4145 | 5.0982 | 7.6322 | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 10.2246 |  | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.067158 | 0.089022 | 0.11903 | 0.16042 | 0.21771 | 0.29733 | 0.40834 | 0.56358 | 0.78125 | 1.0872 | 1.5181 | 2.1263 | 2.9859 |  | 0 | 0 | 0 | 0 | 0 | 0.0029816 | 0.025698 | 0.058542 | 0.10633 | 0.17624 | 0.27904 | 0.43085 | 0.65593 | 0.99076 | 1.4904 | 2.2378 | 3.3584 | 5.0311 | 7.5432 | 10.1056 | 10.0642 | 10.0069 | 9.9273 | 9.8163 | 9.6611 | 9.4434 | 9.1374 | 8.7065 | 8.0984 | 7.2387 |  | 0 | 0 | 0 | 0 | 0 | 1.4448 | 12.4523 | 28.3673 | 51.5222 | 85.3996 | 135.2114 | 208.7757 | 317.8404 | 480.0891 | 722.1783 | 1084.3425 | 1627.3777 | 2437.8851 | 3655.1841 | 4896.83 | 4876.777 | 4849.0135 | 4810.4325 | 4756.641 | 4681.4179 | 4575.9428 | 4427.6946 | 4218.8816 | 3924.1991 | 3507.6273 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 15.4521 | 21.3925 | 29.9813 | 42.4772 | 60.7596 | 87.6414 | 127.3415 | 186.2 | 273.76 | 404.4073 | 599.8549 | 892.9123 | 1333.205 | 1995.8569 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0.77969 | 6.7201 | 15.3089 | 27.8048 | 46.0872 | 72.969 | 112.6691 | 171.5276 | 259.0876 | 389.7349 | 585.1825 | 878.2399 | 1315.643 | 1972.5775 | 2642.6512 | 2631.8293 | 2616.8462 | 2596.0254 | 2566.996 | 2526.4007 | 2469.4794 | 2389.4749 | 2276.7857 | 2117.7556 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1776 | 3.0147 | 4.2251 | 5.9861 | 8.5625 | 12.3508 | 17.9455 | 26.24 | 38.5793 | 56.9906 | 84.5338 | 125.8326 | 187.8803 | 281.2637 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0.10988 | 0.94702 | 2.1574 | 3.9184 | 6.4948 | 10.2831 | 15.8778 | 24.1723 | 36.5116 | 54.9229 | 82.4661 | 123.7649 | 185.4054 | 277.9831 | 372.4124 | 370.8873 | 368.7759 | 365.8417 | 361.7508 | 356.03 | 348.0084 | 336.7339 | 320.8533 | 298.4421 | 266.7611 |  | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013802 | 0.019109 | 0.02678 | 0.037942 | 0.054273 | 0.078285 | 0.11375 | 0.16632 | 0.24453 | 0.36123 | 0.53581 | 0.79758 | 1.1909 | 1.7828 | 2.3883 | 2.3883 | 2.3883 | 2.3883 | 2.3883 | 2.3883 | 2.3883 | 2.3883 | 2.3883 | 2.3883 | 2.3883 |  | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.015687 | 0.020794 | 0.027805 | 0.037471 | 0.050854 | 0.069452 | 0.095383 | 0.13164 | 0.18249 | 0.25395 | 0.35461 | 0.49666 | 0.69747 |  | 0 | 0 | 0 | 0 | 0 | 0.00069645 | 0.0060026 | 0.013674 | 0.024836 | 0.041167 | 0.065179 | 0.10064 | 0.15322 | 0.23143 | 0.34813 | 0.52271 | 0.78448 | 1.1752 | 1.762 | 2.3605 | 2.3509 | 2.3375 | 2.3189 | 2.2929 | 2.2567 | 2.2058 | 2.1344 | 2.0337 | 1.8917 | 1.6909 |  | 0 | 0 | 0 | 0 | 0 | 2.335 | 20.1254 | 45.8473 | 83.2702 | 138.0227 | 218.5287 | 337.4232 | 513.6935 | 775.9197 | 1167.1842 | 1752.5138 | 2630.1669 | 3940.1087 | 5907.5066 | 7914.2541 | 7881.8445 | 7836.9731 | 7774.6185 | 7687.6807 | 7566.1053 | 7395.6364 | 7156.0377 | 6818.5543 | 6342.2885 | 5669.0254
| FALSE | 546 | 22013353 | BC | Blank | 66 | TRANS NO.3 | DIFFERENTIAL & REF | Y | Siemens | 7UT612 | 7UT612 | SIEMENS 7UT61X | Digital |  | 0.0068096 | 1 |  | 1.4709 | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0057849 | 27.1375 | 14.6701 | 2.0677 | 0.0013513 |  | 4.8786 | 0.0081995 | 7.6486e-08 | 0.0081994 | 43.0474 | 0.0091784 | 43.0566 | 23.2757 | 3.2806 | 0.0021439 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0057849 | 27.1375 | 14.6701 | 2.0677 | 0.0013513 |  | 43.8766 | 69.6151 | 43.8766 | 25.7385 |  | 0.11989 |  | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 5.7701e-08 | 7.6486e-08 | 1.0227e-07 | 1.3783e-07 | 1.8706e-07 | 2.5546e-07 | 3.5084e-07 | 4.8422e-07 | 6.7124e-07 | 9.341e-07 | 1.3044e-06 | 1.8269e-06 | 2.5655e-06 | 3.6112e-06 | 5.0937e-06 | 7.198e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 52.5175 | 69.6151 | 93.0848 | 125.4466 | 170.252 | 232.5148 | 319.3246 | 440.7211 | 610.9391 | 850.185 | 1187.1717 | 1662.7364 | 2335.0084 | 3286.7914 | 4636.1145 | 6551.3143 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 |  | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 52.5175 | 69.6151 | 93.0848 | 125.4466 | 170.252 | 232.5148 | 319.3246 | 440.7211 | 610.9391 | 850.185 | 1187.1717 | 1662.7364 | 2335.0084 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 | 2032.433 | 2866.8057 | 4051.096 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9158 | 30.4286 | 50.44 | 78.146 | 116.647 | 170.3271 | 245.3943 | 350.6509 | 493.2487 | 691.0566 | 970.6158 | 1366.3131 | 1927.1553 | 2723.0269 | 3853.6372 | 4671.719 | 4566.4623 | 4418.5213 | 4210.1409 | 3916.0689 | 3500.3602 |  | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0069241 | 0.0091784 | 0.012273 | 0.016539 | 0.022447 | 0.030656 | 0.042101 | 0.058107 | 0.080549 | 0.11209 | 0.15652 | 0.21922 | 0.30786 | 0.43335 | 0.61125 | 0.86375 | 1.0542 | 1.0542 | 1.0542 | 1.0542 | 1.0542 | 1.0542 |  | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0069241 | 0.0091784 | 0.012273 | 0.016539 | 0.022447 | 0.030656 | 0.042101 | 0.058107 | 0.080549 | 0.11209 | 0.15652 | 0.21922 | 0.30786 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011393 | 0.0033935 | 0.0064878 | 0.010755 | 0.016662 | 0.024871 | 0.036316 | 0.052322 | 0.074764 | 0.10517 | 0.14734 | 0.20695 | 0.29132 | 0.4109 | 0.58059 | 0.82165 | 0.99608 | 0.97364 | 0.9421 | 0.89767 | 0.83496 | 0.74633 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3444 | 15.9192 | 30.4351 | 50.4507 | 78.1627 | 116.6719 | 170.3634 | 245.4466 | 350.7257 | 493.3539 | 691.204 | 970.8228 | 1366.6044 | 1927.5662 | 2723.6075 | 3854.4589 | 4672.7151 | 4567.436 | 4419.4634 | 4211.0386 | 3916.9039 | 3501.1065 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 | 1098.9332 | 1550.0771 | 2190.4209 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8891 | 8.6056 | 16.4527 | 27.2728 | 42.2534 | 63.0709 | 92.0956 | 132.6843 | 189.5964 | 266.6988 | 373.6532 | 524.8104 | 738.7632 | 1042.0097 | 1472.3362 | 2083.6553 | 2525.9907 | 2469.0787 | 2389.0872 | 2276.4162 | 2117.412 | 1892.639 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 | 154.8906 | 218.4777 | 308.7319 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.7014 | 26.7229 | 37.5902 | 52.6651 | 73.9701 | 104.126 | 146.8675 | 207.5204 | 293.6837 | 356.0292 | 348.0077 | 336.7332 | 320.8526 | 298.4415 | 266.7606 |  | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0016174 | 0.0021439 | 0.0028667 | 0.0038634 | 0.0052432 | 0.0071607 | 0.0098342 | 0.013573 | 0.018815 | 0.026183 | 0.036561 | 0.051207 | 0.071911 | 0.10122 | 0.14278 | 0.20176 | 0.24624 | 0.24624 | 0.24624 | 0.24624 | 0.24624 | 0.24624 |  | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0016174 | 0.0021439 | 0.0028667 | 0.0038634 | 0.0052432 | 0.0071607 | 0.0098342 | 0.013573 | 0.018815 | 0.026183 | 0.036561 | 0.051207 | 0.071911 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00026611 | 0.00079267 | 0.0015155 | 0.0025121 | 0.003892 | 0.0058095 | 0.0084829 | 0.012222 | 0.017464 | 0.024566 | 0.034417 | 0.04834 | 0.068048 | 0.09598 | 0.13562 | 0.19193 | 0.23267 | 0.22743 | 0.22006 | 0.20968 | 0.19504 | 0.17433 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6409 | 25.7385 | 49.2082 | 81.5701 | 126.3755 | 188.6382 | 275.448 | 396.8445 | 567.0625 | 797.6675 | 1117.5566 | 1569.6516 | 2209.5617 | 3116.5394 | 4403.5997 | 6231.9897 | 7554.9677 | 7384.7497 | 7145.5038 | 6808.5171 | 6332.9524 | 5660.6804
| FALSE | 547 | 22013384 | BC | Blank | 66 | TRANS NO.3 | HT OVERCURRENT | Y | Schweitzer | SEL_351A | SEL 351 | SEL 300s | Digital |  | 0.0068096 | 1 |  | 1.7651 | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0057849 | 27.1375 | 14.6701 | 2.0677 | 0.0013513 |  | 7.1689 | 0.021401 | 1.9963e-07 | 0.021401 | 112.3543 | 0.023956 | 112.3783 | 60.7498 | 8.5625 | 0.0055957 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0057849 | 27.1375 | 14.6701 | 2.0677 | 0.0013513 |  | 43.8766 | 181.6961 | 43.8766 | 137.8195 |  | 0.14015 |  | 2.0307 | 2.3362 | 2.6877 | 3.0921 | 3.5573 | 4.0924 | 4.7082 | 5.4165 | 6.2314 | 7.1689 | 8.2475 | 9.4883 | 10.9158 | 12.5581 | 14.4475 | 16.6211 | 19.1217 | 21.9985 | 25.3082 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054426 | 0.0075349 | 0.01056 | 0.014961 | 0.021401 | 0.030869 | 0.044852 | 0.065583 | 0.096424 | 0.14244 | 0.21128 | 0.3145 | 0.46958 | 0.70298 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 5.0769e-08 | 7.0287e-08 | 9.8506e-08 | 1.3956e-07 | 1.9963e-07 | 2.8795e-07 | 4.1839e-07 | 6.1177e-07 | 8.9946e-07 | 1.3287e-06 | 1.9709e-06 | 2.9337e-06 | 4.3803e-06 | 6.5575e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 46.2082 | 63.9724 | 89.6563 | 127.0242 | 181.6961 | 262.0836 | 380.8031 | 556.8139 | 818.6541 | 1209.3426 | 1793.8106 | 2670.1718 | 3986.8262 | 5968.4256 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 | 7995.6888 |  | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 43.8766 | 52.5175 | 69.6151 | 93.0848 | 125.4466 | 170.252 | 232.5148 | 319.3246 | 440.7211 | 610.9391 | 850.185 | 1187.1717 | 1662.7364 | 2335.0084 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 28.5735 | 39.5582 | 55.4402 | 78.5472 | 112.3543 | 162.063 | 235.4749 | 344.3136 | 506.2261 | 747.8138 | 1109.2277 | 1651.1377 | 2465.3093 | 3690.6587 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 0 | 0 | 0 | 0 | 0 | 1.4418 | 12.4265 | 28.3086 | 51.4155 | 85.2226 | 134.9313 | 208.3432 | 317.1819 | 479.0944 | 720.6821 | 1082.096 | 1624.0061 | 2432.8343 | 3647.6113 | 4886.6847 | 4866.6733 | 4838.9673 | 4800.4662 | 4746.7862 | 4671.719 | 4566.4623 | 4418.5213 | 4210.1409 | 3916.0689 | 3500.3602 |  | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0060923 | 0.0084344 | 0.011821 | 0.016747 | 0.023956 | 0.034554 | 0.050207 | 0.073413 | 0.10794 | 0.15945 | 0.2365 | 0.35205 | 0.52564 | 0.7869 | 1.0542 | 1.0542 | 1.0542 | 1.0542 | 1.0542 | 1.0542 | 1.0542 | 1.0542 | 1.0542 | 1.0542 | 1.0542 |  | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0057849 | 0.0069241 | 0.0091784 | 0.012273 | 0.016539 | 0.022447 | 0.030656 | 0.042101 | 0.058107 | 0.080549 | 0.11209 | 0.15652 | 0.21922 | 0.30786 |  | 0 | 0 | 0 | 0 | 0 | 0.00030741 | 0.0026495 | 0.0060358 | 0.010963 | 0.018171 | 0.028769 | 0.044422 | 0.067628 | 0.10215 | 0.15366 | 0.23072 | 0.34626 | 0.51872 | 0.77773 | 1.0419 | 1.0376 | 1.0317 | 1.0235 | 1.0121 | 0.99608 | 0.97364 | 0.9421 | 0.89767 | 0.83496 | 0.74633 |  | 0 | 0 | 0 | 0 | 0 | 1.4421 | 12.4292 | 28.3146 | 51.4265 | 85.2408 | 134.9601 | 208.3876 | 317.2495 | 479.1966 | 720.8358 | 1082.3267 | 1624.3523 | 2433.353 | 3648.389 | 4887.7266 | 4867.711 | 4839.999 | 4801.4898 | 4747.7983 | 4672.7151 | 4567.436 | 4419.4634 | 4211.0386 | 3916.9039 | 3501.1065 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 15.4496 | 21.3891 | 29.9764 | 42.4703 | 60.7498 | 87.6272 | 127.3209 | 186.1698 | 273.7156 | 404.3417 | 599.7576 | 892.7675 | 1332.9886 | 1995.5331 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 0 | 0 | 0 | 0 | 0 | 0.77956 | 6.719 | 15.3064 | 27.8003 | 46.0797 | 72.9571 | 112.6508 | 171.4997 | 259.0456 | 389.6716 | 585.0875 | 878.0974 | 1315.4295 | 1972.2574 | 2642.2224 | 2631.4022 | 2616.4216 | 2595.6042 | 2566.5794 | 2525.9907 | 2469.0787 | 2389.0872 | 2276.4162 | 2117.412 | 1892.639 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1776 | 3.0147 | 4.2251 | 5.986 | 8.5625 | 12.3507 | 17.9454 | 26.24 | 38.5792 | 56.9905 | 84.5337 | 125.8323 | 187.8799 | 281.2631 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0.10988 | 0.94702 | 2.1574 | 3.9183 | 6.4948 | 10.283 | 15.8777 | 24.1723 | 36.5115 | 54.9228 | 82.466 | 123.7646 | 185.405 | 277.9825 | 372.4117 | 370.8866 | 368.7751 | 365.841 | 361.7501 | 356.0292 | 348.0077 | 336.7332 | 320.8526 | 298.4415 | 266.7606 |  | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0014231 | 0.0019702 | 0.0027611 | 0.003912 | 0.0055957 | 0.0080714 | 0.011728 | 0.017148 | 0.025212 | 0.037244 | 0.055244 | 0.082233 | 0.12278 | 0.18381 | 0.24624 | 0.24624 | 0.24624 | 0.24624 | 0.24624 | 0.24624 | 0.24624 | 0.24624 | 0.24624 | 0.24624 | 0.24624 |  | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0013513 | 0.0016174 | 0.0021439 | 0.0028667 | 0.0038634 | 0.0052432 | 0.0071607 | 0.0098342 | 0.013573 | 0.018815 | 0.026183 | 0.036561 | 0.051207 | 0.071911 |  | 0 | 0 | 0 | 0 | 0 | 7.1806e-05 | 0.00061889 | 0.0014099 | 0.0025607 | 0.0042444 | 0.0067201 | 0.010376 | 0.015797 | 0.023861 | 0.035893 | 0.053893 | 0.080882 | 0.12116 | 0.18167 | 0.24338 | 0.24238 | 0.241 | 0.23908 | 0.23641 | 0.23267 | 0.22743 | 0.22006 | 0.20968 | 0.19504 | 0.17433 |  | 0 | 0 | 0 | 0 | 0 | 2.3316 | 20.0958 | 45.7798 | 83.1476 | 137.8195 | 218.207 | 336.9265 | 512.9373 | 774.7775 | 1165.4661 | 1749.934 | 2626.2952 | 3934.3087 | 5898.8106 | 7902.604 | 7870.2422 | 7825.4368 | 7763.174 | 7676.3642 | 7554.9677 | 7384.7497 | 7145.5038 | 6808.5171 | 6332.9524 | 5660.6804
| FALSE | 548 | 22013349 | BC | Blank | 66 | TRANS NO.3 | DIFFERENTIAL | X | Schweitzer | SEL_387E | SEL 387E | SEL 300s | Digital |  | 0.066046 | 1 |  | 1.7651 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.056108 | 27.188 | 14.6724 | 2.0677 | 0.013106 |  | 7.1689 | 0.021401 | 1.9362e-06 | 0.021399 | 112.3552 | 0.23235 | 112.5876 | 60.7596 | 8.5625 | 0.054273 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.056108 | 27.188 | 14.6724 | 2.0677 | 0.013106 |  | 43.9413 | 181.964 | 43.9413 | 138.0227 |  | 0.14015 |  | 2.0307 | 2.3362 | 2.6877 | 3.0921 | 3.5573 | 4.0924 | 4.7082 | 5.4165 | 6.2314 | 7.1689 | 8.2475 | 9.4883 | 10.9158 | 12.5581 | 14.4475 | 16.6211 | 19.1217 | 21.9985 | 25.3082 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054426 | 0.0075349 | 0.01056 | 0.014961 | 0.021401 | 0.030869 | 0.044852 | 0.065583 | 0.096424 | 0.14244 | 0.21128 | 0.3145 | 0.46958 | 0.70298 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.9241e-07 | 6.8172e-07 | 9.5541e-07 | 1.3536e-06 | 1.9362e-06 | 2.7929e-06 | 4.058e-06 | 5.9336e-06 | 8.7239e-06 | 1.2887e-05 | 1.9116e-05 | 2.8454e-05 | 4.2485e-05 | 6.3602e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 46.2763 | 64.0667 | 89.7885 | 127.2115 | 181.964 | 262.4699 | 381.3645 | 557.6348 | 819.8609 | 1211.1255 | 1796.4551 | 2674.1082 | 3992.7036 | 5977.2243 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 | 8007.4761 |  | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 52.5949 | 69.7177 | 93.222 | 125.6316 | 170.503 | 232.8575 | 319.7954 | 441.3708 | 611.8397 | 851.4384 | 1188.9218 | 1665.1876 | 2338.4506 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 28.5737 | 39.5585 | 55.4407 | 78.5478 | 112.3552 | 162.0643 | 235.4768 | 344.3164 | 506.2302 | 747.8199 | 1109.2367 | 1651.1511 | 2465.3293 | 3690.6887 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 1.4418 | 12.4266 | 28.3088 | 51.4159 | 85.2233 | 134.9324 | 208.3449 | 317.1845 | 479.0983 | 720.6879 | 1082.1047 | 1624.0192 | 2432.8541 | 3647.6409 | 4886.7244 | 4866.7128 | 4839.0065 | 4800.5052 | 4746.8247 | 4671.7569 | 4566.4994 | 4418.5572 | 4210.1751 | 3916.1007 | 3500.3886 |  | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.05909 | 0.081806 | 0.11465 | 0.16243 | 0.23235 | 0.33514 | 0.48696 | 0.71204 | 1.0469 | 1.5465 | 2.2939 | 3.4145 | 5.0982 | 7.6322 | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 10.2246 |  | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.056108 | 0.067158 | 0.089022 | 0.11903 | 0.16042 | 0.21771 | 0.29733 | 0.40834 | 0.56358 | 0.78125 | 1.0872 | 1.5181 | 2.1263 | 2.9859 |  | 0 | 0 | 0 | 0 | 0 | 0.0029816 | 0.025698 | 0.058542 | 0.10633 | 0.17624 | 0.27904 | 0.43085 | 0.65593 | 0.99076 | 1.4904 | 2.2378 | 3.3584 | 5.0311 | 7.5432 | 10.1056 | 10.0642 | 10.0069 | 9.9273 | 9.8163 | 9.6611 | 9.4434 | 9.1374 | 8.7065 | 8.0984 | 7.2387 |  | 0 | 0 | 0 | 0 | 0 | 1.4448 | 12.4523 | 28.3673 | 51.5222 | 85.3996 | 135.2114 | 208.7757 | 317.8404 | 480.0891 | 722.1783 | 1084.3425 | 1627.3777 | 2437.8851 | 3655.1841 | 4896.83 | 4876.777 | 4849.0135 | 4810.4325 | 4756.641 | 4681.4179 | 4575.9428 | 4427.6946 | 4218.8816 | 3924.1991 | 3507.6273 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 15.4521 | 21.3925 | 29.9813 | 42.4772 | 60.7596 | 87.6414 | 127.3415 | 186.2 | 273.76 | 404.4073 | 599.8549 | 892.9123 | 1333.205 | 1995.8569 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0.77969 | 6.7201 | 15.3089 | 27.8048 | 46.0872 | 72.969 | 112.6691 | 171.5276 | 259.0876 | 389.7349 | 585.1825 | 878.2399 | 1315.643 | 1972.5775 | 2642.6512 | 2631.8293 | 2616.8462 | 2596.0254 | 2566.996 | 2526.4007 | 2469.4794 | 2389.4749 | 2276.7857 | 2117.7556 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1776 | 3.0147 | 4.2251 | 5.9861 | 8.5625 | 12.3508 | 17.9455 | 26.24 | 38.5793 | 56.9906 | 84.5338 | 125.8326 | 187.8803 | 281.2637 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0.10988 | 0.94702 | 2.1574 | 3.9184 | 6.4948 | 10.2831 | 15.8778 | 24.1723 | 36.5116 | 54.9229 | 82.4661 | 123.7649 | 185.4054 | 277.9831 | 372.4124 | 370.8873 | 368.7759 | 365.8417 | 361.7508 | 356.03 | 348.0084 | 336.7339 | 320.8533 | 298.4421 | 266.7611 |  | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013802 | 0.019109 | 0.02678 | 0.037942 | 0.054273 | 0.078285 | 0.11375 | 0.16632 | 0.24453 | 0.36123 | 0.53581 | 0.79758 | 1.1909 | 1.7828 | 2.3883 | 2.3883 | 2.3883 | 2.3883 | 2.3883 | 2.3883 | 2.3883 | 2.3883 | 2.3883 | 2.3883 | 2.3883 |  | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.013106 | 0.015687 | 0.020794 | 0.027805 | 0.037471 | 0.050854 | 0.069452 | 0.095383 | 0.13164 | 0.18249 | 0.25395 | 0.35461 | 0.49666 | 0.69747 |  | 0 | 0 | 0 | 0 | 0 | 0.00069645 | 0.0060026 | 0.013674 | 0.024836 | 0.041167 | 0.065179 | 0.10064 | 0.15322 | 0.23143 | 0.34813 | 0.52271 | 0.78448 | 1.1752 | 1.762 | 2.3605 | 2.3509 | 2.3375 | 2.3189 | 2.2929 | 2.2567 | 2.2058 | 2.1344 | 2.0337 | 1.8917 | 1.6909 |  | 0 | 0 | 0 | 0 | 0 | 2.335 | 20.1254 | 45.8473 | 83.2702 | 138.0227 | 218.5287 | 337.4232 | 513.6935 | 775.9197 | 1167.1842 | 1752.5138 | 2630.1669 | 3940.1087 | 5907.5066 | 7914.2541 | 7881.8445 | 7836.9731 | 7774.6185 | 7687.6807 | 7566.1053 | 7395.6364 | 7156.0377 | 6818.5543 | 6342.2885 | 5669.0254
| FALSE | 1544 | 22009921 | FB | Blank | 11 | BUS ALL | POWER QUALITY | I | Schneider | ION_7650 | ION 7650 | ION 7000s | Digital |  | 0.033587 | 1 |  | 6.6 | 0.017308 | 7.9633e-07 | 0.017307 | 95.1936 | 0.25483 | 95.4485 | 49.1349 | 6.9249 | 0.0078282 |  | 9.0234 | 0.0392 | 1.8036e-06 | 0.039198 | 215.6015 | 0.57715 | 216.1786 | 111.2842 | 15.684 | 0.01773 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.0023374 |  | 151.5161 | 343.1646 | 45.241 | 297.9236 |  | 0.031275 |  | 6.8097 | 7.026 | 7.2492 | 7.4795 | 7.7172 | 7.9623 | 8.2153 | 8.4763 | 8.7456 | 9.0234 | 9.3101 | 9.6059 | 9.911 | 10.2259 | 10.5508 | 10.886 | 11.2318 | 11.5886 | 11.9568 | 12.3367 | 12.7286 | 13.133 | 13.5502 | 13.9807 | 14.4249 | 14.8831 | 15.356 | 15.8438 | 16.3472 | 16.8665 |  | 0.018748 | 0.020317 | 0.022027 | 0.02389 | 0.025921 | 0.028136 | 0.030552 | 0.033187 | 0.036062 | 0.0392 | 0.042625 | 0.046364 | 0.050446 | 0.054905 | 0.059775 | 0.065095 | 0.070908 | 0.077261 | 0.084205 | 0.091795 | 0.10009 | 0.10917 | 0.11909 | 0.12995 | 0.14182 | 0.15481 | 0.16902 | 0.18457 | 0.20159 | 0.22022 |  | 8.626e-07 | 9.3479e-07 | 1.0134e-06 | 1.0992e-06 | 1.1926e-06 | 1.2946e-06 | 1.4057e-06 | 1.5269e-06 | 1.6592e-06 | 1.8036e-06 | 1.9612e-06 | 2.1332e-06 | 2.321e-06 | 2.5262e-06 | 2.7502e-06 | 2.995e-06 | 3.2625e-06 | 3.5548e-06 | 3.8743e-06 | 4.2235e-06 | 4.6053e-06 | 5.0228e-06 | 5.4794e-06 | 5.9788e-06 | 6.525e-06 | 7.1227e-06 | 7.7766e-06 | 8.4922e-06 | 9.2753e-06 | 1.0132e-05 | 164.1243 | 177.8596 | 192.8262 | 209.1383 | 226.9209 | 246.311 | 267.4584 | 290.5271 | 315.6969 | 343.1646 | 373.1457 | 405.8764 | 441.6154 | 480.6459 | 523.2786 | 569.8536 | 620.7437 | 676.3574 | 737.1424 | 803.5896 | 876.2368 | 955.6736 | 1042.5462 | 1137.5634 | 1241.502 | 1355.2136 | 1479.6323 | 1615.782 | 1764.7858 | 1927.8751 |  | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 37.1408 | 49.2323 | 65.8303 | 88.7169 | 120.4036 | 164.4363 | 225.8289 | 311.6815 | 432.061 | 601.2576 | 839.5773 | 1175.9004 | 1651.3365 |  | 103.1151 | 111.7446 | 121.1477 | 131.3962 | 142.5686 | 154.7509 | 168.0372 | 182.5307 | 198.3442 | 215.6015 | 234.4379 | 255.0017 | 277.4556 | 301.9775 | 328.7625 | 358.0244 | 389.9973 | 424.9379 | 463.1277 | 504.8747 | 550.5171 | 600.4251 | 655.005 | 714.7019 | 780.0038 | 851.4459 | 929.6149 | 1015.1543 | 1108.7696 | 1211.2344 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 88.9032 | 97.5327 | 106.9358 | 117.1843 | 128.3567 | 140.539 | 153.8253 | 168.3188 | 184.1324 | 201.3896 | 220.226 | 240.7898 | 263.2437 | 287.7656 | 314.5506 | 343.8125 | 375.7854 | 407.9272 | 440.5789 | 474.724 | 509.8841 | 545.2795 | 579.6921 | 611.2707 | 637.2515 | 653.559 | 654.2348 | 630.6222 | 570.1992 | 454.911 |  | 0.27603 | 0.29913 | 0.3243 | 0.35174 | 0.38165 | 0.41426 | 0.44982 | 0.48862 | 0.53095 | 0.57715 | 0.62757 | 0.68262 | 0.74273 | 0.80837 | 0.88007 | 0.95841 | 1.044 | 1.1375 | 1.2398 | 1.3515 | 1.4737 | 1.6073 | 1.7534 | 1.9132 | 2.088 | 2.2793 | 2.4885 | 2.7175 | 2.9681 | 3.2424 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 0.19994 | 0.22304 | 0.24822 | 0.27565 | 0.30556 | 0.33817 | 0.37374 | 0.41253 | 0.45487 | 0.50106 | 0.55149 | 0.60653 | 0.66664 | 0.73228 | 0.80399 | 0.88232 | 0.96791 | 1.0465 | 1.119 | 1.1901 | 1.2562 | 1.3121 | 1.3502 | 1.3595 | 1.3237 | 1.2198 | 1.0142 | 0.65877 | 0.084668 | -0.80686 |  | 89.1032 | 97.7558 | 107.1841 | 117.46 | 128.6623 | 140.8772 | 154.1991 | 168.7313 | 184.5872 | 201.8907 | 220.7775 | 241.3964 | 263.9103 | 288.4979 | 315.3546 | 344.6948 | 376.7533 | 408.9737 | 441.6979 | 475.9141 | 511.1403 | 546.5915 | 581.0422 | 612.6301 | 638.5753 | 654.7788 | 655.249 | 631.281 | 570.2838 | 454.1042 |  | 53.2236 | 57.6778 | 62.5313 | 67.8211 | 73.5878 | 79.8758 | 86.7336 | 94.2145 | 102.3768 | 111.2842 | 121.0068 | 131.621 | 143.2107 | 155.8678 | 169.6931 | 184.7968 | 201.2999 | 219.3347 | 239.0466 | 260.5947 | 284.1533 | 309.9137 | 338.0855 | 368.8985 | 402.6045 | 439.4799 | 479.8274 | 523.9791 | 572.2993 | 625.1873 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 38.5525 | 43.0066 | 47.8601 | 53.1499 | 58.9167 | 65.2046 | 72.0625 | 79.5434 | 87.7057 | 96.6131 | 106.3356 | 116.9498 | 128.5395 | 141.1967 | 155.022 | 170.1257 | 186.6287 | 201.7743 | 215.7692 | 229.4697 | 242.2073 | 252.9861 | 260.3389 | 262.125 | 255.2393 | 235.1984 | 195.5486 | 127.0211 | 16.3254 | -155.5761 |  | 7.5011 | 8.1289 | 8.8129 | 9.5584 | 10.3712 | 11.2574 | 12.2239 | 13.2782 | 14.4286 | 15.684 | 17.0542 | 18.5502 | 20.1836 | 21.9674 | 23.9159 | 26.0446 | 28.3704 | 30.9122 | 33.6903 | 36.7272 | 40.0475 | 43.678 | 47.6485 | 51.9911 | 56.7415 | 61.9386 | 67.625 | 73.8476 | 80.6577 | 88.1115 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 5.4334 | 6.0612 | 6.7452 | 7.4907 | 8.3035 | 9.1897 | 10.1562 | 11.2105 | 12.3609 | 13.6163 | 14.9865 | 16.4825 | 18.1159 | 19.8997 | 21.8482 | 23.9769 | 26.3027 | 28.4373 | 30.4097 | 32.3406 | 34.1358 | 35.6549 | 36.6912 | 36.9429 | 35.9725 | 33.148 | 27.5599 | 17.9019 | 2.3008 | -21.9263 |  | 0.0084796 | 0.0091893 | 0.0099625 | 0.010805 | 0.011724 | 0.012726 | 0.013818 | 0.01501 | 0.016311 | 0.01773 | 0.019279 | 0.02097 | 0.022816 | 0.024833 | 0.027036 | 0.029442 | 0.032071 | 0.034945 | 0.038085 | 0.041518 | 0.045272 | 0.049376 | 0.053864 | 0.058773 | 0.064143 | 0.070018 | 0.076447 | 0.083481 | 0.091179 | 0.099605 |  | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0027977 | 0.0037086 | 0.0049589 | 0.0066829 | 0.0090698 | 0.012387 | 0.017011 | 0.023478 | 0.032546 | 0.045292 | 0.063244 | 0.088578 | 0.12439 |  | 0.0061422 | 0.0068519 | 0.0076251 | 0.0084679 | 0.0093867 | 0.010388 | 0.011481 | 0.012673 | 0.013973 | 0.015392 | 0.016941 | 0.018633 | 0.020479 | 0.022496 | 0.024698 | 0.027105 | 0.029734 | 0.032147 | 0.034377 | 0.036559 | 0.038589 | 0.040306 | 0.041477 | 0.041762 | 0.040665 | 0.037472 | 0.031155 | 0.020237 | 0.002601 | -0.024787 |  | 133.0952 | 146.8304 | 161.797 | 178.1091 | 195.8918 | 215.2819 | 236.4292 | 259.4979 | 284.6678 | 312.1354 | 342.1166 | 374.8473 | 410.5862 | 449.6168 | 492.2495 | 538.8244 | 589.7145 | 639.2174 | 687.9113 | 737.7609 | 787.522 | 835.2728 | 878.1138 | 911.7398 | 929.8277 | 923.1627 | 878.3886 | 776.2242 | 588.9127 | 276.5769
| TRUE | 1545 | 22014874 | FB | Blank | 11 | BUS ALL | STRUCTURE LEAKAGE | Blank | EMAIL | RC3_170 | RC3_170 | RC3 | Electromechanical |  | 0 | 2190 |  | 5.5 | 0.0019187 | 0 | 0.0019187 | 10.5531 | 0 | 10.5531 | 5.4466 | 0.76769 | 0 |  | 7.3552 | 0.0040026 | 0 | 0.0040026 | 22.0142 | 0 | 22.0142 | 11.3618 | 1.6014 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 16.7674 | 34.9775 | 45.1611 | -10.1836 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.0127 | 19.3593 | 20.8156 | 22.3909 | 24.0955 | 25.9403 | 27.9373 | 30.0995 | 32.4411 | 34.9775 | 37.7254 | 40.7031 | 43.9303 | 47.4287 | 51.2217 | 55.3348 | 59.7958 | 64.635 | 69.8852 | 75.5823 | 81.7653 | 88.4766 | 95.7623 | 103.6728 | 112.2629 | 121.5922 | 131.7256 | 142.7338 | 154.6938 | 167.6895 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 11.3369 | 12.1844 | 13.101 | 14.0925 | 15.1653 | 16.3264 | 17.5833 | 18.9441 | 20.4179 | 22.0142 | 23.7437 | 25.6178 | 27.649 | 29.8508 | 32.2381 | 34.8268 | 37.6345 | 40.6802 | 43.9846 | 47.5702 | 51.4617 | 55.6856 | 60.2712 | 65.2499 | 70.6564 | 76.5281 | 82.9058 | 89.8342 | 97.3616 | 105.5409 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | -2.8749 | -2.0274 | -1.1109 | -0.11935 | 0.95348 | 2.1146 | 3.3714 | 4.7323 | 6.2061 | 7.8024 | 9.5319 | 11.406 | 13.4372 | 15.639 | 18.0262 | 20.615 | 23.4227 | 23.6695 | 21.4359 | 17.4197 | 10.829 | 0.54024 | -15.0414 | -38.1808 | -72.0952 | -121.3579 | -192.473 | -294.6961 | -441.2063 | -650.779 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -2.8749 | -2.0274 | -1.1109 | -0.11935 | 0.95348 | 2.1146 | 3.3714 | 4.7323 | 6.2061 | 7.8024 | 9.5319 | 11.406 | 13.4372 | 15.639 | 18.0262 | 20.615 | 23.4227 | 23.6695 | 21.4359 | 17.4197 | 10.829 | 0.54024 | -15.0414 | -38.1808 | -72.0952 | -121.3579 | -192.473 | -294.6961 | -441.2063 | -650.779 |  | 5.8511 | 6.2885 | 6.7616 | 7.2733 | 7.827 | 8.4262 | 9.0749 | 9.7773 | 10.5379 | 11.3618 | 12.2544 | 13.2217 | 14.27 | 15.4064 | 16.6384 | 17.9745 | 19.4236 | 20.9955 | 22.701 | 24.5516 | 26.56 | 28.74 | 31.1067 | 33.6763 | 36.4666 | 39.4971 | 42.7887 | 46.3645 | 50.2495 | 54.4709 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | -8.8187 | -8.3813 | -7.9082 | -7.3965 | -6.8428 | -6.2435 | -5.5949 | -4.8925 | -4.1319 | -3.308 | -2.4154 | -1.4481 | -0.39981 | 0.73658 | 1.9687 | 3.3047 | 4.7538 | 3.4367 | -0.57428 | -6.5706 | -15.3821 | -28.1824 | -46.6328 | -73.0874 | -110.885 | -164.7656 | -241.4639 | -350.5569 | -505.6732 | -726.2206 |  | 0.82471 | 0.88636 | 0.95304 | 1.0252 | 1.1032 | 1.1877 | 1.2791 | 1.3781 | 1.4853 | 1.6014 | 1.7272 | 1.8636 | 2.0113 | 2.1715 | 2.3452 | 2.5335 | 2.7377 | 2.9593 | 3.1997 | 3.4605 | 3.7436 | 4.0509 | 4.3845 | 4.7466 | 5.1399 | 5.5671 | 6.031 | 6.535 | 7.0826 | 7.6776 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | -1.243 | -1.1813 | -1.1147 | -1.0425 | -0.96448 | -0.88002 | -0.78859 | -0.68959 | -0.58238 | -0.46626 | -0.34044 | -0.20411 | -0.056353 | 0.10382 | 0.27748 | 0.4658 | 0.67005 | 0.4844 | -0.080944 | -0.92612 | -2.1681 | -3.9723 | -6.5728 | -10.3016 | -15.6291 | -23.2235 | -34.0341 | -49.4106 | -71.2741 | -102.36 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -12.9366 | -11.59 | -10.1337 | -8.5584 | -6.8538 | -5.009 | -3.012 | -0.84979 | 1.4918 | 4.0282 | 6.7761 | 9.7538 | 12.981 | 16.4794 | 20.2724 | 24.3855 | 28.8465 | 27.5906 | 20.7807 | 9.923 | -6.7212 | -31.6144 | -68.2471 | -121.5698 | -198.6093 | -309.347 | -467.971 | -694.6637 | -1018.1536 | -1479.3597
| TRUE | 1546 | 22006088 | FB | Blank | 11 | BUS NO.1 | RESIDUAL BUS PROT | Blank | GEC | CDG14_984 | CDG14 984 | CDG14 | Electromechanical |  | 0.033587 | 2190 |  | 8.25 | 0.0054067 | 0.00050998 | 0.0048967 | 30.0172 | 163.1947 | 193.2118 | 18.2427 | 2.1683 | 5.0133 |  | 11.5885 | 0.013521 | 0.0012753 | 0.012245 | 75.0657 | 408.1105 | 483.1761 | 45.6207 | 5.4224 | 12.5371 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.0023374 |  | 218.6362 | 546.7563 | 45.241 | 501.5153 |  | 0.03398 |  | 8.5352 | 8.8302 | 9.1354 | 9.4511 | 9.7778 | 10.1158 | 10.4654 | 10.8271 | 11.2014 | 11.5885 | 11.9891 | 12.4035 | 12.8322 | 13.2757 | 13.7346 | 14.2093 | 14.7004 | 15.2085 | 15.7342 | 16.278 | 16.8407 | 17.4227 | 18.0249 | 18.6479 | 19.2925 | 19.9593 | 20.6492 | 21.3629 | 22.1013 | 22.8652 |  | 0.0059156 | 0.0064751 | 0.0070903 | 0.007767 | 0.0085115 | 0.0093307 | 0.010232 | 0.011225 | 0.012317 | 0.013521 | 0.014846 | 0.016306 | 0.017915 | 0.019688 | 0.021642 | 0.023795 | 0.02617 | 0.028788 | 0.031676 | 0.034861 | 0.038374 | 0.042249 | 0.046526 | 0.051245 | 0.056453 | 0.062201 | 0.068547 | 0.075552 | 0.083287 | 0.091827 |  | 0.00055799 | 0.00061076 | 0.00066879 | 0.00073262 | 0.00080284 | 0.00088011 | 0.00096516 | 0.0010588 | 0.0011618 | 0.0012753 | 0.0014004 | 0.0015381 | 0.0016898 | 0.001857 | 0.0020413 | 0.0022445 | 0.0024685 | 0.0027154 | 0.0029878 | 0.0032882 | 0.0036196 | 0.0039852 | 0.0043885 | 0.0048337 | 0.0053249 | 0.0058671 | 0.0064657 | 0.0071265 | 0.007856 | 0.0086616 | 239.2158 | 261.8408 | 286.7202 | 314.0848 | 344.1895 | 377.3157 | 413.774 | 453.9075 | 498.0954 | 546.7563 | 600.3525 | 659.3951 | 724.4484 | 796.1361 | 875.1473 | 962.2437 | 1058.2668 | 1164.1468 | 1280.9118 | 1409.6982 | 1551.7621 | 1708.4922 | 1881.4238 | 2072.2542 | 2282.86 | 2515.3161 | 2771.9171 | 3055.2001 | 3367.9709 | 3713.3325 |  | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 37.1408 | 49.2323 | 65.8303 | 88.7169 | 120.4036 | 164.4363 | 225.8289 | 311.6815 | 432.061 | 601.2576 | 839.5773 | 1175.9004 | 1651.3365 |  | 32.8426 | 35.9488 | 39.3646 | 43.1216 | 47.2547 | 51.8027 | 56.8081 | 62.3182 | 68.3849 | 75.0657 | 82.424 | 90.5301 | 99.4615 | 109.3037 | 120.1514 | 132.1091 | 145.2923 | 159.8289 | 175.8599 | 193.5413 | 213.0456 | 234.5635 | 258.3058 | 284.5054 | 313.42 | 345.3346 | 380.564 | 419.4567 | 462.3979 | 509.8135 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 18.6307 | 21.7369 | 25.1527 | 28.9097 | 33.0428 | 37.5908 | 42.5963 | 48.1063 | 54.173 | 60.8538 | 68.2121 | 76.3183 | 85.2496 | 95.0918 | 105.9395 | 117.8972 | 131.0804 | 142.8181 | 153.3111 | 163.3906 | 172.4127 | 179.4179 | 182.9928 | 181.0742 | 170.6678 | 147.4477 | 105.1839 | 34.9246 | -76.1725 | -246.5099 |  | 178.5557 | 195.4435 | 214.014 | 234.4396 | 256.9104 | 281.6364 | 308.8496 | 338.8062 | 371.789 | 408.1105 | 448.1159 | 492.1865 | 540.7436 | 594.2528 | 653.2285 | 718.2391 | 789.9128 | 868.9438 | 956.0997 | 1052.2286 | 1158.2681 | 1275.2548 | 1404.3346 | 1546.7744 | 1703.975 | 1877.4852 | 2069.0176 | 2280.4661 | 2513.9249 | 2771.71 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 178.4796 | 195.3674 | 213.9379 | 234.3635 | 256.8343 | 281.5603 | 308.7736 | 338.7301 | 371.7129 | 408.0344 | 448.0398 | 492.1104 | 540.6675 | 594.1767 | 653.1524 | 718.163 | 789.8367 | 868.8528 | 955.979 | 1052.0672 | 1158.0506 | 1274.9596 | 1403.9314 | 1546.2207 | 1703.2108 | 1876.4258 | 2067.5433 | 2278.4074 | 2511.0414 | 2767.6608 |  | 197.1103 | 217.1043 | 239.0906 | 263.2731 | 289.8771 | 319.1511 | 351.3698 | 386.8364 | 425.8859 | 468.8882 | 516.2519 | 568.4286 | 625.9171 | 689.2685 | 759.0919 | 836.0602 | 920.9171 | 1011.6709 | 1109.2901 | 1215.4577 | 1330.4633 | 1454.3774 | 1586.9242 | 1727.2949 | 1873.8786 | 2023.8735 | 2172.7272 | 2313.332 | 2434.8689 | 2521.1509 |  | 19.9599 | 21.8477 | 23.9236 | 26.2069 | 28.7188 | 31.4828 | 34.5248 | 37.8735 | 41.5605 | 45.6207 | 50.0927 | 55.0191 | 60.4471 | 66.4286 | 73.0213 | 80.2885 | 88.3005 | 97.135 | 106.8778 | 117.6235 | 129.4772 | 142.5546 | 156.9838 | 172.9064 | 190.4791 | 209.875 | 231.2855 | 254.9223 | 281.0195 | 309.836 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 5.2887 | 7.1765 | 9.2525 | 11.5357 | 14.0476 | 16.8116 | 19.8537 | 23.2024 | 26.8894 | 30.9496 | 35.4216 | 40.348 | 45.776 | 51.7575 | 58.3501 | 65.6173 | 73.6294 | 79.5746 | 83.6004 | 86.4985 | 87.5312 | 85.6269 | 79.2371 | 66.1329 | 43.114 | 5.5936 | -52.9933 | -142.0357 | -274.9544 | -470.9273 |  | 2.3724 | 2.5968 | 2.8435 | 3.1149 | 3.4135 | 3.742 | 4.1036 | 4.5016 | 4.9398 | 5.4224 | 5.9539 | 6.5395 | 7.1847 | 7.8956 | 8.6792 | 9.543 | 10.4953 | 11.5453 | 12.7033 | 13.9806 | 15.3895 | 16.9438 | 18.6589 | 20.5514 | 22.6401 | 24.9454 | 27.4903 | 30.2997 | 33.4016 | 36.8267 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0.30471 | 0.52909 | 0.77583 | 1.0472 | 1.3458 | 1.6743 | 2.0359 | 2.4339 | 2.8721 | 3.3547 | 3.8863 | 4.4718 | 5.117 | 5.8279 | 6.6115 | 7.4753 | 8.4276 | 9.0704 | 9.4227 | 9.5939 | 9.4778 | 8.9207 | 7.7016 | 5.5032 | 1.871 | -3.8452 | -12.5749 | -25.646 | -44.9552 | -73.2111 |  | 5.4852 | 6.004 | 6.5745 | 7.2019 | 7.8922 | 8.6518 | 9.4878 | 10.408 | 11.4213 | 12.5371 | 13.766 | 15.1198 | 16.6115 | 18.2553 | 20.067 | 22.0641 | 24.2659 | 26.6937 | 29.3711 | 32.3242 | 35.5817 | 39.1755 | 43.1408 | 47.5165 | 52.3457 | 57.6759 | 63.5597 | 70.0553 | 77.2271 | 85.1462 |  | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0027977 | 0.0037086 | 0.0049589 | 0.0066829 | 0.0090698 | 0.012387 | 0.017011 | 0.023478 | 0.032546 | 0.045292 | 0.063244 | 0.088578 | 0.12439 |  | 5.4829 | 6.0016 | 6.5721 | 7.1996 | 7.8899 | 8.6495 | 9.4854 | 10.4057 | 11.4189 | 12.5347 | 13.7637 | 15.1175 | 16.6092 | 18.253 | 20.0647 | 22.0618 | 24.2636 | 26.6909 | 29.3674 | 32.3192 | 35.575 | 39.1664 | 43.1284 | 47.4995 | 52.3222 | 57.6433 | 63.5144 | 69.9921 | 77.1386 | 85.0218 |  | 208.1867 | 230.8116 | 255.691 | 283.0557 | 313.1604 | 346.2865 | 382.7448 | 422.8784 | 467.0663 | 515.7272 | 569.3234 | 628.3659 | 693.4192 | 765.1069 | 844.1182 | 931.2146 | 1027.2377 | 1127.0069 | 1231.6806 | 1343.8694 | 1463.0473 | 1588.0914 | 1716.9914 | 1846.4305 | 1971.1857 | 2083.2652 | 2170.6734 | 2215.6423 | 2192.0978 | 2062.0343
| TRUE | 1547 | 22006090 | FB | Blank | 11 | BUS NO.1 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.033587 | 2190 |  | 9.9 | 0.0088019 | 0.00083024 | 0.0079716 | 48.8669 | 265.6753 | 314.5422 | 29.6986 | 3.5299 | 8.1615 |  | 14.217 | 0.023831 | 0.0022479 | 0.021583 | 132.3088 | 719.325 | 851.6338 | 80.4099 | 9.5574 | 22.0975 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.0023374 |  | 355.9322 | 963.6986 | 45.241 | 918.4575 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.00091573 | 0.0010104 | 0.0011153 | 0.0012316 | 0.0013604 | 0.0015032 | 0.0016615 | 0.0018371 | 0.0020319 | 0.0022479 | 0.0024876 | 0.0027536 | 0.0030488 | 0.0033765 | 0.0037403 | 0.0041442 | 0.0045928 | 0.005091 | 0.0056445 | 0.0062593 | 0.0069424 | 0.0077015 | 0.0085451 | 0.0094827 | 0.010525 | 0.011683 | 0.012971 | 0.014404 | 0.015546 | 0.015546 | 392.5858 | 433.1824 | 478.1561 | 527.9895 | 583.2193 | 644.4421 | 712.3213 | 787.5947 | 871.0829 | 963.6986 | 1066.457 | 1180.4875 | 1307.0464 | 1447.5317 | 1603.4987 | 1776.678 | 1968.9954 | 2182.5942 | 2419.8595 | 2683.4461 | 2976.3087 | 3301.7362 | 3663.3897 | 4065.3448 | 4512.1387 | 5008.8225 | 5561.0201 | 6174.9932 | 6664.7992 | 6664.7992 |  | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 37.1408 | 49.2323 | 65.8303 | 88.7169 | 120.4036 | 164.4363 | 225.8289 | 311.6815 | 432.061 | 601.2576 | 839.5773 | 1175.9004 | 1651.3365 |  | 53.8992 | 59.4728 | 65.6473 | 72.4891 | 80.0718 | 88.4772 | 97.7965 | 108.131 | 119.5933 | 132.3088 | 146.4168 | 162.0723 | 179.4479 | 198.7356 | 220.1487 | 243.9249 | 270.3287 | 299.6543 | 332.2291 | 368.4176 | 408.6255 | 453.3043 | 502.9567 | 558.1422 | 619.4838 | 687.6748 | 763.4875 | 847.7816 | 915.0284 | 915.0284 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 39.6873 | 45.2609 | 51.4355 | 58.2772 | 65.8599 | 74.2653 | 83.5846 | 93.9191 | 105.3814 | 118.0969 | 132.2049 | 147.8604 | 165.2361 | 184.5237 | 205.9368 | 229.713 | 256.1168 | 282.6435 | 309.6803 | 338.2669 | 367.9926 | 398.1587 | 427.6438 | 454.711 | 476.7315 | 489.788 | 488.1075 | 463.2495 | 376.458 | 158.705 |  | 293.0344 | 323.3365 | 356.9058 | 394.1026 | 435.3273 | 481.0252 | 531.6917 | 587.8773 | 650.1947 | 719.325 | 796.0261 | 881.1408 | 975.6071 | 1080.4683 | 1196.8854 | 1326.1501 | 1469.6999 | 1629.1345 | 1806.2344 | 2002.981 | 2221.5798 | 2464.4858 | 2734.4317 | 3034.4595 | 3367.9559 | 3738.6912 | 4150.8632 | 4609.1457 | 4974.7473 | 4974.7473 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 292.9583 | 323.2604 | 356.8298 | 394.0265 | 435.2512 | 480.9491 | 531.6156 | 587.8013 | 650.1186 | 719.2489 | 795.95 | 881.0648 | 975.531 | 1080.3922 | 1196.8093 | 1326.074 | 1469.6238 | 1629.0435 | 1806.1137 | 2002.8196 | 2221.3623 | 2464.1906 | 2734.0285 | 3033.9057 | 3367.1916 | 3737.6318 | 4149.3889 | 4607.087 | 4971.8639 | 4970.698 |  | 332.6456 | 368.5213 | 408.2652 | 452.3037 | 501.1111 | 555.2145 | 615.2002 | 681.7204 | 755.5001 | 837.3458 | 928.1549 | 1028.9252 | 1140.7671 | 1264.9159 | 1402.7461 | 1555.787 | 1725.7406 | 1911.687 | 2115.794 | 2341.0865 | 2589.3549 | 2862.3492 | 3161.6722 | 3488.6168 | 3843.9231 | 4227.4197 | 4637.4963 | 5070.3364 | 5348.3218 | 5129.403 |  | 32.7569 | 36.1442 | 39.8968 | 44.0548 | 48.6631 | 53.7715 | 59.4352 | 65.716 | 72.6821 | 80.4099 | 88.9839 | 98.4985 | 109.0584 | 120.7803 | 133.794 | 148.2439 | 164.2906 | 182.1131 | 201.9102 | 223.9036 | 248.3397 | 275.4929 | 305.6689 | 339.2075 | 376.4875 | 417.9302 | 464.0049 | 515.2341 | 556.1029 | 556.1029 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 18.0858 | 21.4731 | 25.2256 | 29.3837 | 33.992 | 39.1003 | 44.7641 | 51.0448 | 58.011 | 65.7387 | 74.3128 | 83.8273 | 94.3873 | 106.1092 | 119.1229 | 133.5728 | 149.6195 | 164.5526 | 178.6328 | 192.7785 | 206.3937 | 218.5653 | 227.9223 | 232.4341 | 229.1223 | 213.6488 | 179.7261 | 118.2761 | 0.12902 | -224.6605 |  | 3.8934 | 4.2961 | 4.7421 | 5.2363 | 5.784 | 6.3912 | 7.0644 | 7.8109 | 8.6389 | 9.5574 | 10.5765 | 11.7074 | 12.9625 | 14.3558 | 15.9026 | 17.6201 | 19.5274 | 21.6457 | 23.9988 | 26.6129 | 29.5173 | 32.7447 | 36.3314 | 40.3177 | 44.7488 | 49.6746 | 55.151 | 61.24 | 66.0976 | 66.0976 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 1.8257 | 2.2284 | 2.6744 | 3.1686 | 3.7163 | 4.3235 | 4.9967 | 5.7432 | 6.5712 | 7.4897 | 8.5088 | 9.6397 | 10.8948 | 12.2881 | 13.8349 | 15.5524 | 17.4597 | 19.1708 | 20.7181 | 22.2262 | 23.6056 | 24.7215 | 25.3741 | 25.2695 | 23.9797 | 20.884 | 15.0858 | 5.2943 | -12.2592 | -43.9402 |  | 9.0019 | 9.9328 | 10.9641 | 12.1067 | 13.3731 | 14.777 | 16.3334 | 18.0594 | 19.9738 | 22.0975 | 24.4537 | 27.0684 | 29.9704 | 33.1917 | 36.768 | 40.739 | 45.1488 | 50.0466 | 55.4871 | 61.5311 | 68.2464 | 75.7084 | 84.0011 | 93.2178 | 103.4628 | 114.8517 | 127.5135 | 141.5918 | 152.823 | 152.823 |  | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0027977 | 0.0037086 | 0.0049589 | 0.0066829 | 0.0090698 | 0.012387 | 0.017011 | 0.023478 | 0.032546 | 0.045292 | 0.063244 | 0.088578 | 0.12439 |  | 8.9996 | 9.9305 | 10.9617 | 12.1044 | 13.3708 | 14.7746 | 16.3311 | 18.0571 | 19.9715 | 22.0951 | 24.4514 | 27.0661 | 29.9681 | 33.1894 | 36.7657 | 40.7367 | 45.1465 | 50.0438 | 55.4834 | 61.5261 | 68.2397 | 75.6993 | 83.9887 | 93.2008 | 103.4393 | 114.8191 | 127.4682 | 141.5286 | 152.7344 | 152.6986 |  | 361.5567 | 402.1533 | 447.127 | 496.9604 | 552.1902 | 613.4129 | 681.2921 | 756.5655 | 840.0537 | 932.6694 | 1035.4278 | 1149.4583 | 1276.0173 | 1416.5026 | 1572.4695 | 1745.6488 | 1937.9663 | 2145.4543 | 2370.6283 | 2617.6173 | 2887.5939 | 3181.3354 | 3498.9572 | 3839.5211 | 4200.4644 | 4576.7716 | 4959.7765 | 5335.4354 | 5488.926 | 5013.501
| TRUE | 1548 | 22006092 | FB | Blank | 11 | BUS NO.2 | RESIDUAL BUS PROT | Blank | GEC | CDG14_984 | CDG14 984 | CDG14 | Electromechanical |  | 0.033587 | 2190 |  | 8.25 | 0.0054067 | 0.00050998 | 0.0048967 | 30.0172 | 163.1947 | 193.2118 | 18.2427 | 2.1683 | 5.0133 |  | 11.5885 | 0.013521 | 0.0012753 | 0.012245 | 75.0657 | 408.1105 | 483.1761 | 45.6207 | 5.4224 | 12.5371 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.0023374 |  | 218.6362 | 546.7563 | 45.241 | 501.5153 |  | 0.03398 |  | 8.5352 | 8.8302 | 9.1354 | 9.4511 | 9.7778 | 10.1158 | 10.4654 | 10.8271 | 11.2014 | 11.5885 | 11.9891 | 12.4035 | 12.8322 | 13.2757 | 13.7346 | 14.2093 | 14.7004 | 15.2085 | 15.7342 | 16.278 | 16.8407 | 17.4227 | 18.0249 | 18.6479 | 19.2925 | 19.9593 | 20.6492 | 21.3629 | 22.1013 | 22.8652 |  | 0.0059156 | 0.0064751 | 0.0070903 | 0.007767 | 0.0085115 | 0.0093307 | 0.010232 | 0.011225 | 0.012317 | 0.013521 | 0.014846 | 0.016306 | 0.017915 | 0.019688 | 0.021642 | 0.023795 | 0.02617 | 0.028788 | 0.031676 | 0.034861 | 0.038374 | 0.042249 | 0.046526 | 0.051245 | 0.056453 | 0.062201 | 0.068547 | 0.075552 | 0.083287 | 0.091827 |  | 0.00055799 | 0.00061076 | 0.00066879 | 0.00073262 | 0.00080284 | 0.00088011 | 0.00096516 | 0.0010588 | 0.0011618 | 0.0012753 | 0.0014004 | 0.0015381 | 0.0016898 | 0.001857 | 0.0020413 | 0.0022445 | 0.0024685 | 0.0027154 | 0.0029878 | 0.0032882 | 0.0036196 | 0.0039852 | 0.0043885 | 0.0048337 | 0.0053249 | 0.0058671 | 0.0064657 | 0.0071265 | 0.007856 | 0.0086616 | 239.2158 | 261.8408 | 286.7202 | 314.0848 | 344.1895 | 377.3157 | 413.774 | 453.9075 | 498.0954 | 546.7563 | 600.3525 | 659.3951 | 724.4484 | 796.1361 | 875.1473 | 962.2437 | 1058.2668 | 1164.1468 | 1280.9118 | 1409.6982 | 1551.7621 | 1708.4922 | 1881.4238 | 2072.2542 | 2282.86 | 2515.3161 | 2771.9171 | 3055.2001 | 3367.9709 | 3713.3325 |  | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 37.1408 | 49.2323 | 65.8303 | 88.7169 | 120.4036 | 164.4363 | 225.8289 | 311.6815 | 432.061 | 601.2576 | 839.5773 | 1175.9004 | 1651.3365 |  | 32.8426 | 35.9488 | 39.3646 | 43.1216 | 47.2547 | 51.8027 | 56.8081 | 62.3182 | 68.3849 | 75.0657 | 82.424 | 90.5301 | 99.4615 | 109.3037 | 120.1514 | 132.1091 | 145.2923 | 159.8289 | 175.8599 | 193.5413 | 213.0456 | 234.5635 | 258.3058 | 284.5054 | 313.42 | 345.3346 | 380.564 | 419.4567 | 462.3979 | 509.8135 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 18.6307 | 21.7369 | 25.1527 | 28.9097 | 33.0428 | 37.5908 | 42.5963 | 48.1063 | 54.173 | 60.8538 | 68.2121 | 76.3183 | 85.2496 | 95.0918 | 105.9395 | 117.8972 | 131.0804 | 142.8181 | 153.3111 | 163.3906 | 172.4127 | 179.4179 | 182.9928 | 181.0742 | 170.6678 | 147.4477 | 105.1839 | 34.9246 | -76.1725 | -246.5099 |  | 178.5557 | 195.4435 | 214.014 | 234.4396 | 256.9104 | 281.6364 | 308.8496 | 338.8062 | 371.789 | 408.1105 | 448.1159 | 492.1865 | 540.7436 | 594.2528 | 653.2285 | 718.2391 | 789.9128 | 868.9438 | 956.0997 | 1052.2286 | 1158.2681 | 1275.2548 | 1404.3346 | 1546.7744 | 1703.975 | 1877.4852 | 2069.0176 | 2280.4661 | 2513.9249 | 2771.71 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 178.4796 | 195.3674 | 213.9379 | 234.3635 | 256.8343 | 281.5603 | 308.7736 | 338.7301 | 371.7129 | 408.0344 | 448.0398 | 492.1104 | 540.6675 | 594.1767 | 653.1524 | 718.163 | 789.8367 | 868.8528 | 955.979 | 1052.0672 | 1158.0506 | 1274.9596 | 1403.9314 | 1546.2207 | 1703.2108 | 1876.4258 | 2067.5433 | 2278.4074 | 2511.0414 | 2767.6608 |  | 197.1103 | 217.1043 | 239.0906 | 263.2731 | 289.8771 | 319.1511 | 351.3698 | 386.8364 | 425.8859 | 468.8882 | 516.2519 | 568.4286 | 625.9171 | 689.2685 | 759.0919 | 836.0602 | 920.9171 | 1011.6709 | 1109.2901 | 1215.4577 | 1330.4633 | 1454.3774 | 1586.9242 | 1727.2949 | 1873.8786 | 2023.8735 | 2172.7272 | 2313.332 | 2434.8689 | 2521.1509 |  | 19.9599 | 21.8477 | 23.9236 | 26.2069 | 28.7188 | 31.4828 | 34.5248 | 37.8735 | 41.5605 | 45.6207 | 50.0927 | 55.0191 | 60.4471 | 66.4286 | 73.0213 | 80.2885 | 88.3005 | 97.135 | 106.8778 | 117.6235 | 129.4772 | 142.5546 | 156.9838 | 172.9064 | 190.4791 | 209.875 | 231.2855 | 254.9223 | 281.0195 | 309.836 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 5.2887 | 7.1765 | 9.2525 | 11.5357 | 14.0476 | 16.8116 | 19.8537 | 23.2024 | 26.8894 | 30.9496 | 35.4216 | 40.348 | 45.776 | 51.7575 | 58.3501 | 65.6173 | 73.6294 | 79.5746 | 83.6004 | 86.4985 | 87.5312 | 85.6269 | 79.2371 | 66.1329 | 43.114 | 5.5936 | -52.9933 | -142.0357 | -274.9544 | -470.9273 |  | 2.3724 | 2.5968 | 2.8435 | 3.1149 | 3.4135 | 3.742 | 4.1036 | 4.5016 | 4.9398 | 5.4224 | 5.9539 | 6.5395 | 7.1847 | 7.8956 | 8.6792 | 9.543 | 10.4953 | 11.5453 | 12.7033 | 13.9806 | 15.3895 | 16.9438 | 18.6589 | 20.5514 | 22.6401 | 24.9454 | 27.4903 | 30.2997 | 33.4016 | 36.8267 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0.30471 | 0.52909 | 0.77583 | 1.0472 | 1.3458 | 1.6743 | 2.0359 | 2.4339 | 2.8721 | 3.3547 | 3.8863 | 4.4718 | 5.117 | 5.8279 | 6.6115 | 7.4753 | 8.4276 | 9.0704 | 9.4227 | 9.5939 | 9.4778 | 8.9207 | 7.7016 | 5.5032 | 1.871 | -3.8452 | -12.5749 | -25.646 | -44.9552 | -73.2111 |  | 5.4852 | 6.004 | 6.5745 | 7.2019 | 7.8922 | 8.6518 | 9.4878 | 10.408 | 11.4213 | 12.5371 | 13.766 | 15.1198 | 16.6115 | 18.2553 | 20.067 | 22.0641 | 24.2659 | 26.6937 | 29.3711 | 32.3242 | 35.5817 | 39.1755 | 43.1408 | 47.5165 | 52.3457 | 57.6759 | 63.5597 | 70.0553 | 77.2271 | 85.1462 |  | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0027977 | 0.0037086 | 0.0049589 | 0.0066829 | 0.0090698 | 0.012387 | 0.017011 | 0.023478 | 0.032546 | 0.045292 | 0.063244 | 0.088578 | 0.12439 |  | 5.4829 | 6.0016 | 6.5721 | 7.1996 | 7.8899 | 8.6495 | 9.4854 | 10.4057 | 11.4189 | 12.5347 | 13.7637 | 15.1175 | 16.6092 | 18.253 | 20.0647 | 22.0618 | 24.2636 | 26.6909 | 29.3674 | 32.3192 | 35.575 | 39.1664 | 43.1284 | 47.4995 | 52.3222 | 57.6433 | 63.5144 | 69.9921 | 77.1386 | 85.0218 |  | 208.1867 | 230.8116 | 255.691 | 283.0557 | 313.1604 | 346.2865 | 382.7448 | 422.8784 | 467.0663 | 515.7272 | 569.3234 | 628.3659 | 693.4192 | 765.1069 | 844.1182 | 931.2146 | 1027.2377 | 1127.0069 | 1231.6806 | 1343.8694 | 1463.0473 | 1588.0914 | 1716.9914 | 1846.4305 | 1971.1857 | 2083.2652 | 2170.6734 | 2215.6423 | 2192.0978 | 2062.0343
| TRUE | 1549 | 22006094 | FB | Blank | 11 | BUS NO.2 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.033587 | 2190 |  | 9.9 | 0.0088019 | 0.00083024 | 0.0079716 | 48.8669 | 265.6753 | 314.5422 | 29.6986 | 3.5299 | 8.1615 |  | 14.217 | 0.023831 | 0.0022479 | 0.021583 | 132.3088 | 719.325 | 851.6338 | 80.4099 | 9.5574 | 22.0975 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.0023374 |  | 355.9322 | 963.6986 | 45.241 | 918.4575 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.00091573 | 0.0010104 | 0.0011153 | 0.0012316 | 0.0013604 | 0.0015032 | 0.0016615 | 0.0018371 | 0.0020319 | 0.0022479 | 0.0024876 | 0.0027536 | 0.0030488 | 0.0033765 | 0.0037403 | 0.0041442 | 0.0045928 | 0.005091 | 0.0056445 | 0.0062593 | 0.0069424 | 0.0077015 | 0.0085451 | 0.0094827 | 0.010525 | 0.011683 | 0.012971 | 0.014404 | 0.015546 | 0.015546 | 392.5858 | 433.1824 | 478.1561 | 527.9895 | 583.2193 | 644.4421 | 712.3213 | 787.5947 | 871.0829 | 963.6986 | 1066.457 | 1180.4875 | 1307.0464 | 1447.5317 | 1603.4987 | 1776.678 | 1968.9954 | 2182.5942 | 2419.8595 | 2683.4461 | 2976.3087 | 3301.7362 | 3663.3897 | 4065.3448 | 4512.1387 | 5008.8225 | 5561.0201 | 6174.9932 | 6664.7992 | 6664.7992 |  | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 37.1408 | 49.2323 | 65.8303 | 88.7169 | 120.4036 | 164.4363 | 225.8289 | 311.6815 | 432.061 | 601.2576 | 839.5773 | 1175.9004 | 1651.3365 |  | 53.8992 | 59.4728 | 65.6473 | 72.4891 | 80.0718 | 88.4772 | 97.7965 | 108.131 | 119.5933 | 132.3088 | 146.4168 | 162.0723 | 179.4479 | 198.7356 | 220.1487 | 243.9249 | 270.3287 | 299.6543 | 332.2291 | 368.4176 | 408.6255 | 453.3043 | 502.9567 | 558.1422 | 619.4838 | 687.6748 | 763.4875 | 847.7816 | 915.0284 | 915.0284 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 39.6873 | 45.2609 | 51.4355 | 58.2772 | 65.8599 | 74.2653 | 83.5846 | 93.9191 | 105.3814 | 118.0969 | 132.2049 | 147.8604 | 165.2361 | 184.5237 | 205.9368 | 229.713 | 256.1168 | 282.6435 | 309.6803 | 338.2669 | 367.9926 | 398.1587 | 427.6438 | 454.711 | 476.7315 | 489.788 | 488.1075 | 463.2495 | 376.458 | 158.705 |  | 293.0344 | 323.3365 | 356.9058 | 394.1026 | 435.3273 | 481.0252 | 531.6917 | 587.8773 | 650.1947 | 719.325 | 796.0261 | 881.1408 | 975.6071 | 1080.4683 | 1196.8854 | 1326.1501 | 1469.6999 | 1629.1345 | 1806.2344 | 2002.981 | 2221.5798 | 2464.4858 | 2734.4317 | 3034.4595 | 3367.9559 | 3738.6912 | 4150.8632 | 4609.1457 | 4974.7473 | 4974.7473 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 292.9583 | 323.2604 | 356.8298 | 394.0265 | 435.2512 | 480.9491 | 531.6156 | 587.8013 | 650.1186 | 719.2489 | 795.95 | 881.0648 | 975.531 | 1080.3922 | 1196.8093 | 1326.074 | 1469.6238 | 1629.0435 | 1806.1137 | 2002.8196 | 2221.3623 | 2464.1906 | 2734.0285 | 3033.9057 | 3367.1916 | 3737.6318 | 4149.3889 | 4607.087 | 4971.8639 | 4970.698 |  | 332.6456 | 368.5213 | 408.2652 | 452.3037 | 501.1111 | 555.2145 | 615.2002 | 681.7204 | 755.5001 | 837.3458 | 928.1549 | 1028.9252 | 1140.7671 | 1264.9159 | 1402.7461 | 1555.787 | 1725.7406 | 1911.687 | 2115.794 | 2341.0865 | 2589.3549 | 2862.3492 | 3161.6722 | 3488.6168 | 3843.9231 | 4227.4197 | 4637.4963 | 5070.3364 | 5348.3218 | 5129.403 |  | 32.7569 | 36.1442 | 39.8968 | 44.0548 | 48.6631 | 53.7715 | 59.4352 | 65.716 | 72.6821 | 80.4099 | 88.9839 | 98.4985 | 109.0584 | 120.7803 | 133.794 | 148.2439 | 164.2906 | 182.1131 | 201.9102 | 223.9036 | 248.3397 | 275.4929 | 305.6689 | 339.2075 | 376.4875 | 417.9302 | 464.0049 | 515.2341 | 556.1029 | 556.1029 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 18.0858 | 21.4731 | 25.2256 | 29.3837 | 33.992 | 39.1003 | 44.7641 | 51.0448 | 58.011 | 65.7387 | 74.3128 | 83.8273 | 94.3873 | 106.1092 | 119.1229 | 133.5728 | 149.6195 | 164.5526 | 178.6328 | 192.7785 | 206.3937 | 218.5653 | 227.9223 | 232.4341 | 229.1223 | 213.6488 | 179.7261 | 118.2761 | 0.12902 | -224.6605 |  | 3.8934 | 4.2961 | 4.7421 | 5.2363 | 5.784 | 6.3912 | 7.0644 | 7.8109 | 8.6389 | 9.5574 | 10.5765 | 11.7074 | 12.9625 | 14.3558 | 15.9026 | 17.6201 | 19.5274 | 21.6457 | 23.9988 | 26.6129 | 29.5173 | 32.7447 | 36.3314 | 40.3177 | 44.7488 | 49.6746 | 55.151 | 61.24 | 66.0976 | 66.0976 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 1.8257 | 2.2284 | 2.6744 | 3.1686 | 3.7163 | 4.3235 | 4.9967 | 5.7432 | 6.5712 | 7.4897 | 8.5088 | 9.6397 | 10.8948 | 12.2881 | 13.8349 | 15.5524 | 17.4597 | 19.1708 | 20.7181 | 22.2262 | 23.6056 | 24.7215 | 25.3741 | 25.2695 | 23.9797 | 20.884 | 15.0858 | 5.2943 | -12.2592 | -43.9402 |  | 9.0019 | 9.9328 | 10.9641 | 12.1067 | 13.3731 | 14.777 | 16.3334 | 18.0594 | 19.9738 | 22.0975 | 24.4537 | 27.0684 | 29.9704 | 33.1917 | 36.768 | 40.739 | 45.1488 | 50.0466 | 55.4871 | 61.5311 | 68.2464 | 75.7084 | 84.0011 | 93.2178 | 103.4628 | 114.8517 | 127.5135 | 141.5918 | 152.823 | 152.823 |  | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0027977 | 0.0037086 | 0.0049589 | 0.0066829 | 0.0090698 | 0.012387 | 0.017011 | 0.023478 | 0.032546 | 0.045292 | 0.063244 | 0.088578 | 0.12439 |  | 8.9996 | 9.9305 | 10.9617 | 12.1044 | 13.3708 | 14.7746 | 16.3311 | 18.0571 | 19.9715 | 22.0951 | 24.4514 | 27.0661 | 29.9681 | 33.1894 | 36.7657 | 40.7367 | 45.1465 | 50.0438 | 55.4834 | 61.5261 | 68.2397 | 75.6993 | 83.9887 | 93.2008 | 103.4393 | 114.8191 | 127.4682 | 141.5286 | 152.7344 | 152.6986 |  | 361.5567 | 402.1533 | 447.127 | 496.9604 | 552.1902 | 613.4129 | 681.2921 | 756.5655 | 840.0537 | 932.6694 | 1035.4278 | 1149.4583 | 1276.0173 | 1416.5026 | 1572.4695 | 1745.6488 | 1937.9663 | 2145.4543 | 2370.6283 | 2617.6173 | 2887.5939 | 3181.3354 | 3498.9572 | 3839.5211 | 4200.4644 | 4576.7716 | 4959.7765 | 5335.4354 | 5488.926 | 5013.501
| TRUE | 1550 | 22006097 | FB | Blank | 11 | BUS NO.3 | RESIDUAL BUS PROT | Blank | GEC | CDG14_984 | CDG14 984 | CDG14 | Electromechanical |  | 0.033587 | 2190 |  | 8.25 | 0.0054067 | 0.00050998 | 0.0048967 | 30.0172 | 163.1947 | 193.2118 | 18.2427 | 2.1683 | 5.0133 |  | 11.5885 | 0.013521 | 0.0012753 | 0.012245 | 75.0657 | 408.1105 | 483.1761 | 45.6207 | 5.4224 | 12.5371 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.0023374 |  | 218.6362 | 546.7563 | 45.241 | 501.5153 |  | 0.03398 |  | 8.5352 | 8.8302 | 9.1354 | 9.4511 | 9.7778 | 10.1158 | 10.4654 | 10.8271 | 11.2014 | 11.5885 | 11.9891 | 12.4035 | 12.8322 | 13.2757 | 13.7346 | 14.2093 | 14.7004 | 15.2085 | 15.7342 | 16.278 | 16.8407 | 17.4227 | 18.0249 | 18.6479 | 19.2925 | 19.9593 | 20.6492 | 21.3629 | 22.1013 | 22.8652 |  | 0.0059156 | 0.0064751 | 0.0070903 | 0.007767 | 0.0085115 | 0.0093307 | 0.010232 | 0.011225 | 0.012317 | 0.013521 | 0.014846 | 0.016306 | 0.017915 | 0.019688 | 0.021642 | 0.023795 | 0.02617 | 0.028788 | 0.031676 | 0.034861 | 0.038374 | 0.042249 | 0.046526 | 0.051245 | 0.056453 | 0.062201 | 0.068547 | 0.075552 | 0.083287 | 0.091827 |  | 0.00055799 | 0.00061076 | 0.00066879 | 0.00073262 | 0.00080284 | 0.00088011 | 0.00096516 | 0.0010588 | 0.0011618 | 0.0012753 | 0.0014004 | 0.0015381 | 0.0016898 | 0.001857 | 0.0020413 | 0.0022445 | 0.0024685 | 0.0027154 | 0.0029878 | 0.0032882 | 0.0036196 | 0.0039852 | 0.0043885 | 0.0048337 | 0.0053249 | 0.0058671 | 0.0064657 | 0.0071265 | 0.007856 | 0.0086616 | 239.2158 | 261.8408 | 286.7202 | 314.0848 | 344.1895 | 377.3157 | 413.774 | 453.9075 | 498.0954 | 546.7563 | 600.3525 | 659.3951 | 724.4484 | 796.1361 | 875.1473 | 962.2437 | 1058.2668 | 1164.1468 | 1280.9118 | 1409.6982 | 1551.7621 | 1708.4922 | 1881.4238 | 2072.2542 | 2282.86 | 2515.3161 | 2771.9171 | 3055.2001 | 3367.9709 | 3713.3325 |  | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 37.1408 | 49.2323 | 65.8303 | 88.7169 | 120.4036 | 164.4363 | 225.8289 | 311.6815 | 432.061 | 601.2576 | 839.5773 | 1175.9004 | 1651.3365 |  | 32.8426 | 35.9488 | 39.3646 | 43.1216 | 47.2547 | 51.8027 | 56.8081 | 62.3182 | 68.3849 | 75.0657 | 82.424 | 90.5301 | 99.4615 | 109.3037 | 120.1514 | 132.1091 | 145.2923 | 159.8289 | 175.8599 | 193.5413 | 213.0456 | 234.5635 | 258.3058 | 284.5054 | 313.42 | 345.3346 | 380.564 | 419.4567 | 462.3979 | 509.8135 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 18.6307 | 21.7369 | 25.1527 | 28.9097 | 33.0428 | 37.5908 | 42.5963 | 48.1063 | 54.173 | 60.8538 | 68.2121 | 76.3183 | 85.2496 | 95.0918 | 105.9395 | 117.8972 | 131.0804 | 142.8181 | 153.3111 | 163.3906 | 172.4127 | 179.4179 | 182.9928 | 181.0742 | 170.6678 | 147.4477 | 105.1839 | 34.9246 | -76.1725 | -246.5099 |  | 178.5557 | 195.4435 | 214.014 | 234.4396 | 256.9104 | 281.6364 | 308.8496 | 338.8062 | 371.789 | 408.1105 | 448.1159 | 492.1865 | 540.7436 | 594.2528 | 653.2285 | 718.2391 | 789.9128 | 868.9438 | 956.0997 | 1052.2286 | 1158.2681 | 1275.2548 | 1404.3346 | 1546.7744 | 1703.975 | 1877.4852 | 2069.0176 | 2280.4661 | 2513.9249 | 2771.71 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 178.4796 | 195.3674 | 213.9379 | 234.3635 | 256.8343 | 281.5603 | 308.7736 | 338.7301 | 371.7129 | 408.0344 | 448.0398 | 492.1104 | 540.6675 | 594.1767 | 653.1524 | 718.163 | 789.8367 | 868.8528 | 955.979 | 1052.0672 | 1158.0506 | 1274.9596 | 1403.9314 | 1546.2207 | 1703.2108 | 1876.4258 | 2067.5433 | 2278.4074 | 2511.0414 | 2767.6608 |  | 197.1103 | 217.1043 | 239.0906 | 263.2731 | 289.8771 | 319.1511 | 351.3698 | 386.8364 | 425.8859 | 468.8882 | 516.2519 | 568.4286 | 625.9171 | 689.2685 | 759.0919 | 836.0602 | 920.9171 | 1011.6709 | 1109.2901 | 1215.4577 | 1330.4633 | 1454.3774 | 1586.9242 | 1727.2949 | 1873.8786 | 2023.8735 | 2172.7272 | 2313.332 | 2434.8689 | 2521.1509 |  | 19.9599 | 21.8477 | 23.9236 | 26.2069 | 28.7188 | 31.4828 | 34.5248 | 37.8735 | 41.5605 | 45.6207 | 50.0927 | 55.0191 | 60.4471 | 66.4286 | 73.0213 | 80.2885 | 88.3005 | 97.135 | 106.8778 | 117.6235 | 129.4772 | 142.5546 | 156.9838 | 172.9064 | 190.4791 | 209.875 | 231.2855 | 254.9223 | 281.0195 | 309.836 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 5.2887 | 7.1765 | 9.2525 | 11.5357 | 14.0476 | 16.8116 | 19.8537 | 23.2024 | 26.8894 | 30.9496 | 35.4216 | 40.348 | 45.776 | 51.7575 | 58.3501 | 65.6173 | 73.6294 | 79.5746 | 83.6004 | 86.4985 | 87.5312 | 85.6269 | 79.2371 | 66.1329 | 43.114 | 5.5936 | -52.9933 | -142.0357 | -274.9544 | -470.9273 |  | 2.3724 | 2.5968 | 2.8435 | 3.1149 | 3.4135 | 3.742 | 4.1036 | 4.5016 | 4.9398 | 5.4224 | 5.9539 | 6.5395 | 7.1847 | 7.8956 | 8.6792 | 9.543 | 10.4953 | 11.5453 | 12.7033 | 13.9806 | 15.3895 | 16.9438 | 18.6589 | 20.5514 | 22.6401 | 24.9454 | 27.4903 | 30.2997 | 33.4016 | 36.8267 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0.30471 | 0.52909 | 0.77583 | 1.0472 | 1.3458 | 1.6743 | 2.0359 | 2.4339 | 2.8721 | 3.3547 | 3.8863 | 4.4718 | 5.117 | 5.8279 | 6.6115 | 7.4753 | 8.4276 | 9.0704 | 9.4227 | 9.5939 | 9.4778 | 8.9207 | 7.7016 | 5.5032 | 1.871 | -3.8452 | -12.5749 | -25.646 | -44.9552 | -73.2111 |  | 5.4852 | 6.004 | 6.5745 | 7.2019 | 7.8922 | 8.6518 | 9.4878 | 10.408 | 11.4213 | 12.5371 | 13.766 | 15.1198 | 16.6115 | 18.2553 | 20.067 | 22.0641 | 24.2659 | 26.6937 | 29.3711 | 32.3242 | 35.5817 | 39.1755 | 43.1408 | 47.5165 | 52.3457 | 57.6759 | 63.5597 | 70.0553 | 77.2271 | 85.1462 |  | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0027977 | 0.0037086 | 0.0049589 | 0.0066829 | 0.0090698 | 0.012387 | 0.017011 | 0.023478 | 0.032546 | 0.045292 | 0.063244 | 0.088578 | 0.12439 |  | 5.4829 | 6.0016 | 6.5721 | 7.1996 | 7.8899 | 8.6495 | 9.4854 | 10.4057 | 11.4189 | 12.5347 | 13.7637 | 15.1175 | 16.6092 | 18.253 | 20.0647 | 22.0618 | 24.2636 | 26.6909 | 29.3674 | 32.3192 | 35.575 | 39.1664 | 43.1284 | 47.4995 | 52.3222 | 57.6433 | 63.5144 | 69.9921 | 77.1386 | 85.0218 |  | 208.1867 | 230.8116 | 255.691 | 283.0557 | 313.1604 | 346.2865 | 382.7448 | 422.8784 | 467.0663 | 515.7272 | 569.3234 | 628.3659 | 693.4192 | 765.1069 | 844.1182 | 931.2146 | 1027.2377 | 1127.0069 | 1231.6806 | 1343.8694 | 1463.0473 | 1588.0914 | 1716.9914 | 1846.4305 | 1971.1857 | 2083.2652 | 2170.6734 | 2215.6423 | 2192.0978 | 2062.0343
| TRUE | 1551 | 22006099 | FB | Blank | 11 | BUS NO.3 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.033587 | 2190 |  | 9.9 | 0.0088019 | 0.00083024 | 0.0079716 | 48.8669 | 265.6753 | 314.5422 | 29.6986 | 3.5299 | 8.1615 |  | 14.217 | 0.023831 | 0.0022479 | 0.021583 | 132.3088 | 719.325 | 851.6338 | 80.4099 | 9.5574 | 22.0975 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.076088 | 28.4999 | 14.6711 | 2.0677 | 0.0023374 |  | 355.9322 | 963.6986 | 45.241 | 918.4575 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.00091573 | 0.0010104 | 0.0011153 | 0.0012316 | 0.0013604 | 0.0015032 | 0.0016615 | 0.0018371 | 0.0020319 | 0.0022479 | 0.0024876 | 0.0027536 | 0.0030488 | 0.0033765 | 0.0037403 | 0.0041442 | 0.0045928 | 0.005091 | 0.0056445 | 0.0062593 | 0.0069424 | 0.0077015 | 0.0085451 | 0.0094827 | 0.010525 | 0.011683 | 0.012971 | 0.014404 | 0.015546 | 0.015546 | 392.5858 | 433.1824 | 478.1561 | 527.9895 | 583.2193 | 644.4421 | 712.3213 | 787.5947 | 871.0829 | 963.6986 | 1066.457 | 1180.4875 | 1307.0464 | 1447.5317 | 1603.4987 | 1776.678 | 1968.9954 | 2182.5942 | 2419.8595 | 2683.4461 | 2976.3087 | 3301.7362 | 3663.3897 | 4065.3448 | 4512.1387 | 5008.8225 | 5561.0201 | 6174.9932 | 6664.7992 | 6664.7992 |  | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 31.0299 | 37.1408 | 49.2323 | 65.8303 | 88.7169 | 120.4036 | 164.4363 | 225.8289 | 311.6815 | 432.061 | 601.2576 | 839.5773 | 1175.9004 | 1651.3365 |  | 53.8992 | 59.4728 | 65.6473 | 72.4891 | 80.0718 | 88.4772 | 97.7965 | 108.131 | 119.5933 | 132.3088 | 146.4168 | 162.0723 | 179.4479 | 198.7356 | 220.1487 | 243.9249 | 270.3287 | 299.6543 | 332.2291 | 368.4176 | 408.6255 | 453.3043 | 502.9567 | 558.1422 | 619.4838 | 687.6748 | 763.4875 | 847.7816 | 915.0284 | 915.0284 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 39.6873 | 45.2609 | 51.4355 | 58.2772 | 65.8599 | 74.2653 | 83.5846 | 93.9191 | 105.3814 | 118.0969 | 132.2049 | 147.8604 | 165.2361 | 184.5237 | 205.9368 | 229.713 | 256.1168 | 282.6435 | 309.6803 | 338.2669 | 367.9926 | 398.1587 | 427.6438 | 454.711 | 476.7315 | 489.788 | 488.1075 | 463.2495 | 376.458 | 158.705 |  | 293.0344 | 323.3365 | 356.9058 | 394.1026 | 435.3273 | 481.0252 | 531.6917 | 587.8773 | 650.1947 | 719.325 | 796.0261 | 881.1408 | 975.6071 | 1080.4683 | 1196.8854 | 1326.1501 | 1469.6999 | 1629.1345 | 1806.2344 | 2002.981 | 2221.5798 | 2464.4858 | 2734.4317 | 3034.4595 | 3367.9559 | 3738.6912 | 4150.8632 | 4609.1457 | 4974.7473 | 4974.7473 |  | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.076088 | 0.091073 | 0.12072 | 0.16142 | 0.21754 | 0.29524 | 0.40321 | 0.55376 | 0.76428 | 1.0595 | 1.4743 | 2.0587 | 2.8834 | 4.0492 |  | 292.9583 | 323.2604 | 356.8298 | 394.0265 | 435.2512 | 480.9491 | 531.6156 | 587.8013 | 650.1186 | 719.2489 | 795.95 | 881.0648 | 975.531 | 1080.3922 | 1196.8093 | 1326.074 | 1469.6238 | 1629.0435 | 1806.1137 | 2002.8196 | 2221.3623 | 2464.1906 | 2734.0285 | 3033.9057 | 3367.1916 | 3737.6318 | 4149.3889 | 4607.087 | 4971.8639 | 4970.698 |  | 332.6456 | 368.5213 | 408.2652 | 452.3037 | 501.1111 | 555.2145 | 615.2002 | 681.7204 | 755.5001 | 837.3458 | 928.1549 | 1028.9252 | 1140.7671 | 1264.9159 | 1402.7461 | 1555.787 | 1725.7406 | 1911.687 | 2115.794 | 2341.0865 | 2589.3549 | 2862.3492 | 3161.6722 | 3488.6168 | 3843.9231 | 4227.4197 | 4637.4963 | 5070.3364 | 5348.3218 | 5129.403 |  | 32.7569 | 36.1442 | 39.8968 | 44.0548 | 48.6631 | 53.7715 | 59.4352 | 65.716 | 72.6821 | 80.4099 | 88.9839 | 98.4985 | 109.0584 | 120.7803 | 133.794 | 148.2439 | 164.2906 | 182.1131 | 201.9102 | 223.9036 | 248.3397 | 275.4929 | 305.6689 | 339.2075 | 376.4875 | 417.9302 | 464.0049 | 515.2341 | 556.1029 | 556.1029 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 18.0858 | 21.4731 | 25.2256 | 29.3837 | 33.992 | 39.1003 | 44.7641 | 51.0448 | 58.011 | 65.7387 | 74.3128 | 83.8273 | 94.3873 | 106.1092 | 119.1229 | 133.5728 | 149.6195 | 164.5526 | 178.6328 | 192.7785 | 206.3937 | 218.5653 | 227.9223 | 232.4341 | 229.1223 | 213.6488 | 179.7261 | 118.2761 | 0.12902 | -224.6605 |  | 3.8934 | 4.2961 | 4.7421 | 5.2363 | 5.784 | 6.3912 | 7.0644 | 7.8109 | 8.6389 | 9.5574 | 10.5765 | 11.7074 | 12.9625 | 14.3558 | 15.9026 | 17.6201 | 19.5274 | 21.6457 | 23.9988 | 26.6129 | 29.5173 | 32.7447 | 36.3314 | 40.3177 | 44.7488 | 49.6746 | 55.151 | 61.24 | 66.0976 | 66.0976 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 1.8257 | 2.2284 | 2.6744 | 3.1686 | 3.7163 | 4.3235 | 4.9967 | 5.7432 | 6.5712 | 7.4897 | 8.5088 | 9.6397 | 10.8948 | 12.2881 | 13.8349 | 15.5524 | 17.4597 | 19.1708 | 20.7181 | 22.2262 | 23.6056 | 24.7215 | 25.3741 | 25.2695 | 23.9797 | 20.884 | 15.0858 | 5.2943 | -12.2592 | -43.9402 |  | 9.0019 | 9.9328 | 10.9641 | 12.1067 | 13.3731 | 14.777 | 16.3334 | 18.0594 | 19.9738 | 22.0975 | 24.4537 | 27.0684 | 29.9704 | 33.1917 | 36.768 | 40.739 | 45.1488 | 50.0466 | 55.4871 | 61.5311 | 68.2464 | 75.7084 | 84.0011 | 93.2178 | 103.4628 | 114.8517 | 127.5135 | 141.5918 | 152.823 | 152.823 |  | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0023374 | 0.0027977 | 0.0037086 | 0.0049589 | 0.0066829 | 0.0090698 | 0.012387 | 0.017011 | 0.023478 | 0.032546 | 0.045292 | 0.063244 | 0.088578 | 0.12439 |  | 8.9996 | 9.9305 | 10.9617 | 12.1044 | 13.3708 | 14.7746 | 16.3311 | 18.0571 | 19.9715 | 22.0951 | 24.4514 | 27.0661 | 29.9681 | 33.1894 | 36.7657 | 40.7367 | 45.1465 | 50.0438 | 55.4834 | 61.5261 | 68.2397 | 75.6993 | 83.9887 | 93.2008 | 103.4393 | 114.8191 | 127.4682 | 141.5286 | 152.7344 | 152.6986 |  | 361.5567 | 402.1533 | 447.127 | 496.9604 | 552.1902 | 613.4129 | 681.2921 | 756.5655 | 840.0537 | 932.6694 | 1035.4278 | 1149.4583 | 1276.0173 | 1416.5026 | 1572.4695 | 1745.6488 | 1937.9663 | 2145.4543 | 2370.6283 | 2617.6173 | 2887.5939 | 3181.3354 | 3498.9572 | 3839.5211 | 4200.4644 | 4576.7716 | 4959.7765 | 5335.4354 | 5488.926 | 5013.501
| TRUE | 1552 | 22006102 | FB | Blank | 11 | CAP NO.1 | CURRENT BALANCE | Blank | English Electric | CDG11_525 | CDG11 525 | CDG11 | Electromechanical |  | 0.2894 | 2190 |  | 9.9 | 0.0088019 | 0.0046268 | 0.0041751 | 50.955 | 1480.5706 | 1531.5256 | 51.2524 | 3.5679 | 45.4828 |  | 14.217 | 0.023831 | 0.012527 | 0.011304 | 137.9624 | 4008.6955 | 4146.6579 | 138.7677 | 9.6602 | 123.1461 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.02014 |  | 1631.8287 | 4418.232 | 45.8496 | 4372.3824 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0051032 | 0.005631 | 0.0062156 | 0.0068634 | 0.0075813 | 0.0083771 | 0.0092595 | 0.010238 | 0.011323 | 0.012527 | 0.013863 | 0.015345 | 0.01699 | 0.018817 | 0.020844 | 0.023095 | 0.025595 | 0.028372 | 0.031456 | 0.034882 | 0.038689 | 0.042919 | 0.047621 | 0.052846 | 0.058654 | 0.06511 | 0.072288 | 0.080269 | 0.086636 | 0.086636 | 1799.8731 | 1985.9948 | 2192.184 | 2420.6535 | 2673.8634 | 2954.549 | 3265.7521 | 3610.8552 | 3993.6204 | 4418.232 | 4889.3445 | 5412.1357 | 5992.3657 | 6636.4433 | 7351.4991 | 8145.4675 | 9027.1779 | 10006.4562 | 11094.2375 | 12302.6928 | 13645.3686 | 15137.3436 | 16795.4027 | 18638.2309 | 20686.6296 | 22963.757 | 25495.3963 | 28310.255 | 30555.8499 | 30555.8499 |  | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 37.8752 | 50.2059 | 67.132 | 90.4712 | 122.7845 | 167.6879 | 230.2945 | 317.8447 | 440.6046 | 613.147 | 856.1792 | 1199.1529 | 1683.9903 |  | 56.2023 | 62.0141 | 68.4525 | 75.5866 | 83.4933 | 92.2579 | 101.9754 | 112.7515 | 124.7036 | 137.9624 | 152.6732 | 168.9977 | 187.1158 | 207.2276 | 229.5557 | 254.3479 | 281.88 | 312.4586 | 346.4254 | 384.1602 | 426.0862 | 472.6742 | 524.4482 | 581.9919 | 645.9545 | 717.0594 | 796.1117 | 884.0076 | 954.1279 | 954.1279 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 41.9899 | 47.8017 | 54.2401 | 61.3742 | 69.2809 | 78.0455 | 87.763 | 98.5391 | 110.4912 | 123.75 | 138.4608 | 154.7854 | 172.9034 | 193.0152 | 215.3433 | 240.1356 | 267.6676 | 295.4473 | 323.8758 | 354.0084 | 385.4519 | 417.5266 | 449.1327 | 478.557 | 503.1973 | 519.1656 | 520.7219 | 499.462 | 415.5386 | 197.778 |  | 1633.0386 | 1801.9082 | 1988.9852 | 2196.2773 | 2426.0166 | 2680.6848 | 2963.0417 | 3276.1564 | 3623.4422 | 4008.6955 | 4436.1395 | 4910.4719 | 5436.9191 | 6021.2956 | 6670.0711 | 7390.4447 | 8190.4273 | 9078.9339 | 10065.8862 | 11162.3269 | 12380.5468 | 13734.2271 | 15238.5968 | 16910.6089 | 18769.1366 | 20835.1916 | 23132.1673 | 25686.11 | 27723.5553 | 27723.5553 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 1632.383 | 1801.2526 | 1988.3296 | 2195.6217 | 2425.361 | 2680.0292 | 2962.3861 | 3275.5008 | 3622.7866 | 4008.0399 | 4435.4839 | 4909.8163 | 5436.2635 | 6020.6399 | 6669.4155 | 7389.7891 | 8189.7717 | 9078.1492 | 10064.846 | 11160.936 | 12378.6724 | 13731.6832 | 15235.1226 | 16905.8376 | 18762.5514 | 20826.063 | 23119.4639 | 25668.3713 | 27698.7108 | 27688.6658 |  | 1674.3729 | 1849.0543 | 2042.5697 | 2256.996 | 2494.6419 | 2758.0747 | 3050.1491 | 3374.0399 | 3733.2778 | 4131.79 | 4573.9448 | 5064.6017 | 5609.1669 | 6213.6552 | 6884.7588 | 7629.9247 | 8457.4393 | 9373.5965 | 10388.7218 | 11514.9444 | 12764.1243 | 14149.2098 | 15684.2552 | 17384.3946 | 19265.7487 | 21345.2286 | 23640.1858 | 26167.8333 | 28114.2494 | 27886.4438 |  | 56.5304 | 62.3761 | 68.8521 | 76.0278 | 83.9806 | 92.7964 | 102.5707 | 113.4097 | 125.4315 | 138.7677 | 153.5644 | 169.9842 | 188.2081 | 208.4373 | 230.8957 | 255.8327 | 283.5254 | 314.2826 | 348.4476 | 386.4027 | 428.5734 | 475.4334 | 527.5097 | 585.3892 | 649.7252 | 721.2452 | 800.7589 | 889.1679 | 959.6975 | 959.6975 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 41.849 | 47.6947 | 54.1707 | 61.3464 | 69.2992 | 78.115 | 87.8893 | 98.7282 | 110.7501 | 124.0863 | 138.883 | 155.3028 | 173.5267 | 193.7559 | 216.2143 | 241.1513 | 268.844 | 296.7098 | 325.1539 | 355.2559 | 386.5981 | 418.4658 | 449.7085 | 478.5409 | 502.2568 | 516.8206 | 516.2809 | 491.9317 | 403.334 | 178.3869 |  | 3.9353 | 4.3423 | 4.7931 | 5.2926 | 5.8462 | 6.4599 | 7.1404 | 7.8949 | 8.7318 | 9.6602 | 10.6903 | 11.8333 | 13.1019 | 14.5102 | 16.0736 | 17.8096 | 19.7374 | 21.8785 | 24.2569 | 26.8991 | 29.8348 | 33.0969 | 36.7221 | 40.7514 | 45.2301 | 50.2089 | 55.7441 | 61.8987 | 66.8085 | 66.8085 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.8676 | 2.2745 | 2.7254 | 3.2249 | 3.7785 | 4.3922 | 5.0727 | 5.8272 | 6.6641 | 7.5925 | 8.6225 | 9.7656 | 11.0342 | 12.4425 | 14.0059 | 15.7419 | 17.6697 | 19.4036 | 20.9762 | 22.5124 | 23.923 | 25.0736 | 25.7647 | 25.703 | 24.4608 | 21.418 | 15.6786 | 5.9524 | -11.549 | -43.2302 |  | 50.1665 | 55.3542 | 61.1011 | 67.4691 | 74.5266 | 82.35 | 91.0239 | 100.6427 | 111.3112 | 123.1461 | 136.2771 | 150.8485 | 167.0208 | 184.9727 | 204.9029 | 227.0326 | 251.6079 | 278.9026 | 309.2215 | 342.9039 | 380.3273 | 421.912 | 468.1259 | 519.4897 | 576.5832 | 640.0519 | 710.6144 | 789.0709 | 851.6607 | 851.6607 |  | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.024106 | 0.031954 | 0.042727 | 0.057582 | 0.078148 | 0.10673 | 0.14657 | 0.2023 | 0.28043 | 0.39025 | 0.54493 | 0.76322 | 1.0718 |  | 50.1464 | 55.334 | 61.081 | 67.4489 | 74.5065 | 82.3298 | 91.0038 | 100.6226 | 111.2911 | 123.126 | 136.257 | 150.8283 | 167.0006 | 184.9525 | 204.8828 | 227.0125 | 251.5877 | 278.8785 | 309.1895 | 342.8612 | 380.2697 | 421.8339 | 468.0191 | 519.3431 | 576.3809 | 639.7714 | 710.2241 | 788.5259 | 850.8974 | 850.5889 |  | 1768.2359 | 1954.3575 | 2160.5467 | 2389.0162 | 2642.2261 | 2922.9117 | 3234.1148 | 3579.2179 | 3961.9831 | 4386.5947 | 4857.7073 | 5380.4984 | 5960.7285 | 6604.806 | 7319.8618 | 8113.8302 | 8995.5407 | 9968.5883 | 11044.0415 | 12235.5739 | 13554.9151 | 15014.5831 | 16627.7476 | 18407.9816 | 20368.8472 | 22523.2386 | 24882.3694 | 27454.2434 | 29356.9319 | 28872.1894
| TRUE | 1553 | 22006103 | FB | Blank | 11 | CAP NO.1 | CURRENT BALANCE | Blank | English Electric | CDG11_525 | CDG11 525 | CDG11 | Electromechanical |  | 0.2894 | 2190 |  | 9.9 | 0.0088019 | 0.0046268 | 0.0041751 | 50.955 | 1480.5706 | 1531.5256 | 51.2524 | 3.5679 | 45.4828 |  | 14.217 | 0.023831 | 0.012527 | 0.011304 | 137.9624 | 4008.6955 | 4146.6579 | 138.7677 | 9.6602 | 123.1461 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.02014 |  | 1631.8287 | 4418.232 | 45.8496 | 4372.3824 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0051032 | 0.005631 | 0.0062156 | 0.0068634 | 0.0075813 | 0.0083771 | 0.0092595 | 0.010238 | 0.011323 | 0.012527 | 0.013863 | 0.015345 | 0.01699 | 0.018817 | 0.020844 | 0.023095 | 0.025595 | 0.028372 | 0.031456 | 0.034882 | 0.038689 | 0.042919 | 0.047621 | 0.052846 | 0.058654 | 0.06511 | 0.072288 | 0.080269 | 0.086636 | 0.086636 | 1799.8731 | 1985.9948 | 2192.184 | 2420.6535 | 2673.8634 | 2954.549 | 3265.7521 | 3610.8552 | 3993.6204 | 4418.232 | 4889.3445 | 5412.1357 | 5992.3657 | 6636.4433 | 7351.4991 | 8145.4675 | 9027.1779 | 10006.4562 | 11094.2375 | 12302.6928 | 13645.3686 | 15137.3436 | 16795.4027 | 18638.2309 | 20686.6296 | 22963.757 | 25495.3963 | 28310.255 | 30555.8499 | 30555.8499 |  | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 37.8752 | 50.2059 | 67.132 | 90.4712 | 122.7845 | 167.6879 | 230.2945 | 317.8447 | 440.6046 | 613.147 | 856.1792 | 1199.1529 | 1683.9903 |  | 56.2023 | 62.0141 | 68.4525 | 75.5866 | 83.4933 | 92.2579 | 101.9754 | 112.7515 | 124.7036 | 137.9624 | 152.6732 | 168.9977 | 187.1158 | 207.2276 | 229.5557 | 254.3479 | 281.88 | 312.4586 | 346.4254 | 384.1602 | 426.0862 | 472.6742 | 524.4482 | 581.9919 | 645.9545 | 717.0594 | 796.1117 | 884.0076 | 954.1279 | 954.1279 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 41.9899 | 47.8017 | 54.2401 | 61.3742 | 69.2809 | 78.0455 | 87.763 | 98.5391 | 110.4912 | 123.75 | 138.4608 | 154.7854 | 172.9034 | 193.0152 | 215.3433 | 240.1356 | 267.6676 | 295.4473 | 323.8758 | 354.0084 | 385.4519 | 417.5266 | 449.1327 | 478.557 | 503.1973 | 519.1656 | 520.7219 | 499.462 | 415.5386 | 197.778 |  | 1633.0386 | 1801.9082 | 1988.9852 | 2196.2773 | 2426.0166 | 2680.6848 | 2963.0417 | 3276.1564 | 3623.4422 | 4008.6955 | 4436.1395 | 4910.4719 | 5436.9191 | 6021.2956 | 6670.0711 | 7390.4447 | 8190.4273 | 9078.9339 | 10065.8862 | 11162.3269 | 12380.5468 | 13734.2271 | 15238.5968 | 16910.6089 | 18769.1366 | 20835.1916 | 23132.1673 | 25686.11 | 27723.5553 | 27723.5553 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 1632.383 | 1801.2526 | 1988.3296 | 2195.6217 | 2425.361 | 2680.0292 | 2962.3861 | 3275.5008 | 3622.7866 | 4008.0399 | 4435.4839 | 4909.8163 | 5436.2635 | 6020.6399 | 6669.4155 | 7389.7891 | 8189.7717 | 9078.1492 | 10064.846 | 11160.936 | 12378.6724 | 13731.6832 | 15235.1226 | 16905.8376 | 18762.5514 | 20826.063 | 23119.4639 | 25668.3713 | 27698.7108 | 27688.6658 |  | 1674.3729 | 1849.0543 | 2042.5697 | 2256.996 | 2494.6419 | 2758.0747 | 3050.1491 | 3374.0399 | 3733.2778 | 4131.79 | 4573.9448 | 5064.6017 | 5609.1669 | 6213.6552 | 6884.7588 | 7629.9247 | 8457.4393 | 9373.5965 | 10388.7218 | 11514.9444 | 12764.1243 | 14149.2098 | 15684.2552 | 17384.3946 | 19265.7487 | 21345.2286 | 23640.1858 | 26167.8333 | 28114.2494 | 27886.4438 |  | 56.5304 | 62.3761 | 68.8521 | 76.0278 | 83.9806 | 92.7964 | 102.5707 | 113.4097 | 125.4315 | 138.7677 | 153.5644 | 169.9842 | 188.2081 | 208.4373 | 230.8957 | 255.8327 | 283.5254 | 314.2826 | 348.4476 | 386.4027 | 428.5734 | 475.4334 | 527.5097 | 585.3892 | 649.7252 | 721.2452 | 800.7589 | 889.1679 | 959.6975 | 959.6975 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 41.849 | 47.6947 | 54.1707 | 61.3464 | 69.2992 | 78.115 | 87.8893 | 98.7282 | 110.7501 | 124.0863 | 138.883 | 155.3028 | 173.5267 | 193.7559 | 216.2143 | 241.1513 | 268.844 | 296.7098 | 325.1539 | 355.2559 | 386.5981 | 418.4658 | 449.7085 | 478.5409 | 502.2568 | 516.8206 | 516.2809 | 491.9317 | 403.334 | 178.3869 |  | 3.9353 | 4.3423 | 4.7931 | 5.2926 | 5.8462 | 6.4599 | 7.1404 | 7.8949 | 8.7318 | 9.6602 | 10.6903 | 11.8333 | 13.1019 | 14.5102 | 16.0736 | 17.8096 | 19.7374 | 21.8785 | 24.2569 | 26.8991 | 29.8348 | 33.0969 | 36.7221 | 40.7514 | 45.2301 | 50.2089 | 55.7441 | 61.8987 | 66.8085 | 66.8085 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.8676 | 2.2745 | 2.7254 | 3.2249 | 3.7785 | 4.3922 | 5.0727 | 5.8272 | 6.6641 | 7.5925 | 8.6225 | 9.7656 | 11.0342 | 12.4425 | 14.0059 | 15.7419 | 17.6697 | 19.4036 | 20.9762 | 22.5124 | 23.923 | 25.0736 | 25.7647 | 25.703 | 24.4608 | 21.418 | 15.6786 | 5.9524 | -11.549 | -43.2302 |  | 50.1665 | 55.3542 | 61.1011 | 67.4691 | 74.5266 | 82.35 | 91.0239 | 100.6427 | 111.3112 | 123.1461 | 136.2771 | 150.8485 | 167.0208 | 184.9727 | 204.9029 | 227.0326 | 251.6079 | 278.9026 | 309.2215 | 342.9039 | 380.3273 | 421.912 | 468.1259 | 519.4897 | 576.5832 | 640.0519 | 710.6144 | 789.0709 | 851.6607 | 851.6607 |  | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.024106 | 0.031954 | 0.042727 | 0.057582 | 0.078148 | 0.10673 | 0.14657 | 0.2023 | 0.28043 | 0.39025 | 0.54493 | 0.76322 | 1.0718 |  | 50.1464 | 55.334 | 61.081 | 67.4489 | 74.5065 | 82.3298 | 91.0038 | 100.6226 | 111.2911 | 123.126 | 136.257 | 150.8283 | 167.0006 | 184.9525 | 204.8828 | 227.0125 | 251.5877 | 278.8785 | 309.1895 | 342.8612 | 380.2697 | 421.8339 | 468.0191 | 519.3431 | 576.3809 | 639.7714 | 710.2241 | 788.5259 | 850.8974 | 850.5889 |  | 1768.2359 | 1954.3575 | 2160.5467 | 2389.0162 | 2642.2261 | 2922.9117 | 3234.1148 | 3579.2179 | 3961.9831 | 4386.5947 | 4857.7073 | 5380.4984 | 5960.7285 | 6604.806 | 7319.8618 | 8113.8302 | 8995.5407 | 9968.5883 | 11044.0415 | 12235.5739 | 13554.9151 | 15014.5831 | 16627.7476 | 18407.9816 | 20368.8472 | 22523.2386 | 24882.3694 | 27454.2434 | 29356.9319 | 28872.1894
| TRUE | 1554 | 22006101 | FB | Blank | 11 | CAP NO.1 | CURRENT BALANCE | Blank | English Electric | CDG11_525 | CDG11 525 | CDG11 | Electromechanical |  | 0.2894 | 2190 |  | 9.9 | 0.0088019 | 0.0046268 | 0.0041751 | 50.955 | 1480.5706 | 1531.5256 | 51.2524 | 3.5679 | 45.4828 |  | 14.217 | 0.023831 | 0.012527 | 0.011304 | 137.9624 | 4008.6955 | 4146.6579 | 138.7677 | 9.6602 | 123.1461 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.02014 |  | 1631.8287 | 4418.232 | 45.8496 | 4372.3824 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0051032 | 0.005631 | 0.0062156 | 0.0068634 | 0.0075813 | 0.0083771 | 0.0092595 | 0.010238 | 0.011323 | 0.012527 | 0.013863 | 0.015345 | 0.01699 | 0.018817 | 0.020844 | 0.023095 | 0.025595 | 0.028372 | 0.031456 | 0.034882 | 0.038689 | 0.042919 | 0.047621 | 0.052846 | 0.058654 | 0.06511 | 0.072288 | 0.080269 | 0.086636 | 0.086636 | 1799.8731 | 1985.9948 | 2192.184 | 2420.6535 | 2673.8634 | 2954.549 | 3265.7521 | 3610.8552 | 3993.6204 | 4418.232 | 4889.3445 | 5412.1357 | 5992.3657 | 6636.4433 | 7351.4991 | 8145.4675 | 9027.1779 | 10006.4562 | 11094.2375 | 12302.6928 | 13645.3686 | 15137.3436 | 16795.4027 | 18638.2309 | 20686.6296 | 22963.757 | 25495.3963 | 28310.255 | 30555.8499 | 30555.8499 |  | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 37.8752 | 50.2059 | 67.132 | 90.4712 | 122.7845 | 167.6879 | 230.2945 | 317.8447 | 440.6046 | 613.147 | 856.1792 | 1199.1529 | 1683.9903 |  | 56.2023 | 62.0141 | 68.4525 | 75.5866 | 83.4933 | 92.2579 | 101.9754 | 112.7515 | 124.7036 | 137.9624 | 152.6732 | 168.9977 | 187.1158 | 207.2276 | 229.5557 | 254.3479 | 281.88 | 312.4586 | 346.4254 | 384.1602 | 426.0862 | 472.6742 | 524.4482 | 581.9919 | 645.9545 | 717.0594 | 796.1117 | 884.0076 | 954.1279 | 954.1279 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 41.9899 | 47.8017 | 54.2401 | 61.3742 | 69.2809 | 78.0455 | 87.763 | 98.5391 | 110.4912 | 123.75 | 138.4608 | 154.7854 | 172.9034 | 193.0152 | 215.3433 | 240.1356 | 267.6676 | 295.4473 | 323.8758 | 354.0084 | 385.4519 | 417.5266 | 449.1327 | 478.557 | 503.1973 | 519.1656 | 520.7219 | 499.462 | 415.5386 | 197.778 |  | 1633.0386 | 1801.9082 | 1988.9852 | 2196.2773 | 2426.0166 | 2680.6848 | 2963.0417 | 3276.1564 | 3623.4422 | 4008.6955 | 4436.1395 | 4910.4719 | 5436.9191 | 6021.2956 | 6670.0711 | 7390.4447 | 8190.4273 | 9078.9339 | 10065.8862 | 11162.3269 | 12380.5468 | 13734.2271 | 15238.5968 | 16910.6089 | 18769.1366 | 20835.1916 | 23132.1673 | 25686.11 | 27723.5553 | 27723.5553 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 1632.383 | 1801.2526 | 1988.3296 | 2195.6217 | 2425.361 | 2680.0292 | 2962.3861 | 3275.5008 | 3622.7866 | 4008.0399 | 4435.4839 | 4909.8163 | 5436.2635 | 6020.6399 | 6669.4155 | 7389.7891 | 8189.7717 | 9078.1492 | 10064.846 | 11160.936 | 12378.6724 | 13731.6832 | 15235.1226 | 16905.8376 | 18762.5514 | 20826.063 | 23119.4639 | 25668.3713 | 27698.7108 | 27688.6658 |  | 1674.3729 | 1849.0543 | 2042.5697 | 2256.996 | 2494.6419 | 2758.0747 | 3050.1491 | 3374.0399 | 3733.2778 | 4131.79 | 4573.9448 | 5064.6017 | 5609.1669 | 6213.6552 | 6884.7588 | 7629.9247 | 8457.4393 | 9373.5965 | 10388.7218 | 11514.9444 | 12764.1243 | 14149.2098 | 15684.2552 | 17384.3946 | 19265.7487 | 21345.2286 | 23640.1858 | 26167.8333 | 28114.2494 | 27886.4438 |  | 56.5304 | 62.3761 | 68.8521 | 76.0278 | 83.9806 | 92.7964 | 102.5707 | 113.4097 | 125.4315 | 138.7677 | 153.5644 | 169.9842 | 188.2081 | 208.4373 | 230.8957 | 255.8327 | 283.5254 | 314.2826 | 348.4476 | 386.4027 | 428.5734 | 475.4334 | 527.5097 | 585.3892 | 649.7252 | 721.2452 | 800.7589 | 889.1679 | 959.6975 | 959.6975 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 41.849 | 47.6947 | 54.1707 | 61.3464 | 69.2992 | 78.115 | 87.8893 | 98.7282 | 110.7501 | 124.0863 | 138.883 | 155.3028 | 173.5267 | 193.7559 | 216.2143 | 241.1513 | 268.844 | 296.7098 | 325.1539 | 355.2559 | 386.5981 | 418.4658 | 449.7085 | 478.5409 | 502.2568 | 516.8206 | 516.2809 | 491.9317 | 403.334 | 178.3869 |  | 3.9353 | 4.3423 | 4.7931 | 5.2926 | 5.8462 | 6.4599 | 7.1404 | 7.8949 | 8.7318 | 9.6602 | 10.6903 | 11.8333 | 13.1019 | 14.5102 | 16.0736 | 17.8096 | 19.7374 | 21.8785 | 24.2569 | 26.8991 | 29.8348 | 33.0969 | 36.7221 | 40.7514 | 45.2301 | 50.2089 | 55.7441 | 61.8987 | 66.8085 | 66.8085 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.8676 | 2.2745 | 2.7254 | 3.2249 | 3.7785 | 4.3922 | 5.0727 | 5.8272 | 6.6641 | 7.5925 | 8.6225 | 9.7656 | 11.0342 | 12.4425 | 14.0059 | 15.7419 | 17.6697 | 19.4036 | 20.9762 | 22.5124 | 23.923 | 25.0736 | 25.7647 | 25.703 | 24.4608 | 21.418 | 15.6786 | 5.9524 | -11.549 | -43.2302 |  | 50.1665 | 55.3542 | 61.1011 | 67.4691 | 74.5266 | 82.35 | 91.0239 | 100.6427 | 111.3112 | 123.1461 | 136.2771 | 150.8485 | 167.0208 | 184.9727 | 204.9029 | 227.0326 | 251.6079 | 278.9026 | 309.2215 | 342.9039 | 380.3273 | 421.912 | 468.1259 | 519.4897 | 576.5832 | 640.0519 | 710.6144 | 789.0709 | 851.6607 | 851.6607 |  | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.024106 | 0.031954 | 0.042727 | 0.057582 | 0.078148 | 0.10673 | 0.14657 | 0.2023 | 0.28043 | 0.39025 | 0.54493 | 0.76322 | 1.0718 |  | 50.1464 | 55.334 | 61.081 | 67.4489 | 74.5065 | 82.3298 | 91.0038 | 100.6226 | 111.2911 | 123.126 | 136.257 | 150.8283 | 167.0006 | 184.9525 | 204.8828 | 227.0125 | 251.5877 | 278.8785 | 309.1895 | 342.8612 | 380.2697 | 421.8339 | 468.0191 | 519.3431 | 576.3809 | 639.7714 | 710.2241 | 788.5259 | 850.8974 | 850.5889 |  | 1768.2359 | 1954.3575 | 2160.5467 | 2389.0162 | 2642.2261 | 2922.9117 | 3234.1148 | 3579.2179 | 3961.9831 | 4386.5947 | 4857.7073 | 5380.4984 | 5960.7285 | 6604.806 | 7319.8618 | 8113.8302 | 8995.5407 | 9968.5883 | 11044.0415 | 12235.5739 | 13554.9151 | 15014.5831 | 16627.7476 | 18407.9816 | 20368.8472 | 22523.2386 | 24882.3694 | 27454.2434 | 29356.9319 | 28872.1894
| TRUE | 1555 | 22006105 | FB | Blank | 11 | CAP NO.1 | OVERCURRENT | Blank | Brown Boveri | ICM21_1060 | ICM21 1060 | ICM21 | Electromechanical |  | 0.2894 | 2190 |  | 9.9 | 0.0088019 | 0.0046268 | 0.0041751 | 50.955 | 1480.5706 | 1531.5256 | 51.2524 | 3.5679 | 45.4828 |  | 14.217 | 0.023831 | 0.012527 | 0.011304 | 137.9624 | 4008.6955 | 4146.6579 | 138.7677 | 9.6602 | 123.1461 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.02014 |  | 1631.8287 | 4418.232 | 45.8496 | 4372.3824 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0051032 | 0.005631 | 0.0062156 | 0.0068634 | 0.0075813 | 0.0083771 | 0.0092595 | 0.010238 | 0.011323 | 0.012527 | 0.013863 | 0.015345 | 0.01699 | 0.018817 | 0.020844 | 0.023095 | 0.025595 | 0.028372 | 0.031456 | 0.034882 | 0.038689 | 0.042919 | 0.047621 | 0.052846 | 0.058654 | 0.06511 | 0.072288 | 0.080269 | 0.086636 | 0.086636 | 1799.8731 | 1985.9948 | 2192.184 | 2420.6535 | 2673.8634 | 2954.549 | 3265.7521 | 3610.8552 | 3993.6204 | 4418.232 | 4889.3445 | 5412.1357 | 5992.3657 | 6636.4433 | 7351.4991 | 8145.4675 | 9027.1779 | 10006.4562 | 11094.2375 | 12302.6928 | 13645.3686 | 15137.3436 | 16795.4027 | 18638.2309 | 20686.6296 | 22963.757 | 25495.3963 | 28310.255 | 30555.8499 | 30555.8499 |  | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 37.8752 | 50.2059 | 67.132 | 90.4712 | 122.7845 | 167.6879 | 230.2945 | 317.8447 | 440.6046 | 613.147 | 856.1792 | 1199.1529 | 1683.9903 |  | 56.2023 | 62.0141 | 68.4525 | 75.5866 | 83.4933 | 92.2579 | 101.9754 | 112.7515 | 124.7036 | 137.9624 | 152.6732 | 168.9977 | 187.1158 | 207.2276 | 229.5557 | 254.3479 | 281.88 | 312.4586 | 346.4254 | 384.1602 | 426.0862 | 472.6742 | 524.4482 | 581.9919 | 645.9545 | 717.0594 | 796.1117 | 884.0076 | 954.1279 | 954.1279 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 41.9899 | 47.8017 | 54.2401 | 61.3742 | 69.2809 | 78.0455 | 87.763 | 98.5391 | 110.4912 | 123.75 | 138.4608 | 154.7854 | 172.9034 | 193.0152 | 215.3433 | 240.1356 | 267.6676 | 295.4473 | 323.8758 | 354.0084 | 385.4519 | 417.5266 | 449.1327 | 478.557 | 503.1973 | 519.1656 | 520.7219 | 499.462 | 415.5386 | 197.778 |  | 1633.0386 | 1801.9082 | 1988.9852 | 2196.2773 | 2426.0166 | 2680.6848 | 2963.0417 | 3276.1564 | 3623.4422 | 4008.6955 | 4436.1395 | 4910.4719 | 5436.9191 | 6021.2956 | 6670.0711 | 7390.4447 | 8190.4273 | 9078.9339 | 10065.8862 | 11162.3269 | 12380.5468 | 13734.2271 | 15238.5968 | 16910.6089 | 18769.1366 | 20835.1916 | 23132.1673 | 25686.11 | 27723.5553 | 27723.5553 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 1632.383 | 1801.2526 | 1988.3296 | 2195.6217 | 2425.361 | 2680.0292 | 2962.3861 | 3275.5008 | 3622.7866 | 4008.0399 | 4435.4839 | 4909.8163 | 5436.2635 | 6020.6399 | 6669.4155 | 7389.7891 | 8189.7717 | 9078.1492 | 10064.846 | 11160.936 | 12378.6724 | 13731.6832 | 15235.1226 | 16905.8376 | 18762.5514 | 20826.063 | 23119.4639 | 25668.3713 | 27698.7108 | 27688.6658 |  | 1674.3729 | 1849.0543 | 2042.5697 | 2256.996 | 2494.6419 | 2758.0747 | 3050.1491 | 3374.0399 | 3733.2778 | 4131.79 | 4573.9448 | 5064.6017 | 5609.1669 | 6213.6552 | 6884.7588 | 7629.9247 | 8457.4393 | 9373.5965 | 10388.7218 | 11514.9444 | 12764.1243 | 14149.2098 | 15684.2552 | 17384.3946 | 19265.7487 | 21345.2286 | 23640.1858 | 26167.8333 | 28114.2494 | 27886.4438 |  | 56.5304 | 62.3761 | 68.8521 | 76.0278 | 83.9806 | 92.7964 | 102.5707 | 113.4097 | 125.4315 | 138.7677 | 153.5644 | 169.9842 | 188.2081 | 208.4373 | 230.8957 | 255.8327 | 283.5254 | 314.2826 | 348.4476 | 386.4027 | 428.5734 | 475.4334 | 527.5097 | 585.3892 | 649.7252 | 721.2452 | 800.7589 | 889.1679 | 959.6975 | 959.6975 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 41.849 | 47.6947 | 54.1707 | 61.3464 | 69.2992 | 78.115 | 87.8893 | 98.7282 | 110.7501 | 124.0863 | 138.883 | 155.3028 | 173.5267 | 193.7559 | 216.2143 | 241.1513 | 268.844 | 296.7098 | 325.1539 | 355.2559 | 386.5981 | 418.4658 | 449.7085 | 478.5409 | 502.2568 | 516.8206 | 516.2809 | 491.9317 | 403.334 | 178.3869 |  | 3.9353 | 4.3423 | 4.7931 | 5.2926 | 5.8462 | 6.4599 | 7.1404 | 7.8949 | 8.7318 | 9.6602 | 10.6903 | 11.8333 | 13.1019 | 14.5102 | 16.0736 | 17.8096 | 19.7374 | 21.8785 | 24.2569 | 26.8991 | 29.8348 | 33.0969 | 36.7221 | 40.7514 | 45.2301 | 50.2089 | 55.7441 | 61.8987 | 66.8085 | 66.8085 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.8676 | 2.2745 | 2.7254 | 3.2249 | 3.7785 | 4.3922 | 5.0727 | 5.8272 | 6.6641 | 7.5925 | 8.6225 | 9.7656 | 11.0342 | 12.4425 | 14.0059 | 15.7419 | 17.6697 | 19.4036 | 20.9762 | 22.5124 | 23.923 | 25.0736 | 25.7647 | 25.703 | 24.4608 | 21.418 | 15.6786 | 5.9524 | -11.549 | -43.2302 |  | 50.1665 | 55.3542 | 61.1011 | 67.4691 | 74.5266 | 82.35 | 91.0239 | 100.6427 | 111.3112 | 123.1461 | 136.2771 | 150.8485 | 167.0208 | 184.9727 | 204.9029 | 227.0326 | 251.6079 | 278.9026 | 309.2215 | 342.9039 | 380.3273 | 421.912 | 468.1259 | 519.4897 | 576.5832 | 640.0519 | 710.6144 | 789.0709 | 851.6607 | 851.6607 |  | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.024106 | 0.031954 | 0.042727 | 0.057582 | 0.078148 | 0.10673 | 0.14657 | 0.2023 | 0.28043 | 0.39025 | 0.54493 | 0.76322 | 1.0718 |  | 50.1464 | 55.334 | 61.081 | 67.4489 | 74.5065 | 82.3298 | 91.0038 | 100.6226 | 111.2911 | 123.126 | 136.257 | 150.8283 | 167.0006 | 184.9525 | 204.8828 | 227.0125 | 251.5877 | 278.8785 | 309.1895 | 342.8612 | 380.2697 | 421.8339 | 468.0191 | 519.3431 | 576.3809 | 639.7714 | 710.2241 | 788.5259 | 850.8974 | 850.5889 |  | 1768.2359 | 1954.3575 | 2160.5467 | 2389.0162 | 2642.2261 | 2922.9117 | 3234.1148 | 3579.2179 | 3961.9831 | 4386.5947 | 4857.7073 | 5380.4984 | 5960.7285 | 6604.806 | 7319.8618 | 8113.8302 | 8995.5407 | 9968.5883 | 11044.0415 | 12235.5739 | 13554.9151 | 15014.5831 | 16627.7476 | 18407.9816 | 20368.8472 | 22523.2386 | 24882.3694 | 27454.2434 | 29356.9319 | 28872.1894
| TRUE | 1556 | 22006106 | FB | Blank | 11 | CAP NO.1 | OVERCURRENT | Blank | Brown Boveri | ICM21_1060 | ICM21 1060 | ICM21 | Electromechanical |  | 0.2894 | 2190 |  | 9.9 | 0.0088019 | 0.0046268 | 0.0041751 | 50.955 | 1480.5706 | 1531.5256 | 51.2524 | 3.5679 | 45.4828 |  | 14.217 | 0.023831 | 0.012527 | 0.011304 | 137.9624 | 4008.6955 | 4146.6579 | 138.7677 | 9.6602 | 123.1461 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.02014 |  | 1631.8287 | 4418.232 | 45.8496 | 4372.3824 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0051032 | 0.005631 | 0.0062156 | 0.0068634 | 0.0075813 | 0.0083771 | 0.0092595 | 0.010238 | 0.011323 | 0.012527 | 0.013863 | 0.015345 | 0.01699 | 0.018817 | 0.020844 | 0.023095 | 0.025595 | 0.028372 | 0.031456 | 0.034882 | 0.038689 | 0.042919 | 0.047621 | 0.052846 | 0.058654 | 0.06511 | 0.072288 | 0.080269 | 0.086636 | 0.086636 | 1799.8731 | 1985.9948 | 2192.184 | 2420.6535 | 2673.8634 | 2954.549 | 3265.7521 | 3610.8552 | 3993.6204 | 4418.232 | 4889.3445 | 5412.1357 | 5992.3657 | 6636.4433 | 7351.4991 | 8145.4675 | 9027.1779 | 10006.4562 | 11094.2375 | 12302.6928 | 13645.3686 | 15137.3436 | 16795.4027 | 18638.2309 | 20686.6296 | 22963.757 | 25495.3963 | 28310.255 | 30555.8499 | 30555.8499 |  | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 37.8752 | 50.2059 | 67.132 | 90.4712 | 122.7845 | 167.6879 | 230.2945 | 317.8447 | 440.6046 | 613.147 | 856.1792 | 1199.1529 | 1683.9903 |  | 56.2023 | 62.0141 | 68.4525 | 75.5866 | 83.4933 | 92.2579 | 101.9754 | 112.7515 | 124.7036 | 137.9624 | 152.6732 | 168.9977 | 187.1158 | 207.2276 | 229.5557 | 254.3479 | 281.88 | 312.4586 | 346.4254 | 384.1602 | 426.0862 | 472.6742 | 524.4482 | 581.9919 | 645.9545 | 717.0594 | 796.1117 | 884.0076 | 954.1279 | 954.1279 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 41.9899 | 47.8017 | 54.2401 | 61.3742 | 69.2809 | 78.0455 | 87.763 | 98.5391 | 110.4912 | 123.75 | 138.4608 | 154.7854 | 172.9034 | 193.0152 | 215.3433 | 240.1356 | 267.6676 | 295.4473 | 323.8758 | 354.0084 | 385.4519 | 417.5266 | 449.1327 | 478.557 | 503.1973 | 519.1656 | 520.7219 | 499.462 | 415.5386 | 197.778 |  | 1633.0386 | 1801.9082 | 1988.9852 | 2196.2773 | 2426.0166 | 2680.6848 | 2963.0417 | 3276.1564 | 3623.4422 | 4008.6955 | 4436.1395 | 4910.4719 | 5436.9191 | 6021.2956 | 6670.0711 | 7390.4447 | 8190.4273 | 9078.9339 | 10065.8862 | 11162.3269 | 12380.5468 | 13734.2271 | 15238.5968 | 16910.6089 | 18769.1366 | 20835.1916 | 23132.1673 | 25686.11 | 27723.5553 | 27723.5553 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 1632.383 | 1801.2526 | 1988.3296 | 2195.6217 | 2425.361 | 2680.0292 | 2962.3861 | 3275.5008 | 3622.7866 | 4008.0399 | 4435.4839 | 4909.8163 | 5436.2635 | 6020.6399 | 6669.4155 | 7389.7891 | 8189.7717 | 9078.1492 | 10064.846 | 11160.936 | 12378.6724 | 13731.6832 | 15235.1226 | 16905.8376 | 18762.5514 | 20826.063 | 23119.4639 | 25668.3713 | 27698.7108 | 27688.6658 |  | 1674.3729 | 1849.0543 | 2042.5697 | 2256.996 | 2494.6419 | 2758.0747 | 3050.1491 | 3374.0399 | 3733.2778 | 4131.79 | 4573.9448 | 5064.6017 | 5609.1669 | 6213.6552 | 6884.7588 | 7629.9247 | 8457.4393 | 9373.5965 | 10388.7218 | 11514.9444 | 12764.1243 | 14149.2098 | 15684.2552 | 17384.3946 | 19265.7487 | 21345.2286 | 23640.1858 | 26167.8333 | 28114.2494 | 27886.4438 |  | 56.5304 | 62.3761 | 68.8521 | 76.0278 | 83.9806 | 92.7964 | 102.5707 | 113.4097 | 125.4315 | 138.7677 | 153.5644 | 169.9842 | 188.2081 | 208.4373 | 230.8957 | 255.8327 | 283.5254 | 314.2826 | 348.4476 | 386.4027 | 428.5734 | 475.4334 | 527.5097 | 585.3892 | 649.7252 | 721.2452 | 800.7589 | 889.1679 | 959.6975 | 959.6975 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 41.849 | 47.6947 | 54.1707 | 61.3464 | 69.2992 | 78.115 | 87.8893 | 98.7282 | 110.7501 | 124.0863 | 138.883 | 155.3028 | 173.5267 | 193.7559 | 216.2143 | 241.1513 | 268.844 | 296.7098 | 325.1539 | 355.2559 | 386.5981 | 418.4658 | 449.7085 | 478.5409 | 502.2568 | 516.8206 | 516.2809 | 491.9317 | 403.334 | 178.3869 |  | 3.9353 | 4.3423 | 4.7931 | 5.2926 | 5.8462 | 6.4599 | 7.1404 | 7.8949 | 8.7318 | 9.6602 | 10.6903 | 11.8333 | 13.1019 | 14.5102 | 16.0736 | 17.8096 | 19.7374 | 21.8785 | 24.2569 | 26.8991 | 29.8348 | 33.0969 | 36.7221 | 40.7514 | 45.2301 | 50.2089 | 55.7441 | 61.8987 | 66.8085 | 66.8085 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.8676 | 2.2745 | 2.7254 | 3.2249 | 3.7785 | 4.3922 | 5.0727 | 5.8272 | 6.6641 | 7.5925 | 8.6225 | 9.7656 | 11.0342 | 12.4425 | 14.0059 | 15.7419 | 17.6697 | 19.4036 | 20.9762 | 22.5124 | 23.923 | 25.0736 | 25.7647 | 25.703 | 24.4608 | 21.418 | 15.6786 | 5.9524 | -11.549 | -43.2302 |  | 50.1665 | 55.3542 | 61.1011 | 67.4691 | 74.5266 | 82.35 | 91.0239 | 100.6427 | 111.3112 | 123.1461 | 136.2771 | 150.8485 | 167.0208 | 184.9727 | 204.9029 | 227.0326 | 251.6079 | 278.9026 | 309.2215 | 342.9039 | 380.3273 | 421.912 | 468.1259 | 519.4897 | 576.5832 | 640.0519 | 710.6144 | 789.0709 | 851.6607 | 851.6607 |  | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.024106 | 0.031954 | 0.042727 | 0.057582 | 0.078148 | 0.10673 | 0.14657 | 0.2023 | 0.28043 | 0.39025 | 0.54493 | 0.76322 | 1.0718 |  | 50.1464 | 55.334 | 61.081 | 67.4489 | 74.5065 | 82.3298 | 91.0038 | 100.6226 | 111.2911 | 123.126 | 136.257 | 150.8283 | 167.0006 | 184.9525 | 204.8828 | 227.0125 | 251.5877 | 278.8785 | 309.1895 | 342.8612 | 380.2697 | 421.8339 | 468.0191 | 519.3431 | 576.3809 | 639.7714 | 710.2241 | 788.5259 | 850.8974 | 850.5889 |  | 1768.2359 | 1954.3575 | 2160.5467 | 2389.0162 | 2642.2261 | 2922.9117 | 3234.1148 | 3579.2179 | 3961.9831 | 4386.5947 | 4857.7073 | 5380.4984 | 5960.7285 | 6604.806 | 7319.8618 | 8113.8302 | 8995.5407 | 9968.5883 | 11044.0415 | 12235.5739 | 13554.9151 | 15014.5831 | 16627.7476 | 18407.9816 | 20368.8472 | 22523.2386 | 24882.3694 | 27454.2434 | 29356.9319 | 28872.1894
| TRUE | 1557 | 22006104 | FB | Blank | 11 | CAP NO.1 | OVERCURRENT | Blank | Brown Boveri | ICM21_1060 | ICM21 1060 | ICM21 | Electromechanical |  | 0.2894 | 2190 |  | 9.9 | 0.0088019 | 0.0046268 | 0.0041751 | 50.955 | 1480.5706 | 1531.5256 | 51.2524 | 3.5679 | 45.4828 |  | 14.217 | 0.023831 | 0.012527 | 0.011304 | 137.9624 | 4008.6955 | 4146.6579 | 138.7677 | 9.6602 | 123.1461 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.02014 |  | 1631.8287 | 4418.232 | 45.8496 | 4372.3824 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0051032 | 0.005631 | 0.0062156 | 0.0068634 | 0.0075813 | 0.0083771 | 0.0092595 | 0.010238 | 0.011323 | 0.012527 | 0.013863 | 0.015345 | 0.01699 | 0.018817 | 0.020844 | 0.023095 | 0.025595 | 0.028372 | 0.031456 | 0.034882 | 0.038689 | 0.042919 | 0.047621 | 0.052846 | 0.058654 | 0.06511 | 0.072288 | 0.080269 | 0.086636 | 0.086636 | 1799.8731 | 1985.9948 | 2192.184 | 2420.6535 | 2673.8634 | 2954.549 | 3265.7521 | 3610.8552 | 3993.6204 | 4418.232 | 4889.3445 | 5412.1357 | 5992.3657 | 6636.4433 | 7351.4991 | 8145.4675 | 9027.1779 | 10006.4562 | 11094.2375 | 12302.6928 | 13645.3686 | 15137.3436 | 16795.4027 | 18638.2309 | 20686.6296 | 22963.757 | 25495.3963 | 28310.255 | 30555.8499 | 30555.8499 |  | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 37.8752 | 50.2059 | 67.132 | 90.4712 | 122.7845 | 167.6879 | 230.2945 | 317.8447 | 440.6046 | 613.147 | 856.1792 | 1199.1529 | 1683.9903 |  | 56.2023 | 62.0141 | 68.4525 | 75.5866 | 83.4933 | 92.2579 | 101.9754 | 112.7515 | 124.7036 | 137.9624 | 152.6732 | 168.9977 | 187.1158 | 207.2276 | 229.5557 | 254.3479 | 281.88 | 312.4586 | 346.4254 | 384.1602 | 426.0862 | 472.6742 | 524.4482 | 581.9919 | 645.9545 | 717.0594 | 796.1117 | 884.0076 | 954.1279 | 954.1279 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 41.9899 | 47.8017 | 54.2401 | 61.3742 | 69.2809 | 78.0455 | 87.763 | 98.5391 | 110.4912 | 123.75 | 138.4608 | 154.7854 | 172.9034 | 193.0152 | 215.3433 | 240.1356 | 267.6676 | 295.4473 | 323.8758 | 354.0084 | 385.4519 | 417.5266 | 449.1327 | 478.557 | 503.1973 | 519.1656 | 520.7219 | 499.462 | 415.5386 | 197.778 |  | 1633.0386 | 1801.9082 | 1988.9852 | 2196.2773 | 2426.0166 | 2680.6848 | 2963.0417 | 3276.1564 | 3623.4422 | 4008.6955 | 4436.1395 | 4910.4719 | 5436.9191 | 6021.2956 | 6670.0711 | 7390.4447 | 8190.4273 | 9078.9339 | 10065.8862 | 11162.3269 | 12380.5468 | 13734.2271 | 15238.5968 | 16910.6089 | 18769.1366 | 20835.1916 | 23132.1673 | 25686.11 | 27723.5553 | 27723.5553 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 1632.383 | 1801.2526 | 1988.3296 | 2195.6217 | 2425.361 | 2680.0292 | 2962.3861 | 3275.5008 | 3622.7866 | 4008.0399 | 4435.4839 | 4909.8163 | 5436.2635 | 6020.6399 | 6669.4155 | 7389.7891 | 8189.7717 | 9078.1492 | 10064.846 | 11160.936 | 12378.6724 | 13731.6832 | 15235.1226 | 16905.8376 | 18762.5514 | 20826.063 | 23119.4639 | 25668.3713 | 27698.7108 | 27688.6658 |  | 1674.3729 | 1849.0543 | 2042.5697 | 2256.996 | 2494.6419 | 2758.0747 | 3050.1491 | 3374.0399 | 3733.2778 | 4131.79 | 4573.9448 | 5064.6017 | 5609.1669 | 6213.6552 | 6884.7588 | 7629.9247 | 8457.4393 | 9373.5965 | 10388.7218 | 11514.9444 | 12764.1243 | 14149.2098 | 15684.2552 | 17384.3946 | 19265.7487 | 21345.2286 | 23640.1858 | 26167.8333 | 28114.2494 | 27886.4438 |  | 56.5304 | 62.3761 | 68.8521 | 76.0278 | 83.9806 | 92.7964 | 102.5707 | 113.4097 | 125.4315 | 138.7677 | 153.5644 | 169.9842 | 188.2081 | 208.4373 | 230.8957 | 255.8327 | 283.5254 | 314.2826 | 348.4476 | 386.4027 | 428.5734 | 475.4334 | 527.5097 | 585.3892 | 649.7252 | 721.2452 | 800.7589 | 889.1679 | 959.6975 | 959.6975 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 41.849 | 47.6947 | 54.1707 | 61.3464 | 69.2992 | 78.115 | 87.8893 | 98.7282 | 110.7501 | 124.0863 | 138.883 | 155.3028 | 173.5267 | 193.7559 | 216.2143 | 241.1513 | 268.844 | 296.7098 | 325.1539 | 355.2559 | 386.5981 | 418.4658 | 449.7085 | 478.5409 | 502.2568 | 516.8206 | 516.2809 | 491.9317 | 403.334 | 178.3869 |  | 3.9353 | 4.3423 | 4.7931 | 5.2926 | 5.8462 | 6.4599 | 7.1404 | 7.8949 | 8.7318 | 9.6602 | 10.6903 | 11.8333 | 13.1019 | 14.5102 | 16.0736 | 17.8096 | 19.7374 | 21.8785 | 24.2569 | 26.8991 | 29.8348 | 33.0969 | 36.7221 | 40.7514 | 45.2301 | 50.2089 | 55.7441 | 61.8987 | 66.8085 | 66.8085 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.8676 | 2.2745 | 2.7254 | 3.2249 | 3.7785 | 4.3922 | 5.0727 | 5.8272 | 6.6641 | 7.5925 | 8.6225 | 9.7656 | 11.0342 | 12.4425 | 14.0059 | 15.7419 | 17.6697 | 19.4036 | 20.9762 | 22.5124 | 23.923 | 25.0736 | 25.7647 | 25.703 | 24.4608 | 21.418 | 15.6786 | 5.9524 | -11.549 | -43.2302 |  | 50.1665 | 55.3542 | 61.1011 | 67.4691 | 74.5266 | 82.35 | 91.0239 | 100.6427 | 111.3112 | 123.1461 | 136.2771 | 150.8485 | 167.0208 | 184.9727 | 204.9029 | 227.0326 | 251.6079 | 278.9026 | 309.2215 | 342.9039 | 380.3273 | 421.912 | 468.1259 | 519.4897 | 576.5832 | 640.0519 | 710.6144 | 789.0709 | 851.6607 | 851.6607 |  | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.024106 | 0.031954 | 0.042727 | 0.057582 | 0.078148 | 0.10673 | 0.14657 | 0.2023 | 0.28043 | 0.39025 | 0.54493 | 0.76322 | 1.0718 |  | 50.1464 | 55.334 | 61.081 | 67.4489 | 74.5065 | 82.3298 | 91.0038 | 100.6226 | 111.2911 | 123.126 | 136.257 | 150.8283 | 167.0006 | 184.9525 | 204.8828 | 227.0125 | 251.5877 | 278.8785 | 309.1895 | 342.8612 | 380.2697 | 421.8339 | 468.0191 | 519.3431 | 576.3809 | 639.7714 | 710.2241 | 788.5259 | 850.8974 | 850.5889 |  | 1768.2359 | 1954.3575 | 2160.5467 | 2389.0162 | 2642.2261 | 2922.9117 | 3234.1148 | 3579.2179 | 3961.9831 | 4386.5947 | 4857.7073 | 5380.4984 | 5960.7285 | 6604.806 | 7319.8618 | 8113.8302 | 8995.5407 | 9968.5883 | 11044.0415 | 12235.5739 | 13554.9151 | 15014.5831 | 16627.7476 | 18407.9816 | 20368.8472 | 22523.2386 | 24882.3694 | 27454.2434 | 29356.9319 | 28872.1894
| FALSE | 1558 | 22009922 | FB | Blank | 11 | CAP NO.1 | METER (DIGITAL MULTI FN.) | I | Schneider | ION_6200 | ION 6200 | ION 6000s | Digital |  | 0 | 1 |  | 1.4709 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 4.8786 | 0.0081995 | 0 | 0.0081995 | 22.5486 | 0 | 22.5486 | 23.2752 | 3.2806 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 49.1045 | 30.9493 | 18.1552 |  | 0.11989 |  | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 132.6818 | 189.5929 | 266.6938 | 373.6462 | 524.8006 | 738.7495 | 1041.9903 | 1472.3087 | 2083.6164 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.7014 | 26.7229 | 37.5902 | 52.665 | 73.9701 | 104.126 | 146.8675 | 207.5204 | 293.6836 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 133.0601 | 194.2933 | 279.9229 | 399.9899 | 562.6522 | 788.2929 | 1107.188 | 1558.5626 | 2198.3191 | 3106.1752 | 4395.87 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 1559 | 22006108 | FB | Blank | 11 | CAP NO.3 | CURRENT BALANCE | Blank | English Electric | CDG11_525 | CDG11 525 | CDG11 | Electromechanical |  | 0.2894 | 2190 |  | 9.9 | 0.0088019 | 0.0046268 | 0.0041751 | 50.955 | 1480.5706 | 1531.5256 | 51.2524 | 3.5679 | 45.4828 |  | 14.217 | 0.023831 | 0.012527 | 0.011304 | 137.9624 | 4008.6955 | 4146.6579 | 138.7677 | 9.6602 | 123.1461 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.02014 |  | 1631.8287 | 4418.232 | 45.8496 | 4372.3824 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0051032 | 0.005631 | 0.0062156 | 0.0068634 | 0.0075813 | 0.0083771 | 0.0092595 | 0.010238 | 0.011323 | 0.012527 | 0.013863 | 0.015345 | 0.01699 | 0.018817 | 0.020844 | 0.023095 | 0.025595 | 0.028372 | 0.031456 | 0.034882 | 0.038689 | 0.042919 | 0.047621 | 0.052846 | 0.058654 | 0.06511 | 0.072288 | 0.080269 | 0.086636 | 0.086636 | 1799.8731 | 1985.9948 | 2192.184 | 2420.6535 | 2673.8634 | 2954.549 | 3265.7521 | 3610.8552 | 3993.6204 | 4418.232 | 4889.3445 | 5412.1357 | 5992.3657 | 6636.4433 | 7351.4991 | 8145.4675 | 9027.1779 | 10006.4562 | 11094.2375 | 12302.6928 | 13645.3686 | 15137.3436 | 16795.4027 | 18638.2309 | 20686.6296 | 22963.757 | 25495.3963 | 28310.255 | 30555.8499 | 30555.8499 |  | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 37.8752 | 50.2059 | 67.132 | 90.4712 | 122.7845 | 167.6879 | 230.2945 | 317.8447 | 440.6046 | 613.147 | 856.1792 | 1199.1529 | 1683.9903 |  | 56.2023 | 62.0141 | 68.4525 | 75.5866 | 83.4933 | 92.2579 | 101.9754 | 112.7515 | 124.7036 | 137.9624 | 152.6732 | 168.9977 | 187.1158 | 207.2276 | 229.5557 | 254.3479 | 281.88 | 312.4586 | 346.4254 | 384.1602 | 426.0862 | 472.6742 | 524.4482 | 581.9919 | 645.9545 | 717.0594 | 796.1117 | 884.0076 | 954.1279 | 954.1279 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 41.9899 | 47.8017 | 54.2401 | 61.3742 | 69.2809 | 78.0455 | 87.763 | 98.5391 | 110.4912 | 123.75 | 138.4608 | 154.7854 | 172.9034 | 193.0152 | 215.3433 | 240.1356 | 267.6676 | 295.4473 | 323.8758 | 354.0084 | 385.4519 | 417.5266 | 449.1327 | 478.557 | 503.1973 | 519.1656 | 520.7219 | 499.462 | 415.5386 | 197.778 |  | 1633.0386 | 1801.9082 | 1988.9852 | 2196.2773 | 2426.0166 | 2680.6848 | 2963.0417 | 3276.1564 | 3623.4422 | 4008.6955 | 4436.1395 | 4910.4719 | 5436.9191 | 6021.2956 | 6670.0711 | 7390.4447 | 8190.4273 | 9078.9339 | 10065.8862 | 11162.3269 | 12380.5468 | 13734.2271 | 15238.5968 | 16910.6089 | 18769.1366 | 20835.1916 | 23132.1673 | 25686.11 | 27723.5553 | 27723.5553 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 1632.383 | 1801.2526 | 1988.3296 | 2195.6217 | 2425.361 | 2680.0292 | 2962.3861 | 3275.5008 | 3622.7866 | 4008.0399 | 4435.4839 | 4909.8163 | 5436.2635 | 6020.6399 | 6669.4155 | 7389.7891 | 8189.7717 | 9078.1492 | 10064.846 | 11160.936 | 12378.6724 | 13731.6832 | 15235.1226 | 16905.8376 | 18762.5514 | 20826.063 | 23119.4639 | 25668.3713 | 27698.7108 | 27688.6658 |  | 1674.3729 | 1849.0543 | 2042.5697 | 2256.996 | 2494.6419 | 2758.0747 | 3050.1491 | 3374.0399 | 3733.2778 | 4131.79 | 4573.9448 | 5064.6017 | 5609.1669 | 6213.6552 | 6884.7588 | 7629.9247 | 8457.4393 | 9373.5965 | 10388.7218 | 11514.9444 | 12764.1243 | 14149.2098 | 15684.2552 | 17384.3946 | 19265.7487 | 21345.2286 | 23640.1858 | 26167.8333 | 28114.2494 | 27886.4438 |  | 56.5304 | 62.3761 | 68.8521 | 76.0278 | 83.9806 | 92.7964 | 102.5707 | 113.4097 | 125.4315 | 138.7677 | 153.5644 | 169.9842 | 188.2081 | 208.4373 | 230.8957 | 255.8327 | 283.5254 | 314.2826 | 348.4476 | 386.4027 | 428.5734 | 475.4334 | 527.5097 | 585.3892 | 649.7252 | 721.2452 | 800.7589 | 889.1679 | 959.6975 | 959.6975 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 41.849 | 47.6947 | 54.1707 | 61.3464 | 69.2992 | 78.115 | 87.8893 | 98.7282 | 110.7501 | 124.0863 | 138.883 | 155.3028 | 173.5267 | 193.7559 | 216.2143 | 241.1513 | 268.844 | 296.7098 | 325.1539 | 355.2559 | 386.5981 | 418.4658 | 449.7085 | 478.5409 | 502.2568 | 516.8206 | 516.2809 | 491.9317 | 403.334 | 178.3869 |  | 3.9353 | 4.3423 | 4.7931 | 5.2926 | 5.8462 | 6.4599 | 7.1404 | 7.8949 | 8.7318 | 9.6602 | 10.6903 | 11.8333 | 13.1019 | 14.5102 | 16.0736 | 17.8096 | 19.7374 | 21.8785 | 24.2569 | 26.8991 | 29.8348 | 33.0969 | 36.7221 | 40.7514 | 45.2301 | 50.2089 | 55.7441 | 61.8987 | 66.8085 | 66.8085 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.8676 | 2.2745 | 2.7254 | 3.2249 | 3.7785 | 4.3922 | 5.0727 | 5.8272 | 6.6641 | 7.5925 | 8.6225 | 9.7656 | 11.0342 | 12.4425 | 14.0059 | 15.7419 | 17.6697 | 19.4036 | 20.9762 | 22.5124 | 23.923 | 25.0736 | 25.7647 | 25.703 | 24.4608 | 21.418 | 15.6786 | 5.9524 | -11.549 | -43.2302 |  | 50.1665 | 55.3542 | 61.1011 | 67.4691 | 74.5266 | 82.35 | 91.0239 | 100.6427 | 111.3112 | 123.1461 | 136.2771 | 150.8485 | 167.0208 | 184.9727 | 204.9029 | 227.0326 | 251.6079 | 278.9026 | 309.2215 | 342.9039 | 380.3273 | 421.912 | 468.1259 | 519.4897 | 576.5832 | 640.0519 | 710.6144 | 789.0709 | 851.6607 | 851.6607 |  | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.024106 | 0.031954 | 0.042727 | 0.057582 | 0.078148 | 0.10673 | 0.14657 | 0.2023 | 0.28043 | 0.39025 | 0.54493 | 0.76322 | 1.0718 |  | 50.1464 | 55.334 | 61.081 | 67.4489 | 74.5065 | 82.3298 | 91.0038 | 100.6226 | 111.2911 | 123.126 | 136.257 | 150.8283 | 167.0006 | 184.9525 | 204.8828 | 227.0125 | 251.5877 | 278.8785 | 309.1895 | 342.8612 | 380.2697 | 421.8339 | 468.0191 | 519.3431 | 576.3809 | 639.7714 | 710.2241 | 788.5259 | 850.8974 | 850.5889 |  | 1768.2359 | 1954.3575 | 2160.5467 | 2389.0162 | 2642.2261 | 2922.9117 | 3234.1148 | 3579.2179 | 3961.9831 | 4386.5947 | 4857.7073 | 5380.4984 | 5960.7285 | 6604.806 | 7319.8618 | 8113.8302 | 8995.5407 | 9968.5883 | 11044.0415 | 12235.5739 | 13554.9151 | 15014.5831 | 16627.7476 | 18407.9816 | 20368.8472 | 22523.2386 | 24882.3694 | 27454.2434 | 29356.9319 | 28872.1894
| TRUE | 1560 | 22006109 | FB | Blank | 11 | CAP NO.3 | CURRENT BALANCE | Blank | English Electric | CDG11_525 | CDG11 525 | CDG11 | Electromechanical |  | 0.2894 | 2190 |  | 9.9 | 0.0088019 | 0.0046268 | 0.0041751 | 50.955 | 1480.5706 | 1531.5256 | 51.2524 | 3.5679 | 45.4828 |  | 14.217 | 0.023831 | 0.012527 | 0.011304 | 137.9624 | 4008.6955 | 4146.6579 | 138.7677 | 9.6602 | 123.1461 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.02014 |  | 1631.8287 | 4418.232 | 45.8496 | 4372.3824 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0051032 | 0.005631 | 0.0062156 | 0.0068634 | 0.0075813 | 0.0083771 | 0.0092595 | 0.010238 | 0.011323 | 0.012527 | 0.013863 | 0.015345 | 0.01699 | 0.018817 | 0.020844 | 0.023095 | 0.025595 | 0.028372 | 0.031456 | 0.034882 | 0.038689 | 0.042919 | 0.047621 | 0.052846 | 0.058654 | 0.06511 | 0.072288 | 0.080269 | 0.086636 | 0.086636 | 1799.8731 | 1985.9948 | 2192.184 | 2420.6535 | 2673.8634 | 2954.549 | 3265.7521 | 3610.8552 | 3993.6204 | 4418.232 | 4889.3445 | 5412.1357 | 5992.3657 | 6636.4433 | 7351.4991 | 8145.4675 | 9027.1779 | 10006.4562 | 11094.2375 | 12302.6928 | 13645.3686 | 15137.3436 | 16795.4027 | 18638.2309 | 20686.6296 | 22963.757 | 25495.3963 | 28310.255 | 30555.8499 | 30555.8499 |  | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 37.8752 | 50.2059 | 67.132 | 90.4712 | 122.7845 | 167.6879 | 230.2945 | 317.8447 | 440.6046 | 613.147 | 856.1792 | 1199.1529 | 1683.9903 |  | 56.2023 | 62.0141 | 68.4525 | 75.5866 | 83.4933 | 92.2579 | 101.9754 | 112.7515 | 124.7036 | 137.9624 | 152.6732 | 168.9977 | 187.1158 | 207.2276 | 229.5557 | 254.3479 | 281.88 | 312.4586 | 346.4254 | 384.1602 | 426.0862 | 472.6742 | 524.4482 | 581.9919 | 645.9545 | 717.0594 | 796.1117 | 884.0076 | 954.1279 | 954.1279 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 41.9899 | 47.8017 | 54.2401 | 61.3742 | 69.2809 | 78.0455 | 87.763 | 98.5391 | 110.4912 | 123.75 | 138.4608 | 154.7854 | 172.9034 | 193.0152 | 215.3433 | 240.1356 | 267.6676 | 295.4473 | 323.8758 | 354.0084 | 385.4519 | 417.5266 | 449.1327 | 478.557 | 503.1973 | 519.1656 | 520.7219 | 499.462 | 415.5386 | 197.778 |  | 1633.0386 | 1801.9082 | 1988.9852 | 2196.2773 | 2426.0166 | 2680.6848 | 2963.0417 | 3276.1564 | 3623.4422 | 4008.6955 | 4436.1395 | 4910.4719 | 5436.9191 | 6021.2956 | 6670.0711 | 7390.4447 | 8190.4273 | 9078.9339 | 10065.8862 | 11162.3269 | 12380.5468 | 13734.2271 | 15238.5968 | 16910.6089 | 18769.1366 | 20835.1916 | 23132.1673 | 25686.11 | 27723.5553 | 27723.5553 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 1632.383 | 1801.2526 | 1988.3296 | 2195.6217 | 2425.361 | 2680.0292 | 2962.3861 | 3275.5008 | 3622.7866 | 4008.0399 | 4435.4839 | 4909.8163 | 5436.2635 | 6020.6399 | 6669.4155 | 7389.7891 | 8189.7717 | 9078.1492 | 10064.846 | 11160.936 | 12378.6724 | 13731.6832 | 15235.1226 | 16905.8376 | 18762.5514 | 20826.063 | 23119.4639 | 25668.3713 | 27698.7108 | 27688.6658 |  | 1674.3729 | 1849.0543 | 2042.5697 | 2256.996 | 2494.6419 | 2758.0747 | 3050.1491 | 3374.0399 | 3733.2778 | 4131.79 | 4573.9448 | 5064.6017 | 5609.1669 | 6213.6552 | 6884.7588 | 7629.9247 | 8457.4393 | 9373.5965 | 10388.7218 | 11514.9444 | 12764.1243 | 14149.2098 | 15684.2552 | 17384.3946 | 19265.7487 | 21345.2286 | 23640.1858 | 26167.8333 | 28114.2494 | 27886.4438 |  | 56.5304 | 62.3761 | 68.8521 | 76.0278 | 83.9806 | 92.7964 | 102.5707 | 113.4097 | 125.4315 | 138.7677 | 153.5644 | 169.9842 | 188.2081 | 208.4373 | 230.8957 | 255.8327 | 283.5254 | 314.2826 | 348.4476 | 386.4027 | 428.5734 | 475.4334 | 527.5097 | 585.3892 | 649.7252 | 721.2452 | 800.7589 | 889.1679 | 959.6975 | 959.6975 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 41.849 | 47.6947 | 54.1707 | 61.3464 | 69.2992 | 78.115 | 87.8893 | 98.7282 | 110.7501 | 124.0863 | 138.883 | 155.3028 | 173.5267 | 193.7559 | 216.2143 | 241.1513 | 268.844 | 296.7098 | 325.1539 | 355.2559 | 386.5981 | 418.4658 | 449.7085 | 478.5409 | 502.2568 | 516.8206 | 516.2809 | 491.9317 | 403.334 | 178.3869 |  | 3.9353 | 4.3423 | 4.7931 | 5.2926 | 5.8462 | 6.4599 | 7.1404 | 7.8949 | 8.7318 | 9.6602 | 10.6903 | 11.8333 | 13.1019 | 14.5102 | 16.0736 | 17.8096 | 19.7374 | 21.8785 | 24.2569 | 26.8991 | 29.8348 | 33.0969 | 36.7221 | 40.7514 | 45.2301 | 50.2089 | 55.7441 | 61.8987 | 66.8085 | 66.8085 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.8676 | 2.2745 | 2.7254 | 3.2249 | 3.7785 | 4.3922 | 5.0727 | 5.8272 | 6.6641 | 7.5925 | 8.6225 | 9.7656 | 11.0342 | 12.4425 | 14.0059 | 15.7419 | 17.6697 | 19.4036 | 20.9762 | 22.5124 | 23.923 | 25.0736 | 25.7647 | 25.703 | 24.4608 | 21.418 | 15.6786 | 5.9524 | -11.549 | -43.2302 |  | 50.1665 | 55.3542 | 61.1011 | 67.4691 | 74.5266 | 82.35 | 91.0239 | 100.6427 | 111.3112 | 123.1461 | 136.2771 | 150.8485 | 167.0208 | 184.9727 | 204.9029 | 227.0326 | 251.6079 | 278.9026 | 309.2215 | 342.9039 | 380.3273 | 421.912 | 468.1259 | 519.4897 | 576.5832 | 640.0519 | 710.6144 | 789.0709 | 851.6607 | 851.6607 |  | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.024106 | 0.031954 | 0.042727 | 0.057582 | 0.078148 | 0.10673 | 0.14657 | 0.2023 | 0.28043 | 0.39025 | 0.54493 | 0.76322 | 1.0718 |  | 50.1464 | 55.334 | 61.081 | 67.4489 | 74.5065 | 82.3298 | 91.0038 | 100.6226 | 111.2911 | 123.126 | 136.257 | 150.8283 | 167.0006 | 184.9525 | 204.8828 | 227.0125 | 251.5877 | 278.8785 | 309.1895 | 342.8612 | 380.2697 | 421.8339 | 468.0191 | 519.3431 | 576.3809 | 639.7714 | 710.2241 | 788.5259 | 850.8974 | 850.5889 |  | 1768.2359 | 1954.3575 | 2160.5467 | 2389.0162 | 2642.2261 | 2922.9117 | 3234.1148 | 3579.2179 | 3961.9831 | 4386.5947 | 4857.7073 | 5380.4984 | 5960.7285 | 6604.806 | 7319.8618 | 8113.8302 | 8995.5407 | 9968.5883 | 11044.0415 | 12235.5739 | 13554.9151 | 15014.5831 | 16627.7476 | 18407.9816 | 20368.8472 | 22523.2386 | 24882.3694 | 27454.2434 | 29356.9319 | 28872.1894
| TRUE | 1561 | 22006107 | FB | Blank | 11 | CAP NO.3 | CURRENT BALANCE | Blank | English Electric | CDG11_525 | CDG11 525 | CDG11 | Electromechanical |  | 0.2894 | 2190 |  | 9.9 | 0.0088019 | 0.0046268 | 0.0041751 | 50.955 | 1480.5706 | 1531.5256 | 51.2524 | 3.5679 | 45.4828 |  | 14.217 | 0.023831 | 0.012527 | 0.011304 | 137.9624 | 4008.6955 | 4146.6579 | 138.7677 | 9.6602 | 123.1461 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.02014 |  | 1631.8287 | 4418.232 | 45.8496 | 4372.3824 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0051032 | 0.005631 | 0.0062156 | 0.0068634 | 0.0075813 | 0.0083771 | 0.0092595 | 0.010238 | 0.011323 | 0.012527 | 0.013863 | 0.015345 | 0.01699 | 0.018817 | 0.020844 | 0.023095 | 0.025595 | 0.028372 | 0.031456 | 0.034882 | 0.038689 | 0.042919 | 0.047621 | 0.052846 | 0.058654 | 0.06511 | 0.072288 | 0.080269 | 0.086636 | 0.086636 | 1799.8731 | 1985.9948 | 2192.184 | 2420.6535 | 2673.8634 | 2954.549 | 3265.7521 | 3610.8552 | 3993.6204 | 4418.232 | 4889.3445 | 5412.1357 | 5992.3657 | 6636.4433 | 7351.4991 | 8145.4675 | 9027.1779 | 10006.4562 | 11094.2375 | 12302.6928 | 13645.3686 | 15137.3436 | 16795.4027 | 18638.2309 | 20686.6296 | 22963.757 | 25495.3963 | 28310.255 | 30555.8499 | 30555.8499 |  | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 37.8752 | 50.2059 | 67.132 | 90.4712 | 122.7845 | 167.6879 | 230.2945 | 317.8447 | 440.6046 | 613.147 | 856.1792 | 1199.1529 | 1683.9903 |  | 56.2023 | 62.0141 | 68.4525 | 75.5866 | 83.4933 | 92.2579 | 101.9754 | 112.7515 | 124.7036 | 137.9624 | 152.6732 | 168.9977 | 187.1158 | 207.2276 | 229.5557 | 254.3479 | 281.88 | 312.4586 | 346.4254 | 384.1602 | 426.0862 | 472.6742 | 524.4482 | 581.9919 | 645.9545 | 717.0594 | 796.1117 | 884.0076 | 954.1279 | 954.1279 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 41.9899 | 47.8017 | 54.2401 | 61.3742 | 69.2809 | 78.0455 | 87.763 | 98.5391 | 110.4912 | 123.75 | 138.4608 | 154.7854 | 172.9034 | 193.0152 | 215.3433 | 240.1356 | 267.6676 | 295.4473 | 323.8758 | 354.0084 | 385.4519 | 417.5266 | 449.1327 | 478.557 | 503.1973 | 519.1656 | 520.7219 | 499.462 | 415.5386 | 197.778 |  | 1633.0386 | 1801.9082 | 1988.9852 | 2196.2773 | 2426.0166 | 2680.6848 | 2963.0417 | 3276.1564 | 3623.4422 | 4008.6955 | 4436.1395 | 4910.4719 | 5436.9191 | 6021.2956 | 6670.0711 | 7390.4447 | 8190.4273 | 9078.9339 | 10065.8862 | 11162.3269 | 12380.5468 | 13734.2271 | 15238.5968 | 16910.6089 | 18769.1366 | 20835.1916 | 23132.1673 | 25686.11 | 27723.5553 | 27723.5553 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 1632.383 | 1801.2526 | 1988.3296 | 2195.6217 | 2425.361 | 2680.0292 | 2962.3861 | 3275.5008 | 3622.7866 | 4008.0399 | 4435.4839 | 4909.8163 | 5436.2635 | 6020.6399 | 6669.4155 | 7389.7891 | 8189.7717 | 9078.1492 | 10064.846 | 11160.936 | 12378.6724 | 13731.6832 | 15235.1226 | 16905.8376 | 18762.5514 | 20826.063 | 23119.4639 | 25668.3713 | 27698.7108 | 27688.6658 |  | 1674.3729 | 1849.0543 | 2042.5697 | 2256.996 | 2494.6419 | 2758.0747 | 3050.1491 | 3374.0399 | 3733.2778 | 4131.79 | 4573.9448 | 5064.6017 | 5609.1669 | 6213.6552 | 6884.7588 | 7629.9247 | 8457.4393 | 9373.5965 | 10388.7218 | 11514.9444 | 12764.1243 | 14149.2098 | 15684.2552 | 17384.3946 | 19265.7487 | 21345.2286 | 23640.1858 | 26167.8333 | 28114.2494 | 27886.4438 |  | 56.5304 | 62.3761 | 68.8521 | 76.0278 | 83.9806 | 92.7964 | 102.5707 | 113.4097 | 125.4315 | 138.7677 | 153.5644 | 169.9842 | 188.2081 | 208.4373 | 230.8957 | 255.8327 | 283.5254 | 314.2826 | 348.4476 | 386.4027 | 428.5734 | 475.4334 | 527.5097 | 585.3892 | 649.7252 | 721.2452 | 800.7589 | 889.1679 | 959.6975 | 959.6975 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 41.849 | 47.6947 | 54.1707 | 61.3464 | 69.2992 | 78.115 | 87.8893 | 98.7282 | 110.7501 | 124.0863 | 138.883 | 155.3028 | 173.5267 | 193.7559 | 216.2143 | 241.1513 | 268.844 | 296.7098 | 325.1539 | 355.2559 | 386.5981 | 418.4658 | 449.7085 | 478.5409 | 502.2568 | 516.8206 | 516.2809 | 491.9317 | 403.334 | 178.3869 |  | 3.9353 | 4.3423 | 4.7931 | 5.2926 | 5.8462 | 6.4599 | 7.1404 | 7.8949 | 8.7318 | 9.6602 | 10.6903 | 11.8333 | 13.1019 | 14.5102 | 16.0736 | 17.8096 | 19.7374 | 21.8785 | 24.2569 | 26.8991 | 29.8348 | 33.0969 | 36.7221 | 40.7514 | 45.2301 | 50.2089 | 55.7441 | 61.8987 | 66.8085 | 66.8085 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.8676 | 2.2745 | 2.7254 | 3.2249 | 3.7785 | 4.3922 | 5.0727 | 5.8272 | 6.6641 | 7.5925 | 8.6225 | 9.7656 | 11.0342 | 12.4425 | 14.0059 | 15.7419 | 17.6697 | 19.4036 | 20.9762 | 22.5124 | 23.923 | 25.0736 | 25.7647 | 25.703 | 24.4608 | 21.418 | 15.6786 | 5.9524 | -11.549 | -43.2302 |  | 50.1665 | 55.3542 | 61.1011 | 67.4691 | 74.5266 | 82.35 | 91.0239 | 100.6427 | 111.3112 | 123.1461 | 136.2771 | 150.8485 | 167.0208 | 184.9727 | 204.9029 | 227.0326 | 251.6079 | 278.9026 | 309.2215 | 342.9039 | 380.3273 | 421.912 | 468.1259 | 519.4897 | 576.5832 | 640.0519 | 710.6144 | 789.0709 | 851.6607 | 851.6607 |  | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.024106 | 0.031954 | 0.042727 | 0.057582 | 0.078148 | 0.10673 | 0.14657 | 0.2023 | 0.28043 | 0.39025 | 0.54493 | 0.76322 | 1.0718 |  | 50.1464 | 55.334 | 61.081 | 67.4489 | 74.5065 | 82.3298 | 91.0038 | 100.6226 | 111.2911 | 123.126 | 136.257 | 150.8283 | 167.0006 | 184.9525 | 204.8828 | 227.0125 | 251.5877 | 278.8785 | 309.1895 | 342.8612 | 380.2697 | 421.8339 | 468.0191 | 519.3431 | 576.3809 | 639.7714 | 710.2241 | 788.5259 | 850.8974 | 850.5889 |  | 1768.2359 | 1954.3575 | 2160.5467 | 2389.0162 | 2642.2261 | 2922.9117 | 3234.1148 | 3579.2179 | 3961.9831 | 4386.5947 | 4857.7073 | 5380.4984 | 5960.7285 | 6604.806 | 7319.8618 | 8113.8302 | 8995.5407 | 9968.5883 | 11044.0415 | 12235.5739 | 13554.9151 | 15014.5831 | 16627.7476 | 18407.9816 | 20368.8472 | 22523.2386 | 24882.3694 | 27454.2434 | 29356.9319 | 28872.1894
| TRUE | 1562 | 22006111 | FB | Blank | 11 | CAP NO.3 | OVERCURRENT | Blank | Brown Boveri | ICM21_1060 | ICM21 1060 | ICM21 | Electromechanical |  | 0.2894 | 2190 |  | 9.9 | 0.0088019 | 0.0046268 | 0.0041751 | 50.955 | 1480.5706 | 1531.5256 | 51.2524 | 3.5679 | 45.4828 |  | 14.217 | 0.023831 | 0.012527 | 0.011304 | 137.9624 | 4008.6955 | 4146.6579 | 138.7677 | 9.6602 | 123.1461 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.02014 |  | 1631.8287 | 4418.232 | 45.8496 | 4372.3824 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0051032 | 0.005631 | 0.0062156 | 0.0068634 | 0.0075813 | 0.0083771 | 0.0092595 | 0.010238 | 0.011323 | 0.012527 | 0.013863 | 0.015345 | 0.01699 | 0.018817 | 0.020844 | 0.023095 | 0.025595 | 0.028372 | 0.031456 | 0.034882 | 0.038689 | 0.042919 | 0.047621 | 0.052846 | 0.058654 | 0.06511 | 0.072288 | 0.080269 | 0.086636 | 0.086636 | 1799.8731 | 1985.9948 | 2192.184 | 2420.6535 | 2673.8634 | 2954.549 | 3265.7521 | 3610.8552 | 3993.6204 | 4418.232 | 4889.3445 | 5412.1357 | 5992.3657 | 6636.4433 | 7351.4991 | 8145.4675 | 9027.1779 | 10006.4562 | 11094.2375 | 12302.6928 | 13645.3686 | 15137.3436 | 16795.4027 | 18638.2309 | 20686.6296 | 22963.757 | 25495.3963 | 28310.255 | 30555.8499 | 30555.8499 |  | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 37.8752 | 50.2059 | 67.132 | 90.4712 | 122.7845 | 167.6879 | 230.2945 | 317.8447 | 440.6046 | 613.147 | 856.1792 | 1199.1529 | 1683.9903 |  | 56.2023 | 62.0141 | 68.4525 | 75.5866 | 83.4933 | 92.2579 | 101.9754 | 112.7515 | 124.7036 | 137.9624 | 152.6732 | 168.9977 | 187.1158 | 207.2276 | 229.5557 | 254.3479 | 281.88 | 312.4586 | 346.4254 | 384.1602 | 426.0862 | 472.6742 | 524.4482 | 581.9919 | 645.9545 | 717.0594 | 796.1117 | 884.0076 | 954.1279 | 954.1279 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 41.9899 | 47.8017 | 54.2401 | 61.3742 | 69.2809 | 78.0455 | 87.763 | 98.5391 | 110.4912 | 123.75 | 138.4608 | 154.7854 | 172.9034 | 193.0152 | 215.3433 | 240.1356 | 267.6676 | 295.4473 | 323.8758 | 354.0084 | 385.4519 | 417.5266 | 449.1327 | 478.557 | 503.1973 | 519.1656 | 520.7219 | 499.462 | 415.5386 | 197.778 |  | 1633.0386 | 1801.9082 | 1988.9852 | 2196.2773 | 2426.0166 | 2680.6848 | 2963.0417 | 3276.1564 | 3623.4422 | 4008.6955 | 4436.1395 | 4910.4719 | 5436.9191 | 6021.2956 | 6670.0711 | 7390.4447 | 8190.4273 | 9078.9339 | 10065.8862 | 11162.3269 | 12380.5468 | 13734.2271 | 15238.5968 | 16910.6089 | 18769.1366 | 20835.1916 | 23132.1673 | 25686.11 | 27723.5553 | 27723.5553 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 1632.383 | 1801.2526 | 1988.3296 | 2195.6217 | 2425.361 | 2680.0292 | 2962.3861 | 3275.5008 | 3622.7866 | 4008.0399 | 4435.4839 | 4909.8163 | 5436.2635 | 6020.6399 | 6669.4155 | 7389.7891 | 8189.7717 | 9078.1492 | 10064.846 | 11160.936 | 12378.6724 | 13731.6832 | 15235.1226 | 16905.8376 | 18762.5514 | 20826.063 | 23119.4639 | 25668.3713 | 27698.7108 | 27688.6658 |  | 1674.3729 | 1849.0543 | 2042.5697 | 2256.996 | 2494.6419 | 2758.0747 | 3050.1491 | 3374.0399 | 3733.2778 | 4131.79 | 4573.9448 | 5064.6017 | 5609.1669 | 6213.6552 | 6884.7588 | 7629.9247 | 8457.4393 | 9373.5965 | 10388.7218 | 11514.9444 | 12764.1243 | 14149.2098 | 15684.2552 | 17384.3946 | 19265.7487 | 21345.2286 | 23640.1858 | 26167.8333 | 28114.2494 | 27886.4438 |  | 56.5304 | 62.3761 | 68.8521 | 76.0278 | 83.9806 | 92.7964 | 102.5707 | 113.4097 | 125.4315 | 138.7677 | 153.5644 | 169.9842 | 188.2081 | 208.4373 | 230.8957 | 255.8327 | 283.5254 | 314.2826 | 348.4476 | 386.4027 | 428.5734 | 475.4334 | 527.5097 | 585.3892 | 649.7252 | 721.2452 | 800.7589 | 889.1679 | 959.6975 | 959.6975 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 41.849 | 47.6947 | 54.1707 | 61.3464 | 69.2992 | 78.115 | 87.8893 | 98.7282 | 110.7501 | 124.0863 | 138.883 | 155.3028 | 173.5267 | 193.7559 | 216.2143 | 241.1513 | 268.844 | 296.7098 | 325.1539 | 355.2559 | 386.5981 | 418.4658 | 449.7085 | 478.5409 | 502.2568 | 516.8206 | 516.2809 | 491.9317 | 403.334 | 178.3869 |  | 3.9353 | 4.3423 | 4.7931 | 5.2926 | 5.8462 | 6.4599 | 7.1404 | 7.8949 | 8.7318 | 9.6602 | 10.6903 | 11.8333 | 13.1019 | 14.5102 | 16.0736 | 17.8096 | 19.7374 | 21.8785 | 24.2569 | 26.8991 | 29.8348 | 33.0969 | 36.7221 | 40.7514 | 45.2301 | 50.2089 | 55.7441 | 61.8987 | 66.8085 | 66.8085 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.8676 | 2.2745 | 2.7254 | 3.2249 | 3.7785 | 4.3922 | 5.0727 | 5.8272 | 6.6641 | 7.5925 | 8.6225 | 9.7656 | 11.0342 | 12.4425 | 14.0059 | 15.7419 | 17.6697 | 19.4036 | 20.9762 | 22.5124 | 23.923 | 25.0736 | 25.7647 | 25.703 | 24.4608 | 21.418 | 15.6786 | 5.9524 | -11.549 | -43.2302 |  | 50.1665 | 55.3542 | 61.1011 | 67.4691 | 74.5266 | 82.35 | 91.0239 | 100.6427 | 111.3112 | 123.1461 | 136.2771 | 150.8485 | 167.0208 | 184.9727 | 204.9029 | 227.0326 | 251.6079 | 278.9026 | 309.2215 | 342.9039 | 380.3273 | 421.912 | 468.1259 | 519.4897 | 576.5832 | 640.0519 | 710.6144 | 789.0709 | 851.6607 | 851.6607 |  | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.024106 | 0.031954 | 0.042727 | 0.057582 | 0.078148 | 0.10673 | 0.14657 | 0.2023 | 0.28043 | 0.39025 | 0.54493 | 0.76322 | 1.0718 |  | 50.1464 | 55.334 | 61.081 | 67.4489 | 74.5065 | 82.3298 | 91.0038 | 100.6226 | 111.2911 | 123.126 | 136.257 | 150.8283 | 167.0006 | 184.9525 | 204.8828 | 227.0125 | 251.5877 | 278.8785 | 309.1895 | 342.8612 | 380.2697 | 421.8339 | 468.0191 | 519.3431 | 576.3809 | 639.7714 | 710.2241 | 788.5259 | 850.8974 | 850.5889 |  | 1768.2359 | 1954.3575 | 2160.5467 | 2389.0162 | 2642.2261 | 2922.9117 | 3234.1148 | 3579.2179 | 3961.9831 | 4386.5947 | 4857.7073 | 5380.4984 | 5960.7285 | 6604.806 | 7319.8618 | 8113.8302 | 8995.5407 | 9968.5883 | 11044.0415 | 12235.5739 | 13554.9151 | 15014.5831 | 16627.7476 | 18407.9816 | 20368.8472 | 22523.2386 | 24882.3694 | 27454.2434 | 29356.9319 | 28872.1894
| TRUE | 1563 | 22006112 | FB | Blank | 11 | CAP NO.3 | OVERCURRENT | Blank | Brown Boveri | ICM21_1060 | ICM21 1060 | ICM21 | Electromechanical |  | 0.2894 | 2190 |  | 9.9 | 0.0088019 | 0.0046268 | 0.0041751 | 50.955 | 1480.5706 | 1531.5256 | 51.2524 | 3.5679 | 45.4828 |  | 14.217 | 0.023831 | 0.012527 | 0.011304 | 137.9624 | 4008.6955 | 4146.6579 | 138.7677 | 9.6602 | 123.1461 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.02014 |  | 1631.8287 | 4418.232 | 45.8496 | 4372.3824 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0051032 | 0.005631 | 0.0062156 | 0.0068634 | 0.0075813 | 0.0083771 | 0.0092595 | 0.010238 | 0.011323 | 0.012527 | 0.013863 | 0.015345 | 0.01699 | 0.018817 | 0.020844 | 0.023095 | 0.025595 | 0.028372 | 0.031456 | 0.034882 | 0.038689 | 0.042919 | 0.047621 | 0.052846 | 0.058654 | 0.06511 | 0.072288 | 0.080269 | 0.086636 | 0.086636 | 1799.8731 | 1985.9948 | 2192.184 | 2420.6535 | 2673.8634 | 2954.549 | 3265.7521 | 3610.8552 | 3993.6204 | 4418.232 | 4889.3445 | 5412.1357 | 5992.3657 | 6636.4433 | 7351.4991 | 8145.4675 | 9027.1779 | 10006.4562 | 11094.2375 | 12302.6928 | 13645.3686 | 15137.3436 | 16795.4027 | 18638.2309 | 20686.6296 | 22963.757 | 25495.3963 | 28310.255 | 30555.8499 | 30555.8499 |  | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 37.8752 | 50.2059 | 67.132 | 90.4712 | 122.7845 | 167.6879 | 230.2945 | 317.8447 | 440.6046 | 613.147 | 856.1792 | 1199.1529 | 1683.9903 |  | 56.2023 | 62.0141 | 68.4525 | 75.5866 | 83.4933 | 92.2579 | 101.9754 | 112.7515 | 124.7036 | 137.9624 | 152.6732 | 168.9977 | 187.1158 | 207.2276 | 229.5557 | 254.3479 | 281.88 | 312.4586 | 346.4254 | 384.1602 | 426.0862 | 472.6742 | 524.4482 | 581.9919 | 645.9545 | 717.0594 | 796.1117 | 884.0076 | 954.1279 | 954.1279 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 41.9899 | 47.8017 | 54.2401 | 61.3742 | 69.2809 | 78.0455 | 87.763 | 98.5391 | 110.4912 | 123.75 | 138.4608 | 154.7854 | 172.9034 | 193.0152 | 215.3433 | 240.1356 | 267.6676 | 295.4473 | 323.8758 | 354.0084 | 385.4519 | 417.5266 | 449.1327 | 478.557 | 503.1973 | 519.1656 | 520.7219 | 499.462 | 415.5386 | 197.778 |  | 1633.0386 | 1801.9082 | 1988.9852 | 2196.2773 | 2426.0166 | 2680.6848 | 2963.0417 | 3276.1564 | 3623.4422 | 4008.6955 | 4436.1395 | 4910.4719 | 5436.9191 | 6021.2956 | 6670.0711 | 7390.4447 | 8190.4273 | 9078.9339 | 10065.8862 | 11162.3269 | 12380.5468 | 13734.2271 | 15238.5968 | 16910.6089 | 18769.1366 | 20835.1916 | 23132.1673 | 25686.11 | 27723.5553 | 27723.5553 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 1632.383 | 1801.2526 | 1988.3296 | 2195.6217 | 2425.361 | 2680.0292 | 2962.3861 | 3275.5008 | 3622.7866 | 4008.0399 | 4435.4839 | 4909.8163 | 5436.2635 | 6020.6399 | 6669.4155 | 7389.7891 | 8189.7717 | 9078.1492 | 10064.846 | 11160.936 | 12378.6724 | 13731.6832 | 15235.1226 | 16905.8376 | 18762.5514 | 20826.063 | 23119.4639 | 25668.3713 | 27698.7108 | 27688.6658 |  | 1674.3729 | 1849.0543 | 2042.5697 | 2256.996 | 2494.6419 | 2758.0747 | 3050.1491 | 3374.0399 | 3733.2778 | 4131.79 | 4573.9448 | 5064.6017 | 5609.1669 | 6213.6552 | 6884.7588 | 7629.9247 | 8457.4393 | 9373.5965 | 10388.7218 | 11514.9444 | 12764.1243 | 14149.2098 | 15684.2552 | 17384.3946 | 19265.7487 | 21345.2286 | 23640.1858 | 26167.8333 | 28114.2494 | 27886.4438 |  | 56.5304 | 62.3761 | 68.8521 | 76.0278 | 83.9806 | 92.7964 | 102.5707 | 113.4097 | 125.4315 | 138.7677 | 153.5644 | 169.9842 | 188.2081 | 208.4373 | 230.8957 | 255.8327 | 283.5254 | 314.2826 | 348.4476 | 386.4027 | 428.5734 | 475.4334 | 527.5097 | 585.3892 | 649.7252 | 721.2452 | 800.7589 | 889.1679 | 959.6975 | 959.6975 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 41.849 | 47.6947 | 54.1707 | 61.3464 | 69.2992 | 78.115 | 87.8893 | 98.7282 | 110.7501 | 124.0863 | 138.883 | 155.3028 | 173.5267 | 193.7559 | 216.2143 | 241.1513 | 268.844 | 296.7098 | 325.1539 | 355.2559 | 386.5981 | 418.4658 | 449.7085 | 478.5409 | 502.2568 | 516.8206 | 516.2809 | 491.9317 | 403.334 | 178.3869 |  | 3.9353 | 4.3423 | 4.7931 | 5.2926 | 5.8462 | 6.4599 | 7.1404 | 7.8949 | 8.7318 | 9.6602 | 10.6903 | 11.8333 | 13.1019 | 14.5102 | 16.0736 | 17.8096 | 19.7374 | 21.8785 | 24.2569 | 26.8991 | 29.8348 | 33.0969 | 36.7221 | 40.7514 | 45.2301 | 50.2089 | 55.7441 | 61.8987 | 66.8085 | 66.8085 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.8676 | 2.2745 | 2.7254 | 3.2249 | 3.7785 | 4.3922 | 5.0727 | 5.8272 | 6.6641 | 7.5925 | 8.6225 | 9.7656 | 11.0342 | 12.4425 | 14.0059 | 15.7419 | 17.6697 | 19.4036 | 20.9762 | 22.5124 | 23.923 | 25.0736 | 25.7647 | 25.703 | 24.4608 | 21.418 | 15.6786 | 5.9524 | -11.549 | -43.2302 |  | 50.1665 | 55.3542 | 61.1011 | 67.4691 | 74.5266 | 82.35 | 91.0239 | 100.6427 | 111.3112 | 123.1461 | 136.2771 | 150.8485 | 167.0208 | 184.9727 | 204.9029 | 227.0326 | 251.6079 | 278.9026 | 309.2215 | 342.9039 | 380.3273 | 421.912 | 468.1259 | 519.4897 | 576.5832 | 640.0519 | 710.6144 | 789.0709 | 851.6607 | 851.6607 |  | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.024106 | 0.031954 | 0.042727 | 0.057582 | 0.078148 | 0.10673 | 0.14657 | 0.2023 | 0.28043 | 0.39025 | 0.54493 | 0.76322 | 1.0718 |  | 50.1464 | 55.334 | 61.081 | 67.4489 | 74.5065 | 82.3298 | 91.0038 | 100.6226 | 111.2911 | 123.126 | 136.257 | 150.8283 | 167.0006 | 184.9525 | 204.8828 | 227.0125 | 251.5877 | 278.8785 | 309.1895 | 342.8612 | 380.2697 | 421.8339 | 468.0191 | 519.3431 | 576.3809 | 639.7714 | 710.2241 | 788.5259 | 850.8974 | 850.5889 |  | 1768.2359 | 1954.3575 | 2160.5467 | 2389.0162 | 2642.2261 | 2922.9117 | 3234.1148 | 3579.2179 | 3961.9831 | 4386.5947 | 4857.7073 | 5380.4984 | 5960.7285 | 6604.806 | 7319.8618 | 8113.8302 | 8995.5407 | 9968.5883 | 11044.0415 | 12235.5739 | 13554.9151 | 15014.5831 | 16627.7476 | 18407.9816 | 20368.8472 | 22523.2386 | 24882.3694 | 27454.2434 | 29356.9319 | 28872.1894
| TRUE | 1564 | 22006110 | FB | Blank | 11 | CAP NO.3 | OVERCURRENT | Blank | Brown Boveri | ICM21_1060 | ICM21 1060 | ICM21 | Electromechanical |  | 0.2894 | 2190 |  | 9.9 | 0.0088019 | 0.0046268 | 0.0041751 | 50.955 | 1480.5706 | 1531.5256 | 51.2524 | 3.5679 | 45.4828 |  | 14.217 | 0.023831 | 0.012527 | 0.011304 | 137.9624 | 4008.6955 | 4146.6579 | 138.7677 | 9.6602 | 123.1461 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.6556 | 29.0804 | 14.6814 | 2.0677 | 0.02014 |  | 1631.8287 | 4418.232 | 45.8496 | 4372.3824 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0051032 | 0.005631 | 0.0062156 | 0.0068634 | 0.0075813 | 0.0083771 | 0.0092595 | 0.010238 | 0.011323 | 0.012527 | 0.013863 | 0.015345 | 0.01699 | 0.018817 | 0.020844 | 0.023095 | 0.025595 | 0.028372 | 0.031456 | 0.034882 | 0.038689 | 0.042919 | 0.047621 | 0.052846 | 0.058654 | 0.06511 | 0.072288 | 0.080269 | 0.086636 | 0.086636 | 1799.8731 | 1985.9948 | 2192.184 | 2420.6535 | 2673.8634 | 2954.549 | 3265.7521 | 3610.8552 | 3993.6204 | 4418.232 | 4889.3445 | 5412.1357 | 5992.3657 | 6636.4433 | 7351.4991 | 8145.4675 | 9027.1779 | 10006.4562 | 11094.2375 | 12302.6928 | 13645.3686 | 15137.3436 | 16795.4027 | 18638.2309 | 20686.6296 | 22963.757 | 25495.3963 | 28310.255 | 30555.8499 | 30555.8499 |  | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 31.6435 | 37.8752 | 50.2059 | 67.132 | 90.4712 | 122.7845 | 167.6879 | 230.2945 | 317.8447 | 440.6046 | 613.147 | 856.1792 | 1199.1529 | 1683.9903 |  | 56.2023 | 62.0141 | 68.4525 | 75.5866 | 83.4933 | 92.2579 | 101.9754 | 112.7515 | 124.7036 | 137.9624 | 152.6732 | 168.9977 | 187.1158 | 207.2276 | 229.5557 | 254.3479 | 281.88 | 312.4586 | 346.4254 | 384.1602 | 426.0862 | 472.6742 | 524.4482 | 581.9919 | 645.9545 | 717.0594 | 796.1117 | 884.0076 | 954.1279 | 954.1279 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 41.9899 | 47.8017 | 54.2401 | 61.3742 | 69.2809 | 78.0455 | 87.763 | 98.5391 | 110.4912 | 123.75 | 138.4608 | 154.7854 | 172.9034 | 193.0152 | 215.3433 | 240.1356 | 267.6676 | 295.4473 | 323.8758 | 354.0084 | 385.4519 | 417.5266 | 449.1327 | 478.557 | 503.1973 | 519.1656 | 520.7219 | 499.462 | 415.5386 | 197.778 |  | 1633.0386 | 1801.9082 | 1988.9852 | 2196.2773 | 2426.0166 | 2680.6848 | 2963.0417 | 3276.1564 | 3623.4422 | 4008.6955 | 4436.1395 | 4910.4719 | 5436.9191 | 6021.2956 | 6670.0711 | 7390.4447 | 8190.4273 | 9078.9339 | 10065.8862 | 11162.3269 | 12380.5468 | 13734.2271 | 15238.5968 | 16910.6089 | 18769.1366 | 20835.1916 | 23132.1673 | 25686.11 | 27723.5553 | 27723.5553 |  | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.6556 | 0.78471 | 1.0402 | 1.3909 | 1.8744 | 2.5439 | 3.4742 | 4.7713 | 6.5852 | 9.1286 | 12.7034 | 17.7386 | 24.8445 | 34.8896 |  | 1632.383 | 1801.2526 | 1988.3296 | 2195.6217 | 2425.361 | 2680.0292 | 2962.3861 | 3275.5008 | 3622.7866 | 4008.0399 | 4435.4839 | 4909.8163 | 5436.2635 | 6020.6399 | 6669.4155 | 7389.7891 | 8189.7717 | 9078.1492 | 10064.846 | 11160.936 | 12378.6724 | 13731.6832 | 15235.1226 | 16905.8376 | 18762.5514 | 20826.063 | 23119.4639 | 25668.3713 | 27698.7108 | 27688.6658 |  | 1674.3729 | 1849.0543 | 2042.5697 | 2256.996 | 2494.6419 | 2758.0747 | 3050.1491 | 3374.0399 | 3733.2778 | 4131.79 | 4573.9448 | 5064.6017 | 5609.1669 | 6213.6552 | 6884.7588 | 7629.9247 | 8457.4393 | 9373.5965 | 10388.7218 | 11514.9444 | 12764.1243 | 14149.2098 | 15684.2552 | 17384.3946 | 19265.7487 | 21345.2286 | 23640.1858 | 26167.8333 | 28114.2494 | 27886.4438 |  | 56.5304 | 62.3761 | 68.8521 | 76.0278 | 83.9806 | 92.7964 | 102.5707 | 113.4097 | 125.4315 | 138.7677 | 153.5644 | 169.9842 | 188.2081 | 208.4373 | 230.8957 | 255.8327 | 283.5254 | 314.2826 | 348.4476 | 386.4027 | 428.5734 | 475.4334 | 527.5097 | 585.3892 | 649.7252 | 721.2452 | 800.7589 | 889.1679 | 959.6975 | 959.6975 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 41.849 | 47.6947 | 54.1707 | 61.3464 | 69.2992 | 78.115 | 87.8893 | 98.7282 | 110.7501 | 124.0863 | 138.883 | 155.3028 | 173.5267 | 193.7559 | 216.2143 | 241.1513 | 268.844 | 296.7098 | 325.1539 | 355.2559 | 386.5981 | 418.4658 | 449.7085 | 478.5409 | 502.2568 | 516.8206 | 516.2809 | 491.9317 | 403.334 | 178.3869 |  | 3.9353 | 4.3423 | 4.7931 | 5.2926 | 5.8462 | 6.4599 | 7.1404 | 7.8949 | 8.7318 | 9.6602 | 10.6903 | 11.8333 | 13.1019 | 14.5102 | 16.0736 | 17.8096 | 19.7374 | 21.8785 | 24.2569 | 26.8991 | 29.8348 | 33.0969 | 36.7221 | 40.7514 | 45.2301 | 50.2089 | 55.7441 | 61.8987 | 66.8085 | 66.8085 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.8676 | 2.2745 | 2.7254 | 3.2249 | 3.7785 | 4.3922 | 5.0727 | 5.8272 | 6.6641 | 7.5925 | 8.6225 | 9.7656 | 11.0342 | 12.4425 | 14.0059 | 15.7419 | 17.6697 | 19.4036 | 20.9762 | 22.5124 | 23.923 | 25.0736 | 25.7647 | 25.703 | 24.4608 | 21.418 | 15.6786 | 5.9524 | -11.549 | -43.2302 |  | 50.1665 | 55.3542 | 61.1011 | 67.4691 | 74.5266 | 82.35 | 91.0239 | 100.6427 | 111.3112 | 123.1461 | 136.2771 | 150.8485 | 167.0208 | 184.9727 | 204.9029 | 227.0326 | 251.6079 | 278.9026 | 309.2215 | 342.9039 | 380.3273 | 421.912 | 468.1259 | 519.4897 | 576.5832 | 640.0519 | 710.6144 | 789.0709 | 851.6607 | 851.6607 |  | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.02014 | 0.024106 | 0.031954 | 0.042727 | 0.057582 | 0.078148 | 0.10673 | 0.14657 | 0.2023 | 0.28043 | 0.39025 | 0.54493 | 0.76322 | 1.0718 |  | 50.1464 | 55.334 | 61.081 | 67.4489 | 74.5065 | 82.3298 | 91.0038 | 100.6226 | 111.2911 | 123.126 | 136.257 | 150.8283 | 167.0006 | 184.9525 | 204.8828 | 227.0125 | 251.5877 | 278.8785 | 309.1895 | 342.8612 | 380.2697 | 421.8339 | 468.0191 | 519.3431 | 576.3809 | 639.7714 | 710.2241 | 788.5259 | 850.8974 | 850.5889 |  | 1768.2359 | 1954.3575 | 2160.5467 | 2389.0162 | 2642.2261 | 2922.9117 | 3234.1148 | 3579.2179 | 3961.9831 | 4386.5947 | 4857.7073 | 5380.4984 | 5960.7285 | 6604.806 | 7319.8618 | 8113.8302 | 8995.5407 | 9968.5883 | 11044.0415 | 12235.5739 | 13554.9151 | 15014.5831 | 16627.7476 | 18407.9816 | 20368.8472 | 22523.2386 | 24882.3694 | 27454.2434 | 29356.9319 | 28872.1894
| FALSE | 1565 | 22009923 | FB | Blank | 11 | CAP NO.3 | METER (DIGITAL MULTI FN.) | I | Schneider | ION_6200 | ION 6200 | ION 6000s | Digital |  | 0 | 1 |  | 1.4709 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 4.8786 | 0.0081995 | 0 | 0.0081995 | 22.5486 | 0 | 22.5486 | 23.2752 | 3.2806 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 49.1045 | 30.9493 | 18.1552 |  | 0.11989 |  | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 128.5398 | 183.6741 | 258.3682 | 361.9817 | 508.4173 | 715.6872 | 1009.4614 | 1426.3461 | 2018.57 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 132.6818 | 189.5929 | 266.6938 | 373.6462 | 524.8006 | 738.7495 | 1041.9903 | 1472.3087 | 2083.6164 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.7014 | 26.7229 | 37.5902 | 52.665 | 73.9701 | 104.126 | 146.8675 | 207.5204 | 293.6836 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 133.0601 | 194.2933 | 279.9229 | 399.9899 | 562.6522 | 788.2929 | 1107.188 | 1558.5626 | 2198.3191 | 3106.1752 | 4395.87 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 1566 | 22009631 | FB | Blank | 11 | CB TR NO.1 | CB FAIL TIMER | Blank | RMS | 2T105 | 2T105 | RMS 2T1XX | Electronic |  | 0 | 2190 |  | 3.6151 | 0.004397 | 0 | 0.004397 | 12.0918 | 0 | 12.0918 | 12.4815 | 1.7593 | 0 |  | 10.5562 | 0.050929 | 0 | 0.050929 | 140.0552 | 0 | 140.0552 | 144.5683 | 20.3768 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 26.3326 | 305.0003 | 30.9493 | 274.051 |  | 0.10716 |  | 4.024 | 4.4792 | 4.9858 | 5.5498 | 6.1775 | 6.8763 | 7.654 | 8.5198 | 9.4835 | 10.5562 | 11.7502 | 13.0793 | 14.5587 | 16.2055 | 18.0385 | 20.0789 | 22.3501 | 24.8781 | 27.6922 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0044569 | 0.0057019 | 0.0073492 | 0.0095373 | 0.012454 | 0.016355 | 0.021586 | 0.028623 | 0.03811 | 0.050929 | 0.068287 | 0.091832 | 0.12382 | 0.16736 | 0.22668 | 0.30761 | 0.41814 | 0.56925 | 0.77601 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.691 | 34.1471 | 44.0125 | 57.1163 | 74.5835 | 97.9427 | 129.2745 | 171.4138 | 228.2283 | 305.0003 | 408.9505 | 549.9584 | 741.5521 | 1002.2684 | 1357.5238 | 1842.1881 | 2504.1259 | 3409.0692 | 4647.327 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 12.2564 | 15.6802 | 20.2104 | 26.2276 | 34.2485 | 44.975 | 59.3624 | 78.7127 | 104.8018 | 140.0552 | 187.7888 | 252.5392 | 340.5185 | 460.2386 | 623.3707 | 845.9271 | 1149.8869 | 1565.4341 | 2134.0383 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | -1.9554 | 1.4684 | 5.9986 | 12.0158 | 20.0367 | 30.7632 | 45.1506 | 64.5009 | 90.5899 | 125.8434 | 173.577 | 238.3274 | 326.3066 | 446.0267 | 609.1589 | 831.7153 | 1135.6751 | 1548.4234 | 2111.4896 | 2173.3638 | 2162.8816 | 2148.3689 | 2128.2017 | 2100.0836 | 2060.7628 | 2005.6284 | 1928.1355 | 1818.984 | 1664.9464 | 1447.1944 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -1.9554 | 1.4684 | 5.9986 | 12.0158 | 20.0367 | 30.7632 | 45.1506 | 64.5009 | 90.5899 | 125.8434 | 173.577 | 238.3274 | 326.3066 | 446.0267 | 609.1589 | 831.7153 | 1135.6751 | 1548.4234 | 2111.4896 | 2173.3638 | 2162.8816 | 2148.3689 | 2128.2017 | 2100.0836 | 2060.7628 | 2005.6284 | 1928.1355 | 1818.984 | 1664.9464 | 1447.1944 |  | 12.6514 | 16.1855 | 20.8617 | 27.0728 | 35.3521 | 46.4243 | 61.2753 | 81.2491 | 108.1789 | 144.5683 | 193.8401 | 260.6771 | 351.4913 | 475.0693 | 643.4582 | 873.1863 | 1186.9409 | 1615.8787 | 2202.8055 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | -2.0184 | 1.5157 | 6.1919 | 12.403 | 20.6824 | 31.7545 | 46.6056 | 66.5793 | 93.5091 | 129.8986 | 179.1703 | 246.0073 | 336.8215 | 460.3995 | 628.7885 | 858.5165 | 1172.2711 | 1598.3199 | 2179.5303 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 1.7832 | 2.2813 | 2.9404 | 3.8159 | 4.9828 | 6.5435 | 8.6367 | 11.452 | 15.2477 | 20.3768 | 27.3216 | 36.7422 | 49.5423 | 66.9605 | 90.6948 | 123.0747 | 167.2981 | 227.7564 | 310.4832 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | -0.28449 | 0.21364 | 0.87274 | 1.7482 | 2.9152 | 4.4758 | 6.569 | 9.3843 | 13.18 | 18.3091 | 25.2539 | 34.6745 | 47.4746 | 64.8928 | 88.6271 | 121.007 | 165.2304 | 225.2815 | 307.2025 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -4.2583 | 3.1978 | 13.0632 | 26.167 | 43.6342 | 66.9934 | 98.3252 | 140.4645 | 197.279 | 274.051 | 378.0012 | 519.0091 | 710.6028 | 971.3191 | 1326.5745 | 1811.2388 | 2473.1766 | 3372.0248 | 4598.2225 | 4732.9667 | 4710.1395 | 4678.5351 | 4634.6167 | 4573.3835 | 4487.7538 | 4367.6869 | 4198.9295 | 3961.2286 | 3625.7787 | 3151.5769
| TRUE | 1567 | 22009632 | FB | Blank | 11 | CB TR NO.2 | CB FAIL TIMER | Blank | RMS | 2T105 | 2T105 | RMS 2T1XX | Electronic |  | 0 | 2190 |  | 3.6151 | 0.004397 | 0 | 0.004397 | 12.0918 | 0 | 12.0918 | 12.4815 | 1.7593 | 0 |  | 10.5562 | 0.050929 | 0 | 0.050929 | 140.0552 | 0 | 140.0552 | 144.5683 | 20.3768 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 26.3326 | 305.0003 | 30.9493 | 274.051 |  | 0.10716 |  | 4.024 | 4.4792 | 4.9858 | 5.5498 | 6.1775 | 6.8763 | 7.654 | 8.5198 | 9.4835 | 10.5562 | 11.7502 | 13.0793 | 14.5587 | 16.2055 | 18.0385 | 20.0789 | 22.3501 | 24.8781 | 27.6922 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0044569 | 0.0057019 | 0.0073492 | 0.0095373 | 0.012454 | 0.016355 | 0.021586 | 0.028623 | 0.03811 | 0.050929 | 0.068287 | 0.091832 | 0.12382 | 0.16736 | 0.22668 | 0.30761 | 0.41814 | 0.56925 | 0.77601 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.691 | 34.1471 | 44.0125 | 57.1163 | 74.5835 | 97.9427 | 129.2745 | 171.4138 | 228.2283 | 305.0003 | 408.9505 | 549.9584 | 741.5521 | 1002.2684 | 1357.5238 | 1842.1881 | 2504.1259 | 3409.0692 | 4647.327 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 12.2564 | 15.6802 | 20.2104 | 26.2276 | 34.2485 | 44.975 | 59.3624 | 78.7127 | 104.8018 | 140.0552 | 187.7888 | 252.5392 | 340.5185 | 460.2386 | 623.3707 | 845.9271 | 1149.8869 | 1565.4341 | 2134.0383 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | -1.9554 | 1.4684 | 5.9986 | 12.0158 | 20.0367 | 30.7632 | 45.1506 | 64.5009 | 90.5899 | 125.8434 | 173.577 | 238.3274 | 326.3066 | 446.0267 | 609.1589 | 831.7153 | 1135.6751 | 1548.4234 | 2111.4896 | 2173.3638 | 2162.8816 | 2148.3689 | 2128.2017 | 2100.0836 | 2060.7628 | 2005.6284 | 1928.1355 | 1818.984 | 1664.9464 | 1447.1944 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -1.9554 | 1.4684 | 5.9986 | 12.0158 | 20.0367 | 30.7632 | 45.1506 | 64.5009 | 90.5899 | 125.8434 | 173.577 | 238.3274 | 326.3066 | 446.0267 | 609.1589 | 831.7153 | 1135.6751 | 1548.4234 | 2111.4896 | 2173.3638 | 2162.8816 | 2148.3689 | 2128.2017 | 2100.0836 | 2060.7628 | 2005.6284 | 1928.1355 | 1818.984 | 1664.9464 | 1447.1944 |  | 12.6514 | 16.1855 | 20.8617 | 27.0728 | 35.3521 | 46.4243 | 61.2753 | 81.2491 | 108.1789 | 144.5683 | 193.8401 | 260.6771 | 351.4913 | 475.0693 | 643.4582 | 873.1863 | 1186.9409 | 1615.8787 | 2202.8055 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | -2.0184 | 1.5157 | 6.1919 | 12.403 | 20.6824 | 31.7545 | 46.6056 | 66.5793 | 93.5091 | 129.8986 | 179.1703 | 246.0073 | 336.8215 | 460.3995 | 628.7885 | 858.5165 | 1172.2711 | 1598.3199 | 2179.5303 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 1.7832 | 2.2813 | 2.9404 | 3.8159 | 4.9828 | 6.5435 | 8.6367 | 11.452 | 15.2477 | 20.3768 | 27.3216 | 36.7422 | 49.5423 | 66.9605 | 90.6948 | 123.0747 | 167.2981 | 227.7564 | 310.4832 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | -0.28449 | 0.21364 | 0.87274 | 1.7482 | 2.9152 | 4.4758 | 6.569 | 9.3843 | 13.18 | 18.3091 | 25.2539 | 34.6745 | 47.4746 | 64.8928 | 88.6271 | 121.007 | 165.2304 | 225.2815 | 307.2025 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -4.2583 | 3.1978 | 13.0632 | 26.167 | 43.6342 | 66.9934 | 98.3252 | 140.4645 | 197.279 | 274.051 | 378.0012 | 519.0091 | 710.6028 | 971.3191 | 1326.5745 | 1811.2388 | 2473.1766 | 3372.0248 | 4598.2225 | 4732.9667 | 4710.1395 | 4678.5351 | 4634.6167 | 4573.3835 | 4487.7538 | 4367.6869 | 4198.9295 | 3961.2286 | 3625.7787 | 3151.5769
| TRUE | 1568 | 22009633 | FB | Blank | 11 | CB TR NO.3 | CB FAIL TIMER | Blank | RMS | 2T105 | 2T105 | RMS 2T1XX | Electronic |  | 0 | 2190 |  | 3.6151 | 0.004397 | 0 | 0.004397 | 12.0918 | 0 | 12.0918 | 12.4815 | 1.7593 | 0 |  | 10.5562 | 0.050929 | 0 | 0.050929 | 140.0552 | 0 | 140.0552 | 144.5683 | 20.3768 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 26.3326 | 305.0003 | 30.9493 | 274.051 |  | 0.10716 |  | 4.024 | 4.4792 | 4.9858 | 5.5498 | 6.1775 | 6.8763 | 7.654 | 8.5198 | 9.4835 | 10.5562 | 11.7502 | 13.0793 | 14.5587 | 16.2055 | 18.0385 | 20.0789 | 22.3501 | 24.8781 | 27.6922 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0044569 | 0.0057019 | 0.0073492 | 0.0095373 | 0.012454 | 0.016355 | 0.021586 | 0.028623 | 0.03811 | 0.050929 | 0.068287 | 0.091832 | 0.12382 | 0.16736 | 0.22668 | 0.30761 | 0.41814 | 0.56925 | 0.77601 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.691 | 34.1471 | 44.0125 | 57.1163 | 74.5835 | 97.9427 | 129.2745 | 171.4138 | 228.2283 | 305.0003 | 408.9505 | 549.9584 | 741.5521 | 1002.2684 | 1357.5238 | 1842.1881 | 2504.1259 | 3409.0692 | 4647.327 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 12.2564 | 15.6802 | 20.2104 | 26.2276 | 34.2485 | 44.975 | 59.3624 | 78.7127 | 104.8018 | 140.0552 | 187.7888 | 252.5392 | 340.5185 | 460.2386 | 623.3707 | 845.9271 | 1149.8869 | 1565.4341 | 2134.0383 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | -1.9554 | 1.4684 | 5.9986 | 12.0158 | 20.0367 | 30.7632 | 45.1506 | 64.5009 | 90.5899 | 125.8434 | 173.577 | 238.3274 | 326.3066 | 446.0267 | 609.1589 | 831.7153 | 1135.6751 | 1548.4234 | 2111.4896 | 2173.3638 | 2162.8816 | 2148.3689 | 2128.2017 | 2100.0836 | 2060.7628 | 2005.6284 | 1928.1355 | 1818.984 | 1664.9464 | 1447.1944 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -1.9554 | 1.4684 | 5.9986 | 12.0158 | 20.0367 | 30.7632 | 45.1506 | 64.5009 | 90.5899 | 125.8434 | 173.577 | 238.3274 | 326.3066 | 446.0267 | 609.1589 | 831.7153 | 1135.6751 | 1548.4234 | 2111.4896 | 2173.3638 | 2162.8816 | 2148.3689 | 2128.2017 | 2100.0836 | 2060.7628 | 2005.6284 | 1928.1355 | 1818.984 | 1664.9464 | 1447.1944 |  | 12.6514 | 16.1855 | 20.8617 | 27.0728 | 35.3521 | 46.4243 | 61.2753 | 81.2491 | 108.1789 | 144.5683 | 193.8401 | 260.6771 | 351.4913 | 475.0693 | 643.4582 | 873.1863 | 1186.9409 | 1615.8787 | 2202.8055 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | -2.0184 | 1.5157 | 6.1919 | 12.403 | 20.6824 | 31.7545 | 46.6056 | 66.5793 | 93.5091 | 129.8986 | 179.1703 | 246.0073 | 336.8215 | 460.3995 | 628.7885 | 858.5165 | 1172.2711 | 1598.3199 | 2179.5303 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 1.7832 | 2.2813 | 2.9404 | 3.8159 | 4.9828 | 6.5435 | 8.6367 | 11.452 | 15.2477 | 20.3768 | 27.3216 | 36.7422 | 49.5423 | 66.9605 | 90.6948 | 123.0747 | 167.2981 | 227.7564 | 310.4832 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | -0.28449 | 0.21364 | 0.87274 | 1.7482 | 2.9152 | 4.4758 | 6.569 | 9.3843 | 13.18 | 18.3091 | 25.2539 | 34.6745 | 47.4746 | 64.8928 | 88.6271 | 121.007 | 165.2304 | 225.2815 | 307.2025 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -4.2583 | 3.1978 | 13.0632 | 26.167 | 43.6342 | 66.9934 | 98.3252 | 140.4645 | 197.279 | 274.051 | 378.0012 | 519.0091 | 710.6028 | 971.3191 | 1326.5745 | 1811.2388 | 2473.1766 | 3372.0248 | 4598.2225 | 4732.9667 | 4710.1395 | 4678.5351 | 4634.6167 | 4573.3835 | 4487.7538 | 4367.6869 | 4198.9295 | 3961.2286 | 3625.7787 | 3151.5769
| TRUE | 1569 | 22006113 | FB | Blank | 11 | ALLFDRS | MASTER EARTH FAULT | Blank | English Electric | CMU_590 | RI 009 | RI | Electromechanical |  | 0.81881 | 2190 |  | 6.6 | 0.003029 | 0.0024176 | 0.00061135 | 17.9891 | 773.6443 | 791.6335 | 22.3236 | 1.2361 | 23.7662 |  | 9.0234 | 0.0068603 | 0.0054756 | 0.0013846 | 40.7431 | 1752.2059 | 1792.949 | 50.5602 | 2.7996 | 53.8273 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 28.4268 | 1.8549 | 30.2818 | 14.7027 | 2.0677 | 0.056983 |  | 838.9594 | 1900.1361 | 47.1092 | 1853.0269 |  | 0.031275 |  | 6.8097 | 7.026 | 7.2492 | 7.4795 | 7.7172 | 7.9623 | 8.2153 | 8.4763 | 8.7456 | 9.0234 | 9.3101 | 9.6059 | 9.911 | 10.2259 | 10.5508 | 10.886 | 11.2318 | 11.5886 | 11.9568 | 12.3367 | 12.7286 | 13.133 | 13.5502 | 13.9807 | 14.4249 | 14.8831 | 15.356 | 15.8438 | 16.3472 | 16.8665 |  | 0.003281 | 0.0035556 | 0.0038548 | 0.0041809 | 0.0045364 | 0.0049241 | 0.0053468 | 0.005808 | 0.0063112 | 0.0068603 | 0.0074596 | 0.008114 | 0.0088284 | 0.0096087 | 0.010461 | 0.011392 | 0.012409 | 0.013521 | 0.014736 | 0.016065 | 0.017517 | 0.019105 | 0.020842 | 0.022741 | 0.024819 | 0.027092 | 0.02958 | 0.032301 | 0.03528 | 0.038541 |  | 0.0026188 | 0.002838 | 0.0030768 | 0.0033371 | 0.0036208 | 0.0039302 | 0.0042677 | 0.0046357 | 0.0050374 | 0.0054756 | 0.005954 | 0.0064763 | 0.0070466 | 0.0076693 | 0.0083496 | 0.0090928 | 0.0099048 | 0.010792 | 0.011762 | 0.012822 | 0.013982 | 0.015249 | 0.016635 | 0.018151 | 0.01981 | 0.021624 | 0.023609 | 0.025782 | 0.028159 | 0.030762 | 908.7726 | 984.826 | 1067.6975 | 1158.0192 | 1256.4835 | 1363.8483 | 1480.9433 | 1608.6771 | 1748.0448 | 1900.1361 | 2066.1446 | 2247.3777 | 2445.2678 | 2661.3839 | 2897.4451 | 3155.3353 | 3437.1187 | 3745.0573 | 4081.6302 | 4449.5548 | 4851.8094 | 5291.6585 | 5772.6811 | 6298.8006 | 6874.3185 | 7503.9511 | 8192.8694 | 8946.7439 | 9771.7925 | 10674.8342 |  | 32.9133 | 32.9133 | 32.9133 | 32.9133 | 32.9133 | 32.9133 | 32.9133 | 32.9133 | 32.9133 | 32.9133 | 32.9133 | 32.9133 | 32.9133 | 32.9133 | 32.9133 | 32.9133 | 32.9133 | 39.3952 | 52.2206 | 69.8261 | 94.1018 | 127.7118 | 174.4172 | 239.5362 | 330.5999 | 458.2862 | 637.7527 | 890.5378 | 1247.2751 | 1751.5691 |  | 19.4861 | 21.1168 | 22.8938 | 24.8305 | 26.9418 | 29.2439 | 31.7547 | 34.4936 | 37.4819 | 40.7431 | 44.3027 | 48.1887 | 52.4319 | 57.0659 | 62.1276 | 67.6573 | 73.6994 | 80.3023 | 87.5191 | 95.4083 | 104.0335 | 113.4648 | 123.779 | 135.0602 | 147.4005 | 160.9012 | 175.6732 | 191.8379 | 209.5288 | 228.892 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 5.2727 | 6.9034 | 8.6804 | 10.6171 | 12.7284 | 15.0305 | 17.5413 | 20.2802 | 23.2685 | 26.5297 | 30.0893 | 33.9753 | 38.2185 | 42.8525 | 47.9142 | 53.4439 | 59.486 | 63.2897 | 64.968 | 65.2543 | 63.3962 | 58.3132 | 48.458 | 31.6179 | 4.6329 | -37.0069 | -99.7365 | -192.7356 | -329.0996 | -527.5128 |  | 838.0225 | 908.155 | 984.5746 | 1067.8646 | 1158.6633 | 1257.6694 | 1365.6483 | 1483.4377 | 1611.9553 | 1752.2059 | 1905.2903 | 2072.414 | 2254.8978 | 2454.1887 | 2671.8721 | 2909.6849 | 3169.5307 | 3453.4955 | 3763.8655 | 4103.1463 | 4474.0843 | 4879.6902 | 5323.264 | 5808.4238 | 6339.1363 | 6919.7504 | 7555.0348 | 8250.2184 | 9011.035 | 9843.7727 |  | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 2.2202 | 2.9431 | 3.9353 | 5.3034 | 7.1976 | 9.8298 | 13.4998 | 18.632 | 25.8281 | 35.9425 | 50.189 | 70.294 | 98.7151 |  | 836.1675 | 906.3 | 982.7197 | 1066.0097 | 1156.8083 | 1255.8145 | 1363.7933 | 1481.5828 | 1610.1004 | 1750.351 | 1903.4353 | 2070.5591 | 2253.0429 | 2452.3338 | 2670.0171 | 2907.83 | 3167.6758 | 3451.2753 | 3760.9225 | 4099.211 | 4468.7809 | 4872.4926 | 5313.4342 | 5794.924 | 6320.5043 | 6893.9223 | 7519.0923 | 8200.0294 | 8940.7409 | 9745.0576 |  | 841.4402 | 913.2035 | 991.4001 | 1076.6268 | 1169.5367 | 1270.845 | 1381.3346 | 1501.8629 | 1633.3689 | 1776.8807 | 1933.5246 | 2104.5344 | 2291.2614 | 2495.1863 | 2717.9313 | 2961.2739 | 3227.1618 | 3514.565 | 3825.8904 | 4164.4653 | 4532.1771 | 4930.8058 | 5361.8921 | 5826.5419 | 6325.1373 | 6856.9154 | 7419.3558 | 8007.2938 | 8611.6414 | 9217.5449 |  | 24.1813 | 26.205 | 28.4101 | 30.8134 | 33.4334 | 36.2902 | 39.406 | 42.8048 | 46.5132 | 50.5602 | 54.9775 | 59.7998 | 65.0654 | 70.816 | 77.0973 | 83.9594 | 91.4573 | 99.6512 | 108.6069 | 118.3969 | 129.1004 | 140.8042 | 153.6036 | 167.603 | 182.9168 | 199.6705 | 218.0017 | 238.0614 | 260.0148 | 284.0436 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 9.4786 | 11.5023 | 13.7074 | 16.1107 | 18.7307 | 21.5876 | 24.7033 | 28.1021 | 31.8105 | 35.8575 | 40.2748 | 45.0971 | 50.3627 | 56.1133 | 62.3946 | 69.2567 | 76.7546 | 82.053 | 85.2795 | 87.205 | 87.0642 | 83.7541 | 75.6898 | 60.5998 | 35.2346 | -5.0504 | -66.8886 | -159.7505 | -297.155 | -498.3993 |  | 1.3389 | 1.451 | 1.5731 | 1.7062 | 1.8512 | 2.0094 | 2.1819 | 2.3701 | 2.5755 | 2.7996 | 3.0441 | 3.3112 | 3.6027 | 3.9211 | 4.2689 | 4.6489 | 5.0641 | 5.5178 | 6.0136 | 6.5557 | 7.1484 | 7.7964 | 8.5051 | 9.2803 | 10.1282 | 11.0559 | 12.0709 | 13.1816 | 14.3972 | 15.7277 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | -0.72882 | -0.61676 | -0.49466 | -0.36159 | -0.21652 | -0.058333 | 0.11419 | 0.30238 | 0.50772 | 0.7318 | 0.97639 | 1.2434 | 1.535 | 1.8534 | 2.2012 | 2.5811 | 2.9963 | 3.0428 | 2.7329 | 2.169 | 1.2365 | -0.22695 | -2.4525 | -5.7684 | -10.6414 | -17.7355 | -27.9953 | -42.7656 | -63.9617 | -94.3131 |  | 25.7438 | 27.8983 | 30.2459 | 32.8045 | 35.5938 | 38.6353 | 41.9524 | 45.5708 | 49.5189 | 53.8273 | 58.53 | 63.664 | 69.2699 | 75.3921 | 82.0792 | 89.3848 | 97.3672 | 106.0905 | 115.625 | 126.0476 | 137.4427 | 149.9029 | 163.5293 | 178.4333 | 194.7367 | 212.573 | 232.0888 | 253.4446 | 276.8167 | 302.3982 |  | 0.056983 | 0.056983 | 0.056983 | 0.056983 | 0.056983 | 0.056983 | 0.056983 | 0.056983 | 0.056983 | 0.056983 | 0.056983 | 0.056983 | 0.056983 | 0.056983 | 0.056983 | 0.056983 | 0.056983 | 0.068205 | 0.09041 | 0.12089 | 0.16292 | 0.22111 | 0.30197 | 0.41471 | 0.57237 | 0.79343 | 1.1041 | 1.5418 | 2.1594 | 3.0325 |  | 25.6869 | 27.8413 | 30.1889 | 32.7476 | 35.5369 | 38.5783 | 41.8954 | 45.5139 | 49.4619 | 53.7703 | 58.4731 | 63.6071 | 69.2129 | 75.3351 | 82.0223 | 89.3278 | 97.3102 | 106.0223 | 115.5346 | 125.9267 | 137.2798 | 149.6817 | 163.2274 | 178.0186 | 194.1643 | 211.7796 | 230.9846 | 251.9028 | 274.6573 | 299.3657 |  | 875.8768 | 951.9303 | 1034.8017 | 1125.1234 | 1223.5877 | 1330.9525 | 1448.0475 | 1575.7813 | 1715.149 | 1867.2403 | 2033.2488 | 2214.482 | 2412.372 | 2628.4881 | 2864.5494 | 3122.4396 | 3404.2229 | 3705.6831 | 4029.4374 | 4379.766 | 4757.7577 | 5164.0147 | 5598.3568 | 6059.392 | 6543.8948 | 7045.9091 | 7555.4565 | 8056.6805 | 8525.182 | 8924.1983
| TRUE | 1570 | 22015776 | FB | FB001 | 11 | FB1 | CURRENT INTERLOCK | Blank | English Electric | CAG39_1012 | CAG39 1012 | CAG | Electromechanical |  | 0.57434 | 2190 |  | 5.5 | 0.0019187 | 0.0013801 | 0.00053868 | 11.3121 | 441.6215 | 452.9336 | 13.2815 | 0.78149 | 20.3187 |  | 7.3552 | 0.0040026 | 0.0028789 | 0.0011237 | 23.5976 | 921.2421 | 944.8397 | 27.7059 | 1.6302 | 42.3857 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.059863 |  | 487.3154 | 1016.5616 | 46.5474 | 970.0141 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0.0014826 | 0.0015934 | 0.0017133 | 0.0018429 | 0.0019832 | 0.0021351 | 0.0022994 | 0.0024774 | 0.0026701 | 0.0028789 | 0.0031051 | 0.0033501 | 0.0036158 | 0.0039037 | 0.0042159 | 0.0045544 | 0.0049216 | 0.0053199 | 0.005752 | 0.0062209 | 0.0067298 | 0.0072822 | 0.0078819 | 0.008533 | 0.00924 | 0.010008 | 0.010842 | 0.011748 | 0.012732 | 0.013802 | 523.5095 | 562.6444 | 604.9691 | 650.7545 | 700.2951 | 753.9111 | 811.9504 | 874.7915 | 942.846 | 1016.5616 | 1096.4249 | 1182.9657 | 1276.76 | 1378.4345 | 1488.6711 | 1608.2119 | 1737.8643 | 1878.5069 | 2031.0962 | 2196.6729 | 2376.3703 | 2571.4215 | 2783.1694 | 3013.0757 | 3262.7321 | 3533.8715 | 3828.381 | 4148.3155 | 4495.9129 | 4873.6105 |  | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 38.7171 | 51.3218 | 68.6242 | 92.4821 | 125.5137 | 171.4152 | 235.4133 | 324.9096 | 450.3981 | 626.7756 | 875.2098 | 1225.8069 | 1721.421 |  | 12.1523 | 13.0608 | 14.0433 | 15.1061 | 16.2561 | 17.5007 | 18.8479 | 20.3067 | 21.8865 | 23.5976 | 25.4515 | 27.4604 | 29.6377 | 31.9978 | 34.5568 | 37.3317 | 40.3414 | 43.6061 | 47.1482 | 50.9918 | 55.1631 | 59.6909 | 64.6062 | 69.9431 | 75.7384 | 82.0324 | 88.8689 | 96.2956 | 104.3644 | 113.132 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | -2.0606 | -1.1522 | -0.16969 | 0.89314 | 2.0431 | 3.2877 | 4.635 | 6.0937 | 7.6735 | 9.3847 | 11.2386 | 13.2475 | 15.4247 | 17.7849 | 20.3438 | 23.1188 | 26.1284 | 26.5941 | 24.5978 | 20.8388 | 14.5272 | 4.5411 | -10.7123 | -33.4958 | -67.0244 | -115.8691 | -186.5316 | -288.265 | -434.2459 | -643.2474 |  | 474.4218 | 509.8871 | 548.2432 | 589.7355 | 634.6309 | 683.2194 | 735.8166 | 792.7653 | 854.4386 | 921.2421 | 993.617 | 1072.0431 | 1157.0426 | 1249.1834 | 1349.0835 | 1457.4154 | 1574.9107 | 1702.3658 | 1840.6473 | 1990.6985 | 2153.5462 | 2330.3082 | 2522.2012 | 2730.55 | 2956.7969 | 3202.5125 | 3469.4069 | 3759.3422 | 4074.3466 | 4416.6288 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 473.1207 | 508.586 | 546.9421 | 588.4344 | 633.3298 | 681.9183 | 734.5155 | 791.4642 | 853.1375 | 919.941 | 992.3159 | 1070.742 | 1155.7415 | 1247.8823 | 1347.7824 | 1456.1143 | 1573.6096 | 1700.8084 | 1838.5829 | 1987.9382 | 2149.8263 | 2325.2596 | 2515.3063 | 2721.0809 | 2943.728 | 3184.396 | 3444.1958 | 3724.1382 | 4025.0404 | 4347.3873 |  | 471.0601 | 507.4339 | 546.7724 | 589.3275 | 635.3729 | 685.206 | 739.1505 | 797.558 | 860.811 | 929.3257 | 1003.5544 | 1083.9894 | 1171.1662 | 1265.6672 | 1368.1263 | 1479.2331 | 1599.738 | 1727.4025 | 1863.1807 | 2008.777 | 2164.3534 | 2329.8007 | 2504.594 | 2687.5851 | 2876.7035 | 3068.5268 | 3257.6642 | 3435.8732 | 3590.7946 | 3704.1398 |  | 14.268 | 15.3346 | 16.4881 | 17.736 | 19.0862 | 20.5475 | 22.1293 | 23.842 | 25.6968 | 27.7059 | 29.8825 | 32.2412 | 34.7975 | 37.5686 | 40.573 | 43.831 | 47.3646 | 51.1978 | 55.3565 | 59.8693 | 64.7668 | 70.0828 | 75.8539 | 82.1199 | 88.9242 | 96.314 | 104.3407 | 113.0603 | 122.5339 | 132.8279 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | -0.42487 | 0.64173 | 1.7953 | 3.0431 | 4.3933 | 5.8546 | 7.4364 | 9.1491 | 11.0039 | 13.013 | 15.1897 | 17.5483 | 20.1046 | 22.8757 | 25.8801 | 29.1382 | 32.6718 | 33.6113 | 32.0447 | 28.6981 | 22.7587 | 13.0709 | -2.0079 | -24.8117 | -58.6593 | -108.2701 | -180.3592 | -284.4857 | -434.2636 | -649.0921 |  | 0.83953 | 0.90229 | 0.97017 | 1.0436 | 1.123 | 1.209 | 1.3021 | 1.4029 | 1.512 | 1.6302 | 1.7583 | 1.8971 | 2.0475 | 2.2105 | 2.3873 | 2.579 | 2.787 | 3.0125 | 3.2572 | 3.5227 | 3.8109 | 4.1237 | 4.4633 | 4.832 | 5.2323 | 5.6671 | 6.1394 | 6.6525 | 7.2099 | 7.8156 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | -1.2282 | -1.1654 | -1.0976 | -1.0241 | -0.94469 | -0.85871 | -0.76564 | -0.66486 | -0.55572 | -0.43751 | -0.30943 | -0.17065 | -0.020236 | 0.14282 | 0.3196 | 0.5113 | 0.71922 | 0.53755 | -0.023488 | -0.86399 | -2.1009 | -3.8996 | -6.4942 | -10.2166 | -15.5371 | -23.124 | -33.9265 | -49.2943 | -71.1483 | -102.2242 |  | 21.8278 | 23.4596 | 25.2243 | 27.1333 | 29.1989 | 31.4345 | 33.8544 | 36.4746 | 39.3122 | 42.3857 | 45.7157 | 49.324 | 53.2348 | 57.4741 | 62.0704 | 67.0547 | 72.4606 | 78.3247 | 84.687 | 91.5907 | 99.0832 | 107.2159 | 116.0448 | 125.6308 | 136.0403 | 147.3455 | 159.6251 | 172.9648 | 187.458 | 203.2062 |  | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.071652 | 0.094979 | 0.127 | 0.17115 | 0.23228 | 0.31723 | 0.43567 | 0.6013 | 0.83353 | 1.1599 | 1.6197 | 2.2685 | 3.1858 |  | 21.768 | 23.3997 | 25.1644 | 27.0735 | 29.1391 | 31.3746 | 33.7946 | 36.4147 | 39.2523 | 42.3259 | 45.6558 | 49.2641 | 53.1749 | 57.4142 | 62.0106 | 66.9949 | 72.4007 | 78.2531 | 84.592 | 91.4637 | 98.9121 | 106.9837 | 115.7276 | 125.1951 | 135.439 | 146.5119 | 158.4652 | 171.3451 | 185.1894 | 200.0204 |  | 491.175 | 530.3099 | 572.6346 | 618.42 | 667.9606 | 721.5766 | 779.6159 | 842.457 | 910.5115 | 984.2271 | 1064.0904 | 1150.6312 | 1244.4255 | 1346.1 | 1456.3366 | 1575.8774 | 1705.5297 | 1839.8045 | 1979.7939 | 2128.0748 | 2283.9233 | 2445.9556 | 2611.8194 | 2777.7519 | 2937.9461 | 3083.6446 | 3201.8437 | 3273.4384 | 3270.5721 | 3152.844
| TRUE | 1571 | 22006114 | FB | FB001 | 11 | FB1 | SENSITIVE EF | Blank | English Electric | CMG_1328 | CMG 1328 | CMG | Electromechanical |  | 0.57434 | 2190 |  | 8.25 | 0.0054067 | 0.0038888 | 0.0015179 | 31.8755 | 1244.4067 | 1276.2822 | 37.4249 | 2.2021 | 57.2543 |  | 11.5885 | 0.013521 | 0.0097249 | 0.0037959 | 79.7129 | 3111.9605 | 3191.6734 | 93.5906 | 5.5069 | 143.1792 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.059863 |  | 1373.1635 | 3433.9502 | 46.5474 | 3387.4027 |  | 0.03398 |  | 8.5352 | 8.8302 | 9.1354 | 9.4511 | 9.7778 | 10.1158 | 10.4654 | 10.8271 | 11.2014 | 11.5885 | 11.9891 | 12.4035 | 12.8322 | 13.2757 | 13.7346 | 14.2093 | 14.7004 | 15.2085 | 15.7342 | 16.278 | 16.8407 | 17.4227 | 18.0249 | 18.6479 | 19.2925 | 19.9593 | 20.6492 | 21.3629 | 22.1013 | 22.8652 |  | 0.0059156 | 0.0064751 | 0.0070903 | 0.007767 | 0.0085115 | 0.0093307 | 0.010232 | 0.011225 | 0.012317 | 0.013521 | 0.014846 | 0.016306 | 0.017915 | 0.019688 | 0.021642 | 0.023795 | 0.02617 | 0.028788 | 0.031676 | 0.034861 | 0.038374 | 0.042249 | 0.046526 | 0.051245 | 0.056453 | 0.062201 | 0.068547 | 0.075552 | 0.083287 | 0.091827 |  | 0.0042548 | 0.0046572 | 0.0050997 | 0.0055865 | 0.0061219 | 0.0067111 | 0.0073596 | 0.0080734 | 0.0088594 | 0.0097249 | 0.010678 | 0.011728 | 0.012885 | 0.01416 | 0.015566 | 0.017115 | 0.018823 | 0.020706 | 0.022783 | 0.025074 | 0.0276 | 0.030388 | 0.033464 | 0.036858 | 0.040604 | 0.044739 | 0.049303 | 0.054341 | 0.059904 | 0.066047 | 1502.4155 | 1644.5136 | 1800.7709 | 1972.6369 | 2161.7121 | 2369.7636 | 2598.7431 | 2850.8056 | 3128.3315 | 3433.9502 | 3770.5661 | 4141.3879 | 4549.9607 | 5000.2015 | 5496.4385 | 6043.4548 | 6646.5363 | 7311.5247 | 8044.8773 | 8853.7312 | 9745.976 | 10730.3332 | 11816.445 | 13014.9716 | 14337.6993 | 15797.6602 | 17409.2649 | 19188.4484 | 21152.8326 | 23321.9056 |  | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 38.7171 | 51.3218 | 68.6242 | 92.4821 | 125.5137 | 171.4152 | 235.4133 | 324.9096 | 450.3981 | 626.7756 | 875.2098 | 1225.8069 | 1721.421 |  | 34.8758 | 38.1744 | 41.8016 | 45.7912 | 50.1802 | 55.0097 | 60.3251 | 66.1763 | 72.6185 | 79.7129 | 87.5268 | 96.1348 | 105.619 | 116.0706 | 127.5898 | 140.2878 | 154.2872 | 169.7237 | 186.7472 | 205.5232 | 226.2351 | 249.0851 | 274.2972 | 302.1189 | 332.8236 | 366.7139 | 404.1244 | 445.4249 | 491.0245 | 541.3756 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 20.6629 | 23.9614 | 27.5887 | 31.5782 | 35.9673 | 40.7968 | 46.1121 | 51.9633 | 58.4056 | 65.5 | 73.3139 | 81.9218 | 91.4061 | 101.8576 | 113.3769 | 126.0749 | 140.0743 | 152.7117 | 164.1968 | 175.3703 | 185.5991 | 193.9354 | 198.9787 | 198.68 | 190.0608 | 168.8124 | 128.7239 | 60.8643 | -47.5858 | -215.0038 |  | 1361.5392 | 1490.3132 | 1631.9188 | 1787.6695 | 1959.0158 | 2147.5591 | 2355.0679 | 2583.4953 | 2834.9986 | 3111.9605 | 3417.0131 | 3753.0642 | 4123.3265 | 4531.3498 | 4981.0564 | 5476.7809 | 6023.3134 | 6625.9482 | 7290.5369 | 8023.5473 | 8832.1293 | 9724.1868 | 10708.4577 | 11794.6025 | 12993.3025 | 14316.368 | 15776.8581 | 17389.2136 | 19169.4043 | 21135.0908 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 1360.2381 | 1489.0121 | 1630.6177 | 1786.3684 | 1957.7147 | 2146.258 | 2353.7668 | 2582.1942 | 2833.6975 | 3110.6594 | 3415.712 | 3751.7631 | 4122.0254 | 4530.0487 | 4979.7553 | 5475.4798 | 6022.0123 | 6624.3909 | 7288.4725 | 8020.787 | 8828.4094 | 9719.1382 | 10701.5627 | 11785.1334 | 12980.2336 | 14298.2514 | 15751.647 | 17354.0097 | 19120.0981 | 21065.8493 |  | 1380.9009 | 1512.9735 | 1658.2063 | 1817.9466 | 1993.6819 | 2187.0548 | 2399.8789 | 2634.1576 | 2892.1031 | 3176.1593 | 3489.0258 | 3833.6849 | 4213.4315 | 4631.9063 | 5093.1322 | 5601.5546 | 6162.0866 | 6777.1026 | 7452.6693 | 8196.1573 | 9014.0085 | 9913.0736 | 10900.5415 | 11983.8134 | 13170.2943 | 14467.0638 | 15880.3709 | 17414.8739 | 19072.5122 | 20850.8454 |  | 40.9476 | 44.8204 | 49.0791 | 53.7633 | 58.9164 | 64.5868 | 70.8275 | 77.6973 | 85.2612 | 93.5906 | 102.7649 | 112.8715 | 124.007 | 136.2781 | 149.8028 | 164.7114 | 181.1481 | 199.2721 | 219.2592 | 241.3041 | 265.6218 | 292.45 | 322.0515 | 354.7167 | 390.767 | 430.5576 | 474.4811 | 522.9718 | 576.5102 | 635.6272 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 26.2547 | 30.1276 | 34.3863 | 39.0704 | 44.2235 | 49.8939 | 56.1346 | 63.0045 | 70.5683 | 78.8978 | 88.0721 | 98.1786 | 109.3141 | 121.5852 | 135.1099 | 150.0186 | 166.4552 | 181.6856 | 195.9474 | 210.133 | 223.6138 | 235.438 | 244.1897 | 247.7851 | 243.1836 | 225.9735 | 189.7812 | 125.4258 | 19.7127 | -146.2928 |  | 2.4094 | 2.6372 | 2.8878 | 3.1634 | 3.4667 | 3.8003 | 4.1675 | 4.5717 | 5.0168 | 5.5069 | 6.0467 | 6.6414 | 7.2966 | 8.0187 | 8.8144 | 9.6917 | 10.6588 | 11.7252 | 12.9013 | 14.1984 | 15.6293 | 17.2079 | 18.9496 | 20.8717 | 22.9929 | 25.3342 | 27.9186 | 30.7719 | 33.9221 | 37.4005 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.34164 | 0.56952 | 0.8201 | 1.0957 | 1.3989 | 1.7326 | 2.0998 | 2.504 | 2.9491 | 3.4392 | 3.979 | 4.5737 | 5.2289 | 5.9509 | 6.7467 | 7.6239 | 8.5911 | 9.2503 | 9.6206 | 9.8117 | 9.7175 | 9.1846 | 7.9921 | 5.8231 | 2.2234 | -3.457 | -12.1473 | -25.1749 | -44.4362 | -72.6393 |  | 62.6435 | 68.5683 | 75.0835 | 82.2495 | 90.133 | 98.8078 | 108.3551 | 118.8649 | 130.4364 | 143.1792 | 157.2145 | 172.676 | 189.7115 | 208.4844 | 229.1751 | 251.9831 | 277.1287 | 304.8555 | 335.4328 | 369.1581 | 406.3604 | 447.4034 | 492.689 | 542.6618 | 597.8132 | 658.6866 | 725.8828 | 800.0662 | 881.9716 | 972.4115 |  | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.071652 | 0.094979 | 0.127 | 0.17115 | 0.23228 | 0.31723 | 0.43567 | 0.6013 | 0.83353 | 1.1599 | 1.6197 | 2.2685 | 3.1858 |  | 62.5837 | 68.5085 | 75.0236 | 82.1896 | 90.0732 | 98.7479 | 108.2952 | 118.805 | 130.3765 | 143.1194 | 157.1546 | 172.6161 | 189.6517 | 208.4245 | 229.1152 | 251.9232 | 277.0688 | 304.7838 | 335.3378 | 369.0311 | 406.1893 | 447.1711 | 492.3718 | 542.2262 | 597.2119 | 657.8531 | 724.7228 | 798.4465 | 879.703 | 969.2258 |  | 1470.081 | 1612.1791 | 1768.4363 | 1940.3024 | 2129.3776 | 2337.4291 | 2566.4086 | 2818.4711 | 3095.997 | 3401.6157 | 3738.2315 | 4109.0533 | 4517.6262 | 4967.867 | 5464.104 | 6011.1203 | 6614.2017 | 7272.8224 | 7993.575 | 8785.1331 | 9653.529 | 10604.8673 | 11645.0951 | 12779.6478 | 14012.9132 | 15347.4334 | 16782.7276 | 18313.5713 | 19927.4918 | 21601.1391
| TRUE | 1572 | 22006115 | FB | FB001 | 11 | FB1 | PILOT WIRE | Blank | English Electric | DSF7_1490 | DSF7 1490 | DSF7 | Electromechanical |  | 0.57434 | 2190 |  | 5.5 | 0.0019187 | 0.0013801 | 0.00053868 | 11.3121 | 441.6215 | 452.9336 | 13.2815 | 0.78149 | 20.3187 |  | 7.3552 | 0.0040026 | 0.0028789 | 0.0011237 | 23.5976 | 921.2421 | 944.8397 | 27.7059 | 1.6302 | 42.3857 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.059863 |  | 487.3154 | 1016.5616 | 46.5474 | 970.0141 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0.0014826 | 0.0015934 | 0.0017133 | 0.0018429 | 0.0019832 | 0.0021351 | 0.0022994 | 0.0024774 | 0.0026701 | 0.0028789 | 0.0031051 | 0.0033501 | 0.0036158 | 0.0039037 | 0.0042159 | 0.0045544 | 0.0049216 | 0.0053199 | 0.005752 | 0.0062209 | 0.0067298 | 0.0072822 | 0.0078819 | 0.008533 | 0.00924 | 0.010008 | 0.010842 | 0.011748 | 0.012732 | 0.013802 | 523.5095 | 562.6444 | 604.9691 | 650.7545 | 700.2951 | 753.9111 | 811.9504 | 874.7915 | 942.846 | 1016.5616 | 1096.4249 | 1182.9657 | 1276.76 | 1378.4345 | 1488.6711 | 1608.2119 | 1737.8643 | 1878.5069 | 2031.0962 | 2196.6729 | 2376.3703 | 2571.4215 | 2783.1694 | 3013.0757 | 3262.7321 | 3533.8715 | 3828.381 | 4148.3155 | 4495.9129 | 4873.6105 |  | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 38.7171 | 51.3218 | 68.6242 | 92.4821 | 125.5137 | 171.4152 | 235.4133 | 324.9096 | 450.3981 | 626.7756 | 875.2098 | 1225.8069 | 1721.421 |  | 12.1523 | 13.0608 | 14.0433 | 15.1061 | 16.2561 | 17.5007 | 18.8479 | 20.3067 | 21.8865 | 23.5976 | 25.4515 | 27.4604 | 29.6377 | 31.9978 | 34.5568 | 37.3317 | 40.3414 | 43.6061 | 47.1482 | 50.9918 | 55.1631 | 59.6909 | 64.6062 | 69.9431 | 75.7384 | 82.0324 | 88.8689 | 96.2956 | 104.3644 | 113.132 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | -2.0606 | -1.1522 | -0.16969 | 0.89314 | 2.0431 | 3.2877 | 4.635 | 6.0937 | 7.6735 | 9.3847 | 11.2386 | 13.2475 | 15.4247 | 17.7849 | 20.3438 | 23.1188 | 26.1284 | 26.5941 | 24.5978 | 20.8388 | 14.5272 | 4.5411 | -10.7123 | -33.4958 | -67.0244 | -115.8691 | -186.5316 | -288.265 | -434.2459 | -643.2474 |  | 474.4218 | 509.8871 | 548.2432 | 589.7355 | 634.6309 | 683.2194 | 735.8166 | 792.7653 | 854.4386 | 921.2421 | 993.617 | 1072.0431 | 1157.0426 | 1249.1834 | 1349.0835 | 1457.4154 | 1574.9107 | 1702.3658 | 1840.6473 | 1990.6985 | 2153.5462 | 2330.3082 | 2522.2012 | 2730.55 | 2956.7969 | 3202.5125 | 3469.4069 | 3759.3422 | 4074.3466 | 4416.6288 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 473.1207 | 508.586 | 546.9421 | 588.4344 | 633.3298 | 681.9183 | 734.5155 | 791.4642 | 853.1375 | 919.941 | 992.3159 | 1070.742 | 1155.7415 | 1247.8823 | 1347.7824 | 1456.1143 | 1573.6096 | 1700.8084 | 1838.5829 | 1987.9382 | 2149.8263 | 2325.2596 | 2515.3063 | 2721.0809 | 2943.728 | 3184.396 | 3444.1958 | 3724.1382 | 4025.0404 | 4347.3873 |  | 471.0601 | 507.4339 | 546.7724 | 589.3275 | 635.3729 | 685.206 | 739.1505 | 797.558 | 860.811 | 929.3257 | 1003.5544 | 1083.9894 | 1171.1662 | 1265.6672 | 1368.1263 | 1479.2331 | 1599.738 | 1727.4025 | 1863.1807 | 2008.777 | 2164.3534 | 2329.8007 | 2504.594 | 2687.5851 | 2876.7035 | 3068.5268 | 3257.6642 | 3435.8732 | 3590.7946 | 3704.1398 |  | 14.268 | 15.3346 | 16.4881 | 17.736 | 19.0862 | 20.5475 | 22.1293 | 23.842 | 25.6968 | 27.7059 | 29.8825 | 32.2412 | 34.7975 | 37.5686 | 40.573 | 43.831 | 47.3646 | 51.1978 | 55.3565 | 59.8693 | 64.7668 | 70.0828 | 75.8539 | 82.1199 | 88.9242 | 96.314 | 104.3407 | 113.0603 | 122.5339 | 132.8279 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | -0.42487 | 0.64173 | 1.7953 | 3.0431 | 4.3933 | 5.8546 | 7.4364 | 9.1491 | 11.0039 | 13.013 | 15.1897 | 17.5483 | 20.1046 | 22.8757 | 25.8801 | 29.1382 | 32.6718 | 33.6113 | 32.0447 | 28.6981 | 22.7587 | 13.0709 | -2.0079 | -24.8117 | -58.6593 | -108.2701 | -180.3592 | -284.4857 | -434.2636 | -649.0921 |  | 0.83953 | 0.90229 | 0.97017 | 1.0436 | 1.123 | 1.209 | 1.3021 | 1.4029 | 1.512 | 1.6302 | 1.7583 | 1.8971 | 2.0475 | 2.2105 | 2.3873 | 2.579 | 2.787 | 3.0125 | 3.2572 | 3.5227 | 3.8109 | 4.1237 | 4.4633 | 4.832 | 5.2323 | 5.6671 | 6.1394 | 6.6525 | 7.2099 | 7.8156 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | -1.2282 | -1.1654 | -1.0976 | -1.0241 | -0.94469 | -0.85871 | -0.76564 | -0.66486 | -0.55572 | -0.43751 | -0.30943 | -0.17065 | -0.020236 | 0.14282 | 0.3196 | 0.5113 | 0.71922 | 0.53755 | -0.023488 | -0.86399 | -2.1009 | -3.8996 | -6.4942 | -10.2166 | -15.5371 | -23.124 | -33.9265 | -49.2943 | -71.1483 | -102.2242 |  | 21.8278 | 23.4596 | 25.2243 | 27.1333 | 29.1989 | 31.4345 | 33.8544 | 36.4746 | 39.3122 | 42.3857 | 45.7157 | 49.324 | 53.2348 | 57.4741 | 62.0704 | 67.0547 | 72.4606 | 78.3247 | 84.687 | 91.5907 | 99.0832 | 107.2159 | 116.0448 | 125.6308 | 136.0403 | 147.3455 | 159.6251 | 172.9648 | 187.458 | 203.2062 |  | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.071652 | 0.094979 | 0.127 | 0.17115 | 0.23228 | 0.31723 | 0.43567 | 0.6013 | 0.83353 | 1.1599 | 1.6197 | 2.2685 | 3.1858 |  | 21.768 | 23.3997 | 25.1644 | 27.0735 | 29.1391 | 31.3746 | 33.7946 | 36.4147 | 39.2523 | 42.3259 | 45.6558 | 49.2641 | 53.1749 | 57.4142 | 62.0106 | 66.9949 | 72.4007 | 78.2531 | 84.592 | 91.4637 | 98.9121 | 106.9837 | 115.7276 | 125.1951 | 135.439 | 146.5119 | 158.4652 | 171.3451 | 185.1894 | 200.0204 |  | 491.175 | 530.3099 | 572.6346 | 618.42 | 667.9606 | 721.5766 | 779.6159 | 842.457 | 910.5115 | 984.2271 | 1064.0904 | 1150.6312 | 1244.4255 | 1346.1 | 1456.3366 | 1575.8774 | 1705.5297 | 1839.8045 | 1979.7939 | 2128.0748 | 2283.9233 | 2445.9556 | 2611.8194 | 2777.7519 | 2937.9461 | 3083.6446 | 3201.8437 | 3273.4384 | 3270.5721 | 3152.844
| TRUE | 1573 | 22006116 | FB | FB001 | 11 | FB1 | OVERCURRENT | Blank | ASEA | RACID_3245 | RACID 3245 | RACID | Electronic |  | 0.57434 | 2190 |  | 6.6 | 0.014726 | 0.010592 | 0.0041343 | 86.8187 | 3389.3699 | 3476.1886 | 101.9336 | 5.9978 | 155.9427 |  | 11.1153 | 0.058633 | 0.042172 | 0.016461 | 345.6775 | 13495.1158 | 13840.7933 | 405.8588 | 23.8809 | 620.9013 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.059863 |  | 3740.0627 | 14891.4344 | 46.5474 | 14844.8869 |  | 0.052126 |  | 6.9532 | 7.3252 | 7.7172 | 8.1301 | 8.5651 | 9.0234 | 9.5062 | 10.0149 | 10.5508 | 11.1153 | 11.7101 | 12.3367 | 12.9968 | 13.6922 | 14.4249 | 15.1967 | 16.0099 | 16.8665 | 17.769 | 18.7198 | 19.7215 | 20.7767 | 21.8884 | 23.0596 | 24.2935 | 25.5934 | 26.9629 | 28 | 28 | 28 |  | 0.016829 | 0.019254 | 0.022055 | 0.02529 | 0.029029 | 0.033353 | 0.038356 | 0.044149 | 0.050858 | 0.058633 | 0.067647 | 0.078102 | 0.090233 | 0.10431 | 0.12066 | 0.13966 | 0.16172 | 0.18737 | 0.2172 | 0.25188 | 0.29223 | 0.33918 | 0.39382 | 0.45744 | 0.53152 | 0.61779 | 0.7183 | 0.80128 | 0.80128 | 0.80128 |  | 0.012104 | 0.013849 | 0.015863 | 0.01819 | 0.020879 | 0.023989 | 0.027588 | 0.031754 | 0.03658 | 0.042172 | 0.048656 | 0.056175 | 0.0649 | 0.075028 | 0.086788 | 0.10045 | 0.11632 | 0.13477 | 0.15622 | 0.18117 | 0.21019 | 0.24396 | 0.28326 | 0.32902 | 0.3823 | 0.44435 | 0.51664 | 0.57632 | 0.57632 | 0.57632 | 4274.0732 | 4890.1526 | 5601.3764 | 6422.9486 | 7372.5536 | 8470.7656 | 9741.527 | 11212.706 | 12916.7478 | 14891.4344 | 17180.7705 | 19836.0194 | 22916.9103 | 26493.0488 | 30645.5636 | 35469.0288 | 41073.709 | 47588.1805 | 55162.3931 | 63971.2452 | 74218.7603 | 86142.9646 | 100021.585 | 116178.7052 | 134992.5409 | 156904.5245 | 182429.9177 | 203505.3673 | 203505.3673 | 203505.3673 |  | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 38.7171 | 51.3218 | 68.6242 | 92.4821 | 125.5137 | 171.4152 | 235.4133 | 324.9096 | 450.3981 | 626.7756 | 875.2098 | 1225.8069 | 1721.421 |  | 99.2148 | 113.516 | 130.0257 | 149.0971 | 171.1404 | 196.6334 | 226.1318 | 260.2825 | 299.8388 | 345.6775 | 398.8203 | 460.4571 | 531.9743 | 614.9879 | 711.3809 | 823.3489 | 953.4513 | 1104.6729 | 1280.4945 | 1484.9759 | 1722.8533 | 1999.652 | 2321.8189 | 2696.877 | 3133.6059 | 3642.2527 | 4234.7782 | 4724.0064 | 4724.0064 | 4724.0064 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 85.0019 | 99.303 | 115.8128 | 134.8841 | 156.9275 | 182.4204 | 211.9189 | 246.0696 | 285.6258 | 331.4646 | 384.6073 | 446.2441 | 517.7614 | 600.7749 | 697.168 | 809.1359 | 939.2384 | 1087.6609 | 1257.944 | 1454.823 | 1682.2174 | 1944.5022 | 2246.5004 | 2593.4381 | 2990.8431 | 3444.3512 | 3959.3777 | 4339.4458 | 4185.3961 | 3967.627 |  | 3873.308 | 4431.6198 | 5076.1546 | 5820.6908 | 6681.2546 | 7676.4911 | 8828.0975 | 10161.3291 | 11705.5888 | 13495.1158 | 15569.7888 | 17976.0641 | 20768.0705 | 24008.8868 | 27772.0345 | 32143.22 | 37222.3686 | 43126.0006 | 49990.0053 | 57972.8817 | 67259.5225 | 78065.6353 | 90642.9052 | 105285.0278 | 122334.7549 | 142192.1272 | 165324.0921 | 184423.3694 | 184423.3694 | 184423.3694 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 3872.0069 | 4430.3187 | 5074.8535 | 5819.3897 | 6679.9535 | 7675.19 | 8826.7964 | 10160.028 | 11704.2877 | 13493.8147 | 15568.4877 | 17974.763 | 20766.7694 | 24007.5857 | 27770.7334 | 32141.9189 | 37221.0675 | 43124.4433 | 49987.941 | 57970.1214 | 67255.8026 | 78060.5867 | 90636.0103 | 105275.5587 | 122321.686 | 142174.0107 | 165298.881 | 184388.1654 | 184374.0632 | 184354.1279 |  | 3957.0088 | 4529.6218 | 5190.6663 | 5954.2738 | 6836.881 | 7857.6104 | 9038.7153 | 10406.0976 | 11989.9136 | 13825.2793 | 15953.095 | 18421.0072 | 21284.5308 | 24608.3606 | 28467.9014 | 32951.0549 | 38160.3059 | 44212.1042 | 51245.885 | 59424.9443 | 68938.02 | 80005.0889 | 92882.5107 | 107868.9968 | 125312.5291 | 145618.3618 | 169258.2587 | 188727.6112 | 188559.4592 | 188321.7548 |  | 116.4878 | 133.2787 | 152.6628 | 175.0543 | 200.9354 | 230.8666 | 265.5006 | 305.5969 | 352.0397 | 405.8588 | 468.2536 | 540.6211 | 624.5893 | 722.0552 | 835.23 | 966.6912 | 1119.444 | 1296.9928 | 1503.4242 | 1743.5052 | 2022.7963 | 2347.7847 | 2726.0397 | 3166.3942 | 3679.1562 | 4276.3566 | 4972.0388 | 5546.44 | 5546.44 | 5546.44 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 101.7949 | 118.5859 | 137.9699 | 160.3615 | 186.2425 | 216.1737 | 250.8077 | 290.904 | 337.3468 | 391.1659 | 453.5607 | 525.9282 | 609.8964 | 707.3623 | 820.5371 | 951.9983 | 1104.7511 | 1279.4063 | 1480.1124 | 1712.3341 | 1980.7882 | 2290.7727 | 2648.1779 | 3059.4625 | 3531.5727 | 4071.7726 | 4687.3389 | 5148.894 | 4989.6425 | 4764.52 |  | 6.8542 | 7.8422 | 8.9827 | 10.3003 | 11.8231 | 13.5843 | 15.6222 | 17.9814 | 20.7141 | 23.8809 | 27.5522 | 31.8103 | 36.7511 | 42.486 | 49.1452 | 56.8805 | 65.8685 | 76.3155 | 88.462 | 102.5885 | 119.0221 | 138.1445 | 160.4012 | 186.3118 | 216.4829 | 251.6224 | 292.5566 | 326.3545 | 326.3545 | 326.3545 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.7865 | 5.7744 | 6.915 | 8.2325 | 9.7554 | 11.5165 | 13.5544 | 15.9137 | 18.6464 | 21.8131 | 25.4845 | 29.7426 | 34.6833 | 40.4183 | 47.0775 | 54.8127 | 63.8008 | 73.8406 | 85.1813 | 98.2018 | 113.1103 | 130.1212 | 149.4437 | 171.2633 | 195.7134 | 222.8312 | 252.4907 | 270.4078 | 247.9963 | 216.3147 |  | 178.2083 | 203.8959 | 233.5505 | 267.8061 | 307.4001 | 353.1903 | 406.1749 | 467.516 | 538.5664 | 620.9013 | 716.3557 | 827.0668 | 955.5252 | 1104.633 | 1277.7729 | 1478.8883 | 1712.5765 | 1984.1987 | 2300.007 | 2667.2939 | 3094.5661 | 3591.7482 | 4170.42 | 4844.0944 | 5628.541 | 6542.1656 | 7606.452 | 8485.197 | 8485.197 | 8485.197 |  | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.071652 | 0.094979 | 0.127 | 0.17115 | 0.23228 | 0.31723 | 0.43567 | 0.6013 | 0.83353 | 1.1599 | 1.6197 | 2.2685 | 3.1858 |  | 178.1485 | 203.836 | 233.4906 | 267.7463 | 307.3402 | 353.1304 | 406.1151 | 467.4562 | 538.5065 | 620.8415 | 716.2958 | 827.0069 | 955.4653 | 1104.5731 | 1277.713 | 1478.8284 | 1712.5167 | 1984.1271 | 2299.912 | 2667.1669 | 3094.3949 | 3591.5159 | 4170.1028 | 4843.6587 | 5627.9397 | 6541.332 | 7605.292 | 8483.5773 | 8482.9285 | 8482.0113 |  | 4241.7387 | 4857.8181 | 5569.0419 | 6390.6141 | 7340.2191 | 8438.4311 | 9709.1925 | 11180.3715 | 12884.4133 | 14859.0999 | 17148.436 | 19803.6849 | 22884.5758 | 26460.7143 | 30613.229 | 35436.6943 | 41041.3745 | 47549.4781 | 55111.0908 | 63902.6471 | 74126.3133 | 86017.4987 | 99850.2351 | 115943.3814 | 134667.7549 | 156454.2976 | 181803.3803 | 202630.4902 | 202280.0265 | 201784.6008
| TRUE | 1574 | 22006135 | FB | FB010 | 11 | FB10 | SENSITIVE EF | Blank | English Electric | CMG_1328 | CMG 1328 | CMG | Electromechanical |  | 0.57434 | 2190 |  | 8.25 | 0.0054067 | 0.0038888 | 0.0015179 | 31.8755 | 1244.4067 | 1276.2822 | 37.4249 | 2.2021 | 74.6127 |  | 11.5885 | 0.013521 | 0.0097249 | 0.0037959 | 79.7129 | 3111.9605 | 3191.6734 | 93.5906 | 5.5069 | 186.5882 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 1390.5218 | 3477.3591 | 46.5656 | 3430.7935 |  | 0.03398 |  | 8.5352 | 8.8302 | 9.1354 | 9.4511 | 9.7778 | 10.1158 | 10.4654 | 10.8271 | 11.2014 | 11.5885 | 11.9891 | 12.4035 | 12.8322 | 13.2757 | 13.7346 | 14.2093 | 14.7004 | 15.2085 | 15.7342 | 16.278 | 16.8407 | 17.4227 | 18.0249 | 18.6479 | 19.2925 | 19.9593 | 20.6492 | 21.3629 | 22.1013 | 22.8652 |  | 0.0059156 | 0.0064751 | 0.0070903 | 0.007767 | 0.0085115 | 0.0093307 | 0.010232 | 0.011225 | 0.012317 | 0.013521 | 0.014846 | 0.016306 | 0.017915 | 0.019688 | 0.021642 | 0.023795 | 0.02617 | 0.028788 | 0.031676 | 0.034861 | 0.038374 | 0.042249 | 0.046526 | 0.051245 | 0.056453 | 0.062201 | 0.068547 | 0.075552 | 0.083287 | 0.091827 |  | 0.0042548 | 0.0046572 | 0.0050997 | 0.0055865 | 0.0061219 | 0.0067111 | 0.0073596 | 0.0080734 | 0.0088594 | 0.0097249 | 0.010678 | 0.011728 | 0.012885 | 0.01416 | 0.015566 | 0.017115 | 0.018823 | 0.020706 | 0.022783 | 0.025074 | 0.0276 | 0.030388 | 0.033464 | 0.036858 | 0.040604 | 0.044739 | 0.049303 | 0.054341 | 0.059904 | 0.066047 | 1521.4077 | 1665.3021 | 1823.5346 | 1997.5732 | 2189.0385 | 2399.7201 | 2631.5941 | 2886.8429 | 3167.8771 | 3477.3591 | 3818.2302 | 4193.7396 | 4607.4773 | 5063.4096 | 5565.9197 | 6119.8509 | 6730.5559 | 7403.9506 | 8146.5736 | 8965.6523 | 9869.176 | 10865.9766 | 11965.8181 | 13179.4954 | 14518.9438 | 15997.3603 | 17629.3375 | 19431.0118 | 21420.228 | 23616.7206 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 34.8758 | 38.1744 | 41.8016 | 45.7912 | 50.1802 | 55.0097 | 60.3251 | 66.1763 | 72.6185 | 79.7129 | 87.5268 | 96.1348 | 105.619 | 116.0706 | 127.5898 | 140.2878 | 154.2872 | 169.7237 | 186.7472 | 205.5232 | 226.2351 | 249.0851 | 274.2972 | 302.1189 | 332.8236 | 366.7139 | 404.1244 | 445.4249 | 491.0245 | 541.3756 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 20.6629 | 23.9614 | 27.5887 | 31.5782 | 35.9673 | 40.7968 | 46.1121 | 51.9633 | 58.4056 | 65.5 | 73.3139 | 81.9218 | 91.4061 | 101.8576 | 113.3769 | 126.0749 | 140.0743 | 152.7117 | 164.1968 | 175.3703 | 185.5991 | 193.9354 | 198.9787 | 198.68 | 190.0608 | 168.8124 | 128.7239 | 60.8643 | -47.5858 | -215.0038 |  | 1361.5392 | 1490.3132 | 1631.9188 | 1787.6695 | 1959.0158 | 2147.5591 | 2355.0679 | 2583.4953 | 2834.9986 | 3111.9605 | 3417.0131 | 3753.0642 | 4123.3265 | 4531.3498 | 4981.0564 | 5476.7809 | 6023.3134 | 6625.9482 | 7290.5369 | 8023.5473 | 8832.1293 | 9724.1868 | 10708.4577 | 11794.6025 | 12993.3025 | 14316.368 | 15776.8581 | 17389.2136 | 19169.4043 | 21135.0908 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 1360.2381 | 1489.0121 | 1630.6177 | 1786.3684 | 1957.7147 | 2146.258 | 2353.7668 | 2582.1942 | 2833.6975 | 3110.6594 | 3415.712 | 3751.7631 | 4122.0254 | 4530.0487 | 4979.7553 | 5475.4798 | 6022.0123 | 6624.3909 | 7288.4725 | 8020.787 | 8828.4094 | 9719.1382 | 10701.5627 | 11785.1334 | 12980.2336 | 14298.2514 | 15751.647 | 17354.0097 | 19120.0981 | 21065.8493 |  | 1380.9009 | 1512.9735 | 1658.2063 | 1817.9466 | 1993.6819 | 2187.0548 | 2399.8789 | 2634.1576 | 2892.1031 | 3176.1593 | 3489.0258 | 3833.6849 | 4213.4315 | 4631.9063 | 5093.1322 | 5601.5546 | 6162.0866 | 6777.1026 | 7452.6693 | 8196.1573 | 9014.0085 | 9913.0736 | 10900.5415 | 11983.8134 | 13170.2943 | 14467.0638 | 15880.3709 | 17414.8739 | 19072.5122 | 20850.8454 |  | 40.9476 | 44.8204 | 49.0791 | 53.7633 | 58.9164 | 64.5868 | 70.8275 | 77.6973 | 85.2612 | 93.5906 | 102.7649 | 112.8715 | 124.007 | 136.2781 | 149.8028 | 164.7114 | 181.1481 | 199.2721 | 219.2592 | 241.3041 | 265.6218 | 292.45 | 322.0515 | 354.7167 | 390.767 | 430.5576 | 474.4811 | 522.9718 | 576.5102 | 635.6272 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 26.2547 | 30.1276 | 34.3863 | 39.0704 | 44.2235 | 49.8939 | 56.1346 | 63.0045 | 70.5683 | 78.8978 | 88.0721 | 98.1786 | 109.3141 | 121.5852 | 135.1099 | 150.0186 | 166.4552 | 181.6856 | 195.9474 | 210.133 | 223.6138 | 235.438 | 244.1897 | 247.7851 | 243.1836 | 225.9735 | 189.7812 | 125.4258 | 19.7127 | -146.2928 |  | 2.4094 | 2.6372 | 2.8878 | 3.1634 | 3.4667 | 3.8003 | 4.1675 | 4.5717 | 5.0168 | 5.5069 | 6.0467 | 6.6414 | 7.2966 | 8.0187 | 8.8144 | 9.6917 | 10.6588 | 11.7252 | 12.9013 | 14.1984 | 15.6293 | 17.2079 | 18.9496 | 20.8717 | 22.9929 | 25.3342 | 27.9186 | 30.7719 | 33.9221 | 37.4005 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.34164 | 0.56952 | 0.8201 | 1.0957 | 1.3989 | 1.7326 | 2.0998 | 2.504 | 2.9491 | 3.4392 | 3.979 | 4.5737 | 5.2289 | 5.9509 | 6.7467 | 7.6239 | 8.5911 | 9.2503 | 9.6206 | 9.8117 | 9.7175 | 9.1846 | 7.9921 | 5.8231 | 2.2234 | -3.457 | -12.1473 | -25.1749 | -44.4362 | -72.6393 |  | 81.6357 | 89.3568 | 97.8473 | 107.1858 | 117.4595 | 128.7642 | 141.2061 | 154.9023 | 169.982 | 186.5882 | 204.8787 | 225.0278 | 247.2281 | 271.6925 | 298.6562 | 328.3791 | 361.1483 | 397.2813 | 437.129 | 481.0792 | 529.5605 | 583.0468 | 642.0621 | 707.1856 | 779.0578 | 858.3867 | 945.9554 | 1042.6296 | 1149.367 | 1267.2265 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 81.5577 | 89.2788 | 97.7692 | 107.1078 | 117.3815 | 128.6862 | 141.1281 | 154.8243 | 169.904 | 186.5102 | 204.8007 | 224.9498 | 247.1501 | 271.6145 | 298.5782 | 328.3011 | 361.0703 | 397.188 | 437.0052 | 480.9137 | 529.3374 | 582.7441 | 641.6487 | 706.6179 | 778.2742 | 857.3005 | 944.4437 | 1040.5189 | 1146.4107 | 1263.0749 |  | 1489.055 | 1632.9494 | 1791.182 | 1965.2205 | 2156.6859 | 2367.3674 | 2599.2414 | 2854.4903 | 3135.5245 | 3445.0065 | 3785.8776 | 4161.387 | 4575.1246 | 5031.057 | 5533.567 | 6087.4982 | 6698.2032 | 7365.2265 | 8095.2425 | 8897.0157 | 9776.6772 | 10740.4403 | 11794.372 | 12944.0395 | 14193.9755 | 15546.8808 | 17002.4485 | 18555.6437 | 20194.1995 | 21894.9882
| TRUE | 1575 | 22006136 | FB | FB010 | 11 | FB10 | OVERCURRENT | Blank | ASEA | RACID_3245 | RACID 3245 | RACID | Electronic |  | 0.57434 | 2190 |  | 6.6 | 0.014726 | 0.010592 | 0.0041343 | 86.8187 | 3389.3699 | 3476.1886 | 101.9336 | 5.9978 | 203.2212 |  | 11.1153 | 0.058633 | 0.042172 | 0.016461 | 345.6775 | 13495.1158 | 13840.7933 | 405.8588 | 23.8809 | 809.1457 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 3787.3412 | 15079.6787 | 46.5656 | 15033.1131 |  | 0.052126 |  | 6.9532 | 7.3252 | 7.7172 | 8.1301 | 8.5651 | 9.0234 | 9.5062 | 10.0149 | 10.5508 | 11.1153 | 11.7101 | 12.3367 | 12.9968 | 13.6922 | 14.4249 | 15.1967 | 16.0099 | 16.8665 | 17.769 | 18.7198 | 19.7215 | 20.7767 | 21.8884 | 23.0596 | 24.2935 | 25.5934 | 26.9629 | 28 | 28 | 28 |  | 0.016829 | 0.019254 | 0.022055 | 0.02529 | 0.029029 | 0.033353 | 0.038356 | 0.044149 | 0.050858 | 0.058633 | 0.067647 | 0.078102 | 0.090233 | 0.10431 | 0.12066 | 0.13966 | 0.16172 | 0.18737 | 0.2172 | 0.25188 | 0.29223 | 0.33918 | 0.39382 | 0.45744 | 0.53152 | 0.61779 | 0.7183 | 0.80128 | 0.80128 | 0.80128 |  | 0.012104 | 0.013849 | 0.015863 | 0.01819 | 0.020879 | 0.023989 | 0.027588 | 0.031754 | 0.03658 | 0.042172 | 0.048656 | 0.056175 | 0.0649 | 0.075028 | 0.086788 | 0.10045 | 0.11632 | 0.13477 | 0.15622 | 0.18117 | 0.21019 | 0.24396 | 0.28326 | 0.32902 | 0.3823 | 0.44435 | 0.51664 | 0.57632 | 0.57632 | 0.57632 | 4328.1022 | 4951.9696 | 5672.184 | 6504.1419 | 7465.7509 | 8577.8456 | 9864.6708 | 11354.4471 | 13080.03 | 15079.6787 | 17397.9547 | 20086.7689 | 23206.6057 | 26827.9505 | 31032.9577 | 35917.397 | 41592.9266 | 48189.7483 | 55859.7074 | 64779.9133 | 75156.9684 | 87231.908 | 101285.9697 | 117647.3339 | 136698.9976 | 158887.9731 | 184736.0358 | 206077.9027 | 206077.9027 | 206077.9027 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 99.2148 | 113.516 | 130.0257 | 149.0971 | 171.1404 | 196.6334 | 226.1318 | 260.2825 | 299.8388 | 345.6775 | 398.8203 | 460.4571 | 531.9743 | 614.9879 | 711.3809 | 823.3489 | 953.4513 | 1104.6729 | 1280.4945 | 1484.9759 | 1722.8533 | 1999.652 | 2321.8189 | 2696.877 | 3133.6059 | 3642.2527 | 4234.7782 | 4724.0064 | 4724.0064 | 4724.0064 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 85.0019 | 99.303 | 115.8128 | 134.8841 | 156.9275 | 182.4204 | 211.9189 | 246.0696 | 285.6258 | 331.4646 | 384.6073 | 446.2441 | 517.7614 | 600.7749 | 697.168 | 809.1359 | 939.2384 | 1087.6609 | 1257.944 | 1454.823 | 1682.2174 | 1944.5022 | 2246.5004 | 2593.4381 | 2990.8431 | 3444.3512 | 3959.3777 | 4339.4458 | 4185.3961 | 3967.627 |  | 3873.308 | 4431.6198 | 5076.1546 | 5820.6908 | 6681.2546 | 7676.4911 | 8828.0975 | 10161.3291 | 11705.5888 | 13495.1158 | 15569.7888 | 17976.0641 | 20768.0705 | 24008.8868 | 27772.0345 | 32143.22 | 37222.3686 | 43126.0006 | 49990.0053 | 57972.8817 | 67259.5225 | 78065.6353 | 90642.9052 | 105285.0278 | 122334.7549 | 142192.1272 | 165324.0921 | 184423.3694 | 184423.3694 | 184423.3694 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 3872.0069 | 4430.3187 | 5074.8535 | 5819.3897 | 6679.9535 | 7675.19 | 8826.7964 | 10160.028 | 11704.2877 | 13493.8147 | 15568.4877 | 17974.763 | 20766.7694 | 24007.5857 | 27770.7334 | 32141.9189 | 37221.0675 | 43124.4433 | 49987.941 | 57970.1214 | 67255.8026 | 78060.5867 | 90636.0103 | 105275.5587 | 122321.686 | 142174.0107 | 165298.881 | 184388.1654 | 184374.0632 | 184354.1279 |  | 3957.0088 | 4529.6218 | 5190.6663 | 5954.2738 | 6836.881 | 7857.6104 | 9038.7153 | 10406.0976 | 11989.9136 | 13825.2793 | 15953.095 | 18421.0072 | 21284.5308 | 24608.3606 | 28467.9014 | 32951.0549 | 38160.3059 | 44212.1042 | 51245.885 | 59424.9443 | 68938.02 | 80005.0889 | 92882.5107 | 107868.9968 | 125312.5291 | 145618.3618 | 169258.2587 | 188727.6112 | 188559.4592 | 188321.7548 |  | 116.4878 | 133.2787 | 152.6628 | 175.0543 | 200.9354 | 230.8666 | 265.5006 | 305.5969 | 352.0397 | 405.8588 | 468.2536 | 540.6211 | 624.5893 | 722.0552 | 835.23 | 966.6912 | 1119.444 | 1296.9928 | 1503.4242 | 1743.5052 | 2022.7963 | 2347.7847 | 2726.0397 | 3166.3942 | 3679.1562 | 4276.3566 | 4972.0388 | 5546.44 | 5546.44 | 5546.44 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 101.7949 | 118.5859 | 137.9699 | 160.3615 | 186.2425 | 216.1737 | 250.8077 | 290.904 | 337.3468 | 391.1659 | 453.5607 | 525.9282 | 609.8964 | 707.3623 | 820.5371 | 951.9983 | 1104.7511 | 1279.4063 | 1480.1124 | 1712.3341 | 1980.7882 | 2290.7727 | 2648.1779 | 3059.4625 | 3531.5727 | 4071.7726 | 4687.3389 | 5148.894 | 4989.6425 | 4764.52 |  | 6.8542 | 7.8422 | 8.9827 | 10.3003 | 11.8231 | 13.5843 | 15.6222 | 17.9814 | 20.7141 | 23.8809 | 27.5522 | 31.8103 | 36.7511 | 42.486 | 49.1452 | 56.8805 | 65.8685 | 76.3155 | 88.462 | 102.5885 | 119.0221 | 138.1445 | 160.4012 | 186.3118 | 216.4829 | 251.6224 | 292.5566 | 326.3545 | 326.3545 | 326.3545 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.7865 | 5.7744 | 6.915 | 8.2325 | 9.7554 | 11.5165 | 13.5544 | 15.9137 | 18.6464 | 21.8131 | 25.4845 | 29.7426 | 34.6833 | 40.4183 | 47.0775 | 54.8127 | 63.8008 | 73.8406 | 85.1813 | 98.2018 | 113.1103 | 130.1212 | 149.4437 | 171.2633 | 195.7134 | 222.8312 | 252.4907 | 270.4078 | 247.9963 | 216.3147 |  | 232.2374 | 265.7129 | 304.3582 | 348.9994 | 400.5974 | 460.2702 | 529.3187 | 609.2572 | 701.8485 | 809.1457 | 933.5398 | 1077.8163 | 1245.2205 | 1439.5347 | 1665.1671 | 1927.2564 | 2231.7941 | 2585.7665 | 2997.3214 | 3475.962 | 4032.7742 | 4680.6916 | 5434.8047 | 6312.7231 | 7334.9977 | 8525.6142 | 9912.5701 | 11057.7325 | 11057.7325 | 11057.7325 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 232.1594 | 265.6349 | 304.2802 | 348.9214 | 400.5194 | 460.1922 | 529.2407 | 609.1792 | 701.7705 | 809.0677 | 933.4618 | 1077.7383 | 1245.1425 | 1439.4567 | 1665.0891 | 1927.1784 | 2231.7161 | 2585.6732 | 2997.1976 | 3475.7965 | 4032.5512 | 4680.3889 | 5434.3913 | 6312.1554 | 7334.2141 | 8524.528 | 9911.0585 | 11055.6217 | 11054.7761 | 11053.5808 |  | 4295.7496 | 4919.617 | 5639.8314 | 6471.7892 | 7433.3983 | 8545.4929 | 9832.3181 | 11322.0945 | 13047.6773 | 15047.3261 | 17365.602 | 20054.4162 | 23174.253 | 26795.5979 | 31000.6051 | 35885.0443 | 41560.5739 | 48151.0242 | 55808.3763 | 64711.2766 | 75064.4696 | 87106.3716 | 101114.5236 | 117411.878 | 136374.0293 | 158437.4936 | 184109.1468 | 205202.5346 | 204851.8741 | 204356.1703
| TRUE | 1576 | 22006137 | FB | FB011 | 11 | FB11 | SENSITIVE EF | Blank | EMAIL | GROUP_3328 | GROUP 3328 | GROUP 3000s | Electronic |  | 0.57434 | 2190 |  | 9.9 | 0.042792 | 0.030778 | 0.012014 | 252.2846 | 9849.091 | 10101.3755 | 296.2065 | 17.4289 | 295.2679 |  | 18.0962 | 0.22875 | 0.16453 | 0.064219 | 1348.5871 | 52648.3173 | 53996.9044 | 1583.3716 | 93.1662 | 1578.3548 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.039006 |  | 10710.2788 | 57251.797 | 46.5266 | 57205.2704 |  | 0.060317 |  | 10.5155 | 11.1693 | 11.8637 | 12.6013 | 13.3848 | 14.217 | 15.1009 | 16.0397 | 17.037 | 18.0962 | 19.2213 | 20.4164 | 21.6857 | 23.034 | 24.4661 | 25.9872 | 27.6029 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.050397 | 0.059416 | 0.070118 | 0.082825 | 0.09792 | 0.11586 | 0.1372 | 0.16258 | 0.19278 | 0.22875 | 0.27158 | 0.32262 | 0.38345 | 0.45598 | 0.54247 | 0.64566 | 0.76879 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.036248 | 0.042735 | 0.050433 | 0.059572 | 0.070429 | 0.083334 | 0.098678 | 0.11693 | 0.13866 | 0.16453 | 0.19534 | 0.23204 | 0.2758 | 0.32796 | 0.39018 | 0.46439 | 0.55295 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 12613.6429 | 14870.9242 | 17549.5273 | 20729.8829 | 24507.9883 | 28998.4462 | 34338.1006 | 40690.3861 | 48250.5334 | 57251.797 | 67972.9087 | 80746.999 | 95972.2744 | 114124.7987 | 135773.7931 | 161599.9537 | 192417.3805 | 200549.0365 | 200549.0365 | 200549.0365 | 200549.0365 | 200549.0365 | 200549.0365 | 200549.0365 | 200549.0365 | 200549.0365 | 200549.0365 | 200549.0365 | 200549.0365 | 200549.0365 |  | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 38.6921 | 51.2887 | 68.58 | 92.4225 | 125.4327 | 171.3046 | 235.2615 | 324.7001 | 450.1077 | 626.3715 | 874.6455 | 1225.0165 | 1720.3111 |  | 297.119 | 350.2901 | 413.3856 | 488.3 | 577.2947 | 683.0691 | 808.8466 | 958.477 | 1136.5591 | 1348.5871 | 1601.1269 | 1902.0253 | 2260.6622 | 2688.2516 | 3198.2017 | 3806.5464 | 4532.4622 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 282.9061 | 336.0771 | 399.1726 | 474.0871 | 563.0817 | 668.8561 | 794.6337 | 944.2641 | 1122.3461 | 1334.3742 | 1586.9139 | 1887.8123 | 2246.4493 | 2674.0387 | 3183.9887 | 3792.3334 | 4518.2493 | 4706.9944 | 4701.4559 | 4693.8534 | 4683.3704 | 4668.8566 | 4648.6878 | 4620.5675 | 4581.2435 | 4526.1048 | 4448.6059 | 4339.4458 | 4185.3961 | 3967.627 |  | 11599.4101 | 13675.1888 | 16138.4119 | 19063.0428 | 22537.3598 | 26666.7507 | 31577.0562 | 37418.5697 | 44370.8238 | 52648.3173 | 62507.3701 | 74254.3265 | 88255.374 | 104948.2973 | 124856.548 | 148606.0889 | 176945.5603 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 11598.109 | 13673.8877 | 16137.1108 | 19061.7417 | 22536.0587 | 26665.4496 | 31575.7551 | 37417.2686 | 44369.5227 | 52647.0162 | 62506.069 | 74253.0254 | 88254.0729 | 104946.9962 | 124855.2469 | 148604.7878 | 176944.2592 | 184421.812 | 184421.305 | 184420.6091 | 184419.6494 | 184418.3208 | 184416.4745 | 184413.9002 | 184410.3004 | 184405.2528 | 184398.1583 | 184388.1654 | 184374.0632 | 184354.1279 |  | 11881.0151 | 14009.9649 | 16536.2834 | 19535.8287 | 23099.1404 | 27334.3057 | 32370.3888 | 38361.5327 | 45491.8688 | 53981.3904 | 64092.9829 | 76140.8377 | 90500.5222 | 107621.0349 | 128039.2356 | 152397.1213 | 181462.5085 | 189128.8064 | 189122.761 | 189114.4625 | 189103.0198 | 189087.1774 | 189065.1623 | 189034.4677 | 188991.5439 | 188931.3576 | 188846.7642 | 188727.6112 | 188559.4592 | 188321.7548 |  | 348.8464 | 411.2744 | 485.3546 | 573.3114 | 677.7997 | 801.9891 | 949.6641 | 1125.3446 | 1334.4302 | 1583.3716 | 1879.8777 | 2233.1615 | 2654.2359 | 3156.2672 | 3754.9978 | 4469.2533 | 5321.5486 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 334.1536 | 396.5815 | 470.6617 | 558.6185 | 663.1069 | 787.2962 | 934.9712 | 1110.6518 | 1319.7373 | 1568.6788 | 1865.1848 | 2218.4686 | 2639.5431 | 3141.5743 | 3740.3049 | 4454.5604 | 5306.8558 | 5528.8535 | 5523.1281 | 5515.2688 | 5504.4319 | 5489.428 | 5468.5782 | 5439.5083 | 5398.8565 | 5341.8559 | 5261.7401 | 5148.894 | 4989.6425 | 4764.52 |  | 20.5262 | 24.1995 | 28.5584 | 33.7339 | 39.882 | 47.1893 | 55.8786 | 66.2157 | 78.5184 | 93.1662 | 110.6127 | 131.4 | 156.1762 | 185.7159 | 220.9454 | 262.9725 | 313.1218 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 18.4585 | 22.1318 | 26.4907 | 31.6661 | 37.8143 | 45.1216 | 53.8108 | 64.148 | 76.4506 | 91.0984 | 108.545 | 129.3323 | 154.1085 | 183.6482 | 218.8777 | 260.9047 | 311.0541 | 323.8796 | 323.0738 | 321.9678 | 320.4427 | 318.3312 | 315.397 | 311.306 | 305.5851 | 297.5634 | 286.2886 | 270.4078 | 247.9963 | 216.3147 |  | 347.7411 | 409.9713 | 483.8168 | 571.4949 | 675.6522 | 799.448 | 946.6551 | 1121.779 | 1330.2021 | 1578.3548 | 1873.9213 | 2226.0858 | 2645.8261 | 3146.2666 | 3743.1002 | 4455.0926 | 5304.6874 | 5528.8662 | 5528.8662 | 5528.8662 | 5528.8662 | 5528.8662 | 5528.8662 | 5528.8662 | 5528.8662 | 5528.8662 | 5528.8662 | 5528.8662 | 5528.8662 | 5528.8662 |  | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.046688 | 0.061887 | 0.082752 | 0.11152 | 0.15135 | 0.2067 | 0.28388 | 0.3918 | 0.54312 | 0.75581 | 1.0554 | 1.4782 | 2.0758 |  | 347.7021 | 409.9323 | 483.7778 | 571.4559 | 675.6132 | 799.409 | 946.6161 | 1121.74 | 1330.1631 | 1578.3158 | 1873.8823 | 2226.0468 | 2645.7871 | 3146.2276 | 3743.0612 | 4455.0536 | 5304.6484 | 5528.8195 | 5528.8043 | 5528.7835 | 5528.7547 | 5528.7149 | 5528.6595 | 5528.5824 | 5528.4744 | 5528.3231 | 5528.1104 | 5527.8108 | 5527.3881 | 5526.7904 |  | 12581.3293 | 14838.6105 | 17517.2136 | 20697.5693 | 24475.6747 | 28966.1326 | 34305.7869 | 40658.0725 | 48218.2198 | 57219.4833 | 67940.595 | 80714.6854 | 95939.9608 | 114092.485 | 135741.4795 | 161567.64 | 192385.0668 | 200510.3591 | 200497.7673 | 200480.4826 | 200456.6492 | 200423.6515 | 200377.797 | 200313.8644 | 200224.4599 | 200099.1 | 199922.9033 | 199674.7237 | 199324.486 | 198829.3799
| TRUE | 1577 | 22006138 | FB | FB011 | 11 | FB11 | OVERCURRENT | Blank | ASEA | RACID_3245 | RACID 3245 | RACID | Electronic |  | 0.57434 | 2190 |  | 6.6 | 0.014726 | 0.010592 | 0.0041343 | 86.8187 | 3389.3699 | 3476.1886 | 101.9336 | 5.9978 | 101.6106 |  | 11.1153 | 0.058633 | 0.042172 | 0.016461 | 345.6775 | 13495.1158 | 13840.7933 | 405.8588 | 23.8809 | 404.5729 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.039006 |  | 3685.7306 | 14675.1059 | 46.5266 | 14628.5793 |  | 0.052126 |  | 6.9532 | 7.3252 | 7.7172 | 8.1301 | 8.5651 | 9.0234 | 9.5062 | 10.0149 | 10.5508 | 11.1153 | 11.7101 | 12.3367 | 12.9968 | 13.6922 | 14.4249 | 15.1967 | 16.0099 | 16.8665 | 17.769 | 18.7198 | 19.7215 | 20.7767 | 21.8884 | 23.0596 | 24.2935 | 25.5934 | 26.9629 | 28 | 28 | 28 |  | 0.016829 | 0.019254 | 0.022055 | 0.02529 | 0.029029 | 0.033353 | 0.038356 | 0.044149 | 0.050858 | 0.058633 | 0.067647 | 0.078102 | 0.090233 | 0.10431 | 0.12066 | 0.13966 | 0.16172 | 0.18737 | 0.2172 | 0.25188 | 0.29223 | 0.33918 | 0.39382 | 0.45744 | 0.53152 | 0.61779 | 0.7183 | 0.80128 | 0.80128 | 0.80128 |  | 0.012104 | 0.013849 | 0.015863 | 0.01819 | 0.020879 | 0.023989 | 0.027588 | 0.031754 | 0.03658 | 0.042172 | 0.048656 | 0.056175 | 0.0649 | 0.075028 | 0.086788 | 0.10045 | 0.11632 | 0.13477 | 0.15622 | 0.18117 | 0.21019 | 0.24396 | 0.28326 | 0.32902 | 0.3823 | 0.44435 | 0.51664 | 0.57632 | 0.57632 | 0.57632 | 4211.9835 | 4819.1132 | 5520.005 | 6329.6422 | 7265.4522 | 8347.7104 | 9600.0114 | 11049.8185 | 12729.1057 | 14675.1059 | 16931.1848 | 19547.8608 | 22583.9954 | 26108.1832 | 30200.3742 | 34953.7687 | 40477.0295 | 46896.8651 | 54361.0467 | 63041.9323 | 73140.5813 | 84891.5622 | 98568.5674 | 114490.9724 | 133031.4987 | 154625.166 | 179779.7508 | 200549.0365 | 200549.0365 | 200549.0365 |  | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 32.3259 | 38.6921 | 51.2887 | 68.58 | 92.4225 | 125.4327 | 171.3046 | 235.2615 | 324.7001 | 450.1077 | 626.3715 | 874.6455 | 1225.0165 | 1720.3111 |  | 99.2148 | 113.516 | 130.0257 | 149.0971 | 171.1404 | 196.6334 | 226.1318 | 260.2825 | 299.8388 | 345.6775 | 398.8203 | 460.4571 | 531.9743 | 614.9879 | 711.3809 | 823.3489 | 953.4513 | 1104.6729 | 1280.4945 | 1484.9759 | 1722.8533 | 1999.652 | 2321.8189 | 2696.877 | 3133.6059 | 3642.2527 | 4234.7782 | 4724.0064 | 4724.0064 | 4724.0064 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 85.0019 | 99.303 | 115.8128 | 134.8841 | 156.9275 | 182.4204 | 211.9189 | 246.0696 | 285.6258 | 331.4646 | 384.6073 | 446.2441 | 517.7614 | 600.7749 | 697.168 | 809.1359 | 939.2384 | 1087.6609 | 1257.944 | 1454.823 | 1682.2174 | 1944.5022 | 2246.5004 | 2593.4381 | 2990.8431 | 3444.3512 | 3959.3777 | 4339.4458 | 4185.3961 | 3967.627 |  | 3873.308 | 4431.6198 | 5076.1546 | 5820.6908 | 6681.2546 | 7676.4911 | 8828.0975 | 10161.3291 | 11705.5888 | 13495.1158 | 15569.7888 | 17976.0641 | 20768.0705 | 24008.8868 | 27772.0345 | 32143.22 | 37222.3686 | 43126.0006 | 49990.0053 | 57972.8817 | 67259.5225 | 78065.6353 | 90642.9052 | 105285.0278 | 122334.7549 | 142192.1272 | 165324.0921 | 184423.3694 | 184423.3694 | 184423.3694 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 3872.0069 | 4430.3187 | 5074.8535 | 5819.3897 | 6679.9535 | 7675.19 | 8826.7964 | 10160.028 | 11704.2877 | 13493.8147 | 15568.4877 | 17974.763 | 20766.7694 | 24007.5857 | 27770.7334 | 32141.9189 | 37221.0675 | 43124.4433 | 49987.941 | 57970.1214 | 67255.8026 | 78060.5867 | 90636.0103 | 105275.5587 | 122321.686 | 142174.0107 | 165298.881 | 184388.1654 | 184374.0632 | 184354.1279 |  | 3957.0088 | 4529.6218 | 5190.6663 | 5954.2738 | 6836.881 | 7857.6104 | 9038.7153 | 10406.0976 | 11989.9136 | 13825.2793 | 15953.095 | 18421.0072 | 21284.5308 | 24608.3606 | 28467.9014 | 32951.0549 | 38160.3059 | 44212.1042 | 51245.885 | 59424.9443 | 68938.02 | 80005.0889 | 92882.5107 | 107868.9968 | 125312.5291 | 145618.3618 | 169258.2587 | 188727.6112 | 188559.4592 | 188321.7548 |  | 116.4878 | 133.2787 | 152.6628 | 175.0543 | 200.9354 | 230.8666 | 265.5006 | 305.5969 | 352.0397 | 405.8588 | 468.2536 | 540.6211 | 624.5893 | 722.0552 | 835.23 | 966.6912 | 1119.444 | 1296.9928 | 1503.4242 | 1743.5052 | 2022.7963 | 2347.7847 | 2726.0397 | 3166.3942 | 3679.1562 | 4276.3566 | 4972.0388 | 5546.44 | 5546.44 | 5546.44 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 101.7949 | 118.5859 | 137.9699 | 160.3615 | 186.2425 | 216.1737 | 250.8077 | 290.904 | 337.3468 | 391.1659 | 453.5607 | 525.9282 | 609.8964 | 707.3623 | 820.5371 | 951.9983 | 1104.7511 | 1279.4063 | 1480.1124 | 1712.3341 | 1980.7882 | 2290.7727 | 2648.1779 | 3059.4625 | 3531.5727 | 4071.7726 | 4687.3389 | 5148.894 | 4989.6425 | 4764.52 |  | 6.8542 | 7.8422 | 8.9827 | 10.3003 | 11.8231 | 13.5843 | 15.6222 | 17.9814 | 20.7141 | 23.8809 | 27.5522 | 31.8103 | 36.7511 | 42.486 | 49.1452 | 56.8805 | 65.8685 | 76.3155 | 88.462 | 102.5885 | 119.0221 | 138.1445 | 160.4012 | 186.3118 | 216.4829 | 251.6224 | 292.5566 | 326.3545 | 326.3545 | 326.3545 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.7865 | 5.7744 | 6.915 | 8.2325 | 9.7554 | 11.5165 | 13.5544 | 15.9137 | 18.6464 | 21.8131 | 25.4845 | 29.7426 | 34.6833 | 40.4183 | 47.0775 | 54.8127 | 63.8008 | 73.8406 | 85.1813 | 98.2018 | 113.1103 | 130.1212 | 149.4437 | 171.2633 | 195.7134 | 222.8312 | 252.4907 | 270.4078 | 247.9963 | 216.3147 |  | 116.1187 | 132.8564 | 152.1791 | 174.4997 | 200.2987 | 230.1351 | 264.6594 | 304.6286 | 350.9243 | 404.5729 | 466.7699 | 538.9081 | 622.6103 | 719.7674 | 832.5836 | 963.6282 | 1115.8971 | 1292.8833 | 1498.6607 | 1737.981 | 2016.3871 | 2340.3458 | 2717.4024 | 3156.3616 | 3667.4989 | 4262.8071 | 4956.2851 | 5528.8662 | 5528.8662 | 5528.8662 |  | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.039006 | 0.046688 | 0.061887 | 0.082752 | 0.11152 | 0.15135 | 0.2067 | 0.28388 | 0.3918 | 0.54312 | 0.75581 | 1.0554 | 1.4782 | 2.0758 |  | 116.0797 | 132.8174 | 152.1401 | 174.4607 | 200.2597 | 230.0961 | 264.6203 | 304.5896 | 350.8853 | 404.5339 | 466.7309 | 538.8691 | 622.5713 | 719.7284 | 832.5445 | 963.5892 | 1115.8581 | 1292.8366 | 1498.5988 | 1737.8982 | 2016.2756 | 2340.1944 | 2717.1956 | 3156.0777 | 3667.1071 | 4262.264 | 4955.5292 | 5527.8108 | 5527.3881 | 5526.7904 |  | 4179.6699 | 4786.7995 | 5487.6913 | 6297.3285 | 7233.1386 | 8315.3968 | 9567.6978 | 11017.5049 | 12696.7921 | 14642.7922 | 16898.8711 | 19515.5471 | 22551.6817 | 26075.8695 | 30168.0605 | 34921.4551 | 40444.7159 | 46858.1876 | 54309.7775 | 62973.3784 | 73048.194 | 84766.1772 | 98397.3279 | 114255.8003 | 132706.9222 | 154175.2296 | 179153.6176 | 199674.7237 | 199324.486 | 198829.3799
| TRUE | 1578 | 22006139 | FB | FB013 | 11 | FB13 | PILOT WIRE | Blank | Metropolitan Vickers | HO2_971 | RI 009 | RI | Electromechanical |  | 0.57434 | 2190 |  | 6.6 | 0.003029 | 0.0021786 | 0.00085037 | 17.8577 | 697.1566 | 715.0143 | 20.9666 | 1.2337 | 41.8004 |  | 9.0234 | 0.0068603 | 0.0049343 | 0.001926 | 40.4454 | 1578.971 | 1619.4163 | 47.4868 | 2.7941 | 94.6726 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 779.015 | 1764.3698 | 46.5656 | 1717.8042 |  | 0.031275 |  | 6.8097 | 7.026 | 7.2492 | 7.4795 | 7.7172 | 7.9623 | 8.2153 | 8.4763 | 8.7456 | 9.0234 | 9.3101 | 9.6059 | 9.911 | 10.2259 | 10.5508 | 10.886 | 11.2318 | 11.5886 | 11.9568 | 12.3367 | 12.7286 | 13.133 | 13.5502 | 13.9807 | 14.4249 | 14.8831 | 15.356 | 15.8438 | 16.3472 | 16.8665 |  | 0.003281 | 0.0035556 | 0.0038548 | 0.0041809 | 0.0045364 | 0.0049241 | 0.0053468 | 0.005808 | 0.0063112 | 0.0068603 | 0.0074596 | 0.008114 | 0.0088284 | 0.0096087 | 0.010461 | 0.011392 | 0.012409 | 0.013521 | 0.014736 | 0.016065 | 0.017517 | 0.019105 | 0.020842 | 0.022741 | 0.024819 | 0.027092 | 0.02958 | 0.032301 | 0.03528 | 0.038541 |  | 0.0023599 | 0.0025574 | 0.0027726 | 0.0030072 | 0.0032628 | 0.0035416 | 0.0038457 | 0.0041774 | 0.0045393 | 0.0049343 | 0.0053654 | 0.005836 | 0.0063499 | 0.0069111 | 0.0075241 | 0.0081938 | 0.0089255 | 0.0097252 | 0.010599 | 0.011555 | 0.012599 | 0.013741 | 0.014991 | 0.016357 | 0.017851 | 0.019486 | 0.021275 | 0.023233 | 0.025375 | 0.02772 | 843.84 | 914.4594 | 991.4096 | 1075.2778 | 1166.7068 | 1266.4002 | 1375.1287 | 1493.7358 | 1623.1456 | 1764.3698 | 1918.5169 | 2086.8008 | 2270.5514 | 2471.2258 | 2690.4203 | 2929.8841 | 3191.5338 | 3477.4699 | 3789.9945 | 4131.6305 | 4505.1436 | 4913.5652 | 5360.2183 | 5848.7462 | 6383.1429 | 6967.7877 | 7607.4822 | 8307.4918 | 9073.59 | 9912.1087 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 19.3437 | 20.9625 | 22.7265 | 24.649 | 26.7449 | 29.0302 | 31.5226 | 34.2415 | 37.208 | 40.4454 | 43.9789 | 47.8366 | 52.0488 | 56.6489 | 61.6736 | 67.1629 | 73.1608 | 79.7154 | 86.8796 | 94.711 | 103.2732 | 112.6356 | 122.8744 | 134.0732 | 146.3233 | 159.7254 | 174.3894 | 190.436 | 207.9975 | 227.2192 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 5.1307 | 6.7496 | 8.5135 | 10.4361 | 12.5319 | 14.8173 | 17.3097 | 20.0286 | 22.9951 | 26.2324 | 29.766 | 33.6236 | 37.8358 | 42.436 | 47.4606 | 52.95 | 58.9479 | 62.7034 | 64.3291 | 64.5581 | 62.6373 | 57.4859 | 47.5559 | 30.6343 | 3.5605 | -38.1761 | -101.0111 | -194.1246 | -330.6128 | -529.1602 |  | 755.1699 | 818.3686 | 887.2329 | 962.2883 | 1044.11 | 1133.3277 | 1230.631 | 1336.775 | 1452.5865 | 1578.971 | 1716.9204 | 1867.5211 | 2031.9634 | 2211.551 | 2407.7127 | 2622.0137 | 2856.1694 | 3112.0596 | 3391.7443 | 3697.4815 | 4031.7461 | 4397.2509 | 4796.97 | 5234.1637 | 5712.4063 | 6235.617 | 6808.0929 | 7434.5459 | 8120.143 | 8870.5507 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 753.8688 | 817.0675 | 885.9318 | 960.9872 | 1042.8089 | 1132.0266 | 1229.3299 | 1335.4739 | 1451.2854 | 1577.6699 | 1715.6193 | 1866.22 | 2030.6623 | 2210.2499 | 2406.4116 | 2620.7126 | 2854.8683 | 3110.5022 | 3389.6799 | 3694.7212 | 4028.0261 | 4392.2023 | 4790.0751 | 5224.6946 | 5699.3374 | 6217.5005 | 6782.8818 | 7399.3419 | 8070.8368 | 8801.3092 |  | 758.9995 | 823.8171 | 894.4454 | 971.4233 | 1055.3408 | 1146.8438 | 1246.6396 | 1355.5025 | 1474.2804 | 1603.9023 | 1745.3853 | 1899.8436 | 2068.4981 | 2252.6859 | 2453.8722 | 2673.6626 | 2913.8162 | 3173.2057 | 3454.0091 | 3759.2792 | 4090.6634 | 4449.6882 | 4837.631 | 5255.3289 | 5702.8979 | 6179.3243 | 6681.8707 | 7205.2173 | 7740.2241 | 8272.149 |  | 22.7114 | 24.612 | 26.6831 | 28.9403 | 31.4011 | 34.0843 | 37.0106 | 40.2028 | 43.6858 | 47.4868 | 51.6355 | 56.1648 | 61.1103 | 66.5113 | 72.4107 | 78.8557 | 85.8979 | 93.5936 | 102.005 | 111.1999 | 121.2527 | 132.2451 | 144.2665 | 157.4148 | 171.7977 | 187.533 | 204.75 | 223.5902 | 244.2092 | 266.7773 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 8.0185 | 9.9192 | 11.9902 | 14.2475 | 16.7082 | 19.3914 | 22.3177 | 25.51 | 28.9929 | 32.7939 | 36.9426 | 41.4719 | 46.4174 | 51.8184 | 57.7179 | 64.1629 | 71.205 | 76.0072 | 78.6931 | 80.0288 | 79.2446 | 75.2331 | 66.4047 | 50.4832 | 24.2143 | -17.051 | -79.9499 | -173.9558 | -312.5883 | -515.1426 |  | 1.3363 | 1.4482 | 1.57 | 1.7029 | 1.8477 | 2.0055 | 2.1777 | 2.3655 | 2.5705 | 2.7941 | 3.0383 | 3.3048 | 3.5958 | 3.9135 | 4.2607 | 4.6399 | 5.0543 | 5.5071 | 6.002 | 6.543 | 7.1346 | 7.7813 | 8.4887 | 9.2623 | 10.1086 | 11.0345 | 12.0476 | 13.1561 | 14.3694 | 15.6973 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | -0.73139 | -0.61955 | -0.49769 | -0.36487 | -0.22008 | -0.062202 | 0.10999 | 0.29782 | 0.50276 | 0.72641 | 0.97052 | 1.237 | 1.528 | 1.8458 | 2.1929 | 2.5722 | 2.9865 | 3.0321 | 2.7213 | 2.1563 | 1.2227 | -0.24196 | -2.4688 | -5.7862 | -10.6608 | -17.7567 | -28.0183 | -42.7906 | -63.9889 | -94.3426 |  | 45.2788 | 49.0681 | 53.1971 | 57.6973 | 62.6032 | 67.9525 | 73.7867 | 80.1509 | 87.0948 | 94.6726 | 102.9438 | 111.9736 | 121.8333 | 132.6011 | 144.3626 | 157.2118 | 171.2514 | 186.5942 | 203.3636 | 221.6951 | 241.7371 | 263.6522 | 287.6187 | 313.8321 | 342.5068 | 373.8777 | 408.2024 | 445.7636 | 486.8709 | 531.8641 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 45.2008 | 48.9901 | 53.1191 | 57.6193 | 62.5252 | 67.8745 | 73.7087 | 80.0729 | 87.0168 | 94.5946 | 102.8658 | 111.8956 | 121.7553 | 132.5231 | 144.2846 | 157.1338 | 171.1734 | 186.5008 | 203.2398 | 221.5296 | 241.5141 | 263.3495 | 287.2053 | 313.2644 | 341.7232 | 372.7915 | 406.6908 | 443.6528 | 483.9146 | 527.7125 |  | 811.4874 | 882.1068 | 959.057 | 1042.9251 | 1134.3541 | 1234.0476 | 1342.776 | 1461.3831 | 1590.7929 | 1732.0172 | 1886.1642 | 2054.4481 | 2238.1988 | 2438.8732 | 2658.0677 | 2897.5314 | 3159.1811 | 3438.7458 | 3738.6634 | 4062.9939 | 4412.6448 | 4788.0288 | 5188.7722 | 5613.2903 | 6058.1746 | 6517.3081 | 6980.5932 | 7432.1237 | 7847.5614 | 8190.3763
| TRUE | 1579 | 22006142 | FB | FB013 | 11 | FB13 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 121.4668 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 328.8756 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 2263.7216 | 6129.1037 | 46.5656 | 6082.5381 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2496.8379 | 2755.0314 | 3041.0632 | 3358.003 | 3709.2633 | 4098.6388 | 4530.3491 | 5009.0864 | 5540.0697 | 6129.1037 | 6782.6451 | 7507.8767 | 8312.7892 | 9206.2729 | 10198.2197 | 11299.6364 | 12522.7715 | 13881.2556 | 15390.2585 | 17066.6638 | 18929.2639 | 20998.9763 | 23299.0855 | 25855.5121 | 28697.1121 | 31856.0113 | 35367.9772 | 39272.8334 | 42387.9899 | 42387.9899 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 133.9754 | 147.8295 | 163.1774 | 180.1838 | 199.0317 | 219.9248 | 243.0896 | 268.7777 | 297.2692 | 328.8756 | 363.9433 | 402.8578 | 446.0478 | 493.9904 | 547.2163 | 606.3161 | 671.9471 | 744.8407 | 825.8108 | 915.7634 | 1015.7068 | 1126.7635 | 1250.1828 | 1387.3556 | 1539.8302 | 1709.3305 | 1897.7757 | 2107.3025 | 2274.4557 | 2274.4557 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 133.8974 | 147.7515 | 163.0994 | 180.1058 | 198.9537 | 219.8468 | 243.0116 | 268.6997 | 297.1912 | 328.7976 | 363.8653 | 402.7798 | 445.9698 | 493.9124 | 547.1383 | 606.2381 | 671.8691 | 744.7473 | 825.687 | 915.5979 | 1015.4838 | 1126.4608 | 1249.7694 | 1386.7879 | 1539.0466 | 1708.2443 | 1896.2641 | 2105.1918 | 2271.4993 | 2270.304 |  | 2464.4853 | 2722.6788 | 3008.7106 | 3325.6503 | 3676.9107 | 4066.2862 | 4497.9964 | 4976.7338 | 5507.7171 | 6096.7511 | 6750.2925 | 7475.524 | 8280.4365 | 9173.9202 | 10165.867 | 11267.2838 | 12490.4189 | 13842.5315 | 15338.9274 | 16998.0272 | 18836.765 | 20873.4399 | 23127.6394 | 25620.0562 | 28372.1437 | 31405.5317 | 34741.0882 | 38397.4653 | 41161.9613 | 40666.2576
| TRUE | 1580 | 22006140 | FB | FB013 | 11 | FB13 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 121.4668 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 328.8756 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 2263.7216 | 6129.1037 | 46.5656 | 6082.5381 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2496.8379 | 2755.0314 | 3041.0632 | 3358.003 | 3709.2633 | 4098.6388 | 4530.3491 | 5009.0864 | 5540.0697 | 6129.1037 | 6782.6451 | 7507.8767 | 8312.7892 | 9206.2729 | 10198.2197 | 11299.6364 | 12522.7715 | 13881.2556 | 15390.2585 | 17066.6638 | 18929.2639 | 20998.9763 | 23299.0855 | 25855.5121 | 28697.1121 | 31856.0113 | 35367.9772 | 39272.8334 | 42387.9899 | 42387.9899 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 133.9754 | 147.8295 | 163.1774 | 180.1838 | 199.0317 | 219.9248 | 243.0896 | 268.7777 | 297.2692 | 328.8756 | 363.9433 | 402.8578 | 446.0478 | 493.9904 | 547.2163 | 606.3161 | 671.9471 | 744.8407 | 825.8108 | 915.7634 | 1015.7068 | 1126.7635 | 1250.1828 | 1387.3556 | 1539.8302 | 1709.3305 | 1897.7757 | 2107.3025 | 2274.4557 | 2274.4557 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 133.8974 | 147.7515 | 163.0994 | 180.1058 | 198.9537 | 219.8468 | 243.0116 | 268.6997 | 297.1912 | 328.7976 | 363.8653 | 402.7798 | 445.9698 | 493.9124 | 547.1383 | 606.2381 | 671.8691 | 744.7473 | 825.687 | 915.5979 | 1015.4838 | 1126.4608 | 1249.7694 | 1386.7879 | 1539.0466 | 1708.2443 | 1896.2641 | 2105.1918 | 2271.4993 | 2270.304 |  | 2464.4853 | 2722.6788 | 3008.7106 | 3325.6503 | 3676.9107 | 4066.2862 | 4497.9964 | 4976.7338 | 5507.7171 | 6096.7511 | 6750.2925 | 7475.524 | 8280.4365 | 9173.9202 | 10165.867 | 11267.2838 | 12490.4189 | 13842.5315 | 15338.9274 | 16998.0272 | 18836.765 | 20873.4399 | 23127.6394 | 25620.0562 | 28372.1437 | 31405.5317 | 34741.0882 | 38397.4653 | 41161.9613 | 40666.2576
| TRUE | 1581 | 22006141 | FB | FB013 | 11 | FB13 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 121.4668 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 328.8756 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 2263.7216 | 6129.1037 | 46.5656 | 6082.5381 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2496.8379 | 2755.0314 | 3041.0632 | 3358.003 | 3709.2633 | 4098.6388 | 4530.3491 | 5009.0864 | 5540.0697 | 6129.1037 | 6782.6451 | 7507.8767 | 8312.7892 | 9206.2729 | 10198.2197 | 11299.6364 | 12522.7715 | 13881.2556 | 15390.2585 | 17066.6638 | 18929.2639 | 20998.9763 | 23299.0855 | 25855.5121 | 28697.1121 | 31856.0113 | 35367.9772 | 39272.8334 | 42387.9899 | 42387.9899 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 133.9754 | 147.8295 | 163.1774 | 180.1838 | 199.0317 | 219.9248 | 243.0896 | 268.7777 | 297.2692 | 328.8756 | 363.9433 | 402.8578 | 446.0478 | 493.9904 | 547.2163 | 606.3161 | 671.9471 | 744.8407 | 825.8108 | 915.7634 | 1015.7068 | 1126.7635 | 1250.1828 | 1387.3556 | 1539.8302 | 1709.3305 | 1897.7757 | 2107.3025 | 2274.4557 | 2274.4557 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 133.8974 | 147.7515 | 163.0994 | 180.1058 | 198.9537 | 219.8468 | 243.0116 | 268.6997 | 297.1912 | 328.7976 | 363.8653 | 402.7798 | 445.9698 | 493.9124 | 547.1383 | 606.2381 | 671.8691 | 744.7473 | 825.687 | 915.5979 | 1015.4838 | 1126.4608 | 1249.7694 | 1386.7879 | 1539.0466 | 1708.2443 | 1896.2641 | 2105.1918 | 2271.4993 | 2270.304 |  | 2464.4853 | 2722.6788 | 3008.7106 | 3325.6503 | 3676.9107 | 4066.2862 | 4497.9964 | 4976.7338 | 5507.7171 | 6096.7511 | 6750.2925 | 7475.524 | 8280.4365 | 9173.9202 | 10165.867 | 11267.2838 | 12490.4189 | 13842.5315 | 15338.9274 | 16998.0272 | 18836.765 | 20873.4399 | 23127.6394 | 25620.0562 | 28372.1437 | 31405.5317 | 34741.0882 | 38397.4653 | 41161.9613 | 40666.2576
| TRUE | 1582 | 22006143 | FB | FB014 | 11 | FB14 | SENSITIVE EF | Blank | English Electric | CMG_1328 | CMG 1328 | CMG | Electromechanical |  | 0.57434 | 2190 |  | 8.25 | 0.0054067 | 0.0038888 | 0.0015179 | 31.8755 | 1244.4067 | 1276.2822 | 37.4249 | 2.2021 | 74.6127 |  | 11.5885 | 0.013521 | 0.0097249 | 0.0037959 | 79.7129 | 3111.9605 | 3191.6734 | 93.5906 | 5.5069 | 186.5882 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 1390.5218 | 3477.3591 | 46.5656 | 3430.7935 |  | 0.03398 |  | 8.5352 | 8.8302 | 9.1354 | 9.4511 | 9.7778 | 10.1158 | 10.4654 | 10.8271 | 11.2014 | 11.5885 | 11.9891 | 12.4035 | 12.8322 | 13.2757 | 13.7346 | 14.2093 | 14.7004 | 15.2085 | 15.7342 | 16.278 | 16.8407 | 17.4227 | 18.0249 | 18.6479 | 19.2925 | 19.9593 | 20.6492 | 21.3629 | 22.1013 | 22.8652 |  | 0.0059156 | 0.0064751 | 0.0070903 | 0.007767 | 0.0085115 | 0.0093307 | 0.010232 | 0.011225 | 0.012317 | 0.013521 | 0.014846 | 0.016306 | 0.017915 | 0.019688 | 0.021642 | 0.023795 | 0.02617 | 0.028788 | 0.031676 | 0.034861 | 0.038374 | 0.042249 | 0.046526 | 0.051245 | 0.056453 | 0.062201 | 0.068547 | 0.075552 | 0.083287 | 0.091827 |  | 0.0042548 | 0.0046572 | 0.0050997 | 0.0055865 | 0.0061219 | 0.0067111 | 0.0073596 | 0.0080734 | 0.0088594 | 0.0097249 | 0.010678 | 0.011728 | 0.012885 | 0.01416 | 0.015566 | 0.017115 | 0.018823 | 0.020706 | 0.022783 | 0.025074 | 0.0276 | 0.030388 | 0.033464 | 0.036858 | 0.040604 | 0.044739 | 0.049303 | 0.054341 | 0.059904 | 0.066047 | 1521.4077 | 1665.3021 | 1823.5346 | 1997.5732 | 2189.0385 | 2399.7201 | 2631.5941 | 2886.8429 | 3167.8771 | 3477.3591 | 3818.2302 | 4193.7396 | 4607.4773 | 5063.4096 | 5565.9197 | 6119.8509 | 6730.5559 | 7403.9506 | 8146.5736 | 8965.6523 | 9869.176 | 10865.9766 | 11965.8181 | 13179.4954 | 14518.9438 | 15997.3603 | 17629.3375 | 19431.0118 | 21420.228 | 23616.7206 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 34.8758 | 38.1744 | 41.8016 | 45.7912 | 50.1802 | 55.0097 | 60.3251 | 66.1763 | 72.6185 | 79.7129 | 87.5268 | 96.1348 | 105.619 | 116.0706 | 127.5898 | 140.2878 | 154.2872 | 169.7237 | 186.7472 | 205.5232 | 226.2351 | 249.0851 | 274.2972 | 302.1189 | 332.8236 | 366.7139 | 404.1244 | 445.4249 | 491.0245 | 541.3756 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 20.6629 | 23.9614 | 27.5887 | 31.5782 | 35.9673 | 40.7968 | 46.1121 | 51.9633 | 58.4056 | 65.5 | 73.3139 | 81.9218 | 91.4061 | 101.8576 | 113.3769 | 126.0749 | 140.0743 | 152.7117 | 164.1968 | 175.3703 | 185.5991 | 193.9354 | 198.9787 | 198.68 | 190.0608 | 168.8124 | 128.7239 | 60.8643 | -47.5858 | -215.0038 |  | 1361.5392 | 1490.3132 | 1631.9188 | 1787.6695 | 1959.0158 | 2147.5591 | 2355.0679 | 2583.4953 | 2834.9986 | 3111.9605 | 3417.0131 | 3753.0642 | 4123.3265 | 4531.3498 | 4981.0564 | 5476.7809 | 6023.3134 | 6625.9482 | 7290.5369 | 8023.5473 | 8832.1293 | 9724.1868 | 10708.4577 | 11794.6025 | 12993.3025 | 14316.368 | 15776.8581 | 17389.2136 | 19169.4043 | 21135.0908 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 1360.2381 | 1489.0121 | 1630.6177 | 1786.3684 | 1957.7147 | 2146.258 | 2353.7668 | 2582.1942 | 2833.6975 | 3110.6594 | 3415.712 | 3751.7631 | 4122.0254 | 4530.0487 | 4979.7553 | 5475.4798 | 6022.0123 | 6624.3909 | 7288.4725 | 8020.787 | 8828.4094 | 9719.1382 | 10701.5627 | 11785.1334 | 12980.2336 | 14298.2514 | 15751.647 | 17354.0097 | 19120.0981 | 21065.8493 |  | 1380.9009 | 1512.9735 | 1658.2063 | 1817.9466 | 1993.6819 | 2187.0548 | 2399.8789 | 2634.1576 | 2892.1031 | 3176.1593 | 3489.0258 | 3833.6849 | 4213.4315 | 4631.9063 | 5093.1322 | 5601.5546 | 6162.0866 | 6777.1026 | 7452.6693 | 8196.1573 | 9014.0085 | 9913.0736 | 10900.5415 | 11983.8134 | 13170.2943 | 14467.0638 | 15880.3709 | 17414.8739 | 19072.5122 | 20850.8454 |  | 40.9476 | 44.8204 | 49.0791 | 53.7633 | 58.9164 | 64.5868 | 70.8275 | 77.6973 | 85.2612 | 93.5906 | 102.7649 | 112.8715 | 124.007 | 136.2781 | 149.8028 | 164.7114 | 181.1481 | 199.2721 | 219.2592 | 241.3041 | 265.6218 | 292.45 | 322.0515 | 354.7167 | 390.767 | 430.5576 | 474.4811 | 522.9718 | 576.5102 | 635.6272 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 26.2547 | 30.1276 | 34.3863 | 39.0704 | 44.2235 | 49.8939 | 56.1346 | 63.0045 | 70.5683 | 78.8978 | 88.0721 | 98.1786 | 109.3141 | 121.5852 | 135.1099 | 150.0186 | 166.4552 | 181.6856 | 195.9474 | 210.133 | 223.6138 | 235.438 | 244.1897 | 247.7851 | 243.1836 | 225.9735 | 189.7812 | 125.4258 | 19.7127 | -146.2928 |  | 2.4094 | 2.6372 | 2.8878 | 3.1634 | 3.4667 | 3.8003 | 4.1675 | 4.5717 | 5.0168 | 5.5069 | 6.0467 | 6.6414 | 7.2966 | 8.0187 | 8.8144 | 9.6917 | 10.6588 | 11.7252 | 12.9013 | 14.1984 | 15.6293 | 17.2079 | 18.9496 | 20.8717 | 22.9929 | 25.3342 | 27.9186 | 30.7719 | 33.9221 | 37.4005 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.34164 | 0.56952 | 0.8201 | 1.0957 | 1.3989 | 1.7326 | 2.0998 | 2.504 | 2.9491 | 3.4392 | 3.979 | 4.5737 | 5.2289 | 5.9509 | 6.7467 | 7.6239 | 8.5911 | 9.2503 | 9.6206 | 9.8117 | 9.7175 | 9.1846 | 7.9921 | 5.8231 | 2.2234 | -3.457 | -12.1473 | -25.1749 | -44.4362 | -72.6393 |  | 81.6357 | 89.3568 | 97.8473 | 107.1858 | 117.4595 | 128.7642 | 141.2061 | 154.9023 | 169.982 | 186.5882 | 204.8787 | 225.0278 | 247.2281 | 271.6925 | 298.6562 | 328.3791 | 361.1483 | 397.2813 | 437.129 | 481.0792 | 529.5605 | 583.0468 | 642.0621 | 707.1856 | 779.0578 | 858.3867 | 945.9554 | 1042.6296 | 1149.367 | 1267.2265 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 81.5577 | 89.2788 | 97.7692 | 107.1078 | 117.3815 | 128.6862 | 141.1281 | 154.8243 | 169.904 | 186.5102 | 204.8007 | 224.9498 | 247.1501 | 271.6145 | 298.5782 | 328.3011 | 361.0703 | 397.188 | 437.0052 | 480.9137 | 529.3374 | 582.7441 | 641.6487 | 706.6179 | 778.2742 | 857.3005 | 944.4437 | 1040.5189 | 1146.4107 | 1263.0749 |  | 1489.055 | 1632.9494 | 1791.182 | 1965.2205 | 2156.6859 | 2367.3674 | 2599.2414 | 2854.4903 | 3135.5245 | 3445.0065 | 3785.8776 | 4161.387 | 4575.1246 | 5031.057 | 5533.567 | 6087.4982 | 6698.2032 | 7365.2265 | 8095.2425 | 8897.0157 | 9776.6772 | 10740.4403 | 11794.372 | 12944.0395 | 14193.9755 | 15546.8808 | 17002.4485 | 18555.6437 | 20194.1995 | 21894.9882
| TRUE | 1583 | 22006145 | FB | FB014 | 11 | FB14 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 121.4668 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 328.8756 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 2263.7216 | 6129.1037 | 46.5656 | 6082.5381 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2496.8379 | 2755.0314 | 3041.0632 | 3358.003 | 3709.2633 | 4098.6388 | 4530.3491 | 5009.0864 | 5540.0697 | 6129.1037 | 6782.6451 | 7507.8767 | 8312.7892 | 9206.2729 | 10198.2197 | 11299.6364 | 12522.7715 | 13881.2556 | 15390.2585 | 17066.6638 | 18929.2639 | 20998.9763 | 23299.0855 | 25855.5121 | 28697.1121 | 31856.0113 | 35367.9772 | 39272.8334 | 42387.9899 | 42387.9899 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 133.9754 | 147.8295 | 163.1774 | 180.1838 | 199.0317 | 219.9248 | 243.0896 | 268.7777 | 297.2692 | 328.8756 | 363.9433 | 402.8578 | 446.0478 | 493.9904 | 547.2163 | 606.3161 | 671.9471 | 744.8407 | 825.8108 | 915.7634 | 1015.7068 | 1126.7635 | 1250.1828 | 1387.3556 | 1539.8302 | 1709.3305 | 1897.7757 | 2107.3025 | 2274.4557 | 2274.4557 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 133.8974 | 147.7515 | 163.0994 | 180.1058 | 198.9537 | 219.8468 | 243.0116 | 268.6997 | 297.1912 | 328.7976 | 363.8653 | 402.7798 | 445.9698 | 493.9124 | 547.1383 | 606.2381 | 671.8691 | 744.7473 | 825.687 | 915.5979 | 1015.4838 | 1126.4608 | 1249.7694 | 1386.7879 | 1539.0466 | 1708.2443 | 1896.2641 | 2105.1918 | 2271.4993 | 2270.304 |  | 2464.4853 | 2722.6788 | 3008.7106 | 3325.6503 | 3676.9107 | 4066.2862 | 4497.9964 | 4976.7338 | 5507.7171 | 6096.7511 | 6750.2925 | 7475.524 | 8280.4365 | 9173.9202 | 10165.867 | 11267.2838 | 12490.4189 | 13842.5315 | 15338.9274 | 16998.0272 | 18836.765 | 20873.4399 | 23127.6394 | 25620.0562 | 28372.1437 | 31405.5317 | 34741.0882 | 38397.4653 | 41161.9613 | 40666.2576
| TRUE | 1584 | 22006144 | FB | FB014 | 11 | FB14 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 121.4668 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 328.8756 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 2263.7216 | 6129.1037 | 46.5656 | 6082.5381 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2496.8379 | 2755.0314 | 3041.0632 | 3358.003 | 3709.2633 | 4098.6388 | 4530.3491 | 5009.0864 | 5540.0697 | 6129.1037 | 6782.6451 | 7507.8767 | 8312.7892 | 9206.2729 | 10198.2197 | 11299.6364 | 12522.7715 | 13881.2556 | 15390.2585 | 17066.6638 | 18929.2639 | 20998.9763 | 23299.0855 | 25855.5121 | 28697.1121 | 31856.0113 | 35367.9772 | 39272.8334 | 42387.9899 | 42387.9899 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 133.9754 | 147.8295 | 163.1774 | 180.1838 | 199.0317 | 219.9248 | 243.0896 | 268.7777 | 297.2692 | 328.8756 | 363.9433 | 402.8578 | 446.0478 | 493.9904 | 547.2163 | 606.3161 | 671.9471 | 744.8407 | 825.8108 | 915.7634 | 1015.7068 | 1126.7635 | 1250.1828 | 1387.3556 | 1539.8302 | 1709.3305 | 1897.7757 | 2107.3025 | 2274.4557 | 2274.4557 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 133.8974 | 147.7515 | 163.0994 | 180.1058 | 198.9537 | 219.8468 | 243.0116 | 268.6997 | 297.1912 | 328.7976 | 363.8653 | 402.7798 | 445.9698 | 493.9124 | 547.1383 | 606.2381 | 671.8691 | 744.7473 | 825.687 | 915.5979 | 1015.4838 | 1126.4608 | 1249.7694 | 1386.7879 | 1539.0466 | 1708.2443 | 1896.2641 | 2105.1918 | 2271.4993 | 2270.304 |  | 2464.4853 | 2722.6788 | 3008.7106 | 3325.6503 | 3676.9107 | 4066.2862 | 4497.9964 | 4976.7338 | 5507.7171 | 6096.7511 | 6750.2925 | 7475.524 | 8280.4365 | 9173.9202 | 10165.867 | 11267.2838 | 12490.4189 | 13842.5315 | 15338.9274 | 16998.0272 | 18836.765 | 20873.4399 | 23127.6394 | 25620.0562 | 28372.1437 | 31405.5317 | 34741.0882 | 38397.4653 | 41161.9613 | 40666.2576
| TRUE | 1585 | 22006146 | FB | FB015 | 11 | FB15 | SENSITIVE EF | Blank | English Electric | CMG_1328 | CMG 1328 | CMG | Electromechanical |  | 0.57434 | 2190 |  | 8.25 | 0.0054067 | 0.0038888 | 0.0015179 | 31.8755 | 1244.4067 | 1276.2822 | 37.4249 | 2.2021 | 74.6127 |  | 11.5885 | 0.013521 | 0.0097249 | 0.0037959 | 79.7129 | 3111.9605 | 3191.6734 | 93.5906 | 5.5069 | 186.5882 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 1390.5218 | 3477.3591 | 46.5656 | 3430.7935 |  | 0.03398 |  | 8.5352 | 8.8302 | 9.1354 | 9.4511 | 9.7778 | 10.1158 | 10.4654 | 10.8271 | 11.2014 | 11.5885 | 11.9891 | 12.4035 | 12.8322 | 13.2757 | 13.7346 | 14.2093 | 14.7004 | 15.2085 | 15.7342 | 16.278 | 16.8407 | 17.4227 | 18.0249 | 18.6479 | 19.2925 | 19.9593 | 20.6492 | 21.3629 | 22.1013 | 22.8652 |  | 0.0059156 | 0.0064751 | 0.0070903 | 0.007767 | 0.0085115 | 0.0093307 | 0.010232 | 0.011225 | 0.012317 | 0.013521 | 0.014846 | 0.016306 | 0.017915 | 0.019688 | 0.021642 | 0.023795 | 0.02617 | 0.028788 | 0.031676 | 0.034861 | 0.038374 | 0.042249 | 0.046526 | 0.051245 | 0.056453 | 0.062201 | 0.068547 | 0.075552 | 0.083287 | 0.091827 |  | 0.0042548 | 0.0046572 | 0.0050997 | 0.0055865 | 0.0061219 | 0.0067111 | 0.0073596 | 0.0080734 | 0.0088594 | 0.0097249 | 0.010678 | 0.011728 | 0.012885 | 0.01416 | 0.015566 | 0.017115 | 0.018823 | 0.020706 | 0.022783 | 0.025074 | 0.0276 | 0.030388 | 0.033464 | 0.036858 | 0.040604 | 0.044739 | 0.049303 | 0.054341 | 0.059904 | 0.066047 | 1521.4077 | 1665.3021 | 1823.5346 | 1997.5732 | 2189.0385 | 2399.7201 | 2631.5941 | 2886.8429 | 3167.8771 | 3477.3591 | 3818.2302 | 4193.7396 | 4607.4773 | 5063.4096 | 5565.9197 | 6119.8509 | 6730.5559 | 7403.9506 | 8146.5736 | 8965.6523 | 9869.176 | 10865.9766 | 11965.8181 | 13179.4954 | 14518.9438 | 15997.3603 | 17629.3375 | 19431.0118 | 21420.228 | 23616.7206 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 34.8758 | 38.1744 | 41.8016 | 45.7912 | 50.1802 | 55.0097 | 60.3251 | 66.1763 | 72.6185 | 79.7129 | 87.5268 | 96.1348 | 105.619 | 116.0706 | 127.5898 | 140.2878 | 154.2872 | 169.7237 | 186.7472 | 205.5232 | 226.2351 | 249.0851 | 274.2972 | 302.1189 | 332.8236 | 366.7139 | 404.1244 | 445.4249 | 491.0245 | 541.3756 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 20.6629 | 23.9614 | 27.5887 | 31.5782 | 35.9673 | 40.7968 | 46.1121 | 51.9633 | 58.4056 | 65.5 | 73.3139 | 81.9218 | 91.4061 | 101.8576 | 113.3769 | 126.0749 | 140.0743 | 152.7117 | 164.1968 | 175.3703 | 185.5991 | 193.9354 | 198.9787 | 198.68 | 190.0608 | 168.8124 | 128.7239 | 60.8643 | -47.5858 | -215.0038 |  | 1361.5392 | 1490.3132 | 1631.9188 | 1787.6695 | 1959.0158 | 2147.5591 | 2355.0679 | 2583.4953 | 2834.9986 | 3111.9605 | 3417.0131 | 3753.0642 | 4123.3265 | 4531.3498 | 4981.0564 | 5476.7809 | 6023.3134 | 6625.9482 | 7290.5369 | 8023.5473 | 8832.1293 | 9724.1868 | 10708.4577 | 11794.6025 | 12993.3025 | 14316.368 | 15776.8581 | 17389.2136 | 19169.4043 | 21135.0908 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 1360.2381 | 1489.0121 | 1630.6177 | 1786.3684 | 1957.7147 | 2146.258 | 2353.7668 | 2582.1942 | 2833.6975 | 3110.6594 | 3415.712 | 3751.7631 | 4122.0254 | 4530.0487 | 4979.7553 | 5475.4798 | 6022.0123 | 6624.3909 | 7288.4725 | 8020.787 | 8828.4094 | 9719.1382 | 10701.5627 | 11785.1334 | 12980.2336 | 14298.2514 | 15751.647 | 17354.0097 | 19120.0981 | 21065.8493 |  | 1380.9009 | 1512.9735 | 1658.2063 | 1817.9466 | 1993.6819 | 2187.0548 | 2399.8789 | 2634.1576 | 2892.1031 | 3176.1593 | 3489.0258 | 3833.6849 | 4213.4315 | 4631.9063 | 5093.1322 | 5601.5546 | 6162.0866 | 6777.1026 | 7452.6693 | 8196.1573 | 9014.0085 | 9913.0736 | 10900.5415 | 11983.8134 | 13170.2943 | 14467.0638 | 15880.3709 | 17414.8739 | 19072.5122 | 20850.8454 |  | 40.9476 | 44.8204 | 49.0791 | 53.7633 | 58.9164 | 64.5868 | 70.8275 | 77.6973 | 85.2612 | 93.5906 | 102.7649 | 112.8715 | 124.007 | 136.2781 | 149.8028 | 164.7114 | 181.1481 | 199.2721 | 219.2592 | 241.3041 | 265.6218 | 292.45 | 322.0515 | 354.7167 | 390.767 | 430.5576 | 474.4811 | 522.9718 | 576.5102 | 635.6272 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 26.2547 | 30.1276 | 34.3863 | 39.0704 | 44.2235 | 49.8939 | 56.1346 | 63.0045 | 70.5683 | 78.8978 | 88.0721 | 98.1786 | 109.3141 | 121.5852 | 135.1099 | 150.0186 | 166.4552 | 181.6856 | 195.9474 | 210.133 | 223.6138 | 235.438 | 244.1897 | 247.7851 | 243.1836 | 225.9735 | 189.7812 | 125.4258 | 19.7127 | -146.2928 |  | 2.4094 | 2.6372 | 2.8878 | 3.1634 | 3.4667 | 3.8003 | 4.1675 | 4.5717 | 5.0168 | 5.5069 | 6.0467 | 6.6414 | 7.2966 | 8.0187 | 8.8144 | 9.6917 | 10.6588 | 11.7252 | 12.9013 | 14.1984 | 15.6293 | 17.2079 | 18.9496 | 20.8717 | 22.9929 | 25.3342 | 27.9186 | 30.7719 | 33.9221 | 37.4005 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.34164 | 0.56952 | 0.8201 | 1.0957 | 1.3989 | 1.7326 | 2.0998 | 2.504 | 2.9491 | 3.4392 | 3.979 | 4.5737 | 5.2289 | 5.9509 | 6.7467 | 7.6239 | 8.5911 | 9.2503 | 9.6206 | 9.8117 | 9.7175 | 9.1846 | 7.9921 | 5.8231 | 2.2234 | -3.457 | -12.1473 | -25.1749 | -44.4362 | -72.6393 |  | 81.6357 | 89.3568 | 97.8473 | 107.1858 | 117.4595 | 128.7642 | 141.2061 | 154.9023 | 169.982 | 186.5882 | 204.8787 | 225.0278 | 247.2281 | 271.6925 | 298.6562 | 328.3791 | 361.1483 | 397.2813 | 437.129 | 481.0792 | 529.5605 | 583.0468 | 642.0621 | 707.1856 | 779.0578 | 858.3867 | 945.9554 | 1042.6296 | 1149.367 | 1267.2265 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 81.5577 | 89.2788 | 97.7692 | 107.1078 | 117.3815 | 128.6862 | 141.1281 | 154.8243 | 169.904 | 186.5102 | 204.8007 | 224.9498 | 247.1501 | 271.6145 | 298.5782 | 328.3011 | 361.0703 | 397.188 | 437.0052 | 480.9137 | 529.3374 | 582.7441 | 641.6487 | 706.6179 | 778.2742 | 857.3005 | 944.4437 | 1040.5189 | 1146.4107 | 1263.0749 |  | 1489.055 | 1632.9494 | 1791.182 | 1965.2205 | 2156.6859 | 2367.3674 | 2599.2414 | 2854.4903 | 3135.5245 | 3445.0065 | 3785.8776 | 4161.387 | 4575.1246 | 5031.057 | 5533.567 | 6087.4982 | 6698.2032 | 7365.2265 | 8095.2425 | 8897.0157 | 9776.6772 | 10740.4403 | 11794.372 | 12944.0395 | 14193.9755 | 15546.8808 | 17002.4485 | 18555.6437 | 20194.1995 | 21894.9882
| TRUE | 1586 | 22006148 | FB | FB015 | 11 | FB15 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 121.4668 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 328.8756 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 2263.7216 | 6129.1037 | 46.5656 | 6082.5381 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2496.8379 | 2755.0314 | 3041.0632 | 3358.003 | 3709.2633 | 4098.6388 | 4530.3491 | 5009.0864 | 5540.0697 | 6129.1037 | 6782.6451 | 7507.8767 | 8312.7892 | 9206.2729 | 10198.2197 | 11299.6364 | 12522.7715 | 13881.2556 | 15390.2585 | 17066.6638 | 18929.2639 | 20998.9763 | 23299.0855 | 25855.5121 | 28697.1121 | 31856.0113 | 35367.9772 | 39272.8334 | 42387.9899 | 42387.9899 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 133.9754 | 147.8295 | 163.1774 | 180.1838 | 199.0317 | 219.9248 | 243.0896 | 268.7777 | 297.2692 | 328.8756 | 363.9433 | 402.8578 | 446.0478 | 493.9904 | 547.2163 | 606.3161 | 671.9471 | 744.8407 | 825.8108 | 915.7634 | 1015.7068 | 1126.7635 | 1250.1828 | 1387.3556 | 1539.8302 | 1709.3305 | 1897.7757 | 2107.3025 | 2274.4557 | 2274.4557 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 133.8974 | 147.7515 | 163.0994 | 180.1058 | 198.9537 | 219.8468 | 243.0116 | 268.6997 | 297.1912 | 328.7976 | 363.8653 | 402.7798 | 445.9698 | 493.9124 | 547.1383 | 606.2381 | 671.8691 | 744.7473 | 825.687 | 915.5979 | 1015.4838 | 1126.4608 | 1249.7694 | 1386.7879 | 1539.0466 | 1708.2443 | 1896.2641 | 2105.1918 | 2271.4993 | 2270.304 |  | 2464.4853 | 2722.6788 | 3008.7106 | 3325.6503 | 3676.9107 | 4066.2862 | 4497.9964 | 4976.7338 | 5507.7171 | 6096.7511 | 6750.2925 | 7475.524 | 8280.4365 | 9173.9202 | 10165.867 | 11267.2838 | 12490.4189 | 13842.5315 | 15338.9274 | 16998.0272 | 18836.765 | 20873.4399 | 23127.6394 | 25620.0562 | 28372.1437 | 31405.5317 | 34741.0882 | 38397.4653 | 41161.9613 | 40666.2576
| TRUE | 1587 | 22006147 | FB | FB015 | 11 | FB15 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 121.4668 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 328.8756 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 2263.7216 | 6129.1037 | 46.5656 | 6082.5381 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2496.8379 | 2755.0314 | 3041.0632 | 3358.003 | 3709.2633 | 4098.6388 | 4530.3491 | 5009.0864 | 5540.0697 | 6129.1037 | 6782.6451 | 7507.8767 | 8312.7892 | 9206.2729 | 10198.2197 | 11299.6364 | 12522.7715 | 13881.2556 | 15390.2585 | 17066.6638 | 18929.2639 | 20998.9763 | 23299.0855 | 25855.5121 | 28697.1121 | 31856.0113 | 35367.9772 | 39272.8334 | 42387.9899 | 42387.9899 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 133.9754 | 147.8295 | 163.1774 | 180.1838 | 199.0317 | 219.9248 | 243.0896 | 268.7777 | 297.2692 | 328.8756 | 363.9433 | 402.8578 | 446.0478 | 493.9904 | 547.2163 | 606.3161 | 671.9471 | 744.8407 | 825.8108 | 915.7634 | 1015.7068 | 1126.7635 | 1250.1828 | 1387.3556 | 1539.8302 | 1709.3305 | 1897.7757 | 2107.3025 | 2274.4557 | 2274.4557 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 133.8974 | 147.7515 | 163.0994 | 180.1058 | 198.9537 | 219.8468 | 243.0116 | 268.6997 | 297.1912 | 328.7976 | 363.8653 | 402.7798 | 445.9698 | 493.9124 | 547.1383 | 606.2381 | 671.8691 | 744.7473 | 825.687 | 915.5979 | 1015.4838 | 1126.4608 | 1249.7694 | 1386.7879 | 1539.0466 | 1708.2443 | 1896.2641 | 2105.1918 | 2271.4993 | 2270.304 |  | 2464.4853 | 2722.6788 | 3008.7106 | 3325.6503 | 3676.9107 | 4066.2862 | 4497.9964 | 4976.7338 | 5507.7171 | 6096.7511 | 6750.2925 | 7475.524 | 8280.4365 | 9173.9202 | 10165.867 | 11267.2838 | 12490.4189 | 13842.5315 | 15338.9274 | 16998.0272 | 18836.765 | 20873.4399 | 23127.6394 | 25620.0562 | 28372.1437 | 31405.5317 | 34741.0882 | 38397.4653 | 41161.9613 | 40666.2576
| TRUE | 1588 | 22006152 | FB | FB018 | 11 | FB18 | OVERCURRENT | C | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 158.7269 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 429.7586 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.10194 |  | 2300.9817 | 6229.9868 | 46.5895 | 6183.3973 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2537.9351 | 2800.3783 | 3091.1182 | 3413.2746 | 3770.3166 | 4166.1011 | 4604.9171 | 5091.5344 | 5631.2575 | 6229.9868 | 6894.2853 | 7631.4539 | 8449.615 | 9357.8051 | 10366.0791 | 11485.6248 | 12728.8923 | 14109.7366 | 15643.5771 | 17347.5756 | 19240.8334 | 21344.6126 | 23682.5809 | 26281.0854 | 29169.4573 | 32380.3509 | 35950.1227 | 39919.2516 | 43085.6825 | 43085.6825 |  | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 38.7675 | 51.3886 | 68.7135 | 92.6024 | 125.6769 | 171.6381 | 235.7196 | 325.3322 | 450.984 | 627.591 | 876.3484 | 1227.4015 | 1723.6604 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 175.0725 | 193.1765 | 213.2324 | 235.4554 | 260.085 | 287.3871 | 317.6576 | 351.2256 | 388.4569 | 429.7586 | 475.5835 | 526.435 | 582.8736 | 645.5227 | 715.0757 | 792.3045 | 878.0679 | 973.3217 | 1079.1295 | 1196.6752 | 1327.2764 | 1472.3999 | 1633.6782 | 1812.929 | 2012.1754 | 2233.6702 | 2479.9211 | 2753.7207 | 2972.1483 | 2972.1483 |  | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.12202 | 0.16174 | 0.21627 | 0.29146 | 0.39556 | 0.54022 | 0.74191 | 1.024 | 1.4194 | 1.9753 | 2.7583 | 3.8632 | 5.4251 |  | 174.9706 | 193.0745 | 213.1304 | 235.3535 | 259.9831 | 287.2852 | 317.5557 | 351.1237 | 388.355 | 429.6567 | 475.4815 | 526.3331 | 582.7717 | 645.4207 | 714.9737 | 792.2026 | 877.966 | 973.1997 | 1078.9678 | 1196.4589 | 1326.9849 | 1472.0043 | 1633.138 | 1812.1871 | 2011.1515 | 2232.2507 | 2477.9458 | 2750.9624 | 2968.2851 | 2966.7232 |  | 2505.5585 | 2768.0017 | 3058.7416 | 3380.898 | 3737.94 | 4133.7245 | 4572.5405 | 5059.1578 | 5598.8809 | 6197.6102 | 6861.9087 | 7599.0773 | 8417.2384 | 9325.4285 | 10333.7025 | 11453.2482 | 12696.5157 | 14070.9838 | 15592.2081 | 17278.8882 | 19148.2662 | 21218.9834 | 23511.008 | 26045.4554 | 28844.2486 | 31929.5382 | 35322.77 | 39043.2359 | 41858.7471 | 41362.6767
| TRUE | 1589 | 22006150 | FB | FB018 | 11 | FB18 | OVERCURRENT | C | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 158.7269 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 429.7586 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.10194 |  | 2300.9817 | 6229.9868 | 46.5895 | 6183.3973 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2537.9351 | 2800.3783 | 3091.1182 | 3413.2746 | 3770.3166 | 4166.1011 | 4604.9171 | 5091.5344 | 5631.2575 | 6229.9868 | 6894.2853 | 7631.4539 | 8449.615 | 9357.8051 | 10366.0791 | 11485.6248 | 12728.8923 | 14109.7366 | 15643.5771 | 17347.5756 | 19240.8334 | 21344.6126 | 23682.5809 | 26281.0854 | 29169.4573 | 32380.3509 | 35950.1227 | 39919.2516 | 43085.6825 | 43085.6825 |  | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 38.7675 | 51.3886 | 68.7135 | 92.6024 | 125.6769 | 171.6381 | 235.7196 | 325.3322 | 450.984 | 627.591 | 876.3484 | 1227.4015 | 1723.6604 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 175.0725 | 193.1765 | 213.2324 | 235.4554 | 260.085 | 287.3871 | 317.6576 | 351.2256 | 388.4569 | 429.7586 | 475.5835 | 526.435 | 582.8736 | 645.5227 | 715.0757 | 792.3045 | 878.0679 | 973.3217 | 1079.1295 | 1196.6752 | 1327.2764 | 1472.3999 | 1633.6782 | 1812.929 | 2012.1754 | 2233.6702 | 2479.9211 | 2753.7207 | 2972.1483 | 2972.1483 |  | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.12202 | 0.16174 | 0.21627 | 0.29146 | 0.39556 | 0.54022 | 0.74191 | 1.024 | 1.4194 | 1.9753 | 2.7583 | 3.8632 | 5.4251 |  | 174.9706 | 193.0745 | 213.1304 | 235.3535 | 259.9831 | 287.2852 | 317.5557 | 351.1237 | 388.355 | 429.6567 | 475.4815 | 526.3331 | 582.7717 | 645.4207 | 714.9737 | 792.2026 | 877.966 | 973.1997 | 1078.9678 | 1196.4589 | 1326.9849 | 1472.0043 | 1633.138 | 1812.1871 | 2011.1515 | 2232.2507 | 2477.9458 | 2750.9624 | 2968.2851 | 2966.7232 |  | 2505.5585 | 2768.0017 | 3058.7416 | 3380.898 | 3737.94 | 4133.7245 | 4572.5405 | 5059.1578 | 5598.8809 | 6197.6102 | 6861.9087 | 7599.0773 | 8417.2384 | 9325.4285 | 10333.7025 | 11453.2482 | 12696.5157 | 14070.9838 | 15592.2081 | 17278.8882 | 19148.2662 | 21218.9834 | 23511.008 | 26045.4554 | 28844.2486 | 31929.5382 | 35322.77 | 39043.2359 | 41858.7471 | 41362.6767
| TRUE | 1590 | 22006151 | FB | FB018 | 11 | FB18 | OVERCURRENT | C | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 158.7269 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 429.7586 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.10194 |  | 2300.9817 | 6229.9868 | 46.5895 | 6183.3973 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2537.9351 | 2800.3783 | 3091.1182 | 3413.2746 | 3770.3166 | 4166.1011 | 4604.9171 | 5091.5344 | 5631.2575 | 6229.9868 | 6894.2853 | 7631.4539 | 8449.615 | 9357.8051 | 10366.0791 | 11485.6248 | 12728.8923 | 14109.7366 | 15643.5771 | 17347.5756 | 19240.8334 | 21344.6126 | 23682.5809 | 26281.0854 | 29169.4573 | 32380.3509 | 35950.1227 | 39919.2516 | 43085.6825 | 43085.6825 |  | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 38.7675 | 51.3886 | 68.7135 | 92.6024 | 125.6769 | 171.6381 | 235.7196 | 325.3322 | 450.984 | 627.591 | 876.3484 | 1227.4015 | 1723.6604 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 175.0725 | 193.1765 | 213.2324 | 235.4554 | 260.085 | 287.3871 | 317.6576 | 351.2256 | 388.4569 | 429.7586 | 475.5835 | 526.435 | 582.8736 | 645.5227 | 715.0757 | 792.3045 | 878.0679 | 973.3217 | 1079.1295 | 1196.6752 | 1327.2764 | 1472.3999 | 1633.6782 | 1812.929 | 2012.1754 | 2233.6702 | 2479.9211 | 2753.7207 | 2972.1483 | 2972.1483 |  | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.12202 | 0.16174 | 0.21627 | 0.29146 | 0.39556 | 0.54022 | 0.74191 | 1.024 | 1.4194 | 1.9753 | 2.7583 | 3.8632 | 5.4251 |  | 174.9706 | 193.0745 | 213.1304 | 235.3535 | 259.9831 | 287.2852 | 317.5557 | 351.1237 | 388.355 | 429.6567 | 475.4815 | 526.3331 | 582.7717 | 645.4207 | 714.9737 | 792.2026 | 877.966 | 973.1997 | 1078.9678 | 1196.4589 | 1326.9849 | 1472.0043 | 1633.138 | 1812.1871 | 2011.1515 | 2232.2507 | 2477.9458 | 2750.9624 | 2968.2851 | 2966.7232 |  | 2505.5585 | 2768.0017 | 3058.7416 | 3380.898 | 3737.94 | 4133.7245 | 4572.5405 | 5059.1578 | 5598.8809 | 6197.6102 | 6861.9087 | 7599.0773 | 8417.2384 | 9325.4285 | 10333.7025 | 11453.2482 | 12696.5157 | 14070.9838 | 15592.2081 | 17278.8882 | 19148.2662 | 21218.9834 | 23511.008 | 26045.4554 | 28844.2486 | 31929.5382 | 35322.77 | 39043.2359 | 41858.7471 | 41362.6767
| TRUE | 1591 | 22006153 | FB | FB019 | 11 | FB19 | SENSITIVE EF | Blank | English Electric | CMG_1328 | CMG 1328 | CMG | Electromechanical |  | 0.57434 | 2190 |  | 8.25 | 0.0054067 | 0.0038888 | 0.0015179 | 31.8755 | 1244.4067 | 1276.2822 | 37.4249 | 2.2021 | 97.5002 |  | 11.5885 | 0.013521 | 0.0097249 | 0.0037959 | 79.7129 | 3111.9605 | 3191.6734 | 93.5906 | 5.5069 | 243.8244 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.10194 |  | 1413.4094 | 3534.5954 | 46.5895 | 3488.0058 |  | 0.03398 |  | 8.5352 | 8.8302 | 9.1354 | 9.4511 | 9.7778 | 10.1158 | 10.4654 | 10.8271 | 11.2014 | 11.5885 | 11.9891 | 12.4035 | 12.8322 | 13.2757 | 13.7346 | 14.2093 | 14.7004 | 15.2085 | 15.7342 | 16.278 | 16.8407 | 17.4227 | 18.0249 | 18.6479 | 19.2925 | 19.9593 | 20.6492 | 21.3629 | 22.1013 | 22.8652 |  | 0.0059156 | 0.0064751 | 0.0070903 | 0.007767 | 0.0085115 | 0.0093307 | 0.010232 | 0.011225 | 0.012317 | 0.013521 | 0.014846 | 0.016306 | 0.017915 | 0.019688 | 0.021642 | 0.023795 | 0.02617 | 0.028788 | 0.031676 | 0.034861 | 0.038374 | 0.042249 | 0.046526 | 0.051245 | 0.056453 | 0.062201 | 0.068547 | 0.075552 | 0.083287 | 0.091827 |  | 0.0042548 | 0.0046572 | 0.0050997 | 0.0055865 | 0.0061219 | 0.0067111 | 0.0073596 | 0.0080734 | 0.0088594 | 0.0097249 | 0.010678 | 0.011728 | 0.012885 | 0.01416 | 0.015566 | 0.017115 | 0.018823 | 0.020706 | 0.022783 | 0.025074 | 0.0276 | 0.030388 | 0.033464 | 0.036858 | 0.040604 | 0.044739 | 0.049303 | 0.054341 | 0.059904 | 0.066047 | 1546.4496 | 1692.7124 | 1853.5494 | 2030.4526 | 2225.0694 | 2439.2187 | 2674.9093 | 2934.3594 | 3220.0194 | 3534.5954 | 3881.0771 | 4262.7672 | 4683.3148 | 5146.7517 | 5657.5329 | 6220.5816 | 6841.3387 | 7525.8172 | 8280.6635 | 9113.224 | 10031.6194 | 11044.8271 | 12162.7716 | 13396.4256 | 14757.9209 | 16260.6717 | 17919.5107 | 19750.84 | 21772.7981 | 24005.4441 |  | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 38.7675 | 51.3886 | 68.7135 | 92.6024 | 125.6769 | 171.6381 | 235.7196 | 325.3322 | 450.984 | 627.591 | 876.3484 | 1227.4015 | 1723.6604 |  | 34.8758 | 38.1744 | 41.8016 | 45.7912 | 50.1802 | 55.0097 | 60.3251 | 66.1763 | 72.6185 | 79.7129 | 87.5268 | 96.1348 | 105.619 | 116.0706 | 127.5898 | 140.2878 | 154.2872 | 169.7237 | 186.7472 | 205.5232 | 226.2351 | 249.0851 | 274.2972 | 302.1189 | 332.8236 | 366.7139 | 404.1244 | 445.4249 | 491.0245 | 541.3756 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 20.6629 | 23.9614 | 27.5887 | 31.5782 | 35.9673 | 40.7968 | 46.1121 | 51.9633 | 58.4056 | 65.5 | 73.3139 | 81.9218 | 91.4061 | 101.8576 | 113.3769 | 126.0749 | 140.0743 | 152.7117 | 164.1968 | 175.3703 | 185.5991 | 193.9354 | 198.9787 | 198.68 | 190.0608 | 168.8124 | 128.7239 | 60.8643 | -47.5858 | -215.0038 |  | 1361.5392 | 1490.3132 | 1631.9188 | 1787.6695 | 1959.0158 | 2147.5591 | 2355.0679 | 2583.4953 | 2834.9986 | 3111.9605 | 3417.0131 | 3753.0642 | 4123.3265 | 4531.3498 | 4981.0564 | 5476.7809 | 6023.3134 | 6625.9482 | 7290.5369 | 8023.5473 | 8832.1293 | 9724.1868 | 10708.4577 | 11794.6025 | 12993.3025 | 14316.368 | 15776.8581 | 17389.2136 | 19169.4043 | 21135.0908 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 1360.2381 | 1489.0121 | 1630.6177 | 1786.3684 | 1957.7147 | 2146.258 | 2353.7668 | 2582.1942 | 2833.6975 | 3110.6594 | 3415.712 | 3751.7631 | 4122.0254 | 4530.0487 | 4979.7553 | 5475.4798 | 6022.0123 | 6624.3909 | 7288.4725 | 8020.787 | 8828.4094 | 9719.1382 | 10701.5627 | 11785.1334 | 12980.2336 | 14298.2514 | 15751.647 | 17354.0097 | 19120.0981 | 21065.8493 |  | 1380.9009 | 1512.9735 | 1658.2063 | 1817.9466 | 1993.6819 | 2187.0548 | 2399.8789 | 2634.1576 | 2892.1031 | 3176.1593 | 3489.0258 | 3833.6849 | 4213.4315 | 4631.9063 | 5093.1322 | 5601.5546 | 6162.0866 | 6777.1026 | 7452.6693 | 8196.1573 | 9014.0085 | 9913.0736 | 10900.5415 | 11983.8134 | 13170.2943 | 14467.0638 | 15880.3709 | 17414.8739 | 19072.5122 | 20850.8454 |  | 40.9476 | 44.8204 | 49.0791 | 53.7633 | 58.9164 | 64.5868 | 70.8275 | 77.6973 | 85.2612 | 93.5906 | 102.7649 | 112.8715 | 124.007 | 136.2781 | 149.8028 | 164.7114 | 181.1481 | 199.2721 | 219.2592 | 241.3041 | 265.6218 | 292.45 | 322.0515 | 354.7167 | 390.767 | 430.5576 | 474.4811 | 522.9718 | 576.5102 | 635.6272 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 26.2547 | 30.1276 | 34.3863 | 39.0704 | 44.2235 | 49.8939 | 56.1346 | 63.0045 | 70.5683 | 78.8978 | 88.0721 | 98.1786 | 109.3141 | 121.5852 | 135.1099 | 150.0186 | 166.4552 | 181.6856 | 195.9474 | 210.133 | 223.6138 | 235.438 | 244.1897 | 247.7851 | 243.1836 | 225.9735 | 189.7812 | 125.4258 | 19.7127 | -146.2928 |  | 2.4094 | 2.6372 | 2.8878 | 3.1634 | 3.4667 | 3.8003 | 4.1675 | 4.5717 | 5.0168 | 5.5069 | 6.0467 | 6.6414 | 7.2966 | 8.0187 | 8.8144 | 9.6917 | 10.6588 | 11.7252 | 12.9013 | 14.1984 | 15.6293 | 17.2079 | 18.9496 | 20.8717 | 22.9929 | 25.3342 | 27.9186 | 30.7719 | 33.9221 | 37.4005 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.34164 | 0.56952 | 0.8201 | 1.0957 | 1.3989 | 1.7326 | 2.0998 | 2.504 | 2.9491 | 3.4392 | 3.979 | 4.5737 | 5.2289 | 5.9509 | 6.7467 | 7.6239 | 8.5911 | 9.2503 | 9.6206 | 9.8117 | 9.7175 | 9.1846 | 7.9921 | 5.8231 | 2.2234 | -3.457 | -12.1473 | -25.1749 | -44.4362 | -72.6393 |  | 106.6776 | 116.7671 | 127.862 | 140.0652 | 153.4903 | 168.2628 | 184.5213 | 202.4188 | 222.1243 | 243.8244 | 267.7255 | 294.0554 | 323.0657 | 355.0346 | 390.2695 | 429.1099 | 471.9311 | 519.148 | 571.219 | 628.6509 | 692.0039 | 761.8973 | 839.0156 | 924.1159 | 1018.0349 | 1121.6981 | 1236.1286 | 1362.4578 | 1501.9371 | 1655.9501 |  | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.12202 | 0.16174 | 0.21627 | 0.29146 | 0.39556 | 0.54022 | 0.74191 | 1.024 | 1.4194 | 1.9753 | 2.7583 | 3.8632 | 5.4251 |  | 106.5757 | 116.6652 | 127.7601 | 139.9633 | 153.3884 | 168.1609 | 184.4194 | 202.3168 | 222.0223 | 243.7225 | 267.6236 | 293.9534 | 322.9638 | 354.9327 | 390.1675 | 429.0079 | 471.8291 | 519.026 | 571.0572 | 628.4346 | 691.7124 | 761.5017 | 838.4754 | 923.374 | 1017.011 | 1120.2786 | 1234.1533 | 1359.6996 | 1498.0739 | 1650.525 |  | 1514.073 | 1660.3358 | 1821.1728 | 1998.076 | 2192.6928 | 2406.8421 | 2642.5327 | 2901.9829 | 3187.6428 | 3502.2188 | 3848.7005 | 4230.3906 | 4650.9383 | 5114.3751 | 5625.1563 | 6188.2051 | 6808.9621 | 7487.0645 | 8229.2945 | 9044.5366 | 9939.0522 | 10919.1979 | 11991.1986 | 13160.7956 | 14432.7122 | 15809.8589 | 17292.158 | 18874.8244 | 20545.8626 | 22282.4383
| TRUE | 1592 | 22006154 | FB | FB019 | 11 | FB19 | OVERCURRENT | Blank | ASEA | RACID_3245 | RACID 3245 | RACID | Electronic |  | 0.57434 | 2190 |  | 6.6 | 0.014726 | 0.010592 | 0.0041343 | 86.8187 | 3389.3699 | 3476.1886 | 101.9336 | 5.9978 | 265.5596 |  | 11.1153 | 0.058633 | 0.042172 | 0.016461 | 345.6775 | 13495.1158 | 13840.7933 | 405.8588 | 23.8809 | 1057.3524 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.10194 |  | 3849.6797 | 15327.8854 | 46.5895 | 15281.2959 |  | 0.052126 |  | 6.9532 | 7.3252 | 7.7172 | 8.1301 | 8.5651 | 9.0234 | 9.5062 | 10.0149 | 10.5508 | 11.1153 | 11.7101 | 12.3367 | 12.9968 | 13.6922 | 14.4249 | 15.1967 | 16.0099 | 16.8665 | 17.769 | 18.7198 | 19.7215 | 20.7767 | 21.8884 | 23.0596 | 24.2935 | 25.5934 | 26.9629 | 28 | 28 | 28 |  | 0.016829 | 0.019254 | 0.022055 | 0.02529 | 0.029029 | 0.033353 | 0.038356 | 0.044149 | 0.050858 | 0.058633 | 0.067647 | 0.078102 | 0.090233 | 0.10431 | 0.12066 | 0.13966 | 0.16172 | 0.18737 | 0.2172 | 0.25188 | 0.29223 | 0.33918 | 0.39382 | 0.45744 | 0.53152 | 0.61779 | 0.7183 | 0.80128 | 0.80128 | 0.80128 |  | 0.012104 | 0.013849 | 0.015863 | 0.01819 | 0.020879 | 0.023989 | 0.027588 | 0.031754 | 0.03658 | 0.042172 | 0.048656 | 0.056175 | 0.0649 | 0.075028 | 0.086788 | 0.10045 | 0.11632 | 0.13477 | 0.15622 | 0.18117 | 0.21019 | 0.24396 | 0.28326 | 0.32902 | 0.3823 | 0.44435 | 0.51664 | 0.57632 | 0.57632 | 0.57632 | 4399.3414 | 5033.4774 | 5765.5464 | 6611.1979 | 7588.6348 | 8719.0341 | 10027.04 | 11541.3376 | 13295.323 | 15327.8854 | 17684.3194 | 20417.3906 | 23588.5789 | 27269.5299 | 31543.7502 | 36508.5857 | 42277.5327 | 48982.936 | 56779.1401 | 65846.1697 | 76394.0278 | 88667.717 | 102953.1041 | 119583.771 | 138949.0189 | 161503.2179 | 187776.7313 | 209469.8784 | 209469.8784 | 209469.8784 |  | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 38.7675 | 51.3886 | 68.7135 | 92.6024 | 125.6769 | 171.6381 | 235.7196 | 325.3322 | 450.984 | 627.591 | 876.3484 | 1227.4015 | 1723.6604 |  | 99.2148 | 113.516 | 130.0257 | 149.0971 | 171.1404 | 196.6334 | 226.1318 | 260.2825 | 299.8388 | 345.6775 | 398.8203 | 460.4571 | 531.9743 | 614.9879 | 711.3809 | 823.3489 | 953.4513 | 1104.6729 | 1280.4945 | 1484.9759 | 1722.8533 | 1999.652 | 2321.8189 | 2696.877 | 3133.6059 | 3642.2527 | 4234.7782 | 4724.0064 | 4724.0064 | 4724.0064 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 85.0019 | 99.303 | 115.8128 | 134.8841 | 156.9275 | 182.4204 | 211.9189 | 246.0696 | 285.6258 | 331.4646 | 384.6073 | 446.2441 | 517.7614 | 600.7749 | 697.168 | 809.1359 | 939.2384 | 1087.6609 | 1257.944 | 1454.823 | 1682.2174 | 1944.5022 | 2246.5004 | 2593.4381 | 2990.8431 | 3444.3512 | 3959.3777 | 4339.4458 | 4185.3961 | 3967.627 |  | 3873.308 | 4431.6198 | 5076.1546 | 5820.6908 | 6681.2546 | 7676.4911 | 8828.0975 | 10161.3291 | 11705.5888 | 13495.1158 | 15569.7888 | 17976.0641 | 20768.0705 | 24008.8868 | 27772.0345 | 32143.22 | 37222.3686 | 43126.0006 | 49990.0053 | 57972.8817 | 67259.5225 | 78065.6353 | 90642.9052 | 105285.0278 | 122334.7549 | 142192.1272 | 165324.0921 | 184423.3694 | 184423.3694 | 184423.3694 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 3872.0069 | 4430.3187 | 5074.8535 | 5819.3897 | 6679.9535 | 7675.19 | 8826.7964 | 10160.028 | 11704.2877 | 13493.8147 | 15568.4877 | 17974.763 | 20766.7694 | 24007.5857 | 27770.7334 | 32141.9189 | 37221.0675 | 43124.4433 | 49987.941 | 57970.1214 | 67255.8026 | 78060.5867 | 90636.0103 | 105275.5587 | 122321.686 | 142174.0107 | 165298.881 | 184388.1654 | 184374.0632 | 184354.1279 |  | 3957.0088 | 4529.6218 | 5190.6663 | 5954.2738 | 6836.881 | 7857.6104 | 9038.7153 | 10406.0976 | 11989.9136 | 13825.2793 | 15953.095 | 18421.0072 | 21284.5308 | 24608.3606 | 28467.9014 | 32951.0549 | 38160.3059 | 44212.1042 | 51245.885 | 59424.9443 | 68938.02 | 80005.0889 | 92882.5107 | 107868.9968 | 125312.5291 | 145618.3618 | 169258.2587 | 188727.6112 | 188559.4592 | 188321.7548 |  | 116.4878 | 133.2787 | 152.6628 | 175.0543 | 200.9354 | 230.8666 | 265.5006 | 305.5969 | 352.0397 | 405.8588 | 468.2536 | 540.6211 | 624.5893 | 722.0552 | 835.23 | 966.6912 | 1119.444 | 1296.9928 | 1503.4242 | 1743.5052 | 2022.7963 | 2347.7847 | 2726.0397 | 3166.3942 | 3679.1562 | 4276.3566 | 4972.0388 | 5546.44 | 5546.44 | 5546.44 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 101.7949 | 118.5859 | 137.9699 | 160.3615 | 186.2425 | 216.1737 | 250.8077 | 290.904 | 337.3468 | 391.1659 | 453.5607 | 525.9282 | 609.8964 | 707.3623 | 820.5371 | 951.9983 | 1104.7511 | 1279.4063 | 1480.1124 | 1712.3341 | 1980.7882 | 2290.7727 | 2648.1779 | 3059.4625 | 3531.5727 | 4071.7726 | 4687.3389 | 5148.894 | 4989.6425 | 4764.52 |  | 6.8542 | 7.8422 | 8.9827 | 10.3003 | 11.8231 | 13.5843 | 15.6222 | 17.9814 | 20.7141 | 23.8809 | 27.5522 | 31.8103 | 36.7511 | 42.486 | 49.1452 | 56.8805 | 65.8685 | 76.3155 | 88.462 | 102.5885 | 119.0221 | 138.1445 | 160.4012 | 186.3118 | 216.4829 | 251.6224 | 292.5566 | 326.3545 | 326.3545 | 326.3545 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.7865 | 5.7744 | 6.915 | 8.2325 | 9.7554 | 11.5165 | 13.5544 | 15.9137 | 18.6464 | 21.8131 | 25.4845 | 29.7426 | 34.6833 | 40.4183 | 47.0775 | 54.8127 | 63.8008 | 73.8406 | 85.1813 | 98.2018 | 113.1103 | 130.1212 | 149.4437 | 171.2633 | 195.7134 | 222.8312 | 252.4907 | 270.4078 | 247.9963 | 216.3147 |  | 303.4766 | 347.2207 | 397.7205 | 456.0555 | 523.4813 | 601.4588 | 691.688 | 796.1477 | 917.1416 | 1057.3524 | 1219.9045 | 1408.438 | 1627.1938 | 1881.1141 | 2175.9596 | 2518.4452 | 2916.4003 | 3378.9542 | 3916.7541 | 4542.2184 | 5269.8336 | 6116.5006 | 7101.939 | 8249.1602 | 9585.019 | 11140.8589 | 12953.2656 | 14449.7082 | 14449.7082 | 14449.7082 |  | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.12202 | 0.16174 | 0.21627 | 0.29146 | 0.39556 | 0.54022 | 0.74191 | 1.024 | 1.4194 | 1.9753 | 2.7583 | 3.8632 | 5.4251 |  | 303.3746 | 347.1188 | 397.6185 | 455.9535 | 523.3793 | 601.3568 | 691.5861 | 796.0458 | 917.0397 | 1057.2504 | 1219.8026 | 1408.3361 | 1627.0918 | 1881.0122 | 2175.8576 | 2518.3433 | 2916.2983 | 3378.8322 | 3916.5924 | 4542.0021 | 5269.5422 | 6116.105 | 7101.3988 | 8248.4183 | 9583.9951 | 11139.4395 | 12951.2903 | 14446.9499 | 14445.845 | 14444.283 |  | 4366.9648 | 5001.1009 | 5733.1698 | 6578.8214 | 7556.2582 | 8686.6575 | 9994.6635 | 11508.9611 | 13262.9465 | 15295.5088 | 17651.9428 | 20385.014 | 23556.2023 | 27237.1533 | 31511.3736 | 36476.2091 | 42245.1561 | 48944.1833 | 56727.7711 | 65777.4823 | 76301.4606 | 88542.0878 | 102781.5311 | 119348.141 | 138623.8102 | 161052.4051 | 187149.3786 | 208593.8628 | 208242.943 | 207746.8725
| TRUE | 1593 | 22006118 | FB | FB002 | 11 | FB2 | PILOT WIRE | Blank | Metropolitan Vickers | HO2_971 | RI 009 | RI | Electromechanical |  | 0.57434 | 2190 |  | 6.6 | 0.003029 | 0.0021786 | 0.00085037 | 17.8577 | 697.1566 | 715.0143 | 20.9666 | 1.2337 | 32.0757 |  | 9.0234 | 0.0068603 | 0.0049343 | 0.001926 | 40.4454 | 1578.971 | 1619.4163 | 47.4868 | 2.7941 | 72.6474 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.059863 |  | 769.2903 | 1742.3446 | 46.5474 | 1695.7972 |  | 0.031275 |  | 6.8097 | 7.026 | 7.2492 | 7.4795 | 7.7172 | 7.9623 | 8.2153 | 8.4763 | 8.7456 | 9.0234 | 9.3101 | 9.6059 | 9.911 | 10.2259 | 10.5508 | 10.886 | 11.2318 | 11.5886 | 11.9568 | 12.3367 | 12.7286 | 13.133 | 13.5502 | 13.9807 | 14.4249 | 14.8831 | 15.356 | 15.8438 | 16.3472 | 16.8665 |  | 0.003281 | 0.0035556 | 0.0038548 | 0.0041809 | 0.0045364 | 0.0049241 | 0.0053468 | 0.005808 | 0.0063112 | 0.0068603 | 0.0074596 | 0.008114 | 0.0088284 | 0.0096087 | 0.010461 | 0.011392 | 0.012409 | 0.013521 | 0.014736 | 0.016065 | 0.017517 | 0.019105 | 0.020842 | 0.022741 | 0.024819 | 0.027092 | 0.02958 | 0.032301 | 0.03528 | 0.038541 |  | 0.0023599 | 0.0025574 | 0.0027726 | 0.0030072 | 0.0032628 | 0.0035416 | 0.0038457 | 0.0041774 | 0.0045393 | 0.0049343 | 0.0053654 | 0.005836 | 0.0063499 | 0.0069111 | 0.0075241 | 0.0081938 | 0.0089255 | 0.0097252 | 0.010599 | 0.011555 | 0.012599 | 0.013741 | 0.014991 | 0.016357 | 0.017851 | 0.019486 | 0.021275 | 0.023233 | 0.025375 | 0.02772 | 833.3061 | 903.0439 | 979.0335 | 1061.8548 | 1152.1424 | 1250.5913 | 1357.9625 | 1475.089 | 1602.8833 | 1742.3446 | 1894.5674 | 2060.7506 | 2242.2074 | 2440.3767 | 2656.835 | 2893.3094 | 3151.6928 | 3434.0595 | 3742.6828 | 4080.0541 | 4448.9045 | 4852.2276 | 5293.305 | 5775.7344 | 6303.4601 | 6880.8066 | 7512.5156 | 8203.7867 | 8960.3215 | 9788.3727 |  | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 38.7171 | 51.3218 | 68.6242 | 92.4821 | 125.5137 | 171.4152 | 235.4133 | 324.9096 | 450.3981 | 626.7756 | 875.2098 | 1225.8069 | 1721.421 |  | 19.3437 | 20.9625 | 22.7265 | 24.649 | 26.7449 | 29.0302 | 31.5226 | 34.2415 | 37.208 | 40.4454 | 43.9789 | 47.8366 | 52.0488 | 56.6489 | 61.6736 | 67.1629 | 73.1608 | 79.7154 | 86.8796 | 94.711 | 103.2732 | 112.6356 | 122.8744 | 134.0732 | 146.3233 | 159.7254 | 174.3894 | 190.436 | 207.9975 | 227.2192 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 5.1307 | 6.7496 | 8.5135 | 10.4361 | 12.5319 | 14.8173 | 17.3097 | 20.0286 | 22.9951 | 26.2324 | 29.766 | 33.6236 | 37.8358 | 42.436 | 47.4606 | 52.95 | 58.9479 | 62.7034 | 64.3291 | 64.5581 | 62.6373 | 57.4859 | 47.5559 | 30.6343 | 3.5605 | -38.1761 | -101.0111 | -194.1246 | -330.6128 | -529.1602 |  | 755.1699 | 818.3686 | 887.2329 | 962.2883 | 1044.11 | 1133.3277 | 1230.631 | 1336.775 | 1452.5865 | 1578.971 | 1716.9204 | 1867.5211 | 2031.9634 | 2211.551 | 2407.7127 | 2622.0137 | 2856.1694 | 3112.0596 | 3391.7443 | 3697.4815 | 4031.7461 | 4397.2509 | 4796.97 | 5234.1637 | 5712.4063 | 6235.617 | 6808.0929 | 7434.5459 | 8120.143 | 8870.5507 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 753.8688 | 817.0675 | 885.9318 | 960.9872 | 1042.8089 | 1132.0266 | 1229.3299 | 1335.4739 | 1451.2854 | 1577.6699 | 1715.6193 | 1866.22 | 2030.6623 | 2210.2499 | 2406.4116 | 2620.7126 | 2854.8683 | 3110.5022 | 3389.6799 | 3694.7212 | 4028.0261 | 4392.2023 | 4790.0751 | 5224.6946 | 5699.3374 | 6217.5005 | 6782.8818 | 7399.3419 | 8070.8368 | 8801.3092 |  | 758.9995 | 823.8171 | 894.4454 | 971.4233 | 1055.3408 | 1146.8438 | 1246.6396 | 1355.5025 | 1474.2804 | 1603.9023 | 1745.3853 | 1899.8436 | 2068.4981 | 2252.6859 | 2453.8722 | 2673.6626 | 2913.8162 | 3173.2057 | 3454.0091 | 3759.2792 | 4090.6634 | 4449.6882 | 4837.631 | 5255.3289 | 5702.8979 | 6179.3243 | 6681.8707 | 7205.2173 | 7740.2241 | 8272.149 |  | 22.7114 | 24.612 | 26.6831 | 28.9403 | 31.4011 | 34.0843 | 37.0106 | 40.2028 | 43.6858 | 47.4868 | 51.6355 | 56.1648 | 61.1103 | 66.5113 | 72.4107 | 78.8557 | 85.8979 | 93.5936 | 102.005 | 111.1999 | 121.2527 | 132.2451 | 144.2665 | 157.4148 | 171.7977 | 187.533 | 204.75 | 223.5902 | 244.2092 | 266.7773 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 8.0185 | 9.9192 | 11.9902 | 14.2475 | 16.7082 | 19.3914 | 22.3177 | 25.51 | 28.9929 | 32.7939 | 36.9426 | 41.4719 | 46.4174 | 51.8184 | 57.7179 | 64.1629 | 71.205 | 76.0072 | 78.6931 | 80.0288 | 79.2446 | 75.2331 | 66.4047 | 50.4832 | 24.2143 | -17.051 | -79.9499 | -173.9558 | -312.5883 | -515.1426 |  | 1.3363 | 1.4482 | 1.57 | 1.7029 | 1.8477 | 2.0055 | 2.1777 | 2.3655 | 2.5705 | 2.7941 | 3.0383 | 3.3048 | 3.5958 | 3.9135 | 4.2607 | 4.6399 | 5.0543 | 5.5071 | 6.002 | 6.543 | 7.1346 | 7.7813 | 8.4887 | 9.2623 | 10.1086 | 11.0345 | 12.0476 | 13.1561 | 14.3694 | 15.6973 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | -0.73139 | -0.61955 | -0.49769 | -0.36487 | -0.22008 | -0.062202 | 0.10999 | 0.29782 | 0.50276 | 0.72641 | 0.97052 | 1.237 | 1.528 | 1.8458 | 2.1929 | 2.5722 | 2.9865 | 3.0321 | 2.7213 | 2.1563 | 1.2227 | -0.24196 | -2.4688 | -5.7862 | -10.6608 | -17.7567 | -28.0183 | -42.7906 | -63.9889 | -94.3426 |  | 34.7449 | 37.6526 | 40.821 | 44.2742 | 48.0388 | 52.1437 | 56.6205 | 61.5041 | 66.8325 | 72.6474 | 78.9944 | 85.9234 | 93.4893 | 101.752 | 110.7773 | 120.6371 | 131.4105 | 143.1838 | 156.0519 | 170.1187 | 185.498 | 202.3146 | 220.7054 | 240.8204 | 262.824 | 286.8966 | 313.2358 | 342.0585 | 373.6024 | 408.1282 |  | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.071652 | 0.094979 | 0.127 | 0.17115 | 0.23228 | 0.31723 | 0.43567 | 0.6013 | 0.83353 | 1.1599 | 1.6197 | 2.2685 | 3.1858 |  | 34.685 | 37.5927 | 40.7611 | 44.2144 | 47.9789 | 52.0838 | 56.5607 | 61.4443 | 66.7727 | 72.5875 | 78.9345 | 85.8635 | 93.4294 | 101.6921 | 110.7174 | 120.5773 | 131.3506 | 143.1121 | 155.9569 | 169.9917 | 185.3268 | 202.0823 | 220.3882 | 240.3847 | 262.2227 | 286.0631 | 312.0759 | 340.4388 | 371.3339 | 404.9424 |  | 800.9716 | 870.7094 | 946.699 | 1029.5203 | 1119.8079 | 1218.2568 | 1325.628 | 1442.7545 | 1570.5488 | 1710.0101 | 1862.2329 | 2028.4161 | 2209.8729 | 2408.0422 | 2624.5005 | 2860.9749 | 3119.3583 | 3395.3572 | 3691.3805 | 4011.456 | 4356.4576 | 4726.7617 | 5121.9551 | 5540.4106 | 5978.6741 | 6430.5797 | 6885.9783 | 7328.9097 | 7734.9807 | 8067.6062
| TRUE | 1594 | 22006120 | FB | FB002 | 11 | FB2 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 93.2081 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 252.364 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.059863 |  | 2235.4629 | 6052.5922 | 46.5474 | 6006.0447 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2465.6691 | 2720.6395 | 3003.1007 | 3316.084 | 3662.9594 | 4047.4742 | 4473.7953 | 4946.5564 | 5470.9113 | 6052.5922 | 6697.9752 | 7414.1535 | 8209.018 | 9091.348 | 10070.9121 | 11158.5795 | 12366.4458 | 13707.9715 | 15198.137 | 16853.6153 | 18692.9639 | 20736.8394 | 23008.2357 | 25532.7496 | 28338.877 | 31458.3427 | 34926.4676 | 38782.5782 | 41858.8473 | 41858.8473 |  | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 38.7171 | 51.3218 | 68.6242 | 92.4821 | 125.5137 | 171.4152 | 235.4133 | 324.9096 | 450.3981 | 626.7756 | 875.2098 | 1225.8069 | 1721.421 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 102.8066 | 113.4376 | 125.2149 | 138.2648 | 152.7278 | 168.7602 | 186.5358 | 206.2477 | 228.1107 | 252.364 | 279.2734 | 309.1346 | 342.2766 | 379.0656 | 419.9087 | 465.2592 | 515.6214 | 571.5566 | 633.6894 | 702.7149 | 779.4069 | 864.6267 | 959.333 | 1064.5931 | 1181.5952 | 1311.6619 | 1456.2661 | 1617.0474 | 1745.313 | 1745.313 |  | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.071652 | 0.094979 | 0.127 | 0.17115 | 0.23228 | 0.31723 | 0.43567 | 0.6013 | 0.83353 | 1.1599 | 1.6197 | 2.2685 | 3.1858 |  | 102.7467 | 113.3777 | 125.155 | 138.2049 | 152.668 | 168.7004 | 186.4759 | 206.1878 | 228.0509 | 252.3042 | 279.2136 | 309.0748 | 342.2168 | 379.0057 | 419.8488 | 465.1993 | 515.5616 | 571.485 | 633.5944 | 702.5879 | 779.2357 | 864.3944 | 959.0158 | 1064.1574 | 1180.9939 | 1310.8284 | 1455.1061 | 1615.4277 | 1743.0445 | 1742.1273 |  | 2433.3346 | 2688.305 | 2970.7662 | 3283.7495 | 3630.6249 | 4015.1397 | 4441.4608 | 4914.2219 | 5438.5768 | 6020.2577 | 6665.6407 | 7381.819 | 8176.6835 | 9059.0135 | 10038.5776 | 11126.245 | 12334.1113 | 13669.2691 | 15146.8347 | 16785.0171 | 18600.517 | 20611.3735 | 22836.8857 | 25297.4257 | 28014.0909 | 31008.1158 | 34299.9303 | 37907.7012 | 40633.5065 | 40138.0808
| TRUE | 1595 | 22006121 | FB | FB002 | 11 | FB2 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 93.2081 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 252.364 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.059863 |  | 2235.4629 | 6052.5922 | 46.5474 | 6006.0447 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2465.6691 | 2720.6395 | 3003.1007 | 3316.084 | 3662.9594 | 4047.4742 | 4473.7953 | 4946.5564 | 5470.9113 | 6052.5922 | 6697.9752 | 7414.1535 | 8209.018 | 9091.348 | 10070.9121 | 11158.5795 | 12366.4458 | 13707.9715 | 15198.137 | 16853.6153 | 18692.9639 | 20736.8394 | 23008.2357 | 25532.7496 | 28338.877 | 31458.3427 | 34926.4676 | 38782.5782 | 41858.8473 | 41858.8473 |  | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 38.7171 | 51.3218 | 68.6242 | 92.4821 | 125.5137 | 171.4152 | 235.4133 | 324.9096 | 450.3981 | 626.7756 | 875.2098 | 1225.8069 | 1721.421 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 102.8066 | 113.4376 | 125.2149 | 138.2648 | 152.7278 | 168.7602 | 186.5358 | 206.2477 | 228.1107 | 252.364 | 279.2734 | 309.1346 | 342.2766 | 379.0656 | 419.9087 | 465.2592 | 515.6214 | 571.5566 | 633.6894 | 702.7149 | 779.4069 | 864.6267 | 959.333 | 1064.5931 | 1181.5952 | 1311.6619 | 1456.2661 | 1617.0474 | 1745.313 | 1745.313 |  | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.071652 | 0.094979 | 0.127 | 0.17115 | 0.23228 | 0.31723 | 0.43567 | 0.6013 | 0.83353 | 1.1599 | 1.6197 | 2.2685 | 3.1858 |  | 102.7467 | 113.3777 | 125.155 | 138.2049 | 152.668 | 168.7004 | 186.4759 | 206.1878 | 228.0509 | 252.3042 | 279.2136 | 309.0748 | 342.2168 | 379.0057 | 419.8488 | 465.1993 | 515.5616 | 571.485 | 633.5944 | 702.5879 | 779.2357 | 864.3944 | 959.0158 | 1064.1574 | 1180.9939 | 1310.8284 | 1455.1061 | 1615.4277 | 1743.0445 | 1742.1273 |  | 2433.3346 | 2688.305 | 2970.7662 | 3283.7495 | 3630.6249 | 4015.1397 | 4441.4608 | 4914.2219 | 5438.5768 | 6020.2577 | 6665.6407 | 7381.819 | 8176.6835 | 9059.0135 | 10038.5776 | 11126.245 | 12334.1113 | 13669.2691 | 15146.8347 | 16785.0171 | 18600.517 | 20611.3735 | 22836.8857 | 25297.4257 | 28014.0909 | 31008.1158 | 34299.9303 | 37907.7012 | 40633.5065 | 40138.0808
| TRUE | 1596 | 22006119 | FB | FB002 | 11 | FB2 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 93.2081 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 252.364 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.059863 |  | 2235.4629 | 6052.5922 | 46.5474 | 6006.0447 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2465.6691 | 2720.6395 | 3003.1007 | 3316.084 | 3662.9594 | 4047.4742 | 4473.7953 | 4946.5564 | 5470.9113 | 6052.5922 | 6697.9752 | 7414.1535 | 8209.018 | 9091.348 | 10070.9121 | 11158.5795 | 12366.4458 | 13707.9715 | 15198.137 | 16853.6153 | 18692.9639 | 20736.8394 | 23008.2357 | 25532.7496 | 28338.877 | 31458.3427 | 34926.4676 | 38782.5782 | 41858.8473 | 41858.8473 |  | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 38.7171 | 51.3218 | 68.6242 | 92.4821 | 125.5137 | 171.4152 | 235.4133 | 324.9096 | 450.3981 | 626.7756 | 875.2098 | 1225.8069 | 1721.421 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 102.8066 | 113.4376 | 125.2149 | 138.2648 | 152.7278 | 168.7602 | 186.5358 | 206.2477 | 228.1107 | 252.364 | 279.2734 | 309.1346 | 342.2766 | 379.0656 | 419.9087 | 465.2592 | 515.6214 | 571.5566 | 633.6894 | 702.7149 | 779.4069 | 864.6267 | 959.333 | 1064.5931 | 1181.5952 | 1311.6619 | 1456.2661 | 1617.0474 | 1745.313 | 1745.313 |  | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.071652 | 0.094979 | 0.127 | 0.17115 | 0.23228 | 0.31723 | 0.43567 | 0.6013 | 0.83353 | 1.1599 | 1.6197 | 2.2685 | 3.1858 |  | 102.7467 | 113.3777 | 125.155 | 138.2049 | 152.668 | 168.7004 | 186.4759 | 206.1878 | 228.0509 | 252.3042 | 279.2136 | 309.0748 | 342.2168 | 379.0057 | 419.8488 | 465.1993 | 515.5616 | 571.485 | 633.5944 | 702.5879 | 779.2357 | 864.3944 | 959.0158 | 1064.1574 | 1180.9939 | 1310.8284 | 1455.1061 | 1615.4277 | 1743.0445 | 1742.1273 |  | 2433.3346 | 2688.305 | 2970.7662 | 3283.7495 | 3630.6249 | 4015.1397 | 4441.4608 | 4914.2219 | 5438.5768 | 6020.2577 | 6665.6407 | 7381.819 | 8176.6835 | 9059.0135 | 10038.5776 | 11126.245 | 12334.1113 | 13669.2691 | 15146.8347 | 16785.0171 | 18600.517 | 20611.3735 | 22836.8857 | 25297.4257 | 28014.0909 | 31008.1158 | 34299.9303 | 37907.7012 | 40633.5065 | 40138.0808
| TRUE | 1597 | 22006155 | FB | FB020 | 11 | FB20 | SENSITIVE EF | Blank | English Electric | CMG_1328 | CMG 1328 | CMG | Electromechanical |  | 0.57434 | 2190 |  | 8.25 | 0.0054067 | 0.0038888 | 0.0015179 | 31.8755 | 1244.4067 | 1276.2822 | 37.4249 | 2.2021 | 97.5002 |  | 11.5885 | 0.013521 | 0.0097249 | 0.0037959 | 79.7129 | 3111.9605 | 3191.6734 | 93.5906 | 5.5069 | 243.8244 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.10194 |  | 1413.4094 | 3534.5954 | 46.5895 | 3488.0058 |  | 0.03398 |  | 8.5352 | 8.8302 | 9.1354 | 9.4511 | 9.7778 | 10.1158 | 10.4654 | 10.8271 | 11.2014 | 11.5885 | 11.9891 | 12.4035 | 12.8322 | 13.2757 | 13.7346 | 14.2093 | 14.7004 | 15.2085 | 15.7342 | 16.278 | 16.8407 | 17.4227 | 18.0249 | 18.6479 | 19.2925 | 19.9593 | 20.6492 | 21.3629 | 22.1013 | 22.8652 |  | 0.0059156 | 0.0064751 | 0.0070903 | 0.007767 | 0.0085115 | 0.0093307 | 0.010232 | 0.011225 | 0.012317 | 0.013521 | 0.014846 | 0.016306 | 0.017915 | 0.019688 | 0.021642 | 0.023795 | 0.02617 | 0.028788 | 0.031676 | 0.034861 | 0.038374 | 0.042249 | 0.046526 | 0.051245 | 0.056453 | 0.062201 | 0.068547 | 0.075552 | 0.083287 | 0.091827 |  | 0.0042548 | 0.0046572 | 0.0050997 | 0.0055865 | 0.0061219 | 0.0067111 | 0.0073596 | 0.0080734 | 0.0088594 | 0.0097249 | 0.010678 | 0.011728 | 0.012885 | 0.01416 | 0.015566 | 0.017115 | 0.018823 | 0.020706 | 0.022783 | 0.025074 | 0.0276 | 0.030388 | 0.033464 | 0.036858 | 0.040604 | 0.044739 | 0.049303 | 0.054341 | 0.059904 | 0.066047 | 1546.4496 | 1692.7124 | 1853.5494 | 2030.4526 | 2225.0694 | 2439.2187 | 2674.9093 | 2934.3594 | 3220.0194 | 3534.5954 | 3881.0771 | 4262.7672 | 4683.3148 | 5146.7517 | 5657.5329 | 6220.5816 | 6841.3387 | 7525.8172 | 8280.6635 | 9113.224 | 10031.6194 | 11044.8271 | 12162.7716 | 13396.4256 | 14757.9209 | 16260.6717 | 17919.5107 | 19750.84 | 21772.7981 | 24005.4441 |  | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 38.7675 | 51.3886 | 68.7135 | 92.6024 | 125.6769 | 171.6381 | 235.7196 | 325.3322 | 450.984 | 627.591 | 876.3484 | 1227.4015 | 1723.6604 |  | 34.8758 | 38.1744 | 41.8016 | 45.7912 | 50.1802 | 55.0097 | 60.3251 | 66.1763 | 72.6185 | 79.7129 | 87.5268 | 96.1348 | 105.619 | 116.0706 | 127.5898 | 140.2878 | 154.2872 | 169.7237 | 186.7472 | 205.5232 | 226.2351 | 249.0851 | 274.2972 | 302.1189 | 332.8236 | 366.7139 | 404.1244 | 445.4249 | 491.0245 | 541.3756 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 20.6629 | 23.9614 | 27.5887 | 31.5782 | 35.9673 | 40.7968 | 46.1121 | 51.9633 | 58.4056 | 65.5 | 73.3139 | 81.9218 | 91.4061 | 101.8576 | 113.3769 | 126.0749 | 140.0743 | 152.7117 | 164.1968 | 175.3703 | 185.5991 | 193.9354 | 198.9787 | 198.68 | 190.0608 | 168.8124 | 128.7239 | 60.8643 | -47.5858 | -215.0038 |  | 1361.5392 | 1490.3132 | 1631.9188 | 1787.6695 | 1959.0158 | 2147.5591 | 2355.0679 | 2583.4953 | 2834.9986 | 3111.9605 | 3417.0131 | 3753.0642 | 4123.3265 | 4531.3498 | 4981.0564 | 5476.7809 | 6023.3134 | 6625.9482 | 7290.5369 | 8023.5473 | 8832.1293 | 9724.1868 | 10708.4577 | 11794.6025 | 12993.3025 | 14316.368 | 15776.8581 | 17389.2136 | 19169.4043 | 21135.0908 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 1360.2381 | 1489.0121 | 1630.6177 | 1786.3684 | 1957.7147 | 2146.258 | 2353.7668 | 2582.1942 | 2833.6975 | 3110.6594 | 3415.712 | 3751.7631 | 4122.0254 | 4530.0487 | 4979.7553 | 5475.4798 | 6022.0123 | 6624.3909 | 7288.4725 | 8020.787 | 8828.4094 | 9719.1382 | 10701.5627 | 11785.1334 | 12980.2336 | 14298.2514 | 15751.647 | 17354.0097 | 19120.0981 | 21065.8493 |  | 1380.9009 | 1512.9735 | 1658.2063 | 1817.9466 | 1993.6819 | 2187.0548 | 2399.8789 | 2634.1576 | 2892.1031 | 3176.1593 | 3489.0258 | 3833.6849 | 4213.4315 | 4631.9063 | 5093.1322 | 5601.5546 | 6162.0866 | 6777.1026 | 7452.6693 | 8196.1573 | 9014.0085 | 9913.0736 | 10900.5415 | 11983.8134 | 13170.2943 | 14467.0638 | 15880.3709 | 17414.8739 | 19072.5122 | 20850.8454 |  | 40.9476 | 44.8204 | 49.0791 | 53.7633 | 58.9164 | 64.5868 | 70.8275 | 77.6973 | 85.2612 | 93.5906 | 102.7649 | 112.8715 | 124.007 | 136.2781 | 149.8028 | 164.7114 | 181.1481 | 199.2721 | 219.2592 | 241.3041 | 265.6218 | 292.45 | 322.0515 | 354.7167 | 390.767 | 430.5576 | 474.4811 | 522.9718 | 576.5102 | 635.6272 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 26.2547 | 30.1276 | 34.3863 | 39.0704 | 44.2235 | 49.8939 | 56.1346 | 63.0045 | 70.5683 | 78.8978 | 88.0721 | 98.1786 | 109.3141 | 121.5852 | 135.1099 | 150.0186 | 166.4552 | 181.6856 | 195.9474 | 210.133 | 223.6138 | 235.438 | 244.1897 | 247.7851 | 243.1836 | 225.9735 | 189.7812 | 125.4258 | 19.7127 | -146.2928 |  | 2.4094 | 2.6372 | 2.8878 | 3.1634 | 3.4667 | 3.8003 | 4.1675 | 4.5717 | 5.0168 | 5.5069 | 6.0467 | 6.6414 | 7.2966 | 8.0187 | 8.8144 | 9.6917 | 10.6588 | 11.7252 | 12.9013 | 14.1984 | 15.6293 | 17.2079 | 18.9496 | 20.8717 | 22.9929 | 25.3342 | 27.9186 | 30.7719 | 33.9221 | 37.4005 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.34164 | 0.56952 | 0.8201 | 1.0957 | 1.3989 | 1.7326 | 2.0998 | 2.504 | 2.9491 | 3.4392 | 3.979 | 4.5737 | 5.2289 | 5.9509 | 6.7467 | 7.6239 | 8.5911 | 9.2503 | 9.6206 | 9.8117 | 9.7175 | 9.1846 | 7.9921 | 5.8231 | 2.2234 | -3.457 | -12.1473 | -25.1749 | -44.4362 | -72.6393 |  | 106.6776 | 116.7671 | 127.862 | 140.0652 | 153.4903 | 168.2628 | 184.5213 | 202.4188 | 222.1243 | 243.8244 | 267.7255 | 294.0554 | 323.0657 | 355.0346 | 390.2695 | 429.1099 | 471.9311 | 519.148 | 571.219 | 628.6509 | 692.0039 | 761.8973 | 839.0156 | 924.1159 | 1018.0349 | 1121.6981 | 1236.1286 | 1362.4578 | 1501.9371 | 1655.9501 |  | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.12202 | 0.16174 | 0.21627 | 0.29146 | 0.39556 | 0.54022 | 0.74191 | 1.024 | 1.4194 | 1.9753 | 2.7583 | 3.8632 | 5.4251 |  | 106.5757 | 116.6652 | 127.7601 | 139.9633 | 153.3884 | 168.1609 | 184.4194 | 202.3168 | 222.0223 | 243.7225 | 267.6236 | 293.9534 | 322.9638 | 354.9327 | 390.1675 | 429.0079 | 471.8291 | 519.026 | 571.0572 | 628.4346 | 691.7124 | 761.5017 | 838.4754 | 923.374 | 1017.011 | 1120.2786 | 1234.1533 | 1359.6996 | 1498.0739 | 1650.525 |  | 1514.073 | 1660.3358 | 1821.1728 | 1998.076 | 2192.6928 | 2406.8421 | 2642.5327 | 2901.9829 | 3187.6428 | 3502.2188 | 3848.7005 | 4230.3906 | 4650.9383 | 5114.3751 | 5625.1563 | 6188.2051 | 6808.9621 | 7487.0645 | 8229.2945 | 9044.5366 | 9939.0522 | 10919.1979 | 11991.1986 | 13160.7956 | 14432.7122 | 15809.8589 | 17292.158 | 18874.8244 | 20545.8626 | 22282.4383
| TRUE | 1598 | 22006156 | FB | FB020 | 11 | FB20 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 158.7269 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 429.7586 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.10194 |  | 2300.9817 | 6229.9868 | 46.5895 | 6183.3973 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2537.9351 | 2800.3783 | 3091.1182 | 3413.2746 | 3770.3166 | 4166.1011 | 4604.9171 | 5091.5344 | 5631.2575 | 6229.9868 | 6894.2853 | 7631.4539 | 8449.615 | 9357.8051 | 10366.0791 | 11485.6248 | 12728.8923 | 14109.7366 | 15643.5771 | 17347.5756 | 19240.8334 | 21344.6126 | 23682.5809 | 26281.0854 | 29169.4573 | 32380.3509 | 35950.1227 | 39919.2516 | 43085.6825 | 43085.6825 |  | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 38.7675 | 51.3886 | 68.7135 | 92.6024 | 125.6769 | 171.6381 | 235.7196 | 325.3322 | 450.984 | 627.591 | 876.3484 | 1227.4015 | 1723.6604 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 175.0725 | 193.1765 | 213.2324 | 235.4554 | 260.085 | 287.3871 | 317.6576 | 351.2256 | 388.4569 | 429.7586 | 475.5835 | 526.435 | 582.8736 | 645.5227 | 715.0757 | 792.3045 | 878.0679 | 973.3217 | 1079.1295 | 1196.6752 | 1327.2764 | 1472.3999 | 1633.6782 | 1812.929 | 2012.1754 | 2233.6702 | 2479.9211 | 2753.7207 | 2972.1483 | 2972.1483 |  | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.12202 | 0.16174 | 0.21627 | 0.29146 | 0.39556 | 0.54022 | 0.74191 | 1.024 | 1.4194 | 1.9753 | 2.7583 | 3.8632 | 5.4251 |  | 174.9706 | 193.0745 | 213.1304 | 235.3535 | 259.9831 | 287.2852 | 317.5557 | 351.1237 | 388.355 | 429.6567 | 475.4815 | 526.3331 | 582.7717 | 645.4207 | 714.9737 | 792.2026 | 877.966 | 973.1997 | 1078.9678 | 1196.4589 | 1326.9849 | 1472.0043 | 1633.138 | 1812.1871 | 2011.1515 | 2232.2507 | 2477.9458 | 2750.9624 | 2968.2851 | 2966.7232 |  | 2505.5585 | 2768.0017 | 3058.7416 | 3380.898 | 3737.94 | 4133.7245 | 4572.5405 | 5059.1578 | 5598.8809 | 6197.6102 | 6861.9087 | 7599.0773 | 8417.2384 | 9325.4285 | 10333.7025 | 11453.2482 | 12696.5157 | 14070.9838 | 15592.2081 | 17278.8882 | 19148.2662 | 21218.9834 | 23511.008 | 26045.4554 | 28844.2486 | 31929.5382 | 35322.77 | 39043.2359 | 41858.7471 | 41362.6767
| TRUE | 1599 | 22006157 | FB | FB020 | 11 | FB20 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 158.7269 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 429.7586 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.10194 |  | 2300.9817 | 6229.9868 | 46.5895 | 6183.3973 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2537.9351 | 2800.3783 | 3091.1182 | 3413.2746 | 3770.3166 | 4166.1011 | 4604.9171 | 5091.5344 | 5631.2575 | 6229.9868 | 6894.2853 | 7631.4539 | 8449.615 | 9357.8051 | 10366.0791 | 11485.6248 | 12728.8923 | 14109.7366 | 15643.5771 | 17347.5756 | 19240.8334 | 21344.6126 | 23682.5809 | 26281.0854 | 29169.4573 | 32380.3509 | 35950.1227 | 39919.2516 | 43085.6825 | 43085.6825 |  | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 38.7675 | 51.3886 | 68.7135 | 92.6024 | 125.6769 | 171.6381 | 235.7196 | 325.3322 | 450.984 | 627.591 | 876.3484 | 1227.4015 | 1723.6604 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 175.0725 | 193.1765 | 213.2324 | 235.4554 | 260.085 | 287.3871 | 317.6576 | 351.2256 | 388.4569 | 429.7586 | 475.5835 | 526.435 | 582.8736 | 645.5227 | 715.0757 | 792.3045 | 878.0679 | 973.3217 | 1079.1295 | 1196.6752 | 1327.2764 | 1472.3999 | 1633.6782 | 1812.929 | 2012.1754 | 2233.6702 | 2479.9211 | 2753.7207 | 2972.1483 | 2972.1483 |  | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.12202 | 0.16174 | 0.21627 | 0.29146 | 0.39556 | 0.54022 | 0.74191 | 1.024 | 1.4194 | 1.9753 | 2.7583 | 3.8632 | 5.4251 |  | 174.9706 | 193.0745 | 213.1304 | 235.3535 | 259.9831 | 287.2852 | 317.5557 | 351.1237 | 388.355 | 429.6567 | 475.4815 | 526.3331 | 582.7717 | 645.4207 | 714.9737 | 792.2026 | 877.966 | 973.1997 | 1078.9678 | 1196.4589 | 1326.9849 | 1472.0043 | 1633.138 | 1812.1871 | 2011.1515 | 2232.2507 | 2477.9458 | 2750.9624 | 2968.2851 | 2966.7232 |  | 2505.5585 | 2768.0017 | 3058.7416 | 3380.898 | 3737.94 | 4133.7245 | 4572.5405 | 5059.1578 | 5598.8809 | 6197.6102 | 6861.9087 | 7599.0773 | 8417.2384 | 9325.4285 | 10333.7025 | 11453.2482 | 12696.5157 | 14070.9838 | 15592.2081 | 17278.8882 | 19148.2662 | 21218.9834 | 23511.008 | 26045.4554 | 28844.2486 | 31929.5382 | 35322.77 | 39043.2359 | 41858.7471 | 41362.6767
| TRUE | 1600 | 22006158 | FB | FB022 | 11 | FB22 | SENSITIVE EF | Blank | English Electric | CMG_1328 | CMG 1328 | CMG | Electromechanical |  | 0.81881 | 2190 |  | 8.25 | 0.0054067 | 0.0043154 | 0.0010912 | 32.1101 | 1380.9353 | 1413.0455 | 39.8471 | 2.2064 | 54.0987 |  | 11.5885 | 0.013521 | 0.010792 | 0.0027289 | 80.2997 | 3453.3856 | 3533.6853 | 99.648 | 5.5176 | 135.2877 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 28.4268 | 1.8549 | 30.2818 | 14.7027 | 2.0677 | 0.072668 |  | 1509.1976 | 3774.1385 | 47.1249 | 3727.0136 |  | 0.03398 |  | 8.5352 | 8.8302 | 9.1354 | 9.4511 | 9.7778 | 10.1158 | 10.4654 | 10.8271 | 11.2014 | 11.5885 | 11.9891 | 12.4035 | 12.8322 | 13.2757 | 13.7346 | 14.2093 | 14.7004 | 15.2085 | 15.7342 | 16.278 | 16.8407 | 17.4227 | 18.0249 | 18.6479 | 19.2925 | 19.9593 | 20.6492 | 21.3629 | 22.1013 | 22.8652 |  | 0.0059156 | 0.0064751 | 0.0070903 | 0.007767 | 0.0085115 | 0.0093307 | 0.010232 | 0.011225 | 0.012317 | 0.013521 | 0.014846 | 0.016306 | 0.017915 | 0.019688 | 0.021642 | 0.023795 | 0.02617 | 0.028788 | 0.031676 | 0.034861 | 0.038374 | 0.042249 | 0.046526 | 0.051245 | 0.056453 | 0.062201 | 0.068547 | 0.075552 | 0.083287 | 0.091827 |  | 0.0047216 | 0.0051682 | 0.0056593 | 0.0061994 | 0.0067936 | 0.0074474 | 0.008167 | 0.0089592 | 0.0098314 | 0.010792 | 0.01185 | 0.013015 | 0.014299 | 0.015714 | 0.017274 | 0.018993 | 0.020888 | 0.022978 | 0.025283 | 0.027825 | 0.030629 | 0.033722 | 0.037135 | 0.040902 | 0.045059 | 0.049647 | 0.054712 | 0.060303 | 0.066477 | 0.073293 | 1651.2541 | 1807.4293 | 1979.1664 | 2168.0585 | 2375.8646 | 2604.5271 | 2856.1906 | 3133.224 | 3438.2434 | 3774.1385 | 4144.1017 | 4551.6594 | 5000.7079 | 5495.5524 | 6040.9497 | 6642.1569 | 7304.9833 | 8035.8496 | 8841.8526 | 9730.8366 | 10711.4726 | 11793.3464 | 12987.0552 | 14304.3152 | 15758.0805 | 17362.6742 | 19133.9344 | 21089.3748 | 23248.363 | 25632.3178 |  | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 39.4139 | 52.2455 | 69.8593 | 94.1466 | 127.7727 | 174.5004 | 239.6504 | 330.7574 | 458.5045 | 638.0566 | 890.9622 | 1247.8694 | 1752.4038 |  | 35.1326 | 38.4554 | 42.1093 | 46.1283 | 50.5496 | 55.4147 | 60.7692 | 66.6634 | 73.1531 | 80.2997 | 88.1712 | 96.8425 | 106.3966 | 116.925 | 128.5291 | 141.3206 | 155.4231 | 170.9732 | 188.122 | 207.0362 | 227.9006 | 250.9188 | 276.3165 | 304.343 | 335.2737 | 369.4135 | 407.0994 | 448.704 | 494.6393 | 545.361 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 20.9192 | 24.242 | 27.8959 | 31.9149 | 36.3362 | 41.2013 | 46.5558 | 52.45 | 58.9397 | 66.0863 | 73.9578 | 82.6291 | 92.1832 | 102.7116 | 114.3157 | 127.1071 | 141.2096 | 153.9606 | 165.5708 | 176.8823 | 187.2633 | 195.7672 | 200.9955 | 200.9007 | 192.5061 | 171.5054 | 131.6897 | 64.1305 | -43.9891 | -211.0437 |  | 1510.9188 | 1653.8212 | 1810.9628 | 1983.8016 | 2173.9469 | 2383.176 | 2613.4514 | 2866.9405 | 3146.0372 | 3453.3856 | 3791.9066 | 4164.8272 | 4575.7124 | 5028.5015 | 5527.5472 | 6077.6595 | 6684.1542 | 7352.9064 | 8090.4096 | 8903.8414 | 9801.136 | 10791.0645 | 11883.3235 | 13088.6335 | 14418.8475 | 15887.0715 | 17507.7975 | 19297.0508 | 21272.5529 | 23453.9024 |  | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 2.2202 | 2.9431 | 3.9353 | 5.3034 | 7.1976 | 9.8298 | 13.4998 | 18.632 | 25.8281 | 35.9425 | 50.189 | 70.294 | 98.7151 |  | 1509.0639 | 1651.9662 | 1809.1079 | 1981.9466 | 2172.0919 | 2381.321 | 2611.5965 | 2865.0856 | 3144.1822 | 3451.5306 | 3790.0517 | 4162.9723 | 4573.8575 | 5026.6466 | 5525.6922 | 6075.8045 | 6682.2992 | 7350.6861 | 8087.4665 | 8899.9061 | 9795.8326 | 10783.8669 | 11873.4937 | 13075.1337 | 14400.2155 | 15861.2434 | 17471.855 | 19246.8618 | 21202.2589 | 23355.1873 |  | 1529.9831 | 1676.2082 | 1837.0038 | 2013.8615 | 2208.4281 | 2422.5223 | 2658.1522 | 2917.5356 | 3203.1219 | 3517.6169 | 3864.0094 | 4245.6013 | 4666.0407 | 5129.3582 | 5640.0079 | 6202.9117 | 6823.5089 | 7504.6467 | 8253.0373 | 9076.7884 | 9983.0959 | 10979.6342 | 12074.4892 | 13276.0343 | 14592.7216 | 16032.7488 | 17603.5447 | 19310.9923 | 21158.2698 | 23144.1436 |  | 43.5978 | 47.7213 | 52.2556 | 57.2429 | 62.7296 | 68.7669 | 75.4116 | 82.726 | 90.7794 | 99.648 | 109.4161 | 120.1767 | 132.0329 | 145.0982 | 159.4982 | 175.3718 | 192.8723 | 212.1693 | 233.45 | 256.9218 | 282.8133 | 311.3779 | 342.8952 | 377.6746 | 416.0581 | 458.424 | 505.1903 | 556.8195 | 613.8229 | 676.7661 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 28.8951 | 33.0186 | 37.5529 | 42.5402 | 48.0269 | 54.0642 | 60.7089 | 68.0233 | 76.0767 | 84.9453 | 94.7134 | 105.4741 | 117.3302 | 130.3955 | 144.7956 | 160.6691 | 178.1696 | 194.5711 | 210.1226 | 225.7298 | 240.7771 | 254.3278 | 264.9813 | 270.6714 | 268.376 | 253.7031 | 220.3 | 159.0076 | 56.653 | -105.6768 |  | 2.414 | 2.6424 | 2.8934 | 3.1696 | 3.4734 | 3.8077 | 4.1756 | 4.5806 | 5.0265 | 5.5176 | 6.0584 | 6.6543 | 7.3108 | 8.0342 | 8.8315 | 9.7105 | 10.6795 | 11.748 | 12.9263 | 14.2259 | 15.6596 | 17.2412 | 18.9863 | 20.9121 | 23.0374 | 25.3832 | 27.9727 | 30.8315 | 33.9878 | 37.473 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 0.34629 | 0.57461 | 0.82568 | 1.1018 | 1.4056 | 1.7399 | 2.1078 | 2.5128 | 2.9588 | 3.4498 | 3.9907 | 4.5865 | 5.243 | 5.9664 | 6.7638 | 7.6427 | 8.6117 | 9.273 | 9.6456 | 9.8392 | 9.7477 | 9.2178 | 8.0287 | 5.8635 | 2.2678 | -3.4082 | -12.0935 | -25.1158 | -44.3711 | -72.5678 |  | 59.1908 | 64.7891 | 70.9451 | 77.7162 | 85.1652 | 93.3618 | 102.3829 | 112.3135 | 123.2472 | 135.2877 | 148.5494 | 163.1587 | 179.2552 | 196.9934 | 216.5437 | 238.0946 | 261.8542 | 288.0528 | 316.9448 | 348.8113 | 383.9631 | 422.744 | 465.5336 | 512.7521 | 564.8637 | 622.3819 | 685.8745 | 755.9691 | 833.3602 | 918.8153 |  | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.086979 | 0.1153 | 0.15417 | 0.20776 | 0.28197 | 0.38509 | 0.52886 | 0.72991 | 1.0118 | 1.4081 | 1.9662 | 2.7538 | 3.8672 |  | 59.1181 | 64.7164 | 70.8725 | 77.6435 | 85.0925 | 93.2891 | 102.3103 | 112.2408 | 123.1745 | 135.215 | 148.4767 | 163.086 | 179.1826 | 196.9207 | 216.471 | 238.0219 | 261.7816 | 287.9659 | 316.8295 | 348.6571 | 383.7554 | 422.462 | 465.1485 | 512.2232 | 564.1338 | 621.3701 | 684.4664 | 754.003 | 830.6064 | 914.9481 |  | 1618.3426 | 1774.5178 | 1946.2549 | 2135.147 | 2342.9532 | 2571.6156 | 2823.2792 | 3100.3125 | 3405.3319 | 3741.2271 | 4111.1902 | 4518.7479 | 4967.7965 | 5462.6409 | 6008.0383 | 6609.2454 | 7272.0718 | 7996.4567 | 8789.6349 | 9661.0145 | 10617.3761 | 11665.6418 | 12812.6478 | 14064.7924 | 15427.4992 | 16904.4138 | 18496.2176 | 20198.887 | 22001.1581 | 23880.8472
| TRUE | 1601 | 22006159 | FB | FB022 | 11 | FB22 | OVERCURRENT | X | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.81881 | 2190 |  | 9.9 | 0.0088019 | 0.0070254 | 0.0017765 | 52.2742 | 2248.1151 | 2300.3893 | 64.8697 | 3.5919 | 88.0707 |  | 14.217 | 0.023831 | 0.019021 | 0.00481 | 141.5342 | 6086.8485 | 6228.3827 | 175.637 | 9.7251 | 238.4546 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 28.4268 | 1.8549 | 30.2818 | 14.7027 | 2.0677 | 0.072668 |  | 2456.9217 | 6652.1994 | 47.1249 | 6605.0745 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0077488 | 0.0085501 | 0.0094378 | 0.010421 | 0.011512 | 0.01272 | 0.01406 | 0.015545 | 0.017193 | 0.019021 | 0.02105 | 0.0233 | 0.025798 | 0.028571 | 0.03165 | 0.035068 | 0.038864 | 0.04308 | 0.047763 | 0.052966 | 0.058746 | 0.065169 | 0.072308 | 0.080241 | 0.08906 | 0.098864 | 0.10976 | 0.12188 | 0.13155 | 0.13155 | 2709.9335 | 2990.1629 | 3300.6064 | 3644.5958 | 4025.8348 | 4448.4421 | 4916.9971 | 5436.5929 | 6012.8936 | 6652.1994 | 7361.5181 | 8148.6454 | 9022.2541 | 9991.9932 | 11068.5989 | 12264.0174 | 13591.5425 | 15065.968 | 16703.7585 | 18523.2386 | 20544.8045 | 22791.159 | 25287.5739 | 28062.1817 | 31146.3014 | 34574.8007 | 38386.4996 | 42624.6204 | 46005.6436 | 46005.6436 |  | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 39.4139 | 52.2455 | 69.8593 | 94.1466 | 127.7727 | 174.5004 | 239.6504 | 330.7574 | 458.5045 | 638.0566 | 890.9622 | 1247.8694 | 1752.4038 |  | 57.6574 | 63.6196 | 70.2247 | 77.5435 | 85.6549 | 94.6464 | 104.6155 | 115.6706 | 127.9322 | 141.5342 | 156.6259 | 173.3731 | 191.9602 | 212.5927 | 235.4989 | 260.933 | 289.1778 | 320.5481 | 355.3943 | 394.1061 | 437.1175 | 484.9116 | 538.0261 | 597.0595 | 662.6782 | 735.624 | 816.7229 | 906.8944 | 978.8301 | 978.8301 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 43.444 | 49.4062 | 56.0113 | 63.3301 | 71.4415 | 80.433 | 90.4021 | 101.4572 | 113.7187 | 127.3208 | 142.4125 | 159.1596 | 177.7468 | 198.3793 | 221.2855 | 246.7196 | 274.9644 | 303.5356 | 332.8431 | 363.9521 | 396.4802 | 429.76 | 462.7051 | 493.6172 | 519.9106 | 537.7158 | 541.3132 | 522.3209 | 440.2018 | 222.4254 |  | 2479.6242 | 2736.0377 | 3020.0976 | 3334.8523 | 3683.691 | 4070.3821 | 4499.116 | 4974.5528 | 5501.8755 | 6086.8485 | 6735.8843 | 7456.116 | 8255.4792 | 9142.8031 | 10127.9112 | 11221.7346 | 12436.4372 | 13785.5556 | 15284.1551 | 16949.003 | 18798.7619 | 20854.2054 | 23138.4572 | 25677.2593 | 28499.2687 | 31636.3899 | 35124.1437 | 39002.0791 | 42095.7591 | 42095.7591 |  | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 2.2202 | 2.9431 | 3.9353 | 5.3034 | 7.1976 | 9.8298 | 13.4998 | 18.632 | 25.8281 | 35.9425 | 50.189 | 70.294 | 98.7151 |  | 2477.7693 | 2734.1828 | 3018.2426 | 3332.9973 | 3681.836 | 4068.5271 | 4497.261 | 4972.6979 | 5500.0205 | 6084.9936 | 6734.0294 | 7454.2611 | 8253.6243 | 9140.9481 | 10126.0563 | 11219.8797 | 12434.5822 | 13783.3354 | 15281.2121 | 16945.0677 | 18793.4585 | 20847.0078 | 23128.6274 | 25663.7595 | 28480.6368 | 31610.5618 | 35088.2012 | 38951.8901 | 42025.4651 | 41997.044 |  | 2521.2133 | 2783.589 | 3074.2539 | 3396.3275 | 3753.2775 | 4148.9601 | 4587.6632 | 5074.1551 | 5613.7393 | 6212.3144 | 6876.4419 | 7613.4207 | 8431.3711 | 9339.3274 | 10347.3417 | 11466.5992 | 12709.5466 | 14086.8709 | 15614.0551 | 17309.0198 | 19189.9388 | 21276.7678 | 23591.3325 | 26157.3767 | 29000.5474 | 32148.2776 | 35629.5143 | 39474.211 | 42465.6668 | 42219.4694 |  | 71.5499 | 78.9488 | 87.1454 | 96.2277 | 106.2935 | 117.4515 | 129.8227 | 143.5415 | 158.7575 | 175.637 | 194.365 | 215.1474 | 238.2132 | 263.817 | 292.2425 | 323.8049 | 358.8554 | 397.7844 | 441.0267 | 489.0662 | 542.4412 | 601.7514 | 667.6638 | 740.9214 | 822.3509 | 912.873 | 1013.5127 | 1125.4112 | 1214.6798 | 1214.6798 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 56.8473 | 64.2461 | 72.4427 | 81.525 | 91.5908 | 102.7488 | 115.12 | 128.8388 | 144.0548 | 160.9343 | 179.6623 | 200.4447 | 223.5105 | 249.1143 | 277.5398 | 309.1022 | 344.1527 | 380.1862 | 417.6992 | 457.8742 | 500.4051 | 544.7013 | 589.75 | 633.9182 | 674.6687 | 708.1522 | 728.6224 | 727.5993 | 657.5099 | 432.2369 |  | 3.9618 | 4.3714 | 4.8253 | 5.3282 | 5.8855 | 6.5034 | 7.1884 | 7.948 | 8.7905 | 9.7251 | 10.7621 | 11.9129 | 13.19 | 14.6077 | 16.1817 | 17.9293 | 19.8701 | 22.0256 | 24.4199 | 27.0799 | 30.0353 | 33.3194 | 36.969 | 41.0253 | 45.5341 | 50.5464 | 56.1189 | 62.3148 | 67.2576 | 67.2576 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 1.894 | 2.3037 | 2.7576 | 3.2604 | 3.8178 | 4.4356 | 5.1206 | 5.8802 | 6.7228 | 7.6574 | 8.6944 | 9.8451 | 11.1223 | 12.54 | 14.1139 | 15.8616 | 17.8023 | 19.5506 | 21.1392 | 22.6932 | 24.1235 | 25.296 | 26.0114 | 25.9767 | 24.7645 | 21.755 | 16.0527 | 6.3675 | -11.1013 | -42.7831 |  | 97.1402 | 107.1853 | 118.3134 | 130.6441 | 144.31 | 159.4587 | 176.2545 | 194.88 | 215.538 | 238.4546 | 263.8808 | 292.0961 | 323.4115 | 358.1727 | 396.7647 | 439.6156 | 487.2021 | 540.0543 | 598.7625 | 663.9835 | 736.4485 | 816.9713 | 906.4577 | 1005.9162 | 1116.4695 | 1239.3673 | 1376.0014 | 1527.921 | 1649.117 | 1649.117 |  | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.086979 | 0.1153 | 0.15417 | 0.20776 | 0.28197 | 0.38509 | 0.52886 | 0.72991 | 1.0118 | 1.4081 | 1.9662 | 2.7538 | 3.8672 |  | 97.0675 | 107.1126 | 118.2408 | 130.5714 | 144.2373 | 159.3861 | 176.1819 | 194.8073 | 215.4653 | 238.3819 | 263.8081 | 292.0234 | 323.3388 | 358.1 | 396.692 | 439.543 | 487.1294 | 539.9673 | 598.6472 | 663.8293 | 736.2407 | 816.6893 | 906.0726 | 1005.3873 | 1115.7395 | 1238.3555 | 1374.5933 | 1525.9548 | 1646.3632 | 1645.2498 |  | 2677.0221 | 2957.2514 | 3267.695 | 3611.6843 | 3992.9234 | 4415.5306 | 4884.0857 | 5403.6814 | 5979.9822 | 6619.288 | 7328.6067 | 8115.734 | 8989.3426 | 9959.0818 | 11035.6875 | 12231.106 | 13558.631 | 15026.575 | 16651.5408 | 18453.4165 | 20450.708 | 22663.4544 | 25113.1664 | 27822.6589 | 30815.7202 | 34116.5403 | 37748.7828 | 41734.1326 | 44758.4387 | 44254.173
| TRUE | 1602 | 22006160 | FB | FB022 | 11 | FB22 | OVERCURRENT | X | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.81881 | 2190 |  | 9.9 | 0.0088019 | 0.0070254 | 0.0017765 | 52.2742 | 2248.1151 | 2300.3893 | 64.8697 | 3.5919 | 88.0707 |  | 14.217 | 0.023831 | 0.019021 | 0.00481 | 141.5342 | 6086.8485 | 6228.3827 | 175.637 | 9.7251 | 238.4546 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 28.4268 | 1.8549 | 30.2818 | 14.7027 | 2.0677 | 0.072668 |  | 2456.9217 | 6652.1994 | 47.1249 | 6605.0745 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0077488 | 0.0085501 | 0.0094378 | 0.010421 | 0.011512 | 0.01272 | 0.01406 | 0.015545 | 0.017193 | 0.019021 | 0.02105 | 0.0233 | 0.025798 | 0.028571 | 0.03165 | 0.035068 | 0.038864 | 0.04308 | 0.047763 | 0.052966 | 0.058746 | 0.065169 | 0.072308 | 0.080241 | 0.08906 | 0.098864 | 0.10976 | 0.12188 | 0.13155 | 0.13155 | 2709.9335 | 2990.1629 | 3300.6064 | 3644.5958 | 4025.8348 | 4448.4421 | 4916.9971 | 5436.5929 | 6012.8936 | 6652.1994 | 7361.5181 | 8148.6454 | 9022.2541 | 9991.9932 | 11068.5989 | 12264.0174 | 13591.5425 | 15065.968 | 16703.7585 | 18523.2386 | 20544.8045 | 22791.159 | 25287.5739 | 28062.1817 | 31146.3014 | 34574.8007 | 38386.4996 | 42624.6204 | 46005.6436 | 46005.6436 |  | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 32.929 | 39.4139 | 52.2455 | 69.8593 | 94.1466 | 127.7727 | 174.5004 | 239.6504 | 330.7574 | 458.5045 | 638.0566 | 890.9622 | 1247.8694 | 1752.4038 |  | 57.6574 | 63.6196 | 70.2247 | 77.5435 | 85.6549 | 94.6464 | 104.6155 | 115.6706 | 127.9322 | 141.5342 | 156.6259 | 173.3731 | 191.9602 | 212.5927 | 235.4989 | 260.933 | 289.1778 | 320.5481 | 355.3943 | 394.1061 | 437.1175 | 484.9116 | 538.0261 | 597.0595 | 662.6782 | 735.624 | 816.7229 | 906.8944 | 978.8301 | 978.8301 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 43.444 | 49.4062 | 56.0113 | 63.3301 | 71.4415 | 80.433 | 90.4021 | 101.4572 | 113.7187 | 127.3208 | 142.4125 | 159.1596 | 177.7468 | 198.3793 | 221.2855 | 246.7196 | 274.9644 | 303.5356 | 332.8431 | 363.9521 | 396.4802 | 429.76 | 462.7051 | 493.6172 | 519.9106 | 537.7158 | 541.3132 | 522.3209 | 440.2018 | 222.4254 |  | 2479.6242 | 2736.0377 | 3020.0976 | 3334.8523 | 3683.691 | 4070.3821 | 4499.116 | 4974.5528 | 5501.8755 | 6086.8485 | 6735.8843 | 7456.116 | 8255.4792 | 9142.8031 | 10127.9112 | 11221.7346 | 12436.4372 | 13785.5556 | 15284.1551 | 16949.003 | 18798.7619 | 20854.2054 | 23138.4572 | 25677.2593 | 28499.2687 | 31636.3899 | 35124.1437 | 39002.0791 | 42095.7591 | 42095.7591 |  | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 1.8549 | 2.2202 | 2.9431 | 3.9353 | 5.3034 | 7.1976 | 9.8298 | 13.4998 | 18.632 | 25.8281 | 35.9425 | 50.189 | 70.294 | 98.7151 |  | 2477.7693 | 2734.1828 | 3018.2426 | 3332.9973 | 3681.836 | 4068.5271 | 4497.261 | 4972.6979 | 5500.0205 | 6084.9936 | 6734.0294 | 7454.2611 | 8253.6243 | 9140.9481 | 10126.0563 | 11219.8797 | 12434.5822 | 13783.3354 | 15281.2121 | 16945.0677 | 18793.4585 | 20847.0078 | 23128.6274 | 25663.7595 | 28480.6368 | 31610.5618 | 35088.2012 | 38951.8901 | 42025.4651 | 41997.044 |  | 2521.2133 | 2783.589 | 3074.2539 | 3396.3275 | 3753.2775 | 4148.9601 | 4587.6632 | 5074.1551 | 5613.7393 | 6212.3144 | 6876.4419 | 7613.4207 | 8431.3711 | 9339.3274 | 10347.3417 | 11466.5992 | 12709.5466 | 14086.8709 | 15614.0551 | 17309.0198 | 19189.9388 | 21276.7678 | 23591.3325 | 26157.3767 | 29000.5474 | 32148.2776 | 35629.5143 | 39474.211 | 42465.6668 | 42219.4694 |  | 71.5499 | 78.9488 | 87.1454 | 96.2277 | 106.2935 | 117.4515 | 129.8227 | 143.5415 | 158.7575 | 175.637 | 194.365 | 215.1474 | 238.2132 | 263.817 | 292.2425 | 323.8049 | 358.8554 | 397.7844 | 441.0267 | 489.0662 | 542.4412 | 601.7514 | 667.6638 | 740.9214 | 822.3509 | 912.873 | 1013.5127 | 1125.4112 | 1214.6798 | 1214.6798 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 56.8473 | 64.2461 | 72.4427 | 81.525 | 91.5908 | 102.7488 | 115.12 | 128.8388 | 144.0548 | 160.9343 | 179.6623 | 200.4447 | 223.5105 | 249.1143 | 277.5398 | 309.1022 | 344.1527 | 380.1862 | 417.6992 | 457.8742 | 500.4051 | 544.7013 | 589.75 | 633.9182 | 674.6687 | 708.1522 | 728.6224 | 727.5993 | 657.5099 | 432.2369 |  | 3.9618 | 4.3714 | 4.8253 | 5.3282 | 5.8855 | 6.5034 | 7.1884 | 7.948 | 8.7905 | 9.7251 | 10.7621 | 11.9129 | 13.19 | 14.6077 | 16.1817 | 17.9293 | 19.8701 | 22.0256 | 24.4199 | 27.0799 | 30.0353 | 33.3194 | 36.969 | 41.0253 | 45.5341 | 50.5464 | 56.1189 | 62.3148 | 67.2576 | 67.2576 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 1.894 | 2.3037 | 2.7576 | 3.2604 | 3.8178 | 4.4356 | 5.1206 | 5.8802 | 6.7228 | 7.6574 | 8.6944 | 9.8451 | 11.1223 | 12.54 | 14.1139 | 15.8616 | 17.8023 | 19.5506 | 21.1392 | 22.6932 | 24.1235 | 25.296 | 26.0114 | 25.9767 | 24.7645 | 21.755 | 16.0527 | 6.3675 | -11.1013 | -42.7831 |  | 97.1402 | 107.1853 | 118.3134 | 130.6441 | 144.31 | 159.4587 | 176.2545 | 194.88 | 215.538 | 238.4546 | 263.8808 | 292.0961 | 323.4115 | 358.1727 | 396.7647 | 439.6156 | 487.2021 | 540.0543 | 598.7625 | 663.9835 | 736.4485 | 816.9713 | 906.4577 | 1005.9162 | 1116.4695 | 1239.3673 | 1376.0014 | 1527.921 | 1649.117 | 1649.117 |  | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.072668 | 0.086979 | 0.1153 | 0.15417 | 0.20776 | 0.28197 | 0.38509 | 0.52886 | 0.72991 | 1.0118 | 1.4081 | 1.9662 | 2.7538 | 3.8672 |  | 97.0675 | 107.1126 | 118.2408 | 130.5714 | 144.2373 | 159.3861 | 176.1819 | 194.8073 | 215.4653 | 238.3819 | 263.8081 | 292.0234 | 323.3388 | 358.1 | 396.692 | 439.543 | 487.1294 | 539.9673 | 598.6472 | 663.8293 | 736.2407 | 816.6893 | 906.0726 | 1005.3873 | 1115.7395 | 1238.3555 | 1374.5933 | 1525.9548 | 1646.3632 | 1645.2498 |  | 2677.0221 | 2957.2514 | 3267.695 | 3611.6843 | 3992.9234 | 4415.5306 | 4884.0857 | 5403.6814 | 5979.9822 | 6619.288 | 7328.6067 | 8115.734 | 8989.3426 | 9959.0818 | 11035.6875 | 12231.106 | 13558.631 | 15026.575 | 16651.5408 | 18453.4165 | 20450.708 | 22663.4544 | 25113.1664 | 27822.6589 | 30815.7202 | 34116.5403 | 37748.7828 | 41734.1326 | 44758.4387 | 44254.173
| TRUE | 1603 | 22006161 | FB | FB023 | 11 | FB23 | SENSITIVE EF | Blank | English Electric | CMG_1328 | CMG 1328 | CMG | Electromechanical |  | 0.57434 | 2190 |  | 8.25 | 0.0054067 | 0.0038888 | 0.0015179 | 31.8755 | 1244.4067 | 1276.2822 | 37.4249 | 2.2021 | 97.5002 |  | 11.5885 | 0.013521 | 0.0097249 | 0.0037959 | 79.7129 | 3111.9605 | 3191.6734 | 93.5906 | 5.5069 | 243.8244 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.10194 |  | 1413.4094 | 3534.5954 | 46.5895 | 3488.0058 |  | 0.03398 |  | 8.5352 | 8.8302 | 9.1354 | 9.4511 | 9.7778 | 10.1158 | 10.4654 | 10.8271 | 11.2014 | 11.5885 | 11.9891 | 12.4035 | 12.8322 | 13.2757 | 13.7346 | 14.2093 | 14.7004 | 15.2085 | 15.7342 | 16.278 | 16.8407 | 17.4227 | 18.0249 | 18.6479 | 19.2925 | 19.9593 | 20.6492 | 21.3629 | 22.1013 | 22.8652 |  | 0.0059156 | 0.0064751 | 0.0070903 | 0.007767 | 0.0085115 | 0.0093307 | 0.010232 | 0.011225 | 0.012317 | 0.013521 | 0.014846 | 0.016306 | 0.017915 | 0.019688 | 0.021642 | 0.023795 | 0.02617 | 0.028788 | 0.031676 | 0.034861 | 0.038374 | 0.042249 | 0.046526 | 0.051245 | 0.056453 | 0.062201 | 0.068547 | 0.075552 | 0.083287 | 0.091827 |  | 0.0042548 | 0.0046572 | 0.0050997 | 0.0055865 | 0.0061219 | 0.0067111 | 0.0073596 | 0.0080734 | 0.0088594 | 0.0097249 | 0.010678 | 0.011728 | 0.012885 | 0.01416 | 0.015566 | 0.017115 | 0.018823 | 0.020706 | 0.022783 | 0.025074 | 0.0276 | 0.030388 | 0.033464 | 0.036858 | 0.040604 | 0.044739 | 0.049303 | 0.054341 | 0.059904 | 0.066047 | 1546.4496 | 1692.7124 | 1853.5494 | 2030.4526 | 2225.0694 | 2439.2187 | 2674.9093 | 2934.3594 | 3220.0194 | 3534.5954 | 3881.0771 | 4262.7672 | 4683.3148 | 5146.7517 | 5657.5329 | 6220.5816 | 6841.3387 | 7525.8172 | 8280.6635 | 9113.224 | 10031.6194 | 11044.8271 | 12162.7716 | 13396.4256 | 14757.9209 | 16260.6717 | 17919.5107 | 19750.84 | 21772.7981 | 24005.4441 |  | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 38.7675 | 51.3886 | 68.7135 | 92.6024 | 125.6769 | 171.6381 | 235.7196 | 325.3322 | 450.984 | 627.591 | 876.3484 | 1227.4015 | 1723.6604 |  | 34.8758 | 38.1744 | 41.8016 | 45.7912 | 50.1802 | 55.0097 | 60.3251 | 66.1763 | 72.6185 | 79.7129 | 87.5268 | 96.1348 | 105.619 | 116.0706 | 127.5898 | 140.2878 | 154.2872 | 169.7237 | 186.7472 | 205.5232 | 226.2351 | 249.0851 | 274.2972 | 302.1189 | 332.8236 | 366.7139 | 404.1244 | 445.4249 | 491.0245 | 541.3756 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 20.6629 | 23.9614 | 27.5887 | 31.5782 | 35.9673 | 40.7968 | 46.1121 | 51.9633 | 58.4056 | 65.5 | 73.3139 | 81.9218 | 91.4061 | 101.8576 | 113.3769 | 126.0749 | 140.0743 | 152.7117 | 164.1968 | 175.3703 | 185.5991 | 193.9354 | 198.9787 | 198.68 | 190.0608 | 168.8124 | 128.7239 | 60.8643 | -47.5858 | -215.0038 |  | 1361.5392 | 1490.3132 | 1631.9188 | 1787.6695 | 1959.0158 | 2147.5591 | 2355.0679 | 2583.4953 | 2834.9986 | 3111.9605 | 3417.0131 | 3753.0642 | 4123.3265 | 4531.3498 | 4981.0564 | 5476.7809 | 6023.3134 | 6625.9482 | 7290.5369 | 8023.5473 | 8832.1293 | 9724.1868 | 10708.4577 | 11794.6025 | 12993.3025 | 14316.368 | 15776.8581 | 17389.2136 | 19169.4043 | 21135.0908 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 1360.2381 | 1489.0121 | 1630.6177 | 1786.3684 | 1957.7147 | 2146.258 | 2353.7668 | 2582.1942 | 2833.6975 | 3110.6594 | 3415.712 | 3751.7631 | 4122.0254 | 4530.0487 | 4979.7553 | 5475.4798 | 6022.0123 | 6624.3909 | 7288.4725 | 8020.787 | 8828.4094 | 9719.1382 | 10701.5627 | 11785.1334 | 12980.2336 | 14298.2514 | 15751.647 | 17354.0097 | 19120.0981 | 21065.8493 |  | 1380.9009 | 1512.9735 | 1658.2063 | 1817.9466 | 1993.6819 | 2187.0548 | 2399.8789 | 2634.1576 | 2892.1031 | 3176.1593 | 3489.0258 | 3833.6849 | 4213.4315 | 4631.9063 | 5093.1322 | 5601.5546 | 6162.0866 | 6777.1026 | 7452.6693 | 8196.1573 | 9014.0085 | 9913.0736 | 10900.5415 | 11983.8134 | 13170.2943 | 14467.0638 | 15880.3709 | 17414.8739 | 19072.5122 | 20850.8454 |  | 40.9476 | 44.8204 | 49.0791 | 53.7633 | 58.9164 | 64.5868 | 70.8275 | 77.6973 | 85.2612 | 93.5906 | 102.7649 | 112.8715 | 124.007 | 136.2781 | 149.8028 | 164.7114 | 181.1481 | 199.2721 | 219.2592 | 241.3041 | 265.6218 | 292.45 | 322.0515 | 354.7167 | 390.767 | 430.5576 | 474.4811 | 522.9718 | 576.5102 | 635.6272 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 26.2547 | 30.1276 | 34.3863 | 39.0704 | 44.2235 | 49.8939 | 56.1346 | 63.0045 | 70.5683 | 78.8978 | 88.0721 | 98.1786 | 109.3141 | 121.5852 | 135.1099 | 150.0186 | 166.4552 | 181.6856 | 195.9474 | 210.133 | 223.6138 | 235.438 | 244.1897 | 247.7851 | 243.1836 | 225.9735 | 189.7812 | 125.4258 | 19.7127 | -146.2928 |  | 2.4094 | 2.6372 | 2.8878 | 3.1634 | 3.4667 | 3.8003 | 4.1675 | 4.5717 | 5.0168 | 5.5069 | 6.0467 | 6.6414 | 7.2966 | 8.0187 | 8.8144 | 9.6917 | 10.6588 | 11.7252 | 12.9013 | 14.1984 | 15.6293 | 17.2079 | 18.9496 | 20.8717 | 22.9929 | 25.3342 | 27.9186 | 30.7719 | 33.9221 | 37.4005 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.34164 | 0.56952 | 0.8201 | 1.0957 | 1.3989 | 1.7326 | 2.0998 | 2.504 | 2.9491 | 3.4392 | 3.979 | 4.5737 | 5.2289 | 5.9509 | 6.7467 | 7.6239 | 8.5911 | 9.2503 | 9.6206 | 9.8117 | 9.7175 | 9.1846 | 7.9921 | 5.8231 | 2.2234 | -3.457 | -12.1473 | -25.1749 | -44.4362 | -72.6393 |  | 106.6776 | 116.7671 | 127.862 | 140.0652 | 153.4903 | 168.2628 | 184.5213 | 202.4188 | 222.1243 | 243.8244 | 267.7255 | 294.0554 | 323.0657 | 355.0346 | 390.2695 | 429.1099 | 471.9311 | 519.148 | 571.219 | 628.6509 | 692.0039 | 761.8973 | 839.0156 | 924.1159 | 1018.0349 | 1121.6981 | 1236.1286 | 1362.4578 | 1501.9371 | 1655.9501 |  | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.12202 | 0.16174 | 0.21627 | 0.29146 | 0.39556 | 0.54022 | 0.74191 | 1.024 | 1.4194 | 1.9753 | 2.7583 | 3.8632 | 5.4251 |  | 106.5757 | 116.6652 | 127.7601 | 139.9633 | 153.3884 | 168.1609 | 184.4194 | 202.3168 | 222.0223 | 243.7225 | 267.6236 | 293.9534 | 322.9638 | 354.9327 | 390.1675 | 429.0079 | 471.8291 | 519.026 | 571.0572 | 628.4346 | 691.7124 | 761.5017 | 838.4754 | 923.374 | 1017.011 | 1120.2786 | 1234.1533 | 1359.6996 | 1498.0739 | 1650.525 |  | 1514.073 | 1660.3358 | 1821.1728 | 1998.076 | 2192.6928 | 2406.8421 | 2642.5327 | 2901.9829 | 3187.6428 | 3502.2188 | 3848.7005 | 4230.3906 | 4650.9383 | 5114.3751 | 5625.1563 | 6188.2051 | 6808.9621 | 7487.0645 | 8229.2945 | 9044.5366 | 9939.0522 | 10919.1979 | 11991.1986 | 13160.7956 | 14432.7122 | 15809.8589 | 17292.158 | 18874.8244 | 20545.8626 | 22282.4383
| TRUE | 1604 | 22006162 | FB | FB023 | 11 | FB23 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 158.7269 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 429.7586 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.10194 |  | 2300.9817 | 6229.9868 | 46.5895 | 6183.3973 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2537.9351 | 2800.3783 | 3091.1182 | 3413.2746 | 3770.3166 | 4166.1011 | 4604.9171 | 5091.5344 | 5631.2575 | 6229.9868 | 6894.2853 | 7631.4539 | 8449.615 | 9357.8051 | 10366.0791 | 11485.6248 | 12728.8923 | 14109.7366 | 15643.5771 | 17347.5756 | 19240.8334 | 21344.6126 | 23682.5809 | 26281.0854 | 29169.4573 | 32380.3509 | 35950.1227 | 39919.2516 | 43085.6825 | 43085.6825 |  | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 38.7675 | 51.3886 | 68.7135 | 92.6024 | 125.6769 | 171.6381 | 235.7196 | 325.3322 | 450.984 | 627.591 | 876.3484 | 1227.4015 | 1723.6604 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 175.0725 | 193.1765 | 213.2324 | 235.4554 | 260.085 | 287.3871 | 317.6576 | 351.2256 | 388.4569 | 429.7586 | 475.5835 | 526.435 | 582.8736 | 645.5227 | 715.0757 | 792.3045 | 878.0679 | 973.3217 | 1079.1295 | 1196.6752 | 1327.2764 | 1472.3999 | 1633.6782 | 1812.929 | 2012.1754 | 2233.6702 | 2479.9211 | 2753.7207 | 2972.1483 | 2972.1483 |  | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.12202 | 0.16174 | 0.21627 | 0.29146 | 0.39556 | 0.54022 | 0.74191 | 1.024 | 1.4194 | 1.9753 | 2.7583 | 3.8632 | 5.4251 |  | 174.9706 | 193.0745 | 213.1304 | 235.3535 | 259.9831 | 287.2852 | 317.5557 | 351.1237 | 388.355 | 429.6567 | 475.4815 | 526.3331 | 582.7717 | 645.4207 | 714.9737 | 792.2026 | 877.966 | 973.1997 | 1078.9678 | 1196.4589 | 1326.9849 | 1472.0043 | 1633.138 | 1812.1871 | 2011.1515 | 2232.2507 | 2477.9458 | 2750.9624 | 2968.2851 | 2966.7232 |  | 2505.5585 | 2768.0017 | 3058.7416 | 3380.898 | 3737.94 | 4133.7245 | 4572.5405 | 5059.1578 | 5598.8809 | 6197.6102 | 6861.9087 | 7599.0773 | 8417.2384 | 9325.4285 | 10333.7025 | 11453.2482 | 12696.5157 | 14070.9838 | 15592.2081 | 17278.8882 | 19148.2662 | 21218.9834 | 23511.008 | 26045.4554 | 28844.2486 | 31929.5382 | 35322.77 | 39043.2359 | 41858.7471 | 41362.6767
| TRUE | 1605 | 22006163 | FB | FB023 | 11 | FB23 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 158.7269 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 429.7586 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.10194 |  | 2300.9817 | 6229.9868 | 46.5895 | 6183.3973 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2537.9351 | 2800.3783 | 3091.1182 | 3413.2746 | 3770.3166 | 4166.1011 | 4604.9171 | 5091.5344 | 5631.2575 | 6229.9868 | 6894.2853 | 7631.4539 | 8449.615 | 9357.8051 | 10366.0791 | 11485.6248 | 12728.8923 | 14109.7366 | 15643.5771 | 17347.5756 | 19240.8334 | 21344.6126 | 23682.5809 | 26281.0854 | 29169.4573 | 32380.3509 | 35950.1227 | 39919.2516 | 43085.6825 | 43085.6825 |  | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 32.3889 | 38.7675 | 51.3886 | 68.7135 | 92.6024 | 125.6769 | 171.6381 | 235.7196 | 325.3322 | 450.984 | 627.591 | 876.3484 | 1227.4015 | 1723.6604 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 175.0725 | 193.1765 | 213.2324 | 235.4554 | 260.085 | 287.3871 | 317.6576 | 351.2256 | 388.4569 | 429.7586 | 475.5835 | 526.435 | 582.8736 | 645.5227 | 715.0757 | 792.3045 | 878.0679 | 973.3217 | 1079.1295 | 1196.6752 | 1327.2764 | 1472.3999 | 1633.6782 | 1812.929 | 2012.1754 | 2233.6702 | 2479.9211 | 2753.7207 | 2972.1483 | 2972.1483 |  | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.10194 | 0.12202 | 0.16174 | 0.21627 | 0.29146 | 0.39556 | 0.54022 | 0.74191 | 1.024 | 1.4194 | 1.9753 | 2.7583 | 3.8632 | 5.4251 |  | 174.9706 | 193.0745 | 213.1304 | 235.3535 | 259.9831 | 287.2852 | 317.5557 | 351.1237 | 388.355 | 429.6567 | 475.4815 | 526.3331 | 582.7717 | 645.4207 | 714.9737 | 792.2026 | 877.966 | 973.1997 | 1078.9678 | 1196.4589 | 1326.9849 | 1472.0043 | 1633.138 | 1812.1871 | 2011.1515 | 2232.2507 | 2477.9458 | 2750.9624 | 2968.2851 | 2966.7232 |  | 2505.5585 | 2768.0017 | 3058.7416 | 3380.898 | 3737.94 | 4133.7245 | 4572.5405 | 5059.1578 | 5598.8809 | 6197.6102 | 6861.9087 | 7599.0773 | 8417.2384 | 9325.4285 | 10333.7025 | 11453.2482 | 12696.5157 | 14070.9838 | 15592.2081 | 17278.8882 | 19148.2662 | 21218.9834 | 23511.008 | 26045.4554 | 28844.2486 | 31929.5382 | 35322.77 | 39043.2359 | 41858.7471 | 41362.6767
| TRUE | 1606 | 22006122 | FB | FB004 | 11 | FB4 | SENSITIVE EF | Blank | English Electric | CMG_1328 | CMG 1328 | CMG | Electromechanical |  | 0.57434 | 2190 |  | 8.25 | 0.0054067 | 0.0038888 | 0.0015179 | 31.8755 | 1244.4067 | 1276.2822 | 37.4249 | 2.2021 | 57.2543 |  | 11.5885 | 0.013521 | 0.0097249 | 0.0037959 | 79.7129 | 3111.9605 | 3191.6734 | 93.5906 | 5.5069 | 143.1792 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.059863 |  | 1373.1635 | 3433.9502 | 46.5474 | 3387.4027 |  | 0.03398 |  | 8.5352 | 8.8302 | 9.1354 | 9.4511 | 9.7778 | 10.1158 | 10.4654 | 10.8271 | 11.2014 | 11.5885 | 11.9891 | 12.4035 | 12.8322 | 13.2757 | 13.7346 | 14.2093 | 14.7004 | 15.2085 | 15.7342 | 16.278 | 16.8407 | 17.4227 | 18.0249 | 18.6479 | 19.2925 | 19.9593 | 20.6492 | 21.3629 | 22.1013 | 22.8652 |  | 0.0059156 | 0.0064751 | 0.0070903 | 0.007767 | 0.0085115 | 0.0093307 | 0.010232 | 0.011225 | 0.012317 | 0.013521 | 0.014846 | 0.016306 | 0.017915 | 0.019688 | 0.021642 | 0.023795 | 0.02617 | 0.028788 | 0.031676 | 0.034861 | 0.038374 | 0.042249 | 0.046526 | 0.051245 | 0.056453 | 0.062201 | 0.068547 | 0.075552 | 0.083287 | 0.091827 |  | 0.0042548 | 0.0046572 | 0.0050997 | 0.0055865 | 0.0061219 | 0.0067111 | 0.0073596 | 0.0080734 | 0.0088594 | 0.0097249 | 0.010678 | 0.011728 | 0.012885 | 0.01416 | 0.015566 | 0.017115 | 0.018823 | 0.020706 | 0.022783 | 0.025074 | 0.0276 | 0.030388 | 0.033464 | 0.036858 | 0.040604 | 0.044739 | 0.049303 | 0.054341 | 0.059904 | 0.066047 | 1502.4155 | 1644.5136 | 1800.7709 | 1972.6369 | 2161.7121 | 2369.7636 | 2598.7431 | 2850.8056 | 3128.3315 | 3433.9502 | 3770.5661 | 4141.3879 | 4549.9607 | 5000.2015 | 5496.4385 | 6043.4548 | 6646.5363 | 7311.5247 | 8044.8773 | 8853.7312 | 9745.976 | 10730.3332 | 11816.445 | 13014.9716 | 14337.6993 | 15797.6602 | 17409.2649 | 19188.4484 | 21152.8326 | 23321.9056 |  | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 38.7171 | 51.3218 | 68.6242 | 92.4821 | 125.5137 | 171.4152 | 235.4133 | 324.9096 | 450.3981 | 626.7756 | 875.2098 | 1225.8069 | 1721.421 |  | 34.8758 | 38.1744 | 41.8016 | 45.7912 | 50.1802 | 55.0097 | 60.3251 | 66.1763 | 72.6185 | 79.7129 | 87.5268 | 96.1348 | 105.619 | 116.0706 | 127.5898 | 140.2878 | 154.2872 | 169.7237 | 186.7472 | 205.5232 | 226.2351 | 249.0851 | 274.2972 | 302.1189 | 332.8236 | 366.7139 | 404.1244 | 445.4249 | 491.0245 | 541.3756 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 20.6629 | 23.9614 | 27.5887 | 31.5782 | 35.9673 | 40.7968 | 46.1121 | 51.9633 | 58.4056 | 65.5 | 73.3139 | 81.9218 | 91.4061 | 101.8576 | 113.3769 | 126.0749 | 140.0743 | 152.7117 | 164.1968 | 175.3703 | 185.5991 | 193.9354 | 198.9787 | 198.68 | 190.0608 | 168.8124 | 128.7239 | 60.8643 | -47.5858 | -215.0038 |  | 1361.5392 | 1490.3132 | 1631.9188 | 1787.6695 | 1959.0158 | 2147.5591 | 2355.0679 | 2583.4953 | 2834.9986 | 3111.9605 | 3417.0131 | 3753.0642 | 4123.3265 | 4531.3498 | 4981.0564 | 5476.7809 | 6023.3134 | 6625.9482 | 7290.5369 | 8023.5473 | 8832.1293 | 9724.1868 | 10708.4577 | 11794.6025 | 12993.3025 | 14316.368 | 15776.8581 | 17389.2136 | 19169.4043 | 21135.0908 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 1360.2381 | 1489.0121 | 1630.6177 | 1786.3684 | 1957.7147 | 2146.258 | 2353.7668 | 2582.1942 | 2833.6975 | 3110.6594 | 3415.712 | 3751.7631 | 4122.0254 | 4530.0487 | 4979.7553 | 5475.4798 | 6022.0123 | 6624.3909 | 7288.4725 | 8020.787 | 8828.4094 | 9719.1382 | 10701.5627 | 11785.1334 | 12980.2336 | 14298.2514 | 15751.647 | 17354.0097 | 19120.0981 | 21065.8493 |  | 1380.9009 | 1512.9735 | 1658.2063 | 1817.9466 | 1993.6819 | 2187.0548 | 2399.8789 | 2634.1576 | 2892.1031 | 3176.1593 | 3489.0258 | 3833.6849 | 4213.4315 | 4631.9063 | 5093.1322 | 5601.5546 | 6162.0866 | 6777.1026 | 7452.6693 | 8196.1573 | 9014.0085 | 9913.0736 | 10900.5415 | 11983.8134 | 13170.2943 | 14467.0638 | 15880.3709 | 17414.8739 | 19072.5122 | 20850.8454 |  | 40.9476 | 44.8204 | 49.0791 | 53.7633 | 58.9164 | 64.5868 | 70.8275 | 77.6973 | 85.2612 | 93.5906 | 102.7649 | 112.8715 | 124.007 | 136.2781 | 149.8028 | 164.7114 | 181.1481 | 199.2721 | 219.2592 | 241.3041 | 265.6218 | 292.45 | 322.0515 | 354.7167 | 390.767 | 430.5576 | 474.4811 | 522.9718 | 576.5102 | 635.6272 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 26.2547 | 30.1276 | 34.3863 | 39.0704 | 44.2235 | 49.8939 | 56.1346 | 63.0045 | 70.5683 | 78.8978 | 88.0721 | 98.1786 | 109.3141 | 121.5852 | 135.1099 | 150.0186 | 166.4552 | 181.6856 | 195.9474 | 210.133 | 223.6138 | 235.438 | 244.1897 | 247.7851 | 243.1836 | 225.9735 | 189.7812 | 125.4258 | 19.7127 | -146.2928 |  | 2.4094 | 2.6372 | 2.8878 | 3.1634 | 3.4667 | 3.8003 | 4.1675 | 4.5717 | 5.0168 | 5.5069 | 6.0467 | 6.6414 | 7.2966 | 8.0187 | 8.8144 | 9.6917 | 10.6588 | 11.7252 | 12.9013 | 14.1984 | 15.6293 | 17.2079 | 18.9496 | 20.8717 | 22.9929 | 25.3342 | 27.9186 | 30.7719 | 33.9221 | 37.4005 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.34164 | 0.56952 | 0.8201 | 1.0957 | 1.3989 | 1.7326 | 2.0998 | 2.504 | 2.9491 | 3.4392 | 3.979 | 4.5737 | 5.2289 | 5.9509 | 6.7467 | 7.6239 | 8.5911 | 9.2503 | 9.6206 | 9.8117 | 9.7175 | 9.1846 | 7.9921 | 5.8231 | 2.2234 | -3.457 | -12.1473 | -25.1749 | -44.4362 | -72.6393 |  | 62.6435 | 68.5683 | 75.0835 | 82.2495 | 90.133 | 98.8078 | 108.3551 | 118.8649 | 130.4364 | 143.1792 | 157.2145 | 172.676 | 189.7115 | 208.4844 | 229.1751 | 251.9831 | 277.1287 | 304.8555 | 335.4328 | 369.1581 | 406.3604 | 447.4034 | 492.689 | 542.6618 | 597.8132 | 658.6866 | 725.8828 | 800.0662 | 881.9716 | 972.4115 |  | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.071652 | 0.094979 | 0.127 | 0.17115 | 0.23228 | 0.31723 | 0.43567 | 0.6013 | 0.83353 | 1.1599 | 1.6197 | 2.2685 | 3.1858 |  | 62.5837 | 68.5085 | 75.0236 | 82.1896 | 90.0732 | 98.7479 | 108.2952 | 118.805 | 130.3765 | 143.1194 | 157.1546 | 172.6161 | 189.6517 | 208.4245 | 229.1152 | 251.9232 | 277.0688 | 304.7838 | 335.3378 | 369.0311 | 406.1893 | 447.1711 | 492.3718 | 542.2262 | 597.2119 | 657.8531 | 724.7228 | 798.4465 | 879.703 | 969.2258 |  | 1470.081 | 1612.1791 | 1768.4363 | 1940.3024 | 2129.3776 | 2337.4291 | 2566.4086 | 2818.4711 | 3095.997 | 3401.6157 | 3738.2315 | 4109.0533 | 4517.6262 | 4967.867 | 5464.104 | 6011.1203 | 6614.2017 | 7272.8224 | 7993.575 | 8785.1331 | 9653.529 | 10604.8673 | 11645.0951 | 12779.6478 | 14012.9132 | 15347.4334 | 16782.7276 | 18313.5713 | 19927.4918 | 21601.1391
| TRUE | 1607 | 22006123 | FB | FB004 | 11 | FB4 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 93.2081 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 252.364 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.059863 |  | 2235.4629 | 6052.5922 | 46.5474 | 6006.0447 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2465.6691 | 2720.6395 | 3003.1007 | 3316.084 | 3662.9594 | 4047.4742 | 4473.7953 | 4946.5564 | 5470.9113 | 6052.5922 | 6697.9752 | 7414.1535 | 8209.018 | 9091.348 | 10070.9121 | 11158.5795 | 12366.4458 | 13707.9715 | 15198.137 | 16853.6153 | 18692.9639 | 20736.8394 | 23008.2357 | 25532.7496 | 28338.877 | 31458.3427 | 34926.4676 | 38782.5782 | 41858.8473 | 41858.8473 |  | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 38.7171 | 51.3218 | 68.6242 | 92.4821 | 125.5137 | 171.4152 | 235.4133 | 324.9096 | 450.3981 | 626.7756 | 875.2098 | 1225.8069 | 1721.421 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 102.8066 | 113.4376 | 125.2149 | 138.2648 | 152.7278 | 168.7602 | 186.5358 | 206.2477 | 228.1107 | 252.364 | 279.2734 | 309.1346 | 342.2766 | 379.0656 | 419.9087 | 465.2592 | 515.6214 | 571.5566 | 633.6894 | 702.7149 | 779.4069 | 864.6267 | 959.333 | 1064.5931 | 1181.5952 | 1311.6619 | 1456.2661 | 1617.0474 | 1745.313 | 1745.313 |  | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.071652 | 0.094979 | 0.127 | 0.17115 | 0.23228 | 0.31723 | 0.43567 | 0.6013 | 0.83353 | 1.1599 | 1.6197 | 2.2685 | 3.1858 |  | 102.7467 | 113.3777 | 125.155 | 138.2049 | 152.668 | 168.7004 | 186.4759 | 206.1878 | 228.0509 | 252.3042 | 279.2136 | 309.0748 | 342.2168 | 379.0057 | 419.8488 | 465.1993 | 515.5616 | 571.485 | 633.5944 | 702.5879 | 779.2357 | 864.3944 | 959.0158 | 1064.1574 | 1180.9939 | 1310.8284 | 1455.1061 | 1615.4277 | 1743.0445 | 1742.1273 |  | 2433.3346 | 2688.305 | 2970.7662 | 3283.7495 | 3630.6249 | 4015.1397 | 4441.4608 | 4914.2219 | 5438.5768 | 6020.2577 | 6665.6407 | 7381.819 | 8176.6835 | 9059.0135 | 10038.5776 | 11126.245 | 12334.1113 | 13669.2691 | 15146.8347 | 16785.0171 | 18600.517 | 20611.3735 | 22836.8857 | 25297.4257 | 28014.0909 | 31008.1158 | 34299.9303 | 37907.7012 | 40633.5065 | 40138.0808
| TRUE | 1608 | 22006124 | FB | FB004 | 11 | FB4 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 93.2081 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 252.364 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.059863 |  | 2235.4629 | 6052.5922 | 46.5474 | 6006.0447 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2465.6691 | 2720.6395 | 3003.1007 | 3316.084 | 3662.9594 | 4047.4742 | 4473.7953 | 4946.5564 | 5470.9113 | 6052.5922 | 6697.9752 | 7414.1535 | 8209.018 | 9091.348 | 10070.9121 | 11158.5795 | 12366.4458 | 13707.9715 | 15198.137 | 16853.6153 | 18692.9639 | 20736.8394 | 23008.2357 | 25532.7496 | 28338.877 | 31458.3427 | 34926.4676 | 38782.5782 | 41858.8473 | 41858.8473 |  | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 38.7171 | 51.3218 | 68.6242 | 92.4821 | 125.5137 | 171.4152 | 235.4133 | 324.9096 | 450.3981 | 626.7756 | 875.2098 | 1225.8069 | 1721.421 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 102.8066 | 113.4376 | 125.2149 | 138.2648 | 152.7278 | 168.7602 | 186.5358 | 206.2477 | 228.1107 | 252.364 | 279.2734 | 309.1346 | 342.2766 | 379.0656 | 419.9087 | 465.2592 | 515.6214 | 571.5566 | 633.6894 | 702.7149 | 779.4069 | 864.6267 | 959.333 | 1064.5931 | 1181.5952 | 1311.6619 | 1456.2661 | 1617.0474 | 1745.313 | 1745.313 |  | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.071652 | 0.094979 | 0.127 | 0.17115 | 0.23228 | 0.31723 | 0.43567 | 0.6013 | 0.83353 | 1.1599 | 1.6197 | 2.2685 | 3.1858 |  | 102.7467 | 113.3777 | 125.155 | 138.2049 | 152.668 | 168.7004 | 186.4759 | 206.1878 | 228.0509 | 252.3042 | 279.2136 | 309.0748 | 342.2168 | 379.0057 | 419.8488 | 465.1993 | 515.5616 | 571.485 | 633.5944 | 702.5879 | 779.2357 | 864.3944 | 959.0158 | 1064.1574 | 1180.9939 | 1310.8284 | 1455.1061 | 1615.4277 | 1743.0445 | 1742.1273 |  | 2433.3346 | 2688.305 | 2970.7662 | 3283.7495 | 3630.6249 | 4015.1397 | 4441.4608 | 4914.2219 | 5438.5768 | 6020.2577 | 6665.6407 | 7381.819 | 8176.6835 | 9059.0135 | 10038.5776 | 11126.245 | 12334.1113 | 13669.2691 | 15146.8347 | 16785.0171 | 18600.517 | 20611.3735 | 22836.8857 | 25297.4257 | 28014.0909 | 31008.1158 | 34299.9303 | 37907.7012 | 40633.5065 | 40138.0808
| TRUE | 1609 | 22006125 | FB | FB005 | 11 | FB5 | SENSITIVE EF | Blank | English Electric | CMG_1328 | CMG 1328 | CMG | Electromechanical |  | 0.57434 | 2190 |  | 8.25 | 0.0054067 | 0.0038888 | 0.0015179 | 31.8755 | 1244.4067 | 1276.2822 | 37.4249 | 2.2021 | 28.6272 |  | 11.5885 | 0.013521 | 0.0097249 | 0.0037959 | 79.7129 | 3111.9605 | 3191.6734 | 93.5906 | 5.5069 | 71.5896 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.029931 |  | 1344.5364 | 3362.3606 | 46.5175 | 3315.843 |  | 0.03398 |  | 8.5352 | 8.8302 | 9.1354 | 9.4511 | 9.7778 | 10.1158 | 10.4654 | 10.8271 | 11.2014 | 11.5885 | 11.9891 | 12.4035 | 12.8322 | 13.2757 | 13.7346 | 14.2093 | 14.7004 | 15.2085 | 15.7342 | 16.278 | 16.8407 | 17.4227 | 18.0249 | 18.6479 | 19.2925 | 19.9593 | 20.6492 | 21.3629 | 22.1013 | 22.8652 |  | 0.0059156 | 0.0064751 | 0.0070903 | 0.007767 | 0.0085115 | 0.0093307 | 0.010232 | 0.011225 | 0.012317 | 0.013521 | 0.014846 | 0.016306 | 0.017915 | 0.019688 | 0.021642 | 0.023795 | 0.02617 | 0.028788 | 0.031676 | 0.034861 | 0.038374 | 0.042249 | 0.046526 | 0.051245 | 0.056453 | 0.062201 | 0.068547 | 0.075552 | 0.083287 | 0.091827 |  | 0.0042548 | 0.0046572 | 0.0050997 | 0.0055865 | 0.0061219 | 0.0067111 | 0.0073596 | 0.0080734 | 0.0088594 | 0.0097249 | 0.010678 | 0.011728 | 0.012885 | 0.01416 | 0.015566 | 0.017115 | 0.018823 | 0.020706 | 0.022783 | 0.025074 | 0.0276 | 0.030388 | 0.033464 | 0.036858 | 0.040604 | 0.044739 | 0.049303 | 0.054341 | 0.059904 | 0.066047 | 1471.0937 | 1610.2294 | 1763.2291 | 1931.5121 | 2116.6455 | 2320.3597 | 2544.5655 | 2791.3731 | 3063.1133 | 3362.3606 | 3691.9588 | 4055.0499 | 4455.1049 | 4895.9593 | 5381.851 | 5917.4633 | 6507.9719 | 7159.097 | 7877.1609 | 8669.1522 | 9542.7958 | 10506.6315 | 11570.1005 | 12743.6407 | 14038.7926 | 15468.3169 | 17046.3235 | 18788.4153 | 20711.8468 | 22835.6998 |  | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 38.6813 | 51.2743 | 68.5607 | 92.3965 | 125.3975 | 171.2565 | 235.1955 | 324.6089 | 449.9813 | 626.1957 | 874.4 | 1224.6726 | 1719.8282 |  | 34.8758 | 38.1744 | 41.8016 | 45.7912 | 50.1802 | 55.0097 | 60.3251 | 66.1763 | 72.6185 | 79.7129 | 87.5268 | 96.1348 | 105.619 | 116.0706 | 127.5898 | 140.2878 | 154.2872 | 169.7237 | 186.7472 | 205.5232 | 226.2351 | 249.0851 | 274.2972 | 302.1189 | 332.8236 | 366.7139 | 404.1244 | 445.4249 | 491.0245 | 541.3756 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 20.6629 | 23.9614 | 27.5887 | 31.5782 | 35.9673 | 40.7968 | 46.1121 | 51.9633 | 58.4056 | 65.5 | 73.3139 | 81.9218 | 91.4061 | 101.8576 | 113.3769 | 126.0749 | 140.0743 | 152.7117 | 164.1968 | 175.3703 | 185.5991 | 193.9354 | 198.9787 | 198.68 | 190.0608 | 168.8124 | 128.7239 | 60.8643 | -47.5858 | -215.0038 |  | 1361.5392 | 1490.3132 | 1631.9188 | 1787.6695 | 1959.0158 | 2147.5591 | 2355.0679 | 2583.4953 | 2834.9986 | 3111.9605 | 3417.0131 | 3753.0642 | 4123.3265 | 4531.3498 | 4981.0564 | 5476.7809 | 6023.3134 | 6625.9482 | 7290.5369 | 8023.5473 | 8832.1293 | 9724.1868 | 10708.4577 | 11794.6025 | 12993.3025 | 14316.368 | 15776.8581 | 17389.2136 | 19169.4043 | 21135.0908 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 1360.2381 | 1489.0121 | 1630.6177 | 1786.3684 | 1957.7147 | 2146.258 | 2353.7668 | 2582.1942 | 2833.6975 | 3110.6594 | 3415.712 | 3751.7631 | 4122.0254 | 4530.0487 | 4979.7553 | 5475.4798 | 6022.0123 | 6624.3909 | 7288.4725 | 8020.787 | 8828.4094 | 9719.1382 | 10701.5627 | 11785.1334 | 12980.2336 | 14298.2514 | 15751.647 | 17354.0097 | 19120.0981 | 21065.8493 |  | 1380.9009 | 1512.9735 | 1658.2063 | 1817.9466 | 1993.6819 | 2187.0548 | 2399.8789 | 2634.1576 | 2892.1031 | 3176.1593 | 3489.0258 | 3833.6849 | 4213.4315 | 4631.9063 | 5093.1322 | 5601.5546 | 6162.0866 | 6777.1026 | 7452.6693 | 8196.1573 | 9014.0085 | 9913.0736 | 10900.5415 | 11983.8134 | 13170.2943 | 14467.0638 | 15880.3709 | 17414.8739 | 19072.5122 | 20850.8454 |  | 40.9476 | 44.8204 | 49.0791 | 53.7633 | 58.9164 | 64.5868 | 70.8275 | 77.6973 | 85.2612 | 93.5906 | 102.7649 | 112.8715 | 124.007 | 136.2781 | 149.8028 | 164.7114 | 181.1481 | 199.2721 | 219.2592 | 241.3041 | 265.6218 | 292.45 | 322.0515 | 354.7167 | 390.767 | 430.5576 | 474.4811 | 522.9718 | 576.5102 | 635.6272 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 26.2547 | 30.1276 | 34.3863 | 39.0704 | 44.2235 | 49.8939 | 56.1346 | 63.0045 | 70.5683 | 78.8978 | 88.0721 | 98.1786 | 109.3141 | 121.5852 | 135.1099 | 150.0186 | 166.4552 | 181.6856 | 195.9474 | 210.133 | 223.6138 | 235.438 | 244.1897 | 247.7851 | 243.1836 | 225.9735 | 189.7812 | 125.4258 | 19.7127 | -146.2928 |  | 2.4094 | 2.6372 | 2.8878 | 3.1634 | 3.4667 | 3.8003 | 4.1675 | 4.5717 | 5.0168 | 5.5069 | 6.0467 | 6.6414 | 7.2966 | 8.0187 | 8.8144 | 9.6917 | 10.6588 | 11.7252 | 12.9013 | 14.1984 | 15.6293 | 17.2079 | 18.9496 | 20.8717 | 22.9929 | 25.3342 | 27.9186 | 30.7719 | 33.9221 | 37.4005 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.34164 | 0.56952 | 0.8201 | 1.0957 | 1.3989 | 1.7326 | 2.0998 | 2.504 | 2.9491 | 3.4392 | 3.979 | 4.5737 | 5.2289 | 5.9509 | 6.7467 | 7.6239 | 8.5911 | 9.2503 | 9.6206 | 9.8117 | 9.7175 | 9.1846 | 7.9921 | 5.8231 | 2.2234 | -3.457 | -12.1473 | -25.1749 | -44.4362 | -72.6393 |  | 31.3218 | 34.2842 | 37.5418 | 41.1247 | 45.0665 | 49.4039 | 54.1776 | 59.4325 | 65.2182 | 71.5896 | 78.6073 | 86.338 | 94.8558 | 104.2422 | 114.5876 | 125.9915 | 138.5643 | 152.4277 | 167.7164 | 184.579 | 203.1802 | 223.7017 | 246.3445 | 271.3309 | 298.9066 | 329.3433 | 362.9414 | 400.0331 | 440.9858 | 486.2058 |  | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.035826 | 0.047489 | 0.0635 | 0.085576 | 0.11614 | 0.15862 | 0.21783 | 0.30065 | 0.41677 | 0.57997 | 0.80986 | 1.1343 | 1.5929 |  | 31.2918 | 34.2542 | 37.5118 | 41.0948 | 45.0366 | 49.374 | 54.1476 | 59.4025 | 65.1883 | 71.5597 | 78.5773 | 86.3081 | 94.8258 | 104.2123 | 114.5576 | 125.9616 | 138.5344 | 152.3919 | 167.6689 | 184.5155 | 203.0946 | 223.5856 | 246.1859 | 271.1131 | 298.606 | 328.9265 | 362.3614 | 399.2232 | 439.8515 | 484.6129 |  | 1438.7892 | 1577.9248 | 1730.9245 | 1899.2075 | 2084.341 | 2288.0552 | 2512.2609 | 2759.0685 | 3030.8087 | 3330.056 | 3659.6542 | 4022.7453 | 4422.8003 | 4863.6547 | 5349.5464 | 5885.1587 | 6475.6673 | 7120.4304 | 7825.9061 | 8600.6175 | 9450.4344 | 10381.2817 | 11398.9092 | 12508.5347 | 13714.3073 | 15018.5068 | 16420.3662 | 17914.3481 | 19487.6402 | 21116.5262
| TRUE | 1610 | 22006126 | FB | FB005 | 11 | FB5 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 46.604 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 126.182 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.029931 |  | 2188.8588 | 5926.4102 | 46.5175 | 5879.8927 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2414.2658 | 2663.9207 | 2940.4933 | 3246.9516 | 3586.5955 | 3963.0941 | 4380.5274 | 4843.4326 | 5356.8559 | 5926.4102 | 6558.3385 | 7259.5862 | 8037.8797 | 8901.8153 | 9860.9577 | 10925.9499 | 12108.6351 | 13422.1932 | 14881.2923 | 16502.2578 | 18303.2605 | 20304.5261 | 22528.5692 | 25000.453 | 27748.0794 | 30802.5117 | 34198.3346 | 37974.0546 | 40986.1908 | 40986.1908 |  | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 38.6813 | 51.2743 | 68.5607 | 92.3965 | 125.3975 | 171.2565 | 235.1955 | 324.6089 | 449.9813 | 626.1957 | 874.4 | 1224.6726 | 1719.8282 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 51.4033 | 56.7188 | 62.6074 | 69.1324 | 76.3639 | 84.3801 | 93.2679 | 103.1238 | 114.0554 | 126.182 | 139.6367 | 154.5673 | 171.1383 | 189.5328 | 209.9543 | 232.6296 | 257.8107 | 285.7783 | 316.8447 | 351.3574 | 389.7034 | 432.3133 | 479.6665 | 532.2966 | 590.7976 | 655.8309 | 728.133 | 808.5237 | 872.6565 | 872.6565 |  | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.035826 | 0.047489 | 0.0635 | 0.085576 | 0.11614 | 0.15862 | 0.21783 | 0.30065 | 0.41677 | 0.57997 | 0.80986 | 1.1343 | 1.5929 |  | 51.3734 | 56.6889 | 62.5775 | 69.1025 | 76.334 | 84.3502 | 93.238 | 103.0939 | 114.0254 | 126.1521 | 139.6068 | 154.5374 | 171.1084 | 189.5029 | 209.9244 | 232.5997 | 257.7808 | 285.7425 | 316.7972 | 351.2939 | 389.6179 | 432.1972 | 479.5079 | 532.0787 | 590.4969 | 655.4142 | 727.5531 | 807.7138 | 871.5222 | 871.0636 |  | 2381.9612 | 2631.6161 | 2908.1887 | 3214.647 | 3554.2909 | 3930.7895 | 4348.2228 | 4811.128 | 5324.5514 | 5894.1056 | 6526.034 | 7227.2816 | 8005.5751 | 8869.5107 | 9828.6531 | 10893.6453 | 12076.3305 | 13383.5267 | 14830.0375 | 16433.7232 | 18210.8991 | 20179.1763 | 22357.3778 | 24765.347 | 27423.594 | 30352.7016 | 33572.3772 | 37099.9874 | 39761.9842 | 39267.0172
| TRUE | 1611 | 22006127 | FB | FB005 | 11 | FB5 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 46.604 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 126.182 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.029931 |  | 2188.8588 | 5926.4102 | 46.5175 | 5879.8927 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2414.2658 | 2663.9207 | 2940.4933 | 3246.9516 | 3586.5955 | 3963.0941 | 4380.5274 | 4843.4326 | 5356.8559 | 5926.4102 | 6558.3385 | 7259.5862 | 8037.8797 | 8901.8153 | 9860.9577 | 10925.9499 | 12108.6351 | 13422.1932 | 14881.2923 | 16502.2578 | 18303.2605 | 20304.5261 | 22528.5692 | 25000.453 | 27748.0794 | 30802.5117 | 34198.3346 | 37974.0546 | 40986.1908 | 40986.1908 |  | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 32.3169 | 38.6813 | 51.2743 | 68.5607 | 92.3965 | 125.3975 | 171.2565 | 235.1955 | 324.6089 | 449.9813 | 626.1957 | 874.4 | 1224.6726 | 1719.8282 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 51.4033 | 56.7188 | 62.6074 | 69.1324 | 76.3639 | 84.3801 | 93.2679 | 103.1238 | 114.0554 | 126.182 | 139.6367 | 154.5673 | 171.1383 | 189.5328 | 209.9543 | 232.6296 | 257.8107 | 285.7783 | 316.8447 | 351.3574 | 389.7034 | 432.3133 | 479.6665 | 532.2966 | 590.7976 | 655.8309 | 728.133 | 808.5237 | 872.6565 | 872.6565 |  | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.029931 | 0.035826 | 0.047489 | 0.0635 | 0.085576 | 0.11614 | 0.15862 | 0.21783 | 0.30065 | 0.41677 | 0.57997 | 0.80986 | 1.1343 | 1.5929 |  | 51.3734 | 56.6889 | 62.5775 | 69.1025 | 76.334 | 84.3502 | 93.238 | 103.0939 | 114.0254 | 126.1521 | 139.6068 | 154.5374 | 171.1084 | 189.5029 | 209.9244 | 232.5997 | 257.7808 | 285.7425 | 316.7972 | 351.2939 | 389.6179 | 432.1972 | 479.5079 | 532.0787 | 590.4969 | 655.4142 | 727.5531 | 807.7138 | 871.5222 | 871.0636 |  | 2381.9612 | 2631.6161 | 2908.1887 | 3214.647 | 3554.2909 | 3930.7895 | 4348.2228 | 4811.128 | 5324.5514 | 5894.1056 | 6526.034 | 7227.2816 | 8005.5751 | 8869.5107 | 9828.6531 | 10893.6453 | 12076.3305 | 13383.5267 | 14830.0375 | 16433.7232 | 18210.8991 | 20179.1763 | 22357.3778 | 24765.347 | 27423.594 | 30352.7016 | 33572.3772 | 37099.9874 | 39761.9842 | 39267.0172
| TRUE | 1612 | 22006128 | FB | FB006 | 11 | FB6 | SENSITIVE EF | Blank | English Electric | CMG_1328 | CMG 1328 | CMG | Electromechanical |  | 0.57434 | 2190 |  | 8.25 | 0.0054067 | 0.0038888 | 0.0015179 | 31.8755 | 1244.4067 | 1276.2822 | 37.4249 | 2.2021 | 57.2543 |  | 11.5885 | 0.013521 | 0.0097249 | 0.0037959 | 79.7129 | 3111.9605 | 3191.6734 | 93.5906 | 5.5069 | 143.1792 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.059863 |  | 1373.1635 | 3433.9502 | 46.5474 | 3387.4027 |  | 0.03398 |  | 8.5352 | 8.8302 | 9.1354 | 9.4511 | 9.7778 | 10.1158 | 10.4654 | 10.8271 | 11.2014 | 11.5885 | 11.9891 | 12.4035 | 12.8322 | 13.2757 | 13.7346 | 14.2093 | 14.7004 | 15.2085 | 15.7342 | 16.278 | 16.8407 | 17.4227 | 18.0249 | 18.6479 | 19.2925 | 19.9593 | 20.6492 | 21.3629 | 22.1013 | 22.8652 |  | 0.0059156 | 0.0064751 | 0.0070903 | 0.007767 | 0.0085115 | 0.0093307 | 0.010232 | 0.011225 | 0.012317 | 0.013521 | 0.014846 | 0.016306 | 0.017915 | 0.019688 | 0.021642 | 0.023795 | 0.02617 | 0.028788 | 0.031676 | 0.034861 | 0.038374 | 0.042249 | 0.046526 | 0.051245 | 0.056453 | 0.062201 | 0.068547 | 0.075552 | 0.083287 | 0.091827 |  | 0.0042548 | 0.0046572 | 0.0050997 | 0.0055865 | 0.0061219 | 0.0067111 | 0.0073596 | 0.0080734 | 0.0088594 | 0.0097249 | 0.010678 | 0.011728 | 0.012885 | 0.01416 | 0.015566 | 0.017115 | 0.018823 | 0.020706 | 0.022783 | 0.025074 | 0.0276 | 0.030388 | 0.033464 | 0.036858 | 0.040604 | 0.044739 | 0.049303 | 0.054341 | 0.059904 | 0.066047 | 1502.4155 | 1644.5136 | 1800.7709 | 1972.6369 | 2161.7121 | 2369.7636 | 2598.7431 | 2850.8056 | 3128.3315 | 3433.9502 | 3770.5661 | 4141.3879 | 4549.9607 | 5000.2015 | 5496.4385 | 6043.4548 | 6646.5363 | 7311.5247 | 8044.8773 | 8853.7312 | 9745.976 | 10730.3332 | 11816.445 | 13014.9716 | 14337.6993 | 15797.6602 | 17409.2649 | 19188.4484 | 21152.8326 | 23321.9056 |  | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 38.7171 | 51.3218 | 68.6242 | 92.4821 | 125.5137 | 171.4152 | 235.4133 | 324.9096 | 450.3981 | 626.7756 | 875.2098 | 1225.8069 | 1721.421 |  | 34.8758 | 38.1744 | 41.8016 | 45.7912 | 50.1802 | 55.0097 | 60.3251 | 66.1763 | 72.6185 | 79.7129 | 87.5268 | 96.1348 | 105.619 | 116.0706 | 127.5898 | 140.2878 | 154.2872 | 169.7237 | 186.7472 | 205.5232 | 226.2351 | 249.0851 | 274.2972 | 302.1189 | 332.8236 | 366.7139 | 404.1244 | 445.4249 | 491.0245 | 541.3756 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 20.6629 | 23.9614 | 27.5887 | 31.5782 | 35.9673 | 40.7968 | 46.1121 | 51.9633 | 58.4056 | 65.5 | 73.3139 | 81.9218 | 91.4061 | 101.8576 | 113.3769 | 126.0749 | 140.0743 | 152.7117 | 164.1968 | 175.3703 | 185.5991 | 193.9354 | 198.9787 | 198.68 | 190.0608 | 168.8124 | 128.7239 | 60.8643 | -47.5858 | -215.0038 |  | 1361.5392 | 1490.3132 | 1631.9188 | 1787.6695 | 1959.0158 | 2147.5591 | 2355.0679 | 2583.4953 | 2834.9986 | 3111.9605 | 3417.0131 | 3753.0642 | 4123.3265 | 4531.3498 | 4981.0564 | 5476.7809 | 6023.3134 | 6625.9482 | 7290.5369 | 8023.5473 | 8832.1293 | 9724.1868 | 10708.4577 | 11794.6025 | 12993.3025 | 14316.368 | 15776.8581 | 17389.2136 | 19169.4043 | 21135.0908 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 1360.2381 | 1489.0121 | 1630.6177 | 1786.3684 | 1957.7147 | 2146.258 | 2353.7668 | 2582.1942 | 2833.6975 | 3110.6594 | 3415.712 | 3751.7631 | 4122.0254 | 4530.0487 | 4979.7553 | 5475.4798 | 6022.0123 | 6624.3909 | 7288.4725 | 8020.787 | 8828.4094 | 9719.1382 | 10701.5627 | 11785.1334 | 12980.2336 | 14298.2514 | 15751.647 | 17354.0097 | 19120.0981 | 21065.8493 |  | 1380.9009 | 1512.9735 | 1658.2063 | 1817.9466 | 1993.6819 | 2187.0548 | 2399.8789 | 2634.1576 | 2892.1031 | 3176.1593 | 3489.0258 | 3833.6849 | 4213.4315 | 4631.9063 | 5093.1322 | 5601.5546 | 6162.0866 | 6777.1026 | 7452.6693 | 8196.1573 | 9014.0085 | 9913.0736 | 10900.5415 | 11983.8134 | 13170.2943 | 14467.0638 | 15880.3709 | 17414.8739 | 19072.5122 | 20850.8454 |  | 40.9476 | 44.8204 | 49.0791 | 53.7633 | 58.9164 | 64.5868 | 70.8275 | 77.6973 | 85.2612 | 93.5906 | 102.7649 | 112.8715 | 124.007 | 136.2781 | 149.8028 | 164.7114 | 181.1481 | 199.2721 | 219.2592 | 241.3041 | 265.6218 | 292.45 | 322.0515 | 354.7167 | 390.767 | 430.5576 | 474.4811 | 522.9718 | 576.5102 | 635.6272 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 26.2547 | 30.1276 | 34.3863 | 39.0704 | 44.2235 | 49.8939 | 56.1346 | 63.0045 | 70.5683 | 78.8978 | 88.0721 | 98.1786 | 109.3141 | 121.5852 | 135.1099 | 150.0186 | 166.4552 | 181.6856 | 195.9474 | 210.133 | 223.6138 | 235.438 | 244.1897 | 247.7851 | 243.1836 | 225.9735 | 189.7812 | 125.4258 | 19.7127 | -146.2928 |  | 2.4094 | 2.6372 | 2.8878 | 3.1634 | 3.4667 | 3.8003 | 4.1675 | 4.5717 | 5.0168 | 5.5069 | 6.0467 | 6.6414 | 7.2966 | 8.0187 | 8.8144 | 9.6917 | 10.6588 | 11.7252 | 12.9013 | 14.1984 | 15.6293 | 17.2079 | 18.9496 | 20.8717 | 22.9929 | 25.3342 | 27.9186 | 30.7719 | 33.9221 | 37.4005 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.34164 | 0.56952 | 0.8201 | 1.0957 | 1.3989 | 1.7326 | 2.0998 | 2.504 | 2.9491 | 3.4392 | 3.979 | 4.5737 | 5.2289 | 5.9509 | 6.7467 | 7.6239 | 8.5911 | 9.2503 | 9.6206 | 9.8117 | 9.7175 | 9.1846 | 7.9921 | 5.8231 | 2.2234 | -3.457 | -12.1473 | -25.1749 | -44.4362 | -72.6393 |  | 62.6435 | 68.5683 | 75.0835 | 82.2495 | 90.133 | 98.8078 | 108.3551 | 118.8649 | 130.4364 | 143.1792 | 157.2145 | 172.676 | 189.7115 | 208.4844 | 229.1751 | 251.9831 | 277.1287 | 304.8555 | 335.4328 | 369.1581 | 406.3604 | 447.4034 | 492.689 | 542.6618 | 597.8132 | 658.6866 | 725.8828 | 800.0662 | 881.9716 | 972.4115 |  | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.071652 | 0.094979 | 0.127 | 0.17115 | 0.23228 | 0.31723 | 0.43567 | 0.6013 | 0.83353 | 1.1599 | 1.6197 | 2.2685 | 3.1858 |  | 62.5837 | 68.5085 | 75.0236 | 82.1896 | 90.0732 | 98.7479 | 108.2952 | 118.805 | 130.3765 | 143.1194 | 157.1546 | 172.6161 | 189.6517 | 208.4245 | 229.1152 | 251.9232 | 277.0688 | 304.7838 | 335.3378 | 369.0311 | 406.1893 | 447.1711 | 492.3718 | 542.2262 | 597.2119 | 657.8531 | 724.7228 | 798.4465 | 879.703 | 969.2258 |  | 1470.081 | 1612.1791 | 1768.4363 | 1940.3024 | 2129.3776 | 2337.4291 | 2566.4086 | 2818.4711 | 3095.997 | 3401.6157 | 3738.2315 | 4109.0533 | 4517.6262 | 4967.867 | 5464.104 | 6011.1203 | 6614.2017 | 7272.8224 | 7993.575 | 8785.1331 | 9653.529 | 10604.8673 | 11645.0951 | 12779.6478 | 14012.9132 | 15347.4334 | 16782.7276 | 18313.5713 | 19927.4918 | 21601.1391
| TRUE | 1613 | 22006129 | FB | FB006 | 11 | FB6 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 93.2081 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 252.364 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.059863 |  | 2235.4629 | 6052.5922 | 46.5474 | 6006.0447 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2465.6691 | 2720.6395 | 3003.1007 | 3316.084 | 3662.9594 | 4047.4742 | 4473.7953 | 4946.5564 | 5470.9113 | 6052.5922 | 6697.9752 | 7414.1535 | 8209.018 | 9091.348 | 10070.9121 | 11158.5795 | 12366.4458 | 13707.9715 | 15198.137 | 16853.6153 | 18692.9639 | 20736.8394 | 23008.2357 | 25532.7496 | 28338.877 | 31458.3427 | 34926.4676 | 38782.5782 | 41858.8473 | 41858.8473 |  | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 38.7171 | 51.3218 | 68.6242 | 92.4821 | 125.5137 | 171.4152 | 235.4133 | 324.9096 | 450.3981 | 626.7756 | 875.2098 | 1225.8069 | 1721.421 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 102.8066 | 113.4376 | 125.2149 | 138.2648 | 152.7278 | 168.7602 | 186.5358 | 206.2477 | 228.1107 | 252.364 | 279.2734 | 309.1346 | 342.2766 | 379.0656 | 419.9087 | 465.2592 | 515.6214 | 571.5566 | 633.6894 | 702.7149 | 779.4069 | 864.6267 | 959.333 | 1064.5931 | 1181.5952 | 1311.6619 | 1456.2661 | 1617.0474 | 1745.313 | 1745.313 |  | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.071652 | 0.094979 | 0.127 | 0.17115 | 0.23228 | 0.31723 | 0.43567 | 0.6013 | 0.83353 | 1.1599 | 1.6197 | 2.2685 | 3.1858 |  | 102.7467 | 113.3777 | 125.155 | 138.2049 | 152.668 | 168.7004 | 186.4759 | 206.1878 | 228.0509 | 252.3042 | 279.2136 | 309.0748 | 342.2168 | 379.0057 | 419.8488 | 465.1993 | 515.5616 | 571.485 | 633.5944 | 702.5879 | 779.2357 | 864.3944 | 959.0158 | 1064.1574 | 1180.9939 | 1310.8284 | 1455.1061 | 1615.4277 | 1743.0445 | 1742.1273 |  | 2433.3346 | 2688.305 | 2970.7662 | 3283.7495 | 3630.6249 | 4015.1397 | 4441.4608 | 4914.2219 | 5438.5768 | 6020.2577 | 6665.6407 | 7381.819 | 8176.6835 | 9059.0135 | 10038.5776 | 11126.245 | 12334.1113 | 13669.2691 | 15146.8347 | 16785.0171 | 18600.517 | 20611.3735 | 22836.8857 | 25297.4257 | 28014.0909 | 31008.1158 | 34299.9303 | 37907.7012 | 40633.5065 | 40138.0808
| TRUE | 1614 | 22006130 | FB | FB006 | 11 | FB6 | OVERCURRENT | Blank | Brown Boveri | ICM21_1058 | ICM21 1058 | ICM21 | Electromechanical |  | 0.57434 | 2190 |  | 9.9 | 0.0088019 | 0.0063308 | 0.0024711 | 51.8922 | 2025.8512 | 2077.7434 | 60.9265 | 3.5849 | 93.2081 |  | 14.217 | 0.023831 | 0.017141 | 0.0066905 | 140.4999 | 5485.0615 | 5625.5614 | 164.9605 | 9.7063 | 252.364 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.059863 |  | 2235.4629 | 6052.5922 | 46.5474 | 6006.0447 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0069827 | 0.0077048 | 0.0085047 | 0.0093911 | 0.010373 | 0.011462 | 0.01267 | 0.014009 | 0.015494 | 0.017141 | 0.018969 | 0.020997 | 0.023248 | 0.025747 | 0.028521 | 0.031601 | 0.035022 | 0.038821 | 0.043041 | 0.047729 | 0.052938 | 0.058726 | 0.065159 | 0.072308 | 0.080255 | 0.089089 | 0.098911 | 0.10983 | 0.11854 | 0.11854 | 2465.6691 | 2720.6395 | 3003.1007 | 3316.084 | 3662.9594 | 4047.4742 | 4473.7953 | 4946.5564 | 5470.9113 | 6052.5922 | 6697.9752 | 7414.1535 | 8209.018 | 9091.348 | 10070.9121 | 11158.5795 | 12366.4458 | 13707.9715 | 15198.137 | 16853.6153 | 18692.9639 | 20736.8394 | 23008.2357 | 25532.7496 | 28338.877 | 31458.3427 | 34926.4676 | 38782.5782 | 41858.8473 | 41858.8473 |  | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 32.3468 | 38.7171 | 51.3218 | 68.6242 | 92.4821 | 125.5137 | 171.4152 | 235.4133 | 324.9096 | 450.3981 | 626.7756 | 875.2098 | 1225.8069 | 1721.421 |  | 57.236 | 63.1547 | 69.7115 | 76.9768 | 85.0289 | 93.9547 | 103.851 | 114.8253 | 126.9972 | 140.4999 | 155.4813 | 172.1061 | 190.5574 | 211.0391 | 233.7779 | 259.0261 | 287.0645 | 318.2056 | 352.7971 | 391.226 | 433.9231 | 481.3679 | 534.0943 | 592.6963 | 657.8354 | 730.2481 | 810.7543 | 900.2669 | 971.6769 | 971.6769 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 43.0231 | 48.9417 | 55.4986 | 62.7639 | 70.816 | 79.7418 | 89.6381 | 100.6124 | 112.7843 | 126.287 | 141.2684 | 157.8931 | 176.3445 | 196.8261 | 219.5649 | 244.8132 | 272.8516 | 301.1936 | 330.2466 | 361.073 | 393.2872 | 426.2182 | 458.7757 | 489.2574 | 515.0726 | 532.3466 | 535.3538 | 515.7063 | 433.0666 | 215.2975 |  | 2234.4718 | 2465.5345 | 2721.5103 | 3005.1462 | 3319.4963 | 3667.9565 | 4054.3029 | 4482.7348 | 4957.9228 | 5485.0615 | 6069.9292 | 6718.9539 | 7439.2866 | 8238.8836 | 9126.5973 | 10112.2779 | 11206.8868 | 12422.6222 | 13773.06 | 15273.3098 | 16940.189 | 18792.4174 | 20850.8326 | 23138.6315 | 25681.638 | 28508.6021 | 31651.5329 | 35146.0694 | 37933.8872 | 37933.8872 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 2233.1707 | 2464.2334 | 2720.2092 | 3003.8451 | 3318.1952 | 3666.6554 | 4053.0018 | 4481.4337 | 4956.6217 | 5483.7604 | 6068.6281 | 6717.6528 | 7437.9855 | 8237.5825 | 9125.2962 | 10110.9768 | 11205.5857 | 12421.0649 | 13770.9957 | 15270.5494 | 16936.4691 | 18787.3688 | 20843.9377 | 23129.1624 | 25668.569 | 28490.4856 | 31626.3219 | 35110.8654 | 37884.581 | 37864.6457 |  | 2276.1938 | 2513.1751 | 2775.7077 | 3066.609 | 3389.0112 | 3746.3972 | 4142.6399 | 4582.0461 | 5069.406 | 5610.0473 | 6209.8964 | 6875.5459 | 7614.33 | 8434.4087 | 9344.8611 | 10355.79 | 11478.4372 | 12722.2585 | 14101.2423 | 15631.6225 | 17329.7562 | 19213.587 | 21302.7135 | 23618.4198 | 26183.6416 | 29022.8322 | 32161.6757 | 35626.5717 | 38317.6476 | 38079.9432 |  | 67.2006 | 74.1497 | 81.8481 | 90.3783 | 99.8322 | 110.3119 | 121.9311 | 134.816 | 149.107 | 164.9605 | 182.5501 | 202.0692 | 223.7328 | 247.7803 | 274.4778 | 304.1217 | 337.0415 | 373.6041 | 414.2178 | 459.3371 | 509.4677 | 565.1725 | 627.0783 | 695.8827 | 772.3623 | 857.3819 | 951.9039 | 1057.0003 | 1140.8426 | 1140.8426 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 52.5077 | 59.4568 | 67.1552 | 75.6854 | 85.1393 | 95.6191 | 107.2382 | 120.1231 | 134.4142 | 150.2676 | 167.8572 | 187.3763 | 209.0399 | 233.0874 | 259.7849 | 289.4288 | 322.3486 | 356.0177 | 390.906 | 428.166 | 467.4596 | 508.1605 | 549.2165 | 588.951 | 624.7789 | 652.7978 | 667.204 | 659.4543 | 584.0451 | 358.9226 |  | 3.9541 | 4.363 | 4.816 | 5.3179 | 5.8742 | 6.4908 | 7.1745 | 7.9326 | 8.7735 | 9.7063 | 10.7413 | 11.8898 | 13.1645 | 14.5795 | 16.1504 | 17.8946 | 19.8316 | 21.983 | 24.3727 | 27.0276 | 29.9773 | 33.255 | 36.8975 | 40.946 | 45.4461 | 50.4487 | 56.0104 | 62.1943 | 67.1276 | 67.1276 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 1.8864 | 2.2953 | 2.7482 | 3.2502 | 3.8064 | 4.4231 | 5.1067 | 5.8649 | 6.7058 | 7.6386 | 8.6736 | 9.8221 | 11.0968 | 12.5117 | 14.0826 | 15.8269 | 17.7639 | 19.5081 | 21.092 | 22.6408 | 24.0655 | 25.2316 | 25.94 | 25.8975 | 24.6766 | 21.6575 | 15.9445 | 6.2475 | -11.2307 | -42.9122 |  | 102.8066 | 113.4376 | 125.2149 | 138.2648 | 152.7278 | 168.7602 | 186.5358 | 206.2477 | 228.1107 | 252.364 | 279.2734 | 309.1346 | 342.2766 | 379.0656 | 419.9087 | 465.2592 | 515.6214 | 571.5566 | 633.6894 | 702.7149 | 779.4069 | 864.6267 | 959.333 | 1064.5931 | 1181.5952 | 1311.6619 | 1456.2661 | 1617.0474 | 1745.313 | 1745.313 |  | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.059863 | 0.071652 | 0.094979 | 0.127 | 0.17115 | 0.23228 | 0.31723 | 0.43567 | 0.6013 | 0.83353 | 1.1599 | 1.6197 | 2.2685 | 3.1858 |  | 102.7467 | 113.3777 | 125.155 | 138.2049 | 152.668 | 168.7004 | 186.4759 | 206.1878 | 228.0509 | 252.3042 | 279.2136 | 309.0748 | 342.2168 | 379.0057 | 419.8488 | 465.1993 | 515.5616 | 571.485 | 633.5944 | 702.5879 | 779.2357 | 864.3944 | 959.0158 | 1064.1574 | 1180.9939 | 1310.8284 | 1455.1061 | 1615.4277 | 1743.0445 | 1742.1273 |  | 2433.3346 | 2688.305 | 2970.7662 | 3283.7495 | 3630.6249 | 4015.1397 | 4441.4608 | 4914.2219 | 5438.5768 | 6020.2577 | 6665.6407 | 7381.819 | 8176.6835 | 9059.0135 | 10038.5776 | 11126.245 | 12334.1113 | 13669.2691 | 15146.8347 | 16785.0171 | 18600.517 | 20611.3735 | 22836.8857 | 25297.4257 | 28014.0909 | 31008.1158 | 34299.9303 | 37907.7012 | 40633.5065 | 40138.0808
| TRUE | 1615 | 22015777 | FB | FB009 | 11 | FB9 | CURRENT INTERLOCK | Blank | English Electric | CAG39_1012 | CAG39 1012 | CAG | Electromechanical |  | 0.57434 | 2190 |  | 5.5 | 0.0019187 | 0.0013801 | 0.00053868 | 11.3121 | 441.6215 | 452.9336 | 13.2815 | 0.78149 | 26.4789 |  | 7.3552 | 0.0040026 | 0.0028789 | 0.0011237 | 23.5976 | 921.2421 | 944.8397 | 27.7059 | 1.6302 | 55.2362 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 493.4756 | 1029.4121 | 46.5656 | 982.8465 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0.0014826 | 0.0015934 | 0.0017133 | 0.0018429 | 0.0019832 | 0.0021351 | 0.0022994 | 0.0024774 | 0.0026701 | 0.0028789 | 0.0031051 | 0.0033501 | 0.0036158 | 0.0039037 | 0.0042159 | 0.0045544 | 0.0049216 | 0.0053199 | 0.005752 | 0.0062209 | 0.0067298 | 0.0072822 | 0.0078819 | 0.008533 | 0.00924 | 0.010008 | 0.010842 | 0.011748 | 0.012732 | 0.013802 | 530.1273 | 569.7568 | 612.6165 | 658.9808 | 709.1476 | 763.4413 | 822.2143 | 885.8499 | 954.7647 | 1029.4121 | 1110.285 | 1197.9197 | 1292.8997 | 1395.8594 | 1507.4896 | 1628.5415 | 1759.8328 | 1902.2533 | 2056.7715 | 2224.4413 | 2406.4102 | 2603.9272 | 2818.3518 | 3051.1644 | 3303.9767 | 3578.5436 | 3876.776 | 4200.7548 | 4552.7463 | 4935.2183 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 12.1523 | 13.0608 | 14.0433 | 15.1061 | 16.2561 | 17.5007 | 18.8479 | 20.3067 | 21.8865 | 23.5976 | 25.4515 | 27.4604 | 29.6377 | 31.9978 | 34.5568 | 37.3317 | 40.3414 | 43.6061 | 47.1482 | 50.9918 | 55.1631 | 59.6909 | 64.6062 | 69.9431 | 75.7384 | 82.0324 | 88.8689 | 96.2956 | 104.3644 | 113.132 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | -2.0606 | -1.1522 | -0.16969 | 0.89314 | 2.0431 | 3.2877 | 4.635 | 6.0937 | 7.6735 | 9.3847 | 11.2386 | 13.2475 | 15.4247 | 17.7849 | 20.3438 | 23.1188 | 26.1284 | 26.5941 | 24.5978 | 20.8388 | 14.5272 | 4.5411 | -10.7123 | -33.4958 | -67.0244 | -115.8691 | -186.5316 | -288.265 | -434.2459 | -643.2474 |  | 474.4218 | 509.8871 | 548.2432 | 589.7355 | 634.6309 | 683.2194 | 735.8166 | 792.7653 | 854.4386 | 921.2421 | 993.617 | 1072.0431 | 1157.0426 | 1249.1834 | 1349.0835 | 1457.4154 | 1574.9107 | 1702.3658 | 1840.6473 | 1990.6985 | 2153.5462 | 2330.3082 | 2522.2012 | 2730.55 | 2956.7969 | 3202.5125 | 3469.4069 | 3759.3422 | 4074.3466 | 4416.6288 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 473.1207 | 508.586 | 546.9421 | 588.4344 | 633.3298 | 681.9183 | 734.5155 | 791.4642 | 853.1375 | 919.941 | 992.3159 | 1070.742 | 1155.7415 | 1247.8823 | 1347.7824 | 1456.1143 | 1573.6096 | 1700.8084 | 1838.5829 | 1987.9382 | 2149.8263 | 2325.2596 | 2515.3063 | 2721.0809 | 2943.728 | 3184.396 | 3444.1958 | 3724.1382 | 4025.0404 | 4347.3873 |  | 471.0601 | 507.4339 | 546.7724 | 589.3275 | 635.3729 | 685.206 | 739.1505 | 797.558 | 860.811 | 929.3257 | 1003.5544 | 1083.9894 | 1171.1662 | 1265.6672 | 1368.1263 | 1479.2331 | 1599.738 | 1727.4025 | 1863.1807 | 2008.777 | 2164.3534 | 2329.8007 | 2504.594 | 2687.5851 | 2876.7035 | 3068.5268 | 3257.6642 | 3435.8732 | 3590.7946 | 3704.1398 |  | 14.268 | 15.3346 | 16.4881 | 17.736 | 19.0862 | 20.5475 | 22.1293 | 23.842 | 25.6968 | 27.7059 | 29.8825 | 32.2412 | 34.7975 | 37.5686 | 40.573 | 43.831 | 47.3646 | 51.1978 | 55.3565 | 59.8693 | 64.7668 | 70.0828 | 75.8539 | 82.1199 | 88.9242 | 96.314 | 104.3407 | 113.0603 | 122.5339 | 132.8279 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | -0.42487 | 0.64173 | 1.7953 | 3.0431 | 4.3933 | 5.8546 | 7.4364 | 9.1491 | 11.0039 | 13.013 | 15.1897 | 17.5483 | 20.1046 | 22.8757 | 25.8801 | 29.1382 | 32.6718 | 33.6113 | 32.0447 | 28.6981 | 22.7587 | 13.0709 | -2.0079 | -24.8117 | -58.6593 | -108.2701 | -180.3592 | -284.4857 | -434.2636 | -649.0921 |  | 0.83953 | 0.90229 | 0.97017 | 1.0436 | 1.123 | 1.209 | 1.3021 | 1.4029 | 1.512 | 1.6302 | 1.7583 | 1.8971 | 2.0475 | 2.2105 | 2.3873 | 2.579 | 2.787 | 3.0125 | 3.2572 | 3.5227 | 3.8109 | 4.1237 | 4.4633 | 4.832 | 5.2323 | 5.6671 | 6.1394 | 6.6525 | 7.2099 | 7.8156 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | -1.2282 | -1.1654 | -1.0976 | -1.0241 | -0.94469 | -0.85871 | -0.76564 | -0.66486 | -0.55572 | -0.43751 | -0.30943 | -0.17065 | -0.020236 | 0.14282 | 0.3196 | 0.5113 | 0.71922 | 0.53755 | -0.023488 | -0.86399 | -2.1009 | -3.8996 | -6.4942 | -10.2166 | -15.5371 | -23.124 | -33.9265 | -49.2943 | -71.1483 | -102.2242 |  | 28.4456 | 30.572 | 32.8718 | 35.3596 | 38.0515 | 40.9648 | 44.1184 | 47.533 | 51.2308 | 55.2362 | 59.5757 | 64.278 | 69.3744 | 74.8991 | 80.8889 | 87.3843 | 94.4291 | 102.0711 | 110.3623 | 119.3591 | 129.1232 | 139.7216 | 151.2272 | 163.7194 | 177.2849 | 192.0176 | 208.0201 | 225.4042 | 244.2914 | 264.814 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 28.3676 | 30.494 | 32.7938 | 35.2816 | 37.9734 | 40.8867 | 44.0404 | 47.4549 | 51.1528 | 55.1582 | 59.4977 | 64.2 | 69.2964 | 74.821 | 80.8109 | 87.3063 | 94.3511 | 101.9778 | 110.2385 | 119.1936 | 128.9002 | 139.4189 | 150.8138 | 163.1517 | 176.5013 | 190.9313 | 206.5085 | 223.2934 | 241.335 | 260.6624 |  | 497.7746 | 537.4042 | 580.2639 | 626.6281 | 676.795 | 731.0887 | 789.8617 | 853.4972 | 922.412 | 997.0594 | 1077.9323 | 1165.5671 | 1260.547 | 1363.5068 | 1475.1369 | 1596.1888 | 1727.4801 | 1863.5292 | 2005.4404 | 2155.8047 | 2313.9114 | 2478.3908 | 2646.9056 | 2815.7085 | 2979.0084 | 3128.064 | 3249.887 | 3325.3867 | 3326.7177 | 3213.486
| TRUE | 1616 | 22006131 | FB | FB009 | 11 | FB9 | SENSITIVE EF | Blank | English Electric | CMG_1328 | CMG 1328 | CMG | Electromechanical |  | 0.57434 | 2190 |  | 8.25 | 0.0054067 | 0.0038888 | 0.0015179 | 31.8755 | 1244.4067 | 1276.2822 | 37.4249 | 2.2021 | 74.6127 |  | 11.5885 | 0.013521 | 0.0097249 | 0.0037959 | 79.7129 | 3111.9605 | 3191.6734 | 93.5906 | 5.5069 | 186.5882 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 1390.5218 | 3477.3591 | 46.5656 | 3430.7935 |  | 0.03398 |  | 8.5352 | 8.8302 | 9.1354 | 9.4511 | 9.7778 | 10.1158 | 10.4654 | 10.8271 | 11.2014 | 11.5885 | 11.9891 | 12.4035 | 12.8322 | 13.2757 | 13.7346 | 14.2093 | 14.7004 | 15.2085 | 15.7342 | 16.278 | 16.8407 | 17.4227 | 18.0249 | 18.6479 | 19.2925 | 19.9593 | 20.6492 | 21.3629 | 22.1013 | 22.8652 |  | 0.0059156 | 0.0064751 | 0.0070903 | 0.007767 | 0.0085115 | 0.0093307 | 0.010232 | 0.011225 | 0.012317 | 0.013521 | 0.014846 | 0.016306 | 0.017915 | 0.019688 | 0.021642 | 0.023795 | 0.02617 | 0.028788 | 0.031676 | 0.034861 | 0.038374 | 0.042249 | 0.046526 | 0.051245 | 0.056453 | 0.062201 | 0.068547 | 0.075552 | 0.083287 | 0.091827 |  | 0.0042548 | 0.0046572 | 0.0050997 | 0.0055865 | 0.0061219 | 0.0067111 | 0.0073596 | 0.0080734 | 0.0088594 | 0.0097249 | 0.010678 | 0.011728 | 0.012885 | 0.01416 | 0.015566 | 0.017115 | 0.018823 | 0.020706 | 0.022783 | 0.025074 | 0.0276 | 0.030388 | 0.033464 | 0.036858 | 0.040604 | 0.044739 | 0.049303 | 0.054341 | 0.059904 | 0.066047 | 1521.4077 | 1665.3021 | 1823.5346 | 1997.5732 | 2189.0385 | 2399.7201 | 2631.5941 | 2886.8429 | 3167.8771 | 3477.3591 | 3818.2302 | 4193.7396 | 4607.4773 | 5063.4096 | 5565.9197 | 6119.8509 | 6730.5559 | 7403.9506 | 8146.5736 | 8965.6523 | 9869.176 | 10865.9766 | 11965.8181 | 13179.4954 | 14518.9438 | 15997.3603 | 17629.3375 | 19431.0118 | 21420.228 | 23616.7206 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 34.8758 | 38.1744 | 41.8016 | 45.7912 | 50.1802 | 55.0097 | 60.3251 | 66.1763 | 72.6185 | 79.7129 | 87.5268 | 96.1348 | 105.619 | 116.0706 | 127.5898 | 140.2878 | 154.2872 | 169.7237 | 186.7472 | 205.5232 | 226.2351 | 249.0851 | 274.2972 | 302.1189 | 332.8236 | 366.7139 | 404.1244 | 445.4249 | 491.0245 | 541.3756 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 20.6629 | 23.9614 | 27.5887 | 31.5782 | 35.9673 | 40.7968 | 46.1121 | 51.9633 | 58.4056 | 65.5 | 73.3139 | 81.9218 | 91.4061 | 101.8576 | 113.3769 | 126.0749 | 140.0743 | 152.7117 | 164.1968 | 175.3703 | 185.5991 | 193.9354 | 198.9787 | 198.68 | 190.0608 | 168.8124 | 128.7239 | 60.8643 | -47.5858 | -215.0038 |  | 1361.5392 | 1490.3132 | 1631.9188 | 1787.6695 | 1959.0158 | 2147.5591 | 2355.0679 | 2583.4953 | 2834.9986 | 3111.9605 | 3417.0131 | 3753.0642 | 4123.3265 | 4531.3498 | 4981.0564 | 5476.7809 | 6023.3134 | 6625.9482 | 7290.5369 | 8023.5473 | 8832.1293 | 9724.1868 | 10708.4577 | 11794.6025 | 12993.3025 | 14316.368 | 15776.8581 | 17389.2136 | 19169.4043 | 21135.0908 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 1360.2381 | 1489.0121 | 1630.6177 | 1786.3684 | 1957.7147 | 2146.258 | 2353.7668 | 2582.1942 | 2833.6975 | 3110.6594 | 3415.712 | 3751.7631 | 4122.0254 | 4530.0487 | 4979.7553 | 5475.4798 | 6022.0123 | 6624.3909 | 7288.4725 | 8020.787 | 8828.4094 | 9719.1382 | 10701.5627 | 11785.1334 | 12980.2336 | 14298.2514 | 15751.647 | 17354.0097 | 19120.0981 | 21065.8493 |  | 1380.9009 | 1512.9735 | 1658.2063 | 1817.9466 | 1993.6819 | 2187.0548 | 2399.8789 | 2634.1576 | 2892.1031 | 3176.1593 | 3489.0258 | 3833.6849 | 4213.4315 | 4631.9063 | 5093.1322 | 5601.5546 | 6162.0866 | 6777.1026 | 7452.6693 | 8196.1573 | 9014.0085 | 9913.0736 | 10900.5415 | 11983.8134 | 13170.2943 | 14467.0638 | 15880.3709 | 17414.8739 | 19072.5122 | 20850.8454 |  | 40.9476 | 44.8204 | 49.0791 | 53.7633 | 58.9164 | 64.5868 | 70.8275 | 77.6973 | 85.2612 | 93.5906 | 102.7649 | 112.8715 | 124.007 | 136.2781 | 149.8028 | 164.7114 | 181.1481 | 199.2721 | 219.2592 | 241.3041 | 265.6218 | 292.45 | 322.0515 | 354.7167 | 390.767 | 430.5576 | 474.4811 | 522.9718 | 576.5102 | 635.6272 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 26.2547 | 30.1276 | 34.3863 | 39.0704 | 44.2235 | 49.8939 | 56.1346 | 63.0045 | 70.5683 | 78.8978 | 88.0721 | 98.1786 | 109.3141 | 121.5852 | 135.1099 | 150.0186 | 166.4552 | 181.6856 | 195.9474 | 210.133 | 223.6138 | 235.438 | 244.1897 | 247.7851 | 243.1836 | 225.9735 | 189.7812 | 125.4258 | 19.7127 | -146.2928 |  | 2.4094 | 2.6372 | 2.8878 | 3.1634 | 3.4667 | 3.8003 | 4.1675 | 4.5717 | 5.0168 | 5.5069 | 6.0467 | 6.6414 | 7.2966 | 8.0187 | 8.8144 | 9.6917 | 10.6588 | 11.7252 | 12.9013 | 14.1984 | 15.6293 | 17.2079 | 18.9496 | 20.8717 | 22.9929 | 25.3342 | 27.9186 | 30.7719 | 33.9221 | 37.4005 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.34164 | 0.56952 | 0.8201 | 1.0957 | 1.3989 | 1.7326 | 2.0998 | 2.504 | 2.9491 | 3.4392 | 3.979 | 4.5737 | 5.2289 | 5.9509 | 6.7467 | 7.6239 | 8.5911 | 9.2503 | 9.6206 | 9.8117 | 9.7175 | 9.1846 | 7.9921 | 5.8231 | 2.2234 | -3.457 | -12.1473 | -25.1749 | -44.4362 | -72.6393 |  | 81.6357 | 89.3568 | 97.8473 | 107.1858 | 117.4595 | 128.7642 | 141.2061 | 154.9023 | 169.982 | 186.5882 | 204.8787 | 225.0278 | 247.2281 | 271.6925 | 298.6562 | 328.3791 | 361.1483 | 397.2813 | 437.129 | 481.0792 | 529.5605 | 583.0468 | 642.0621 | 707.1856 | 779.0578 | 858.3867 | 945.9554 | 1042.6296 | 1149.367 | 1267.2265 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 81.5577 | 89.2788 | 97.7692 | 107.1078 | 117.3815 | 128.6862 | 141.1281 | 154.8243 | 169.904 | 186.5102 | 204.8007 | 224.9498 | 247.1501 | 271.6145 | 298.5782 | 328.3011 | 361.0703 | 397.188 | 437.0052 | 480.9137 | 529.3374 | 582.7441 | 641.6487 | 706.6179 | 778.2742 | 857.3005 | 944.4437 | 1040.5189 | 1146.4107 | 1263.0749 |  | 1489.055 | 1632.9494 | 1791.182 | 1965.2205 | 2156.6859 | 2367.3674 | 2599.2414 | 2854.4903 | 3135.5245 | 3445.0065 | 3785.8776 | 4161.387 | 4575.1246 | 5031.057 | 5533.567 | 6087.4982 | 6698.2032 | 7365.2265 | 8095.2425 | 8897.0157 | 9776.6772 | 10740.4403 | 11794.372 | 12944.0395 | 14193.9755 | 15546.8808 | 17002.4485 | 18555.6437 | 20194.1995 | 21894.9882
| TRUE | 1617 | 22006132 | FB | FB009 | 11 | FB9 | PILOT WIRE | Blank | English Electric | DSF7_1490 | DSF7 1490 | DSF7 | Electromechanical |  | 0.57434 | 2190 |  | 5.5 | 0.0019187 | 0.0013801 | 0.00053868 | 11.3121 | 441.6215 | 452.9336 | 13.2815 | 0.78149 | 26.4789 |  | 7.3552 | 0.0040026 | 0.0028789 | 0.0011237 | 23.5976 | 921.2421 | 944.8397 | 27.7059 | 1.6302 | 55.2362 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 493.4756 | 1029.4121 | 46.5656 | 982.8465 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0.0014826 | 0.0015934 | 0.0017133 | 0.0018429 | 0.0019832 | 0.0021351 | 0.0022994 | 0.0024774 | 0.0026701 | 0.0028789 | 0.0031051 | 0.0033501 | 0.0036158 | 0.0039037 | 0.0042159 | 0.0045544 | 0.0049216 | 0.0053199 | 0.005752 | 0.0062209 | 0.0067298 | 0.0072822 | 0.0078819 | 0.008533 | 0.00924 | 0.010008 | 0.010842 | 0.011748 | 0.012732 | 0.013802 | 530.1273 | 569.7568 | 612.6165 | 658.9808 | 709.1476 | 763.4413 | 822.2143 | 885.8499 | 954.7647 | 1029.4121 | 1110.285 | 1197.9197 | 1292.8997 | 1395.8594 | 1507.4896 | 1628.5415 | 1759.8328 | 1902.2533 | 2056.7715 | 2224.4413 | 2406.4102 | 2603.9272 | 2818.3518 | 3051.1644 | 3303.9767 | 3578.5436 | 3876.776 | 4200.7548 | 4552.7463 | 4935.2183 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 12.1523 | 13.0608 | 14.0433 | 15.1061 | 16.2561 | 17.5007 | 18.8479 | 20.3067 | 21.8865 | 23.5976 | 25.4515 | 27.4604 | 29.6377 | 31.9978 | 34.5568 | 37.3317 | 40.3414 | 43.6061 | 47.1482 | 50.9918 | 55.1631 | 59.6909 | 64.6062 | 69.9431 | 75.7384 | 82.0324 | 88.8689 | 96.2956 | 104.3644 | 113.132 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | -2.0606 | -1.1522 | -0.16969 | 0.89314 | 2.0431 | 3.2877 | 4.635 | 6.0937 | 7.6735 | 9.3847 | 11.2386 | 13.2475 | 15.4247 | 17.7849 | 20.3438 | 23.1188 | 26.1284 | 26.5941 | 24.5978 | 20.8388 | 14.5272 | 4.5411 | -10.7123 | -33.4958 | -67.0244 | -115.8691 | -186.5316 | -288.265 | -434.2459 | -643.2474 |  | 474.4218 | 509.8871 | 548.2432 | 589.7355 | 634.6309 | 683.2194 | 735.8166 | 792.7653 | 854.4386 | 921.2421 | 993.617 | 1072.0431 | 1157.0426 | 1249.1834 | 1349.0835 | 1457.4154 | 1574.9107 | 1702.3658 | 1840.6473 | 1990.6985 | 2153.5462 | 2330.3082 | 2522.2012 | 2730.55 | 2956.7969 | 3202.5125 | 3469.4069 | 3759.3422 | 4074.3466 | 4416.6288 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 473.1207 | 508.586 | 546.9421 | 588.4344 | 633.3298 | 681.9183 | 734.5155 | 791.4642 | 853.1375 | 919.941 | 992.3159 | 1070.742 | 1155.7415 | 1247.8823 | 1347.7824 | 1456.1143 | 1573.6096 | 1700.8084 | 1838.5829 | 1987.9382 | 2149.8263 | 2325.2596 | 2515.3063 | 2721.0809 | 2943.728 | 3184.396 | 3444.1958 | 3724.1382 | 4025.0404 | 4347.3873 |  | 471.0601 | 507.4339 | 546.7724 | 589.3275 | 635.3729 | 685.206 | 739.1505 | 797.558 | 860.811 | 929.3257 | 1003.5544 | 1083.9894 | 1171.1662 | 1265.6672 | 1368.1263 | 1479.2331 | 1599.738 | 1727.4025 | 1863.1807 | 2008.777 | 2164.3534 | 2329.8007 | 2504.594 | 2687.5851 | 2876.7035 | 3068.5268 | 3257.6642 | 3435.8732 | 3590.7946 | 3704.1398 |  | 14.268 | 15.3346 | 16.4881 | 17.736 | 19.0862 | 20.5475 | 22.1293 | 23.842 | 25.6968 | 27.7059 | 29.8825 | 32.2412 | 34.7975 | 37.5686 | 40.573 | 43.831 | 47.3646 | 51.1978 | 55.3565 | 59.8693 | 64.7668 | 70.0828 | 75.8539 | 82.1199 | 88.9242 | 96.314 | 104.3407 | 113.0603 | 122.5339 | 132.8279 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | -0.42487 | 0.64173 | 1.7953 | 3.0431 | 4.3933 | 5.8546 | 7.4364 | 9.1491 | 11.0039 | 13.013 | 15.1897 | 17.5483 | 20.1046 | 22.8757 | 25.8801 | 29.1382 | 32.6718 | 33.6113 | 32.0447 | 28.6981 | 22.7587 | 13.0709 | -2.0079 | -24.8117 | -58.6593 | -108.2701 | -180.3592 | -284.4857 | -434.2636 | -649.0921 |  | 0.83953 | 0.90229 | 0.97017 | 1.0436 | 1.123 | 1.209 | 1.3021 | 1.4029 | 1.512 | 1.6302 | 1.7583 | 1.8971 | 2.0475 | 2.2105 | 2.3873 | 2.579 | 2.787 | 3.0125 | 3.2572 | 3.5227 | 3.8109 | 4.1237 | 4.4633 | 4.832 | 5.2323 | 5.6671 | 6.1394 | 6.6525 | 7.2099 | 7.8156 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | -1.2282 | -1.1654 | -1.0976 | -1.0241 | -0.94469 | -0.85871 | -0.76564 | -0.66486 | -0.55572 | -0.43751 | -0.30943 | -0.17065 | -0.020236 | 0.14282 | 0.3196 | 0.5113 | 0.71922 | 0.53755 | -0.023488 | -0.86399 | -2.1009 | -3.8996 | -6.4942 | -10.2166 | -15.5371 | -23.124 | -33.9265 | -49.2943 | -71.1483 | -102.2242 |  | 28.4456 | 30.572 | 32.8718 | 35.3596 | 38.0515 | 40.9648 | 44.1184 | 47.533 | 51.2308 | 55.2362 | 59.5757 | 64.278 | 69.3744 | 74.8991 | 80.8889 | 87.3843 | 94.4291 | 102.0711 | 110.3623 | 119.3591 | 129.1232 | 139.7216 | 151.2272 | 163.7194 | 177.2849 | 192.0176 | 208.0201 | 225.4042 | 244.2914 | 264.814 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 28.3676 | 30.494 | 32.7938 | 35.2816 | 37.9734 | 40.8867 | 44.0404 | 47.4549 | 51.1528 | 55.1582 | 59.4977 | 64.2 | 69.2964 | 74.821 | 80.8109 | 87.3063 | 94.3511 | 101.9778 | 110.2385 | 119.1936 | 128.9002 | 139.4189 | 150.8138 | 163.1517 | 176.5013 | 190.9313 | 206.5085 | 223.2934 | 241.335 | 260.6624 |  | 497.7746 | 537.4042 | 580.2639 | 626.6281 | 676.795 | 731.0887 | 789.8617 | 853.4972 | 922.412 | 997.0594 | 1077.9323 | 1165.5671 | 1260.547 | 1363.5068 | 1475.1369 | 1596.1888 | 1727.4801 | 1863.5292 | 2005.4404 | 2155.8047 | 2313.9114 | 2478.3908 | 2646.9056 | 2815.7085 | 2979.0084 | 3128.064 | 3249.887 | 3325.3867 | 3326.7177 | 3213.486
| TRUE | 1618 | 22006133 | FB | FB009 | 11 | FB9 | OVERCURRENT | Blank | ASEA | RACID_3245 | RACID 3245 | RACID | Electronic |  | 0.57434 | 2190 |  | 6.6 | 0.014726 | 0.010592 | 0.0041343 | 86.8187 | 3389.3699 | 3476.1886 | 101.9336 | 5.9978 | 203.2212 |  | 11.1153 | 0.058633 | 0.042172 | 0.016461 | 345.6775 | 13495.1158 | 13840.7933 | 405.8588 | 23.8809 | 809.1457 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 3787.3412 | 15079.6787 | 46.5656 | 15033.1131 |  | 0.052126 |  | 6.9532 | 7.3252 | 7.7172 | 8.1301 | 8.5651 | 9.0234 | 9.5062 | 10.0149 | 10.5508 | 11.1153 | 11.7101 | 12.3367 | 12.9968 | 13.6922 | 14.4249 | 15.1967 | 16.0099 | 16.8665 | 17.769 | 18.7198 | 19.7215 | 20.7767 | 21.8884 | 23.0596 | 24.2935 | 25.5934 | 26.9629 | 28 | 28 | 28 |  | 0.016829 | 0.019254 | 0.022055 | 0.02529 | 0.029029 | 0.033353 | 0.038356 | 0.044149 | 0.050858 | 0.058633 | 0.067647 | 0.078102 | 0.090233 | 0.10431 | 0.12066 | 0.13966 | 0.16172 | 0.18737 | 0.2172 | 0.25188 | 0.29223 | 0.33918 | 0.39382 | 0.45744 | 0.53152 | 0.61779 | 0.7183 | 0.80128 | 0.80128 | 0.80128 |  | 0.012104 | 0.013849 | 0.015863 | 0.01819 | 0.020879 | 0.023989 | 0.027588 | 0.031754 | 0.03658 | 0.042172 | 0.048656 | 0.056175 | 0.0649 | 0.075028 | 0.086788 | 0.10045 | 0.11632 | 0.13477 | 0.15622 | 0.18117 | 0.21019 | 0.24396 | 0.28326 | 0.32902 | 0.3823 | 0.44435 | 0.51664 | 0.57632 | 0.57632 | 0.57632 | 4328.1022 | 4951.9696 | 5672.184 | 6504.1419 | 7465.7509 | 8577.8456 | 9864.6708 | 11354.4471 | 13080.03 | 15079.6787 | 17397.9547 | 20086.7689 | 23206.6057 | 26827.9505 | 31032.9577 | 35917.397 | 41592.9266 | 48189.7483 | 55859.7074 | 64779.9133 | 75156.9684 | 87231.908 | 101285.9697 | 117647.3339 | 136698.9976 | 158887.9731 | 184736.0358 | 206077.9027 | 206077.9027 | 206077.9027 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 99.2148 | 113.516 | 130.0257 | 149.0971 | 171.1404 | 196.6334 | 226.1318 | 260.2825 | 299.8388 | 345.6775 | 398.8203 | 460.4571 | 531.9743 | 614.9879 | 711.3809 | 823.3489 | 953.4513 | 1104.6729 | 1280.4945 | 1484.9759 | 1722.8533 | 1999.652 | 2321.8189 | 2696.877 | 3133.6059 | 3642.2527 | 4234.7782 | 4724.0064 | 4724.0064 | 4724.0064 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 85.0019 | 99.303 | 115.8128 | 134.8841 | 156.9275 | 182.4204 | 211.9189 | 246.0696 | 285.6258 | 331.4646 | 384.6073 | 446.2441 | 517.7614 | 600.7749 | 697.168 | 809.1359 | 939.2384 | 1087.6609 | 1257.944 | 1454.823 | 1682.2174 | 1944.5022 | 2246.5004 | 2593.4381 | 2990.8431 | 3444.3512 | 3959.3777 | 4339.4458 | 4185.3961 | 3967.627 |  | 3873.308 | 4431.6198 | 5076.1546 | 5820.6908 | 6681.2546 | 7676.4911 | 8828.0975 | 10161.3291 | 11705.5888 | 13495.1158 | 15569.7888 | 17976.0641 | 20768.0705 | 24008.8868 | 27772.0345 | 32143.22 | 37222.3686 | 43126.0006 | 49990.0053 | 57972.8817 | 67259.5225 | 78065.6353 | 90642.9052 | 105285.0278 | 122334.7549 | 142192.1272 | 165324.0921 | 184423.3694 | 184423.3694 | 184423.3694 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 3872.0069 | 4430.3187 | 5074.8535 | 5819.3897 | 6679.9535 | 7675.19 | 8826.7964 | 10160.028 | 11704.2877 | 13493.8147 | 15568.4877 | 17974.763 | 20766.7694 | 24007.5857 | 27770.7334 | 32141.9189 | 37221.0675 | 43124.4433 | 49987.941 | 57970.1214 | 67255.8026 | 78060.5867 | 90636.0103 | 105275.5587 | 122321.686 | 142174.0107 | 165298.881 | 184388.1654 | 184374.0632 | 184354.1279 |  | 3957.0088 | 4529.6218 | 5190.6663 | 5954.2738 | 6836.881 | 7857.6104 | 9038.7153 | 10406.0976 | 11989.9136 | 13825.2793 | 15953.095 | 18421.0072 | 21284.5308 | 24608.3606 | 28467.9014 | 32951.0549 | 38160.3059 | 44212.1042 | 51245.885 | 59424.9443 | 68938.02 | 80005.0889 | 92882.5107 | 107868.9968 | 125312.5291 | 145618.3618 | 169258.2587 | 188727.6112 | 188559.4592 | 188321.7548 |  | 116.4878 | 133.2787 | 152.6628 | 175.0543 | 200.9354 | 230.8666 | 265.5006 | 305.5969 | 352.0397 | 405.8588 | 468.2536 | 540.6211 | 624.5893 | 722.0552 | 835.23 | 966.6912 | 1119.444 | 1296.9928 | 1503.4242 | 1743.5052 | 2022.7963 | 2347.7847 | 2726.0397 | 3166.3942 | 3679.1562 | 4276.3566 | 4972.0388 | 5546.44 | 5546.44 | 5546.44 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 101.7949 | 118.5859 | 137.9699 | 160.3615 | 186.2425 | 216.1737 | 250.8077 | 290.904 | 337.3468 | 391.1659 | 453.5607 | 525.9282 | 609.8964 | 707.3623 | 820.5371 | 951.9983 | 1104.7511 | 1279.4063 | 1480.1124 | 1712.3341 | 1980.7882 | 2290.7727 | 2648.1779 | 3059.4625 | 3531.5727 | 4071.7726 | 4687.3389 | 5148.894 | 4989.6425 | 4764.52 |  | 6.8542 | 7.8422 | 8.9827 | 10.3003 | 11.8231 | 13.5843 | 15.6222 | 17.9814 | 20.7141 | 23.8809 | 27.5522 | 31.8103 | 36.7511 | 42.486 | 49.1452 | 56.8805 | 65.8685 | 76.3155 | 88.462 | 102.5885 | 119.0221 | 138.1445 | 160.4012 | 186.3118 | 216.4829 | 251.6224 | 292.5566 | 326.3545 | 326.3545 | 326.3545 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.7865 | 5.7744 | 6.915 | 8.2325 | 9.7554 | 11.5165 | 13.5544 | 15.9137 | 18.6464 | 21.8131 | 25.4845 | 29.7426 | 34.6833 | 40.4183 | 47.0775 | 54.8127 | 63.8008 | 73.8406 | 85.1813 | 98.2018 | 113.1103 | 130.1212 | 149.4437 | 171.2633 | 195.7134 | 222.8312 | 252.4907 | 270.4078 | 247.9963 | 216.3147 |  | 232.2374 | 265.7129 | 304.3582 | 348.9994 | 400.5974 | 460.2702 | 529.3187 | 609.2572 | 701.8485 | 809.1457 | 933.5398 | 1077.8163 | 1245.2205 | 1439.5347 | 1665.1671 | 1927.2564 | 2231.7941 | 2585.7665 | 2997.3214 | 3475.962 | 4032.7742 | 4680.6916 | 5434.8047 | 6312.7231 | 7334.9977 | 8525.6142 | 9912.5701 | 11057.7325 | 11057.7325 | 11057.7325 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 232.1594 | 265.6349 | 304.2802 | 348.9214 | 400.5194 | 460.1922 | 529.2407 | 609.1792 | 701.7705 | 809.0677 | 933.4618 | 1077.7383 | 1245.1425 | 1439.4567 | 1665.0891 | 1927.1784 | 2231.7161 | 2585.6732 | 2997.1976 | 3475.7965 | 4032.5512 | 4680.3889 | 5434.3913 | 6312.1554 | 7334.2141 | 8524.528 | 9911.0585 | 11055.6217 | 11054.7761 | 11053.5808 |  | 4295.7496 | 4919.617 | 5639.8314 | 6471.7892 | 7433.3983 | 8545.4929 | 9832.3181 | 11322.0945 | 13047.6773 | 15047.3261 | 17365.602 | 20054.4162 | 23174.253 | 26795.5979 | 31000.6051 | 35885.0443 | 41560.5739 | 48151.0242 | 55808.3763 | 64711.2766 | 75064.4696 | 87106.3716 | 101114.5236 | 117411.878 | 136374.0293 | 158437.4936 | 184109.1468 | 205202.5346 | 204851.8741 | 204356.1703
| TRUE | 1619 | 22006134 | FB | FB009 | 11 | FB9 | OVERCURRENT | Blank | ABB | SPAJ_3167 | SPAJ 3167 | SPAJ | Electronic |  | 0.57434 | 2190 |  | 9.9 | 0.042792 | 0.030778 | 0.012014 | 252.2846 | 9849.091 | 10101.3755 | 296.2065 | 17.4289 | 590.5359 |  | 18.0962 | 0.22875 | 0.16453 | 0.064219 | 1348.5871 | 52648.3173 | 53996.9044 | 1583.3716 | 93.1662 | 3156.7095 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 28.4259 | 1.3011 | 29.727 | 14.6929 | 2.0677 | 0.078012 |  | 11005.5467 | 58830.1517 | 46.5656 | 58783.5861 |  | 0.060317 |  | 10.5155 | 11.1693 | 11.8637 | 12.6013 | 13.3848 | 14.217 | 15.1009 | 16.0397 | 17.037 | 18.0962 | 19.2213 | 20.4164 | 21.6857 | 23.034 | 24.4661 | 25.9872 | 27.6029 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.050397 | 0.059416 | 0.070118 | 0.082825 | 0.09792 | 0.11586 | 0.1372 | 0.16258 | 0.19278 | 0.22875 | 0.27158 | 0.32262 | 0.38345 | 0.45598 | 0.54247 | 0.64566 | 0.76879 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.036248 | 0.042735 | 0.050433 | 0.059572 | 0.070429 | 0.083334 | 0.098678 | 0.11693 | 0.13866 | 0.16453 | 0.19534 | 0.23204 | 0.2758 | 0.32796 | 0.39018 | 0.46439 | 0.55295 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 12961.384 | 15280.8955 | 18033.3441 | 21301.3778 | 25183.6405 | 29797.8943 | 35284.7556 | 41812.1651 | 49580.7355 | 58830.1517 | 69846.83 | 82973.0848 | 98618.1005 | 117271.0653 | 139516.8933 | 166055.0463 | 197722.0679 | 206077.9027 | 206077.9027 | 206077.9027 | 206077.9027 | 206077.9027 | 206077.9027 | 206077.9027 | 206077.9027 | 206077.9027 | 206077.9027 | 206077.9027 | 206077.9027 | 206077.9027 |  | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 32.365 | 38.7388 | 51.3506 | 68.6627 | 92.534 | 125.5841 | 171.5113 | 235.5454 | 325.0919 | 450.6508 | 627.1273 | 875.7009 | 1226.4947 | 1722.3869 |  | 297.119 | 350.2901 | 413.3856 | 488.3 | 577.2947 | 683.0691 | 808.8466 | 958.477 | 1136.5591 | 1348.5871 | 1601.1269 | 1902.0253 | 2260.6622 | 2688.2516 | 3198.2017 | 3806.5464 | 4532.4622 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 | 4724.0064 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 282.9061 | 336.0771 | 399.1726 | 474.0871 | 563.0817 | 668.8561 | 794.6337 | 944.2641 | 1122.3461 | 1334.3742 | 1586.9139 | 1887.8123 | 2246.4493 | 2674.0387 | 3183.9887 | 3792.3334 | 4518.2493 | 4706.9944 | 4701.4559 | 4693.8534 | 4683.3704 | 4668.8566 | 4648.6878 | 4620.5675 | 4581.2435 | 4526.1048 | 4448.6059 | 4339.4458 | 4185.3961 | 3967.627 |  | 11599.4101 | 13675.1888 | 16138.4119 | 19063.0428 | 22537.3598 | 26666.7507 | 31577.0562 | 37418.5697 | 44370.8238 | 52648.3173 | 62507.3701 | 74254.3265 | 88255.374 | 104948.2973 | 124856.548 | 148606.0889 | 176945.5603 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 | 184423.3694 |  | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.3011 | 1.5573 | 2.0643 | 2.7603 | 3.72 | 5.0486 | 6.8949 | 9.4691 | 13.069 | 18.1166 | 25.2111 | 35.204 | 49.3062 | 69.2415 |  | 11598.109 | 13673.8877 | 16137.1108 | 19061.7417 | 22536.0587 | 26665.4496 | 31575.7551 | 37417.2686 | 44369.5227 | 52647.0162 | 62506.069 | 74253.0254 | 88254.0729 | 104946.9962 | 124855.2469 | 148604.7878 | 176944.2592 | 184421.812 | 184421.305 | 184420.6091 | 184419.6494 | 184418.3208 | 184416.4745 | 184413.9002 | 184410.3004 | 184405.2528 | 184398.1583 | 184388.1654 | 184374.0632 | 184354.1279 |  | 11881.0151 | 14009.9649 | 16536.2834 | 19535.8287 | 23099.1404 | 27334.3057 | 32370.3888 | 38361.5327 | 45491.8688 | 53981.3904 | 64092.9829 | 76140.8377 | 90500.5222 | 107621.0349 | 128039.2356 | 152397.1213 | 181462.5085 | 189128.8064 | 189122.761 | 189114.4625 | 189103.0198 | 189087.1774 | 189065.1623 | 189034.4677 | 188991.5439 | 188931.3576 | 188846.7642 | 188727.6112 | 188559.4592 | 188321.7548 |  | 348.8464 | 411.2744 | 485.3546 | 573.3114 | 677.7997 | 801.9891 | 949.6641 | 1125.3446 | 1334.4302 | 1583.3716 | 1879.8777 | 2233.1615 | 2654.2359 | 3156.2672 | 3754.9978 | 4469.2533 | 5321.5486 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 334.1536 | 396.5815 | 470.6617 | 558.6185 | 663.1069 | 787.2962 | 934.9712 | 1110.6518 | 1319.7373 | 1568.6788 | 1865.1848 | 2218.4686 | 2639.5431 | 3141.5743 | 3740.3049 | 4454.5604 | 5306.8558 | 5528.8535 | 5523.1281 | 5515.2688 | 5504.4319 | 5489.428 | 5468.5782 | 5439.5083 | 5398.8565 | 5341.8559 | 5261.7401 | 5148.894 | 4989.6425 | 4764.52 |  | 20.5262 | 24.1995 | 28.5584 | 33.7339 | 39.882 | 47.1893 | 55.8786 | 66.2157 | 78.5184 | 93.1662 | 110.6127 | 131.4 | 156.1762 | 185.7159 | 220.9454 | 262.9725 | 313.1218 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 18.4585 | 22.1318 | 26.4907 | 31.6661 | 37.8143 | 45.1216 | 53.8108 | 64.148 | 76.4506 | 91.0984 | 108.545 | 129.3323 | 154.1085 | 183.6482 | 218.8777 | 260.9047 | 311.0541 | 323.8796 | 323.0738 | 321.9678 | 320.4427 | 318.3312 | 315.397 | 311.306 | 305.5851 | 297.5634 | 286.2886 | 270.4078 | 247.9963 | 216.3147 |  | 695.4822 | 819.9426 | 967.6336 | 1142.9898 | 1351.3043 | 1598.896 | 1893.3102 | 2243.558 | 2660.4042 | 3156.7095 | 3747.8427 | 4452.1715 | 5291.6521 | 6292.5333 | 7486.2004 | 8910.1852 | 10609.3749 | 11057.7325 | 11057.7325 | 11057.7325 | 11057.7325 | 11057.7325 | 11057.7325 | 11057.7325 | 11057.7325 | 11057.7325 | 11057.7325 | 11057.7325 | 11057.7325 | 11057.7325 |  | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.078012 | 0.093375 | 0.12377 | 0.1655 | 0.22304 | 0.30271 | 0.41341 | 0.56775 | 0.7836 | 1.0862 | 1.5116 | 2.1108 | 2.9563 | 4.1516 |  | 695.4042 | 819.8646 | 967.5555 | 1142.9118 | 1351.2263 | 1598.818 | 1893.2322 | 2243.48 | 2660.3261 | 3156.6315 | 3747.7647 | 4452.0935 | 5291.5741 | 6292.4553 | 7486.1224 | 8910.1072 | 10609.2969 | 11057.6391 | 11057.6087 | 11057.567 | 11057.5094 | 11057.4297 | 11057.319 | 11057.1647 | 11056.9489 | 11056.6462 | 11056.2208 | 11055.6217 | 11054.7761 | 11053.5808 |  | 12929.0314 | 15248.5428 | 18000.9914 | 21269.0252 | 25151.2878 | 29765.5416 | 35252.403 | 41779.8125 | 49548.3829 | 58797.7991 | 69814.4774 | 82940.7321 | 98585.7478 | 117238.7127 | 139484.5407 | 166022.6936 | 197689.7153 | 206039.1786 | 206026.5716 | 206009.2661 | 205985.4039 | 205952.3663 | 205906.4565 | 205842.4468 | 205752.9344 | 205627.4231 | 205451.0137 | 205202.5346 | 204851.8741 | 204356.1703
| TRUE | 1620 | 22009854 | FB | Blank | 66 | BUS NO.2 | HIBP | A | English Electric | CAG34_1363 | CAG34 1363 | CAG | Electromechanical |  | 0.033587 | 2190 |  | 5.5 | 0.0019187 | 0.00018099 | 0.0017378 | 20.3369 | 86.8731 | 107.2099 | 6.4741 | 0.7695 | 960.2806 |  | 7.3552 | 0.0040026 | 0.00037754 | 0.003625 | 42.4236 | 181.2211 | 223.6447 | 13.5052 | 1.6052 | 2003.1881 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 54.2636 | 0.11413 | 54.3777 | 14.6711 | 2.0677 | 1.2616 |  | 1074.7341 | 2241.9432 | 72.3781 | 2169.5651 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0.00019443 | 0.00020896 | 0.00022468 | 0.00024169 | 0.00026008 | 0.00028 | 0.00030155 | 0.00032489 | 0.00035017 | 0.00037754 | 0.0004072 | 0.00043935 | 0.00047418 | 0.00051194 | 0.00055288 | 0.00059728 | 0.00064543 | 0.00069766 | 0.00075434 | 0.00081583 | 0.00088257 | 0.00095501 | 0.0010336 | 0.001119 | 0.0012118 | 0.0013125 | 0.0014218 | 0.0015407 | 0.0016698 | 0.00181 | 1154.5574 | 1240.866 | 1334.2097 | 1435.1857 | 1544.4435 | 1662.6891 | 1790.69 | 1929.281 | 2079.3697 | 2241.9432 | 2418.0754 | 2608.9339 | 2815.7895 | 3040.0243 | 3283.1421 | 3546.7795 | 3832.7172 | 4142.893 | 4479.4161 | 4844.5821 | 5240.8899 | 5671.0594 | 6138.0521 | 6645.0916 | 7195.6883 | 7793.664 | 8443.1805 | 9148.7698 | 9915.3674 | 10748.3485 |  | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 54.1587 | 71.7906 | 95.9937 | 129.3669 | 175.5724 | 239.7809 | 329.3036 | 454.4937 | 630.031 | 876.7535 | 1224.271 | 1714.6972 | 2407.9778 |  | 21.8473 | 23.4805 | 25.2468 | 27.1576 | 29.225 | 31.4626 | 33.8847 | 36.5072 | 39.3473 | 42.4236 | 45.7565 | 49.3681 | 53.2823 | 57.5255 | 62.1259 | 67.1146 | 72.5253 | 78.3947 | 84.7626 | 91.6725 | 99.1718 | 107.3117 | 116.1485 | 125.743 | 136.1618 | 147.4771 | 159.7677 | 173.1194 | 187.6255 | 203.3877 |  | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 32.4751 | 43.0476 | 57.5605 | 77.572 | 105.2781 | 143.7793 | 197.4595 | 272.527 | 377.784 | 525.7256 | 734.1068 | 1028.1799 | 1443.8901 |  | -5.2845 | -3.6513 | -1.8849 | 0.025792 | 2.0932 | 4.3308 | 6.7529 | 9.3754 | 12.2155 | 15.2918 | 18.6247 | 22.2363 | 26.1505 | 30.3937 | 34.9941 | 39.9828 | 45.3935 | 45.9196 | 41.715 | 34.1121 | 21.5998 | 2.0336 | -27.6308 | -71.7165 | -136.3652 | -230.3069 | -365.9579 | -560.9874 | -840.5544 | -1240.5024 |  | 93.3253 | 100.3019 | 107.847 | 116.0091 | 124.8407 | 134.3987 | 144.7453 | 155.9479 | 168.0799 | 181.2211 | 195.4582 | 210.8857 | 227.6063 | 245.7317 | 265.3834 | 286.6938 | 309.8067 | 334.8789 | 362.0808 | 391.598 | 423.6324 | 458.4039 | 496.1519 | 537.137 | 581.6429 | 629.9786 | 682.4804 | 739.5147 | 801.4804 | 868.812 |  | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.13661 | 0.18108 | 0.24213 | 0.32631 | 0.44286 | 0.60482 | 0.83063 | 1.1464 | 1.5892 | 2.2115 | 3.0881 | 4.3251 | 6.0739 |  | 93.2112 | 100.1877 | 107.7329 | 115.895 | 124.7265 | 134.2846 | 144.6312 | 155.8338 | 167.9658 | 181.1069 | 195.3441 | 210.7716 | 227.4922 | 245.6175 | 265.2693 | 286.5797 | 309.6926 | 334.7423 | 361.8997 | 391.3558 | 423.306 | 457.961 | 495.5471 | 536.3064 | 580.4965 | 628.3894 | 680.2689 | 736.4266 | 797.1553 | 862.7382 |  | 87.9268 | 96.5365 | 105.8479 | 115.9208 | 126.8198 | 138.6154 | 151.3841 | 165.2092 | 180.1813 | 196.3988 | 213.9688 | 233.0079 | 253.6427 | 276.0112 | 300.2634 | 326.5625 | 355.0862 | 380.662 | 403.6147 | 425.4679 | 444.9059 | 459.9947 | 467.9163 | 464.5899 | 444.1313 | 398.0825 | 314.311 | 175.4392 | -43.3991 | -377.7642 |  | 6.9549 | 7.4748 | 8.0371 | 8.6454 | 9.3036 | 10.0159 | 10.7869 | 11.6218 | 12.5259 | 13.5052 | 14.5662 | 15.7159 | 16.962 | 18.3128 | 19.7773 | 21.3654 | 23.0879 | 24.9563 | 26.9835 | 29.1832 | 31.5705 | 34.1618 | 36.9749 | 40.0293 | 43.346 | 46.9482 | 50.8608 | 55.1112 | 59.7291 | 64.7469 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | -7.7162 | -7.1963 | -6.634 | -6.0257 | -5.3676 | -4.6553 | -3.8842 | -3.0494 | -2.1452 | -1.1659 | -0.10492 | 1.0448 | 2.2909 | 3.6416 | 5.1061 | 6.6943 | 8.4167 | 7.3959 | 3.7061 | -1.9418 | -10.3754 | -22.7658 | -40.7717 | -66.7442 | -104.0191 | -157.3333 | -233.418 | -341.8468 | -496.2448 | -716.0165 |  | 0.82665 | 0.88845 | 0.95528 | 1.0276 | 1.1058 | 1.1905 | 1.2821 | 1.3813 | 1.4888 | 1.6052 | 1.7313 | 1.868 | 2.0161 | 2.1766 | 2.3507 | 2.5395 | 2.7442 | 2.9663 | 3.2072 | 3.4687 | 3.7524 | 4.0604 | 4.3948 | 4.7578 | 5.152 | 5.5802 | 6.0452 | 6.5504 | 7.0993 | 7.6957 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | -1.241 | -1.1792 | -1.1124 | -1.0401 | -0.96189 | -0.87722 | -0.78558 | -0.68635 | -0.57888 | -0.46248 | -0.33637 | -0.19972 | -0.051613 | 0.10894 | 0.28301 | 0.47177 | 0.6765 | 0.49137 | -0.073404 | -0.91796 | -2.1593 | -3.9627 | -6.5625 | -10.2904 | -15.617 | -23.2104 | -34.0199 | -49.3953 | -71.2575 | -102.3421 |  | 1031.6031 | 1108.7204 | 1192.1234 | 1282.346 | 1379.9684 | 1485.6215 | 1599.991 | 1723.8228 | 1857.9278 | 2003.1881 | 2160.5631 | 2331.0963 | 2515.9228 | 2716.2777 | 2933.5048 | 3169.0663 | 3424.5531 | 3701.6968 | 4002.382 | 4328.6597 | 4682.7628 | 5067.1216 | 5484.3819 | 5937.4245 | 6429.3855 | 6963.6799 | 7544.0264 | 8174.4742 | 8859.4332 | 9603.7061 |  | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.5101 | 2.0017 | 2.6765 | 3.607 | 4.8953 | 6.6856 | 9.1817 | 12.6723 | 17.5666 | 24.4458 | 34.1353 | 47.8095 | 67.1396 |  | 1030.3415 | 1107.4588 | 1190.8618 | 1281.0844 | 1378.7068 | 1484.3598 | 1598.7294 | 1722.5611 | 1856.6662 | 2001.9265 | 2159.3015 | 2329.8347 | 2514.6612 | 2715.0161 | 2932.2432 | 3167.8047 | 3423.2915 | 3700.1867 | 4000.3803 | 4325.9832 | 4679.1558 | 5062.2262 | 5477.6963 | 5928.2428 | 6416.7132 | 6946.1133 | 7519.5806 | 8140.3389 | 8811.6237 | 9536.5665 |  | 1109.311 | 1195.6197 | 1288.9633 | 1389.9393 | 1499.1971 | 1617.4427 | 1745.4436 | 1884.0346 | 2034.1233 | 2196.6969 | 2372.829 | 2563.6876 | 2770.5432 | 2994.7779 | 3237.8958 | 3501.5332 | 3787.4708 | 4088.736 | 4407.6277 | 4748.5913 | 5111.5269 | 5495.4923 | 5898.2784 | 6315.798 | 6741.2084 | 7163.6521 | 7566.4537 | 7924.536 | 8200.7223 | 8340.4437
| TRUE | 1621 | 22006055 | FB | Blank | 66 | BUS NO.2 | HIBP | B | English Electric | CAG34_1363 | CAG34 1363 | CAG | Electromechanical |  | 0.033587 | 2190 |  | 5.5 | 0.0019187 | 0.00018099 | 0.0017378 | 20.3369 | 86.8731 | 107.2099 | 6.4741 | 0.7695 | 960.2806 |  | 7.3552 | 0.0040026 | 0.00037754 | 0.003625 | 42.4236 | 181.2211 | 223.6447 | 13.5052 | 1.6052 | 2003.1881 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 54.2636 | 0.11413 | 54.3777 | 14.6711 | 2.0677 | 1.2616 |  | 1074.7341 | 2241.9432 | 72.3781 | 2169.5651 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0.00019443 | 0.00020896 | 0.00022468 | 0.00024169 | 0.00026008 | 0.00028 | 0.00030155 | 0.00032489 | 0.00035017 | 0.00037754 | 0.0004072 | 0.00043935 | 0.00047418 | 0.00051194 | 0.00055288 | 0.00059728 | 0.00064543 | 0.00069766 | 0.00075434 | 0.00081583 | 0.00088257 | 0.00095501 | 0.0010336 | 0.001119 | 0.0012118 | 0.0013125 | 0.0014218 | 0.0015407 | 0.0016698 | 0.00181 | 1154.5574 | 1240.866 | 1334.2097 | 1435.1857 | 1544.4435 | 1662.6891 | 1790.69 | 1929.281 | 2079.3697 | 2241.9432 | 2418.0754 | 2608.9339 | 2815.7895 | 3040.0243 | 3283.1421 | 3546.7795 | 3832.7172 | 4142.893 | 4479.4161 | 4844.5821 | 5240.8899 | 5671.0594 | 6138.0521 | 6645.0916 | 7195.6883 | 7793.664 | 8443.1805 | 9148.7698 | 9915.3674 | 10748.3485 |  | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 45.2477 | 54.1587 | 71.7906 | 95.9937 | 129.3669 | 175.5724 | 239.7809 | 329.3036 | 454.4937 | 630.031 | 876.7535 | 1224.271 | 1714.6972 | 2407.9778 |  | 21.8473 | 23.4805 | 25.2468 | 27.1576 | 29.225 | 31.4626 | 33.8847 | 36.5072 | 39.3473 | 42.4236 | 45.7565 | 49.3681 | 53.2823 | 57.5255 | 62.1259 | 67.1146 | 72.5253 | 78.3947 | 84.7626 | 91.6725 | 99.1718 | 107.3117 | 116.1485 | 125.743 | 136.1618 | 147.4771 | 159.7677 | 173.1194 | 187.6255 | 203.3877 |  | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 32.4751 | 43.0476 | 57.5605 | 77.572 | 105.2781 | 143.7793 | 197.4595 | 272.527 | 377.784 | 525.7256 | 734.1068 | 1028.1799 | 1443.8901 |  | -5.2845 | -3.6513 | -1.8849 | 0.025792 | 2.0932 | 4.3308 | 6.7529 | 9.3754 | 12.2155 | 15.2918 | 18.6247 | 22.2363 | 26.1505 | 30.3937 | 34.9941 | 39.9828 | 45.3935 | 45.9196 | 41.715 | 34.1121 | 21.5998 | 2.0336 | -27.6308 | -71.7165 | -136.3652 | -230.3069 | -365.9579 | -560.9874 | -840.5544 | -1240.5024 |  | 93.3253 | 100.3019 | 107.847 | 116.0091 | 124.8407 | 134.3987 | 144.7453 | 155.9479 | 168.0799 | 181.2211 | 195.4582 | 210.8857 | 227.6063 | 245.7317 | 265.3834 | 286.6938 | 309.8067 | 334.8789 | 362.0808 | 391.598 | 423.6324 | 458.4039 | 496.1519 | 537.137 | 581.6429 | 629.9786 | 682.4804 | 739.5147 | 801.4804 | 868.812 |  | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.11413 | 0.13661 | 0.18108 | 0.24213 | 0.32631 | 0.44286 | 0.60482 | 0.83063 | 1.1464 | 1.5892 | 2.2115 | 3.0881 | 4.3251 | 6.0739 |  | 93.2112 | 100.1877 | 107.7329 | 115.895 | 124.7265 | 134.2846 | 144.6312 | 155.8338 | 167.9658 | 181.1069 | 195.3441 | 210.7716 | 227.4922 | 245.6175 | 265.2693 | 286.5797 | 309.6926 | 334.7423 | 361.8997 | 391.3558 | 423.306 | 457.961 | 495.5471 | 536.3064 | 580.4965 | 628.3894 | 680.2689 | 736.4266 | 797.1553 | 862.7382 |  | 87.9268 | 96.5365 | 105.8479 | 115.9208 | 126.8198 | 138.6154 | 151.3841 | 165.2092 | 180.1813 | 196.3988 | 213.9688 | 233.0079 | 253.6427 | 276.0112 | 300.2634 | 326.5625 | 355.0862 | 380.662 | 403.6147 | 425.4679 | 444.9059 | 459.9947 | 467.9163 | 464.5899 | 444.1313 | 398.0825 | 314.311 | 175.4392 | -43.3991 | -377.7642 |  | 6.9549 | 7.4748 | 8.0371 | 8.6454 | 9.3036 | 10.0159 | 10.7869 | 11.6218 | 12.5259 | 13.5052 | 14.5662 | 15.7159 | 16.962 | 18.3128 | 19.7773 | 21.3654 | 23.0879 | 24.9563 | 26.9835 | 29.1832 | 31.5705 | 34.1618 | 36.9749 | 40.0293 | 43.346 | 46.9482 | 50.8608 | 55.1112 | 59.7291 | 64.7469 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | -7.7162 | -7.1963 | -6.634 | -6.0257 | -5.3676 | -4.6553 | -3.8842 | -3.0494 | -2.1452 | -1.1659 | -0.10492 | 1.0448 | 2.2909 | 3.6416 | 5.1061 | 6.6943 | 8.4167 | 7.3959 | 3.7061 | -1.9418 | -10.3754 | -22.7658 | -40.7717 | -66.7442 | -104.0191 | -157.3333 | -233.418 | -341.8468 | -496.2448 | -716.0165 |  | 0.82665 | 0.88845 | 0.95528 | 1.0276 | 1.1058 | 1.1905 | 1.2821 | 1.3813 | 1.4888 | 1.6052 | 1.7313 | 1.868 | 2.0161 | 2.1766 | 2.3507 | 2.5395 | 2.7442 | 2.9663 | 3.2072 | 3.4687 | 3.7524 | 4.0604 | 4.3948 | 4.7578 | 5.152 | 5.5802 | 6.0452 | 6.5504 | 7.0993 | 7.6957 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | -1.241 | -1.1792 | -1.1124 | -1.0401 | -0.96189 | -0.87722 | -0.78558 | -0.68635 | -0.57888 | -0.46248 | -0.33637 | -0.19972 | -0.051613 | 0.10894 | 0.28301 | 0.47177 | 0.6765 | 0.49137 | -0.073404 | -0.91796 | -2.1593 | -3.9627 | -6.5625 | -10.2904 | -15.617 | -23.2104 | -34.0199 | -49.3953 | -71.2575 | -102.3421 |  | 1031.6031 | 1108.7204 | 1192.1234 | 1282.346 | 1379.9684 | 1485.6215 | 1599.991 | 1723.8228 | 1857.9278 | 2003.1881 | 2160.5631 | 2331.0963 | 2515.9228 | 2716.2777 | 2933.5048 | 3169.0663 | 3424.5531 | 3701.6968 | 4002.382 | 4328.6597 | 4682.7628 | 5067.1216 | 5484.3819 | 5937.4245 | 6429.3855 | 6963.6799 | 7544.0264 | 8174.4742 | 8859.4332 | 9603.7061 |  | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.2616 | 1.5101 | 2.0017 | 2.6765 | 3.607 | 4.8953 | 6.6856 | 9.1817 | 12.6723 | 17.5666 | 24.4458 | 34.1353 | 47.8095 | 67.1396 |  | 1030.3415 | 1107.4588 | 1190.8618 | 1281.0844 | 1378.7068 | 1484.3598 | 1598.7294 | 1722.5611 | 1856.6662 | 2001.9265 | 2159.3015 | 2329.8347 | 2514.6612 | 2715.0161 | 2932.2432 | 3167.8047 | 3423.2915 | 3700.1867 | 4000.3803 | 4325.9832 | 4679.1558 | 5062.2262 | 5477.6963 | 5928.2428 | 6416.7132 | 6946.1133 | 7519.5806 | 8140.3389 | 8811.6237 | 9536.5665 |  | 1109.311 | 1195.6197 | 1288.9633 | 1389.9393 | 1499.1971 | 1617.4427 | 1745.4436 | 1884.0346 | 2034.1233 | 2196.6969 | 2372.829 | 2563.6876 | 2770.5432 | 2994.7779 | 3237.8958 | 3501.5332 | 3787.4708 | 4088.736 | 4407.6277 | 4748.5913 | 5111.5269 | 5495.4923 | 5898.2784 | 6315.798 | 6741.2084 | 7163.6521 | 7566.4537 | 7924.536 | 8200.7223 | 8340.4437
| TRUE | 1622 | 22009789 | FB | Blank | 66 | CB BT1-2 | CB FAIL TIMER | Blank | RMS | 2T105 | 2T105 | RMS 2T1XX | Electronic |  | 0 | 2190 |  | 3.6151 | 0.004397 | 0 | 0.004397 | 23.0844 | 0 | 23.0844 | 12.4815 | 1.7593 | 0 |  | 10.5562 | 0.050929 | 0 | 0.050929 | 267.3781 | 0 | 267.3781 | 144.5683 | 20.3768 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 37.3252 | 432.3232 | 43.8691 | 388.4541 |  | 0.10716 |  | 4.024 | 4.4792 | 4.9858 | 5.5498 | 6.1775 | 6.8763 | 7.654 | 8.5198 | 9.4835 | 10.5562 | 11.7502 | 13.0793 | 14.5587 | 16.2055 | 18.0385 | 20.0789 | 22.3501 | 24.8781 | 27.6922 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0044569 | 0.0057019 | 0.0073492 | 0.0095373 | 0.012454 | 0.016355 | 0.021586 | 0.028623 | 0.03811 | 0.050929 | 0.068287 | 0.091832 | 0.12382 | 0.16736 | 0.22668 | 0.30761 | 0.41814 | 0.56925 | 0.77601 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8332 | 48.4018 | 62.3856 | 80.9597 | 105.7185 | 138.8291 | 183.2403 | 242.9708 | 323.5027 | 432.3232 | 579.6676 | 779.5395 | 1051.1144 | 1420.6671 | 1924.2244 | 2611.2128 | 3549.4776 | 4832.1911 | 6587.3618 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 23.3986 | 29.935 | 38.5835 | 50.071 | 65.3835 | 85.8614 | 113.3283 | 150.2697 | 200.0761 | 267.3781 | 358.5059 | 482.1203 | 650.0807 | 878.6373 | 1190.0714 | 1614.9518 | 2195.2386 | 2988.556 | 4074.0731 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | -3.733 | 2.8033 | 11.4518 | 22.9393 | 38.2519 | 58.7297 | 86.1966 | 123.138 | 172.9444 | 240.2464 | 331.3742 | 454.9887 | 622.949 | 851.5056 | 1162.9397 | 1587.8201 | 2168.107 | 2956.0811 | 4031.0257 | 4149.149 | 4129.1376 | 4101.4316 | 4062.9306 | 4009.2506 | 3934.1835 | 3828.9269 | 3680.986 | 3472.6058 | 3178.5341 | 2762.8258 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -3.733 | 2.8033 | 11.4518 | 22.9393 | 38.2519 | 58.7297 | 86.1966 | 123.138 | 172.9444 | 240.2464 | 331.3742 | 454.9887 | 622.949 | 851.5056 | 1162.9397 | 1587.8201 | 2168.107 | 2956.0811 | 4031.0257 | 4149.149 | 4129.1376 | 4101.4316 | 4062.9306 | 4009.2506 | 3934.1835 | 3828.9269 | 3680.986 | 3472.6058 | 3178.5341 | 2762.8258 |  | 12.6514 | 16.1855 | 20.8617 | 27.0728 | 35.3521 | 46.4243 | 61.2753 | 81.2491 | 108.1789 | 144.5683 | 193.8401 | 260.6771 | 351.4913 | 475.0693 | 643.4582 | 873.1863 | 1186.9409 | 1615.8787 | 2202.8055 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | -2.0184 | 1.5157 | 6.1919 | 12.403 | 20.6824 | 31.7545 | 46.6056 | 66.5793 | 93.5091 | 129.8986 | 179.1703 | 246.0073 | 336.8215 | 460.3995 | 628.7885 | 858.5165 | 1172.2711 | 1598.3199 | 2179.5303 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 1.7832 | 2.2813 | 2.9404 | 3.8159 | 4.9828 | 6.5435 | 8.6367 | 11.452 | 15.2477 | 20.3768 | 27.3216 | 36.7422 | 49.5423 | 66.9605 | 90.6948 | 123.0747 | 167.2981 | 227.7564 | 310.4832 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | -0.28449 | 0.21364 | 0.87274 | 1.7482 | 2.9152 | 4.4758 | 6.569 | 9.3843 | 13.18 | 18.3091 | 25.2539 | 34.6745 | 47.4746 | 64.8928 | 88.6271 | 121.007 | 165.2304 | 225.2815 | 307.2025 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -6.0359 | 4.5327 | 18.5164 | 37.0905 | 61.8494 | 94.9599 | 139.3712 | 199.1016 | 279.6335 | 388.4541 | 535.7984 | 735.6704 | 1007.2452 | 1376.7979 | 1880.3553 | 2567.3437 | 3505.6084 | 4779.6825 | 6517.7585 | 6708.7519 | 6676.3955 | 6631.5977 | 6569.3455 | 6482.5504 | 6361.1745 | 6190.9854 | 5951.78 | 5614.8504 | 5139.3663 | 4467.2083
| TRUE | 1623 | 22009790 | FB | Blank | 66 | CB BT2-3 | CB FAIL TIMER | Blank | RMS | 2T105 | 2T105 | RMS 2T1XX | Electronic |  | 0 | 2190 |  | 3.6151 | 0.004397 | 0 | 0.004397 | 23.0844 | 0 | 23.0844 | 12.4815 | 1.7593 | 0 |  | 10.5562 | 0.050929 | 0 | 0.050929 | 267.3781 | 0 | 267.3781 | 144.5683 | 20.3768 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 37.3252 | 432.3232 | 43.8691 | 388.4541 |  | 0.10716 |  | 4.024 | 4.4792 | 4.9858 | 5.5498 | 6.1775 | 6.8763 | 7.654 | 8.5198 | 9.4835 | 10.5562 | 11.7502 | 13.0793 | 14.5587 | 16.2055 | 18.0385 | 20.0789 | 22.3501 | 24.8781 | 27.6922 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0044569 | 0.0057019 | 0.0073492 | 0.0095373 | 0.012454 | 0.016355 | 0.021586 | 0.028623 | 0.03811 | 0.050929 | 0.068287 | 0.091832 | 0.12382 | 0.16736 | 0.22668 | 0.30761 | 0.41814 | 0.56925 | 0.77601 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8332 | 48.4018 | 62.3856 | 80.9597 | 105.7185 | 138.8291 | 183.2403 | 242.9708 | 323.5027 | 432.3232 | 579.6676 | 779.5395 | 1051.1144 | 1420.6671 | 1924.2244 | 2611.2128 | 3549.4776 | 4832.1911 | 6587.3618 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 | 6801.8209 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 23.3986 | 29.935 | 38.5835 | 50.071 | 65.3835 | 85.8614 | 113.3283 | 150.2697 | 200.0761 | 267.3781 | 358.5059 | 482.1203 | 650.0807 | 878.6373 | 1190.0714 | 1614.9518 | 2195.2386 | 2988.556 | 4074.0731 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 | 4206.7092 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | -3.733 | 2.8033 | 11.4518 | 22.9393 | 38.2519 | 58.7297 | 86.1966 | 123.138 | 172.9444 | 240.2464 | 331.3742 | 454.9887 | 622.949 | 851.5056 | 1162.9397 | 1587.8201 | 2168.107 | 2956.0811 | 4031.0257 | 4149.149 | 4129.1376 | 4101.4316 | 4062.9306 | 4009.2506 | 3934.1835 | 3828.9269 | 3680.986 | 3472.6058 | 3178.5341 | 2762.8258 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -3.733 | 2.8033 | 11.4518 | 22.9393 | 38.2519 | 58.7297 | 86.1966 | 123.138 | 172.9444 | 240.2464 | 331.3742 | 454.9887 | 622.949 | 851.5056 | 1162.9397 | 1587.8201 | 2168.107 | 2956.0811 | 4031.0257 | 4149.149 | 4129.1376 | 4101.4316 | 4062.9306 | 4009.2506 | 3934.1835 | 3828.9269 | 3680.986 | 3472.6058 | 3178.5341 | 2762.8258 |  | 12.6514 | 16.1855 | 20.8617 | 27.0728 | 35.3521 | 46.4243 | 61.2753 | 81.2491 | 108.1789 | 144.5683 | 193.8401 | 260.6771 | 351.4913 | 475.0693 | 643.4582 | 873.1863 | 1186.9409 | 1615.8787 | 2202.8055 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | -2.0184 | 1.5157 | 6.1919 | 12.403 | 20.6824 | 31.7545 | 46.6056 | 66.5793 | 93.5091 | 129.8986 | 179.1703 | 246.0073 | 336.8215 | 460.3995 | 628.7885 | 858.5165 | 1172.2711 | 1598.3199 | 2179.5303 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 1.7832 | 2.2813 | 2.9404 | 3.8159 | 4.9828 | 6.5435 | 8.6367 | 11.452 | 15.2477 | 20.3768 | 27.3216 | 36.7422 | 49.5423 | 66.9605 | 90.6948 | 123.0747 | 167.2981 | 227.7564 | 310.4832 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | -0.28449 | 0.21364 | 0.87274 | 1.7482 | 2.9152 | 4.4758 | 6.569 | 9.3843 | 13.18 | 18.3091 | 25.2539 | 34.6745 | 47.4746 | 64.8928 | 88.6271 | 121.007 | 165.2304 | 225.2815 | 307.2025 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -6.0359 | 4.5327 | 18.5164 | 37.0905 | 61.8494 | 94.9599 | 139.3712 | 199.1016 | 279.6335 | 388.4541 | 535.7984 | 735.6704 | 1007.2452 | 1376.7979 | 1880.3553 | 2567.3437 | 3505.6084 | 4779.6825 | 6517.7585 | 6708.7519 | 6676.3955 | 6631.5977 | 6569.3455 | 6482.5504 | 6361.1745 | 6190.9854 | 5951.78 | 5614.8504 | 5139.3663 | 4467.2083
| FALSE | 1624 | 22006050 | FB | FB-FBTS | 66 | FBTS LINE | PILOT WIRE | X | AEI | DS5_649 | DS5 649 | DS5 | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 101.3994 | 1577.827 | 1679.2265 | 45.1415 | 3.7652 | 174.4104 |  | 7.3552 | 0.019459 | 0.0068571 | 0.012602 | 211.5238 | 3291.4176 | 3502.9413 | 94.1672 | 7.8543 | 363.8279 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.5336 | 54.7981 | 14.6761 | 2.0677 | 0.058983 |  | 1902.5436 | 3968.7908 | 71.6009 | 3897.1899 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.010021 | 0.01077 | 0.011581 | 0.012457 | 0.013405 | 0.014432 | 0.015543 | 0.016746 | 0.018048 | 0.019459 | 0.020988 | 0.022645 | 0.02444 | 0.026387 | 0.028497 | 0.030785 | 0.033267 | 0.035959 | 0.03888 | 0.04205 | 0.045489 | 0.049223 | 0.053276 | 0.057677 | 0.062456 | 0.067647 | 0.073284 | 0.079409 | 0.086062 | 0.093293 |  | 0.0035313 | 0.0037953 | 0.0040808 | 0.0043896 | 0.0047238 | 0.0050854 | 0.0054769 | 0.0059008 | 0.0063599 | 0.0068571 | 0.0073958 | 0.0079796 | 0.0086123 | 0.0092981 | 0.010042 | 0.010848 | 0.011723 | 0.012671 | 0.013701 | 0.014817 | 0.01603 | 0.017345 | 0.018774 | 0.020324 | 0.022008 | 0.023837 | 0.025824 | 0.027982 | 0.030327 | 0.032874 | 2043.8504 | 2196.638 | 2361.8792 | 2540.6316 | 2734.0447 | 2943.3684 | 3169.9616 | 3415.3017 | 3680.9956 | 3968.7908 | 4280.5879 | 4618.4546 | 4984.6397 | 5381.5904 | 5811.9688 | 6278.6718 | 6784.8518 | 7333.9392 | 7929.6679 | 8576.1015 | 9277.6637 | 10039.1696 | 10865.8613 | 11763.446 | 12738.1375 | 13796.7015 | 14946.5054 | 16195.572 | 17552.6383 | 19027.2195 |  | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 53.2338 | 70.5646 | 94.3544 | 127.1577 | 172.5742 | 235.6862 | 323.6801 | 446.7325 | 619.2722 | 861.7814 | 1203.3645 | 1685.4158 | 2366.8574 |  | 108.9306 | 117.0737 | 125.8805 | 135.4075 | 145.7158 | 156.872 | 168.9487 | 182.0246 | 196.1852 | 211.5238 | 228.1415 | 246.1487 | 265.6652 | 286.8214 | 309.7592 | 334.633 | 361.6107 | 390.8753 | 422.6257 | 457.0786 | 494.4696 | 535.0554 | 579.1154 | 626.9538 | 678.9017 | 735.3197 | 796.6006 | 863.1718 | 935.499 | 1014.0895 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 81.7984 | 89.9415 | 98.7483 | 108.2752 | 118.5835 | 129.7398 | 141.8165 | 154.8923 | 169.053 | 184.3915 | 201.0093 | 219.0165 | 238.533 | 259.6892 | 282.627 | 307.5007 | 334.4785 | 358.3997 | 379.5774 | 399.5171 | 416.8963 | 429.7755 | 435.3337 | 429.4909 | 406.3701 | 357.5293 | 270.8661 | 129.0526 | -92.6982 | -429.825 |  | 1695.0164 | 1821.7269 | 1958.7656 | 2107.0094 | 2267.4117 | 2441.0092 | 2628.9285 | 2832.3952 | 3052.7418 | 3291.4176 | 3549.9988 | 3830.2 | 4133.8866 | 4463.0877 | 4820.0113 | 5207.0598 | 5626.8475 | 6082.2195 | 6576.2722 | 7112.3758 | 7694.1988 | 8325.7347 | 9011.3309 | 9755.7204 | 10564.0564 | 11441.9501 | 12395.5113 | 13431.3935 | 14556.8425 | 15779.7496 |  | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.63868 | 0.84661 | 1.132 | 1.5256 | 2.0705 | 2.8277 | 3.8834 | 5.3597 | 7.4298 | 10.3393 | 14.4375 | 20.221 | 28.3967 |  | 1694.4828 | 1821.1933 | 1958.232 | 2106.4758 | 2266.8782 | 2440.4756 | 2628.3949 | 2831.8616 | 3052.2082 | 3290.884 | 3549.4652 | 3829.6664 | 4133.353 | 4462.5541 | 4819.4777 | 5206.5262 | 5626.3139 | 6081.5808 | 6575.4256 | 7111.2437 | 7692.6732 | 8323.6643 | 9008.5032 | 9751.837 | 10558.6967 | 11434.5203 | 12385.1719 | 13416.956 | 14536.6215 | 15751.3529 |  | 1776.2811 | 1911.1348 | 2056.9803 | 2214.751 | 2385.4617 | 2570.2154 | 2770.2114 | 2986.754 | 3221.2612 | 3475.2755 | 3750.4745 | 4048.6829 | 4371.886 | 4722.2433 | 5102.1047 | 5514.0269 | 5960.7924 | 6439.9805 | 6955.003 | 7510.7609 | 8109.5695 | 8753.4398 | 9443.8369 | 10181.3279 | 10965.0667 | 11792.0496 | 12656.038 | 13546.0086 | 14443.9233 | 15321.5279 |  | 48.4943 | 52.1195 | 56.0402 | 60.2814 | 64.8705 | 69.8371 | 75.2135 | 81.0346 | 87.3387 | 94.1672 | 101.5652 | 109.5818 | 118.2702 | 127.6887 | 137.9002 | 148.9736 | 160.9837 | 174.0119 | 188.1467 | 203.4846 | 220.1305 | 238.1987 | 257.8136 | 279.1105 | 302.237 | 327.3535 | 354.6348 | 384.2713 | 416.4703 | 451.4576 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 33.8182 | 37.4434 | 41.3641 | 45.6053 | 50.1944 | 55.161 | 60.5374 | 66.3585 | 72.6627 | 79.4912 | 86.8891 | 94.9057 | 103.5941 | 113.0126 | 123.2241 | 134.2976 | 146.3077 | 156.4455 | 164.8615 | 172.3491 | 178.1704 | 181.2518 | 180.0407 | 172.3009 | 154.822 | 123.0029 | 70.2599 | -12.8209 | -139.6916 | -329.5698 |  | 4.0448 | 4.3472 | 4.6742 | 5.0279 | 5.4107 | 5.825 | 6.2734 | 6.7589 | 7.2847 | 7.8543 | 8.4713 | 9.14 | 9.8647 | 10.6502 | 11.5019 | 12.4256 | 13.4273 | 14.5139 | 15.6929 | 16.9722 | 18.3606 | 19.8676 | 21.5037 | 23.28 | 25.2089 | 27.3038 | 29.5793 | 32.0512 | 34.7369 | 37.6551 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 1.9771 | 2.2795 | 2.6065 | 2.9602 | 3.343 | 3.7573 | 4.2057 | 4.6912 | 5.217 | 5.7866 | 6.4036 | 7.0723 | 7.797 | 8.5825 | 9.4342 | 10.3579 | 11.3596 | 12.039 | 12.4123 | 12.5855 | 12.4489 | 11.8444 | 10.5463 | 8.2317 | 4.4397 | -1.4869 | -10.486 | -23.8948 | -43.6203 | -72.3832 |  | 187.3643 | 201.3707 | 216.5187 | 232.9054 | 250.636 | 269.8252 | 290.5975 | 313.0883 | 337.4451 | 363.8279 | 392.4111 | 423.384 | 456.9531 | 493.3424 | 532.7962 | 575.5799 | 621.9825 | 672.3186 | 726.9304 | 786.1904 | 850.5041 | 920.3131 | 996.0978 | 1078.3814 | 1167.7335 | 1264.7744 | 1370.1795 | 1484.6843 | 1609.0895 | 1744.2677 |  | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.070599 | 0.093583 | 0.12513 | 0.16864 | 0.22887 | 0.31257 | 0.42926 | 0.59246 | 0.82128 | 1.1429 | 1.5959 | 2.2352 | 3.1389 |  | 187.3054 | 201.3117 | 216.4598 | 232.8464 | 250.577 | 269.7662 | 290.5385 | 313.0294 | 337.3861 | 363.7689 | 392.3521 | 423.3251 | 456.8941 | 493.2834 | 532.7372 | 575.5209 | 621.9235 | 672.248 | 726.8368 | 786.0652 | 850.3355 | 920.0842 | 995.7852 | 1077.9521 | 1167.141 | 1263.9532 | 1369.0366 | 1483.0884 | 1606.8543 | 1741.1288 |  | 1999.3818 | 2152.1694 | 2317.4106 | 2496.1629 | 2689.5761 | 2898.8998 | 3125.493 | 3370.8331 | 3636.527 | 3924.3222 | 4236.1193 | 4573.9859 | 4940.1711 | 5337.1218 | 5767.5002 | 6234.2032 | 6740.3832 | 7280.7131 | 7859.1135 | 8481.7607 | 9150.5243 | 9866.6202 | 10630.2091 | 11439.8126 | 12291.4695 | 13177.5187 | 14084.8485 | 14992.3813 | 15867.4658 | 16660.7037
| FALSE | 1625 | 22006053 | FB | FB-FBTS | 66 | FBTS LINE | PILOT WIRE | Y | English Electric | DSF7_1489 | DSF7 1489 | DSF7 | Electromechanical |  | 0.016937 | 2190 |  | 5.5 | 0.0019187 | 9.4276e-05 | 0.0018245 | 20.2458 | 45.2523 | 65.4981 | 5.9818 | 0.76863 | 5.0021 |  | 7.3552 | 0.0040026 | 0.00019666 | 0.0038059 | 42.2337 | 94.3983 | 136.6319 | 12.4783 | 1.6034 | 10.4346 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 54.2635 | 0.057554 | 54.321 | 14.6705 | 2.0677 | 0.0063619 |  | 77.2506 | 161.1483 | 71.0655 | 90.0828 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0.00010128 | 0.00010885 | 0.00011704 | 0.00012589 | 0.00013548 | 0.00014585 | 0.00015708 | 0.00016924 | 0.0001824 | 0.00019666 | 0.00021211 | 0.00022886 | 0.000247 | 0.00026667 | 0.000288 | 0.00031112 | 0.00033621 | 0.00036341 | 0.00039293 | 0.00042497 | 0.00045973 | 0.00049746 | 0.00053843 | 0.00058291 | 0.00063121 | 0.00068366 | 0.00074063 | 0.00080253 | 0.00086978 | 0.00094284 | 82.9882 | 89.192 | 95.9014 | 103.1595 | 111.0128 | 119.5122 | 128.7127 | 138.6745 | 149.4627 | 161.1483 | 173.8085 | 187.5272 | 202.3957 | 218.5134 | 235.9885 | 254.9384 | 275.4913 | 297.7864 | 321.9752 | 348.223 | 376.7091 | 407.6292 | 441.1961 | 477.6415 | 517.2178 | 560.1996 | 606.8861 | 657.603 | 712.7051 | 772.5789 |  | 43.9345 | 43.9345 | 43.9345 | 43.9345 | 43.9345 | 43.9345 | 43.9345 | 43.9345 | 43.9345 | 43.9345 | 43.9345 | 43.9345 | 43.9345 | 43.9345 | 43.9345 | 43.9345 | 43.9345 | 52.5868 | 69.707 | 93.2077 | 125.6122 | 170.4768 | 232.8217 | 319.7461 | 441.3029 | 611.7455 | 851.3073 | 1188.7388 | 1664.9312 | 2338.0906 |  | 21.7495 | 23.3754 | 25.1338 | 27.036 | 29.0942 | 31.3217 | 33.733 | 36.3438 | 39.1711 | 42.2337 | 45.5517 | 49.147 | 53.0438 | 57.2679 | 61.8478 | 66.8142 | 72.2006 | 78.0437 | 84.3832 | 91.2621 | 98.7278 | 106.8313 | 115.6285 | 125.1801 | 135.5522 | 146.8169 | 159.0525 | 172.3443 | 186.7855 | 202.4772 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | -5.3822 | -3.7563 | -1.9979 | -0.095727 | 1.9625 | 4.19 | 6.6013 | 9.212 | 12.0394 | 15.102 | 18.4199 | 22.0153 | 25.9121 | 30.1362 | 34.716 | 39.6824 | 45.0689 | 45.5688 | 41.3356 | 33.7018 | 21.156 | 1.5535 | -28.1504 | -72.279 | -136.9741 | -230.9663 | -366.6719 | -561.7607 | -841.392 | -1241.4096 |  | 48.6133 | 52.2474 | 56.1776 | 60.4293 | 65.0296 | 70.0084 | 75.398 | 81.2334 | 87.553 | 94.3983 | 101.8144 | 109.8506 | 118.5604 | 128.0019 | 138.2385 | 149.3391 | 161.3787 | 174.4388 | 188.6083 | 203.9838 | 220.6706 | 238.7831 | 258.4461 | 279.7953 | 302.9784 | 328.1565 | 355.5048 | 385.214 | 417.492 | 452.5651 |  | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.068888 | 0.091315 | 0.1221 | 0.16455 | 0.22332 | 0.30499 | 0.41886 | 0.5781 | 0.80138 | 1.1152 | 1.5572 | 2.181 | 3.0629 |  | 48.5557 | 52.1898 | 56.1201 | 60.3717 | 64.9721 | 69.9509 | 75.3404 | 81.1759 | 87.4955 | 94.3407 | 101.7568 | 109.7931 | 118.5028 | 127.9443 | 138.181 | 149.2816 | 161.3211 | 174.3699 | 188.517 | 203.8617 | 220.506 | 238.5598 | 258.1411 | 279.3764 | 302.4003 | 327.3551 | 354.3896 | 383.6568 | 415.311 | 449.5023 |  | 43.1735 | 48.4335 | 54.1222 | 60.276 | 66.9346 | 74.1409 | 81.9417 | 90.3879 | 99.5349 | 109.4427 | 120.1768 | 131.8084 | 144.4149 | 158.0805 | 172.897 | 188.964 | 206.39 | 219.9387 | 229.8526 | 237.5635 | 241.662 | 240.1132 | 229.9906 | 207.0974 | 165.4262 | 96.3889 | -12.2824 | -178.104 | -426.081 | -791.9073 |  | 6.4261 | 6.9065 | 7.426 | 7.988 | 8.5961 | 9.2543 | 9.9667 | 10.7381 | 11.5735 | 12.4783 | 13.4586 | 14.5209 | 15.6723 | 16.9203 | 18.2735 | 19.7408 | 21.3323 | 23.0587 | 24.9317 | 26.9642 | 29.17 | 31.5643 | 34.1635 | 36.9856 | 40.0501 | 43.3783 | 46.9935 | 50.9207 | 55.1874 | 59.8237 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | -8.2444 | -7.764 | -7.2445 | -6.6824 | -6.0743 | -5.4162 | -4.7038 | -3.9324 | -3.097 | -2.1922 | -1.2118 | -0.14954 | 1.0018 | 2.2498 | 3.603 | 5.0704 | 6.6619 | 5.4991 | 1.6554 | -4.1594 | -12.774 | -25.3608 | -43.5796 | -69.783 | -107.3083 | -160.8938 | -237.2724 | -346.0192 | -500.7611 | -720.9041 |  | 0.82572 | 0.88745 | 0.95421 | 1.0264 | 1.1046 | 1.1891 | 1.2807 | 1.3798 | 1.4871 | 1.6034 | 1.7294 | 1.8659 | 2.0138 | 2.1742 | 2.3481 | 2.5366 | 2.7411 | 2.9629 | 3.2036 | 3.4648 | 3.7482 | 4.0559 | 4.3898 | 4.7525 | 5.1462 | 5.5739 | 6.0384 | 6.5431 | 7.0913 | 7.687 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | -1.242 | -1.1802 | -1.1135 | -1.0413 | -0.96313 | -0.87856 | -0.78702 | -0.6879 | -0.58056 | -0.46429 | -0.33832 | -0.20182 | -0.053884 | 0.10649 | 0.28036 | 0.46891 | 0.67341 | 0.48803 | -0.077016 | -0.92187 | -2.1635 | -3.9673 | -6.5675 | -10.2958 | -15.6228 | -23.2167 | -34.0267 | -49.4026 | -71.2655 | -102.3507 |  | 5.3736 | 5.7753 | 6.2098 | 6.6798 | 7.1883 | 7.7386 | 8.3344 | 8.9794 | 9.678 | 10.4346 | 11.2544 | 12.1427 | 13.1055 | 14.1491 | 15.2807 | 16.5077 | 17.8385 | 19.2822 | 20.8485 | 22.548 | 24.3926 | 26.3947 | 28.5682 | 30.9281 | 33.4907 | 36.2739 | 39.2969 | 42.5809 | 46.1489 | 50.0258 |  | 0.0063619 | 0.0063619 | 0.0063619 | 0.0063619 | 0.0063619 | 0.0063619 | 0.0063619 | 0.0063619 | 0.0063619 | 0.0063619 | 0.0063619 | 0.0063619 | 0.0063619 | 0.0063619 | 0.0063619 | 0.0063619 | 0.0063619 | 0.0076148 | 0.010094 | 0.013497 | 0.018189 | 0.024686 | 0.033714 | 0.046301 | 0.063902 | 0.088583 | 0.12327 | 0.17213 | 0.24109 | 0.33857 |  | 5.3673 | 5.769 | 6.2034 | 6.6734 | 7.1819 | 7.7323 | 8.328 | 8.973 | 9.6716 | 10.4283 | 11.248 | 12.1363 | 13.0991 | 14.1428 | 15.2743 | 16.5013 | 17.8322 | 19.2746 | 20.8384 | 22.5345 | 24.3744 | 26.37 | 28.5345 | 30.8818 | 33.4268 | 36.1853 | 39.1736 | 42.4088 | 45.9078 | 49.6872 |  | 39.0544 | 45.2582 | 51.9676 | 59.2257 | 67.079 | 75.5784 | 84.7789 | 94.7407 | 105.5289 | 117.2145 | 129.8747 | 143.5934 | 158.4619 | 174.5796 | 192.0547 | 211.0046 | 231.5575 | 245.2004 | 252.2694 | 255.0168 | 251.0989 | 237.1551 | 208.3781 | 157.9004 | 75.9219 | -51.5363 | -244.4078 | -531.117 | -952.1998 | -1565.4749
| FALSE | 1626 | 22015773 | FB | FB-FBTS | 66 | FBTS LINE | CURRENT INTERLOCK | X | Alstom | MCAG39 | MCAG39 | MCAG | Electromechanical |  | 0.15703 | 2190 |  | 5.5 | 0.0019187 | 0.00067613 | 0.0012426 | 20.8568 | 324.5419 | 345.3987 | 9.2851 | 0.77445 | 179.3717 |  | 7.3552 | 0.0040026 | 0.0014104 | 0.0025922 | 43.5081 | 677.0089 | 720.517 | 19.3692 | 1.6155 | 374.1773 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.5336 | 54.7981 | 14.6761 | 2.0677 | 0.29491 |  | 534.8299 | 1115.6791 | 71.8368 | 1043.8422 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0.00072635 | 0.00078064 | 0.00083937 | 0.00090289 | 0.00097163 | 0.001046 | 0.0011265 | 0.0012137 | 0.0013082 | 0.0014104 | 0.0015212 | 0.0016413 | 0.0017714 | 0.0019125 | 0.0020655 | 0.0022313 | 0.0024112 | 0.0026063 | 0.0028181 | 0.0030478 | 0.0032971 | 0.0035677 | 0.0038615 | 0.0041805 | 0.0045269 | 0.0049031 | 0.0053117 | 0.0057556 | 0.0062379 | 0.0067619 | 574.5531 | 617.5037 | 663.9552 | 714.2048 | 768.5758 | 827.4194 | 891.1177 | 960.086 | 1034.7761 | 1115.6791 | 1203.3293 | 1298.308 | 1401.2475 | 1512.8355 | 1633.8205 | 1765.0169 | 1907.3107 | 2061.6663 | 2229.1335 | 2410.8544 | 2608.0727 | 2822.142 | 3054.5359 | 3306.8587 | 3580.8572 | 3878.4334 | 4201.6584 | 4552.7874 | 4934.2764 | 5348.8005 |  | 44.711 | 44.711 | 44.711 | 44.711 | 44.711 | 44.711 | 44.711 | 44.711 | 44.711 | 44.711 | 44.711 | 44.711 | 44.711 | 44.711 | 44.711 | 44.711 | 44.711 | 53.5162 | 70.9389 | 94.855 | 127.8323 | 173.4897 | 236.9365 | 325.3972 | 449.1023 | 622.5573 | 866.3529 | 1209.7481 | 1694.3566 | 2379.4131 |  | 22.4059 | 24.0808 | 25.8923 | 27.8518 | 29.9722 | 32.2669 | 34.7509 | 37.4405 | 40.3532 | 43.5081 | 46.9262 | 50.6301 | 54.6445 | 58.9961 | 63.7141 | 68.8304 | 74.3794 | 80.3988 | 86.9295 | 94.0161 | 101.707 | 110.0551 | 119.1178 | 128.9576 | 139.6427 | 151.2473 | 163.8521 | 177.5451 | 192.422 | 208.5872 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | -4.7264 | -3.0515 | -1.24 | 0.7196 | 2.8399 | 5.1346 | 7.6187 | 10.3082 | 13.2209 | 16.3759 | 19.794 | 23.4979 | 27.5122 | 31.8638 | 36.5819 | 41.6981 | 47.2472 | 47.9232 | 43.8812 | 36.4547 | 24.1338 | 4.7752 | -24.6639 | -68.5053 | -132.8889 | -226.5431 | -361.8824 | -556.5741 | -835.7752 | -1235.3273 |  | 348.6465 | 374.7095 | 402.8968 | 433.389 | 466.382 | 502.0891 | 540.7421 | 582.593 | 627.9159 | 677.0089 | 730.1963 | 787.8306 | 850.2956 | 918.0087 | 991.4241 | 1071.0357 | 1157.3815 | 1251.0466 | 1352.6679 | 1462.9386 | 1582.6133 | 1712.5134 | 1853.533 | 2006.6459 | 2172.9119 | 2353.4851 | 2549.6223 | 2762.692 | 2994.1847 | 3245.7234 |  | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.63868 | 0.84661 | 1.132 | 1.5256 | 2.0705 | 2.8277 | 3.8834 | 5.3597 | 7.4298 | 10.3393 | 14.4375 | 20.221 | 28.3967 |  | 348.1129 | 374.1759 | 402.3632 | 432.8554 | 465.8484 | 501.5555 | 540.2085 | 582.0594 | 627.3823 | 676.4753 | 729.6627 | 787.297 | 849.762 | 917.4751 | 990.8905 | 1070.5021 | 1156.8479 | 1250.4079 | 1351.8213 | 1461.8065 | 1581.0877 | 1710.4429 | 1850.7054 | 2002.7625 | 2167.5521 | 2346.0553 | 2539.2829 | 2748.2545 | 2973.9636 | 3217.3267 |  | 343.3865 | 371.1244 | 401.1233 | 433.575 | 468.6883 | 506.6901 | 547.8272 | 592.3676 | 640.6032 | 692.8512 | 749.4567 | 810.7949 | 877.2743 | 949.339 | 1027.4723 | 1112.2003 | 1204.0951 | 1298.3311 | 1395.7025 | 1498.2612 | 1605.2214 | 1715.2181 | 1826.0414 | 1934.2572 | 2034.6632 | 2119.5121 | 2177.4005 | 2191.6804 | 2138.1884 | 1981.9994 |  | 9.9748 | 10.7204 | 11.5269 | 12.3992 | 13.3432 | 14.3647 | 15.4706 | 16.6679 | 17.9646 | 19.3692 | 20.8909 | 22.5398 | 24.3269 | 26.2642 | 28.3646 | 30.6423 | 33.1126 | 35.7924 | 38.6997 | 41.8546 | 45.2785 | 48.9949 | 53.0295 | 57.41 | 62.1669 | 67.3331 | 72.9445 | 79.0404 | 85.6634 | 92.8599 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | -4.7013 | -3.9557 | -3.1492 | -2.2769 | -1.3329 | -0.31136 | 0.7945 | 1.9919 | 3.2885 | 4.6931 | 6.2148 | 7.8637 | 9.6508 | 11.5881 | 13.6885 | 15.9662 | 18.4365 | 18.226 | 15.4145 | 10.719 | 3.3183 | -7.952 | -24.7435 | -49.3996 | -85.2481 | -137.0175 | -211.4304 | -318.0518 | -470.4985 | -688.1675 |  | 0.83197 | 0.89417 | 0.96143 | 1.0342 | 1.1129 | 1.1981 | 1.2904 | 1.3902 | 1.4984 | 1.6155 | 1.7425 | 1.88 | 2.0291 | 2.1906 | 2.3658 | 2.5558 | 2.7618 | 2.9854 | 3.2279 | 3.491 | 3.7766 | 4.0866 | 4.4231 | 4.7884 | 5.1852 | 5.6161 | 6.0841 | 6.5926 | 7.145 | 7.7452 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | -1.2357 | -1.1735 | -1.1063 | -1.0335 | -0.95478 | -0.86957 | -0.77733 | -0.67747 | -0.56931 | -0.45216 | -0.32524 | -0.18771 | -0.038649 | 0.12293 | 0.29812 | 0.4881 | 0.69415 | 0.51045 | -0.052781 | -0.89566 | -2.1352 | -3.9366 | -6.5343 | -10.2599 | -15.584 | -23.1747 | -33.9812 | -49.3534 | -71.2122 | -102.293 |  | 192.6941 | 207.0989 | 222.6778 | 239.5305 | 257.7655 | 277.5005 | 298.8637 | 321.9944 | 347.044 | 374.1773 | 403.5735 | 435.4275 | 469.9514 | 507.3759 | 547.952 | 591.9527 | 639.6753 | 691.4432 | 747.6085 | 808.5542 | 874.6974 | 946.4921 | 1024.4325 | 1109.0568 | 1200.9506 | 1300.7519 | 1409.1554 | 1526.9173 | 1654.8614 | 1793.8848 |  | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.35299 | 0.46791 | 0.62566 | 0.84318 | 1.1443 | 1.5628 | 2.1463 | 2.9623 | 4.1064 | 5.7145 | 7.9795 | 11.176 | 15.6946 |  | 192.3991 | 206.8039 | 222.3829 | 239.2356 | 257.4706 | 277.2056 | 298.5688 | 321.6995 | 346.7491 | 373.8824 | 403.2786 | 435.1326 | 469.6565 | 507.081 | 547.657 | 591.6578 | 639.3804 | 691.0902 | 747.1405 | 807.9285 | 873.8542 | 945.3478 | 1022.8697 | 1106.9104 | 1197.9883 | 1296.6455 | 1403.4409 | 1518.9377 | 1643.6854 | 1778.1901 |  | 529.8486 | 572.7991 | 619.2506 | 669.5002 | 723.8712 | 782.7148 | 846.4131 | 915.3815 | 990.0715 | 1070.9745 | 1158.6248 | 1253.6035 | 1356.5429 | 1468.131 | 1589.116 | 1720.3123 | 1862.6061 | 2008.1578 | 2158.2047 | 2316.0131 | 2480.2588 | 2648.6772 | 2817.6334 | 2981.5082 | 3131.8194 | 3255.9656 | 3335.4298 | 3343.213 | 3240.1631 | 2969.729
| FALSE | 1627 | 22015775 | FB | FB-FBTS | 66 | FBTS LINE | CURRENT INTERLOCK | Y | Alstom | MCAG39 | MCAG39 | MCAG | Electromechanical |  | 0.016937 | 2190 |  | 5.5 | 0.0019187 | 9.4276e-05 | 0.0018245 | 20.2458 | 45.2523 | 65.4981 | 5.9818 | 0.76863 | 25.0106 |  | 7.3552 | 0.0040026 | 0.00019666 | 0.0038059 | 42.2337 | 94.3983 | 136.6319 | 12.4783 | 1.6034 | 52.1731 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 54.2635 | 0.057554 | 54.321 | 14.6705 | 2.0677 | 0.031809 |  | 97.2591 | 202.8868 | 71.091 | 131.7958 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0.00010128 | 0.00010885 | 0.00011704 | 0.00012589 | 0.00013548 | 0.00014585 | 0.00015708 | 0.00016924 | 0.0001824 | 0.00019666 | 0.00021211 | 0.00022886 | 0.000247 | 0.00026667 | 0.000288 | 0.00031112 | 0.00033621 | 0.00036341 | 0.00039293 | 0.00042497 | 0.00045973 | 0.00049746 | 0.00053843 | 0.00058291 | 0.00063121 | 0.00068366 | 0.00074063 | 0.00080253 | 0.00086978 | 0.00094284 | 104.4828 | 112.2934 | 120.7406 | 129.8785 | 139.7659 | 150.4666 | 162.0502 | 174.5921 | 188.1746 | 202.8868 | 218.826 | 236.098 | 254.8176 | 275.1099 | 297.1111 | 320.9692 | 346.8454 | 374.9151 | 405.3691 | 438.4151 | 474.2794 | 513.208 | 555.4689 | 601.3539 | 651.1807 | 705.2951 | 764.0737 | 827.9267 | 897.3007 | 972.6821 |  | 43.9599 | 43.9599 | 43.9599 | 43.9599 | 43.9599 | 43.9599 | 43.9599 | 43.9599 | 43.9599 | 43.9599 | 43.9599 | 43.9599 | 43.9599 | 43.9599 | 43.9599 | 43.9599 | 43.9599 | 52.6173 | 69.7473 | 93.2616 | 125.685 | 170.5755 | 232.9566 | 319.9313 | 441.5585 | 612.0998 | 851.8003 | 1189.4273 | 1665.8955 | 2339.4448 |  | 21.7495 | 23.3754 | 25.1338 | 27.036 | 29.0942 | 31.3217 | 33.733 | 36.3438 | 39.1711 | 42.2337 | 45.5517 | 49.147 | 53.0438 | 57.2679 | 61.8478 | 66.8142 | 72.2006 | 78.0437 | 84.3832 | 91.2621 | 98.7278 | 106.8313 | 115.6285 | 125.1801 | 135.5522 | 146.8169 | 159.0525 | 172.3443 | 186.7855 | 202.4772 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | -5.3822 | -3.7563 | -1.9979 | -0.095727 | 1.9625 | 4.19 | 6.6013 | 9.212 | 12.0394 | 15.102 | 18.4199 | 22.0153 | 25.9121 | 30.1362 | 34.716 | 39.6824 | 45.0689 | 45.5688 | 41.3356 | 33.7018 | 21.156 | 1.5535 | -28.1504 | -72.279 | -136.9741 | -230.9663 | -366.6719 | -561.7607 | -841.392 | -1241.4096 |  | 48.6133 | 52.2474 | 56.1776 | 60.4293 | 65.0296 | 70.0084 | 75.398 | 81.2334 | 87.553 | 94.3983 | 101.8144 | 109.8506 | 118.5604 | 128.0019 | 138.2385 | 149.3391 | 161.3787 | 174.4388 | 188.6083 | 203.9838 | 220.6706 | 238.7831 | 258.4461 | 279.7953 | 302.9784 | 328.1565 | 355.5048 | 385.214 | 417.492 | 452.5651 |  | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.057554 | 0.068888 | 0.091315 | 0.1221 | 0.16455 | 0.22332 | 0.30499 | 0.41886 | 0.5781 | 0.80138 | 1.1152 | 1.5572 | 2.181 | 3.0629 |  | 48.5557 | 52.1898 | 56.1201 | 60.3717 | 64.9721 | 69.9509 | 75.3404 | 81.1759 | 87.4955 | 94.3407 | 101.7568 | 109.7931 | 118.5028 | 127.9443 | 138.181 | 149.2816 | 161.3211 | 174.3699 | 188.517 | 203.8617 | 220.506 | 238.5598 | 258.1411 | 279.3764 | 302.4003 | 327.3551 | 354.3896 | 383.6568 | 415.311 | 449.5023 |  | 43.1735 | 48.4335 | 54.1222 | 60.276 | 66.9346 | 74.1409 | 81.9417 | 90.3879 | 99.5349 | 109.4427 | 120.1768 | 131.8084 | 144.4149 | 158.0805 | 172.897 | 188.964 | 206.39 | 219.9387 | 229.8526 | 237.5635 | 241.662 | 240.1132 | 229.9906 | 207.0974 | 165.4262 | 96.3889 | -12.2824 | -178.104 | -426.081 | -791.9073 |  | 6.4261 | 6.9065 | 7.426 | 7.988 | 8.5961 | 9.2543 | 9.9667 | 10.7381 | 11.5735 | 12.4783 | 13.4586 | 14.5209 | 15.6723 | 16.9203 | 18.2735 | 19.7408 | 21.3323 | 23.0587 | 24.9317 | 26.9642 | 29.17 | 31.5643 | 34.1635 | 36.9856 | 40.0501 | 43.3783 | 46.9935 | 50.9207 | 55.1874 | 59.8237 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | -8.2444 | -7.764 | -7.2445 | -6.6824 | -6.0743 | -5.4162 | -4.7038 | -3.9324 | -3.097 | -2.1922 | -1.2118 | -0.14954 | 1.0018 | 2.2498 | 3.603 | 5.0704 | 6.6619 | 5.4991 | 1.6554 | -4.1594 | -12.774 | -25.3608 | -43.5796 | -69.783 | -107.3083 | -160.8938 | -237.2724 | -346.0192 | -500.7611 | -720.9041 |  | 0.82572 | 0.88745 | 0.95421 | 1.0264 | 1.1046 | 1.1891 | 1.2807 | 1.3798 | 1.4871 | 1.6034 | 1.7294 | 1.8659 | 2.0138 | 2.1742 | 2.3481 | 2.5366 | 2.7411 | 2.9629 | 3.2036 | 3.4648 | 3.7482 | 4.0559 | 4.3898 | 4.7525 | 5.1462 | 5.5739 | 6.0384 | 6.5431 | 7.0913 | 7.687 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | -1.242 | -1.1802 | -1.1135 | -1.0413 | -0.96313 | -0.87856 | -0.78702 | -0.6879 | -0.58056 | -0.46429 | -0.33832 | -0.20182 | -0.053884 | 0.10649 | 0.28036 | 0.46891 | 0.67341 | 0.48803 | -0.077016 | -0.92187 | -2.1635 | -3.9673 | -6.5675 | -10.2958 | -15.6228 | -23.2167 | -34.0267 | -49.4026 | -71.2655 | -102.3507 |  | 26.8682 | 28.8767 | 31.0489 | 33.3988 | 35.9414 | 38.6931 | 41.6719 | 44.8971 | 48.3898 | 52.1731 | 56.272 | 60.7135 | 65.5273 | 70.7456 | 76.4033 | 82.5385 | 89.1927 | 96.4109 | 104.2423 | 112.7402 | 121.9628 | 131.9735 | 142.841 | 154.6405 | 167.4537 | 181.3694 | 196.4846 | 212.9046 | 230.7444 | 250.1291 |  | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.038074 | 0.050469 | 0.067484 | 0.090946 | 0.12343 | 0.16857 | 0.2315 | 0.31951 | 0.44292 | 0.61636 | 0.86067 | 1.2054 | 1.6928 |  | 26.8364 | 28.8449 | 31.0171 | 33.367 | 35.9095 | 38.6613 | 41.64 | 44.8652 | 48.358 | 52.1413 | 56.2402 | 60.6817 | 65.4955 | 70.7138 | 76.3715 | 82.5067 | 89.1609 | 96.3728 | 104.1918 | 112.6727 | 121.8719 | 131.85 | 142.6725 | 154.409 | 167.1342 | 180.9265 | 195.8682 | 212.044 | 229.539 | 248.4362 |  | 60.5235 | 68.3341 | 76.7813 | 85.9193 | 95.8066 | 106.5074 | 118.091 | 130.6329 | 144.2153 | 158.9276 | 174.8668 | 192.1387 | 210.8583 | 231.1507 | 253.1518 | 277.01 | 302.8862 | 322.2986 | 335.6228 | 345.1549 | 348.5963 | 342.6351 | 322.516 | 281.4276 | 209.6292 | 93.2049 | -87.7132 | -361.4819 | -768.5686 | -1366.7259
| FALSE | 1628 | 22006051 | FB | FB-FBTS | 66 | FBTS LINE | NEUTRAL DISPLACEMENT | Blank | RPL | RVL_1274 | RVL 1274 | RVL | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 101.3994 | 1577.827 | 1679.2265 | 45.1415 | 3.7652 | 174.4104 |  | 7.3552 | 0.019459 | 0.0068571 | 0.012602 | 211.5238 | 3291.4176 | 3502.9413 | 94.1672 | 7.8543 | 363.8279 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.5336 | 54.7981 | 14.6761 | 2.0677 | 0.058983 |  | 1902.5436 | 3968.7908 | 71.6009 | 3897.1899 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.010021 | 0.01077 | 0.011581 | 0.012457 | 0.013405 | 0.014432 | 0.015543 | 0.016746 | 0.018048 | 0.019459 | 0.020988 | 0.022645 | 0.02444 | 0.026387 | 0.028497 | 0.030785 | 0.033267 | 0.035959 | 0.03888 | 0.04205 | 0.045489 | 0.049223 | 0.053276 | 0.057677 | 0.062456 | 0.067647 | 0.073284 | 0.079409 | 0.086062 | 0.093293 |  | 0.0035313 | 0.0037953 | 0.0040808 | 0.0043896 | 0.0047238 | 0.0050854 | 0.0054769 | 0.0059008 | 0.0063599 | 0.0068571 | 0.0073958 | 0.0079796 | 0.0086123 | 0.0092981 | 0.010042 | 0.010848 | 0.011723 | 0.012671 | 0.013701 | 0.014817 | 0.01603 | 0.017345 | 0.018774 | 0.020324 | 0.022008 | 0.023837 | 0.025824 | 0.027982 | 0.030327 | 0.032874 | 2043.8504 | 2196.638 | 2361.8792 | 2540.6316 | 2734.0447 | 2943.3684 | 3169.9616 | 3415.3017 | 3680.9956 | 3968.7908 | 4280.5879 | 4618.4546 | 4984.6397 | 5381.5904 | 5811.9688 | 6278.6718 | 6784.8518 | 7333.9392 | 7929.6679 | 8576.1015 | 9277.6637 | 10039.1696 | 10865.8613 | 11763.446 | 12738.1375 | 13796.7015 | 14946.5054 | 16195.572 | 17552.6383 | 19027.2195 |  | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 53.2338 | 70.5646 | 94.3544 | 127.1577 | 172.5742 | 235.6862 | 323.6801 | 446.7325 | 619.2722 | 861.7814 | 1203.3645 | 1685.4158 | 2366.8574 |  | 108.9306 | 117.0737 | 125.8805 | 135.4075 | 145.7158 | 156.872 | 168.9487 | 182.0246 | 196.1852 | 211.5238 | 228.1415 | 246.1487 | 265.6652 | 286.8214 | 309.7592 | 334.633 | 361.6107 | 390.8753 | 422.6257 | 457.0786 | 494.4696 | 535.0554 | 579.1154 | 626.9538 | 678.9017 | 735.3197 | 796.6006 | 863.1718 | 935.499 | 1014.0895 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 81.7984 | 89.9415 | 98.7483 | 108.2752 | 118.5835 | 129.7398 | 141.8165 | 154.8923 | 169.053 | 184.3915 | 201.0093 | 219.0165 | 238.533 | 259.6892 | 282.627 | 307.5007 | 334.4785 | 358.3997 | 379.5774 | 399.5171 | 416.8963 | 429.7755 | 435.3337 | 429.4909 | 406.3701 | 357.5293 | 270.8661 | 129.0526 | -92.6982 | -429.825 |  | 1695.0164 | 1821.7269 | 1958.7656 | 2107.0094 | 2267.4117 | 2441.0092 | 2628.9285 | 2832.3952 | 3052.7418 | 3291.4176 | 3549.9988 | 3830.2 | 4133.8866 | 4463.0877 | 4820.0113 | 5207.0598 | 5626.8475 | 6082.2195 | 6576.2722 | 7112.3758 | 7694.1988 | 8325.7347 | 9011.3309 | 9755.7204 | 10564.0564 | 11441.9501 | 12395.5113 | 13431.3935 | 14556.8425 | 15779.7496 |  | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.63868 | 0.84661 | 1.132 | 1.5256 | 2.0705 | 2.8277 | 3.8834 | 5.3597 | 7.4298 | 10.3393 | 14.4375 | 20.221 | 28.3967 |  | 1694.4828 | 1821.1933 | 1958.232 | 2106.4758 | 2266.8782 | 2440.4756 | 2628.3949 | 2831.8616 | 3052.2082 | 3290.884 | 3549.4652 | 3829.6664 | 4133.353 | 4462.5541 | 4819.4777 | 5206.5262 | 5626.3139 | 6081.5808 | 6575.4256 | 7111.2437 | 7692.6732 | 8323.6643 | 9008.5032 | 9751.837 | 10558.6967 | 11434.5203 | 12385.1719 | 13416.956 | 14536.6215 | 15751.3529 |  | 1776.2811 | 1911.1348 | 2056.9803 | 2214.751 | 2385.4617 | 2570.2154 | 2770.2114 | 2986.754 | 3221.2612 | 3475.2755 | 3750.4745 | 4048.6829 | 4371.886 | 4722.2433 | 5102.1047 | 5514.0269 | 5960.7924 | 6439.9805 | 6955.003 | 7510.7609 | 8109.5695 | 8753.4398 | 9443.8369 | 10181.3279 | 10965.0667 | 11792.0496 | 12656.038 | 13546.0086 | 14443.9233 | 15321.5279 |  | 48.4943 | 52.1195 | 56.0402 | 60.2814 | 64.8705 | 69.8371 | 75.2135 | 81.0346 | 87.3387 | 94.1672 | 101.5652 | 109.5818 | 118.2702 | 127.6887 | 137.9002 | 148.9736 | 160.9837 | 174.0119 | 188.1467 | 203.4846 | 220.1305 | 238.1987 | 257.8136 | 279.1105 | 302.237 | 327.3535 | 354.6348 | 384.2713 | 416.4703 | 451.4576 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 33.8182 | 37.4434 | 41.3641 | 45.6053 | 50.1944 | 55.161 | 60.5374 | 66.3585 | 72.6627 | 79.4912 | 86.8891 | 94.9057 | 103.5941 | 113.0126 | 123.2241 | 134.2976 | 146.3077 | 156.4455 | 164.8615 | 172.3491 | 178.1704 | 181.2518 | 180.0407 | 172.3009 | 154.822 | 123.0029 | 70.2599 | -12.8209 | -139.6916 | -329.5698 |  | 4.0448 | 4.3472 | 4.6742 | 5.0279 | 5.4107 | 5.825 | 6.2734 | 6.7589 | 7.2847 | 7.8543 | 8.4713 | 9.14 | 9.8647 | 10.6502 | 11.5019 | 12.4256 | 13.4273 | 14.5139 | 15.6929 | 16.9722 | 18.3606 | 19.8676 | 21.5037 | 23.28 | 25.2089 | 27.3038 | 29.5793 | 32.0512 | 34.7369 | 37.6551 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 1.9771 | 2.2795 | 2.6065 | 2.9602 | 3.343 | 3.7573 | 4.2057 | 4.6912 | 5.217 | 5.7866 | 6.4036 | 7.0723 | 7.797 | 8.5825 | 9.4342 | 10.3579 | 11.3596 | 12.039 | 12.4123 | 12.5855 | 12.4489 | 11.8444 | 10.5463 | 8.2317 | 4.4397 | -1.4869 | -10.486 | -23.8948 | -43.6203 | -72.3832 |  | 187.3643 | 201.3707 | 216.5187 | 232.9054 | 250.636 | 269.8252 | 290.5975 | 313.0883 | 337.4451 | 363.8279 | 392.4111 | 423.384 | 456.9531 | 493.3424 | 532.7962 | 575.5799 | 621.9825 | 672.3186 | 726.9304 | 786.1904 | 850.5041 | 920.3131 | 996.0978 | 1078.3814 | 1167.7335 | 1264.7744 | 1370.1795 | 1484.6843 | 1609.0895 | 1744.2677 |  | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.070599 | 0.093583 | 0.12513 | 0.16864 | 0.22887 | 0.31257 | 0.42926 | 0.59246 | 0.82128 | 1.1429 | 1.5959 | 2.2352 | 3.1389 |  | 187.3054 | 201.3117 | 216.4598 | 232.8464 | 250.577 | 269.7662 | 290.5385 | 313.0294 | 337.3861 | 363.7689 | 392.3521 | 423.3251 | 456.8941 | 493.2834 | 532.7372 | 575.5209 | 621.9235 | 672.248 | 726.8368 | 786.0652 | 850.3355 | 920.0842 | 995.7852 | 1077.9521 | 1167.141 | 1263.9532 | 1369.0366 | 1483.0884 | 1606.8543 | 1741.1288 |  | 1999.3818 | 2152.1694 | 2317.4106 | 2496.1629 | 2689.5761 | 2898.8998 | 3125.493 | 3370.8331 | 3636.527 | 3924.3222 | 4236.1193 | 4573.9859 | 4940.1711 | 5337.1218 | 5767.5002 | 6234.2032 | 6740.3832 | 7280.7131 | 7859.1135 | 8481.7607 | 9150.5243 | 9866.6202 | 10630.2091 | 11439.8126 | 12291.4695 | 13177.5187 | 14084.8485 | 14992.3813 | 15867.4658 | 16660.7037
| FALSE | 1629 | 22015774 | FB | FB-FBTS | 66 | FBTS LINE | REM TRIP SEND/RCVE UNIT 2 | Y | Schweitzer | SEL_2506 | SEL 2506 | SEL 2000s | Digital |  | 0.016937 | 1 |  | 1.8695 | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.014388 | 27.1461 | 14.6705 | 2.0677 | 0.031809 |  | 6.2006 | 0.014776 | 3.4281e-07 | 0.014775 | 77.5718 | 0.041138 | 77.6129 | 41.944 | 5.9117 | 0.090946 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.014388 | 27.1461 | 14.6705 | 2.0677 | 0.031809 |  | 43.9161 | 125.5596 | 43.9161 | 81.6435 |  | 0.11989 |  | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.4352e-07 | 1.9024e-07 | 2.5438e-07 | 3.4281e-07 | 4.6526e-07 | 6.354e-07 | 8.7263e-07 | 1.2044e-06 | 1.6695e-06 | 2.3233e-06 | 3.2442e-06 | 4.5438e-06 | 6.381e-06 | 8.982e-06 | 1.2669e-05 | 1.7903e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 52.5648 | 69.6778 | 93.1686 | 125.5596 | 170.4053 | 232.7241 | 319.6121 | 441.1179 | 611.4892 | 850.9505 | 1188.2406 | 1664.2335 | 2337.1108 | 3289.7509 | 4640.2889 | 6557.2133 | 8002.8882 | 8002.8882 | 8002.8882 | 8002.8882 | 8002.8882 | 8002.8882 | 8002.8882 | 8002.8882 |  | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 43.9161 | 52.5648 | 69.6778 | 93.1686 | 125.5596 | 170.4053 | 232.7241 | 319.6121 | 441.1179 | 611.4892 | 850.9505 | 1188.2406 | 1664.2335 | 2337.1108 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 | 2032.4358 | 2866.8096 | 4051.1016 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9158 | 30.4286 | 50.4401 | 78.1461 | 116.6472 | 170.3274 | 245.3946 | 350.6514 | 498.5927 | 706.9734 | 995.7025 | 1400.8393 | 1974.8755 | 2789.2379 | 3945.8238 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.017222 | 0.022829 | 0.030525 | 0.041138 | 0.055831 | 0.076249 | 0.10472 | 0.14453 | 0.20035 | 0.2788 | 0.38931 | 0.54526 | 0.76572 | 1.0778 | 1.5203 | 2.1484 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 | 2.622 |  | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.014388 | 0.017222 | 0.022829 | 0.030525 | 0.041138 | 0.055831 | 0.076249 | 0.10472 | 0.14453 | 0.20035 | 0.2788 | 0.38931 | 0.54526 | 0.76572 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.0028336 | 0.0084404 | 0.016137 | 0.026749 | 0.041442 | 0.06186 | 0.090328 | 0.13014 | 0.18596 | 0.26441 | 0.37492 | 0.52804 | 0.74289 | 1.0473 | 1.4792 | 2.0925 | 2.5458 | 2.5173 | 2.4775 | 2.4217 | 2.3432 | 2.2327 | 2.0768 | 1.8563 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5.3461 | 15.9242 | 30.4448 | 50.4668 | 78.1876 | 116.7091 | 170.4177 | 245.5248 | 350.8374 | 498.8571 | 707.3483 | 996.2306 | 1401.5822 | 1975.9228 | 2790.717 | 3947.9163 | 4803.0187 | 4749.3101 | 4674.203 | 4568.8904 | 4420.8707 | 4212.3795 | 3918.1511 | 3502.2214 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 | 1098.9637 | 1550.1201 | 2190.4817 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.8892 | 8.6059 | 16.4531 | 27.2736 | 42.2546 | 63.0726 | 92.0981 | 132.688 | 189.6016 | 269.5953 | 382.2694 | 538.3889 | 757.4514 | 1067.8401 | 1508.1761 | 2133.5566 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 | 154.8907 | 218.4778 | 308.732 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.7014 | 26.7229 | 37.9974 | 53.878 | 75.8819 | 106.7571 | 150.5041 | 212.5661 | 300.7088 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.038074 | 0.050469 | 0.067484 | 0.090946 | 0.12343 | 0.16857 | 0.2315 | 0.31951 | 0.44292 | 0.61636 | 0.86067 | 1.2054 | 1.6928 | 2.3828 | 3.3611 | 4.7495 | 5.7967 | 5.7967 | 5.7967 | 5.7967 | 5.7967 | 5.7967 | 5.7967 | 5.7967 |  | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.031809 | 0.038074 | 0.050469 | 0.067484 | 0.090946 | 0.12343 | 0.16857 | 0.2315 | 0.31951 | 0.44292 | 0.61636 | 0.86067 | 1.2054 | 1.6928 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.0062645 | 0.01866 | 0.035675 | 0.059136 | 0.091619 | 0.13676 | 0.19969 | 0.2877 | 0.41111 | 0.58455 | 0.82886 | 1.1674 | 1.6424 | 2.3154 | 3.2701 | 4.6261 | 5.6281 | 5.5652 | 5.4772 | 5.3538 | 5.1803 | 4.936 | 4.5912 | 4.1039 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8.6487 | 25.7617 | 49.2525 | 81.6435 | 126.4892 | 188.8081 | 275.6961 | 397.2018 | 567.5731 | 807.0344 | 1144.3245 | 1611.6687 | 2267.4331 | 3196.5823 | 4514.7293 | 6386.8079 | 7770.1641 | 7683.2761 | 7561.7703 | 7391.3991 | 7151.9377 | 6814.6476 | 6338.6547 | 5665.7774
| FALSE | 1630 | 22015771 | FB | FB-FBTS | 66 | FBTS LINE | REM TRIP SEND/RCVE UNIT 1 | X | Schweitzer | SEL_2506 | SEL 2506 | SEL 2000s | Digital |  | 0.15703 | 1 |  | 1.8695 | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.1334 | 27.2656 | 14.6761 | 2.0677 | 0.29491 |  | 6.2006 | 0.014776 | 3.1783e-06 | 0.014772 | 77.5733 | 0.3814 | 77.9547 | 41.9601 | 5.9117 | 0.84318 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.1334 | 27.2656 | 14.6761 | 2.0677 | 0.29491 |  | 44.3044 | 126.6697 | 44.3044 | 82.3653 |  | 0.11989 |  | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.3306e-06 | 1.7638e-06 | 2.3584e-06 | 3.1783e-06 | 4.3135e-06 | 5.891e-06 | 8.0904e-06 | 1.1166e-05 | 1.5479e-05 | 2.154e-05 | 3.0078e-05 | 4.2127e-05 | 5.916e-05 | 8.3274e-05 | 0.00011746 | 0.00016598 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 53.0295 | 70.2938 | 93.9923 | 126.6697 | 171.9119 | 234.7817 | 322.4379 | 445.018 | 616.8955 | 858.474 | 1198.7462 | 1678.9475 | 2357.774 | 3318.8366 | 4681.3152 | 6615.1876 | 8073.6443 | 8073.6443 | 8073.6443 | 8073.6443 | 8073.6443 | 8073.6443 | 8073.6443 | 8073.6443 |  | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 44.3044 | 53.0295 | 70.2938 | 93.9923 | 126.6697 | 171.9119 | 234.7817 | 322.4379 | 445.018 | 616.8955 | 858.474 | 1198.7462 | 1678.9475 | 2357.774 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 | 2032.4749 | 2866.8646 | 4051.1794 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5.3434 | 15.9161 | 30.4292 | 50.441 | 78.1476 | 116.6494 | 170.3306 | 245.3994 | 350.6582 | 498.6023 | 706.9869 | 995.7216 | 1400.8662 | 1974.9134 | 2789.2914 | 3945.8995 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.15967 | 0.21165 | 0.28301 | 0.3814 | 0.51762 | 0.70692 | 0.97085 | 1.3399 | 1.8575 | 2.5848 | 3.6094 | 5.0553 | 7.0992 | 9.9929 | 14.0953 | 19.9181 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 |  | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.15967 | 0.21165 | 0.28301 | 0.3814 | 0.51762 | 0.70692 | 0.97085 | 1.3399 | 1.8575 | 2.5848 | 3.6094 | 5.0553 | 7.0992 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.026271 | 0.078253 | 0.14961 | 0.248 | 0.38422 | 0.57352 | 0.83745 | 1.2065 | 1.7241 | 2.4514 | 3.476 | 4.8956 | 6.8875 | 9.7099 | 13.7139 | 19.4005 | 23.6025 | 23.3386 | 22.9695 | 22.452 | 21.7246 | 20.7001 | 19.2542 | 17.2103 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5.3696 | 15.9943 | 30.5788 | 50.689 | 78.5318 | 117.223 | 171.1681 | 246.6059 | 352.3822 | 501.0537 | 710.4629 | 1000.6172 | 1407.7537 | 1984.6233 | 2803.0053 | 3965.3 | 4824.1676 | 4770.2225 | 4694.7846 | 4589.0083 | 4440.3368 | 4230.9276 | 3935.4037 | 3517.6425 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 | 1099.3854 | 1550.715 | 2191.3224 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.8903 | 8.6092 | 16.4595 | 27.284 | 42.2708 | 63.0968 | 92.1335 | 132.7389 | 189.6744 | 269.6988 | 382.4161 | 538.5955 | 757.7422 | 1068.2499 | 1508.7549 | 2134.3755 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 | 154.8914 | 218.4789 | 308.7335 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.9555 | 8.8897 | 12.9806 | 18.7015 | 26.7231 | 37.9976 | 53.8783 | 75.8822 | 106.7576 | 150.5048 | 212.5671 | 300.7103 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.35299 | 0.46791 | 0.62566 | 0.84318 | 1.1443 | 1.5628 | 2.1463 | 2.9623 | 4.1064 | 5.7145 | 7.9795 | 11.176 | 15.6946 | 22.092 | 31.1614 | 44.0343 | 53.7426 | 53.7426 | 53.7426 | 53.7426 | 53.7426 | 53.7426 | 53.7426 | 53.7426 |  | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.29491 | 0.35299 | 0.46791 | 0.62566 | 0.84318 | 1.1443 | 1.5628 | 2.1463 | 2.9623 | 4.1064 | 5.7145 | 7.9795 | 11.176 | 15.6946 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.05808 | 0.173 | 0.33075 | 0.54827 | 0.84943 | 1.2679 | 1.8514 | 2.6674 | 3.8115 | 5.4196 | 7.6846 | 10.823 | 15.2267 | 21.4663 | 30.3182 | 42.8899 | 52.1797 | 51.5962 | 50.7803 | 49.6362 | 48.0281 | 45.7631 | 42.5666 | 38.0479 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8.7252 | 25.9894 | 49.688 | 82.3653 | 127.6076 | 190.4774 | 278.1336 | 400.7136 | 572.5912 | 814.1697 | 1154.4419 | 1625.918 | 2287.4802 | 3224.8443 | 4554.6455 | 6443.2757 | 7838.8626 | 7751.2063 | 7628.6263 | 7456.7488 | 7215.1702 | 6874.8981 | 6394.6967 | 5715.8703
| FALSE | 1631 | 22006048 | FB | FB-WG | 66 | WG LINE | NEUTRAL DISPLACEMENT | Blank | RPL | RVL_1274 | RVL 1274 | RVL | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 101.3994 | 1577.827 | 1679.2265 | 45.1415 | 3.7652 | 174.4104 |  | 7.3552 | 0.019459 | 0.0068571 | 0.012602 | 211.5238 | 3291.4176 | 3502.9413 | 94.1672 | 7.8543 | 363.8279 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.5336 | 54.7981 | 14.6761 | 2.0677 | 0.058983 |  | 1902.5436 | 3968.7908 | 71.6009 | 3897.1899 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.010021 | 0.01077 | 0.011581 | 0.012457 | 0.013405 | 0.014432 | 0.015543 | 0.016746 | 0.018048 | 0.019459 | 0.020988 | 0.022645 | 0.02444 | 0.026387 | 0.028497 | 0.030785 | 0.033267 | 0.035959 | 0.03888 | 0.04205 | 0.045489 | 0.049223 | 0.053276 | 0.057677 | 0.062456 | 0.067647 | 0.073284 | 0.079409 | 0.086062 | 0.093293 |  | 0.0035313 | 0.0037953 | 0.0040808 | 0.0043896 | 0.0047238 | 0.0050854 | 0.0054769 | 0.0059008 | 0.0063599 | 0.0068571 | 0.0073958 | 0.0079796 | 0.0086123 | 0.0092981 | 0.010042 | 0.010848 | 0.011723 | 0.012671 | 0.013701 | 0.014817 | 0.01603 | 0.017345 | 0.018774 | 0.020324 | 0.022008 | 0.023837 | 0.025824 | 0.027982 | 0.030327 | 0.032874 | 2043.8504 | 2196.638 | 2361.8792 | 2540.6316 | 2734.0447 | 2943.3684 | 3169.9616 | 3415.3017 | 3680.9956 | 3968.7908 | 4280.5879 | 4618.4546 | 4984.6397 | 5381.5904 | 5811.9688 | 6278.6718 | 6784.8518 | 7333.9392 | 7929.6679 | 8576.1015 | 9277.6637 | 10039.1696 | 10865.8613 | 11763.446 | 12738.1375 | 13796.7015 | 14946.5054 | 16195.572 | 17552.6383 | 19027.2195 |  | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 44.475 | 53.2338 | 70.5646 | 94.3544 | 127.1577 | 172.5742 | 235.6862 | 323.6801 | 446.7325 | 619.2722 | 861.7814 | 1203.3645 | 1685.4158 | 2366.8574 |  | 108.9306 | 117.0737 | 125.8805 | 135.4075 | 145.7158 | 156.872 | 168.9487 | 182.0246 | 196.1852 | 211.5238 | 228.1415 | 246.1487 | 265.6652 | 286.8214 | 309.7592 | 334.633 | 361.6107 | 390.8753 | 422.6257 | 457.0786 | 494.4696 | 535.0554 | 579.1154 | 626.9538 | 678.9017 | 735.3197 | 796.6006 | 863.1718 | 935.499 | 1014.0895 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 81.7984 | 89.9415 | 98.7483 | 108.2752 | 118.5835 | 129.7398 | 141.8165 | 154.8923 | 169.053 | 184.3915 | 201.0093 | 219.0165 | 238.533 | 259.6892 | 282.627 | 307.5007 | 334.4785 | 358.3997 | 379.5774 | 399.5171 | 416.8963 | 429.7755 | 435.3337 | 429.4909 | 406.3701 | 357.5293 | 270.8661 | 129.0526 | -92.6982 | -429.825 |  | 1695.0164 | 1821.7269 | 1958.7656 | 2107.0094 | 2267.4117 | 2441.0092 | 2628.9285 | 2832.3952 | 3052.7418 | 3291.4176 | 3549.9988 | 3830.2 | 4133.8866 | 4463.0877 | 4820.0113 | 5207.0598 | 5626.8475 | 6082.2195 | 6576.2722 | 7112.3758 | 7694.1988 | 8325.7347 | 9011.3309 | 9755.7204 | 10564.0564 | 11441.9501 | 12395.5113 | 13431.3935 | 14556.8425 | 15779.7496 |  | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.5336 | 0.63868 | 0.84661 | 1.132 | 1.5256 | 2.0705 | 2.8277 | 3.8834 | 5.3597 | 7.4298 | 10.3393 | 14.4375 | 20.221 | 28.3967 |  | 1694.4828 | 1821.1933 | 1958.232 | 2106.4758 | 2266.8782 | 2440.4756 | 2628.3949 | 2831.8616 | 3052.2082 | 3290.884 | 3549.4652 | 3829.6664 | 4133.353 | 4462.5541 | 4819.4777 | 5206.5262 | 5626.3139 | 6081.5808 | 6575.4256 | 7111.2437 | 7692.6732 | 8323.6643 | 9008.5032 | 9751.837 | 10558.6967 | 11434.5203 | 12385.1719 | 13416.956 | 14536.6215 | 15751.3529 |  | 1776.2811 | 1911.1348 | 2056.9803 | 2214.751 | 2385.4617 | 2570.2154 | 2770.2114 | 2986.754 | 3221.2612 | 3475.2755 | 3750.4745 | 4048.6829 | 4371.886 | 4722.2433 | 5102.1047 | 5514.0269 | 5960.7924 | 6439.9805 | 6955.003 | 7510.7609 | 8109.5695 | 8753.4398 | 9443.8369 | 10181.3279 | 10965.0667 | 11792.0496 | 12656.038 | 13546.0086 | 14443.9233 | 15321.5279 |  | 48.4943 | 52.1195 | 56.0402 | 60.2814 | 64.8705 | 69.8371 | 75.2135 | 81.0346 | 87.3387 | 94.1672 | 101.5652 | 109.5818 | 118.2702 | 127.6887 | 137.9002 | 148.9736 | 160.9837 | 174.0119 | 188.1467 | 203.4846 | 220.1305 | 238.1987 | 257.8136 | 279.1105 | 302.237 | 327.3535 | 354.6348 | 384.2713 | 416.4703 | 451.4576 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 33.8182 | 37.4434 | 41.3641 | 45.6053 | 50.1944 | 55.161 | 60.5374 | 66.3585 | 72.6627 | 79.4912 | 86.8891 | 94.9057 | 103.5941 | 113.0126 | 123.2241 | 134.2976 | 146.3077 | 156.4455 | 164.8615 | 172.3491 | 178.1704 | 181.2518 | 180.0407 | 172.3009 | 154.822 | 123.0029 | 70.2599 | -12.8209 | -139.6916 | -329.5698 |  | 4.0448 | 4.3472 | 4.6742 | 5.0279 | 5.4107 | 5.825 | 6.2734 | 6.7589 | 7.2847 | 7.8543 | 8.4713 | 9.14 | 9.8647 | 10.6502 | 11.5019 | 12.4256 | 13.4273 | 14.5139 | 15.6929 | 16.9722 | 18.3606 | 19.8676 | 21.5037 | 23.28 | 25.2089 | 27.3038 | 29.5793 | 32.0512 | 34.7369 | 37.6551 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 1.9771 | 2.2795 | 2.6065 | 2.9602 | 3.343 | 3.7573 | 4.2057 | 4.6912 | 5.217 | 5.7866 | 6.4036 | 7.0723 | 7.797 | 8.5825 | 9.4342 | 10.3579 | 11.3596 | 12.039 | 12.4123 | 12.5855 | 12.4489 | 11.8444 | 10.5463 | 8.2317 | 4.4397 | -1.4869 | -10.486 | -23.8948 | -43.6203 | -72.3832 |  | 187.3643 | 201.3707 | 216.5187 | 232.9054 | 250.636 | 269.8252 | 290.5975 | 313.0883 | 337.4451 | 363.8279 | 392.4111 | 423.384 | 456.9531 | 493.3424 | 532.7962 | 575.5799 | 621.9825 | 672.3186 | 726.9304 | 786.1904 | 850.5041 | 920.3131 | 996.0978 | 1078.3814 | 1167.7335 | 1264.7744 | 1370.1795 | 1484.6843 | 1609.0895 | 1744.2677 |  | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.070599 | 0.093583 | 0.12513 | 0.16864 | 0.22887 | 0.31257 | 0.42926 | 0.59246 | 0.82128 | 1.1429 | 1.5959 | 2.2352 | 3.1389 |  | 187.3054 | 201.3117 | 216.4598 | 232.8464 | 250.577 | 269.7662 | 290.5385 | 313.0294 | 337.3861 | 363.7689 | 392.3521 | 423.3251 | 456.8941 | 493.2834 | 532.7372 | 575.5209 | 621.9235 | 672.248 | 726.8368 | 786.0652 | 850.3355 | 920.0842 | 995.7852 | 1077.9521 | 1167.141 | 1263.9532 | 1369.0366 | 1483.0884 | 1606.8543 | 1741.1288 |  | 1999.3818 | 2152.1694 | 2317.4106 | 2496.1629 | 2689.5761 | 2898.8998 | 3125.493 | 3370.8331 | 3636.527 | 3924.3222 | 4236.1193 | 4573.9859 | 4940.1711 | 5337.1218 | 5767.5002 | 6234.2032 | 6740.3832 | 7280.7131 | 7859.1135 | 8481.7607 | 9150.5243 | 9866.6202 | 10630.2091 | 11439.8126 | 12291.4695 | 13177.5187 | 14084.8485 | 14992.3813 | 15867.4658 | 16660.7037
| FALSE | 1632 | 22015769 | FB | FB-WG | 66 | WG LINE | PILOT WIRE | X | Schweitzer | SEL_311L | SEL 311L | SEL 300s | Digital |  | 0.15703 | 1 |  | 5.1928 | 0.0095288 | 2.0497e-06 | 0.0095267 | 50.0272 | 0.24596 | 50.2731 | 27.0602 | 3.8125 | 0.10875 |  | 12.6825 | 0.099093 | 2.1316e-05 | 0.099072 | 520.2508 | 2.5579 | 522.8087 | 281.4087 | 39.6474 | 1.131 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.1334 | 27.2656 | 14.6761 | 2.0677 | 0.058983 |  | 81.2546 | 844.9959 | 44.0684 | 800.9274 |  | 0.089295 |  | 5.6779 | 6.2082 | 6.7881 | 7.4221 | 8.1153 | 8.8733 | 9.7021 | 10.6083 | 11.5992 | 12.6825 | 13.8671 | 15.1624 | 16.5786 | 18.1271 | 19.8202 | 21.6714 | 23.6956 | 25.9088 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.011859 | 0.014821 | 0.018596 | 0.023416 | 0.029581 | 0.037483 | 0.047626 | 0.060666 | 0.077454 | 0.099093 | 0.12702 | 0.1631 | 0.20976 | 0.27015 | 0.34839 | 0.44983 | 0.58143 | 0.75227 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.5509e-06 | 3.1882e-06 | 4.0001e-06 | 5.0368e-06 | 6.3631e-06 | 8.0629e-06 | 1.0245e-05 | 1.305e-05 | 1.6661e-05 | 2.1316e-05 | 2.7323e-05 | 3.5084e-05 | 4.512e-05 | 5.8112e-05 | 7.4942e-05 | 9.6761e-05 | 0.00012507 | 0.00016182 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 101.124 | 126.3851 | 158.5728 | 199.6713 | 252.2482 | 319.6287 | 406.1222 | 517.318 | 660.4695 | 844.9959 | 1083.1352 | 1390.7962 | 1788.6684 | 2303.671 | 2970.8417 | 3835.8021 | 4957.9741 | 6414.7777 | 8030.6502 | 8030.6502 | 8030.6502 | 8030.6502 | 8030.6502 | 8030.6502 | 8030.6502 | 8030.6502 | 8030.6502 | 8030.6502 | 8030.6502 | 8030.6502 |  | 44.0684 | 44.0684 | 44.0684 | 44.0684 | 44.0684 | 44.0684 | 44.0684 | 44.0684 | 44.0684 | 44.0684 | 44.0684 | 44.0684 | 44.0684 | 44.0684 | 44.0684 | 44.0684 | 44.0684 | 52.7471 | 69.9195 | 93.4918 | 125.9952 | 170.9965 | 233.5315 | 320.7209 | 442.6482 | 613.6104 | 853.9025 | 1192.3626 | 1670.0067 | 2345.2183 |  | 62.2605 | 77.8134 | 97.6308 | 122.9345 | 155.3053 | 196.7904 | 250.0431 | 318.5046 | 406.6408 | 520.2508 | 666.8696 | 856.2916 | 1101.2554 | 1418.3345 | 1829.1011 | 2361.6438 | 3052.5477 | 3949.4791 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 35.1282 | 50.6811 | 70.4986 | 95.8023 | 128.1731 | 169.6582 | 222.9109 | 291.3724 | 379.5085 | 493.1186 | 639.7373 | 829.1594 | 1074.1231 | 1391.2022 | 1801.9689 | 2334.5116 | 3025.4155 | 3917.0035 | 4901.2984 | 4886.7853 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.30611 | 0.38258 | 0.48001 | 0.60442 | 0.76358 | 0.96754 | 1.2294 | 1.566 | 1.9993 | 2.5579 | 3.2787 | 4.2101 | 5.4145 | 6.9734 | 8.993 | 11.6113 | 15.0082 | 19.4181 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 | 24.3095 |  | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.1334 | 0.15967 | 0.21165 | 0.28301 | 0.3814 | 0.51762 | 0.70692 | 0.97085 | 1.3399 | 1.8575 | 2.5848 | 3.6094 | 5.0553 | 7.0992 |  | 0.17271 | 0.24918 | 0.34661 | 0.47102 | 0.63018 | 0.83414 | 1.096 | 1.4326 | 1.8659 | 2.4245 | 3.1453 | 4.0767 | 5.2811 | 6.84 | 8.8596 | 11.4779 | 14.8748 | 19.2584 | 24.0978 | 24.0265 | 23.9281 | 23.7918 | 23.6025 | 23.3386 | 22.9695 | 22.452 | 21.7246 | 20.7001 | 19.2542 | 17.2103 |  | 35.3009 | 50.9303 | 70.8452 | 96.2733 | 128.8032 | 170.4923 | 224.0069 | 292.805 | 381.3744 | 495.5431 | 642.8827 | 833.236 | 1079.4042 | 1398.0422 | 1810.8285 | 2345.9895 | 3040.2903 | 3936.2619 | 4925.3962 | 4910.8117 | 4890.7015 | 4862.8587 | 4824.1676 | 4770.2225 | 4694.7846 | 4589.0083 | 4440.3368 | 4230.9276 | 3935.4037 | 3517.6425 |  | 33.6773 | 42.09 | 52.8095 | 66.4965 | 84.0061 | 106.4459 | 135.2508 | 172.2823 | 219.956 | 281.4087 | 360.7162 | 463.1765 | 595.6798 | 767.1909 | 989.3786 | 1277.4362 | 1651.1528 | 2136.3117 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 19.0012 | 27.4139 | 38.1334 | 51.8204 | 69.3301 | 91.7698 | 120.5747 | 157.6062 | 205.2799 | 266.7327 | 346.0401 | 448.5004 | 581.0037 | 752.5148 | 974.7025 | 1262.7601 | 1636.4767 | 2118.7454 | 2651.16 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 4.7448 | 5.93 | 7.4403 | 9.3686 | 11.8356 | 14.9971 | 19.0554 | 24.2727 | 30.9894 | 39.6474 | 50.821 | 65.2565 | 83.9248 | 108.0889 | 139.3927 | 179.9768 | 232.6295 | 300.9831 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 2.6771 | 3.8623 | 5.3726 | 7.3009 | 9.7678 | 12.9294 | 16.9877 | 22.205 | 28.9217 | 37.5797 | 48.7533 | 63.1888 | 81.8571 | 106.0211 | 137.325 | 177.9091 | 230.5618 | 298.5082 | 373.5196 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.13535 | 0.16916 | 0.21224 | 0.26725 | 0.33762 | 0.4278 | 0.54357 | 0.6924 | 0.884 | 1.131 | 1.4497 | 1.8615 | 2.394 | 3.0833 | 3.9763 | 5.134 | 6.6359 | 8.5858 | 10.7485 | 10.7485 | 10.7485 | 10.7485 | 10.7485 | 10.7485 | 10.7485 | 10.7485 | 10.7485 | 10.7485 | 10.7485 | 10.7485 |  | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.058983 | 0.070599 | 0.093583 | 0.12513 | 0.16864 | 0.22887 | 0.31257 | 0.42926 | 0.59246 | 0.82128 | 1.1429 | 1.5959 | 2.2352 | 3.1389 |  | 0.076365 | 0.11018 | 0.15326 | 0.20826 | 0.27864 | 0.36882 | 0.48459 | 0.63341 | 0.82501 | 1.072 | 1.3907 | 1.8025 | 2.335 | 3.0243 | 3.9173 | 5.075 | 6.5769 | 8.5152 | 10.6549 | 10.6234 | 10.5799 | 10.5196 | 10.4359 | 10.3192 | 10.1561 | 9.9272 | 9.6056 | 9.1526 | 8.5133 | 7.6096 |  | 57.0556 | 82.3167 | 114.5044 | 155.6029 | 208.1798 | 275.5602 | 362.0538 | 473.2495 | 616.401 | 800.9274 | 1039.0668 | 1346.7278 | 1744.6 | 2259.6025 | 2926.7733 | 3791.7337 | 4913.9057 | 6362.0306 | 7960.7308 | 7937.1584 | 7904.6551 | 7859.6538 | 7797.1188 | 7709.9294 | 7588.0021 | 7417.0398 | 7176.7478 | 6838.2876 | 6360.6435 | 5685.432
| TRUE | 1633 | 22006057 | FB | Blank | 66 | TRANS NO.1 | LT OVERCURRENT | Blank | English Electric | CDG11_1055 | CDG11 1055 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1634 | 22006058 | FB | Blank | 66 | TRANS NO.1 | LT OVERCURRENT | Blank | English Electric | CDG11_1055 | CDG11 1055 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1635 | 22006056 | FB | Blank | 66 | TRANS NO.1 | LT OVERCURRENT | Blank | English Electric | CDG11_1055 | CDG11 1055 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1636 | 22006060 | FB | Blank | 66 | TRANS NO.1 | HT OVERCURRENT | Blank | English Electric | CDG11_1056 | CDG11 1056 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1637 | 22006061 | FB | Blank | 66 | TRANS NO.1 | HT OVERCURRENT | Blank | English Electric | CDG11_1056 | CDG11 1056 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1638 | 22006059 | FB | Blank | 66 | TRANS NO.1 | HT OVERCURRENT | Blank | English Electric | CDG11_1056 | CDG11 1056 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1639 | 22006062 | FB | Blank | 66 | TRANS NO.1 | GAS & T/C PROT | Blank | ESP | GP3_234 | ESP - GP3_234 | GP3 | Electromechanical |  | 0.066046 | 2190 |  | 5.5 | 0.0019187 | 0.00033459 | 0.0015842 | 20.4982 | 160.6041 | 181.1023 | 7.3461 | 0.77104 | 17.7529 |  | 7.3552 | 0.0040026 | 0.00069797 | 0.0033046 | 42.7601 | 335.0274 | 377.7874 | 15.3244 | 1.6084 | 37.0334 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 206.9724 | 431.7536 | 71.2532 | 360.5004 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0.00035944 | 0.00038631 | 0.00041537 | 0.00044681 | 0.00048082 | 0.00051764 | 0.00055749 | 0.00060063 | 0.00064736 | 0.00069797 | 0.00075281 | 0.00081223 | 0.00087663 | 0.00094644 | 0.0010221 | 0.0011042 | 0.0011932 | 0.0012898 | 0.0013946 | 0.0015082 | 0.0016316 | 0.0017655 | 0.0019109 | 0.0020688 | 0.0022402 | 0.0024264 | 0.0026286 | 0.0028482 | 0.0030869 | 0.0033462 | 222.3447 | 238.9661 | 256.9422 | 276.3882 | 297.429 | 320.2008 | 344.8512 | 371.5411 | 400.4452 | 431.7536 | 465.6731 | 502.4287 | 542.2649 | 585.4481 | 632.2678 | 683.0391 | 738.105 | 797.8386 | 862.6463 | 932.97 | 1009.291 | 1092.133 | 1182.0665 | 1279.7122 | 1385.7462 | 1500.9044 | 1625.9883 | 1761.8708 | 1909.5022 | 2069.9177 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 22.0206 | 23.6667 | 25.4471 | 27.373 | 29.4568 | 31.7121 | 34.1534 | 36.7967 | 39.6593 | 42.7601 | 46.1194 | 49.7596 | 53.7049 | 57.9817 | 62.6186 | 67.6469 | 73.1005 | 79.0164 | 85.4349 | 92.3996 | 99.9583 | 108.1628 | 117.0696 | 126.7403 | 137.2417 | 148.6467 | 161.0348 | 174.4923 | 189.1135 | 205.0007 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | -5.1113 | -3.4652 | -1.6848 | 0.24105 | 2.3249 | 4.5802 | 7.0215 | 9.6648 | 12.5274 | 15.6281 | 18.9875 | 22.6277 | 26.573 | 30.8498 | 35.4867 | 40.515 | 45.9686 | 46.5412 | 42.3871 | 34.8388 | 22.386 | 2.8842 | -26.7103 | -70.7201 | -135.2865 | -229.139 | -364.6931 | -559.6177 | -839.0709 | -1238.8958 |  | 172.5326 | 185.4302 | 199.3792 | 214.4686 | 230.7957 | 248.4659 | 267.5938 | 288.3043 | 310.733 | 335.0274 | 361.3479 | 389.869 | 420.7807 | 454.2895 | 490.6201 | 530.0171 | 572.7465 | 619.098 | 669.3867 | 723.9557 | 783.1784 | 847.4613 | 917.2469 | 993.0169 | 1075.296 | 1164.6552 | 1261.7164 | 1367.157 | 1481.7144 | 1606.1918 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 172.3082 | 185.2058 | 199.1547 | 214.2442 | 230.5713 | 248.2414 | 267.3694 | 288.0799 | 310.5086 | 334.8029 | 361.1234 | 389.6446 | 420.5563 | 454.0651 | 490.3957 | 529.7927 | 572.5221 | 618.8294 | 669.0306 | 723.4796 | 782.5367 | 846.5904 | 916.0575 | 991.3835 | 1073.0416 | 1161.5302 | 1257.3676 | 1361.0845 | 1473.2093 | 1594.2481 |  | 167.1969 | 181.7407 | 197.4699 | 214.4852 | 232.8962 | 252.8216 | 274.3909 | 297.7447 | 323.036 | 350.4311 | 380.1109 | 412.2723 | 447.1293 | 484.9149 | 525.8824 | 570.3076 | 618.4907 | 665.3706 | 711.4177 | 758.3184 | 804.9227 | 849.4747 | 889.3473 | 920.6634 | 937.7551 | 932.3912 | 892.6745 | 801.4668 | 634.1384 | 355.3523 |  | 7.8918 | 8.4817 | 9.1197 | 9.8099 | 10.5567 | 11.365 | 12.2399 | 13.1872 | 14.2131 | 15.3244 | 16.5283 | 17.8329 | 19.2468 | 20.7795 | 22.4413 | 24.2433 | 26.1978 | 28.3179 | 30.6182 | 33.1142 | 35.8231 | 38.7634 | 41.9555 | 45.4212 | 49.1847 | 53.2721 | 57.7117 | 62.5347 | 67.7746 | 73.4683 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | -6.7807 | -6.1907 | -5.5527 | -4.8625 | -4.1157 | -3.3074 | -2.4325 | -1.4852 | -0.45931 | 0.65193 | 1.8558 | 3.1604 | 4.5743 | 6.1071 | 7.7688 | 9.5709 | 11.5254 | 10.756 | 7.3387 | 1.9864 | -6.1266 | -18.1693 | -35.7981 | -61.3617 | -98.1935 | -151.0275 | -226.5923 | -334.4586 | -488.2487 | -707.3645 |  | 0.8283 | 0.89022 | 0.95719 | 1.0296 | 1.108 | 1.1928 | 1.2847 | 1.3841 | 1.4918 | 1.6084 | 1.7348 | 1.8717 | 2.0201 | 2.181 | 2.3554 | 2.5445 | 2.7497 | 2.9722 | 3.2136 | 3.4756 | 3.7599 | 4.0685 | 4.4036 | 4.7673 | 5.1623 | 5.5913 | 6.0573 | 6.5635 | 7.1135 | 7.7111 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | -1.2394 | -1.1775 | -1.1105 | -1.0381 | -0.95968 | -0.87485 | -0.78302 | -0.68359 | -0.57591 | -0.45928 | -0.33292 | -0.19599 | -0.047591 | 0.11328 | 0.2877 | 0.47684 | 0.68197 | 0.49729 | -0.067006 | -0.91104 | -2.1518 | -3.9546 | -6.5538 | -10.2809 | -15.6068 | -23.1993 | -34.0079 | -49.3823 | -71.2434 | -102.3268 |  | 19.0715 | 20.4972 | 22.039 | 23.707 | 25.5118 | 27.465 | 29.5794 | 31.8687 | 34.3479 | 37.0334 | 39.9428 | 43.0955 | 46.5124 | 50.2164 | 54.2323 | 58.5872 | 63.3105 | 68.4341 | 73.9929 | 80.0249 | 86.5713 | 93.677 | 101.391 | 109.7665 | 118.8615 | 128.7391 | 139.4681 | 151.1233 | 163.7863 | 177.5458 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 19.0467 | 20.4723 | 22.0142 | 23.6822 | 25.487 | 27.4402 | 29.5546 | 31.8439 | 34.3231 | 37.0086 | 39.918 | 43.0707 | 46.4876 | 50.1916 | 54.2075 | 58.5624 | 63.2857 | 68.4044 | 73.9535 | 79.9722 | 86.5003 | 93.5807 | 101.2595 | 109.5859 | 118.6123 | 128.3936 | 138.9874 | 150.4521 | 162.8461 | 176.2256 |  | 178.2235 | 194.8448 | 212.8209 | 232.2669 | 253.3078 | 276.0795 | 300.7299 | 327.4198 | 356.3239 | 387.6323 | 421.5518 | 458.3074 | 498.1437 | 541.3268 | 588.1465 | 638.9178 | 693.9837 | 745.0282 | 792.6429 | 839.366 | 883.1447 | 920.9315 | 948.2549 | 958.6067 | 942.5671 | 886.558 | 771.0616 | 568.078 | 237.4924 | -278.1135
| TRUE | 1640 | 22006064 | FB | Blank | 66 | TRANS NO.1 | DIFFERENTIAL | Blank | ASEA | RYDSA_1105 | RYDSA 1105 | RYDSA | Electromechanical |  | 0.066046 | 2190 |  | 5.5 | 0.0019187 | 0.00033459 | 0.0015842 | 20.4982 | 160.6041 | 181.1023 | 7.3461 | 0.77104 | 17.7529 |  | 7.3552 | 0.0040026 | 0.00069797 | 0.0033046 | 42.7601 | 335.0274 | 377.7874 | 15.3244 | 1.6084 | 37.0334 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 206.9724 | 431.7536 | 71.2532 | 360.5004 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0.00035944 | 0.00038631 | 0.00041537 | 0.00044681 | 0.00048082 | 0.00051764 | 0.00055749 | 0.00060063 | 0.00064736 | 0.00069797 | 0.00075281 | 0.00081223 | 0.00087663 | 0.00094644 | 0.0010221 | 0.0011042 | 0.0011932 | 0.0012898 | 0.0013946 | 0.0015082 | 0.0016316 | 0.0017655 | 0.0019109 | 0.0020688 | 0.0022402 | 0.0024264 | 0.0026286 | 0.0028482 | 0.0030869 | 0.0033462 | 222.3447 | 238.9661 | 256.9422 | 276.3882 | 297.429 | 320.2008 | 344.8512 | 371.5411 | 400.4452 | 431.7536 | 465.6731 | 502.4287 | 542.2649 | 585.4481 | 632.2678 | 683.0391 | 738.105 | 797.8386 | 862.6463 | 932.97 | 1009.291 | 1092.133 | 1182.0665 | 1279.7122 | 1385.7462 | 1500.9044 | 1625.9883 | 1761.8708 | 1909.5022 | 2069.9177 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 22.0206 | 23.6667 | 25.4471 | 27.373 | 29.4568 | 31.7121 | 34.1534 | 36.7967 | 39.6593 | 42.7601 | 46.1194 | 49.7596 | 53.7049 | 57.9817 | 62.6186 | 67.6469 | 73.1005 | 79.0164 | 85.4349 | 92.3996 | 99.9583 | 108.1628 | 117.0696 | 126.7403 | 137.2417 | 148.6467 | 161.0348 | 174.4923 | 189.1135 | 205.0007 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | -5.1113 | -3.4652 | -1.6848 | 0.24105 | 2.3249 | 4.5802 | 7.0215 | 9.6648 | 12.5274 | 15.6281 | 18.9875 | 22.6277 | 26.573 | 30.8498 | 35.4867 | 40.515 | 45.9686 | 46.5412 | 42.3871 | 34.8388 | 22.386 | 2.8842 | -26.7103 | -70.7201 | -135.2865 | -229.139 | -364.6931 | -559.6177 | -839.0709 | -1238.8958 |  | 172.5326 | 185.4302 | 199.3792 | 214.4686 | 230.7957 | 248.4659 | 267.5938 | 288.3043 | 310.733 | 335.0274 | 361.3479 | 389.869 | 420.7807 | 454.2895 | 490.6201 | 530.0171 | 572.7465 | 619.098 | 669.3867 | 723.9557 | 783.1784 | 847.4613 | 917.2469 | 993.0169 | 1075.296 | 1164.6552 | 1261.7164 | 1367.157 | 1481.7144 | 1606.1918 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 172.3082 | 185.2058 | 199.1547 | 214.2442 | 230.5713 | 248.2414 | 267.3694 | 288.0799 | 310.5086 | 334.8029 | 361.1234 | 389.6446 | 420.5563 | 454.0651 | 490.3957 | 529.7927 | 572.5221 | 618.8294 | 669.0306 | 723.4796 | 782.5367 | 846.5904 | 916.0575 | 991.3835 | 1073.0416 | 1161.5302 | 1257.3676 | 1361.0845 | 1473.2093 | 1594.2481 |  | 167.1969 | 181.7407 | 197.4699 | 214.4852 | 232.8962 | 252.8216 | 274.3909 | 297.7447 | 323.036 | 350.4311 | 380.1109 | 412.2723 | 447.1293 | 484.9149 | 525.8824 | 570.3076 | 618.4907 | 665.3706 | 711.4177 | 758.3184 | 804.9227 | 849.4747 | 889.3473 | 920.6634 | 937.7551 | 932.3912 | 892.6745 | 801.4668 | 634.1384 | 355.3523 |  | 7.8918 | 8.4817 | 9.1197 | 9.8099 | 10.5567 | 11.365 | 12.2399 | 13.1872 | 14.2131 | 15.3244 | 16.5283 | 17.8329 | 19.2468 | 20.7795 | 22.4413 | 24.2433 | 26.1978 | 28.3179 | 30.6182 | 33.1142 | 35.8231 | 38.7634 | 41.9555 | 45.4212 | 49.1847 | 53.2721 | 57.7117 | 62.5347 | 67.7746 | 73.4683 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | -6.7807 | -6.1907 | -5.5527 | -4.8625 | -4.1157 | -3.3074 | -2.4325 | -1.4852 | -0.45931 | 0.65193 | 1.8558 | 3.1604 | 4.5743 | 6.1071 | 7.7688 | 9.5709 | 11.5254 | 10.756 | 7.3387 | 1.9864 | -6.1266 | -18.1693 | -35.7981 | -61.3617 | -98.1935 | -151.0275 | -226.5923 | -334.4586 | -488.2487 | -707.3645 |  | 0.8283 | 0.89022 | 0.95719 | 1.0296 | 1.108 | 1.1928 | 1.2847 | 1.3841 | 1.4918 | 1.6084 | 1.7348 | 1.8717 | 2.0201 | 2.181 | 2.3554 | 2.5445 | 2.7497 | 2.9722 | 3.2136 | 3.4756 | 3.7599 | 4.0685 | 4.4036 | 4.7673 | 5.1623 | 5.5913 | 6.0573 | 6.5635 | 7.1135 | 7.7111 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | -1.2394 | -1.1775 | -1.1105 | -1.0381 | -0.95968 | -0.87485 | -0.78302 | -0.68359 | -0.57591 | -0.45928 | -0.33292 | -0.19599 | -0.047591 | 0.11328 | 0.2877 | 0.47684 | 0.68197 | 0.49729 | -0.067006 | -0.91104 | -2.1518 | -3.9546 | -6.5538 | -10.2809 | -15.6068 | -23.1993 | -34.0079 | -49.3823 | -71.2434 | -102.3268 |  | 19.0715 | 20.4972 | 22.039 | 23.707 | 25.5118 | 27.465 | 29.5794 | 31.8687 | 34.3479 | 37.0334 | 39.9428 | 43.0955 | 46.5124 | 50.2164 | 54.2323 | 58.5872 | 63.3105 | 68.4341 | 73.9929 | 80.0249 | 86.5713 | 93.677 | 101.391 | 109.7665 | 118.8615 | 128.7391 | 139.4681 | 151.1233 | 163.7863 | 177.5458 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 19.0467 | 20.4723 | 22.0142 | 23.6822 | 25.487 | 27.4402 | 29.5546 | 31.8439 | 34.3231 | 37.0086 | 39.918 | 43.0707 | 46.4876 | 50.1916 | 54.2075 | 58.5624 | 63.2857 | 68.4044 | 73.9535 | 79.9722 | 86.5003 | 93.5807 | 101.2595 | 109.5859 | 118.6123 | 128.3936 | 138.9874 | 150.4521 | 162.8461 | 176.2256 |  | 178.2235 | 194.8448 | 212.8209 | 232.2669 | 253.3078 | 276.0795 | 300.7299 | 327.4198 | 356.3239 | 387.6323 | 421.5518 | 458.3074 | 498.1437 | 541.3268 | 588.1465 | 638.9178 | 693.9837 | 745.0282 | 792.6429 | 839.366 | 883.1447 | 920.9315 | 948.2549 | 958.6067 | 942.5671 | 886.558 | 771.0616 | 568.078 | 237.4924 | -278.1135
| TRUE | 1641 | 22006067 | FB | Blank | 66 | TRANS NO.2 | LT OVERCURRENT | Blank | English Electric | CDG11_1055 | CDG11 1055 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1642 | 22006068 | FB | Blank | 66 | TRANS NO.2 | LT OVERCURRENT | Blank | English Electric | CDG11_1055 | CDG11 1055 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1643 | 22006066 | FB | Blank | 66 | TRANS NO.2 | LT OVERCURRENT | Blank | English Electric | CDG11_1055 | CDG11 1055 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1644 | 22006070 | FB | Blank | 66 | TRANS NO.2 | HT OVERCURRENT | Blank | English Electric | CDG11_1056 | CDG11 1056 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1645 | 22006071 | FB | Blank | 66 | TRANS NO.2 | HT OVERCURRENT | Blank | English Electric | CDG11_1056 | CDG11 1056 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1646 | 22006069 | FB | Blank | 66 | TRANS NO.2 | HT OVERCURRENT | Blank | English Electric | CDG11_1056 | CDG11 1056 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1647 | 22006072 | FB | Blank | 66 | TRANS NO.2 | GAS & T/C PROT | Blank | ESP | GP3_1630 | GP3 1630 | GP3 | Electromechanical |  | 0.066046 | 2190 |  | 5.5 | 0.0019187 | 0.00033459 | 0.0015842 | 20.4982 | 160.6041 | 181.1023 | 7.3461 | 0.77104 | 17.7529 |  | 7.3552 | 0.0040026 | 0.00069797 | 0.0033046 | 42.7601 | 335.0274 | 377.7874 | 15.3244 | 1.6084 | 37.0334 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 206.9724 | 431.7536 | 71.2532 | 360.5004 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0.00035944 | 0.00038631 | 0.00041537 | 0.00044681 | 0.00048082 | 0.00051764 | 0.00055749 | 0.00060063 | 0.00064736 | 0.00069797 | 0.00075281 | 0.00081223 | 0.00087663 | 0.00094644 | 0.0010221 | 0.0011042 | 0.0011932 | 0.0012898 | 0.0013946 | 0.0015082 | 0.0016316 | 0.0017655 | 0.0019109 | 0.0020688 | 0.0022402 | 0.0024264 | 0.0026286 | 0.0028482 | 0.0030869 | 0.0033462 | 222.3447 | 238.9661 | 256.9422 | 276.3882 | 297.429 | 320.2008 | 344.8512 | 371.5411 | 400.4452 | 431.7536 | 465.6731 | 502.4287 | 542.2649 | 585.4481 | 632.2678 | 683.0391 | 738.105 | 797.8386 | 862.6463 | 932.97 | 1009.291 | 1092.133 | 1182.0665 | 1279.7122 | 1385.7462 | 1500.9044 | 1625.9883 | 1761.8708 | 1909.5022 | 2069.9177 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 22.0206 | 23.6667 | 25.4471 | 27.373 | 29.4568 | 31.7121 | 34.1534 | 36.7967 | 39.6593 | 42.7601 | 46.1194 | 49.7596 | 53.7049 | 57.9817 | 62.6186 | 67.6469 | 73.1005 | 79.0164 | 85.4349 | 92.3996 | 99.9583 | 108.1628 | 117.0696 | 126.7403 | 137.2417 | 148.6467 | 161.0348 | 174.4923 | 189.1135 | 205.0007 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | -5.1113 | -3.4652 | -1.6848 | 0.24105 | 2.3249 | 4.5802 | 7.0215 | 9.6648 | 12.5274 | 15.6281 | 18.9875 | 22.6277 | 26.573 | 30.8498 | 35.4867 | 40.515 | 45.9686 | 46.5412 | 42.3871 | 34.8388 | 22.386 | 2.8842 | -26.7103 | -70.7201 | -135.2865 | -229.139 | -364.6931 | -559.6177 | -839.0709 | -1238.8958 |  | 172.5326 | 185.4302 | 199.3792 | 214.4686 | 230.7957 | 248.4659 | 267.5938 | 288.3043 | 310.733 | 335.0274 | 361.3479 | 389.869 | 420.7807 | 454.2895 | 490.6201 | 530.0171 | 572.7465 | 619.098 | 669.3867 | 723.9557 | 783.1784 | 847.4613 | 917.2469 | 993.0169 | 1075.296 | 1164.6552 | 1261.7164 | 1367.157 | 1481.7144 | 1606.1918 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 172.3082 | 185.2058 | 199.1547 | 214.2442 | 230.5713 | 248.2414 | 267.3694 | 288.0799 | 310.5086 | 334.8029 | 361.1234 | 389.6446 | 420.5563 | 454.0651 | 490.3957 | 529.7927 | 572.5221 | 618.8294 | 669.0306 | 723.4796 | 782.5367 | 846.5904 | 916.0575 | 991.3835 | 1073.0416 | 1161.5302 | 1257.3676 | 1361.0845 | 1473.2093 | 1594.2481 |  | 167.1969 | 181.7407 | 197.4699 | 214.4852 | 232.8962 | 252.8216 | 274.3909 | 297.7447 | 323.036 | 350.4311 | 380.1109 | 412.2723 | 447.1293 | 484.9149 | 525.8824 | 570.3076 | 618.4907 | 665.3706 | 711.4177 | 758.3184 | 804.9227 | 849.4747 | 889.3473 | 920.6634 | 937.7551 | 932.3912 | 892.6745 | 801.4668 | 634.1384 | 355.3523 |  | 7.8918 | 8.4817 | 9.1197 | 9.8099 | 10.5567 | 11.365 | 12.2399 | 13.1872 | 14.2131 | 15.3244 | 16.5283 | 17.8329 | 19.2468 | 20.7795 | 22.4413 | 24.2433 | 26.1978 | 28.3179 | 30.6182 | 33.1142 | 35.8231 | 38.7634 | 41.9555 | 45.4212 | 49.1847 | 53.2721 | 57.7117 | 62.5347 | 67.7746 | 73.4683 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | -6.7807 | -6.1907 | -5.5527 | -4.8625 | -4.1157 | -3.3074 | -2.4325 | -1.4852 | -0.45931 | 0.65193 | 1.8558 | 3.1604 | 4.5743 | 6.1071 | 7.7688 | 9.5709 | 11.5254 | 10.756 | 7.3387 | 1.9864 | -6.1266 | -18.1693 | -35.7981 | -61.3617 | -98.1935 | -151.0275 | -226.5923 | -334.4586 | -488.2487 | -707.3645 |  | 0.8283 | 0.89022 | 0.95719 | 1.0296 | 1.108 | 1.1928 | 1.2847 | 1.3841 | 1.4918 | 1.6084 | 1.7348 | 1.8717 | 2.0201 | 2.181 | 2.3554 | 2.5445 | 2.7497 | 2.9722 | 3.2136 | 3.4756 | 3.7599 | 4.0685 | 4.4036 | 4.7673 | 5.1623 | 5.5913 | 6.0573 | 6.5635 | 7.1135 | 7.7111 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | -1.2394 | -1.1775 | -1.1105 | -1.0381 | -0.95968 | -0.87485 | -0.78302 | -0.68359 | -0.57591 | -0.45928 | -0.33292 | -0.19599 | -0.047591 | 0.11328 | 0.2877 | 0.47684 | 0.68197 | 0.49729 | -0.067006 | -0.91104 | -2.1518 | -3.9546 | -6.5538 | -10.2809 | -15.6068 | -23.1993 | -34.0079 | -49.3823 | -71.2434 | -102.3268 |  | 19.0715 | 20.4972 | 22.039 | 23.707 | 25.5118 | 27.465 | 29.5794 | 31.8687 | 34.3479 | 37.0334 | 39.9428 | 43.0955 | 46.5124 | 50.2164 | 54.2323 | 58.5872 | 63.3105 | 68.4341 | 73.9929 | 80.0249 | 86.5713 | 93.677 | 101.391 | 109.7665 | 118.8615 | 128.7391 | 139.4681 | 151.1233 | 163.7863 | 177.5458 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 19.0467 | 20.4723 | 22.0142 | 23.6822 | 25.487 | 27.4402 | 29.5546 | 31.8439 | 34.3231 | 37.0086 | 39.918 | 43.0707 | 46.4876 | 50.1916 | 54.2075 | 58.5624 | 63.2857 | 68.4044 | 73.9535 | 79.9722 | 86.5003 | 93.5807 | 101.2595 | 109.5859 | 118.6123 | 128.3936 | 138.9874 | 150.4521 | 162.8461 | 176.2256 |  | 178.2235 | 194.8448 | 212.8209 | 232.2669 | 253.3078 | 276.0795 | 300.7299 | 327.4198 | 356.3239 | 387.6323 | 421.5518 | 458.3074 | 498.1437 | 541.3268 | 588.1465 | 638.9178 | 693.9837 | 745.0282 | 792.6429 | 839.366 | 883.1447 | 920.9315 | 948.2549 | 958.6067 | 942.5671 | 886.558 | 771.0616 | 568.078 | 237.4924 | -278.1135
| TRUE | 1648 | 22006074 | FB | Blank | 66 | TRANS NO.2 | DIFFERENTIAL | Blank | ASEA | RYDSA_1105 | RYDSA 1105 | RYDSA | Electromechanical |  | 0.066046 | 2190 |  | 5.5 | 0.0019187 | 0.00033459 | 0.0015842 | 20.4982 | 160.6041 | 181.1023 | 7.3461 | 0.77104 | 17.7529 |  | 7.3552 | 0.0040026 | 0.00069797 | 0.0033046 | 42.7601 | 335.0274 | 377.7874 | 15.3244 | 1.6084 | 37.0334 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 206.9724 | 431.7536 | 71.2532 | 360.5004 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0.00035944 | 0.00038631 | 0.00041537 | 0.00044681 | 0.00048082 | 0.00051764 | 0.00055749 | 0.00060063 | 0.00064736 | 0.00069797 | 0.00075281 | 0.00081223 | 0.00087663 | 0.00094644 | 0.0010221 | 0.0011042 | 0.0011932 | 0.0012898 | 0.0013946 | 0.0015082 | 0.0016316 | 0.0017655 | 0.0019109 | 0.0020688 | 0.0022402 | 0.0024264 | 0.0026286 | 0.0028482 | 0.0030869 | 0.0033462 | 222.3447 | 238.9661 | 256.9422 | 276.3882 | 297.429 | 320.2008 | 344.8512 | 371.5411 | 400.4452 | 431.7536 | 465.6731 | 502.4287 | 542.2649 | 585.4481 | 632.2678 | 683.0391 | 738.105 | 797.8386 | 862.6463 | 932.97 | 1009.291 | 1092.133 | 1182.0665 | 1279.7122 | 1385.7462 | 1500.9044 | 1625.9883 | 1761.8708 | 1909.5022 | 2069.9177 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 22.0206 | 23.6667 | 25.4471 | 27.373 | 29.4568 | 31.7121 | 34.1534 | 36.7967 | 39.6593 | 42.7601 | 46.1194 | 49.7596 | 53.7049 | 57.9817 | 62.6186 | 67.6469 | 73.1005 | 79.0164 | 85.4349 | 92.3996 | 99.9583 | 108.1628 | 117.0696 | 126.7403 | 137.2417 | 148.6467 | 161.0348 | 174.4923 | 189.1135 | 205.0007 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | -5.1113 | -3.4652 | -1.6848 | 0.24105 | 2.3249 | 4.5802 | 7.0215 | 9.6648 | 12.5274 | 15.6281 | 18.9875 | 22.6277 | 26.573 | 30.8498 | 35.4867 | 40.515 | 45.9686 | 46.5412 | 42.3871 | 34.8388 | 22.386 | 2.8842 | -26.7103 | -70.7201 | -135.2865 | -229.139 | -364.6931 | -559.6177 | -839.0709 | -1238.8958 |  | 172.5326 | 185.4302 | 199.3792 | 214.4686 | 230.7957 | 248.4659 | 267.5938 | 288.3043 | 310.733 | 335.0274 | 361.3479 | 389.869 | 420.7807 | 454.2895 | 490.6201 | 530.0171 | 572.7465 | 619.098 | 669.3867 | 723.9557 | 783.1784 | 847.4613 | 917.2469 | 993.0169 | 1075.296 | 1164.6552 | 1261.7164 | 1367.157 | 1481.7144 | 1606.1918 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 172.3082 | 185.2058 | 199.1547 | 214.2442 | 230.5713 | 248.2414 | 267.3694 | 288.0799 | 310.5086 | 334.8029 | 361.1234 | 389.6446 | 420.5563 | 454.0651 | 490.3957 | 529.7927 | 572.5221 | 618.8294 | 669.0306 | 723.4796 | 782.5367 | 846.5904 | 916.0575 | 991.3835 | 1073.0416 | 1161.5302 | 1257.3676 | 1361.0845 | 1473.2093 | 1594.2481 |  | 167.1969 | 181.7407 | 197.4699 | 214.4852 | 232.8962 | 252.8216 | 274.3909 | 297.7447 | 323.036 | 350.4311 | 380.1109 | 412.2723 | 447.1293 | 484.9149 | 525.8824 | 570.3076 | 618.4907 | 665.3706 | 711.4177 | 758.3184 | 804.9227 | 849.4747 | 889.3473 | 920.6634 | 937.7551 | 932.3912 | 892.6745 | 801.4668 | 634.1384 | 355.3523 |  | 7.8918 | 8.4817 | 9.1197 | 9.8099 | 10.5567 | 11.365 | 12.2399 | 13.1872 | 14.2131 | 15.3244 | 16.5283 | 17.8329 | 19.2468 | 20.7795 | 22.4413 | 24.2433 | 26.1978 | 28.3179 | 30.6182 | 33.1142 | 35.8231 | 38.7634 | 41.9555 | 45.4212 | 49.1847 | 53.2721 | 57.7117 | 62.5347 | 67.7746 | 73.4683 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | -6.7807 | -6.1907 | -5.5527 | -4.8625 | -4.1157 | -3.3074 | -2.4325 | -1.4852 | -0.45931 | 0.65193 | 1.8558 | 3.1604 | 4.5743 | 6.1071 | 7.7688 | 9.5709 | 11.5254 | 10.756 | 7.3387 | 1.9864 | -6.1266 | -18.1693 | -35.7981 | -61.3617 | -98.1935 | -151.0275 | -226.5923 | -334.4586 | -488.2487 | -707.3645 |  | 0.8283 | 0.89022 | 0.95719 | 1.0296 | 1.108 | 1.1928 | 1.2847 | 1.3841 | 1.4918 | 1.6084 | 1.7348 | 1.8717 | 2.0201 | 2.181 | 2.3554 | 2.5445 | 2.7497 | 2.9722 | 3.2136 | 3.4756 | 3.7599 | 4.0685 | 4.4036 | 4.7673 | 5.1623 | 5.5913 | 6.0573 | 6.5635 | 7.1135 | 7.7111 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | -1.2394 | -1.1775 | -1.1105 | -1.0381 | -0.95968 | -0.87485 | -0.78302 | -0.68359 | -0.57591 | -0.45928 | -0.33292 | -0.19599 | -0.047591 | 0.11328 | 0.2877 | 0.47684 | 0.68197 | 0.49729 | -0.067006 | -0.91104 | -2.1518 | -3.9546 | -6.5538 | -10.2809 | -15.6068 | -23.1993 | -34.0079 | -49.3823 | -71.2434 | -102.3268 |  | 19.0715 | 20.4972 | 22.039 | 23.707 | 25.5118 | 27.465 | 29.5794 | 31.8687 | 34.3479 | 37.0334 | 39.9428 | 43.0955 | 46.5124 | 50.2164 | 54.2323 | 58.5872 | 63.3105 | 68.4341 | 73.9929 | 80.0249 | 86.5713 | 93.677 | 101.391 | 109.7665 | 118.8615 | 128.7391 | 139.4681 | 151.1233 | 163.7863 | 177.5458 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 19.0467 | 20.4723 | 22.0142 | 23.6822 | 25.487 | 27.4402 | 29.5546 | 31.8439 | 34.3231 | 37.0086 | 39.918 | 43.0707 | 46.4876 | 50.1916 | 54.2075 | 58.5624 | 63.2857 | 68.4044 | 73.9535 | 79.9722 | 86.5003 | 93.5807 | 101.2595 | 109.5859 | 118.6123 | 128.3936 | 138.9874 | 150.4521 | 162.8461 | 176.2256 |  | 178.2235 | 194.8448 | 212.8209 | 232.2669 | 253.3078 | 276.0795 | 300.7299 | 327.4198 | 356.3239 | 387.6323 | 421.5518 | 458.3074 | 498.1437 | 541.3268 | 588.1465 | 638.9178 | 693.9837 | 745.0282 | 792.6429 | 839.366 | 883.1447 | 920.9315 | 948.2549 | 958.6067 | 942.5671 | 886.558 | 771.0616 | 568.078 | 237.4924 | -278.1135
| TRUE | 1649 | 22006077 | FB | Blank | 66 | TRANS NO.3 | LT OVERCURRENT | Blank | English Electric | CDG11_1055 | CDG11 1055 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1650 | 22006078 | FB | Blank | 66 | TRANS NO.3 | LT OVERCURRENT | Blank | English Electric | CDG11_1055 | CDG11 1055 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1651 | 22006076 | FB | Blank | 66 | TRANS NO.3 | LT OVERCURRENT | Blank | English Electric | CDG11_1055 | CDG11 1055 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1652 | 22006080 | FB | Blank | 66 | TRANS NO.3 | HT OVERCURRENT | Blank | English Electric | CDG11_1056 | CDG11 1056 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1653 | 22006081 | FB | Blank | 66 | TRANS NO.3 | HT OVERCURRENT | Blank | English Electric | CDG11_1056 | CDG11 1056 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1654 | 22006079 | FB | Blank | 66 | TRANS NO.3 | HT OVERCURRENT | Blank | English Electric | CDG11_1056 | CDG11 1056 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 736.7397 | 830.7709 | 33.699 | 3.537 | 81.438 |  | 14.217 | 0.023831 | 0.0041557 | 0.019676 | 254.5927 | 1994.7479 | 2249.3406 | 91.2411 | 9.5765 | 220.4962 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 949.4448 | 2570.6543 | 71.2532 | 2499.4011 |  | 0.03619 |  | 10.2648 | 10.6431 | 11.0354 | 11.442 | 11.8637 | 12.3009 | 12.7543 | 13.2243 | 13.7116 | 14.217 | 14.7409 | 15.2841 | 15.8474 | 16.4314 | 17.037 | 17.6648 | 18.3158 | 18.9908 | 19.6907 | 20.4164 | 21.1688 | 21.9489 | 22.7578 | 23.5965 | 24.4661 | 25.3677 | 26.3026 | 27.2719 | 28 | 28 |  | 0.0097083 | 0.010712 | 0.011824 | 0.013057 | 0.014422 | 0.015936 | 0.017615 | 0.019476 | 0.021541 | 0.023831 | 0.026372 | 0.029192 | 0.032322 | 0.035796 | 0.039653 | 0.043936 | 0.048691 | 0.053973 | 0.059841 | 0.066359 | 0.073601 | 0.081649 | 0.090592 | 0.10053 | 0.11158 | 0.12386 | 0.13752 | 0.1527 | 0.16481 | 0.16481 |  | 0.0016929 | 0.001868 | 0.0020619 | 0.0022768 | 0.002515 | 0.002779 | 0.0030717 | 0.0033963 | 0.0037563 | 0.0041557 | 0.0045988 | 0.0050906 | 0.0056363 | 0.0062421 | 0.0069147 | 0.0076615 | 0.0084908 | 0.0094119 | 0.010435 | 0.011572 | 0.012835 | 0.014238 | 0.015798 | 0.017531 | 0.019458 | 0.021599 | 0.023981 | 0.026628 | 0.02874 | 0.02874 | 1047.2179 | 1155.5088 | 1275.4756 | 1408.4058 | 1555.7305 | 1719.0415 | 1900.1084 | 2100.8993 | 2323.6031 | 2570.6543 | 2844.7612 | 3148.9361 | 3486.5306 | 3861.2734 | 4277.3134 | 4739.2671 | 5252.2715 | 5822.0437 | 6454.9462 | 7158.0602 | 7939.2676 | 8807.3415 | 9772.0479 | 10844.2584 | 12036.0756 | 13360.9737 | 14833.9542 | 16471.7199 | 17778.2715 | 17778.2715 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 103.7145 | 114.4394 | 126.3207 | 139.4858 | 154.0766 | 170.2506 | 188.1831 | 208.0691 | 230.1252 | 254.5927 | 281.7398 | 311.8647 | 345.2994 | 382.4132 | 423.617 | 469.368 | 520.175 | 576.6042 | 639.2856 | 708.9207 | 786.29 | 872.2624 | 967.8051 | 1073.9948 | 1192.0301 | 1323.2455 | 1469.1267 | 1631.3279 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.5826 | 87.3075 | 99.1888 | 112.3539 | 126.9447 | 143.1187 | 161.0512 | 180.9372 | 202.9933 | 227.4608 | 254.6078 | 284.7328 | 318.1675 | 355.2813 | 396.4851 | 442.2361 | 493.0431 | 544.129 | 596.2378 | 651.36 | 708.7177 | 766.9839 | 824.0252 | 876.5344 | 919.5019 | 945.4598 | 943.3988 | 897.2179 | 732.5419 | 316.8298 |  | 812.6086 | 896.6389 | 989.7294 | 1092.8791 | 1207.1986 | 1333.9228 | 1474.4251 | 1630.2326 | 1803.0438 | 1994.7479 | 2207.4462 | 2443.4765 | 2705.4394 | 2996.2282 | 3319.0623 | 3677.524 | 4075.5995 | 4517.725 | 5008.8376 | 5554.4323 | 6160.6249 | 6834.2233 | 7582.8055 | 8414.8075 | 9339.6206 | 10367.7004 | 11510.6875 | 12781.5427 | 13795.3862 | 13795.3862 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 812.3841 | 896.4145 | 989.505 | 1092.6547 | 1206.9741 | 1333.6984 | 1474.2006 | 1630.0081 | 1802.8194 | 1994.5234 | 2207.2218 | 2443.2521 | 2705.2149 | 2996.0037 | 3318.8379 | 3677.2995 | 4075.375 | 4517.4564 | 5008.4815 | 5553.9561 | 6159.9832 | 6833.3524 | 7581.6162 | 8413.1741 | 9337.3663 | 10364.5754 | 11506.3387 | 12775.4703 | 13786.8812 | 13783.4425 |  | 888.9667 | 983.722 | 1088.6938 | 1205.0086 | 1333.9188 | 1476.8171 | 1635.2519 | 1810.9453 | 2005.8127 | 2221.9843 | 2461.8297 | 2727.9849 | 3023.3824 | 3351.285 | 3715.323 | 4119.5357 | 4568.4182 | 5061.5854 | 5604.7194 | 6205.3161 | 6868.7009 | 7600.3363 | 8405.6414 | 9289.7085 | 10256.8682 | 11310.0352 | 12449.7375 | 13672.6882 | 14519.4231 | 14100.2723 |  | 37.1692 | 41.0129 | 45.2709 | 49.989 | 55.2181 | 61.0145 | 67.4412 | 74.5679 | 82.4724 | 91.2411 | 100.97 | 111.7662 | 123.7486 | 137.0494 | 151.8161 | 168.2124 | 186.4206 | 206.6437 | 229.1075 | 254.0634 | 281.791 | 312.6019 | 346.8425 | 384.8988 | 427.2004 | 474.2254 | 526.5064 | 584.6362 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.4968 | 26.3404 | 30.5984 | 35.3166 | 40.5456 | 46.3421 | 52.7687 | 59.8955 | 67.8 | 76.5686 | 86.2976 | 97.0938 | 109.0761 | 122.377 | 137.1437 | 153.5399 | 171.7482 | 189.0817 | 205.8281 | 222.9356 | 239.8414 | 255.6691 | 269.089 | 278.1158 | 279.8221 | 269.9258 | 242.2024 | 187.6429 | 74.9867 | -149.8228 |  | 3.9012 | 4.3046 | 4.7515 | 5.2467 | 5.7956 | 6.404 | 7.0785 | 7.8265 | 8.6561 | 9.5765 | 10.5976 | 11.7308 | 12.9884 | 14.3844 | 15.9343 | 17.6552 | 19.5663 | 21.6889 | 24.0467 | 26.666 | 29.5762 | 32.8101 | 36.4039 | 40.3982 | 44.8381 | 49.7738 | 55.2611 | 61.3622 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8335 | 2.2369 | 2.6838 | 3.1791 | 3.7279 | 4.3363 | 5.0108 | 5.7588 | 6.5884 | 7.5088 | 8.5299 | 9.6631 | 10.9207 | 12.3167 | 13.8666 | 15.5875 | 17.4986 | 19.214 | 20.766 | 22.2793 | 23.6645 | 24.7869 | 25.4466 | 25.35 | 24.069 | 20.9831 | 15.1959 | 5.4165 | -12.1274 | -43.8084 |  | 89.8244 | 99.113 | 109.4031 | 120.8051 | 133.4418 | 147.4496 | 162.9805 | 180.2032 | 199.3055 | 220.4962 | 244.0075 | 270.0979 | 299.0548 | 331.1982 | 366.8837 | 406.5075 | 450.5101 | 499.3819 | 553.6687 | 613.9779 | 680.9854 | 755.4439 | 838.1909 | 930.159 | 1032.3864 | 1146.0286 | 1272.3726 | 1412.8508 | 1524.9194 | 1524.9194 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 89.7996 | 99.0882 | 109.3783 | 120.7803 | 133.4169 | 147.4248 | 162.9557 | 180.1784 | 199.2807 | 220.4714 | 243.9827 | 270.0731 | 299.03 | 331.1733 | 366.8589 | 406.4827 | 450.4853 | 499.3522 | 553.6294 | 613.9252 | 680.9145 | 755.3476 | 838.0594 | 929.9785 | 1032.1372 | 1145.6832 | 1271.8918 | 1412.1796 | 1523.9793 | 1523.5992 |  | 1003.0966 | 1111.3875 | 1231.3543 | 1364.2845 | 1511.6093 | 1674.9202 | 1855.9871 | 2056.778 | 2279.4818 | 2526.5331 | 2800.6399 | 3104.8148 | 3442.4093 | 3817.1521 | 4233.1921 | 4695.1458 | 5208.1502 | 5769.2333 | 6384.9429 | 7064.4563 | 7813.1213 | 8636.1399 | 9538.2364 | 10523.1528 | 11592.8965 | 12746.6273 | 13979.0276 | 15277.9271 | 16106.2617 | 15430.2403
| TRUE | 1655 | 22006082 | FB | Blank | 66 | TRANS NO.3 | GAS & T/C PROT | Blank | ESP | GP3_234 | ESP - GP3_234 | GP3 | Electromechanical |  | 0.066046 | 2190 |  | 5.5 | 0.0019187 | 0.00033459 | 0.0015842 | 20.4982 | 160.6041 | 181.1023 | 7.3461 | 0.77104 | 17.7529 |  | 7.3552 | 0.0040026 | 0.00069797 | 0.0033046 | 42.7601 | 335.0274 | 377.7874 | 15.3244 | 1.6084 | 37.0334 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 206.9724 | 431.7536 | 71.2532 | 360.5004 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0.00035944 | 0.00038631 | 0.00041537 | 0.00044681 | 0.00048082 | 0.00051764 | 0.00055749 | 0.00060063 | 0.00064736 | 0.00069797 | 0.00075281 | 0.00081223 | 0.00087663 | 0.00094644 | 0.0010221 | 0.0011042 | 0.0011932 | 0.0012898 | 0.0013946 | 0.0015082 | 0.0016316 | 0.0017655 | 0.0019109 | 0.0020688 | 0.0022402 | 0.0024264 | 0.0026286 | 0.0028482 | 0.0030869 | 0.0033462 | 222.3447 | 238.9661 | 256.9422 | 276.3882 | 297.429 | 320.2008 | 344.8512 | 371.5411 | 400.4452 | 431.7536 | 465.6731 | 502.4287 | 542.2649 | 585.4481 | 632.2678 | 683.0391 | 738.105 | 797.8386 | 862.6463 | 932.97 | 1009.291 | 1092.133 | 1182.0665 | 1279.7122 | 1385.7462 | 1500.9044 | 1625.9883 | 1761.8708 | 1909.5022 | 2069.9177 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 22.0206 | 23.6667 | 25.4471 | 27.373 | 29.4568 | 31.7121 | 34.1534 | 36.7967 | 39.6593 | 42.7601 | 46.1194 | 49.7596 | 53.7049 | 57.9817 | 62.6186 | 67.6469 | 73.1005 | 79.0164 | 85.4349 | 92.3996 | 99.9583 | 108.1628 | 117.0696 | 126.7403 | 137.2417 | 148.6467 | 161.0348 | 174.4923 | 189.1135 | 205.0007 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | -5.1113 | -3.4652 | -1.6848 | 0.24105 | 2.3249 | 4.5802 | 7.0215 | 9.6648 | 12.5274 | 15.6281 | 18.9875 | 22.6277 | 26.573 | 30.8498 | 35.4867 | 40.515 | 45.9686 | 46.5412 | 42.3871 | 34.8388 | 22.386 | 2.8842 | -26.7103 | -70.7201 | -135.2865 | -229.139 | -364.6931 | -559.6177 | -839.0709 | -1238.8958 |  | 172.5326 | 185.4302 | 199.3792 | 214.4686 | 230.7957 | 248.4659 | 267.5938 | 288.3043 | 310.733 | 335.0274 | 361.3479 | 389.869 | 420.7807 | 454.2895 | 490.6201 | 530.0171 | 572.7465 | 619.098 | 669.3867 | 723.9557 | 783.1784 | 847.4613 | 917.2469 | 993.0169 | 1075.296 | 1164.6552 | 1261.7164 | 1367.157 | 1481.7144 | 1606.1918 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 172.3082 | 185.2058 | 199.1547 | 214.2442 | 230.5713 | 248.2414 | 267.3694 | 288.0799 | 310.5086 | 334.8029 | 361.1234 | 389.6446 | 420.5563 | 454.0651 | 490.3957 | 529.7927 | 572.5221 | 618.8294 | 669.0306 | 723.4796 | 782.5367 | 846.5904 | 916.0575 | 991.3835 | 1073.0416 | 1161.5302 | 1257.3676 | 1361.0845 | 1473.2093 | 1594.2481 |  | 167.1969 | 181.7407 | 197.4699 | 214.4852 | 232.8962 | 252.8216 | 274.3909 | 297.7447 | 323.036 | 350.4311 | 380.1109 | 412.2723 | 447.1293 | 484.9149 | 525.8824 | 570.3076 | 618.4907 | 665.3706 | 711.4177 | 758.3184 | 804.9227 | 849.4747 | 889.3473 | 920.6634 | 937.7551 | 932.3912 | 892.6745 | 801.4668 | 634.1384 | 355.3523 |  | 7.8918 | 8.4817 | 9.1197 | 9.8099 | 10.5567 | 11.365 | 12.2399 | 13.1872 | 14.2131 | 15.3244 | 16.5283 | 17.8329 | 19.2468 | 20.7795 | 22.4413 | 24.2433 | 26.1978 | 28.3179 | 30.6182 | 33.1142 | 35.8231 | 38.7634 | 41.9555 | 45.4212 | 49.1847 | 53.2721 | 57.7117 | 62.5347 | 67.7746 | 73.4683 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | -6.7807 | -6.1907 | -5.5527 | -4.8625 | -4.1157 | -3.3074 | -2.4325 | -1.4852 | -0.45931 | 0.65193 | 1.8558 | 3.1604 | 4.5743 | 6.1071 | 7.7688 | 9.5709 | 11.5254 | 10.756 | 7.3387 | 1.9864 | -6.1266 | -18.1693 | -35.7981 | -61.3617 | -98.1935 | -151.0275 | -226.5923 | -334.4586 | -488.2487 | -707.3645 |  | 0.8283 | 0.89022 | 0.95719 | 1.0296 | 1.108 | 1.1928 | 1.2847 | 1.3841 | 1.4918 | 1.6084 | 1.7348 | 1.8717 | 2.0201 | 2.181 | 2.3554 | 2.5445 | 2.7497 | 2.9722 | 3.2136 | 3.4756 | 3.7599 | 4.0685 | 4.4036 | 4.7673 | 5.1623 | 5.5913 | 6.0573 | 6.5635 | 7.1135 | 7.7111 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | -1.2394 | -1.1775 | -1.1105 | -1.0381 | -0.95968 | -0.87485 | -0.78302 | -0.68359 | -0.57591 | -0.45928 | -0.33292 | -0.19599 | -0.047591 | 0.11328 | 0.2877 | 0.47684 | 0.68197 | 0.49729 | -0.067006 | -0.91104 | -2.1518 | -3.9546 | -6.5538 | -10.2809 | -15.6068 | -23.1993 | -34.0079 | -49.3823 | -71.2434 | -102.3268 |  | 19.0715 | 20.4972 | 22.039 | 23.707 | 25.5118 | 27.465 | 29.5794 | 31.8687 | 34.3479 | 37.0334 | 39.9428 | 43.0955 | 46.5124 | 50.2164 | 54.2323 | 58.5872 | 63.3105 | 68.4341 | 73.9929 | 80.0249 | 86.5713 | 93.677 | 101.391 | 109.7665 | 118.8615 | 128.7391 | 139.4681 | 151.1233 | 163.7863 | 177.5458 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 19.0467 | 20.4723 | 22.0142 | 23.6822 | 25.487 | 27.4402 | 29.5546 | 31.8439 | 34.3231 | 37.0086 | 39.918 | 43.0707 | 46.4876 | 50.1916 | 54.2075 | 58.5624 | 63.2857 | 68.4044 | 73.9535 | 79.9722 | 86.5003 | 93.5807 | 101.2595 | 109.5859 | 118.6123 | 128.3936 | 138.9874 | 150.4521 | 162.8461 | 176.2256 |  | 178.2235 | 194.8448 | 212.8209 | 232.2669 | 253.3078 | 276.0795 | 300.7299 | 327.4198 | 356.3239 | 387.6323 | 421.5518 | 458.3074 | 498.1437 | 541.3268 | 588.1465 | 638.9178 | 693.9837 | 745.0282 | 792.6429 | 839.366 | 883.1447 | 920.9315 | 948.2549 | 958.6067 | 942.5671 | 886.558 | 771.0616 | 568.078 | 237.4924 | -278.1135
| TRUE | 1656 | 22006084 | FB | Blank | 66 | TRANS NO.3 | DIFFERENTIAL | Blank | ASEA | RYDSA_1105 | RYDSA 1105 | RYDSA | Electromechanical |  | 0.066046 | 2190 |  | 5.5 | 0.0019187 | 0.00033459 | 0.0015842 | 20.4982 | 160.6041 | 181.1023 | 7.3461 | 0.77104 | 17.7529 |  | 7.3552 | 0.0040026 | 0.00069797 | 0.0033046 | 42.7601 | 335.0274 | 377.7874 | 15.3244 | 1.6084 | 37.0334 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.22443 | 54.4883 | 14.6724 | 2.0677 | 0.024808 |  | 206.9724 | 431.7536 | 71.2532 | 360.5004 |  | 0.029065 |  | 5.6622 | 5.8292 | 6.0011 | 6.1781 | 6.3603 | 6.5479 | 6.741 | 6.9398 | 7.1445 | 7.3552 | 7.5721 | 7.7954 | 8.0253 | 8.262 | 8.5056 | 8.7565 | 9.0147 | 9.2806 | 9.5543 | 9.8361 | 10.1262 | 10.4248 | 10.7322 | 11.0488 | 11.3746 | 11.7101 | 12.0554 | 12.411 | 12.777 | 13.1538 |  | 0.0020613 | 0.0022153 | 0.002382 | 0.0025623 | 0.0027573 | 0.0029684 | 0.003197 | 0.0034444 | 0.0037123 | 0.0040026 | 0.004317 | 0.0046578 | 0.0050271 | 0.0054274 | 0.0058615 | 0.0063321 | 0.0068426 | 0.0073964 | 0.0079972 | 0.0086491 | 0.0093567 | 0.010125 | 0.010958 | 0.011864 | 0.012847 | 0.013914 | 0.015074 | 0.016333 | 0.017702 | 0.019189 |  | 0.00035944 | 0.00038631 | 0.00041537 | 0.00044681 | 0.00048082 | 0.00051764 | 0.00055749 | 0.00060063 | 0.00064736 | 0.00069797 | 0.00075281 | 0.00081223 | 0.00087663 | 0.00094644 | 0.0010221 | 0.0011042 | 0.0011932 | 0.0012898 | 0.0013946 | 0.0015082 | 0.0016316 | 0.0017655 | 0.0019109 | 0.0020688 | 0.0022402 | 0.0024264 | 0.0026286 | 0.0028482 | 0.0030869 | 0.0033462 | 222.3447 | 238.9661 | 256.9422 | 276.3882 | 297.429 | 320.2008 | 344.8512 | 371.5411 | 400.4452 | 431.7536 | 465.6731 | 502.4287 | 542.2649 | 585.4481 | 632.2678 | 683.0391 | 738.105 | 797.8386 | 862.6463 | 932.97 | 1009.291 | 1092.133 | 1182.0665 | 1279.7122 | 1385.7462 | 1500.9044 | 1625.9883 | 1761.8708 | 1909.5022 | 2069.9177 |  | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 44.124 | 52.8136 | 70.0076 | 93.6097 | 126.154 | 171.212 | 233.8259 | 321.1252 | 443.2062 | 614.384 | 854.979 | 1193.8659 | 1672.1121 | 2348.1749 |  | 22.0206 | 23.6667 | 25.4471 | 27.373 | 29.4568 | 31.7121 | 34.1534 | 36.7967 | 39.6593 | 42.7601 | 46.1194 | 49.7596 | 53.7049 | 57.9817 | 62.6186 | 67.6469 | 73.1005 | 79.0164 | 85.4349 | 92.3996 | 99.9583 | 108.1628 | 117.0696 | 126.7403 | 137.2417 | 148.6467 | 161.0348 | 174.4923 | 189.1135 | 205.0007 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | -5.1113 | -3.4652 | -1.6848 | 0.24105 | 2.3249 | 4.5802 | 7.0215 | 9.6648 | 12.5274 | 15.6281 | 18.9875 | 22.6277 | 26.573 | 30.8498 | 35.4867 | 40.515 | 45.9686 | 46.5412 | 42.3871 | 34.8388 | 22.386 | 2.8842 | -26.7103 | -70.7201 | -135.2865 | -229.139 | -364.6931 | -559.6177 | -839.0709 | -1238.8958 |  | 172.5326 | 185.4302 | 199.3792 | 214.4686 | 230.7957 | 248.4659 | 267.5938 | 288.3043 | 310.733 | 335.0274 | 361.3479 | 389.869 | 420.7807 | 454.2895 | 490.6201 | 530.0171 | 572.7465 | 619.098 | 669.3867 | 723.9557 | 783.1784 | 847.4613 | 917.2469 | 993.0169 | 1075.296 | 1164.6552 | 1261.7164 | 1367.157 | 1481.7144 | 1606.1918 |  | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.22443 | 0.26863 | 0.35609 | 0.47614 | 0.64167 | 0.87085 | 1.1893 | 1.6334 | 2.2543 | 3.125 | 4.3488 | 6.0725 | 8.505 | 11.9437 |  | 172.3082 | 185.2058 | 199.1547 | 214.2442 | 230.5713 | 248.2414 | 267.3694 | 288.0799 | 310.5086 | 334.8029 | 361.1234 | 389.6446 | 420.5563 | 454.0651 | 490.3957 | 529.7927 | 572.5221 | 618.8294 | 669.0306 | 723.4796 | 782.5367 | 846.5904 | 916.0575 | 991.3835 | 1073.0416 | 1161.5302 | 1257.3676 | 1361.0845 | 1473.2093 | 1594.2481 |  | 167.1969 | 181.7407 | 197.4699 | 214.4852 | 232.8962 | 252.8216 | 274.3909 | 297.7447 | 323.036 | 350.4311 | 380.1109 | 412.2723 | 447.1293 | 484.9149 | 525.8824 | 570.3076 | 618.4907 | 665.3706 | 711.4177 | 758.3184 | 804.9227 | 849.4747 | 889.3473 | 920.6634 | 937.7551 | 932.3912 | 892.6745 | 801.4668 | 634.1384 | 355.3523 |  | 7.8918 | 8.4817 | 9.1197 | 9.8099 | 10.5567 | 11.365 | 12.2399 | 13.1872 | 14.2131 | 15.3244 | 16.5283 | 17.8329 | 19.2468 | 20.7795 | 22.4413 | 24.2433 | 26.1978 | 28.3179 | 30.6182 | 33.1142 | 35.8231 | 38.7634 | 41.9555 | 45.4212 | 49.1847 | 53.2721 | 57.7117 | 62.5347 | 67.7746 | 73.4683 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | -6.7807 | -6.1907 | -5.5527 | -4.8625 | -4.1157 | -3.3074 | -2.4325 | -1.4852 | -0.45931 | 0.65193 | 1.8558 | 3.1604 | 4.5743 | 6.1071 | 7.7688 | 9.5709 | 11.5254 | 10.756 | 7.3387 | 1.9864 | -6.1266 | -18.1693 | -35.7981 | -61.3617 | -98.1935 | -151.0275 | -226.5923 | -334.4586 | -488.2487 | -707.3645 |  | 0.8283 | 0.89022 | 0.95719 | 1.0296 | 1.108 | 1.1928 | 1.2847 | 1.3841 | 1.4918 | 1.6084 | 1.7348 | 1.8717 | 2.0201 | 2.181 | 2.3554 | 2.5445 | 2.7497 | 2.9722 | 3.2136 | 3.4756 | 3.7599 | 4.0685 | 4.4036 | 4.7673 | 5.1623 | 5.5913 | 6.0573 | 6.5635 | 7.1135 | 7.7111 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | -1.2394 | -1.1775 | -1.1105 | -1.0381 | -0.95968 | -0.87485 | -0.78302 | -0.68359 | -0.57591 | -0.45928 | -0.33292 | -0.19599 | -0.047591 | 0.11328 | 0.2877 | 0.47684 | 0.68197 | 0.49729 | -0.067006 | -0.91104 | -2.1518 | -3.9546 | -6.5538 | -10.2809 | -15.6068 | -23.1993 | -34.0079 | -49.3823 | -71.2434 | -102.3268 |  | 19.0715 | 20.4972 | 22.039 | 23.707 | 25.5118 | 27.465 | 29.5794 | 31.8687 | 34.3479 | 37.0334 | 39.9428 | 43.0955 | 46.5124 | 50.2164 | 54.2323 | 58.5872 | 63.3105 | 68.4341 | 73.9929 | 80.0249 | 86.5713 | 93.677 | 101.391 | 109.7665 | 118.8615 | 128.7391 | 139.4681 | 151.1233 | 163.7863 | 177.5458 |  | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.024808 | 0.029694 | 0.039361 | 0.052631 | 0.070929 | 0.096263 | 0.13147 | 0.18055 | 0.24919 | 0.34543 | 0.4807 | 0.67124 | 0.94013 | 1.3202 |  | 19.0467 | 20.4723 | 22.0142 | 23.6822 | 25.487 | 27.4402 | 29.5546 | 31.8439 | 34.3231 | 37.0086 | 39.918 | 43.0707 | 46.4876 | 50.1916 | 54.2075 | 58.5624 | 63.2857 | 68.4044 | 73.9535 | 79.9722 | 86.5003 | 93.5807 | 101.2595 | 109.5859 | 118.6123 | 128.3936 | 138.9874 | 150.4521 | 162.8461 | 176.2256 |  | 178.2235 | 194.8448 | 212.8209 | 232.2669 | 253.3078 | 276.0795 | 300.7299 | 327.4198 | 356.3239 | 387.6323 | 421.5518 | 458.3074 | 498.1437 | 541.3268 | 588.1465 | 638.9178 | 693.9837 | 745.0282 | 792.6429 | 839.366 | 883.1447 | 920.9315 | 948.2549 | 958.6067 | 942.5671 | 886.558 | 771.0616 | 568.078 | 237.4924 | -278.1135
Aggregated by ZSS
| AllBC | Future | All | BC | [145 empty] | 197145.2726 | 214514.5035 | 233615.3188 | 254638.7227 | 277803.6183 | 303382.9092 | 331817.6312 | 363823.5633 | 399724.5571 | 439843.1823 | 484773.0223 | 535296.8141 | 592392.0252 | 657300.5702 | 731629.1637 | 817495.1423 | 917740.1098 | 1036245.1854 | 1177094.5474 | 1337807.8262 | 1491262.7321 | 1660954.6308 | 1818841.7189 | 1971890.4131 | 2135118.0374 | 2301463.4296 | 2485680.7644 | 2689851.0319 | 2916324.4194 | 3167759.6771 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3444.2155 | 3701.5638 | 3986.1038 | 4301.293 | 4652.7959 | 5062.0822 | 5627.975 | 6317.7867 | 7215.4575 | 8372.0773 | 9853.7535 | 11791.3522 | 14376.752 | 17892.9934 | 22759.7521 | 29602.0632 | 39354.3595 | 53418.2195 | 73230.2277 | 96061.2449 | 105596.8214 | 113357.0758 | 122153.0892 | 133050.9281 | 141900.1569 | 144104.7562 | 146533.735 | 149211.0685 | 152163.469 | 155420.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64901.7627 | 70698.5708 | 77063.6482 | 84057.5774 | 91748.2095 | 100211.7316 | 109534.1763 | 119861.9561 | 131286.2795 | 143913.7028 | 157887.8874 | 173372.8804 | 190556.6321 | 209655.2366 | 230918.0648 | 254634.0019 | 281139.0599 | 310825.7143 | 344154.4072 | 381651.8907 | 423870.2767 | 471600.6203 | 516593.0089 | 560151.4377 | 608107.9116 | 660924.1304 | 719113.1675 | 783245.0412 | 853953.7873 | 931945.2621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2970.7377 | 3200.7814 | 3455.5812 | 3738.3611 | 4054.5771 | 4419.5679 | 4899.0117 | 5482.4848 | 6226.2912 | 7165.82 | 8347.8989 | 9864.709 | 11850.1148 | 14499.9086 | 18102.2313 | 23083.3898 | 30076.9996 | 40028.5175 | 53798.8886 | 69964.1675 | 77594.8599 | 84466.5178 | 91811.1193 | 100538.7037 | 107712.4383 | 109772.0933 | 112052.5589 | 114579.5691 | 117382.1996 | 120493.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254.7442 | 272.5867 | 292.433 | 314.5666 | 339.5625 | 369.3615 | 412.9651 | 468.1222 | 542.6135 | 641.2125 | 770.0451 | 941.5506 | 1173.9492 | 1494.0759 | 1941.6448 | 2575.6776 | 3484.2132 | 4798.9955 | 6639.551 | 8803.1036 | 9747.2962 | 10564.6006 | 11470.0624 | 12586.2715 | 13471.2133 | 13621.6439 | 13787.8879 | 13971.7362 | 14175.2041 | 14400.5621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125573.8126 | 136641.0007 | 148817.5527 | 162226.9246 | 177008.4734 | 193320.166 | 211343.5031 | 231693.2134 | 254453.9155 | 279750.3697 | 307913.4374 | 339326.3219 | 374434.5771 | 413758.3558 | 457907.4707 | 507600.0099 | 563685.4775 | 627173.7385 | 699271.473 | 781327.4196 | 874453.4779 | 980965.8163 | 1076814.439 | 1165563.0721 | 1263926.3172 | 1373040.8059 | 1494193.4151 | 1628843.6169 | 1778649.7595 | 1945499.7635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AllFB | Future | All | FB | [145 empty] | 186385.5722 | 207910.2554 | 232230.995 | 259749.507 | 290930.8919 | 326314.5525 | 366544.5379 | 412349.8673 | 464589.0802 | 524260.7449 | 592532.5453 | 670783.2489 | 760637.4908 | 864014.9612 | 983190.812 | 1120870.231 | 1280281.0264 | 1407197.7894 | 1533141.2658 | 1666472.255 | 1816535.8843 | 1986894.7831 | 2178169.8654 | 2391540.6772 | 2631762.4953 | 2901251.3458 | 3206381.2646 | 3508446.3651 | 3674512.7612 | 3713915.7949 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6760.6001 | 7514.3138 | 8366.7419 | 9333.2751 | 10432.27 | 11685.7581 | 13131.0432 | 14800.2772 | 16736.1507 | 18990.6204 | 21627.5979 | 24731.1539 | 28408.5413 | 32797.6431 | 38077.0332 | 44479.6117 | 52311.1428 | 60625.7662 | 70420.6198 | 76720.5817 | 83692.998 | 92140.7284 | 100934.461 | 109065.8782 | 117748.1278 | 126462.3756 | 136271.4801 | 146314.4681 | 152713.1903 | 154073.7096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162043.0455 | 180896.6911 | 202206.7929 | 226325.1435 | 253658.2278 | 284676.317 | 319924.1822 | 360033.6004 | 405738.1658 | 457890.7282 | 517483.9102 | 585674.3222 | 663811.1456 | 753469.8913 | 856492.2979 | 975033.5143 | 1111617.929 | 1216511.1549 | 1317811.0249 | 1431984.0694 | 1560764.1812 | 1706124.2784 | 1870312.8528 | 2055899.6039 | 2265831.069 | 2503472.6502 | 2772677.0078 | 3038595.5726 | 3182832.0018 | 3215984.1487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5539.3699 | 6182.9184 | 6913.6244 | 7745.2589 | 8694.1947 | 9780.0014 | 11031.9791 | 12478.4421 | 14158.3697 | 16115.6836 | 18403.5778 | 21091.8874 | 24268.6993 | 28045.962 | 32567.0096 | 38016.6934 | 44635.0734 | 51151.2372 | 58626.5781 | 63685.0643 | 69255.4657 | 75927.3583 | 83158.14 | 90491.2029 | 98292.9622 | 106019.3153 | 114758.2751 | 123468.8095 | 128409.3459 | 129542.1049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.2197 | 444.0307 | 496.2286 | 555.9033 | 624.3783 | 703.2723 | 795.3939 | 903.2002 | 1030.4034 | 1181.1208 | 1360.435 | 1575.373 | 1835.0633 | 2151.4433 | 2540.2223 | 3022.1931 | 3625.0247 | 4292.4697 | 5104.8311 | 5545.7119 | 6023.7186 | 6617.191 | 7244.2385 | 7834.311 | 8431.9144 | 8952.2208 | 9539.2634 | 10132.5779 | 10491.4795 | 10573.2859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11644.337 | 12872.3013 | 14247.6071 | 15789.9263 | 17521.8211 | 19469.2037 | 21661.9394 | 24134.3473 | 26925.9906 | 30082.5918 | 33657.0245 | 37710.5124 | 42314.0413 | 47550.0215 | 53514.249 | 60318.2184 | 68091.8565 | 74617.1615 | 81178.2119 | 88536.8277 | 96799.5208 | 106085.227 | 116520.173 | 128249.6812 | 141458.4219 | 156344.7839 | 173135.2382 | 189934.9371 | 200066.7436 | 203742.5458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not replacedBC | Future | Not replaced | BC | [145 empty] | 1210.8717 | 1234.3522 | 1263.8706 | 1301.0856 | 1351.704 | 1447.9816 | 1752.1016 | 2201.2566 | 2938.0124 | 4044.7518 | 5626.303 | 7901.7459 | 11196.1349 | 15993.3925 | 23016.1663 | 33346.5979 | 48609.2419 | 71248.5063 | 103645.5154 | 141292.6703 | 154644.3737 | 164286.8859 | 176351.6394 | 193474.134 | 206389.3003 | 206396.477 | 206404.2168 | 206412.5647 | 206421.5695 | 206431.2839 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 663.6974 | 675.9272 | 691.2762 | 710.5993 | 736.6365 | 787.5629 | 955.6823 | 1201.6282 | 1606.1404 | 2214.9217 | 3086.5625 | 4342.9983 | 6165.3981 | 8823.8284 | 12722.0805 | 18465.523 | 26963.9616 | 39587.7782 | 57733.5868 | 78620.4624 | 85866.1429 | 90901.049 | 97301.5043 | 106384.9415 | 113236.6001 | 113241.117 | 113245.9883 | 113251.2423 | 113256.9098 | 113263.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4229 | 1.4229 | 1.4229 | 1.4229 | 1.4229 | 1.4615 | 1.8556 | 2.5872 | 3.6597 | 5.2345 | 7.5539 | 10.9858 | 16.0848 | 23.6884 | 35.0626 | 52.1251 | 77.7829 | 116.4485 | 174.8252 | 247.1971 | 258.5489 | 258.6744 | 258.8523 | 259.1048 | 259.2952 | 259.2952 | 259.2952 | 259.2952 | 259.2952 | 259.2952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 469.715 | 479.5759 | 491.9948 | 507.6764 | 529.2209 | 568.7208 | 685.2588 | 858.2695 | 1142.0414 | 1567.5971 | 2173.7735 | 3043.1697 | 4298.0609 | 6120.0939 | 8779.979 | 12682.332 | 18433.5035 | 26944.3322 | 39031.3652 | 53213.1536 | 58485.0122 | 62523.2754 | 67487.634 | 74533.302 | 79847.5397 | 79849.8709 | 79852.385 | 79855.0967 | 79858.0218 | 79861.1773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.1932 | 67.5831 | 69.3335 | 71.5438 | 74.5805 | 80.1477 | 96.5702 | 120.9494 | 160.9373 | 220.9051 | 306.3247 | 428.8349 | 605.6657 | 862.4124 | 1237.2202 | 1787.1025 | 2597.4981 | 3796.7498 | 5499.8899 | 7498.148 | 8241.1027 | 8810.2909 | 9510.011 | 10503.0889 | 11252.124 | 11252.4526 | 11252.8069 | 11253.1891 | 11253.6014 | 11254.0462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8432 | 9.8432 | 9.8432 | 9.8432 | 9.8432 | 10.0887 | 12.7347 | 17.8222 | 25.2337 | 36.0934 | 52.0885 | 75.7572 | 110.9255 | 163.3694 | 241.8239 | 359.5153 | 536.4958 | 803.1975 | 1205.8483 | 1713.7092 | 1793.567 | 1793.5963 | 1793.6378 | 1793.6968 | 1793.7413 | 1793.7413 | 1793.7413 | 1793.7413 | 1793.7413 | 1793.7413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not replacedFB | Future | Not replaced | FB | [145 empty] | 7308.9428 | 7863.2668 | 8467.7527 | 9128.066 | 9850.7768 | 10643.5622 | 11532.8389 | 12528.9729 | 13652.8161 | 14924.6853 | 16367.6446 | 18018.4484 | 19924.8958 | 22149.7017 | 24775.8167 | 27913.7648 | 31711.7858 | 36369.8948 | 41882.9538 | 46714.3193 | 52814.6416 | 60656.0327 | 68338.8829 | 74163.1635 | 79592.2201 | 83276.2963 | 87278.8168 | 91627.8652 | 96354.0329 | 101490.6451 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640.76 | 694.2984 | 755.2677 | 825.1646 | 905.8694 | 999.7553 | 1120.5177 | 1271.7565 | 1461.3792 | 1698.6414 | 1994.6205 | 2367.4899 | 2841.6515 | 3449.9913 | 4236.9859 | 5262.9879 | 6610.1541 | 8390.6617 | 10587.9094 | 12239.0441 | 14523.7491 | 17705.1503 | 20578.9886 | 22051.8276 | 23240.0816 | 23514.9118 | 23813.9993 | 24139.5291 | 24493.8853 | 24879.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5531.652 | 5945.2143 | 6392.5009 | 6876.3796 | 7399.9695 | 7966.663 | 8580.1797 | 9244.5346 | 9964.0912 | 10743.6157 | 11588.3011 | 12503.8077 | 13496.3089 | 14572.5419 | 15739.8658 | 17006.3267 | 18380.7323 | 19872.7387 | 21492.115 | 23244.7652 | 25147.9496 | 27215.267 | 29457.4122 | 31886.5517 | 34524.3669 | 37389.1686 | 40500.8951 | 43881.2589 | 47553.9053 | 51544.5859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313.8969 | 339.3457 | 368.5262 | 402.2232 | 441.427 | 487.3924 | 547.4944 | 623.646 | 722.8373 | 849.9752 | 1010.3432 | 1214.5246 | 1476.7956 | 1816.4819 | 2259.8338 | 2842.6218 | 3613.7385 | 4640.2077 | 5922.0935 | 6951.4714 | 8384.8269 | 10390.7081 | 12355.2889 | 13740.6812 | 14820.4829 | 14944.5303 | 15079.5635 | 15226.5752 | 15386.6489 | 15560.9678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.1345 | 38.0403 | 41.4164 | 45.3687 | 50.0317 | 55.5765 | 63.0363 | 72.6742 | 85.4679 | 102.1013 | 123.31 | 150.5764 | 185.9019 | 231.9988 | 292.5542 | 372.5957 | 478.9987 | 621.1925 | 799.1716 | 941.3602 | 1140.2345 | 1419.5261 | 1692.7165 | 1883.987 | 2031.8412 | 2044.6093 | 2058.5192 | 2073.6752 | 2090.1912 | 2108.1913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 787.4994 | 846.3681 | 910.0416 | 978.9299 | 1053.4792 | 1134.175 | 1221.6108 | 1316.3616 | 1419.0405 | 1530.3516 | 1651.0698 | 1782.0498 | 1924.2381 | 2078.6878 | 2246.577 | 2429.2327 | 2628.1622 | 2845.0942 | 3081.6643 | 3337.6784 | 3617.8814 | 3925.3813 | 4254.4767 | 4600.116 | 4975.4475 | 5383.0763 | 5825.8396 | 6306.8268 | 6829.4022 | 7397.2301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ReplacedBC | New | Replaced | BC | [145 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2442.1476 | 3237.2113 | 4328.5903 | 5833.4678 | 7916.9895 | 10812.3058 | 14849.1013 | 20494.23 | 28409.6353 | 39534.9511 | 55205.3658 | 77319.8784 | 108581.5919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 1082.5469 | 1434.9801 | 1918.7629 | 2585.8399 | 3509.4163 | 4792.8424 | 6582.2594 | 9084.613 | 12593.3272 | 17524.9196 | 24471.2481 | 34274.0945 | 48131.6813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 45.5936 | 60.4371 | 80.8125 | 108.9078 | 147.8061 | 201.8601 | 277.225 | 382.6166 | 530.3931 | 738.097 | 1030.6555 | 1443.522 | 2027.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 1054.5544 | 1397.8743 | 1869.1474 | 2518.9751 | 3418.6697 | 4668.9089 | 6412.0551 | 8849.7027 | 12267.6883 | 17071.7594 | 23838.4694 | 33387.8334 | 46887.0901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 148.4956 | 196.8397 | 263.2014 | 354.706 | 481.3952 | 657.4459 | 902.9046 | 1246.1586 | 1727.4575 | 2403.9361 | 3356.781 | 4701.4614 | 6602.3404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 110.5616 | 146.556 | 195.9652 | 264.0945 | 358.4203 | 489.4979 | 672.2529 | 927.8209 | 1286.1694 | 1789.838 | 2499.2737 | 3500.4485 | 4915.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ReplacedFB | New | Replaced | FB | [145 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3579.5473 | 3579.5473 | 3579.5473 | 3579.5473 | 3579.5473 | 3579.5473 | 3579.5473 | 3579.5473 | 3579.5473 | 3579.5473 | 3579.5473 | 3579.5473 | 3579.5473 | 3579.5473 | 3579.5473 | 3579.5473 | 3579.5473 | 4284.4938 | 5679.3504 | 7594.0611 | 10234.2121 | 13889.534 | 18969.0652 | 26051.2026 | 35954.9934 | 49841.7481 | 69359.9569 | 96852.0685 | 135649.6789 | 190495.1017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 2151.162 | 2851.4927 | 3812.8322 | 5138.4014 | 6973.6683 | 9524.0033 | 13079.8085 | 18052.3116 | 25024.5845 | 34824.3022 | 48627.5634 | 68107.0985 | 95643.9318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 98.7591 | 130.911 | 175.0458 | 235.9022 | 320.1586 | 437.2436 | 600.4894 | 828.7753 | 1148.8698 | 1598.7714 | 2232.4743 | 3126.7728 | 4390.9791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1775.1526 | 2353.07 | 3146.3734 | 4240.2415 | 5754.7154 | 7859.2682 | 10793.5412 | 14896.8825 | 20650.4464 | 28737.2359 | 40127.775 | 56202.4113 | 78925.9816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 249.9676 | 331.3468 | 443.0556 | 597.0884 | 810.3485 | 1106.7005 | 1519.8893 | 2097.7001 | 2907.8865 | 4046.6253 | 5650.5807 | 7914.1259 | 11113.9387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 8.5015 | 11.2693 | 15.0686 | 20.3073 | 27.5604 | 37.6395 | 51.6923 | 71.344 | 98.8989 | 137.6281 | 192.1796 | 269.1641 | 377.9916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Risk_consol
CitiPower
Relay replacements
RISK CONSOLIDATION CALCS
All
|  | Risk | Assets | ZSS | Type | Option 1 Yr | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
[7 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
Risk without replacement
| Safety | Future | All | BC | Safety |  | 2970.7377 | 3200.7814 | 3455.5812 | 3738.3611 | 4054.5771 | 4419.5679 | 4899.0117 | 5482.4848 | 6226.2912 | 7165.82 | 8347.8989 | 9864.709 | 11850.1148 | 14499.9086 | 18102.2313 | 23083.3898 | 30076.9996 | 40028.5175 | 53798.8886 | 69964.1675 | 77594.8599 | 84466.5178 | 91811.1193 | 100538.7037 | 107712.4383 | 109772.0933 | 112052.5589 | 114579.5691 | 117382.1996 | 120493.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3444.2155 | 3701.5638 | 3986.1038 | 4301.293 | 4652.7959 | 5062.0822 | 5627.975 | 6317.7867 | 7215.4575 | 8372.0773 | 9853.7535 | 11791.3522 | 14376.752 | 17892.9934 | 22759.7521 | 29602.0632 | 39354.3595 | 53418.2195 | 73230.2277 | 96061.2449 | 105596.8214 | 113357.0758 | 122153.0892 | 133050.9281 | 141900.1569 | 144104.7562 | 146533.735 | 149211.0685 | 152163.469 | 155420.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64901.7627 | 70698.5708 | 77063.6482 | 84057.5774 | 91748.2095 | 100211.7316 | 109534.1763 | 119861.9561 | 131286.2795 | 143913.7028 | 157887.8874 | 173372.8804 | 190556.6321 | 209655.2366 | 230918.0648 | 254634.0019 | 281139.0599 | 310825.7143 | 344154.4072 | 381651.8907 | 423870.2767 | 471600.6203 | 516593.0089 | 560151.4377 | 608107.9116 | 660924.1304 | 719113.1675 | 783245.0412 | 853953.7873 | 931945.2621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2970.7377 | 3200.7814 | 3455.5812 | 3738.3611 | 4054.5771 | 4419.5679 | 4899.0117 | 5482.4848 | 6226.2912 | 7165.82 | 8347.8989 | 9864.709 | 11850.1148 | 14499.9086 | 18102.2313 | 23083.3898 | 30076.9996 | 40028.5175 | 53798.8886 | 69964.1675 | 77594.8599 | 84466.5178 | 91811.1193 | 100538.7037 | 107712.4383 | 109772.0933 | 112052.5589 | 114579.5691 | 117382.1996 | 120493.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254.7442 | 272.5867 | 292.433 | 314.5666 | 339.5625 | 369.3615 | 412.9651 | 468.1222 | 542.6135 | 641.2125 | 770.0451 | 941.5506 | 1173.9492 | 1494.0759 | 1941.6448 | 2575.6776 | 3484.2132 | 4798.9955 | 6639.551 | 8803.1036 | 9747.2962 | 10564.6006 | 11470.0624 | 12586.2715 | 13471.2133 | 13621.6439 | 13787.8879 | 13971.7362 | 14175.2041 | 14400.5621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125573.8126 | 136641.0007 | 148817.5527 | 162226.9246 | 177008.4734 | 193320.166 | 211343.5031 | 231693.2134 | 254453.9155 | 279750.3697 | 307913.4374 | 339326.3219 | 374434.5771 | 413758.3558 | 457907.4707 | 507600.0099 | 563685.4775 | 627173.7385 | 699271.473 | 781327.4196 | 874453.4779 | 980965.8163 | 1076814.439 | 1165563.0721 | 1263926.3172 | 1373040.8059 | 1494193.4151 | 1628843.6169 | 1778649.7595 | 1945499.7635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety | Future | All | FB | Safety |  | 5539.3699 | 6182.9184 | 6913.6244 | 7745.2589 | 8694.1947 | 9780.0014 | 11031.9791 | 12478.4421 | 14158.3697 | 16115.6836 | 18403.5778 | 21091.8874 | 24268.6993 | 28045.962 | 32567.0096 | 38016.6934 | 44635.0734 | 51151.2372 | 58626.5781 | 63685.0643 | 69255.4657 | 75927.3583 | 83158.14 | 90491.2029 | 98292.9622 | 106019.3153 | 114758.2751 | 123468.8095 | 128409.3459 | 129542.1049
| Environment | Future | All | BC | Environment |  | 254.7442 | 272.5867 | 292.433 | 314.5666 | 339.5625 | 369.3615 | 412.9651 | 468.1222 | 542.6135 | 641.2125 | 770.0451 | 941.5506 | 1173.9492 | 1494.0759 | 1941.6448 | 2575.6776 | 3484.2132 | 4798.9955 | 6639.551 | 8803.1036 | 9747.2962 | 10564.6006 | 11470.0624 | 12586.2715 | 13471.2133 | 13621.6439 | 13787.8879 | 13971.7362 | 14175.2041 | 14400.5621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3444.2155 | 3701.5638 | 3986.1038 | 4301.293 | 4652.7959 | 5062.0822 | 5627.975 | 6317.7867 | 7215.4575 | 8372.0773 | 9853.7535 | 11791.3522 | 14376.752 | 17892.9934 | 22759.7521 | 29602.0632 | 39354.3595 | 53418.2195 | 73230.2277 | 96061.2449 | 105596.8214 | 113357.0758 | 122153.0892 | 133050.9281 | 141900.1569 | 144104.7562 | 146533.735 | 149211.0685 | 152163.469 | 155420.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64901.7627 | 70698.5708 | 77063.6482 | 84057.5774 | 91748.2095 | 100211.7316 | 109534.1763 | 119861.9561 | 131286.2795 | 143913.7028 | 157887.8874 | 173372.8804 | 190556.6321 | 209655.2366 | 230918.0648 | 254634.0019 | 281139.0599 | 310825.7143 | 344154.4072 | 381651.8907 | 423870.2767 | 471600.6203 | 516593.0089 | 560151.4377 | 608107.9116 | 660924.1304 | 719113.1675 | 783245.0412 | 853953.7873 | 931945.2621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2970.7377 | 3200.7814 | 3455.5812 | 3738.3611 | 4054.5771 | 4419.5679 | 4899.0117 | 5482.4848 | 6226.2912 | 7165.82 | 8347.8989 | 9864.709 | 11850.1148 | 14499.9086 | 18102.2313 | 23083.3898 | 30076.9996 | 40028.5175 | 53798.8886 | 69964.1675 | 77594.8599 | 84466.5178 | 91811.1193 | 100538.7037 | 107712.4383 | 109772.0933 | 112052.5589 | 114579.5691 | 117382.1996 | 120493.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254.7442 | 272.5867 | 292.433 | 314.5666 | 339.5625 | 369.3615 | 412.9651 | 468.1222 | 542.6135 | 641.2125 | 770.0451 | 941.5506 | 1173.9492 | 1494.0759 | 1941.6448 | 2575.6776 | 3484.2132 | 4798.9955 | 6639.551 | 8803.1036 | 9747.2962 | 10564.6006 | 11470.0624 | 12586.2715 | 13471.2133 | 13621.6439 | 13787.8879 | 13971.7362 | 14175.2041 | 14400.5621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125573.8126 | 136641.0007 | 148817.5527 | 162226.9246 | 177008.4734 | 193320.166 | 211343.5031 | 231693.2134 | 254453.9155 | 279750.3697 | 307913.4374 | 339326.3219 | 374434.5771 | 413758.3558 | 457907.4707 | 507600.0099 | 563685.4775 | 627173.7385 | 699271.473 | 781327.4196 | 874453.4779 | 980965.8163 | 1076814.439 | 1165563.0721 | 1263926.3172 | 1373040.8059 | 1494193.4151 | 1628843.6169 | 1778649.7595 | 1945499.7635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environment | Future | All | FB | Environment |  | 398.2197 | 444.0307 | 496.2286 | 555.9033 | 624.3783 | 703.2723 | 795.3939 | 903.2002 | 1030.4034 | 1181.1208 | 1360.435 | 1575.373 | 1835.0633 | 2151.4433 | 2540.2223 | 3022.1931 | 3625.0247 | 4292.4697 | 5104.8311 | 5545.7119 | 6023.7186 | 6617.191 | 7244.2385 | 7834.311 | 8431.9144 | 8952.2208 | 9539.2634 | 10132.5779 | 10491.4795 | 10573.2859
| NP | Future | All | BC | NP |  | 125573.8126 | 136641.0007 | 148817.5527 | 162226.9246 | 177008.4734 | 193320.166 | 211343.5031 | 231693.2134 | 254453.9155 | 279750.3697 | 307913.4374 | 339326.3219 | 374434.5771 | 413758.3558 | 457907.4707 | 507600.0099 | 563685.4775 | 627173.7385 | 699271.473 | 781327.4196 | 874453.4779 | 980965.8163 | 1076814.439 | 1165563.0721 | 1263926.3172 | 1373040.8059 | 1494193.4151 | 1628843.6169 | 1778649.7595 | 1945499.7635
| NP | Future | All | FB | NP |  | 11644.337 | 12872.3013 | 14247.6071 | 15789.9263 | 17521.8211 | 19469.2037 | 21661.9394 | 24134.3473 | 26925.9906 | 30082.5918 | 33657.0245 | 37710.5124 | 42314.0413 | 47550.0215 | 53514.249 | 60318.2184 | 68091.8565 | 74617.1615 | 81178.2119 | 88536.8277 | 96799.5208 | 106085.227 | 116520.173 | 128249.6812 | 141458.4219 | 156344.7839 | 173135.2382 | 189934.9371 | 200066.7436 | 203742.5458
| Opex | Future | All | BC | Financial |  | 3444.2155 | 3701.5638 | 3986.1038 | 4301.293 | 4652.7959 | 5062.0822 | 5627.975 | 6317.7867 | 7215.4575 | 8372.0773 | 9853.7535 | 11791.3522 | 14376.752 | 17892.9934 | 22759.7521 | 29602.0632 | 39354.3595 | 53418.2195 | 73230.2277 | 96061.2449 | 105596.8214 | 113357.0758 | 122153.0892 | 133050.9281 | 141900.1569 | 144104.7562 | 146533.735 | 149211.0685 | 152163.469 | 155420.729
| Opex | Future | All | FB | Financial |  | 6760.6001 | 7514.3138 | 8366.7419 | 9333.2751 | 10432.27 | 11685.7581 | 13131.0432 | 14800.2772 | 16736.1507 | 18990.6204 | 21627.5979 | 24731.1539 | 28408.5413 | 32797.6431 | 38077.0332 | 44479.6117 | 52311.1428 | 60625.7662 | 70420.6198 | 76720.5817 | 83692.998 | 92140.7284 | 100934.461 | 109065.8782 | 117748.1278 | 126462.3756 | 136271.4801 | 146314.4681 | 152713.1903 | 154073.7096
| Capex | Future | All | BC | Financial |  | 64901.7627 | 70698.5708 | 77063.6482 | 84057.5774 | 91748.2095 | 100211.7316 | 109534.1763 | 119861.9561 | 131286.2795 | 143913.7028 | 157887.8874 | 173372.8804 | 190556.6321 | 209655.2366 | 230918.0648 | 254634.0019 | 281139.0599 | 310825.7143 | 344154.4072 | 381651.8907 | 423870.2767 | 471600.6203 | 516593.0089 | 560151.4377 | 608107.9116 | 660924.1304 | 719113.1675 | 783245.0412 | 853953.7873 | 931945.2621
| Capex | Future | All | FB | Financial |  | 162043.0455 | 180896.6911 | 202206.7929 | 226325.1435 | 253658.2278 | 284676.317 | 319924.1822 | 360033.6004 | 405738.1658 | 457890.7282 | 517483.9102 | 585674.3222 | 663811.1456 | 753469.8913 | 856492.2979 | 975033.5143 | 1111617.929 | 1216511.1549 | 1317811.0249 | 1431984.0694 | 1560764.1812 | 1706124.2784 | 1870312.8528 | 2055899.6039 | 2265831.069 | 2503472.6502 | 2772677.0078 | 3038595.5726 | 3182832.0018 | 3215984.1487
Residual risk of assets not replaced
| Safety | Future | Not replaced | BC | Safety | 27 | 2970.7377 | 3200.7814 | 491.9948 | 507.6764 | 529.2209 | 568.7208 | 685.2588 | 858.2695 | 1142.0414 | 1567.5971 | 2173.7735 | 3043.1697 | 4298.0609 | 6120.0939 | 8779.979 | 12682.332 | 18433.5035 | 26944.3322 | 39031.3652 | 53213.1536 | 58485.0122 | 62523.2754 | 67487.634 | 74533.302 | 79847.5397 | 79849.8709 | 79852.385 | 79855.0967 | 79858.0218 | 79861.1773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 663.6974 | 675.9272 | 691.2762 | 710.5993 | 736.6365 | 787.5629 | 955.6823 | 1201.6282 | 1606.1404 | 2214.9217 | 3086.5625 | 4342.9983 | 6165.3981 | 8823.8284 | 12722.0805 | 18465.523 | 26963.9616 | 39587.7782 | 57733.5868 | 78620.4624 | 85866.1429 | 90901.049 | 97301.5043 | 106384.9415 | 113236.6001 | 113241.117 | 113245.9883 | 113251.2423 | 113256.9098 | 113263.0239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4229 | 1.4229 | 1.4229 | 1.4229 | 1.4229 | 1.4615 | 1.8556 | 2.5872 | 3.6597 | 5.2345 | 7.5539 | 10.9858 | 16.0848 | 23.6884 | 35.0626 | 52.1251 | 77.7829 | 116.4485 | 174.8252 | 247.1971 | 258.5489 | 258.6744 | 258.8523 | 259.1048 | 259.2952 | 259.2952 | 259.2952 | 259.2952 | 259.2952 | 259.2952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 469.715 | 479.5759 | 491.9948 | 507.6764 | 529.2209 | 568.7208 | 685.2588 | 858.2695 | 1142.0414 | 1567.5971 | 2173.7735 | 3043.1697 | 4298.0609 | 6120.0939 | 8779.979 | 12682.332 | 18433.5035 | 26944.3322 | 39031.3652 | 53213.1536 | 58485.0122 | 62523.2754 | 67487.634 | 74533.302 | 79847.5397 | 79849.8709 | 79852.385 | 79855.0967 | 79858.0218 | 79861.1773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.1932 | 67.5831 | 69.3335 | 71.5438 | 74.5805 | 80.1477 | 96.5702 | 120.9494 | 160.9373 | 220.9051 | 306.3247 | 428.8349 | 605.6657 | 862.4124 | 1237.2202 | 1787.1025 | 2597.4981 | 3796.7498 | 5499.8899 | 7498.148 | 8241.1027 | 8810.2909 | 9510.011 | 10503.0889 | 11252.124 | 11252.4526 | 11252.8069 | 11253.1891 | 11253.6014 | 11254.0462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8432 | 9.8432 | 9.8432 | 9.8432 | 9.8432 | 10.0887 | 12.7347 | 17.8222 | 25.2337 | 36.0934 | 52.0885 | 75.7572 | 110.9255 | 163.3694 | 241.8239 | 359.5153 | 536.4958 | 803.1975 | 1205.8483 | 1713.7092 | 1793.567 | 1793.5963 | 1793.6378 | 1793.6968 | 1793.7413 | 1793.7413 | 1793.7413 | 1793.7413 | 1793.7413 | 1793.7413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety | Future | Not replaced | FB | Safety | 28 | 5539.3699 | 6182.9184 | 6913.6244 | 402.2232 | 441.427 | 487.3924 | 547.4944 | 623.646 | 722.8373 | 849.9752 | 1010.3432 | 1214.5246 | 1476.7956 | 1816.4819 | 2259.8338 | 2842.6218 | 3613.7385 | 4640.2077 | 5922.0935 | 6951.4714 | 8384.8269 | 10390.7081 | 12355.2889 | 13740.6812 | 14820.4829 | 14944.5303 | 15079.5635 | 15226.5752 | 15386.6489 | 15560.9678
| Environment | Future | Not replaced | BC | Environment | 27 | 254.7442 | 272.5867 | 69.3335 | 71.5438 | 74.5805 | 80.1477 | 96.5702 | 120.9494 | 160.9373 | 220.9051 | 306.3247 | 428.8349 | 605.6657 | 862.4124 | 1237.2202 | 1787.1025 | 2597.4981 | 3796.7498 | 5499.8899 | 7498.148 | 8241.1027 | 8810.2909 | 9510.011 | 10503.0889 | 11252.124 | 11252.4526 | 11252.8069 | 11253.1891 | 11253.6014 | 11254.0462
| Environment | Future | Not replaced | FB | Environment | 28 | 398.2197 | 444.0307 | 496.2286 | 45.3687 | 50.0317 | 55.5765 | 63.0363 | 72.6742 | 85.4679 | 102.1013 | 123.31 | 150.5764 | 185.9019 | 231.9988 | 292.5542 | 372.5957 | 478.9987 | 621.1925 | 799.1716 | 941.3602 | 1140.2345 | 1419.5261 | 1692.7165 | 1883.987 | 2031.8412 | 2044.6093 | 2058.5192 | 2073.6752 | 2090.1912 | 2108.1913
| NP | Future | Not replaced | BC | NP | 27 | 125573.8126 | 136641.0007 | 9.8432 | 9.8432 | 9.8432 | 10.0887 | 12.7347 | 17.8222 | 25.2337 | 36.0934 | 52.0885 | 75.7572 | 110.9255 | 163.3694 | 241.8239 | 359.5153 | 536.4958 | 803.1975 | 1205.8483 | 1713.7092 | 1793.567 | 1793.5963 | 1793.6378 | 1793.6968 | 1793.7413 | 1793.7413 | 1793.7413 | 1793.7413 | 1793.7413 | 1793.7413
| NP | Future | Not replaced | FB | NP | 28 | 11644.337 | 12872.3013 | 14247.6071 | 978.9299 | 1053.4792 | 1134.175 | 1221.6108 | 1316.3616 | 1419.0405 | 1530.3516 | 1651.0698 | 1782.0498 | 1924.2381 | 2078.6878 | 2246.577 | 2429.2327 | 2628.1622 | 2845.0942 | 3081.6643 | 3337.6784 | 3617.8814 | 3925.3813 | 4254.4767 | 4600.116 | 4975.4475 | 5383.0763 | 5825.8396 | 6306.8268 | 6829.4022 | 7397.2301
| Opex | Future | Not replaced | BC | Financial | 27 | 3444.2155 | 3701.5638 | 691.2762 | 710.5993 | 736.6365 | 787.5629 | 955.6823 | 1201.6282 | 1606.1404 | 2214.9217 | 3086.5625 | 4342.9983 | 6165.3981 | 8823.8284 | 12722.0805 | 18465.523 | 26963.9616 | 39587.7782 | 57733.5868 | 78620.4624 | 85866.1429 | 90901.049 | 97301.5043 | 106384.9415 | 113236.6001 | 113241.117 | 113245.9883 | 113251.2423 | 113256.9098 | 113263.0239
| Opex | Future | Not replaced | FB | Financial | 28 | 6760.6001 | 7514.3138 | 8366.7419 | 825.1646 | 905.8694 | 999.7553 | 1120.5177 | 1271.7565 | 1461.3792 | 1698.6414 | 1994.6205 | 2367.4899 | 2841.6515 | 3449.9913 | 4236.9859 | 5262.9879 | 6610.1541 | 8390.6617 | 10587.9094 | 12239.0441 | 14523.7491 | 17705.1503 | 20578.9886 | 22051.8276 | 23240.0816 | 23514.9118 | 23813.9993 | 24139.5291 | 24493.8853 | 24879.67
| Capex | Future | Not replaced | BC | Financial | 27 | 64901.7627 | 70698.5708 | 1.4229 | 1.4229 | 1.4229 | 1.4615 | 1.8556 | 2.5872 | 3.6597 | 5.2345 | 7.5539 | 10.9858 | 16.0848 | 23.6884 | 35.0626 | 52.1251 | 77.7829 | 116.4485 | 174.8252 | 247.1971 | 258.5489 | 258.6744 | 258.8523 | 259.1048 | 259.2952 | 259.2952 | 259.2952 | 259.2952 | 259.2952 | 259.2952
| Capex | Future | Not replaced | FB | Financial | 28 | 162043.0455 | 180896.6911 | 202206.7929 | 6876.3796 | 7399.9695 | 7966.663 | 8580.1797 | 9244.5346 | 9964.0912 | 10743.6157 | 11588.3011 | 12503.8077 | 13496.3089 | 14572.5419 | 15739.8658 | 17006.3267 | 18380.7323 | 19872.7387 | 21492.115 | 23244.7652 | 25147.9496 | 27215.267 | 29457.4122 | 31886.5517 | 34524.3669 | 37389.1686 | 40500.8951 | 43881.2589 | 47553.9053 | 51544.5859
Risk after replacement
| Safety | New | Replaced | BC | Safety | 27 | 0 | 0 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 1054.5544 | 1397.8743 | 1869.1474 | 2518.9751 | 3418.6697 | 4668.9089 | 6412.0551 | 8849.7027 | 12267.6883 | 17071.7594 | 23838.4694 | 33387.8334 | 46887.0901 | 0 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2442.1476 | 3237.2113 | 4328.5903 | 5833.4678 | 7916.9895 | 10812.3058 | 14849.1013 | 20494.23 | 28409.6353 | 39534.9511 | 55205.3658 | 77319.8784 | 108581.5919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 1082.5469 | 1434.9801 | 1918.7629 | 2585.8399 | 3509.4163 | 4792.8424 | 6582.2594 | 9084.613 | 12593.3272 | 17524.9196 | 24471.2481 | 34274.0945 | 48131.6813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 45.5936 | 60.4371 | 80.8125 | 108.9078 | 147.8061 | 201.8601 | 277.225 | 382.6166 | 530.3931 | 738.097 | 1030.6555 | 1443.522 | 2027.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 1054.5544 | 1397.8743 | 1869.1474 | 2518.9751 | 3418.6697 | 4668.9089 | 6412.0551 | 8849.7027 | 12267.6883 | 17071.7594 | 23838.4694 | 33387.8334 | 46887.0901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 148.4956 | 196.8397 | 263.2014 | 354.706 | 481.3952 | 657.4459 | 902.9046 | 1246.1586 | 1727.4575 | 2403.9361 | 3356.781 | 4701.4614 | 6602.3404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 110.5616 | 146.556 | 195.9652 | 264.0945 | 358.4203 | 489.4979 | 672.2529 | 927.8209 | 1286.1694 | 1789.838 | 2499.2737 | 3500.4485 | 4915.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety | New | Replaced | FB | Safety | 28 | 0 | 0 | 0 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1483.079 | 1775.1526 | 2353.07 | 3146.3734 | 4240.2415 | 5754.7154 | 7859.2682 | 10793.5412 | 14896.8825 | 20650.4464 | 28737.2359 | 40127.775 | 56202.4113 | 78925.9816
| Environment | New | Replaced | BC | Environment | 27 | 0 | 0 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 148.4956 | 196.8397 | 263.2014 | 354.706 | 481.3952 | 657.4459 | 902.9046 | 1246.1586 | 1727.4575 | 2403.9361 | 3356.781 | 4701.4614 | 6602.3404 | 0 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2040.3304 | 2442.1476 | 3237.2113 | 4328.5903 | 5833.4678 | 7916.9895 | 10812.3058 | 14849.1013 | 20494.23 | 28409.6353 | 39534.9511 | 55205.3658 | 77319.8784 | 108581.5919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 1082.5469 | 1434.9801 | 1918.7629 | 2585.8399 | 3509.4163 | 4792.8424 | 6582.2594 | 9084.613 | 12593.3272 | 17524.9196 | 24471.2481 | 34274.0945 | 48131.6813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 45.5936 | 60.4371 | 80.8125 | 108.9078 | 147.8061 | 201.8601 | 277.225 | 382.6166 | 530.3931 | 738.097 | 1030.6555 | 1443.522 | 2027.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 881.0439 | 1054.5544 | 1397.8743 | 1869.1474 | 2518.9751 | 3418.6697 | 4668.9089 | 6412.0551 | 8849.7027 | 12267.6883 | 17071.7594 | 23838.4694 | 33387.8334 | 46887.0901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 124.063 | 148.4956 | 196.8397 | 263.2014 | 354.706 | 481.3952 | 657.4459 | 902.9046 | 1246.1586 | 1727.4575 | 2403.9361 | 3356.781 | 4701.4614 | 6602.3404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 110.5616 | 146.556 | 195.9652 | 264.0945 | 358.4203 | 489.4979 | 672.2529 | 927.8209 | 1286.1694 | 1789.838 | 2499.2737 | 3500.4485 | 4915.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environment | New | Replaced | FB | Environment | 28 | 0 | 0 | 0 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 208.8393 | 249.9676 | 331.3468 | 443.0556 | 597.0884 | 810.3485 | 1106.7005 | 1519.8893 | 2097.7001 | 2907.8865 | 4046.6253 | 5650.5807 | 7914.1259 | 11113.9387
| NP | New | Replaced | BC | NP | 27 | 0 | 0 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 92.3704 | 110.5616 | 146.556 | 195.9652 | 264.0945 | 358.4203 | 489.4979 | 672.2529 | 927.8209 | 1286.1694 | 1789.838 | 2499.2737 | 3500.4485 | 4915.738
| NP | New | Replaced | FB | NP | 28 | 0 | 0 | 0 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 7.1027 | 8.5015 | 11.2693 | 15.0686 | 20.3073 | 27.5604 | 37.6395 | 51.6923 | 71.344 | 98.8989 | 137.6281 | 192.1796 | 269.1641 | 377.9916
| Opex | New | Replaced | BC | Financial | 27 | 0 | 0 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 904.4308 | 1082.5469 | 1434.9801 | 1918.7629 | 2585.8399 | 3509.4163 | 4792.8424 | 6582.2594 | 9084.613 | 12593.3272 | 17524.9196 | 24471.2481 | 34274.0945 | 48131.6813
| Opex | New | Replaced | FB | Financial | 28 | 0 | 0 | 0 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 1797.2219 | 2151.162 | 2851.4927 | 3812.8322 | 5138.4014 | 6973.6683 | 9524.0033 | 13079.8085 | 18052.3116 | 25024.5845 | 34824.3022 | 48627.5634 | 68107.0985 | 95643.9318
| Capex | New | Replaced | BC | Financial | 27 | 0 | 0 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 38.0919 | 45.5936 | 60.4371 | 80.8125 | 108.9078 | 147.8061 | 201.8601 | 277.225 | 382.6166 | 530.3931 | 738.097 | 1030.6555 | 1443.522 | 2027.1619
| Capex | New | Replaced | FB | Financial | 28 | 0 | 0 | 0 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 82.5098 | 98.7591 | 130.911 | 175.0458 | 235.9022 | 320.1586 | 437.2436 | 600.4894 | 828.7753 | 1148.8698 | 1598.7714 | 2232.4743 | 3126.7728 | 4390.9791
Summary
Base case risk
Risk before replacement
| Base case |  | All |  | Safety |  | 8510.1076 | 9383.6998 | 10369.2056 | 11483.62 | 12748.7718 | 14199.5693 | 15930.9908 | 17960.9269 | 20384.6609 | 23281.5036 | 26751.4767 | 30956.5965 | 36118.8141 | 42545.8705 | 50669.2409 | 61100.0832 | 74712.073 | 91179.7547 | 112425.4667 | 133649.2318 | 146850.3256 | 160393.8761 | 174969.2593 | 191029.9066 | 206005.4004 | 215791.4086 | 226810.834 | 238048.3786 | 245791.5455 | 250035.4652
| Base case |  | All |  | Environment |  | 652.9639 | 716.6175 | 788.6616 | 870.4699 | 963.9408 | 1072.6339 | 1208.359 | 1371.3224 | 1573.0169 | 1822.3333 | 2130.4801 | 2516.9236 | 3009.0125 | 3645.5192 | 4481.8671 | 5597.8707 | 7109.2379 | 9091.4653 | 11744.3821 | 14348.8155 | 15771.0148 | 17181.7916 | 18714.3008 | 20420.5825 | 21903.1277 | 22573.8647 | 23327.1513 | 24104.3141 | 24666.6836 | 24973.848
| Base case |  | All |  | NP |  | 137218.1496 | 149513.302 | 163065.1597 | 178016.851 | 194530.2945 | 212789.3697 | 233005.4425 | 255827.5608 | 281379.9061 | 309832.9615 | 341570.4619 | 377036.8343 | 416748.6183 | 461308.3773 | 511421.7197 | 567918.2283 | 631777.3339 | 701790.9 | 780449.6849 | 869864.2472 | 971252.9987 | 1087051.0433 | 1193334.6121 | 1293812.7533 | 1405384.7391 | 1529385.5898 | 1667328.6533 | 1818778.554 | 1978716.5031 | 2149242.3093
| Base case |  | All |  | Financial |  | 237149.6237 | 262811.1396 | 291623.2868 | 324017.289 | 360491.5031 | 401635.8889 | 448217.3767 | 501013.6204 | 560976.0535 | 629167.1287 | 706853.1489 | 795569.7086 | 897153.071 | 1013815.7644 | 1148247.148 | 1303749.1911 | 1484422.4914 | 1641380.8548 | 1805616.2795 | 1986417.7867 | 2173924.2772 | 2383222.7029 | 2609993.412 | 2858167.8479 | 3133587.2654 | 3434963.9124 | 3774595.3903 | 4117366.1503 | 4341662.4484 | 4457423.8495
Option 2 risk
Residual risk of assets not replaced
| Option 2 |  | Not replaced |  | Safety |  | 8510.1076 | 9383.6998 | 7405.6193 | 909.8996 | 970.6479 | 1056.1132 | 1232.7532 | 1481.9155 | 1864.8787 | 2417.5723 | 3184.1167 | 4257.6943 | 5774.8565 | 7936.5758 | 11039.8129 | 15524.9538 | 22047.242 | 31584.5399 | 44953.4586 | 60164.625 | 66869.8391 | 72913.9835 | 79842.923 | 88273.9832 | 94668.0226 | 94794.4013 | 94931.9486 | 95081.6719 | 95244.6707 | 95422.1451
| Option 2 |  | Not replaced |  | Environment |  | 652.9639 | 716.6175 | 565.5621 | 116.9125 | 124.6122 | 135.7241 | 159.6065 | 193.6236 | 246.4053 | 323.0064 | 429.6347 | 579.4113 | 791.5675 | 1094.4111 | 1529.7744 | 2159.6982 | 3076.4968 | 4417.9423 | 6299.0616 | 8439.5082 | 9381.3372 | 10229.817 | 11202.7274 | 12387.0759 | 13283.9652 | 13297.0618 | 13311.3261 | 13326.8644 | 13343.7926 | 13362.2375
| Option 2 |  | Not replaced |  | NP |  | 137218.1496 | 149513.302 | 14257.4503 | 988.7732 | 1063.3224 | 1144.2636 | 1234.3455 | 1334.1838 | 1444.2742 | 1566.445 | 1703.1583 | 1857.807 | 2035.1635 | 2242.0572 | 2488.4009 | 2788.748 | 3164.658 | 3648.2917 | 4287.5126 | 5051.3876 | 5411.4484 | 5718.9775 | 6048.1145 | 6393.8129 | 6769.1888 | 7176.8176 | 7619.5809 | 8100.5681 | 8623.1435 | 9190.9714
| Option 2 |  | Not replaced |  | Financial |  | 237149.6237 | 262811.1396 | 211266.2339 | 8413.5664 | 9043.8983 | 9755.4429 | 10658.2353 | 11720.5065 | 13035.2704 | 14662.4134 | 16677.038 | 19225.2817 | 22519.4432 | 26870.0499 | 32733.9948 | 40786.9627 | 52032.6308 | 67967.6271 | 89988.4364 | 114351.4688 | 125796.3905 | 136080.1406 | 147596.7574 | 160582.4255 | 171260.3439 | 174404.4926 | 177820.1779 | 181531.3255 | 185563.9956 | 189946.575
Risk of replaced assets
| Option 2 |  | Replaced |  | Safety |  | 0 | 0 | 881.0439 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2829.707 | 3750.9443 | 5015.5208 | 6759.2167 | 9173.3851 | 12528.177 | 17205.5963 | 23746.5852 | 32918.1348 | 45808.9953 | 63966.2444 | 89590.2447 | 125813.0717
| Option 2 |  | Replaced |  | Environment |  | 0 | 0 | 124.063 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 398.4632 | 528.1866 | 706.257 | 951.7943 | 1291.7438 | 1764.1464 | 2422.7939 | 3343.8587 | 4635.344 | 6450.5614 | 9007.3617 | 12615.5872 | 17716.2791
| Option 2 |  | Replaced |  | NP |  | 0 | 0 | 92.3704 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 119.0632 | 157.8253 | 211.0338 | 284.4018 | 385.9807 | 527.1375 | 723.9453 | 999.1649 | 1385.0684 | 1927.4662 | 2691.4533 | 3769.6126 | 5293.7297
| Option 2 |  | Replaced |  | Financial |  | 0 | 0 | 942.5227 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 3378.0617 | 4477.8209 | 5987.4534 | 8069.0513 | 10951.0493 | 14955.9494 | 20539.7823 | 28348.3166 | 39297.1746 | 54686.0902 | 76361.9413 | 106951.4878 | 150193.7542
Option 3 risk
Residual risk of assets not replaced
| Option 3 |  | Not replaced |  | Safety | 33 | 8510.1076 | 9383.6998 | 10369.2056 | 11483.62 | 12748.7718 | 14199.5693 | 15930.9908 | 17960.9269 | 1864.8787 | 2417.5723 | 3184.1167 | 4257.6943 | 5774.8565 | 7936.5758 | 11039.8129 | 15524.9538 | 22047.242 | 31584.5399 | 44953.4586 | 60164.625 | 66869.8391 | 72913.9835 | 79842.923 | 88273.9832 | 94668.0226 | 94794.4013 | 94931.9486 | 95081.6719 | 95244.6707 | 95422.1451
| Option 3 |  | Not replaced |  | Environment | 33 | 652.9639 | 716.6175 | 788.6616 | 870.4699 | 963.9408 | 1072.6339 | 1208.359 | 1371.3224 | 246.4053 | 323.0064 | 429.6347 | 579.4113 | 791.5675 | 1094.4111 | 1529.7744 | 2159.6982 | 3076.4968 | 4417.9423 | 6299.0616 | 8439.5082 | 9381.3372 | 10229.817 | 11202.7274 | 12387.0759 | 13283.9652 | 13297.0618 | 13311.3261 | 13326.8644 | 13343.7926 | 13362.2375
| Option 3 |  | Not replaced |  | NP | 33 | 137218.1496 | 149513.302 | 163065.1597 | 178016.851 | 194530.2945 | 212789.3697 | 233005.4425 | 255827.5608 | 1444.2742 | 1566.445 | 1703.1583 | 1857.807 | 2035.1635 | 2242.0572 | 2488.4009 | 2788.748 | 3164.658 | 3648.2917 | 4287.5126 | 5051.3876 | 5411.4484 | 5718.9775 | 6048.1145 | 6393.8129 | 6769.1888 | 7176.8176 | 7619.5809 | 8100.5681 | 8623.1435 | 9190.9714
| Option 3 |  | Not replaced |  | Financial | 33 | 237149.6237 | 262811.1396 | 291623.2868 | 324017.289 | 360491.5031 | 401635.8889 | 448217.3767 | 501013.6204 | 13035.2704 | 14662.4134 | 16677.038 | 19225.2817 | 22519.4432 | 26870.0499 | 32733.9948 | 40786.9627 | 52032.6308 | 67967.6271 | 89988.4364 | 114351.4688 | 125796.3905 | 136080.1406 | 147596.7574 | 160582.4255 | 171260.3439 | 174404.4926 | 177820.1779 | 181531.3255 | 185563.9956 | 189946.575
Risk of replaced assets
| Option 3 |  | Replaced |  | Safety | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2364.1229 | 2829.707 | 3750.9443 | 5015.5208 | 6759.2167 | 9173.3851 | 12528.177 | 17205.5963 | 23746.5852 | 32918.1348 | 45808.9953 | 63966.2444 | 89590.2447 | 125813.0717
| Option 3 |  | Replaced |  | Environment | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 332.9023 | 398.4632 | 528.1866 | 706.257 | 951.7943 | 1291.7438 | 1764.1464 | 2422.7939 | 3343.8587 | 4635.344 | 6450.5614 | 9007.3617 | 12615.5872 | 17716.2791
| Option 3 |  | Replaced |  | NP | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 99.4732 | 119.0632 | 157.8253 | 211.0338 | 284.4018 | 385.9807 | 527.1375 | 723.9453 | 999.1649 | 1385.0684 | 1927.4662 | 2691.4533 | 3769.6126 | 5293.7297
| Option 3 |  | Replaced |  | Financial | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 2822.2544 | 3378.0617 | 4477.8209 | 5987.4534 | 8069.0513 | 10951.0493 | 14955.9494 | 20539.7823 | 28348.3166 | 39297.1746 | 54686.0902 | 76361.9413 | 106951.4878 | 150193.7542

## Misc_calcs
CitiPower
Relay replacements
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR | bar: 2021-06-30 to 2025-06-30
| Option | First year | Option included
| Option 2 | 1 | TRUE
| Option 3 | 7 | TRUE
| Option 4 | Not used | FALSE
| Option 5 | Not used | FALSE
| First year | 1
FLAGS | bar: 2021-06-30 to 2025-06-30
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
CitiPower
Relay replacements
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | TRUE | Not used |  | TRUE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
CitiPower
| Reliability in worst-served areas | per MWh | 0
| Network resilience | per MWh | 0
| Enabling solar exports | per MWh | 4220.9954
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.54769
| Customer value of time - business | per minute customer time | 0.54769
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | FALSE | June | 6 | CY | Not used |  | 2026 | No | 2026-27 | 2026-27
| Powercor | PA | PAL: |  | Capex | TRUE | December | 12 | FY |  |  | 2025 | Yes | 2025-26 | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25 | 2024-25
2023
2022
2021
2020