## Ratings
Substation (MVA) | Summer (N) | Winter (N) | Summer (N-1) | Winter (N-1)
AW | 130 | 130 | 100.5 | 102
BD | 123 | 123 | 123.7 | 125.1
EPN | 66 | 66 | 38 | 38
FE | 61 | 61 | 47.6 | 47.6
FF | 54 | 54 | 38 | 38
FT | 60 | 60 | 34.8 | 34.8
FW | 90 | 90 | 70.3 | 77.2
NH | 93 | 93 | 75.2 | 76
ST | 95.2 | 95.2 | 79.7 | 89.3
TH | 90 | 90 | 47.6 | 47.6
TMA | 66 | 66 | 38 | 39.6
KTS66 East | 490 | 490 | 327 | 327 | <-- B125
KTS66 West | 331 | 331 | 331 | 331 | <-- B34
TTS66 East | 325 | 356 | 325 | 356 | <-- B12
TTS66 West | 500 | 575 | 340 | 397 | <-- B34
SMTS66 | 530 | 588 | 265 | 294
BLTS66 | 505 | 575 | 339 | 386 | <-- Includes ATS East
WMTS66 | 879 | 879 | 586 | 586
BTS22 | 262 | 262 | 175 | 175
BLTS22 | 180 | 190 | 90 | 95
Sub-transmission Loop (MVA) | Summer | Winter | Line | Length (km)
BLTS-FW-BLTS | 86.3 | 86.3 | BLTS-FW1 | 2.98
| 65.7 | 86.3 | BLTS-FW2 | 2.92
| 65.7 | 86.3 | Overall (N-1)
| 130 | 170 | Overall (N)
BLTS-BKN-TH-BLTS | 100.6 | 125.7 | BLTS-BKN (BLTS-TH1) | 3.28
| 100.6 | 125.7 | BLTS-TH (BLTS-TH2) | 2.91
| 100.6 | 125.7 | Overall (N-1)
| 150 | 160 | Overall (N)
BTS-FF-BTS | 11.4 | 13 | BTS-FF181 | 6.09
| 13.1 | 13.7 | BTS-FF188 | 4.34
| 13.1 | 13.7 | BTS-FF184 | 4.32
| 24.5 | 26.7 | Overall (N-1)
| 37.6 | 40.4 | Overall (N)
KTS-AW-NDT-PV-KTS | 117 | 126 | KTS-AW (KTS-AW1) | 4.83
| 117 | 126 | KTS-NDT (KTS-AW2) | 5.67
| 100.6 | 105.7 | KTS-PV | 11.52
| 166 | 182 | Overall (N-1)
| 266 | 291 | Overall (N)
KTS-TMA-MAT-KTS | 101.7 | 105.7 | KTS-TMA | 5.62
| 97.1 | 114 | KTS-MAT | 10.03
| 97.1 | 105.7 | Overall (N-1)
| 160 | 170 | Overall (N)
SMTS-ST-SSS-SMTS | 117.2 | 121.7 | SMTS-SSS | 17.83
| 117.2 | 126.3 | SMTS-ST | 11.6
| 117.2 | 126.3 | Overall (N-1)
| 190 | 200 | Overall (N)
TTS-BD-BMS-COO-VCO-TTS | 101.7 | 104.6 | TTS-BMS | 9.1
| 117.2 | 126.3 | TTS-BD | 8.45
| 101.7 | 112.6 | TTS-COO | 10.3
| 196 | 217 | Overall (N-1)
| 293 | 324 | Overall (N)
TTS-NEI-NH-WT-TTS | 117.2 | 126.3 | TTS-NH | 9.6
| 117.2 | 126.3 | TTS-WT | 7.9
| 117.2 | 126.3 | Overall (N-1)
| 180 | 190 | Overall (N)
TTS-PTN-EPN-EP-TTS | 81.2 | 107.5 | TTS-PTN | 4.9
| 78.9 | 93.2 | TTS-EP | 8.7
| 78.9 | 93.2 | Overall (N-1)
| 140 | 170 | Overall (N)
WMTS-FE-WGT-WMTS | 84.6 | 91.5 | WMTS-FE1 | 3.07
| 83.5 | 91.5 | WMTS-FE2 | 6.34
| 83.5 | 91.5 | Overall (N-1)
| 160 | 175 | Overall (N)
WMTS-FT | 52 | 64 | WMTS-FT1 | 1.45
| 65.2 | 76.6 | WMTS-FT2 | 1.3
| 52 | 64 | Overall (N-1)
| 101 | 120 | Overall (N)

## Historical
Summer (MVA) | N-1 Rating | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Winter (MVA) | Rating | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
AW | 100.5 |  | 70.9 | 66.5 | 67.3 | 69.8 | 71.4 | AW | 102 |  | 58.9 | 53.9 | 56.8 | 52.4 | 56.4
BD | 123.7 |  | 72.4 | 64 | 68 | 70.5 | 71.2 | BD | 125.1 |  | 65.4 | 66.5 | 69.7 | 70.7 | 75.1
EPN | 38 |  | 20.6 | 9.9 | 10.8 | 11 | 25.4 | EPN | 38 |  | 8.5 | 7.7 | 8.2 | 22.2 | 23.9
FE | 47.6 |  | 32 | 26.6 | 26.8 | 18.7 | 31.1 | FE | 47.6 |  | 30.3 | 30.5 | 18.3 | 27.2 | 33
FF | 38 |  | 24.2 | 20.9 | 21.8 | 23.3 | 24.1 | FF | 38 |  | 20.8 | 20.1 | 21 | 19.5 | 21.2
FT | 34.8 |  | 37.6 | 32.3 | 32.3 | 34.1 | 37.9 | FT | 34.8 |  | 29.3 | 32.2 | 31.3 | 32.5 | 35.9
FW | 70.3 |  | 44.6 | 39 | 37.2 | 37.3 | 42.1 | FW | 77.2 |  | 39 | 38.1 | 38 | 36.6 | 39.9
NH | 75.2 |  | 65.6 | 57.9 | 58.6 | 60.6 | 50.8 | NH | 76 |  | 49.7 | 49.1 | 51.7 | 39.2 | 42.3
ST | 79.7 |  | 76.4 | 65.6 | 71.1 | 70.4 | 71.9 | ST | 89.3 |  | 69.7 | 73.1 | 75.4 | 69.6 | 74.2
TH | 47.6 |  | 26.4 | 26.6 | 28.1 | 26.2 | 20.8 | TH | 47.6 |  | 26.4 | 27.9 | 29 | 28.5 | 30
TMA | 38 |  | 20.6 | 22 | 24.9 | 24.8 | 25.2 | TMA | 39.6 |  | 16.7 | 23.1 | 24.5 | 24.3 | 26
BLTS-FW-BLTS | 65.7 |  | 44.6 | 39 | 37.2 | 37.3 | 42.1 | BLTS-FW-BLTS | 86.3 |  | 39 | 38.1 | 38 | 36.6 | 39.9
BLTS-BKN-TH-BLTS | 100.6 |  | 26.4 | 26.6 | 28.1 | 26.2 | 20.8 | BLTS-BKN-TH-BLTS | 125.7 |  | 26.4 | 27.9 | 29 | 28.5 | 30
BTS-FF-BTS | 24.5 |  | 24.2 | 20.9 | 21.8 | 23.3 | 24.1 | BTS-FF-BTS | 26.7 |  | 20.8 | 20.1 | 21 | 19.5 | 21.2
KTS-AW-NDT-PV-KTS | 166 |  | 112.7 | 100.3 | 103.3 | 108.6 | 108.6 | KTS-AW-NDT-PV-KTS | 182 |  | 90.4 | 84.6 | 87.7 | 83.6 | 87.6
KTS-TMA-MAT-KTS | 97.1 |  | 49.7196 | 42.4332 | 49.5201 | 51.2523 | 51.6523 | KTS-TMA-MAT-KTS | 105.7 |  | 33.8 | 42.5 | 48.2 | 48.3 | 50
SMTS-ST-SSS-SMTS | 117.2 |  | 76.4 | 65.6 | 71.1 | 70.4 | 71.9 | SMTS-ST-SSS-SMTS | 126.3 |  | 69.7 | 73.1 | 75.4 | 69.6 | 74.2
TTS-BD-BMS-COO-VCO-TTS | 196 |  | 169.6 | 156.8 | 169.1 | 166.5 | 167.2 | TTS-BD-BMS-COO-VCO-TTS | 217 |  | 152.2 | 156.3 | 162.1 | 164.6 | 169
TTS-NEI-NH-WT-TTS | 117.2 |  | 125 | 131.3 | 127.5 | 115.8 | 116.8 | TTS-NEI-NH-WT-TTS | 126.3 |  | 95 | 98 | 97.3 | 96 | 100.7
TTS-PTN-EPN-EP-TTS | 78.9 |  | 48.4 | 54.4 | 59.1 | 60.3 | 74.7 | TTS-PTN-EPN-EP-TTS | 93.2 |  | 50.2 | 52.5 | 49.3 | 64.1 | 65.8
WMTS-FE-WGT-WMTS | 83.5 |  | 32 | 26.6 | 26.8 | 18.7 | 31.1 | WMTS-FE-WGT-WMTS | 91.5 |  | 30.3 | 30.5 | 18.3 | 27.2 | 33
WMTS-FT | 52 |  | 37.6 | 32.3 | 32.3 | 34.1 | 37.9 | WMTS-FT | 64 |  | 29.3 | 32.2 | 31.3 | 32.5 | 35.9
KTS66 East | 327 |  | 323.3 | 284.4 | 291.9 | 279.6 | 279.6 | KTS66 East | 327
KTS66 West | 331 |  | 242.6 | 184.6 | 197.4 | 209.1 | 209.1 | KTS66 West | 331
TTS66 East | 325 |  | 219 | 208.2 | 217.3 | 212.3 | 212.3 | TTS66 East | 356
TTS66 West | 340 |  | 260 | 229.1 | 247.7 | 214.4 | 214.4 | TTS66 West | 397
SMTS66 | 265 |  | 381.7 | 297.3 | 333.4 | 356.6 | 356.6 | SMTS66 | 294
BLTS66 | 339 |  | 236 | 240 | 266 | 270 | 270 | BLTS66 | 386
WMTS66 | 586 |  | 301 | 253 | 250 | 296 | 296 | WMTS66 | 586
BTS22 | 175 |  | 112.6 | 93.3 | 99.2 | 93.3 | 93.3 | BTS22 | 175
BLTS22 | 90 |  | 63.3 | 60.6 | 55 | 42.49 | 42.49 | BLTS22 | 95

## Summer 10PoE
Option 1 - Do Nothing Weighted Scenario | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
AW | 100.5 | 75.0106 | 76.7808 | 78.9809 | 80.9275 | 80.9005 | 82.0787 | 83.4746 | 84.89 | 86.2529 | 87.3103
BD | 123.7 | 75.4032 | 78.7292 | 81.7286 | 83.7367 | 84.3173 | 85.3908 | 86.6886 | 88.0007 | 89.2516 | 90.1771
EPN | 38 | 29.3322 | 30.2624 | 37.9604 | 43.2999 | 46.7852 | 50.5124 | 51.2296 | 51.9538 | 52.6402 | 53.1331
FE | 47.6 | 40.8301 | 40.9525 | 41.4808 | 42.4625 | 43.4807 | 44.7586 | 46.1907 | 47.6692 | 49.1527 | 50.4899
FF | 38 | 26.0897 | 26.8494 | 29.1651 | 31.4533 | 33.1303 | 34.4837 | 35.4216 | 36.3808 | 37.1898 | 37.8739
FT | 34.8 | 41.9843 | 44.1996 | 47.0021 | 49.3729 | 51.2732 | 52.6147 | 54.1238 | 55.6734 | 57.2156 | 58.5773
FW | 70.3 | 46.0772 | 53.5152 | 55.3107 | 56.4474 | 58.8549 | 58.8793 | 59.0464 | 59.21 | 59.3199 | 59.2051
NH | 75.2 | 54.8148 | 50.4837 | 51.6187 | 52.3678 | 52.7453 | 53.5721 | 54.5435 | 55.5296 | 56.483 | 57.237
ST | 79.7 | 80.658 | 85.3108 | 90.573 | 94.9504 | 98.1886 | 100.5649 | 103.2501 | 105.9993 | 108.7212 | 111.0872
TH | 47.6 | 21.8353 | 19.4092 | 21.4883 | 22.3299 | 23.0239 | 22.2887 | 22.3963 | 22.5031 | 22.5901 | 22.5925
TMA | 38 | 22.4876 | 22.6361 | 22.7642 | 22.3243 | 22.6392 | 23.0151 | 23.4539 | 23.8999 | 24.3328 | 24.681
BLTS-FW-BLTS | 65.7 | 46.0772 | 53.5152 | 55.3107 | 56.4474 | 58.8549 | 58.8793 | 59.0464 | 59.21 | 59.3199 | 59.2051
BLTS-BKN-TH-BLTS | 100.6 | 38.6963 | 42.9107 | 46.2079 | 50.6866 | 54.8115 | 59.7599 | 64.4997 | 72.231 | 82.4089 | 92.5023
BTS-FF-BTS | 24.5 | 26.7905 | 27.6134 | 30.2273 | 32.7249 | 34.7225 | 36.1021 | 37.1903 | 38.2099 | 39.2047 | 39.9881
KTS-AW-NDT-PV-KTS | 166 | 120.9917 | 125.3947 | 132.777 | 142.7822 | 149.5215 | 157.7291 | 168.1563 | 179.2535 | 188.9127 | 198.1034
KTS-TMA-MAT-KTS | 97.1 | 48.0254 | 66.54 | 74.7776 | 83.896 | 102.3981 | 125.9682 | 151.9448 | 168.6884 | 177.2538 | 185.8193
SMTS-ST-SSS-SMTS | 117.2 | 80.658 | 86.7734 | 95.2894 | 102.1242 | 107.9435 | 115.0301 | 123.0178 | 130.3831 | 136.18 | 141.621
TTS-BD-BMS-COO-VCO-TTS | 196 | 185.0247 | 189.6026 | 193.9504 | 197.1108 | 198.5542 | 201.4063 | 204.7982 | 208.237 | 211.5444 | 214.0949
TTS-NEI-NH-WT-TTS | 117.2 | 130.7148 | 132.4337 | 136.4437 | 139.0678 | 140.4453 | 145.6721 | 161.6935 | 163.5196 | 167.0305 | 170.342
TTS-PTN-EPN-EP-TTS | 78.9 | 76.9856 | 83.7834 | 85.5037 | 87.7702 | 88.7776 | 90.0935 | 93.3819 | 94.7971 | 96.151 | 97.1714
WMTS-FE-WGT-WMTS | 83.5 | 47.8301 | 47.9525 | 48.4808 | 49.4625 | 50.4807 | 51.7586 | 53.1907 | 54.6692 | 56.1527 | 57.4899
WMTS-FT | 52 | 41.9843 | 44.1996 | 47.0021 | 49.3729 | 51.2732 | 52.6147 | 54.1238 | 55.6734 | 57.2156 | 58.5773
TTS-NEI-NH-NEL-WT-PTN-EPN-TTS | 277.3 | 207.7005 | 216.2171 | 221.9474 | 226.838 | 229.2229 | 235.7655 | 255.0754 | 258.3167 | 263.1815 | 267.5134
KTS66 East | 327 | 333.0012 | 352.3495 | 366.0736 | 385.6603 | 415.2343 | 450.0716 | 467.551 | 522.4514 | 545.6216 | 568.7918
KTS66 West | 331 | 239.6157 | 243.4613 | 247.9078 | 252.613 | 258.9101 | 268.0901 | 280.5114 | 296.426 | 316.2681 | 336.1103
TTS66 East | 325 | 243.1531 | 260.9901 | 267.0038 | 273.2769 | 278.4772 | 287.889 | 314.6423 | 320.9569 | 328.9549 | 336.9529
TTS66 West | 340 | 261.5381 | 267.1583 | 270.969 | 275.098 | 281.7717 | 289.9131 | 299.0283 | 308.4549 | 317.1845 | 325.9142
SMTS66 | 265 | 406.1196 | 426.6353 | 448.0841 | 471.0813 | 492.7832 | 516.7137 | 542.7781 | 568.3944 | 593.2449 | 618.0954
BLTS66 | 339 | 381.9611 | 399.7015 | 414.0196 | 443.7567 | 450.4876 | 460.7712 | 470.5034 | 483.7279 | 499.8188 | 515.9098
WMTS66 | 586 | 387.0925 | 401.9691 | 415.9898 | 431.9239 | 447.7444 | 463.8186 | 480.2412 | 498.5379 | 519.7383 | 540.9387
BTS22 | 175 | 98.4179 | 101.9027 | 106.7071 | 111.9986 | 116.3377 | 121.5403 | 127.5319 | 133.6906 | 139.6818 | 145.673
BLTS22 | 90 | 79.2 | 84.5 | 83.9 | 83.1 | 82.7 | 82.7 | 82.9 | 83.1 | 83.6 | 84.1
AW Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EPN Block Load | 0 | 0 | 0 | 0.81 | 1.86 | 1.86 | 2.01 | 3.9 | 3.9 | 3.9 | 3.9
NH Block Load | 0 | 0 | 0 | 0.675 | 1.55 | 1.55 | 2.35 | 3.9 | 3.44 | 3.2975 | 3.155
TH Block Load | 0 | 13 | 18 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0
BLTS-BKN-TH-BLTS Block Load | 0 | 16.8611 | 23.5015 | 24.7196 | 28.3567 | 31.7876 | 37.4712 | 42.1034 | 49.7279 | 59.8188 | 69.9098
KTS-AW-NDT-PV-KTS Block Load | 0 | 4 | 6.65 | 11.4938 | 19.0246 | 25.3607 | 31.8823 | 40.2922 | 49.7706 | 57.4882 | 65.2057
KTS-TMA-MAT-KTS Block Load | 0 | 0 | 18.5848 | 26.6471 | 35.9322 | 53.5787 | 76.0879 | 100.855 | 116.3482 | 123.7445 | 131.1409
SMTS-ST-SSS-SMTS Block Load | 0 | 0 | 1.4625 | 4.7164 | 7.1738 | 9.7549 | 14.4653 | 19.7677 | 24.3837 | 27.4588 | 30.5338
TTS-BD-BMS-COO-VCO-TTS Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TTS-NEI-NH-WT-TTS Block Load | 0 | 6 | 11.25 | 13.425 | 14.3 | 14.3 | 17.6 | 31.65 | 31.19 | 32.5475 | 33.905
TTS-PTN-EPN-EP-TTS Block Load | 0 | 0 | 0 | 0.81 | 1.86 | 1.86 | 2.01 | 3.9 | 3.9 | 3.9 | 3.9
KTS66 East Block Load | 0 | 4 | 25.2348 | 38.1409 | 54.9569 | 78.9394 | 107.9703 | 141.1472 | 166.1188 | 181.2327 | 196.3466
KTS66 West Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 6.716 | 13.8845 | 24.797 | 35.7095
TTS66 East Block Load | 0 | 6 | 11.25 | 14.235 | 16.16 | 16.16 | 19.61 | 35.55 | 35.09 | 36.4475 | 37.805
TTS66 West Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SMTS66 Block Load | 0 | 0 | 1.4625 | 4.7164 | 7.1738 | 9.7549 | 14.4653 | 19.7677 | 24.3837 | 27.4588 | 30.5338
BLTS66 Block Load | 0 | 16.8611 | 23.5015 | 24.7196 | 28.3567 | 31.7876 | 37.4712 | 42.1034 | 49.7279 | 59.8188 | 69.9098
WMTS66 Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BTS22 Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLTS22 Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023 TCPR (TSDF) |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
KTS66 East |  | 338.0012 | 381.1147 | 398.9328 | 417.7034 | 462.2948 | 502.1013 | 554.4038 | 583.3326 | 603.3889
KTS66 West |  | 239.6157 | 243.4613 | 247.9078 | 252.613 | 258.9101 | 266.2901 | 273.7954 | 282.5415 | 291.4711
TTS66 East |  | 237.1531 | 249.7401 | 252.7688 | 257.1169 | 262.3172 | 268.279 | 279.0923 | 285.8669 | 292.5074
TTS66 West |  | 261.5381 | 267.1583 | 270.969 | 275.098 | 281.7717 | 289.9131 | 299.0283 | 308.4549 | 317.1845
SMTS66 |  | 406.1196 | 425.1728 | 443.3677 | 463.9074 | 483.0283 | 502.2484 | 523.0104 | 544.0106 | 565.7861
BLTS66 |  | 365.1 | 406.2 | 419.3 | 445.4 | 448.7 | 453.3 | 458.4 | 464 | 486
WMTS66 |  | 387.0925 | 401.9691 | 415.9898 | 431.9239 | 447.7444 | 463.8186 | 480.2412 | 498.5379 | 519.7383
BTS22 |  | 98.4179 | 101.9027 | 106.7071 | 111.9986 | 116.3377 | 121.5403 | 127.5319 | 133.6906 | 139.6818
BLTS22 |  | 79.2 | 84.5 | 83.9 | 83.1 | 82.7 | 82.7 | 82.9 | 83.1 | 83.6
KTS East Backout |  | 9 | 54 | 71 | 87 | 126 | 160 | 228 | 227 | 239
BLTS66 Backout |  | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 46

## Summer 50PoE
Option 1 - Do Nothing Weighted Scenario | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
AW | 100.5 | 70.846 | 72.6829 | 74.7467 | 76.7723 | 77.2171 | 78.3208 | 79.6018 | 81.0607 | 81.8521 | 83.1056
BD | 123.7 | 71.7808 | 75.1083 | 77.9443 | 80.0467 | 80.5843 | 81.5683 | 82.7324 | 84.0761 | 85.2768 | 86.4267
EPN | 38 | 27.3263 | 28.2531 | 35.8883 | 41.247 | 44.6901 | 47.8291 | 48.4636 | 49.202 | 49.8551 | 50.4772
FE | 47.6 | 38.8491 | 39.0533 | 39.5444 | 40.5717 | 41.5309 | 42.7244 | 44.046 | 45.5014 | 46.9167 | 48.3406
FF | 38 | 24.5107 | 25.2801 | 27.4508 | 29.6725 | 31.247 | 32.5067 | 33.361 | 34.3018 | 35.0672 | 35.8217
FT | 34.8 | 39.5309 | 41.7028 | 44.3279 | 46.6696 | 48.4523 | 49.6931 | 51.0705 | 52.5893 | 54.049 | 55.5061
FW | 70.3 | 43.9763 | 51.2375 | 52.9048 | 54.1155 | 56.403 | 56.3986 | 56.5082 | 56.727 | 56.8368 | 56.9021
NH | 75.2 | 51.0817 | 47.4177 | 48.2122 | 49.0248 | 49.3669 | 50.1133 | 50.9738 | 51.9494 | 52.8429 | 53.7105
ST | 79.7 | 77.495 | 82.1532 | 87.1991 | 91.6347 | 94.7408 | 96.9857 | 99.4867 | 102.2509 | 104.8863 | 107.5035
TH | 47.6 | 21.4936 | 19.1517 | 21.1975 | 22.874 | 22.765 | 22.8122 | 22.9083 | 23.0517 | 22.3475 | 22.4182
TMA | 38 | 21.2578 | 21.4464 | 21.5627 | 21.9532 | 22.2582 | 22.6161 | 23.0258 | 22.6778 | 23.0893 | 23.4903
BLTS-FW-BLTS | 65.7 | 43.9763 | 51.2375 | 52.9048 | 54.1155 | 56.403 | 56.3986 | 56.5082 | 56.727 | 56.8368 | 56.9021
BLTS-BKN-TH-BLTS | 100.6 | 38.3546 | 42.6532 | 45.9172 | 51.2306 | 54.5525 | 60.2834 | 65.0118 | 72.7796 | 82.1663 | 92.3279
BTS-FF-BTS | 24.5 | 25.1645 | 25.985 | 28.3387 | 30.7995 | 32.4992 | 33.8565 | 34.9515 | 35.7733 | 36.8774 | 37.718
KTS-AW-NDT-PV-KTS | 166 | 112.2589 | 116.8162 | 124.0168 | 134.1364 | 141.2945 | 149.3547 | 159.566 | 171.1087 | 180.1528 | 189.6332
KTS-TMA-MAT-KTS | 97.1 | 46.2115 | 64.7907 | 73.0194 | 82.9541 | 101.4712 | 125.0159 | 150.9251 | 166.8325 | 175.3608 | 183.8892
SMTS-ST-SSS-SMTS | 117.2 | 77.495 | 83.6157 | 91.9155 | 98.8085 | 104.4957 | 111.4509 | 119.2543 | 126.6346 | 132.345 | 138.0373
TTS-BD-BMS-COO-VCO-TTS | 196 | 175.1101 | 179.7955 | 183.8387 | 187.2633 | 188.5823 | 191.1772 | 194.2041 | 197.6639 | 200.8002 | 203.8292
TTS-NEI-NH-WT-TTS | 117.2 | 121.9817 | 124.3677 | 127.8372 | 130.4248 | 131.6669 | 136.7133 | 152.7238 | 154.2394 | 157.5904 | 160.9155
TTS-PTN-EPN-EP-TTS | 78.9 | 72.4149 | 78.9368 | 80.5741 | 82.955 | 83.884 | 85.0912 | 88.2231 | 89.6495 | 90.9322 | 92.165
WMTS-FE-WGT-WMTS | 83.5 | 45.8491 | 46.0533 | 46.5444 | 47.5717 | 48.5309 | 49.7244 | 51.046 | 52.5014 | 53.9167 | 55.3406
WMTS-FT | 52 | 39.5309 | 41.7028 | 44.3279 | 46.6696 | 48.4523 | 49.6931 | 51.0705 | 52.5893 | 54.049 | 55.5061
KTS66 East | 327 | 296.401 | 317.3742 | 331.4247 | 350.8272 | 381.2657 | 415.911 | 433.3604 | 487.9079 | 510.6184 | 533.3289
KTS66 West | 331 | 220.9674 | 224.574 | 228.6654 | 232.6945 | 238.9714 | 248.1462 | 260.3612 | 275.2082 | 294.1795 | 313.1509
TTS66 East | 325 | 228.6587 | 246.3045 | 252.6209 | 258.5747 | 263.5151 | 272.5864 | 298.533 | 304.5163 | 312.0228 | 319.5293
TTS66 West | 340 | 251.6291 | 257.2424 | 260.9677 | 264.8724 | 271.6854 | 279.6039 | 288.1517 | 296.9643 | 305.3732 | 313.782
SMTS66 | 265 | 378.5413 | 396.9546 | 417.2294 | 439.1487 | 459.4486 | 483.0627 | 507.2661 | 531.1734 | 555.4238 | 579.6741
BLTS66 | 339 | 365.3611 | 383.1015 | 397.4196 | 426.7567 | 433.8876 | 443.9712 | 453.4034 | 466.2279 | 481.6188 | 497.0098
WMTS66 | 586 | 358.6826 | 371.5597 | 383.9657 | 398.8348 | 413.8509 | 429.3763 | 444.9018 | 462.0974 | 482.3907 | 502.6839
BTS22 | 175 | 91.9364 | 95.3676 | 100.0986 | 105.1394 | 109.5752 | 114.4906 | 120.2178 | 126.0164 | 131.8554 | 137.6944
BLTS22 | 90 | 71.2 | 76.8 | 76.3 | 75.6 | 75.3 | 75.2 | 75.4 | 75.7 | 76.2 | 76.7
AW Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EPN Block Load | 0 | 0 | 0 | 0.81 | 1.86 | 1.86 | 2.01 | 3.9 | 3.9 | 3.9 | 3.9
NH Block Load | 0 | 0 | 0 | 0.675 | 1.55 | 1.55 | 2.35 | 3.9 | 3.44 | 3.2975 | 3.155
TH Block Load | 0 | 13 | 18 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0
BLTS-BKN-TH-BLTS Block Load | 0 | 16.8611 | 23.5015 | 24.7196 | 28.3567 | 31.7876 | 37.4712 | 42.1034 | 49.7279 | 59.8188 | 69.9098
KTS-AW-NDT-PV-KTS Block Load | 0 | 4 | 6.65 | 11.4938 | 19.0246 | 25.3607 | 31.8823 | 40.2922 | 49.7706 | 57.4882 | 65.2057
KTS-TMA-MAT-KTS Block Load | 0 | 0 | 18.5848 | 26.6471 | 35.9322 | 53.5787 | 76.0879 | 100.855 | 116.3482 | 123.7445 | 131.1409
SMTS-ST-SSS-SMTS Block Load | 0 | 0 | 1.4625 | 4.7164 | 7.1738 | 9.7549 | 14.4653 | 19.7677 | 24.3837 | 27.4588 | 30.5338
TTS-BD-BMS-COO-VCO-TTS Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TTS-NEI-NH-WT-TTS Block Load | 0 | 6 | 11.25 | 13.425 | 14.3 | 14.3 | 17.6 | 31.65 | 31.19 | 32.5475 | 33.905
TTS-PTN-EPN-EP-TTS Block Load | 0 | 0 | 0 | 0.81 | 1.86 | 1.86 | 2.01 | 3.9 | 3.9 | 3.9 | 3.9
KTS66 East Block Load | 0 | 4 | 25.2348 | 38.1409 | 54.9569 | 78.9394 | 107.9703 | 141.1472 | 166.1188 | 181.2327 | 196.3466
KTS66 West Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 6.716 | 13.8845 | 24.797 | 35.7095
TTS66 East Block Load | 0 | 6 | 11.25 | 14.235 | 16.16 | 16.16 | 19.61 | 35.55 | 35.09 | 36.4475 | 37.805
TTS66 West Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SMTS66 Block Load | 0 | 0 | 1.4625 | 4.7164 | 7.1738 | 9.7549 | 14.4653 | 19.7677 | 24.3837 | 27.4588 | 30.5338
BLTS66 Block Load | 0 | 16.8611 | 23.5015 | 24.7196 | 28.3567 | 31.7876 | 37.4712 | 42.1034 | 49.7279 | 59.8188 | 69.9098
WMTS66 Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BTS22 Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLTS22 Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023 TCPR (TSDF) |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
KTS66 East |  | 301.401 | 346.1394 | 364.2839 | 382.8703 | 428.3263 | 467.9407 | 520.2132 | 548.7891 | 568.3857
KTS66 West |  | 220.9674 | 224.574 | 228.6654 | 232.6945 | 238.9714 | 246.3462 | 253.6452 | 261.3237 | 269.3825
TTS66 East |  | 222.6587 | 235.0545 | 238.3859 | 242.4147 | 247.3551 | 252.9764 | 262.983 | 269.4263 | 275.5753
TTS66 West |  | 251.6291 | 257.2424 | 260.9677 | 264.8724 | 271.6854 | 279.6039 | 288.1517 | 296.9643 | 305.3732
SMTS66 |  | 378.5413 | 395.4921 | 412.513 | 431.9749 | 449.6937 | 468.5974 | 487.4984 | 506.7897 | 527.965
BLTS66 |  | 348.5 | 389.6 | 402.7 | 428.4 | 432.1 | 436.5 | 441.3 | 446.5 | 467.8
WMTS66 |  | 358.6826 | 371.5597 | 383.9657 | 398.8348 | 413.8509 | 429.3763 | 444.9018 | 462.0974 | 482.3907
BTS22 |  | 91.9364 | 95.3676 | 100.0986 | 105.1394 | 109.5752 | 114.4906 | 120.2178 | 126.0164 | 131.8554
BLTS22 |  | 71.2 | 76.8 | 76.3 | 75.6 | 75.3 | 75.2 | 75.4 | 75.7 | 76.2
KTS East Backout |  | 9 | 54 | 71 | 87 | 126 | 160 | 228 | 227 | 239
BLTS66 Backout |  | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 46

## Winter 10PoE
Option 1 - Do Nothing Weighted Scenario | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
AW | 102 | 58.2921 | 61.3894 | 64.506 | 66.9041 | 67.8726 | 69.0564 | 70.1655 | 71.2563 | 72.3564 | 73.4581
BD | 125.1 | 78.3879 | 83.1142 | 87.0781 | 89.5606 | 90.6427 | 91.7146 | 92.7645 | 93.7892 | 94.8314 | 95.878
EPN | 38 | 26.2334 | 27.808 | 35.9876 | 41.6435 | 45.4607 | 50.9818 | 51.6988 | 52.3946 | 53.0867 | 53.7706
FE | 47.6 | 40.1549 | 41.1681 | 42.3127 | 43.6672 | 45.076 | 46.5397 | 47.2256 | 48.5772 | 49.96 | 51.3703
FF | 38 | 22.9652 | 24.3885 | 27.242 | 29.9594 | 31.7636 | 33.4056 | 34.4289 | 35.4551 | 36.3459 | 37.2408
FT | 34.8 | 38.7946 | 41.7452 | 45.371 | 48.3261 | 51.0362 | 53.344 | 55.0771 | 56.7917 | 58.4701 | 60.12
FW | 77.2 | 43.1081 | 51.4752 | 54.2036 | 55.9828 | 59.0962 | 59.4967 | 59.7121 | 59.8882 | 60.0156 | 60.1445
NH | 76 | 44.6574 | 41.7498 | 43.6415 | 44.7235 | 45.5375 | 46.4867 | 47.3769 | 48.2565 | 49.1435 | 50.0327
ST | 89.3 | 82.0015 | 87.8877 | 93.9279 | 98.6593 | 102.3469 | 104.7825 | 107.0161 | 109.2417 | 111.4937 | 113.763
TH | 47.6 | 31.2981 | 29.4629 | 31.6919 | 33.3998 | 33.4477 | 33.5177 | 33.5747 | 33.6179 | 33.6629 | 33.7051
TMA | 39.6 | 22.5063 | 23.0467 | 23.4233 | 23.8764 | 24.3039 | 24.6643 | 25.0212 | 25.3735 | 25.7328 | 26.0955
BLTS-FW-BLTS | 86.3 | 43.1081 | 51.4752 | 54.2036 | 55.9828 | 59.0962 | 59.4967 | 59.7121 | 59.8882 | 60.0156 | 60.1445
BLTS-BKN-TH-BLTS | 125.7 | 45.63 | 49.4391 | 52.7036 | 57.503 | 60.4671 | 65.3682 | 69.3626 | 75.8866 | 84.509 | 93.1284
BTS-FF-BTS | 26.7 | 23.3034 | 24.7164 | 27.7721 | 30.7278 | 33.008 | 34.7547 | 35.896 | 37.0951 | 38.1435 | 39.2094
KTS-AW-NDT-PV-KTS | 182 | 95.6064 | 101.9478 | 110.2403 | 120.0511 | 127.3356 | 134.8869 | 143.8114 | 153.6048 | 161.8977 | 170.1778
KTS-TMA-MAT-KTS | 105.7 | 49.6195 | 66.2424 | 73.7882 | 82.4995 | 98.3138 | 118.064 | 139.9356 | 153.857 | 160.9015 | 167.946
SMTS-ST-SSS-SMTS | 126.3 | 82.0015 | 89.1308 | 97.9368 | 104.757 | 110.6385 | 117.078 | 123.8186 | 129.9679 | 134.8336 | 139.7168
TTS-BD-BMS-COO-VCO-TTS | 217 | 177.4421 | 185.1824 | 191.5535 | 195.5579 | 197.8863 | 200.416 | 202.6239 | 204.4973 | 206.8821 | 209.28
TTS-NEI-NH-WT-TTS | 126.3 | 103.5574 | 106.3123 | 111.3527 | 114.4785 | 116.5925 | 121.6467 | 135.7794 | 137.668 | 141.1089 | 144.652
TTS-PTN-EPN-EP-TTS | 93.2 | 69.1478 | 77.225 | 80.1619 | 83.0112 | 84.8497 | 86.5155 | 89.4941 | 90.7769 | 92.0854 | 93.2753
WMTS-FE-WGT-WMTS | 91.5 | 47.1549 | 48.1681 | 49.3127 | 50.6672 | 52.076 | 53.5397 | 54.2256 | 55.5772 | 56.96 | 58.3703
WMTS-FT | 64 | 38.7946 | 41.7452 | 45.371 | 48.3261 | 51.0362 | 53.344 | 55.0771 | 56.7917 | 58.4701 | 60.12
TTS-NEI-NH-NEL-WT-PTN-EPN-TTS | 327 | 172.7051 | 183.5372 | 191.5146 | 197.4897 | 201.4421 | 208.1622 | 225.2735 | 228.4449 | 233.1943 | 237.9273
KTS66 East | 327 | 275.3585 | 308.0401 | 329.6422 | 354.9992 | 390.7917 | 427.9998 | 450.9483 | 501.1298 | 523.3921 | 545.6545
KTS66 West | 331 | 236.5945 | 246.4037 | 255.9936 | 265.9689 | 276.4409 | 288.9972 | 301.903 | 316.9769 | 336.368 | 355.759
TTS66 East | 356 | 230.6306 | 251.8596 | 261.2421 | 268.5134 | 274.1576 | 282.3568 | 305.6925 | 310.9342 | 317.6879 | 324.4415
TTS66 West | 397 | 279.6699 | 294.0779 | 304.3219 | 312.9499 | 321.2213 | 328.3483 | 336.8186 | 344.7462 | 352.6143 | 360.4823
SMTS66 | 294 | 384.957 | 412.4923 | 442.3047 | 468.4182 | 493.9067 | 520.634 | 547.8703 | 576.2661 | 603.7031 | 631.1402
BLTS66 | 386 | 377.9319 | 397.3762 | 414.7117 | 446.3032 | 452.9194 | 461.4505 | 469.3879 | 480.0687 | 492.646 | 505.2233
WMTS66 | 586 | 308.1958 | 324.6594 | 349.4144 | 371.6405 | 393.962 | 416.4805 | 437.1593 | 456.1677 | 482.1051 | 508.0424
BTS22 | 175 | 90.7058 | 94.4027 | 98.4511 | 102.777 | 106.5336 | 111.5869 | 117.7987 | 124.5068 | 131.3033 | 138.0998
BLTS22 | 95 | 78.9 | 85.1 | 86.1 | 87 | 88.3 | 89.7 | 90.5 | 91.5 | 91.5 | 91.5
AW Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EPN Block Load | 0 | 0 | 0 | 0.6885 | 1.581 | 1.581 | 1.7085 | 3.315 | 3.315 | 3.315 | 3.315
NH Block Load | 0 | 0 | 0 | 0.57375 | 1.3175 | 1.3175 | 1.9975 | 3.315 | 2.924 | 2.8029 | 2.6818
TH Block Load | 0 | 11.05 | 15.3 | 15.3 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0
BLTS-BKN-TH-BLTS Block Load | 0 | 14.3319 | 19.9762 | 21.0117 | 24.1032 | 27.0194 | 31.8505 | 35.7879 | 42.2687 | 50.846 | 59.4233
KTS-AW-NDT-PV-KTS Block Load | 0 | 3.4 | 5.6525 | 9.7697 | 16.1709 | 21.5566 | 27.1 | 34.2483 | 42.305 | 48.8649 | 55.4248
KTS-TMA-MAT-KTS Block Load | 0 | 0 | 15.7971 | 22.65 | 30.5424 | 45.5419 | 64.6747 | 85.7267 | 98.8959 | 105.1829 | 111.4698
SMTS-ST-SSS-SMTS Block Load | 0 | 0 | 1.2431 | 4.009 | 6.0978 | 8.2917 | 12.2955 | 16.8025 | 20.7262 | 23.34 | 25.9537
TTS-BD-BMS-COO-VCO-TTS Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TTS-NEI-NH-WT-TTS Block Load | 0 | 5.1 | 9.5625 | 11.4113 | 12.155 | 12.155 | 14.96 | 26.9025 | 26.5115 | 27.6654 | 28.8193
TTS-PTN-EPN-EP-TTS Block Load | 0 | 0 | 0 | 0.6885 | 1.581 | 1.581 | 1.7085 | 3.315 | 3.315 | 3.315 | 3.315
KTS66 East Block Load | 0 | 3.4 | 21.4496 | 32.4197 | 46.7134 | 67.0985 | 91.7747 | 119.9751 | 141.201 | 154.0478 | 166.8946
KTS66 West Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 1.53 | 5.7086 | 11.8018 | 21.0775 | 30.3531
TTS66 East Block Load | 0 | 5.1 | 9.5625 | 12.0997 | 13.736 | 13.736 | 16.6685 | 30.2175 | 29.8265 | 30.9804 | 32.1342
TTS66 West Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SMTS66 Block Load | 0 | 0 | 1.2431 | 4.009 | 6.0978 | 8.2917 | 12.2955 | 16.8025 | 20.7262 | 23.34 | 25.9537
BLTS66 Block Load | 0 | 14.3319 | 19.9762 | 21.0117 | 24.1032 | 27.0194 | 31.8505 | 35.7879 | 42.2687 | 50.846 | 59.4233
WMTS66 Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BTS22 Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLTS22 Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023 TCPR (TSDF) |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
KTS66 East |  | 279.6085 | 332.4905 | 357.5725 | 382.2359 | 430.7932 | 472.2251 | 524.7732 | 552.8788 | 572.4943
KTS66 West |  | 236.5945 | 246.4037 | 255.9936 | 265.9689 | 276.4409 | 287.4672 | 296.1944 | 305.1751 | 315.2905
TTS66 East |  | 225.5306 | 242.2971 | 249.1424 | 254.7774 | 260.4216 | 265.6883 | 275.475 | 281.1077 | 286.7075
TTS66 West |  | 279.6699 | 294.0779 | 304.3219 | 312.9499 | 321.2213 | 328.3483 | 336.8186 | 344.7462 | 352.6143
SMTS66 |  | 384.957 | 411.2492 | 438.2957 | 462.3204 | 485.6151 | 508.3385 | 531.0678 | 555.5399 | 580.3632
BLTS66 |  | 363.6 | 402.9 | 419.2 | 447.7 | 451.4 | 455.1 | 459.1 | 463.3 | 480.9
WMTS66 |  | 308.1958 | 324.6594 | 349.4144 | 371.6405 | 393.962 | 416.4805 | 437.1593 | 456.1677 | 482.1051
BTS22 |  | 90.7058 | 94.4027 | 98.4511 | 102.777 | 106.5336 | 111.5869 | 117.7987 | 124.5068 | 131.3033
BLTS22 |  | 78.9 | 85.1 | 86.1 | 87 | 88.3 | 89.7 | 90.5 | 91.5 | 91.5
KTS East Backout |  | 7.65 | 45.9 | 60.35 | 73.95 | 107.1 | 136 | 193.8 | 192.95 | 203.15
BLTS66 Backout |  | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 39.1

## Winter 50PoE
Option 1 - Do Nothing Weighted Scenario | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
AW | 102 | 55.6329 | 58.7729 | 61.7663 | 64.1297 | 65.099 | 66.2265 | 67.3014 | 68.3802 | 69.4589 | 70.5392
BD | 125.1 | 74.8055 | 79.4407 | 83.3388 | 85.806 | 86.898 | 87.9154 | 88.9371 | 89.963 | 90.9933 | 92.0278
EPN | 38 | 25.0337 | 26.5808 | 34.7423 | 40.3846 | 44.1847 | 48.8818 | 49.578 | 50.2697 | 50.9511 | 51.6246
FE | 47.6 | 38.287 | 39.3211 | 40.4715 | 41.8137 | 43.1911 | 44.589 | 45.9306 | 46.6198 | 47.958 | 49.3233
FF | 38 | 21.9245 | 23.3229 | 26.0878 | 28.7214 | 30.4699 | 32.0406 | 33.0275 | 34.0281 | 34.8946 | 35.7653
FT | 34.8 | 37.0047 | 40.2539 | 43.4399 | 46.313 | 48.9369 | 51.1411 | 52.8101 | 54.4791 | 56.107 | 57.7083
FW | 77.2 | 41.1192 | 49.2176 | 51.9196 | 53.6928 | 56.6775 | 57.0547 | 57.2712 | 57.4679 | 57.6357 | 57.7796
NH | 76 | 42.7237 | 39.9126 | 41.7786 | 42.9676 | 43.7834 | 44.5879 | 45.4491 | 46.3147 | 47.1813 | 48.0503
ST | 89.3 | 78.4801 | 84.0416 | 89.936 | 94.5664 | 98.1622 | 100.4868 | 102.6465 | 104.8319 | 107.0288 | 109.2432
TH | 47.6 | 29.8576 | 28.1665 | 30.3255 | 31.987 | 32.0538 | 32.1173 | 32.1777 | 32.2351 | 32.2894 | 32.3408
TMA | 39.6 | 21.4864 | 22.0397 | 22.4309 | 22.8898 | 23.3147 | 23.658 | 24.0047 | 24.3547 | 24.708 | 25.0646
BLTS-FW-BLTS | 86.3 | 41.1192 | 49.2176 | 51.9196 | 53.6928 | 56.6775 | 57.0547 | 57.2712 | 57.4679 | 57.6357 | 57.7796
BLTS-BKN-TH-BLTS | 125.7 | 44.1895 | 48.1427 | 51.3372 | 56.0901 | 59.0732 | 63.9678 | 67.9656 | 74.5038 | 83.1354 | 91.7641
BTS-FF-BTS | 26.7 | 22.202 | 23.6034 | 26.5483 | 29.4065 | 31.5527 | 33.3062 | 34.3223 | 35.4001 | 36.4177 | 37.5055
KTS-AW-NDT-PV-KTS | 182 | 91.4105 | 97.8061 | 105.9768 | 115.7488 | 123.0191 | 130.4768 | 139.3469 | 149.1208 | 157.3803 | 165.6278
KTS-TMA-MAT-KTS | 105.7 | 46.1078 | 62.7701 | 70.3396 | 79.0303 | 94.8602 | 114.7455 | 136.5566 | 150.4917 | 157.5514 | 164.611
SMTS-ST-SSS-SMTS | 126.3 | 78.4801 | 85.2847 | 93.945 | 100.6641 | 106.4538 | 112.7823 | 119.4491 | 125.558 | 130.3688 | 135.1969
TTS-BD-BMS-COO-VCO-TTS | 217 | 169.3581 | 177.0352 | 183.3731 | 187.4086 | 189.7616 | 192.1666 | 194.5132 | 196.6818 | 199.0406 | 201.412
TTS-NEI-NH-WT-TTS | 126.3 | 98.6237 | 101.4751 | 106.3899 | 109.6226 | 111.7384 | 116.6479 | 130.7516 | 132.6262 | 136.0466 | 139.4695
TTS-PTN-EPN-EP-TTS | 93.2 | 66.7629 | 74.8049 | 77.7208 | 80.6323 | 82.4401 | 84.0428 | 86.9636 | 88.2734 | 89.5675 | 90.8507
WMTS-FE-WGT-WMTS | 91.5 | 45.287 | 46.3211 | 47.4715 | 48.8137 | 50.1911 | 51.589 | 52.9306 | 53.6198 | 54.958 | 56.3233
WMTS-FT | 64 | 37.0047 | 40.2539 | 43.4399 | 46.313 | 48.9369 | 51.1411 | 52.8101 | 54.4791 | 56.107 | 57.7083
KTS66 East | 327 | 256.1095 | 288.5425 | 309.8989 | 334.7535 | 370.4011 | 408.5355 | 430.819 | 480.9061 | 503.1363 | 503.2801
KTS66 West | 331 | 222.8596 | 232.1204 | 241.223 | 250.6791 | 260.5454 | 273.2282 | 285.6319 | 300.516 | 319.8465 | 320.7155
TTS66 East | 356 | 212.6358 | 233.8864 | 243.2307 | 250.5468 | 256.1157 | 264.8649 | 288.1931 | 293.5775 | 300.543 | 302.7574
TTS66 West | 397 | 255.9265 | 269.6768 | 279.4973 | 287.4994 | 295.6949 | 304.2634 | 311.9589 | 319.869 | 327.7927 | 327.8441
SMTS66 | 294 | 354.3266 | 380.0087 | 407.9282 | 432.8481 | 457.2366 | 483.835 | 510.0569 | 537.4751 | 563.8885 | 564.2451
BLTS66 | 386 | 359.8319 | 378.8762 | 396.0117 | 427.3032 | 434.1194 | 443.5505 | 451.2879 | 462.0687 | 474.646 | 474.646
WMTS66 | 586 | 296.1239 | 310.4937 | 332.9912 | 353.6674 | 374.0785 | 395.2128 | 415.4377 | 433.7065 | 459.8102 | 459.9541
BTS22 | 175 | 88.7397 | 94.6789 | 101.6457 | 108.5344 | 113.814 | 119.9309 | 125.7432 | 131.6404 | 137.5105 | 146.1392
BLTS22 | 95 | 73.9 | 80 | 80.8 | 81.7 | 82.9 | 84.5 | 85.2 | 86.3 | 86.3 | 87.3878
AW Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EPN Block Load | 0 | 0 | 0 | 0.6885 | 1.581 | 1.581 | 1.7085 | 3.315 | 3.315 | 3.315 | 3.315
NH Block Load | 0 | 0 | 0 | 0.57375 | 1.3175 | 1.3175 | 1.9975 | 3.315 | 2.924 | 2.8029 | 2.6818
TH Block Load | 0 | 11.05 | 15.3 | 15.3 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0
BLTS-BKN-TH-BLTS Block Load | 0 | 14.3319 | 19.9762 | 21.0117 | 24.1032 | 27.0194 | 31.8505 | 35.7879 | 42.2687 | 50.846 | 59.4233
KTS-AW-NDT-PV-KTS Block Load | 0 | 3.4 | 5.6525 | 9.7697 | 16.1709 | 21.5566 | 27.1 | 34.2483 | 42.305 | 48.8649 | 55.4248
KTS-TMA-MAT-KTS Block Load | 0 | 0 | 15.7971 | 22.65 | 30.5424 | 45.5419 | 64.6747 | 85.7267 | 98.8959 | 105.1829 | 111.4698
SMTS-ST-SSS-SMTS Block Load | 0 | 0 | 1.2431 | 4.009 | 6.0978 | 8.2917 | 12.2955 | 16.8025 | 20.7262 | 23.34 | 25.9537
TTS-BD-BMS-COO-VCO-TTS Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TTS-NEI-NH-WT-TTS Block Load | 0 | 5.1 | 9.5625 | 11.4113 | 12.155 | 12.155 | 14.96 | 26.9025 | 26.5115 | 27.6654 | 28.8193
TTS-PTN-EPN-EP-TTS Block Load | 0 | 0 | 0 | 0.6885 | 1.581 | 1.581 | 1.7085 | 3.315 | 3.315 | 3.315 | 3.315
KTS66 East Block Load | 0 | 3.4 | 21.4496 | 32.4197 | 46.7134 | 67.0985 | 91.7747 | 119.9751 | 141.201 | 154.0478 | 166.8946
KTS66 West Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 1.53 | 5.7086 | 11.8018 | 21.0775 | 30.3531
TTS66 East Block Load | 0 | 5.1 | 9.5625 | 12.0997 | 13.736 | 13.736 | 16.6685 | 30.2175 | 29.8265 | 30.9804 | 32.1342
TTS66 West Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SMTS66 Block Load | 0 | 0 | 1.2431 | 4.009 | 6.0978 | 8.2917 | 12.2955 | 16.8025 | 20.7262 | 23.34 | 25.9537
BLTS66 Block Load | 0 | 14.3319 | 19.9762 | 21.0117 | 24.1032 | 27.0194 | 31.8505 | 35.7879 | 42.2687 | 50.846 | 59.4233
WMTS66 Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BTS22 Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLTS22 Block Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023 TCPR (TSDF) |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
KTS66 East |  | 260.3595 | 312.9929 | 337.8292 | 361.9901 | 410.4026 | 452.7608 | 504.644 | 532.6551 | 552.2385
KTS66 West |  | 222.8596 | 232.1204 | 241.223 | 250.6791 | 260.5454 | 271.6982 | 279.9233 | 288.7141 | 298.7691
TTS66 East |  | 207.5358 | 224.3239 | 231.131 | 236.8108 | 242.3797 | 248.1964 | 257.9756 | 263.751 | 269.5627
TTS66 West |  | 255.9265 | 269.6768 | 279.4973 | 287.4994 | 295.6949 | 304.2634 | 311.9589 | 319.869 | 327.7927
SMTS66 |  | 354.3266 | 378.7655 | 403.9193 | 426.7504 | 448.9449 | 471.5395 | 493.2544 | 516.7489 | 540.5485
BLTS66 |  | 345.5 | 384.4 | 400.5 | 428.7 | 432.6 | 437.2 | 441 | 445.3 | 462.9
WMTS66 |  | 296.1239 | 310.4937 | 332.9912 | 353.6674 | 374.0785 | 395.2128 | 415.4377 | 433.7065 | 459.8102
BTS22 |  | 88.7397 | 94.6789 | 101.6457 | 108.5344 | 113.814 | 119.9309 | 125.7432 | 131.6404 | 137.5105
BLTS22 |  | 73.9 | 80 | 80.8 | 81.7 | 82.9 | 84.5 | 85.2 | 86.3 | 86.3
KTS East Backout |  | 7.65 | 45.9 | 60.35 | 73.95 | 107.1 | 136 | 193.8 | 192.95 | 203.15
BLTS66 Backout |  | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 39.1

## EUE
Results from EUE modellling | [9 empty] | WACC | 5.18% |  | O&M | 1% | [5 empty] | Discount Rate | 5.18%
Expected Unserved Energy for each Option (MWh) – Terminal Station Overload (from NDS TS EUE model) | [28 empty] | Value of Expected Unserved Energy for each Option ($k) – Terminal Station Overload
Option | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | Option | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn
TS | KTS66 East | [6 empty] | BLTS66 | [6 empty] | TTS66 East | [6 empty] | SMTS66 | [6 empty] | TS | KTS66 East | 0 | 0 | 0 | 0 | 0 | 0 | BLTS66 | 0 | 0 | 0 | 0 | 0 | 0 | TTS66 East | 0 | 0 | 0 | 0 | 0 | 0 | SMTS66 | 0 | 0 | 0 | 0 | 0 | 0
Solution Applied | Nil | 4xTX | 4xTX / TMTS | 4xTX |  |  |  | Nil | 2xTX | 2xTX | Nil |  |  |  | Nil | Nil | Nil | Nil |  |  |  | Nil | 1TX | 3TX | 1TX |  |  |  | Solution Applied | Nil | 4xTX | 4xTX / TMTS | 4xTX | 0 | 0 | 0 | Nil | 2xTX | 2xTX | Nil | 0 | 0 | 0 | Nil | Nil | Nil | Nil | 0 | 0 | 0 | Nil | 1TX | 3TX | 1TX | 0 | 0 | 0
2025 | 0.011702 | 0.011702 | 0.011702 | 0.011702 |  |  |  | 2.3182 | 2.3182 | 2.3182 | 2.3182 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 201.946 | 201.946 | 201.946 | 201.946 |  |  |  | 2025 | 0.56631 | [6 empty] | 119.1071 | [6 empty] | 0 | [6 empty] | 9888.4501
2026 | 0.074777 | 0.074777 | 0.074777 | 0.074777 |  |  |  | 13.1625 | 13.1625 | 13.1625 | 13.1625 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 374.7498 | 0 | 0 | 0 |  |  |  | 2026 | 3.6187 | 3.6187 | 3.6187 | 3.6187 | 0 | 0 | 0 | 676.2815 | 676.2815 | 676.2815 | 676.2815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18349.9249 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 0.26858 | 0.26858 | 0.26858 | 0.26858 |  |  |  | 37.3328 | 37.3328 | 37.3328 | 37.3328 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 620.5676 | 0 | 0 | 0 |  |  |  | 2027 | 12.9976 | 12.9976 | 12.9976 | 12.9976 | 0 | 0 | 0 | 1918.1431 | 1918.1431 | 1918.1431 | 1918.1431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30386.5919 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 2.6149 | 2.6149 | 2.6149 | 2.6149 |  |  |  | 143.9154 | 0 | 0 | 143.9154 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 898.1812 | 0 | 0 | 0 |  |  |  | 2028 | 126.5451 | 126.5451 | 126.5451 | 126.5451 | 0 | 0 | 0 | 7394.3035 | 0 | 0 | 7394.3035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43980.1682 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 37.7105 | 37.7105 | 37.7105 | 37.7105 |  |  |  | 179.2958 | 0 | 0 | 179.2958 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 1191.5626 | 0 | 0 | 0 |  |  |  | 2029 | 1824.9259 | 1824.9259 | 1824.9259 | 1824.9259 | 0 | 0 | 0 | 9212.1285 | 0 | 0 | 9212.1285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58345.8236 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 175.9826 | 0 | 0 | 0 |  |  |  | 236.0785 | 0 | 0 | 236.0785 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 1539.774 | 0 | 0 | 0 |  |  |  | 2030 | 8516.327 | 0 | 0 | 0 | 0 | 0 | 0 | 12129.5948 | 0 | 0 | 12129.5948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75396.2735 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 320.1604 | 0 | 0 | 0 |  |  |  | 295.0014 | 0 | 0 | 295.0014 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 1932.4633 | 0.070104 | 0.070104 | 0.070104 |  |  |  | 2031 | 15493.5258 | 0 | 0 | 0 | 0 | 0 | 0 | 15157.0222 | 0 | 0 | 15157.0222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94624.6254 | 3.4327 | 3.4327 | 3.4327 | 0 | 0 | 0
2032 | 813.8649 | 0 | 0 | 0 |  |  |  | 383.8389 | 0 | 0 | 383.8389 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2419.165 | 0.49432 | 0 | 0.49432 |  |  |  | 2032 | 39385.3764 | 0 | 0 | 0 | 0 | 0 | 0 | 19721.4496 | 0 | 0 | 19721.4496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118456.3644 | 24.2047 | 0 | 24.2047 | 0 | 0 | 0
2033 | 1313.2862 | 0 | 0 | 0 |  |  |  | 501.0479 | 0 | 0 | 501.0479 |  |  |  | 1.9256 | 1.9256 | 1.9256 | 1.9256 |  |  |  | 3130.0155 | 2.2371 | 0 | 2.2371 |  |  |  | 2033 | 63553.8775 | 0 | 0 | 0 | 0 | 0 | 0 | 25743.593 | 0 | 0 | 25743.593 | 0 | 0 | 0 | 89.3163 | 89.3163 | 89.3163 | 89.3163 | 0 | 0 | 0 | 153263.7327 | 109.5415 | 0 | 109.5415 | 0 | 0 | 0
2034 | 2245.8441 | 0 | 0 | 0 |  |  |  | 594.4733 | 3.2729 | 3.2729 | 594.4733 |  |  |  | 11.9983 | 11.9983 | 11.9983 | 11.9983 |  |  |  | 4261.9059 | 7.6921 | 0 | 7.6921 |  |  |  | 2034 | 108683.1681 | 0 | 0 | 0 | 0 | 0 | 0 | 30543.7383 | 168.1613 | 168.1613 | 30543.7383 | 0 | 0 | 0 | 556.5185 | 556.5185 | 556.5185 | 556.5185 | 0 | 0 | 0 | 208687.66 | 376.6485 | 0 | 376.6485 | 0 | 0 | 0
Expected Unserved Energy for each Option (MWh) – Zone Substations Overload (from NDS ZSS EUE model) | [28 empty] | Value of Expected Unserved Energy for each Option ($k) – ZSS Overload
Option | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | Option | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn
ZSS | EPN | [6 empty] | FF | [6 empty] | NH | [6 empty] | KTS66 West | [6 empty] | ZSS | EPN | 0 | 0 | 0 | 0 | 0 | 0 | FF | 0 | 0 | 0 | 0 | 0 | 0 | NH | 0 | 0 | 0 | 0 | 0 | 0 | KTS66 West | 0 | 0 | 0 | 0 | 0 | 0
Solution Applied | Nil | 50% | 100% | 50% |  | Nil | Nil | Nil | 50% | 100% | 50% |  | Nil | Nil | Nil | 50% | 100% | 50% |  | Nil | Nil | Nil | 1xTX | 1xTX | 1xTX |  |  |  | Solution Applied | Nil | 0.5 | 1 | 0.5 | 0 | Nil | Nil | Nil | 0.5 | 1 | 0.5 | 0 | Nil | Nil | Nil | 0.5 | 1 | 0.5 | 0 | Nil | Nil | Nil | 1xTX | 1xTX | 1xTX | 0 | 0 | 0 | NH and EPN
2025 | 0 | 0 | 0 | 0 |  | 7.2462 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2025 | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
2026 | 0 | 0 | 0 | 0 |  | 13.5512 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2026 | 0 | 0 | 0 | 0 | 0 | 663.2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 0 | 0 | 0 | 0 |  | 21.7535 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2027 | 0 | 0 | 0 | 0 | 0 | 1064.6256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 0.93584 | 0.46792 | 0 | 0.93584 |  | 31.6262 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2028 | 45.8004 | 22.9002 | 0 | 45.8004 | 0 | 1547.8023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.8004
2029 | 8.1124 | 4.0562 | 0 | 8.1124 |  | 50.0539 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2029 | 397.0235 | 198.5118 | 0 | 397.0235 | 0 | 2449.6648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.0235
2030 | 29.2375 | 14.6187 | 0 | 29.2375 |  | 73.0543 | 0 | 0 | 0 | 0 | 0 |  | 0.00094569 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2030 | 1430.8987 | 715.4493 | 0 | 1430.8987 | 0 | 3575.3147 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1430.8987
2031 | 33.1413 | 16.5707 | 0 | 16.5707 |  | 59.1508 | 0 | 0 | 0 | 0 | 0 |  | 0.019981 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2031 | 1621.9551 | 810.9776 | 0 | 810.9776 | 0 | 2894.8708 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1621.9551
2032 | 37.3003 | 18.6501 | 0 | 18.6501 |  | 63.9749 | 0 | 0 | 0 | 0 | 0 |  | 0.075727 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2032 | 1825.4965 | 912.7482 | 0 | 912.7482 | 0 | 3130.9638 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1825.4965
2033 | 41.4906 | 20.7453 | 0 | 20.7453 |  | 70.2502 | 0 | 0 | 0 | 0 | 0 |  | 0.24058 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6.4462 | 0.041901 | 0.041901 | 0.041901 |  |  |  | 2033 | 2030.5723 | 1015.2862 | 0 | 1015.2862 | 0 | 3438.0842 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311.9534 | 2.0277 | 2.0277 | 2.0277 | 0 | 0 | 0 | 2030.5723
2034 | 45.6353 | 22.8176 | 0 | 22.8176 |  | 76.7775 | 0 | 0 | 0 | 0 | 0 |  | 0.58902 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 104.4949 | 0.67922 | 0.67922 | 0.67922 |  |  |  | 2034 | 2233.4157 | 1116.7079 | 0 | 1116.7079 | 0 | 3757.5298 | 0 | 0 | 0 | 0 | 0 | 0 | 22.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5056.8248 | 32.8694 | 32.8694 | 32.8694 | 0 | 0 | 0 | 2233.4157
Expected Unserved Energy for each Option (MWh) – SubT Overload (from NDS SUBT EUE model) | [28 empty] | Value of Expected Unserved Energy for each Option ($k) – SubT Overload
Option | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | Option | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn
SUBT | KTS-TMA-MAT-KTS | [6 empty] | KTS-AW-NDT-PV-KTS | [20 empty] | SUBT | KTS-TMA-MAT-KTS | 0 | 0 | 0 | 0 | 0 | 0 | KTS-AW-NDT-PV-KTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solution Applied | Nil | 50% | 100% | 50% | Nil | Nil | Nil | Nil | 50% | 100% | 50% |  | Nil | Nil | [14 empty] | Solution Applied | Nil | 0.5 | 1 | 0.5 | Nil | Nil | Nil | Nil | 0.5 | 1 | 0.5 | 0 | Nil | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KTS-TMA-MAT-KTS and KTS-AW-NDT-PV-KTS
2025 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [14 empty] | 2025 | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
2026 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [14 empty] | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [14 empty] | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 76.1604 | 38.0802 | 0 | 38.0802 |  | 0 | 76.1604 | 0 | 0 | 0 | 0 |  | 0 | 0 | [14 empty] | 2028 | 4051.7857 | 2025.8928 | 0 | 2025.8928 | 0 | 0 | 4051.7857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4051.7857
2029 | 1500.002 | 750.001 | 0 | 750.001 |  | 0.0019828 | 1500 | 0 | 0 | 0 | 0 |  | 0 | 0 | [14 empty] | 2029 | 79801.0912 | 39900.5456 | 0 | 39900.5456 | 0 | 0.10549 | 79800.9857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79801.0912
2030 | 1500.3908 | 750.1954 | 0 | 750.1954 |  | 0.39084 | 1500 | 0 | 0 | 0 | 0 |  | 0 | 0 | [14 empty] | 2030 | 79821.7786 | 39910.8893 | 0 | 39910.8893 | 0 | 20.7929 | 79800.9857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79821.7786
2031 | 1506.7852 | 753.3926 | 0 | 753.3926 |  | 6.7852 | 1500 | 7.4465e-05 | 3.7232e-05 | 0 | 3.7232e-05 |  | 7.4465e-05 | 0 | [14 empty] | 2031 | 80161.9608 | 40080.9804 | 0 | 40080.9804 | 0 | 360.9751 | 79800.9857 | 0.0034466 | 0.0017233 | 0 | 0.0017233 | 0 | 0.0034466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80161.9643
2032 | 1527.5555 | 763.7778 | 0 | 763.7778 |  | 27.5555 | 1500 | 0.0021596 | 0.0010798 | 0 | 0.0010798 |  | 0.0021596 | 0 | [14 empty] | 2032 | 81266.9586 | 40633.4793 | 0 | 40633.4793 | 0 | 1465.9729 | 79800.9857 | 0.099959 | 0.04998 | 0 | 0.04998 | 0 | 0.099959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81267.0585
2033 | 1558.7022 | 779.3511 | 0 | 779.3511 |  | 58.7022 | 1500 | 60.8771 | 30.4385 | 0 | 30.4385 |  | 0.0099391 | 60.8671 | [14 empty] | 2033 | 82923.9817 | 41461.9909 | 0 | 41461.9909 | 0 | 3122.996 | 79800.9857 | 2817.7311 | 1408.8656 | 0 | 1408.8656 | 0 | 0.46003 | 2817.2711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85741.7128
2034 | 1616.0544 | 808.0272 | 0 | 808.0272 |  | 116.0544 | 1500 | 491.6978 | 245.8489 | 0 | 245.8489 |  | 0.028758 | 491.669 | [14 empty] | 2034 | 85975.1538 | 42987.5769 | 0 | 42987.5769 | 0 | 6174.1681 | 79800.9857 | 22758.5223 | 11379.2612 | 0 | 11379.2612 | 0 | 1.3311 | 22757.1912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108733.6761
Expected Unserved Energy for each Option (MWh) – SubT Overload (from NDS SUBT EUE model) | [28 empty] | Value of Expected Unserved Energy for each Option ($k) – SubT Overload
Option | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | Option | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn
SUBT | TTS-BD-BMS-COO-VCO-TTS | [6 empty] | SMTS-ST-SSS-SMTS | [6 empty] | BLTS-BKN-TH-BLTS | [13 empty] | SUBT | TTS-BD-BMS-COO-VCO-TTS | 0 | 0 | 0 | 0 | 0 | 0 | SMTS-ST-SSS-SMTS | 0 | 0 | 0 | 0 | 0 | 0 | BLTS-BKN-TH-BLTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solution Applied | Nil | 50% | 100% | 50% |  | Nil | Nil | Nil | 50% | 100% | 50% |  | Nil | Nil | Nil | 100% | 100% | 10% |  | Nil | Nil | [7 empty] | Solution Applied | Nil | 0.5 | 1 | 0.5 | 0 | Nil | Nil | Nil | 0.5 | 1 | 0.5 | 0 | Nil | Nil | Nil | 1 | 1 | 0.1 | 0 | Nil | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [7 empty] | 2025 | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
2026 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [7 empty] | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 8.9912e-05 | 8.9912e-05 | 8.9912e-05 | 8.9912e-05 |  | 8.9912e-05 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [7 empty] | 2027 | 0.0045822 | 0.0045822 | 0.0045822 | 0.0045822 | 0 | 0.0045822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 0.00027504 | 0.00027504 | 0.00027504 | 0.00027504 |  | 0.00027504 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [7 empty] | 2028 | 0.014017 | 0.014017 | 0.014017 | 0.014017 | 0 | 0.014017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 0.00047814 | 0.00047814 | 0.00047814 | 0.00047814 |  | 0.00047814 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [7 empty] | 2029 | 0.024368 | 0.024368 | 0.024368 | 0.024368 | 0 | 0.024368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 0.0011922 | 0.0011922 | 0.0011922 | 0.0011922 |  | 0.0011922 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 39.3974 | 39.3974 | 39.3974 | 39.3974 |  | 0 | 39.3974 | [7 empty] | 2030 | 0.06076 | 0.06076 | 0.06076 | 0.06076 | 0 | 0.06076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2314.9564 | 2314.9564 | 2314.9564 | 2314.9564 | 0 | 0 | 2314.9564 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 0.0026793 | 0.0026793 | 0.0026793 | 0.0026793 |  | 0.0026793 | 0 | 0.0068441 | 0.0068441 | 0.0068441 | 0.0068441 |  | 0.0068441 | 0 | 350.0113 | 0 | 0 | 315.0102 |  | 0 | 350.0113 | [7 empty] | 2031 | 0.13655 | 0.13655 | 0.13655 | 0.13655 | 0 | 0.13655 | 0 | 0.35933 | 0.35933 | 0.35933 | 0.35933 | 0 | 0.35933 | 0 | 20566.3462 | 0 | 0 | 18509.7116 | 0 | 0 | 20566.3462 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2032 | 0.0050842 | 0.0050842 | 0.0050842 | 0.0050842 |  | 0.0050842 | 0 | 0.40087 | 0.40087 | 0 | 0.40087 |  | 0.10495 | 0.29592 | 1500 | 0 | 0 | 1350 |  | 0 | 1500 | [7 empty] | 2032 | 0.25911 | 0.25911 | 0.25911 | 0.25911 | 0 | 0.25911 | 0 | 21.0468 | 21.0468 | 0 | 21.0468 | 0 | 5.5102 | 15.5366 | 88138.6392 | 0 | 0 | 79324.7753 | 0 | 0 | 88138.6392 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2033 | 0.0092347 | 0.0092347 | 0.0092347 | 0.0092347 |  | 0.0092347 | 0 | 49.8892 | 49.8892 | 0 | 49.8892 |  | 0.40882 | 49.4804 | 1500 | 0 | 0 | 1350 |  | 0 | 1500 | [7 empty] | 2033 | 0.47063 | 0.47063 | 0.47063 | 0.47063 | 0 | 0.47063 | 0 | 2619.3013 | 2619.3013 | 0 | 2619.3013 | 0 | 21.4639 | 2597.8374 | 88138.6392 | 0 | 0 | 79324.7753 | 0 | 0 | 88138.6392 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2034 | 0.014908 | 0.014908 | 0.014908 | 0.014908 |  | 0.014908 | 0 | 337.7286 | 337.7286 | 0 | 337.7286 |  | 1.1883 | 336.5403 | 1500 | 0 | 0 | 1350 |  | 0 | 1500 | [7 empty] | 2034 | 0.75977 | 0.75977 | 0.75977 | 0.75977 | 0 | 0.75977 | 0 | 17731.553 | 17731.553 | 0 | 17731.553 | 0 | 62.3882 | 17669.1648 | 88138.6392 | 0 | 0 | 79324.7753 | 0 | 0 | 88138.6392 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Expected Unserved Energy for each Option (MWh) – SubT Overload (from NDS SUBT EUE model) | [28 empty] | Value of Expected Unserved Energy for each Option ($k) – SubT Overload
Option | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | Option | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn | 1 | 2 | 3 | 4 | 5 | Upstream | Connectn
SUBT | TTS-NEI-NH-WT-TTS | [6 empty] | TTS-PTN-EPN-EP-TTS | [6 empty] | BTS-FF-BTS | [13 empty] | SUBT | TTS-NEI-NH-WT-TTS | 0 | 0 | 0 | 0 | 0 | 0 | TTS-PTN-EPN-EP-TTS | 0 | 0 | 0 | 0 | 0 | 0 | BTS-FF-BTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TTS-NEI-NH-WT-TTS and TTS-PTN-EPN-EP-TTS
Solution Applied | Nil | 50% | 100% | 50% |  | Nil | Nil | Nil | 50% | 100% | 50% |  | Nil | Nil | Nil | 100% | 100% | 50% |  | Nil | Nil | [7 empty] | Solution Applied | Nil | 0.5 | 1 | 0.5 | 0 | Nil | Nil | Nil | 0.5 | 1 | 0.5 | 0 | Nil | Nil | Nil | 1 | 1 | 0.5 | 0 | Nil | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 8.8233 | 8.8233 | 8.8233 | 8.8233 |  | 0 | 0 | [7 empty] | 2025 | 0 | [6 empty] | 0 | [6 empty] | 330.3411 | [6 empty] | 0 | [6 empty] | 0
2026 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.0012064 | 0.0012064 | 0.0012064 | 0.0012064 |  | 0.0012064 | 0 | 13.5434 | 13.5434 | 0 | 6.7717 |  | 0 | 0 | [7 empty] | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051235 | 0.051235 | 0.051235 | 0.051235 | 0 | 0.051235 | 0 | 507.0598 | 507.0598 | 0 | 253.5299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051235
2027 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.0032741 | 0.0032741 | 0.0032741 | 0.0032741 |  | 0.0032741 | 0 | 38.04 | 0 | 0 | 19.02 |  | 0.00016465 | 0 | [7 empty] | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13905 | 0.13905 | 0.13905 | 0.13905 | 0 | 0.13905 | 0 | 1424.2071 | 0 | 0 | 712.1036 | 0 | 0.0061643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13905
2028 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.0090223 | 0.0090223 | 0.0090223 | 0.0090223 |  | 0.0090223 | 0 | 84.0149 | 0 | 0 | 42.0075 |  | 0.0014832 | 0 | [7 empty] | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38317 | 0.38317 | 0.38317 | 0.38317 | 0 | 0.38317 | 0 | 3145.4948 | 0 | 0 | 1572.7474 | 0 | 0.055532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38317
2029 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.012869 | 0.012869 | 0.012869 | 0.012869 |  | 0.012869 | 0 | 156.6888 | 0 | 0 | 78.3444 |  | 0.0037185 | 0 | [7 empty] | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0 | 0.54652 | 0 | 5866.3842 | 0 | 0 | 2933.1921 | 0 | 0.13922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54652
2030 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.019612 | 0.019612 | 0.019612 | 0.019612 |  | 0.019612 | 0 | 256.1283 | 0 | 0 | 128.0641 |  | 0.0070086 | 0 | [7 empty] | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83289 | 0.83289 | 0.83289 | 0.83289 | 0 | 0.83289 | 0 | 9589.37 | 0 | 0 | 4794.685 | 0 | 0.2624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83289
2031 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.047587 | 0.023794 | 0.047587 | 0.023794 |  | 0.047587 | 0 | 368.1647 | 0 | 0 | 184.0823 |  | 0.011041 | 0 | [7 empty] | 2031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.021 | 1.0105 | 2.021 | 1.0105 | 0 | 2.021 | 0 | 13783.9808 | 0 | 0 | 6891.9904 | 0 | 0.41336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.021
2032 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.065465 | 0.032732 | 0.065465 | 0.032732 |  | 0.065465 | 0 | 541.1914 | 0 | 0 | 270.5957 |  | 0.017168 | 0 | [7 empty] | 2032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7802 | 1.3901 | 2.7802 | 1.3901 | 0 | 2.7802 | 0 | 20262.0513 | 0 | 0 | 10131.0257 | 0 | 0.64275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7802
2033 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.085367 | 0.042683 | 0.085367 | 0.042683 |  | 0.085367 | 0 | 831.2461 | 0 | 0 | 415.6231 |  | 0.024539 | 0 | [7 empty] | 2033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6255 | 1.8127 | 3.6255 | 1.8127 | 0 | 3.6255 | 0 | 31121.6202 | 0 | 0 | 15560.8101 | 0 | 0.91874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6255
2034 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.10564 | 0.052818 | 0 | 0.052818 |  | 0.10564 | 0 | 1238.5762 | 0 | 0 | 619.2881 |  | 0.034141 | 0 | [7 empty] | 2034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4863 | 2.2431 | 0 | 2.2431 | 0 | 4.4863 | 0 | 46371.9414 | 0 | 0 | 23185.9707 | 0 | 1.2782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4863
Total EUE (MWh) | [8 empty] | Total TS EUE (MWh) | [19 empty] | Total EUE ($k) | [8 empty] | Total TS EUE ($k)
Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | [12 empty] | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7
2025 | 8.8233 | 8.8233 | 8.8233 | 8.8233 | 0 | 7.2462 | 0 |  | 2025 | 204.2759 | 204.2759 | 204.2759 | 204.2759 | 0 | 0 | 0 | [12 empty] | 2025 | 330.3411 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2025 | 10008.1236 | 0 | 0 | 0 | 0 | 0 | 0
2026 | 13.5446 | 13.5446 | 0.0012064 | 6.7729 | 0 | 13.5524 | 0 |  | 2026 | 387.987 | 13.2373 | 13.2373 | 13.2373 | 0 | 0 | 0 | [12 empty] | 2026 | 507.111 | 507.111 | 0.051235 | 253.5811 | 0 | 663.2537 | 0 |  | 2026 | 19029.825 | 679.9002 | 679.9002 | 679.9002 | 0 | 0 | 0
2027 | 38.0434 | 0.003364 | 0.003364 | 19.0234 | 0 | 21.757 | 0 |  | 2027 | 658.169 | 37.6014 | 37.6014 | 37.6014 | 0 | 0 | 0 | [12 empty] | 2027 | 1424.3508 | 0.14363 | 0.14363 | 712.2472 | 0 | 1064.7754 | 0 |  | 2027 | 32317.7326 | 1931.1407 | 1931.1407 | 1931.1407 | 0 | 0 | 0
2028 | 161.1205 | 38.5574 | 0.0092974 | 81.0328 | 0 | 31.637 | 76.1604 |  | 2028 | 1044.7116 | 2.6149 | 2.6149 | 146.5304 | 0 | 0 | 0 | [12 empty] | 2028 | 7243.4781 | 2049.1902 | 0.39719 | 3644.8378 | 0 | 1548.255 | 4051.7857 |  | 2028 | 51501.0168 | 126.5451 | 126.5451 | 7520.8486 | 0 | 0 | 0
2029 | 1664.8165 | 754.0705 | 0.013347 | 836.4711 | 0 | 50.073 | 1500 |  | 2029 | 1408.5689 | 37.7105 | 37.7105 | 217.0063 | 0 | 0 | 0 | [12 empty] | 2029 | 86065.0698 | 40099.6283 | 0.57089 | 43231.3321 | 0 | 2450.4804 | 79800.9857 |  | 2029 | 69382.878 | 1824.9259 | 1824.9259 | 11037.0544 | 0 | 0 | 0
2030 | 1825.1748 | 804.2324 | 39.4182 | 946.9153 | 0 | 73.4739 | 1539.3974 |  | 2030 | 1951.835 | 0 | 0 | 236.0785 | 0 | 0 | 0 | [12 empty] | 2030 | 93157.8974 | 42942.1887 | 2315.85 | 48452.323 | 0 | 3597.299 | 82115.9421 |  | 2030 | 96042.1954 | 0 | 0 | 12129.5948 | 0 | 0 | 0
2031 | 2258.1596 | 769.9966 | 0.057111 | 1269.0891 | 0 | 66.0241 | 1850.0113 |  | 2031 | 2547.6251 | 0.070104 | 0.070104 | 295.0715 | 0 | 0 | 0 | [12 empty] | 2031 | 116136.7633 | 40893.4661 | 2.5169 | 66295.1681 | 0 | 3259.5277 | 100367.332 |  | 2031 | 125275.1733 | 3.4327 | 3.4327 | 15160.4549 | 0 | 0 | 0
2032 | 3606.5208 | 782.8677 | 0.070549 | 2403.4634 | 0 | 91.801 | 3000.2959 |  | 2032 | 3616.8688 | 0.49432 | 0 | 384.3332 | 0 | 0 | 0 | [12 empty] | 2032 | 191517.3318 | 41568.9736 | 3.0393 | 131024.7745 | 0 | 4609.0641 | 167955.1615 |  | 2032 | 177563.1904 | 24.2047 | 0 | 19745.6543 | 0 | 0 | 0
2033 | 4042.2998 | 880.4761 | 0.094602 | 2646.0991 | 0 | 129.7309 | 3110.3475 |  | 2033 | 4952.7215 | 4.2046 | 1.9675 | 505.2526 | 0 | 0 | 0 | [12 empty] | 2033 | 209655.9419 | 46507.7272 | 4.0961 | 141393.3126 | 0 | 6597.026 | 173354.7334 |  | 2033 | 242962.4728 | 200.8854 | 91.344 | 25944.4784 | 0 | 0 | 0
2034 | 5229.8128 | 1414.4901 | 0.014908 | 3383.7781 | 0 | 194.7926 | 3828.2093 |  | 2034 | 7218.7165 | 23.6425 | 15.9504 | 614.8428 | 0 | 0 | 0 | [12 empty] | 2034 | 263214.4715 | 73218.1018 | 0.75977 | 175728.8478 | 0 | 10023.994 | 208365.981 |  | 2034 | 353527.9097 | 1134.1976 | 757.5492 | 31509.7746 | 0 | 0 | 0

## Costs
PV Risk Mitigation Option Costs and Timing |  |  |  | Evaluation Period |  | 20 | years
CAPEX PV RESULTS $m |  |  | Option | Capex Costs | [6 empty] | Option | Opex Costs | [5 empty] | Option | EUE Costs
| Year | Ratio | 1 | 2 | 3 | 4 | 2 | 3 | 4 |  | 1 | 2 | 3 | 4 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 2 | 3 | 4 | 1
|  |  |  | 22.41% | 100% | 14.74%
|  | PV $m | 0 | 47.1672 | 181.3654 | 31.1566 | 207.7592 | 414.7088 | 162.5628 |  | 0 | 7.0442 | 25.8143 | 4.6593 | 30.5184 | 59.2822 | 23.791 | 678.3266 | 205.6164 | 2.1376 | 424.2248 | 14.8736 | 14.5444 | 99.6896 | 836.6989
|  | Sum $m | 0 | 51.591 | 230.208 | 33.923 | 240 | 520 | 190 |  | 0 | 9.3664 | 34.6438 | 6.1908 | 41 | 79 | 32 | 969.2528 | 288.1169 | 2.6578 | 611.0668 | 15.9334 | 15.423 | 135.667 | 1177.6105
0 | 2025 | 1 | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | 0.33034 | 0.33034 | 0.33034 | 0.33034 | 10.0081 | 10.0081 | 10.0081 | 10.0081
1 | 2026 | 0.95075 | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | 0.50711 | 0.50711 | 5.1235e-05 | 0.25358 | 0.6799 | 0.6799 | 0.6799 | 19.0298
2 | 2027 | 0.90393 | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | 1.4244 | 0.00014363 | 0.00014363 | 0.71225 | 1.9311 | 1.9311 | 1.9311 | 32.3177
3 | 2028 | 0.85941 | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | 7.2435 | 2.0492 | 0.00039719 | 3.6448 | 0.12655 | 0.12655 | 7.5208 | 51.501
4 | 2029 | 0.81709 | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | 86.0651 | 40.0996 | 0.00057089 | 43.2313 | 1.8249 | 1.8249 | 11.0371 | 69.3829
5 | 2030 | 0.77684 | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | 93.1579 | 42.9422 | 2.3159 | 48.4523 | 0 | 0 | 12.1296 | 96.0422
6 | 2031 | 0.73859 | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | 116.1368 | 40.8935 | 0.0025169 | 66.2952 | 0.0034327 | 0.0034327 | 15.1605 | 125.2752
7 | 2032 | 0.70221 | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | 191.5173 | 41.569 | 0.0030393 | 131.0248 | 0.024205 | 0 | 19.7457 | 177.5632
8 | 2033 | 0.66763 | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | 209.6559 | 46.5077 | 0.0040961 | 141.3933 | 0.20089 | 0.091344 | 25.9445 | 242.9625
9 | 2034 | 0.63475 | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | 263.2145 | 73.2181 | 0.00075977 | 175.7288 | 1.1342 | 0.75755 | 31.5098 | 353.5279
10 | 2035 | 0.60349 | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | XXXX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solutions |  |  |  |  | Ref. | Capex $m | Annualised $k | Network Limitation | Optimum Timing | Option 2 - Base | Option 3 - High | Option 4 - Low
First new 66 kV circuit from BLTS |  |  |  |  | 9.1.3 | XXXX | XXXX | BLTS-BKN-TH-BLTS, part of Customer Connection Works | 2031
Second new 66 kV circuit from BLTS |  |  |  |  | 9.1.4 | XXXX | XXXX | BLTS-BKN-TH-BLTS | 2030 |  | 4.587
New KTS-ADT-VDT 66 kV line |  |  |  |  | 9.2.4 | XXXX | XXXX | KTS-TMA-MAT-KTS and KTS-AW-NDT-PV-KTS | 2028 |  | 15.447
New KTS-NDT2.5 66 kV line |  |  |  |  | 9.2.5 | XXXX | XXXX | KTS-TMA-MAT-KTS and KTS-AW-NDT-PV-KTS | 2035 |  | 15.447
TMTS New Sub-Transmission Loop |  |  |  |  | 9.2.6 | XXXX | XXXX | KTS-TMA-MAT-KTS and KTS-AW-NDT-PV-KTS | 2028
SYTS New Sub-Transmission Loop |  |  |  |  | 9.2.7 | XXXX | XXXX | KTS-TMA-MAT-KTS and KTS-AW-NDT-PV-KTS | 2029
New KTS-ATK 66 kV line |  |  |  |  | 9.2.8 | XXXX | XXXX | KTS-SHM-SBY-KTS | 2028 |  | 17.936
EPN Third Transformer and feeders |  |  |  |  | 9.3.1 | XXXX | XXXX | NH and EPN | 2030 |  | 14
New Zone Substation to offload NH and EPN |  |  |  |  | 9.3.3 | XXXX | XXXX | NH and EPN | 2030 |  | 23
Third line into TTS-NEI-NH-WT-TTS |  |  |  |  | 9.3.5 | XXXX | XXXX | TTS-NEI-NH-WT-TTS and TTS-PTN-EPN-EP-TTS | 2035 |  | 11.1
Fourth transformer at FF (beyond 2035) |  |  |  |  | 9.3.6 | XXXX | XXXX | FF | 2035 | 0 |  | 0
FF Conversion |  |  |  |  | 9.3.7 | XXXX | XXXX | FF | 2035 |  | 3.5
Reconductor BTS-FF 181 |  |  |  |  | 9.3.8 | XXXX | XXXX | BTS-FF-BTS | 2026 |  | 2.6 | 2.6
TTS New Sub-Transmission Loop |  |  |  |  | 9.4.1 | XXXX | XXXX | TTS-BD-BMS-COO-VCO-TTS | 2035 |  | 22
SMTS New Sub-Transmission Loop |  |  |  |  | 9.4.3 | XXXX | XXXX | SMTS-ST-SSS-SMTS | 2033 |  | 49
DBTS New Sub-Transmission Loop |  |  |  |  | 9.4.5 | XXXX | XXXX | SMTS-ST-SSS-SMTS | 2033
Future major customer project | [5 empty] | XXXX | XXXX | Future major customer project | 2028 | 5.504 | 5.504 | 5.504
Future major customer project | [5 empty] | XXXX | XXXX | Future major customer project | 2029 | 5.018 | 5.018 | 5.018
Future major customer project | [5 empty] | XXXX | XXXX | Future major customer project | 2030 | 3.152 | 3.152 | 3.152
Future major customer project | [5 empty] | XXXX | XXXX | Future major customer project | 2031 | 2.292 | 2.292 | 2.292
[6 empty] | XXXX | XXXX
[6 empty] | XXXX | XXXX
[6 empty] | XXXX | XXXX
Tie TH-FW 66kV line |  |  |  |  | 9.1.1 | XXXX | XXXX | BLTS-BKN-TH-BLTS | 2031 | 4.587 | 4.6
Augment KTS-AW 66 kV line |  |  |  |  | 9.2.3 | XXXX | XXXX | KTS-TMA-MAT-KTS and KTS-AW-NDT-PV-KTS | 2028 | 4.623 | 4.623 | 4.623
Augment TTS-NH(NEI)-NEL-WT-TTS 66kV loop |  |  |  |  | 9.3.4 | XXXX | XXXX | 22kV Central Area NDS
ST-SSS 66kV Line Extension |  |  |  |  | 9.4.2 | XXXX | XXXX | Committed | 2026 | 10.734 | 10.734 | 10.734
New 66kV line incomer at FW No.2 66kV bus |  |  |  |  | 9.1.1 | XXXX | XXXX | BLTS-BKN-TH-BLTS | 2026 | 2.813 | 2.8
3rd Transformer and 66kV Works at FT |  |  |  |  | 9.1.5 | XXXX | XXXX | 11kV Central Area NDS
FF #4 6.6kV Bus |  |  |  |  | 9.3.9 | XXXX | XXXX | Committed - Published RIT-D
Augment TTS-PTN-EPN-EP-TTS 66kV loop |  |  |  |  | 9.3.2 | XXXX | XXXX | Committed
Augment BTS-FF 22kV Loop |  |  |  |  | 9.3.10 | XXXX | XXXX | BTS-FF-BTS | 2027 | 12.868 | 12.868
New BLTS-BKN 66 kV line ($11.37 million) |  |  |  |  | 9.1.2 | XXXX | XXXX | BLTS-BKN-TH-BLTS | 2031 | 0 | 0
New KTS-TMA 66kV line ($13.03 million) |  |  |  |  | 9.2.1 | XXXX | XXXX | KTS-TMA-MAT-KTS and KTS-AW-NDT-PV-KTS | 2027 | 0 | 0 | 0
Reconfigure existing KTS-TMA to be KTS-MAT-MDT 66kV line ($14.43 million) |  |  |  |  | 9.2.2 | XXXX | XXXX | KTS-TMA-MAT-KTS and KTS-AW-NDT-PV-KTS | 2026 | 0 | 0 | 0
BLTS 2 x 220/66 kV 150 MVA (B2 & B4) Transformers |  |  |  |  | 12.1.1 | XXXX | XXXX | BLTS66 | 2028 | 50 | 50
KTS 3 x 220/66 kV 225 MVA (B1, B2 & B5) & 1 x 220/66 kV 150 MVA (B6) Transformers |  |  |  |  | 12.2.1 | XXXX | XXXX | KTS66 East | 2030 | 150 | 150 | 150
SMTS 2 x 220/66 kV 225 MVA (B4 & B5) Transformers |  |  |  |  | 12.3.1 | XXXX | XXXX | SMTS66 | 2026 |  | 80
SMTS 1 x 220/66 kV 225 MVA (B2) Transformer |  |  |  |  | 12.3.2 | XXXX | XXXX | SMTS66 | 2026 | 40 | 40 | 40
TMTS New Terminal Station with 2 x 220/66 kV 225 MVA (B1 & B2) Transformers |  |  |  |  | 12.4.1 | XXXX | XXXX | KTS66 East | 2035 |  | 200
SYTS 2 x 500/220 kV 1000 MVA (A1&A2) & 2 x 220/66 kV 225 MVA (B1&B2) Transformers |  |  |  |  | 12.5.1 | XXXX | XXXX | KTS66 East | 2031
TTS 1 x 220/66 kV 150 MVA (B6 – West Group, B7 – East Group) Transformer(s) |  |  |  |  | 12.7.1 | XXXX | XXXX | TTS66 East | 2035
DBTS New Terminal Station with 2 x 220/66 kV 225 MVA (B1 & B2) Transformers |  |  |  |  | 12.6.1 | XXXX | XXXX | SMTS66 | 2035
Purple = connection asset works (costs not included)
Red = upstream augmentation works (bold in works program - base scenario)
Black = upstream augmentation works (alternative scenarios)
Green = transmission asset works

## NPV
Base Case NPV ($ million)
Option | PV of Project Capital Cost | PV of Annual O&M Cost | PV of EUE Cost | PV of Total Costs | Ranking |  | Option | PV of Capital and O&M Cost | PV of EUE Benefit | NPV | NPV Ranking
Option 1 | 0 | 0 | 678.3266 | 678.3266 | 6 |  | Option 1 | 0 | 0 | 0 | 6
Option 2 | 47.1672 | 7.0442 | 205.6164 | 259.8279 | 2 |  | Option 2 | 54.2115 | 472.7102 | 418.4987 | 2
Option 3 | 181.3654 | 25.8143 | 2.1376 | 209.3172 | 1 |  | Option 3 | 207.1797 | 676.189 | 469.0093 | 1
Option 4 | 31.1566 | 4.6593 | 424.2248 | 460.0407 | 5 |  | Option 4 | 35.8159 | 254.1018 | 218.2859 | 5
Option 6 | 0 | 352.8802 | 2.1376 | 355.0178 | 3 |  | Option 6 | 352.8802 | 676.189 | 323.3088 | 3
Option 7 | 0 | 427.4562 | 2.1376 | 429.5938 | 4 |  | Option 7 | 427.4562 | 676.189 | 248.7328 | 4
Option 1 TS | 0 | 0 | 836.6989 | 836.6989 | 4 |  | Option 1 TS | 0 | 0 | 0 | 4
Option 2 TS | 207.7592 | 30.5184 | 14.8736 | 253.1511 | 1 |  | Option 2 TS | 238.2775 | 821.8253 | 583.5478 | 1
Option 3 TS | 414.7088 | 59.2822 | 14.5444 | 488.5354 | 3 |  | Option 3 TS | 473.991 | 822.1545 | 348.1635 | 3
Option 4 TS | 162.5628 | 23.791 | 99.6896 | 286.0434 | 2 |  | Option 4 TS | 186.3538 | 737.0093 | 550.6555 | 2
Sensitivity NPV ($ million)
Option | Baseline | Customer Benefit 10% Lower | Customer Benefit 10% Higher | Discount Rate 1% Higher | Discount Rate 1% Lower | Capital Costs 30% Higher | Capital Costs 30% Lower
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 418.4987 | 371.2277 | 465.7697 | 388.651 | 450.9034 | 402.2353 | 434.7621
3 | 469.0093 | 401.3904 | 536.6282 | 436.7221 | 506.4216 | 406.8554 | 531.1632
4 | 218.2859 | 192.8757 | 243.6961 | 203.3718 | 234.4282 | 207.5411 | 229.0307
2 | 583.5478 | 501.3652 | 665.7303 | 547.92 | 631.0127 | 512.0645 | 655.031
3 | 348.1635 | 265.9481 | 430.379 | 324.2677 | 382.7558 | 205.9662 | 490.3608
4 | 550.6555 | 476.9545 | 624.3564 | 519.0619 | 593.7098 | 494.7493 | 606.5616
Sensitivity Rank |  |  | Yellow highlights copied from Sensitivities sheet
Option | Baseline | Customer Benefit 10% Lower | Customer Benefit 10% Higher | Discount Rate 1% Higher | Discount Rate 1% Lower | Capital Costs 30% Higher | Capital Costs 30% Lower
1 | 4 | 4 | 4 | 4 | 4 | 4 | 4
2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
3 | 1 | 1 | 1 | 1 | 1 | 1 | 1
4 | 3 | 3 | 3 | 3 | 3 | 3 | 3
2 | 1 | 1 | 1 | 1 | 1 | 1 | 1
3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
4 | 2 | 2 | 2 | 2 | 2 | 2 | 2

## VCR
Network Asset | VCR $/MWh
AW | 46285.5892 | 46285.5892
BD | 50963.0333 | 50963.0333
EPN | 48940.535 | 48940.535
FE | 42064.6415 | 42064.6415
FF | 37439.7172 | 37439.7172
FT | 48817.5936 | 48817.5936
FW | 44902.4105 | 44902.4105
NH | 47110.4745 | 47110.4745
ST | 52502.373 | 52502.373
TH | 58759.0928 | 58759.0928
TMA | 53200.6572 | 53200.6572
BLTS-FW-BLTS | 44902.4105 | 44902.4105
BLTS-BKN-TH-BLTS | 58759.0928 | 58759.0928
BTS-FF-BTS | 37439.7172 | 37439.7172
KTS-AW-NDT-PV-KTS | 46285.5892 | 46285.5892
KTS-TMA-MAT-KTS | 53200.6572 | 53200.6572
SMTS-ST-SSS-SMTS | 52502.373 | 52502.373
TTS-BD-BMS-COO-VCO-TTS | 50963.0333 | 50963.0333
TTS-NEI-NH-WT-TTS | 47110.4745 | 47110.4745
TTS-PTN-EPN-EP-TTS | 42469.1406 | 42469.1406
WMTS-FE-WGT-WMTS | 42064.6415 | 42064.6415
WMTS-FT | 48817.5936 | 48817.5936
KTS66 East | 48393.0149 | 48393.0149
KTS66 West | 48393.0149 | 48393.0149
TTS66 East | 46383.2561 | 46383.2561
TTS66 West | 51489.8518 | 51489.8518
SMTS66 | 48965.8061 | 48965.8061
BLTS66 | 51379.4999 | 51379.4999
WMTS66 | 45855.988 | 45855.988
BTS22 | 39720.3026 | 39720.3026
BLTS22 | 74785.717 | 74785.717
0 | 0