## Ratings
Zone Substation (MVA) | Summer (N) | Winter (N) | Summer (N-1) | Winter (N-1) | Feeder (MVA) | Summer | Winter
SBY | 65 | 65 | 38 | 38 | SHM11 | 14.3 | 14.3
SHM | 66 | 66 | 38 | 39.6 | SHM12 | 14.3 | 14.3
[5 empty] | SHM14 | 14.3 | 14.3
[5 empty] | SHM21 | 14.3 | 14.3
SBY Replace No.1 transformer | 82 | 82 | 49 | 49 | SHM22 | 14.3 | 14.3
SBY Replace No.1 & 3 transformers | 99 | 99 | 76 | 79.2 | SHM23 | 14.3 | 14.3
SHM 3rd transformer | 99 | 99 | 76 | 79.2 | SHM24 | 14.3 | 14.3
PLN New zone substation | 33 | 33 | 0 | 0 | SBY12 | 14.3 | 14.3
[5 empty] | SBY13 | 12.5 | 14.1
[5 empty] | SBY23 | 14.3 | 14.3
[5 empty] | SBY24 | 14.3 | 14.3
[5 empty] | SBY32 | 14.3 | 14.3
[5 empty] | SBY34 | 14.3 | 14.3
[5 empty] | SBY35 | 14.3 | 14.3
[5 empty] | SA 02 | 5.3 | 7.4
[5 empty] | SA 06 | 12 | 12.8
[5 empty] | SA 10 | 0 | 0
[5 empty] | SA 12 | 8.8 | 12.8
[5 empty] | ACR51070 (SBY13) | 2 | 2
Sub-transmission Loop (MVA) | Summer | Winter | Line |  | ACR55612 (SBY23) | 3 | 3
|  |  | Overall N Rating |  | sw51196 (SBY24) | 1.5 | 1.5
|  |  | Overall N-1 Rating |  | sw56781 (SBY24) | 0.6 | 0.6
Overall N Rating
Overall N-1 Rating
Overall N Rating
Overall N-1 Rating
Overall N Rating
Overall N-1 Rating
KTS-SBY-SHM-GSB-WND | 290 | 337 | Overall N Rating
| 180 | 216 | Overall N-1 Rating
| 96 | 116.6 | KTS-SBY No.1
| 94.3 | 100.6 | KTS-SBY No.2 |  | SBY31 new | 14.3 | 14.3
| 117.2 | 128 | KTS-SHM |  | SBY22 new | 14.3 | 14.3
| 117.2 | 128 | SBY-SHM |  | SBY15 new | 14.3 | 14.3
|  |  | Overall N Rating |  | SHM31 new | 14.3 | 14.3
|  |  | Overall N-1 Rating |  | SHM32 new | 14.3 | 14.3
[5 empty] | SHM33 new | 14.3 | 14.3
[5 empty] | PLN11 new | 14.3 | 14.3
[5 empty] | PLN12 new | 14.3 | 14.3
|  |  | Overall N Rating |  | PLN13 new | 14.3 | 14.3
|  |  | Overall N-1 Rating |  | ACR 51070 (SBY13) regulator | 5.7 | 5.7
[5 empty] | SHM13 new | 14.3 | 14.3
[5 empty] | SBY14 new | 14.3 | 14.3
[5 empty] | ACR 55612 (SBY23) regulator | 9 | 9
|  |  | Overall N Rating |  | sw 51196 upgrade | 11 | 11
|  |  | Overall N-1 Rating |  | sw 56781 upgrade | 11 | 11
Overall N Rating
Overall N-1 Rating
Overall N Rating
Overall N-1 Rating
Overall N Rating
Overall N-1 Rating
Overall N Rating
Overall N-1 Rating

## Customers
Feeder | Actual 2022
SA 02 | 49
SA 06 | 154
SA 10 | 43
SA 12 | 1846
SBY13 | 3317
SBY34 | 1
SBY32 | 3402
SBY12 | 1953
SBY23 | 3964
SBY24 | 3111
SBY35 | 1453
SHM11 | 3110
SHM12 | 2919
SHM14 | 3987
SHM21 | 4394
SHM22 | 2382
SHM23 | -
SHM24 | 1
TOTAL | 36086

## Population
Suburb | Actual 2022 | Forecast 2046 | Increase | % Increase | % Increase (pa)
Bulla / Wildwood (part) | 380.75 | 578.75 | 198 | 52% | 2.167%
Clarkefield | 350.84 | 517.23 | 166.39 | 47.43% | 1.976%
Gisborne South | 894.24 | 1210.2 | 315.96 | 35.33% | 1.472%
Sunbury | 40700 | 101065 | 60365 | 148.3% | 6.18%
Diggers Rest | 6408 | 12716 | 6308 | 98.44% | 4.102%
Plumpton area (part) | 7665 | 29970 | 22305 | 291% | 12.12%
Hillside | 16137 | 16506 | 369 | 2.287% | 0.09528%
Sydenham | 11856 | 12685 | 829 | 6.992% | 0.2913%
Taylors Lakes (part) | 6888.8 | 7000.4 | 111.6 | 1.62% | 0.0675%
Calder Park | 0 | 0 | 0 | 0% | 0%
TOTAL | 91280.63 | 182248.58 | 90967.95 | 99.66% | 4.152%

## Historical
Network Asset (MVA) | N-1 Rating | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Feeder (A) | Rating | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
SBY | 38 | 41.7696 | 45.6391 | 39.1855 | 40.887 | 45.2882 |  | SHM11 | 14.3 | 4.7631 | 6.1349 | 5.3728 | 6.4779 | 3.5438
SHM | 38 | 41.133 | 45.6218 | 34.3464 | 39.2262 | 39.7896 |  | SHM12 | 14.3 | 8.7642 | 9.1833 | 6.9351 | 8.0021 | 8.1164
KTS-SBY-SHM-GSB-WND | 180 | 132.6442 | 146.0174 | 117.6511 | 128.1812 | 136.1246 |  | SHM14 | 14.3 | 8.4212 | 9.2976 | 7.8115 | 9.5263 | 10.517
[8 empty] | SHM21 | 14.3 | 9.3358 | 10.0216 | 8.1545 | 8.8023 | 8.9166
[8 empty] | SHM22 | 14.3 | 5.792 | 6.516 | 5.0299 | 5.449 | 5.7539
[8 empty] | SHM23 | 14.3 | 0 | 0 | 0 | 0 | 1.7909
[8 empty] | SHM24 | 14.3 | 6.3636 | 6.7827 | 5.1823 | 6.173 | 6.5541
[8 empty] | SBY12 | 14.3 | 7.3162 | 7.5067 | 6.3254 | 6.1349 | 6.5541
[8 empty] | SBY13 | 12.5 | 6.8589 | 7.4305 | 6.2111 | 6.516 | 6.8208
[8 empty] | SBY23 | 14.3 | 8.4212 | 9.9454 | 8.0783 | 9.069 | 9.7168
[8 empty] | SBY24 | 14.3 | 7.8878 | 8.5355 | 8.1545 | 7.8115 | 8.9547
[8 empty] | SBY32 | 14.3 | 7.4686 | 8.0021 | 6.4017 | 6.0587 | 10.5551
[8 empty] | SBY34 | 14.3 | 3.5819 | 3.3914 | 8.0402 | 7.5448 | 3.8105
[8 empty] | SBY35 | 14.3 | 3.5438 | 3.8486 | 3.2008 | 3.5057 | 3.62
[8 empty] | SA 02 | 5.3 | 0.44926 | 0.27931 | 0.19861 | 0.40967 | 0.45612
[8 empty] | SA 06 | 12 | 0.54986 | 0.6878 | 0.49223 | 0.38141 | 0.41535
[8 empty] | SA 10 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | SA 12 | 8.8 | 3.0484 | 3.9629 | 3.4242 | 3.3151 | 3.4676
[8 empty] | ACR51070 (SBY13) | 2 | 2.0055 | 2.1727 | 1.8161 | 1.9053 | 2.6299
[8 empty] | ACR55612 (SBY23) | 3 | 1.8527 | 2.188 | 1.7772 | 1.9952 | 2.1377
[8 empty] | sw51196 (SBY24) | 1.5 | 0.80213 | 0.86801 | 0.82925 | 0.79438 | 0.91063
[8 empty] | sw56781 (SBY24) | 0.6 | 0.37003 | 0.40042 | 0.38254 | 0.36645 | 0.42008

## Summer 10PoE
Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 3.774% | Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
SBY | 38 | 51.5302 | 54.6793 | 57.0837 | 59.0455 | 60.1785 | 61.5481 | 63.1003 | 64.6873 | 66.2544 | 67.6051 | 4.114% | SHM11 | 14.3 | 5.5813 | 7.8358 | 10.0844 | 11.6744 | 12.5487 | 13.2209 | 13.8212 | 14.2509 | 14.6808 | 15.0672
SHM | 38 | 46.5908 | 49.3891 | 51.8818 | 53.8646 | 55.1609 | 56.7521 | 58.5301 | 60.3604 | 62.1924 | 63.8399 | 17.2491 | SHM12 | 14.3 | 8.5921 | 8.7105 | 8.7592 | 8.8774 | 8.991 | 9.2491 | 9.5373 | 9.8338 | 10.1304 | 10.3971
KTS-SBY-SHM-GSB-WND | 180 | 154.7 | 159.5 | 163.9 | 168.6 | 184.5431 | 189.2803 | 194.6086 | 200.0764 | 205.5149 | 210.3119 | 1.9166 | SHM14 | 14.3 | 14.6368 | 17.1115 | 18.819 | 20.1263 | 20.7781 | 21.529 | 22.1999 | 22.8901 | 23.5806 | 24.2013
[13 empty] | SHM21 | 14.3 | 10.7461 | 11.4913 | 12.0077 | 12.1349 | 12.2903 | 12.643 | 13.037 | 13.4423 | 13.8478 | 14.2123
[13 empty] | SHM22 | 14.3 | 6.1298 | 6.1331 | 6.2096 | 6.3251 | 6.406 | 6.5899 | 6.7953 | 7.0065 | 7.2179 | 7.4079
[13 empty] | SHM23 | 14.3 | 2.0006 | 1.9854 | 1.9889 | 2.01 | 2.0357 | 2.0941 | 2.1594 | 2.2265 | 2.2937 | 2.354
[13 empty] | SHM24 | 14.3 | 5.9164 | 5.8716 | 5.8818 | 5.9441 | 6.0202 | 6.193 | 6.386 | 6.5846 | 6.7832 | 6.9617
[13 empty] | SBY12 | 14.3 | 7.1706 | 7.4442 | 7.665 | 7.8478 | 7.9334 | 8.1131 | 8.3166 | 8.5246 | 8.73 | 8.907
[13 empty] | SBY13 | 12.5 | 7.1865 | 7.4265 | 7.5954 | 7.7341 | 7.8251 | 8.0087 | 8.2096 | 8.4149 | 8.6177 | 8.7924
[13 empty] | SBY23 | 14.3 | 10.6704 | 11.0506 | 11.3361 | 11.525 | 11.6931 | 11.9596 | 12.2595 | 12.5662 | 12.869 | 13.1298
[13 empty] | SBY24 | 14.3 | 8.5267 | 11.5616 | 14.1498 | 15.9708 | 16.791 | 17.5343 | 17.9741 | 18.4237 | 18.8676 | 19.2501
[13 empty] | SBY32 | 14.3 | 13.4026 | 15.1597 | 15.9827 | 16.6474 | 17.0037 | 17.5059 | 17.945 | 18.3939 | 18.8371 | 19.2189
[13 empty] | SBY34 | 14.3 | 3.2184 | 3.1902 | 3.19 | 3.2162 | 3.2476 | 3.3212 | 3.4045 | 3.4896 | 3.5737 | 3.6461
[13 empty] | SBY35 | 14.3 | 6.4984 | 6.4628 | 6.4624 | 6.5153 | 6.5791 | 6.7281 | 6.8968 | 7.0694 | 7.2397 | 7.3864
[13 empty] | SA 02 | 5.3 | 0.956 | 0.94536 | 0.94192 | 0.9451 | 0.94866 | 0.95863 | 0.97102 | 0.98351 | 0.99526 | 1.0034
[13 empty] | SA 06 | 12 | 0.38943 | 0.3851 | 0.38369 | 0.38499 | 0.38644 | 0.3905 | 0.39555 | 0.40064 | 0.40542 | 0.40874
[13 empty] | SA 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | SA 12 | 8.8 | 3.4762 | 3.4375 | 3.425 | 3.4365 | 3.4495 | 3.4857 | 3.5308 | 3.5762 | 3.6189 | 3.6485
[13 empty] | ACR51070 (SBY13) | 2 | 2.766 | 2.8082 | 2.8415 | 2.8871 | 2.9809 | 3.0959 | 3.262 | 3.4265 | 3.5911 | 3.7556
[13 empty] | ACR55612 (SBY23) | 3 | 2.3475 | 2.4311 | 2.4939 | 2.5355 | 2.5725 | 2.6311 | 2.6971 | 2.7646 | 2.8312 | 3.2825
[13 empty] | sw51196 (SBY24) | 1.5 | 1 | 1.3559 | 1.6595 | 1.873 | 1.9692 | 2.0564 | 2.108 | 2.1607 | 2.2128 | 2.2648
[13 empty] | sw56781 (SBY24) | 0.6 | 0.4 | 0.54237 | 0.66379 | 0.74922 | 0.78769 | 0.82256 | 0.84319 | 0.86428 | 0.88511 | 0.90593
ZSS/SubT Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 |  | Feeder Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
Option 2 | [12 empty] | Option 2
SBY Replace No.1 & 3 transformers | 76 | 7 | 61.6793 | 64.0837 | 66.0455 | 67.1785 | 68.5481 | 70.1003 | 71.6873 | 73.2544 | 74.6051 |  | SBY14 new | 14.3 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
SHM | 38 | -27 | 22.3891 | 24.8818 | 26.8646 | 28.1609 | 29.7521 | 31.5301 | 33.3604 | 35.1924 | 36.8399 |  | SBY22 new | 14.3 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
PLN New zone substation | 33 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | SBY24 | 14.3 | -17 | -5.4384 | -2.8502 | -1.0292 | -0.20903 | 0.53427 | 0.9741 | 1.4237 | 1.8676 | 2.2501
SBY Replace No.1 transformer | 49 | 7 | 61.6793 | 64.0837 | 66.0455 | 67.1785 | 68.5481 | 70.1003 | 71.6873 | 73.2544 | 74.6051 |  | SBY35 | 14.3 | 6 | 12.4628 | 12.4624 | 12.5153 | 12.5791 | 12.7281 | 12.8968 | 13.0694 | 13.2397 | 13.3864
[13 empty] | SHM11 | 14.3 | -7 | 0.83585 | 3.0844 | 4.6744 | 5.5487 | 6.2209 | 6.8212 | 7.2509 | 7.6808 | 8.0672
[13 empty] | SHM13 new | 14.3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
[13 empty] | SHM14 | 14.3 | -22 | -4.8885 | -3.181 | -1.8737 | -1.2219 | -0.47097 | 0.19991 | 0.89014 | 1.5806 | 2.2013
[13 empty] | PLN11 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
[13 empty] | PLN12 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Option 3 | [12 empty] | PLN13 new | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SBY Replace No.1 & 3 transformers | 76 | 7 | 61.6793 | 64.0837 | 66.0455 | 67.1785 | 68.5481 | 70.1003 | 71.6873 | 73.2544 | 74.6051 |  | SBY32 | 14.3 | -5 | 10.1597 | 10.9827 | 11.6474 | 12.0037 | 12.5059 | 12.945 | 13.3939 | 13.8371 | 14.2189
SHM 3rd transformer | 76 | -7 | 42.3891 | 44.8818 | 46.8646 | 48.1609 | 49.7521 | 51.5301 | 53.3604 | 55.1924 | 56.8399 |  | SBY23 | 14.3 | -4 | 7.0506 | 7.3361 | 7.525 | 7.6931 | 7.9596 | 8.2595 | 8.5662 | 8.869 | 9.1298
SBY Replace No.1 transformer | 49 | 7 | 61.6793 | 64.0837 | 66.0455 | 67.1785 | 68.5481 | 70.1003 | 71.6873 | 73.2544 | 74.6051 |  | SBY15 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
SHM Bus 1&2 | 66 |  | 36.3356 | 41.1719 | 44.7633 | 46.6993 | 48.677 | 50.9956 | 53.2673 | 55.5665 | 57.7315 |  | SBY13 | 12.5 | -3 | 4.4265 | 4.5954 | 4.7341 | 4.8251 | 5.0087 | 5.2096 | 5.4149 | 5.6177 | 5.7924
SHM Bus 3 | 33 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Option 3
[13 empty] | SBY14 new | 14.3 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
[13 empty] | SBY22 new | 14.3 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
[13 empty] | SBY24 | 14.3 | -17 | -5.4384 | -2.8502 | -1.0292 | -0.20903 | 0.53427 | 0.9741 | 1.4237 | 1.8676 | 2.2501
Option 4 | [12 empty] | SBY35 | 14.3 | 6 | 12.4628 | 12.4624 | 12.5153 | 12.5791 | 12.7281 | 12.8968 | 13.0694 | 13.2397 | 13.3864
[13 empty] | SHM11 | 14.3 | -7 | 0.83585 | 3.0844 | 4.6744 | 5.5487 | 6.2209 | 6.8212 | 7.2509 | 7.6808 | 8.0672
SHM | 38 | -17 | 32.3891 | 34.8818 | 36.8646 | 38.1609 | 39.7521 | 41.5301 | 43.3604 | 45.1924 | 46.8399 |  | SHM13 new | 14.3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
SBY Replace No.1 & 3 transformers | 76 | 17 | 71.6793 | 74.0837 | 76.0455 | 77.1785 | 78.5481 | 80.1003 | 81.6873 | 83.2544 | 84.6051 |  | SHM14 | 14.3 | -15 | 2.1115 | 3.819 | 5.1263 | 5.7781 | 6.529 | 7.1999 | 7.8901 | 8.5806 | 9.2013
SHM Bus 1 | 33 |  | 16.5394 | 20.6139 | 23.5599 | 25.2042 | 26.741 | 28.2702 | 29.6784 | 31.0952 | 32.3989 |  | SHM22 | 14.3 | -4 | 2.1331 | 2.2096 | 2.3251 | 2.406 | 2.5899 | 2.7953 | 3.0065 | 3.2179 | 3.4079
SHM Bus 2 | 33 |  | 24.7778 | 25.4849 | 26.1091 | 26.4399 | 26.8106 | 27.5853 | 28.4448 | 29.3271 | 30.2029 |  | SHM31 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
[13 empty] | SHM32 new | 14.3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
[13 empty] | SHM33 new | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | SBY32 | 14.3 | -5 | 10.1597 | 10.9827 | 11.6474 | 12.0037 | 12.5059 | 12.945 | 13.3939 | 13.8371 | 14.2189
[13 empty] | SBY23 | 14.3 | -4 | 7.0506 | 7.3361 | 7.525 | 7.6931 | 7.9596 | 8.2595 | 8.5662 | 8.869 | 9.1298
[13 empty] | SBY15 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
[13 empty] | SBY13 | 12.5 | -3 | 4.4265 | 4.5954 | 4.7341 | 4.8251 | 5.0087 | 5.2096 | 5.4149 | 5.6177 | 5.7924
Option 4
[13 empty] | SBY14 new | 14.3 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
[13 empty] | SBY15 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
[13 empty] | SBY22 new | 14.3 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
[13 empty] | SBY24 | 14.3 | -17 | -5.4384 | -2.8502 | -1.0292 | -0.20903 | 0.53427 | 0.9741 | 1.4237 | 1.8676 | 2.2501
[13 empty] | SBY31 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
[13 empty] | SBY35 | 14.3 | 6 | 12.4628 | 12.4624 | 12.5153 | 12.5791 | 12.7281 | 12.8968 | 13.0694 | 13.2397 | 13.3864
[13 empty] | SHM11 | 14.3 | -17 | -9.1642 | -6.9156 | -5.3256 | -4.4513 | -3.7791 | -3.1788 | -2.7491 | -2.3192 | -1.9328
[13 empty] | SHM13 new | 14.3 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
[13 empty] | SHM14 | 14.3 | -14 | 3.1115 | 4.819 | 6.1263 | 6.7781 | 7.529 | 8.1999 | 8.8901 | 9.5806 | 10.2013
[13 empty] | SHM23 | 14.3 | 0 | 1.9854 | 1.9889 | 2.01 | 2.0357 | 2.0941 | 2.1594 | 2.2265 | 2.2937 | 2.354
[13 empty] | SBY32 | 14.3 | -5 | 10.1597 | 10.9827 | 11.6474 | 12.0037 | 12.5059 | 12.945 | 13.3939 | 13.8371 | 14.2189
[13 empty] | SBY23 | 14.3 | -4 | 7.0506 | 7.3361 | 7.525 | 7.6931 | 7.9596 | 8.2595 | 8.5662 | 8.869 | 9.1298
[13 empty] | SBY13 | 12.5 | -3 | 4.4265 | 4.5954 | 4.7341 | 4.8251 | 5.0087 | 5.2096 | 5.4149 | 5.6177 | 5.7924

## Winter 10PoE
Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 5.721% | Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
SBY | 38 | 44.4145 | 48.6916 | 51.9225 | 54.5715 | 56.4362 | 58.3602 | 59.9139 | 61.4508 | 62.9716 | 64.4781 | 6.578% | SHM11 | 14.3 | 5.8412 | 8.6779 | 11.59 | 13.7592 | 15.1082 | 16.2273 | 17.0378 | 17.6123 | 18.1785 | 18.7385
SHM | 39.6 | 35.7159 | 39.4103 | 42.8144 | 45.5596 | 47.6522 | 49.9315 | 51.6875 | 53.4344 | 55.156 | 56.8592 | 21.1433 | SHM12 | 14.3 | 5.9286 | 6.193 | 6.3736 | 6.5835 | 6.7949 | 7.1193 | 7.3691 | 7.6176 | 7.8625 | 8.1047
KTS-SBY-SHM-GSB-WND | 216 | 126.3356 | 135.029 | 142.498 | 149.5181 | 166.5414 | 173.2667 | 178.5621 | 183.8164 | 189.0041 | 194.1919 | 2.3493 | SHM14 | 14.3 | 9.3985 | 11.3335 | 12.7632 | 13.9157 | 14.6416 | 15.4521 | 15.9943 | 16.5337 | 17.0652 | 17.5909
[13 empty] | SHM21 | 14.3 | 7.6426 | 8.4204 | 9.0044 | 9.2745 | 9.5723 | 10.0293 | 10.3812 | 10.7313 | 11.0763 | 11.4175
[13 empty] | SHM22 | 14.3 | 4.5263 | 4.6665 | 4.8354 | 5.0198 | 5.181 | 5.4283 | 5.6188 | 5.8083 | 5.995 | 6.1797
[13 empty] | SHM23 | 14.3 | 1.9287 | 1.9724 | 2.0221 | 2.0828 | 2.1497 | 2.2523 | 2.3313 | 2.4099 | 2.4874 | 2.564
[13 empty] | SHM24 | 14.3 | 5.9648 | 5.9763 | 6.0004 | 6.037 | 6.0875 | 6.1977 | 6.3081 | 6.4186 | 6.5319 | 6.6472
[13 empty] | SBY12 | 14.3 | 6.2464 | 6.661 | 6.9923 | 7.2476 | 7.4159 | 7.6284 | 7.8428 | 8.0587 | 8.2797 | 8.5049
[13 empty] | SBY13 | 14.1 | 7.0703 | 7.5285 | 7.8801 | 8.1779 | 8.4318 | 8.7893 | 9.0442 | 9.294 | 9.5363 | 9.7721
[13 empty] | SBY23 | 14.3 | 9.942 | 10.6092 | 11.1381 | 11.5409 | 11.9325 | 12.4302 | 12.7906 | 13.144 | 13.4866 | 13.8201
[13 empty] | SBY24 | 14.3 | 6.7642 | 9.448 | 11.8321 | 13.6103 | 14.5816 | 15.5087 | 15.9583 | 16.3993 | 16.8266 | 17.2427
[13 empty] | SBY32 | 14.3 | 11.2981 | 13.1667 | 14.2064 | 15.0808 | 15.697 | 16.4597 | 16.9369 | 17.4049 | 17.8584 | 18.3001
[13 empty] | SBY34 | 14.3 | 3.6385 | 3.6412 | 3.6493 | 3.6629 | 3.6825 | 3.7271 | 3.7712 | 3.8146 | 3.859 | 3.904
[13 empty] | SBY35 | 14.3 | 5.7571 | 5.8822 | 5.9967 | 6.1208 | 6.2559 | 6.4352 | 6.616 | 6.7981 | 6.9846 | 7.1745
[13 empty] | SA 02 | 7.4 | 0.36188 | 0.3676 | 0.37341 | 0.37932 | 0.38538 | 0.39172 | 0.39795 | 0.40406 | 0.41022 | 0.41638
[13 empty] | SA 06 | 12.8 | 0.39554 | 0.40179 | 0.40815 | 0.4146 | 0.42123 | 0.42816 | 0.43497 | 0.44165 | 0.44838 | 0.45511
[13 empty] | SA 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | SA 12 | 12.8 | 2.8964 | 2.9513 | 3.0095 | 3.0776 | 3.1481 | 3.2401 | 3.2945 | 3.3454 | 3.3918 | 3.4345
[13 empty] | ACR51070 (SBY13) | 2 | 2.5637 | 2.5964 | 2.6221 | 2.6621 | 2.731 | 2.8594 | 3.0056 | 3.1535 | 3.3015 | 3.4494
[13 empty] | ACR55612 (SBY23) | 3 | 2.1872 | 2.334 | 2.4504 | 2.539 | 2.6251 | 2.7346 | 2.8139 | 2.8917 | 2.967 | 3.0424
[13 empty] | sw51196 (SBY24) | 1.5 | 0.7933 | 1.108 | 1.3877 | 1.5962 | 1.7101 | 1.8188 | 1.8716 | 1.9233 | 1.9734 | 2.0235
[13 empty] | sw56781 (SBY24) | 0.6 | 0.31732 | 0.44322 | 0.55506 | 0.63848 | 0.68404 | 0.72753 | 0.74863 | 0.76931 | 0.78936 | 0.80941
ZSS/SubT Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 |  | Feeder Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
Option 2 | [12 empty] | Option 2
SBY Replace No.1 & 3 transformers | 79.2 | 7 | 55.6916 | 58.9225 | 61.5715 | 63.4362 | 65.3602 | 66.9139 | 68.4508 | 69.9716 | 71.4781 |  | SBY14 new | 14.3 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
SHM | 39.6 | -27 | 12.4103 | 15.8144 | 18.5596 | 20.6522 | 22.9315 | 24.6875 | 26.4344 | 28.156 | 29.8592 |  | SBY22 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
PLN New zone substation | 33 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | SBY24 | 14.3 | -17 | -7.552 | -5.1679 | -3.3897 | -2.4184 | -1.4913 | -1.0417 | -0.60075 | -0.17338 | 0.24275
SBY Replace No.1 transformer | 49 | 7 | 55.6916 | 58.9225 | 61.5715 | 63.4362 | 65.3602 | 66.9139 | 68.4508 | 69.9716 | 71.4781 |  | SBY35 | 14.3 | 6 | 11.8822 | 11.9967 | 12.1208 | 12.2559 | 12.4352 | 12.616 | 12.7981 | 12.9846 | 13.1745
[13 empty] | SHM11 | 14.3 | -7 | 1.6779 | 4.59 | 6.7592 | 8.1082 | 9.2273 | 10.0378 | 10.6123 | 11.1785 | 11.7385
[13 empty] | SHM13 new | 14.3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
[13 empty] | SHM14 | 14.3 | -22 | -10.6665 | -9.2368 | -8.0843 | -7.3584 | -6.5479 | -6.0057 | -5.4663 | -4.9348 | -4.4091
[13 empty] | PLN11 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
[13 empty] | PLN12 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Option 3 | [12 empty] | PLN13 new | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SBY Replace No.1 & 3 transformers | 79.2 | 7 | 55.6916 | 58.9225 | 61.5715 | 63.4362 | 65.3602 | 66.9139 | 68.4508 | 69.9716 | 71.4781 |  | SBY32 | 14.3 | -4 | 9.1667 | 10.2064 | 11.0808 | 11.697 | 12.4597 | 12.9369 | 13.4049 | 13.8584 | 14.3001
SHM 3rd transformer | 79.2 | -7 | 32.4103 | 35.8144 | 38.5596 | 40.6522 | 42.9315 | 44.6875 | 46.4344 | 48.156 | 49.8592 |  | SBY23 | 14.3 | -4 | 6.6092 | 7.1381 | 7.5409 | 7.9325 | 8.4302 | 8.7906 | 9.144 | 9.4866 | 9.8201
SBY Replace No.1 transformer | 49 | 7 | 55.6916 | 58.9225 | 61.5715 | 63.4362 | 65.3602 | 66.9139 | 68.4508 | 69.9716 | 71.4781 |  | SBY15 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
SHM Bus 1&2 | 66 |  | 24.1426 | 29.7506 | 34.0952 | 36.9087 | 39.712 | 42.2495 | 44.3442 | 46.4161 | 48.467 |  | SBY13 | 14.1 | -3 | 4.5285 | 4.8801 | 5.1779 | 5.4318 | 5.7893 | 6.0442 | 6.294 | 6.5363 | 6.7721
SHM Bus 3 | 33 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Option 3
[13 empty] | SBY14 new | 14.3 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
[13 empty] | SBY22 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
[13 empty] | SBY24 | 14.3 | -17 | -7.552 | -5.1679 | -3.3897 | -2.4184 | -1.4913 | -1.0417 | -0.60075 | -0.17338 | 0.24275
Option 4 | [12 empty] | SBY35 | 14.3 | 6 | 11.8822 | 11.9967 | 12.1208 | 12.2559 | 12.4352 | 12.616 | 12.7981 | 12.9846 | 13.1745
[13 empty] | SHM11 | 14.3 | -7 | 1.6779 | 4.59 | 6.7592 | 8.1082 | 9.2273 | 10.0378 | 10.6123 | 11.1785 | 11.7385
SHM | 39.6 | -17 | 22.4103 | 25.8144 | 28.5596 | 30.6522 | 32.9315 | 34.6875 | 36.4344 | 38.156 | 39.8592 |  | SHM13 new | 14.3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
SBY Replace No.1 & 3 transformers | 79.2 | 17 | 65.6916 | 68.9225 | 71.5715 | 73.4362 | 75.3602 | 76.9139 | 78.4508 | 79.9716 | 81.4781 |  | SHM14 | 14.3 | -15 | -3.6665 | -2.2368 | -1.0843 | -0.35839 | 0.45206 | 0.99434 | 1.5337 | 2.0652 | 2.5909
SHM Bus 1 | 33 |  | 8.94 | 13.5461 | 17.0485 | 19.3334 | 21.4743 | 23.1514 | 24.5152 | 25.8613 | 27.1918 |  | SHM22 | 14.3 | -4 | 0.6665 | 0.83544 | 1.0198 | 1.181 | 1.4283 | 1.6188 | 1.8083 | 1.995 | 2.1797
SHM Bus 2 | 33 |  | 20.1061 | 21.0853 | 21.923 | 22.481 | 23.093 | 23.9866 | 24.7181 | 25.4456 | 26.1672 |  | SHM31 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
[13 empty] | SHM32 new | 14.3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
[13 empty] | SHM33 new | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | SBY32 | 14.3 | -4 | 9.1667 | 10.2064 | 11.0808 | 11.697 | 12.4597 | 12.9369 | 13.4049 | 13.8584 | 14.3001
[13 empty] | SBY23 | 14.3 | -4 | 6.6092 | 7.1381 | 7.5409 | 7.9325 | 8.4302 | 8.7906 | 9.144 | 9.4866 | 9.8201
[13 empty] | SBY15 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
[13 empty] | SBY13 | 14.1 | -3 | 4.5285 | 4.8801 | 5.1779 | 5.4318 | 5.7893 | 6.0442 | 6.294 | 6.5363 | 6.7721
Option 4
[13 empty] | SBY14 new | 14.3 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
[13 empty] | SBY15 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
[13 empty] | SBY22 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
[13 empty] | SBY24 | 14.3 | -17 | -7.552 | -5.1679 | -3.3897 | -2.4184 | -1.4913 | -1.0417 | -0.60075 | -0.17338 | 0.24275
[13 empty] | SBY31 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
[13 empty] | SBY35 | 14.3 | 6 | 11.8822 | 11.9967 | 12.1208 | 12.2559 | 12.4352 | 12.616 | 12.7981 | 12.9846 | 13.1745
[13 empty] | SHM11 | 14.3 | -17 | -8.3221 | -5.41 | -3.2408 | -1.8918 | -0.77268 | 0.037772 | 0.61234 | 1.1785 | 1.7385
[13 empty] | SHM13 new | 14.3 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
[13 empty] | SHM14 | 14.3 | -14 | -2.6665 | -1.2368 | -0.084284 | 0.64161 | 1.4521 | 1.9943 | 2.5337 | 3.0652 | 3.5909
[13 empty] | SHM23 | 14.3 | 0 | 1.9724 | 2.0221 | 2.0828 | 2.1497 | 2.2523 | 2.3313 | 2.4099 | 2.4874 | 2.564
[13 empty] | SBY32 | 14.3 | -4 | 9.1667 | 10.2064 | 11.0808 | 11.697 | 12.4597 | 12.9369 | 13.4049 | 13.8584 | 14.3001
[13 empty] | SBY23 | 14.3 | -4 | 6.6092 | 7.1381 | 7.5409 | 7.9325 | 8.4302 | 8.7906 | 9.144 | 9.4866 | 9.8201
[13 empty] | SBY13 | 14.1 | -3 | 4.5285 | 4.8801 | 5.1779 | 5.4318 | 5.7893 | 6.0442 | 6.294 | 6.5363 | 6.7721

## Summer 50PoE
Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 3.948% | Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
SBY | 38 | 48.1166 | 51.1705 | 53.4068 | 55.3727 | 56.4235 | 57.6791 | 59.0812 | 60.6336 | 62.1076 | 63.5676 | 4.16% | SHM11 | 14.3 | 5.4995 | 7.7384 | 9.9566 | 11.5537 | 12.4165 | 13.0753 | 13.657 | 14.0971 | 14.5235 | 14.9513
SHM | 38 | 44.0105 | 46.5829 | 48.919 | 50.9067 | 52.1201 | 53.5959 | 55.225 | 57.0135 | 58.7477 | 60.4879 | 16.4774 | SHM12 | 14.3 | 8.4662 | 8.6021 | 8.6482 | 8.7856 | 8.8963 | 9.1472 | 9.424 | 9.7276 | 10.0219 | 10.3171
KTS-SBY-SHM-GSB-WND | 180 | 145.2499 | 149.8214 | 153.9129 | 158.6988 | 173.6698 | 178.04 | 182.89 | 188.2353 | 193.3684 | 198.5014 | 1.8308 | SHM14 | 14.3 | 13.6416 | 15.984 | 17.5749 | 18.8402 | 19.4464 | 20.1395 | 20.7489 | 21.4175 | 22.0654 | 22.7152
[13 empty] | SHM21 | 14.3 | 9.9331 | 10.6459 | 11.1216 | 11.266 | 11.408 | 11.7297 | 12.0846 | 12.4741 | 12.8514 | 13.2299
[13 empty] | SHM22 | 14.3 | 5.6661 | 5.6818 | 5.7514 | 5.8722 | 5.9462 | 6.1139 | 6.2989 | 6.5018 | 6.6985 | 6.8958
[13 empty] | SHM23 | 14.3 | 1.9712 | 1.9607 | 1.9637 | 1.9892 | 2.0142 | 2.071 | 2.1337 | 2.2025 | 2.2691 | 2.3359
[13 empty] | SHM24 | 14.3 | 5.8296 | 5.7986 | 5.8072 | 5.8827 | 5.9568 | 6.1248 | 6.3101 | 6.5135 | 6.7105 | 6.9081
[13 empty] | SBY12 | 14.3 | 6.7621 | 7.036 | 7.243 | 7.4331 | 7.5128 | 7.6792 | 7.8649 | 8.0705 | 8.2656 | 8.4589
[13 empty] | SBY13 | 12.5 | 6.6289 | 6.8656 | 7.0202 | 7.1653 | 7.2481 | 7.4146 | 7.5939 | 7.7924 | 7.9808 | 8.1674
[13 empty] | SBY23 | 14.3 | 9.8858 | 10.261 | 10.5237 | 10.7243 | 10.8786 | 11.1211 | 11.3901 | 11.6878 | 11.9704 | 12.2503
[13 empty] | SBY24 | 14.3 | 8.0089 | 10.8839 | 13.3172 | 15.0667 | 15.8373 | 16.5303 | 16.9302 | 17.3727 | 17.7928 | 18.2088
[13 empty] | SBY32 | 14.3 | 12.6984 | 14.3955 | 15.1735 | 15.8419 | 16.1777 | 16.6474 | 17.0501 | 17.4958 | 17.9188 | 18.3378
[13 empty] | SBY34 | 14.3 | 3.1712 | 3.1505 | 3.1496 | 3.1829 | 3.2134 | 3.2846 | 3.364 | 3.4519 | 3.5354 | 3.6181
[13 empty] | SBY35 | 14.3 | 6.157 | 6.137 | 6.1352 | 6.2001 | 6.2595 | 6.3981 | 6.5529 | 6.7242 | 6.8868 | 7.0478
[13 empty] | SA 02 | 5.3 | 0.891 | 0.88307 | 0.87965 | 0.8847 | 0.88786 | 0.89676 | 0.90756 | 0.92024 | 0.93131 | 0.94179
[13 empty] | SA 06 | 12 | 0.36295 | 0.35972 | 0.35833 | 0.36039 | 0.36167 | 0.3653 | 0.3697 | 0.37486 | 0.37937 | 0.38364
[13 empty] | SA 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | SA 12 | 8.8 | 3.4252 | 3.3947 | 3.3815 | 3.401 | 3.4131 | 3.4473 | 3.4888 | 3.5376 | 3.5802 | 3.6204
[13 empty] | ACR51070 (SBY13) | 2 | 2.5352 | 2.5709 | 2.5962 | 2.635 | 2.716 | 2.8207 | 2.97 | 3.1226 | 3.2753 | 3.428
[13 empty] | ACR55612 (SBY23) | 3 | 2.1749 | 2.2574 | 2.3152 | 2.3593 | 2.3933 | 2.4466 | 2.5058 | 2.5713 | 2.6335 | 2.6957
[13 empty] | sw51196 (SBY24) | 1.5 | 0.93927 | 1.2765 | 1.5618 | 1.767 | 1.8574 | 1.9387 | 1.9855 | 2.0374 | 2.0867 | 2.136
[13 empty] | sw56781 (SBY24) | 0.6 | 0.37571 | 0.51058 | 0.62473 | 0.7068 | 0.74295 | 0.77546 | 0.79422 | 0.81498 | 0.83469 | 0.85439
ZSS/SubT Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 |  | Feeder Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
Option 2 | [12 empty] | Option 2
SBY Replace No.1 & 3 transformers | 76 | 7 | 58.1705 | 60.4068 | 62.3727 | 63.4235 | 64.6791 | 66.0812 | 67.6336 | 69.1076 | 70.5676 |  | SBY14 new | 14.3 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
SHM | 38 | -27 | 19.5829 | 21.919 | 23.9067 | 25.1201 | 26.5959 | 28.225 | 30.0135 | 31.7477 | 33.4879 |  | SBY22 new | 14.3 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
PLN New zone substation | 33 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | SBY24 | 14.3 | -17 | -6.1161 | -3.6828 | -1.9333 | -1.1627 | -0.46968 | -0.069849 | 0.3727 | 0.79278 | 1.2088
SBY Replace No.1 transformer | 49 | 7 | 58.1705 | 60.4068 | 62.3727 | 63.4235 | 64.6791 | 66.0812 | 67.6336 | 69.1076 | 70.5676 |  | SBY35 | 14.3 | 6 | 12.137 | 12.1352 | 12.2001 | 12.2595 | 12.3981 | 12.5529 | 12.7242 | 12.8868 | 13.0478
[13 empty] | SHM11 | 14.3 | -7 | 0.73836 | 2.9566 | 4.5537 | 5.4165 | 6.0753 | 6.657 | 7.0971 | 7.5235 | 7.9513
[13 empty] | SHM13 new | 14.3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
[13 empty] | SHM14 | 14.3 | -22 | -6.016 | -4.4251 | -3.1598 | -2.5536 | -1.8605 | -1.2511 | -0.58252 | 0.065417 | 0.71525
[13 empty] | PLN11 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
[13 empty] | PLN12 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Option 3 | [12 empty] | PLN13 new | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SBY Replace No.1 & 3 transformers | 76 | 7 | 58.1705 | 60.4068 | 62.3727 | 63.4235 | 64.6791 | 66.0812 | 67.6336 | 69.1076 | 70.5676 |  | SBY32 | 14.3 | -5 | 9.3955 | 10.1735 | 10.8419 | 11.1777 | 11.6474 | 12.0501 | 12.4958 | 12.9188 | 13.3378
SHM 3rd transformer | 76 | -7 | 39.5829 | 41.919 | 43.9067 | 45.1201 | 46.5959 | 48.225 | 50.0135 | 51.7477 | 53.4879 |  | SBY23 | 14.3 | -4 | 6.261 | 6.5237 | 6.7243 | 6.8786 | 7.1211 | 7.3901 | 7.6878 | 7.9704 | 8.2503
SBY Replace No.1 transformer | 49 | 7 | 58.1705 | 60.4068 | 62.3727 | 63.4235 | 64.6791 | 66.0812 | 67.6336 | 69.1076 | 70.5676 |  | SBY15 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
SHM Bus 1&2 | 66 |  | 33.6043 | 38.2901 | 41.8068 | 43.7326 | 45.6039 | 47.7775 | 49.9688 | 52.2051 | 54.4153 |  | SBY13 | 12.5 | -3 | 3.8656 | 4.0202 | 4.1653 | 4.2481 | 4.4146 | 4.5939 | 4.7924 | 4.9808 | 5.1674
SHM Bus 3 | 33 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Option 3
[13 empty] | SBY14 new | 14.3 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
[13 empty] | SBY22 new | 14.3 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
[13 empty] | SBY24 | 14.3 | -17 | -6.1161 | -3.6828 | -1.9333 | -1.1627 | -0.46968 | -0.069849 | 0.3727 | 0.79278 | 1.2088
Option 4 | [12 empty] | SBY35 | 14.3 | 6 | 12.137 | 12.1352 | 12.2001 | 12.2595 | 12.3981 | 12.5529 | 12.7242 | 12.8868 | 13.0478
[13 empty] | SHM11 | 14.3 | -7 | 0.73836 | 2.9566 | 4.5537 | 5.4165 | 6.0753 | 6.657 | 7.0971 | 7.5235 | 7.9513
SHM | 38 | -17 | 29.5829 | 31.919 | 33.9067 | 35.1201 | 36.5959 | 38.225 | 40.0135 | 41.7477 | 43.4879 |  | SHM13 new | 14.3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
SBY Replace No.1 & 3 transformers | 76 | 17 | 68.1705 | 70.4068 | 72.3727 | 73.4235 | 74.6791 | 76.0812 | 77.6336 | 79.1076 | 80.5676 |  | SHM14 | 14.3 | -15 | 0.98397 | 2.5749 | 3.8402 | 4.4464 | 5.1395 | 5.7489 | 6.4175 | 7.0654 | 7.7152
SHM Bus 1 | 33 |  | 15.1885 | 19.1336 | 22.0421 | 23.6485 | 25.111 | 26.553 | 27.9385 | 29.3166 | 30.6884 |  | SHM22 | 14.3 | -4 | 1.6818 | 1.7514 | 1.8722 | 1.9462 | 2.1139 | 2.2989 | 2.5018 | 2.6985 | 2.8958
SHM Bus 2 | 33 |  | 23.3895 | 24.0899 | 24.6694 | 25.0352 | 25.382 | 26.1021 | 26.8961 | 27.7585 | 28.5964 |  | SHM31 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
[13 empty] | SHM32 new | 14.3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
[13 empty] | SHM33 new | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | SBY32 | 14.3 | -5 | 9.3955 | 10.1735 | 10.8419 | 11.1777 | 11.6474 | 12.0501 | 12.4958 | 12.9188 | 13.3378
[13 empty] | SBY23 | 14.3 | -4 | 6.261 | 6.5237 | 6.7243 | 6.8786 | 7.1211 | 7.3901 | 7.6878 | 7.9704 | 8.2503
[13 empty] | SBY15 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
[13 empty] | SBY13 | 12.5 | -3 | 3.8656 | 4.0202 | 4.1653 | 4.2481 | 4.4146 | 4.5939 | 4.7924 | 4.9808 | 5.1674
Option 4
[13 empty] | SBY14 new | 14.3 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
[13 empty] | SBY15 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
[13 empty] | SBY22 new | 14.3 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
[13 empty] | SBY24 | 14.3 | -17 | -6.1161 | -3.6828 | -1.9333 | -1.1627 | -0.46968 | -0.069849 | 0.3727 | 0.79278 | 1.2088
[13 empty] | SBY31 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
[13 empty] | SBY35 | 14.3 | 6 | 12.137 | 12.1352 | 12.2001 | 12.2595 | 12.3981 | 12.5529 | 12.7242 | 12.8868 | 13.0478
[13 empty] | SHM11 | 14.3 | -17 | -9.2616 | -7.0434 | -5.4463 | -4.5835 | -3.9247 | -3.343 | -2.9029 | -2.4765 | -2.0487
[13 empty] | SHM13 new | 14.3 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
[13 empty] | SHM14 | 14.3 | -14 | 1.984 | 3.5749 | 4.8402 | 5.4464 | 6.1395 | 6.7489 | 7.4175 | 8.0654 | 8.7152
[13 empty] | SHM23 | 14.3 | 0 | 1.9607 | 1.9637 | 1.9892 | 2.0142 | 2.071 | 2.1337 | 2.2025 | 2.2691 | 2.3359
[13 empty] | SBY32 | 14.3 | -5 | 9.3955 | 10.1735 | 10.8419 | 11.1777 | 11.6474 | 12.0501 | 12.4958 | 12.9188 | 13.3378
[13 empty] | SBY23 | 14.3 | -4 | 6.261 | 6.5237 | 6.7243 | 6.8786 | 7.1211 | 7.3901 | 7.6878 | 7.9704 | 8.2503
[13 empty] | SBY13 | 12.5 | -3 | 3.8656 | 4.0202 | 4.1653 | 4.2481 | 4.4146 | 4.5939 | 4.7924 | 4.9808 | 5.1674

## Winter 50PoE
Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 5.824% | Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
SBY | 38 | 42.3953 | 46.5569 | 49.8048 | 52.3151 | 54.1367 | 55.9759 | 57.4761 | 58.979 | 60.4589 | 61.9257 | 6.684% | SHM11 | 14.3 | 5.5766 | 8.2987 | 11.0989 | 13.1907 | 14.4933 | 15.5653 | 16.3456 | 16.9051 | 17.4545 | 17.9983
SHM | 39.6 | 34.0975 | 37.895 | 40.9987 | 43.6744 | 45.7094 | 47.8905 | 49.5835 | 51.2843 | 52.9545 | 54.608 | 20.5104 | SHM12 | 14.3 | 5.6599 | 5.9224 | 6.1035 | 6.3115 | 6.5183 | 6.8288 | 7.0698 | 7.3118 | 7.5494 | 7.7845
KTS-SBY-SHM-GSB-WND | 216 | 120.6004 | 129.4347 | 136.5818 | 143.3337 | 159.7538 | 166.1863 | 171.2955 | 176.4212 | 181.4615 | 186.5019 | 2.2789 | SHM14 | 14.3 | 8.9726 | 10.8383 | 12.2224 | 13.3407 | 14.0456 | 14.8216 | 15.3446 | 15.8698 | 16.3856 | 16.896
[13 empty] | SHM21 | 14.3 | 7.2963 | 8.0525 | 8.6229 | 8.8913 | 9.1826 | 9.6201 | 9.9595 | 10.3004 | 10.6352 | 10.9665
[13 empty] | SHM22 | 14.3 | 4.3212 | 4.4626 | 4.6306 | 4.8124 | 4.9701 | 5.2068 | 5.3906 | 5.5751 | 5.7562 | 5.9356
[13 empty] | SHM23 | 14.3 | 1.8413 | 1.8862 | 1.9364 | 1.9967 | 2.0622 | 2.1604 | 2.2366 | 2.3132 | 2.3883 | 2.4627
[13 empty] | SHM24 | 14.3 | 5.6945 | 5.7151 | 5.7461 | 5.7876 | 5.8397 | 5.9449 | 6.0519 | 6.1608 | 6.2717 | 6.3847
[13 empty] | SBY12 | 14.3 | 5.9634 | 6.37 | 6.6961 | 6.9481 | 7.1141 | 7.3172 | 7.5242 | 7.7351 | 7.95 | 8.1689
[13 empty] | SBY13 | 14.1 | 6.7499 | 7.1995 | 7.5462 | 7.84 | 8.0886 | 8.4307 | 8.6768 | 8.9209 | 9.1565 | 9.3861
[13 empty] | SBY23 | 14.3 | 9.4915 | 10.1456 | 10.6662 | 11.064 | 11.4468 | 11.9231 | 12.271 | 12.6163 | 12.9495 | 13.2742
[13 empty] | SBY24 | 14.3 | 6.4577 | 9.0352 | 11.3308 | 13.0478 | 13.988 | 14.8759 | 15.31 | 15.7408 | 16.1565 | 16.5616
[13 empty] | SBY32 | 14.3 | 10.7862 | 12.5914 | 13.6045 | 14.4576 | 15.0581 | 15.7881 | 16.2488 | 16.706 | 17.1472 | 17.5772
[13 empty] | SBY34 | 14.3 | 3.4737 | 3.4821 | 3.4947 | 3.5115 | 3.5326 | 3.575 | 3.618 | 3.6614 | 3.7053 | 3.7498
[13 empty] | SBY35 | 14.3 | 5.4962 | 5.6252 | 5.7426 | 5.8679 | 6.0013 | 6.1726 | 6.3473 | 6.5252 | 6.7065 | 6.8911
[13 empty] | SA 02 | 7.4 | 0.34548 | 0.35154 | 0.35759 | 0.36364 | 0.36969 | 0.37574 | 0.38179 | 0.38784 | 0.39388 | 0.39993
[13 empty] | SA 06 | 12.8 | 0.37762 | 0.38424 | 0.39086 | 0.39747 | 0.40408 | 0.41069 | 0.4173 | 0.42391 | 0.43052 | 0.43713
[13 empty] | SA 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | SA 12 | 12.8 | 2.7651 | 2.8224 | 2.882 | 2.9505 | 3.02 | 3.1079 | 3.1607 | 3.211 | 3.2568 | 3.2988
[13 empty] | ACR51070 (SBY13) | 2 | 2.3833 | 2.4111 | 2.4408 | 2.4879 | 2.5704 | 2.6916 | 2.8391 | 2.9901 | 3.1411 | 3.2921
[13 empty] | ACR55612 (SBY23) | 3 | 2.0881 | 2.232 | 2.3466 | 2.4341 | 2.5183 | 2.6231 | 2.6996 | 2.7756 | 2.8489 | 2.9222
[13 empty] | sw51196 (SBY24) | 1.5 | 0.75735 | 1.0596 | 1.3289 | 1.5302 | 1.6405 | 1.7446 | 1.7955 | 1.8461 | 1.8948 | 1.9436
[13 empty] | sw56781 (SBY24) | 0.6 | 0.30294 | 0.42385 | 0.53155 | 0.61209 | 0.6562 | 0.69785 | 0.71822 | 0.73842 | 0.75793 | 0.77743
ZSS/SubT Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 |  | Feeder Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
Option 2 | [12 empty] | Option 2
SBY Replace No.1 & 3 transformers | 79.2 | 7 | 53.5569 | 56.8048 | 59.3151 | 61.1367 | 62.9759 | 64.4761 | 65.979 | 67.4589 | 68.9257 |  | SBY14 new | 14.3 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
SHM | 39.6 | -27 | 10.895 | 13.9987 | 16.6744 | 18.7094 | 20.8905 | 22.5835 | 24.2843 | 25.9545 | 27.608 |  | SBY22 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
PLN New zone substation | 33 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | SBY24 | 14.3 | -17 | -7.9648 | -5.6692 | -3.9522 | -3.012 | -2.1241 | -1.69 | -1.2592 | -0.84348 | -0.43837
SBY Replace No.1 transformer | 49 | 7 | 53.5569 | 56.8048 | 59.3151 | 61.1367 | 62.9759 | 64.4761 | 65.979 | 67.4589 | 68.9257 |  | SBY35 | 14.3 | 6 | 11.6252 | 11.7426 | 11.8679 | 12.0013 | 12.1726 | 12.3473 | 12.5252 | 12.7065 | 12.8911
[13 empty] | SHM11 | 14.3 | -7 | 1.2987 | 4.0989 | 6.1907 | 7.4933 | 8.5653 | 9.3456 | 9.9051 | 10.4545 | 10.9983
[13 empty] | SHM13 new | 14.3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
[13 empty] | SHM14 | 14.3 | -22 | -11.1617 | -9.7776 | -8.6593 | -7.9544 | -7.1784 | -6.6554 | -6.1302 | -5.6144 | -5.104
[13 empty] | PLN11 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
[13 empty] | PLN12 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Option 3 | [12 empty] | PLN13 new | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SBY Replace No.1 & 3 transformers | 79.2 | 7 | 53.5569 | 56.8048 | 59.3151 | 61.1367 | 62.9759 | 64.4761 | 65.979 | 67.4589 | 68.9257 |  | SBY32 | 14.3 | -4 | 8.5914 | 9.6045 | 10.4576 | 11.0581 | 11.7881 | 12.2488 | 12.706 | 13.1472 | 13.5772
SHM 3rd transformer | 79.2 | -7 | 30.895 | 33.9987 | 36.6744 | 38.7094 | 40.8905 | 42.5835 | 44.2843 | 45.9545 | 47.608 |  | SBY23 | 14.3 | -4 | 6.1456 | 6.6662 | 7.064 | 7.4468 | 7.9231 | 8.271 | 8.6163 | 8.9495 | 9.2742
SBY Replace No.1 transformer | 49 | 7 | 53.5569 | 56.8048 | 59.3151 | 61.1367 | 62.9759 | 64.4761 | 65.979 | 67.4589 | 68.9257 |  | SBY15 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
SHM Bus 1&2 | 66 |  | 22.0916 | 27.528 | 31.7527 | 34.496 | 37.1965 | 39.6349 | 41.6678 | 43.6825 | 45.6745 |  | SBY13 | 14.1 | -3 | 4.1995 | 4.5462 | 4.84 | 5.0886 | 5.4307 | 5.6768 | 5.9209 | 6.1565 | 6.3861
SHM Bus 3 | 33 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Option 3
[13 empty] | SBY14 new | 14.3 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
[13 empty] | SBY22 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
[13 empty] | SBY24 | 14.3 | -17 | -7.9648 | -5.6692 | -3.9522 | -3.012 | -2.1241 | -1.69 | -1.2592 | -0.84348 | -0.43837
Option 4 | [12 empty] | SBY35 | 14.3 | 6 | 11.6252 | 11.7426 | 11.8679 | 12.0013 | 12.1726 | 12.3473 | 12.5252 | 12.7065 | 12.8911
[13 empty] | SHM11 | 14.3 | -7 | 1.2987 | 4.0989 | 6.1907 | 7.4933 | 8.5653 | 9.3456 | 9.9051 | 10.4545 | 10.9983
SHM | 39.6 | -17 | 20.895 | 23.9987 | 26.6744 | 28.7094 | 30.8905 | 32.5835 | 34.2843 | 35.9545 | 37.608 |  | SHM13 new | 14.3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
SBY Replace No.1 & 3 transformers | 79.2 | 17 | 63.5569 | 66.8048 | 69.3151 | 71.1367 | 72.9759 | 74.4761 | 75.979 | 77.4589 | 78.9257 |  | SHM14 | 14.3 | -15 | -4.1617 | -2.7776 | -1.6593 | -0.95436 | -0.17837 | 0.3446 | 0.86984 | 1.3856 | 1.896
SHM Bus 1 | 33 |  | 7.7969 | 12.2437 | 15.6349 | 17.8504 | 19.9052 | 21.519 | 22.8447 | 24.1518 | 25.4436 |  | SHM22 | 14.3 | -4 | 0.4626 | 0.63056 | 0.81237 | 0.97008 | 1.2068 | 1.3906 | 1.5751 | 1.7562 | 1.9356
SHM Bus 2 | 33 |  | 19.1982 | 20.1667 | 20.9963 | 21.5534 | 22.1528 | 23.0084 | 23.7151 | 24.4247 | 25.1259 |  | SHM31 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
[13 empty] | SHM32 new | 14.3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
[13 empty] | SHM33 new | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | SBY32 | 14.3 | -4 | 8.5914 | 9.6045 | 10.4576 | 11.0581 | 11.7881 | 12.2488 | 12.706 | 13.1472 | 13.5772
[13 empty] | SBY23 | 14.3 | -4 | 6.1456 | 6.6662 | 7.064 | 7.4468 | 7.9231 | 8.271 | 8.6163 | 8.9495 | 9.2742
[13 empty] | SBY15 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
[13 empty] | SBY13 | 14.1 | -3 | 4.1995 | 4.5462 | 4.84 | 5.0886 | 5.4307 | 5.6768 | 5.9209 | 6.1565 | 6.3861
Option 4
[13 empty] | SBY14 new | 14.3 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
[13 empty] | SBY15 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
[13 empty] | SBY22 new | 14.3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
[13 empty] | SBY24 | 14.3 | -17 | -7.9648 | -5.6692 | -3.9522 | -3.012 | -2.1241 | -1.69 | -1.2592 | -0.84348 | -0.43837
[13 empty] | SBY31 new | 14.3 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
[13 empty] | SBY35 | 14.3 | 6 | 11.6252 | 11.7426 | 11.8679 | 12.0013 | 12.1726 | 12.3473 | 12.5252 | 12.7065 | 12.8911
[13 empty] | SHM11 | 14.3 | -17 | -8.7013 | -5.9011 | -3.8093 | -2.5067 | -1.4347 | -0.65436 | -0.094856 | 0.45452 | 0.99826
[13 empty] | SHM13 new | 14.3 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
[13 empty] | SHM14 | 14.3 | -14 | -3.1617 | -1.7776 | -0.65932 | 0.045637 | 0.82163 | 1.3446 | 1.8698 | 2.3856 | 2.896
[13 empty] | SHM23 | 14.3 | 0 | 1.8862 | 1.9364 | 1.9967 | 2.0622 | 2.1604 | 2.2366 | 2.3132 | 2.3883 | 2.4627
[13 empty] | SBY32 | 14.3 | -4 | 8.5914 | 9.6045 | 10.4576 | 11.0581 | 11.7881 | 12.2488 | 12.706 | 13.1472 | 13.5772
[13 empty] | SBY23 | 14.3 | -4 | 6.1456 | 6.6662 | 7.064 | 7.4468 | 7.9231 | 8.271 | 8.6163 | 8.9495 | 9.2742
[13 empty] | SBY13 | 14.1 | -3 | 4.1995 | 4.5462 | 4.84 | 5.0886 | 5.4307 | 5.6768 | 5.9209 | 6.1565 | 6.3861

## REFCL
| Actual | [11 empty] | Ico (OH) | 0.072 | A/km
SHM | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | Limit | Ico (UG) | 3.36 | A/km
Ico | 300.9 | 320 | 338.482 | 350.5002 | 359.3756 | 364.074 | 365.7943 | 367.4827 | 369.1392 | 370.7639 | 372.3567 | 400
OH Growth km |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
SHM-011 |  | 0 | 0.6051 | 0.60184 | 0.59859 | 0.59534 | 0.59208 | 0.58883 | 0.58558 | 0.58232 | 0.57907
SHM-012 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHM-014 |  | 0 | 0.91757 | 0.99161 | 1.0657 | 1.1397 | 1.2137 | 1.2878 | 1.3618 | 1.4359 | 1.5099
SHM-021 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHM-022 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHM-023 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHM-024 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 0 | 1.5227 | 1.5935 | 1.6642 | 1.735 | 1.8058 | 1.8766 | 1.9474 | 2.0182 | 2.089
UG Growth km
SHM-011 |  | 0 | 0.29434 | 0.27655 | 0.25876 | 0.24097 | 0.22318 | 0.20539 | 0.1876 | 0.16981 | 0.15202
SHM-012 |  | 0 | 0.13287 | 0.0022439 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHM-014 |  | 0 | 4.92 | 3.14 | 2.22 | 0.99 | 0.11675 | 0.12038 | 0.12402 | 0.12766 | 0.1313
SHM-021 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHM-022 |  | 0 | 0.12076 | 0.12391 | 0.12706 | 0.13021 | 0.13336 | 0.13651 | 0.13967 | 0.14282 | 0.14597
SHM-023 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHM-024 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 0 | 5.468 | 3.5427 | 2.6058 | 1.3612 | 0.47329 | 0.46229 | 0.45129 | 0.44029 | 0.42929

## EUE
Results from EUE modellling | [5 empty] | VCR | 47905 | $/MWh |  | WACC | 5.18% |  | O&M | 1% |  | Asset Life | 45 | years |  | Discount Rate | 5.18%
Expected Unserved Energy for each Option (MWh) – Feeder (N) Overload (from NDS FDR EUE model) | [28 empty] | Value of Expected Unserved Energy for each Option ($k) – Feeder (N) Overload
Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7
FDR | SHM11 | [6 empty] | SHM14 | [20 empty] | FDR | SHM11 | 0 | 0 | 0 | 0 | 0 | 0 | SHM14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solution Applied | Nil | [6 empty] | Nil | [20 empty] | Solution Applied | Nil | 0 | 0 | 0 | 0 | 0 | 0 | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 15.4135 | [6 empty] | 0.56926 | [20 empty] | 2025 | 738.3822 | [6 empty] | 27.2706 | [6 empty] | 0 | [6 empty] | 0
2026 | 111.2925 | 0 | 0 | 0 |  |  |  | 14.1071 | 0 | 0 | 0 | [17 empty] | 2026 | 5331.466 | 0 | 0 | 0 | 0 | 0 | 0 | 675.8022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 227.108 | 0 | 0 | 0 |  |  |  | 58.1225 | 0 | 0 | 0 | [17 empty] | 2027 | 10879.6075 | 0 | 0 | 0 | 0 | 0 | 0 | 2784.3595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 311.7601 | 0 | 0 | 0 |  |  |  | 130.6448 | 0 | 0 | 0 | [17 empty] | 2028 | 14934.8678 | 0 | 0 | 0 | 0 | 0 | 0 | 6258.5368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 356.0615 | 0 | 0 | 0 |  |  |  | 180.8715 | 0 | 0 | 0 | [17 empty] | 2029 | 17057.1274 | 0 | 0 | 0 | 0 | 0 | 0 | 8664.6511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 408.3399 | 0 | 0 | 0 |  |  |  | 237.5182 | 0 | 0 | 0 | [17 empty] | 2030 | 19561.5236 | 0 | 0 | 0 | 0 | 0 | 0 | 11378.3115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 489.6952 | 0 | 0 | 0 |  |  |  | 297.6247 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2031 | 23458.8468 | 0 | 0 | 0 | 0 | 0 | 0 | 14257.7136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2032 | 571.0504 | 0 | 0 | 0 |  |  |  | 357.7313 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2032 | 27356.17 | 0 | 0 | 0 | 0 | 0 | 0 | 17137.1157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2033 | 652.4057 | 0 | 0 | 0 |  |  |  | 417.8378 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2033 | 31253.4933 | 0 | 0 | 0 | 0 | 0 | 0 | 20016.5178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2034 | 733.7609 | 0 | 0 | 0 |  |  |  | 477.9443 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2034 | 35150.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 22895.9199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Expected Unserved Energy for each Option (MWh) – Feeder (N) Overload (from NDS FDR EUE model) | [28 empty] | Value of Expected Unserved Energy for each Option ($k) – Feeder (N) Overload
Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7
FDR | SBY23 | [6 empty] | SBY24 | [20 empty] | FDR | SBY23 | 0 | 0 | 0 | 0 | 0 | 0 | SBY24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solution Applied | Nil | [6 empty] | Nil | [20 empty] | Solution Applied | Nil | 0 | 0 | 0 | 0 | 0 | 0 | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 3.2954 | [6 empty] | 0.0072161 | [20 empty] | 2025 | 157.866 | [6 empty] | 0.34569 | [6 empty] | 0 | [6 empty] | 0
2026 | 22.3423 | 0 | 0 | 0 |  |  |  | 0.86804 | 0.86804 | 0.86804 | 0.86804 | [17 empty] | 2026 | 1070.3068 | 0 | 0 | 0 | 0 | 0 | 0 | 41.5837 | 41.5837 | 41.5837 | 41.5837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 51.177 | 0 | 0 | 0 |  |  |  | 9.8809 | 0 | 0 | 0 | [17 empty] | 2027 | 2451.6344 | 0 | 0 | 0 | 0 | 0 | 0 | 473.3441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 76.3321 | 0.00019811 | 0.00019811 | 0.00019811 |  |  |  | 32.145 | 0.29261 | 0.29261 | 0.29261 | [17 empty] | 2028 | 3656.6878 | 0.0094906 | 0.0094906 | 0.0094906 | 0 | 0 | 0 | 1539.9081 | 14.0173 | 14.0173 | 14.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 90.0567 | 0.18261 | 0.18261 | 0.18261 |  |  |  | 56.995 | 5.4918 | 5.4918 | 5.4918 | [17 empty] | 2029 | 4314.1677 | 8.7479 | 8.7479 | 8.7479 | 0 | 0 | 0 | 2730.3449 | 263.0828 | 263.0828 | 263.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 109.3722 | 1.2329 | 1.2329 | 1.2329 |  |  |  | 98.2912 | 22.2562 | 22.2562 | 22.2562 | [17 empty] | 2030 | 5239.4753 | 59.0623 | 59.0623 | 59.0623 | 0 | 0 | 0 | 4708.6401 | 1066.1824 | 1066.1824 | 1066.1824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 127.6319 | 2.4656 | 2.4656 | 2.4656 |  |  |  | 137.2962 | 44.2198 | 44.2198 | 44.2198 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2031 | 6114.2046 | 118.1152 | 118.1152 | 118.1152 | 0 | 0 | 0 | 6577.1764 | 2118.3475 | 2118.3475 | 2118.3475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2032 | 145.8915 | 4.7486 | 4.7486 | 4.7486 |  |  |  | 176.3013 | 82.9478 | 82.9478 | 82.9478 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2032 | 6988.9338 | 227.4824 | 227.4824 | 227.4824 | 0 | 0 | 0 | 8445.7127 | 3973.6121 | 3973.6121 | 3973.6121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2033 | 164.1512 | 8.2643 | 8.2643 | 8.2643 |  |  |  | 215.3063 | 143.6393 | 143.6393 | 143.6393 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2033 | 7863.6631 | 395.9025 | 395.9025 | 395.9025 | 0 | 0 | 0 | 10314.249 | 6881.0418 | 6881.0418 | 6881.0418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2034 | 182.4109 | 14.063 | 14.063 | 14.063 |  |  |  | 254.3114 | 243.0589 | 243.0589 | 243.0589 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2034 | 8738.3923 | 673.6899 | 673.6899 | 673.6899 | 0 | 0 | 0 | 12182.7853 | 11643.7362 | 11643.7362 | 11643.7362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Expected Unserved Energy for each Option (MWh) – Feeder (N) Overload (from NDS FDR EUE model) | [28 empty] | Value of Expected Unserved Energy for each Option ($k) – Feeder (N) Overload
Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7
FDR | ACR51070 | [6 empty] | ACR55612 | [6 empty] | SW51196 | [6 empty] | SW56781 | [6 empty] | FDR | ACR51070 | 0 | 0 | 0 | 0 | 0 | 0 | ACR55612 | 0 | 0 | 0 | 0 | 0 | 0 | SW51196 | 0 | 0 | 0 | 0 | 0 | 0 | SW56781 | 0 | 0 | 0 | 0 | 0 | 0
Solution Applied | Nil | [6 empty] | Nil | [6 empty] | Nil | [6 empty] | Nil | [6 empty] | Solution Applied | Nil | 0 | 0 | 0 | 0 | 0 | 0 | Nil | 0 | 0 | 0 | 0 | 0 | 0 | Nil | 0 | 0 | 0 | 0 | 0 | 0 | Nil | 0 | 0 | 0 | 0 | 0 | 0
2025 | 55.5375 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 2025 | 2660.5261 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
2026 | 65.727 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2026 | 3148.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 75.8414 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0.0039631 | 0.0039631 | 0.0039631 | 0.0039631 |  |  |  | 0.0015853 | 0.0015853 | 0.0015853 | 0.0015853 |  |  |  | 2027 | 3633.1818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18985 | 0.18985 | 0.18985 | 0.18985 | 0 | 0 | 0 | 0.075942 | 0.075942 | 0.075942 | 0.075942 | 0 | 0 | 0
2028 | 93.2808 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2.5424 | 2.5424 | 2.5424 | 2.5424 |  |  |  | 1.0169 | 1.0169 | 1.0169 | 1.0169 |  |  |  | 2028 | 4468.615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.7919 | 121.7919 | 121.7919 | 121.7919 | 0 | 0 | 0 | 48.7168 | 48.7168 | 48.7168 | 48.7168 | 0 | 0 | 0
2029 | 129.8009 | 0 | 0 | 0 |  |  |  | 0.14237 | 0.14237 | 0.14237 | 0.14237 |  |  |  | 15.924 | 0 | 0 | 0 |  |  |  | 6.3696 | 0 | 0 | 0 |  |  |  | 2029 | 6218.1105 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8204 | 6.8204 | 6.8204 | 6.8204 | 0 | 0 | 0 | 762.8368 | 0 | 0 | 0 | 0 | 0 | 0 | 305.1347 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 199.7104 | 0 | 0 | 0 |  |  |  | 1.3729 | 0 | 0 | 0 |  |  |  | 48.4002 | 0 | 0 | 0 |  |  |  | 19.3601 | 0 | 0 | 0 |  |  |  | 2030 | 9567.1252 | 0 | 0 | 0 | 0 | 0 | 0 | 65.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 2318.612 | 0 | 0 | 0 | 0 | 0 | 0 | 927.4448 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 308.1803 | 0 | 0 | 0 |  |  |  | 4.984 | 0 | 0 | 0 |  |  |  | 78.3127 | 0 | 0 | 0 |  |  |  | 31.3251 | 0 | 0 | 0 |  |  |  | 2031 | 14763.3792 | 0 | 0 | 0 | 0 | 0 | 0 | 238.7599 | 0 | 0 | 0 | 0 | 0 | 0 | 3751.5682 | 0 | 0 | 0 | 0 | 0 | 0 | 1500.6273 | 0 | 0 | 0 | 0 | 0 | 0
2032 | 416.6503 | 0 | 0 | 0 |  |  |  | 8.5951 | 0 | 0 | 0 |  |  |  | 108.2251 | 0 | 0 | 0 |  |  |  | 43.29 | 0 | 0 | 0 |  |  |  | 2032 | 19959.6332 | 0 | 0 | 0 | 0 | 0 | 0 | 411.7493 | 0 | 0 | 0 | 0 | 0 | 0 | 5184.5244 | 0 | 0 | 0 | 0 | 0 | 0 | 2073.8097 | 0 | 0 | 0 | 0 | 0 | 0
2033 | 525.1203 | 0 | 0 | 0 |  |  |  | 12.2062 | 0 | 0 | 0 |  |  |  | 138.1376 | 0 | 0 | 0 |  |  |  | 55.255 | 0 | 0 | 0 |  |  |  | 2033 | 25155.8872 | 0 | 0 | 0 | 0 | 0 | 0 | 584.7387 | 0 | 0 | 0 | 0 | 0 | 0 | 6617.4805 | 0 | 0 | 0 | 0 | 0 | 0 | 2646.9922 | 0 | 0 | 0 | 0 | 0 | 0
2034 | 633.5903 | 0 | 0 | 0 |  |  |  | 15.8173 | 0 | 0 | 0 |  |  |  | 168.05 | 0 | 0 | 0 |  |  |  | 67.22 | 0 | 0 | 0 |  |  |  | 2034 | 30352.1412 | 0 | 0 | 0 | 0 | 0 | 0 | 757.7281 | 0 | 0 | 0 | 0 | 0 | 0 | 8050.4367 | 0 | 0 | 0 | 0 | 0 | 0 | 3220.1747 | 0 | 0 | 0 | 0 | 0 | 0
Expected Unserved Energy for each Option (MWh) – Zone Substations Overload (from NDS ZSS EUE model) | [28 empty] | Value of Expected Unserved Energy for each Option ($k) – Zone Substations Overload
Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7
ZSS | SBY | [6 empty] | SHM | [13 empty] | PLN | [6 empty] | ZSS | SBY | 0 | 0 | 0 | 0 | 0 | 0 | SHM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PLN | 0 | 0 | 0 | 0 | 0 | 0
Solution Applied | Nil | 8.4.1 8.4.2 | 8.4.1 8.4.2 | 8.4.1 8.4.2 |  |  |  | Nil | 8.2.1 8.4.1 & 2 | 8.3.1 8.4.1 & 2 | 8.4.1 & 2 | [10 empty] | Nil | 8.2.1 | Nil | Nil |  |  |  | Solution Applied | Nil | 8.4.1 8.4.2 | 8.4.1 8.4.2 | 8.4.1 8.4.2 | 0 | 0 | 0 | Nil | 8.2.1 8.4.1 & 2 | 8.3.1 8.4.1 & 2 | 8.4.1 & 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Nil | 8.2.1 | Nil | Nil | 0 | 0 | 0 | SHM
2025 | 7.8742 | [6 empty] | 0.158 | [13 empty] | 0 | [6 empty] | 2025 | 377.2156 | [6 empty] | 7.5692 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 7.5692
2026 | 9.1686 | 9.1686 | 9.1686 | 9.1686 |  |  |  | 0.30931 | 0.30931 | 0.30931 | 0.30931 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  | 2026 | 439.2214 | 439.2214 | 439.2214 | 439.2214 | 0 | 0 | 0 | 14.8177 | 14.8177 | 14.8177 | 14.8177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.8177
2027 | 18.4794 | 0 | 0 | 0 |  |  |  | 0.56133 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  | 2027 | 885.2539 | 0 | 0 | 0 | 0 | 0 | 0 | 26.8906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.8906
2028 | 28.5187 | 0 | 0 | 0 |  |  |  | 1.1962 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  | 2028 | 1366.1885 | 0 | 0 | 0 | 0 | 0 | 0 | 57.3041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.3041
2029 | 37.0877 | 0.0025834 | 0 | 0.0025834 |  |  |  | 2.2481 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  | 2029 | 1776.6847 | 0.12376 | 0 | 0.12376 | 0 | 0 | 0 | 107.6932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.6932
2030 | 47.4901 | 0.032842 | 0 | 0.032842 |  |  |  | 4.3924 | 0.0034107 | 0.0034107 | 0.0034107 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  | 2030 | 2275.0136 | 1.5733 | 0 | 1.5733 | 0 | 0 | 0 | 210.4171 | 0.16339 | 0.16339 | 0.16339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.4171
2031 | 57.5927 | 0.11219 | 0 | 0.11219 |  |  |  | 6.9474 | 0.084325 | 0.084325 | 0.084325 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  | 2031 | 2758.9776 | 5.3743 | 0 | 5.3743 | 0 | 0 | 0 | 332.8155 | 4.0396 | 4.0396 | 4.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332.8155
2032 | 69.0264 | 0.28686 | 0 | 0.28686 |  |  |  | 10.1852 | 0.44939 | 0.44939 | 0.44939 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  | 2032 | 3306.7112 | 13.7419 | 0 | 13.7419 | 0 | 0 | 0 | 487.9234 | 21.5279 | 21.5279 | 21.5279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 487.9234
2033 | 81.9679 | 0.67121 | 0 | 0.67121 |  |  |  | 13.9461 | 2.9886 | 0 | 2.9886 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  | 2033 | 3926.6743 | 32.1541 | 0 | 32.1541 | 0 | 0 | 0 | 668.0879 | 143.1684 | 0 | 143.1684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 668.0879
2034 | 96.1779 | 1.3304 | 0.0095712 | 1.3304 |  |  |  | 18.1917 | 23.0777 | 0 | 23.0777 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  | 2034 | 4607.4022 | 63.7349 | 0.45851 | 63.7349 | 0 | 0 | 0 | 871.471 | 1105.5348 | 0 | 1105.5348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 871.471
Expected Unserved Energy for each Option (MWh) – SubT Overload (from NDS SUBT EUE model) | [28 empty] | Value of Expected Unserved Energy for each Option ($k) – SubT Overload
Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7
SUBT | KTS-SBY-SHM-GSB-WND | [27 empty] | SUBT | KTS-SBY-SHM-GSB-WND | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solution Applied | Nil | Nil | Nil | Nil | [24 empty] | Solution Applied | Nil | Nil | Nil | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 0 | [27 empty] | 2025 | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
2026 | 0 | 0 | 0 | 0 | [24 empty] | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 0 | 0 | 0 | 0 | [24 empty] | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 0 | 0 | 0 | 0 | [24 empty] | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 0 | 0 | 0 | 0 | [24 empty] | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 0.00017362 | 0.00017362 | 0.00017362 | 0.00017362 | [24 empty] | 2030 | 0.0083171 | 0.0083171 | 0.0083171 | 0.0083171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 0.0016229 | 0.0016229 | 0.0016229 | 0.0016229 | [24 empty] | 2031 | 0.077745 | 0.077745 | 0.077745 | 0.077745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2032 | 0.0072661 | 0.0072661 | 0.0072661 | 0.0072661 | [24 empty] | 2032 | 0.34808 | 0.34808 | 0.34808 | 0.34808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2033 | 0.02083 | 0.02083 | 0.02083 | 0.02083 | [24 empty] | 2033 | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2034 | 0.058241 | 0.058241 | 0.058241 | 0.058241 | [24 empty] | 2034 | 2.79 | 2.79 | 2.79 | 2.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) | [8 empty] | Total EUE (MWh) - Zone Substations and Sub-Transmission | [8 empty] | Total EUE (MWh) - Distribution Feeders | [10 empty] | Total EUE ($k) | [8 empty] | Total EUE ($k) - Zone Substations and Sub-Transmission | [8 empty] | Total EUE ($k) - Distribution Feeders
Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  |  |  | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7
2025 | 82.8551 | 82.8551 | 82.8551 | 82.8551 | 82.8551 | 82.8551 | 82.8551 |  | 2025 | 8.0322 | 8.0322 | 8.0322 | 8.0322 | 8.0322 | 8.0322 | 8.0322 |  | 2025 | 74.8229 | 74.8229 | 74.8229 | 74.8229 | 74.8229 | 74.8229 | 74.8229 |  |  |  | 2025 | 3969.1753 | 3969.1753 | 3969.1753 | 3969.1753 | 3969.1753 | 3969.1753 | 3969.1753 |  | 2025 | 384.7847 | 384.7847 | 384.7847 | 384.7847 | 384.7847 | 384.7847 | 384.7847 |  | 2025 | 3584.3905 | 3584.3905 | 3584.3905 | 3584.3905 | 3584.3905 | 3584.3905 | 3584.3905
2026 | 223.8148 | 10.346 | 10.346 | 10.346 | 0 | 0 | 0 |  | 2026 | 9.4779 | 9.4779 | 9.4779 | 9.4779 | 0 | 0 | 0 |  | 2026 | 214.3369 | 0.86804 | 0.86804 | 0.86804 | 0 | 0 | 0 |  |  |  | 2026 | 10721.8477 | 495.6228 | 495.6228 | 495.6228 | 0 | 0 | 0 |  | 2026 | 454.0391 | 454.0391 | 454.0391 | 454.0391 | 0 | 0 | 0 |  | 2026 | 10267.8086 | 41.5837 | 41.5837 | 41.5837 | 0 | 0 | 0
2027 | 319.0407 | 0.0055484 | 0.0055484 | 0.0055484 | 0 | 0 | 0 |  | 2027 | 19.0407 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2027 | 300 | 0.0055484 | 0.0055484 | 0.0055484 | 0 | 0 | 0 |  |  |  | 2027 | 15283.6445 | 0.2658 | 0.2658 | 0.2658 | 0 | 0 | 0 |  | 2027 | 912.1445 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2027 | 14371.5 | 0.2658 | 0.2658 | 0.2658 | 0 | 0 | 0
2028 | 329.7149 | 3.8521 | 3.8521 | 3.8521 | 0 | 0 | 0 |  | 2028 | 29.7149 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2028 | 300 | 3.8521 | 3.8521 | 3.8521 | 0 | 0 | 0 |  |  |  | 2028 | 15794.9925 | 184.5354 | 184.5354 | 184.5354 | 0 | 0 | 0 |  | 2028 | 1423.4925 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2028 | 14371.5 | 184.5354 | 184.5354 | 184.5354 | 0 | 0 | 0
2029 | 339.3357 | 5.8193 | 5.8167 | 5.8193 | 0 | 0 | 0 |  | 2029 | 39.3357 | 0.0025834 | 0 | 0.0025834 | 0 | 0 | 0 |  | 2029 | 300 | 5.8167 | 5.8167 | 5.8167 | 0 | 0 | 0 |  |  |  | 2029 | 16255.8779 | 278.7748 | 278.6511 | 278.7748 | 0 | 0 | 0 |  | 2029 | 1884.3779 | 0.12376 | 0 | 0.12376 | 0 | 0 | 0 |  | 2029 | 14371.5 | 278.6511 | 278.6511 | 278.6511 | 0 | 0 | 0
2030 | 351.8827 | 23.5255 | 23.4927 | 23.5255 | 0 | 0 | 0 |  | 2030 | 51.8827 | 0.036427 | 0.0035843 | 0.036427 | 0 | 0 | 0 |  | 2030 | 300 | 23.4891 | 23.4891 | 23.4891 | 0 | 0 | 0 |  |  |  | 2030 | 16856.939 | 1126.9897 | 1125.4164 | 1126.9897 | 0 | 0 | 0 |  | 2030 | 2485.439 | 1.745 | 0.17171 | 1.745 | 0 | 0 | 0 |  | 2030 | 14371.5 | 1125.2447 | 1125.2447 | 1125.2447 | 0 | 0 | 0
2031 | 364.5417 | 46.8835 | 46.7713 | 46.8835 | 0 | 0 | 0 |  | 2031 | 64.5417 | 0.19814 | 0.085948 | 0.19814 | 0 | 0 | 0 |  | 2031 | 300 | 46.6854 | 46.6854 | 46.6854 | 0 | 0 | 0 |  |  |  | 2031 | 17463.3709 | 2245.9543 | 2240.58 | 2245.9543 | 0 | 0 | 0 |  | 2031 | 3091.8709 | 9.4917 | 4.1174 | 9.4917 | 0 | 0 | 0 |  | 2031 | 14371.5 | 2236.4626 | 2236.4626 | 2236.4626 | 0 | 0 | 0
2032 | 379.2189 | 88.4399 | 88.153 | 88.4399 | 0 | 0 | 0 |  | 2032 | 79.2189 | 0.74351 | 0.45665 | 0.74351 | 0 | 0 | 0 |  | 2032 | 300 | 87.6964 | 87.6964 | 87.6964 | 0 | 0 | 0 |  |  |  | 2032 | 18166.4827 | 4236.7124 | 4222.9705 | 4236.7124 | 0 | 0 | 0 |  | 2032 | 3794.9827 | 35.6179 | 21.876 | 35.6179 | 0 | 0 | 0 |  | 2032 | 14371.5 | 4201.0945 | 4201.0945 | 4201.0945 | 0 | 0 | 0
2033 | 395.9349 | 155.5843 | 151.9245 | 155.5843 | 0 | 0 | 0 |  | 2033 | 95.9349 | 3.6806 | 0.02083 | 3.6806 | 0 | 0 | 0 |  | 2033 | 300 | 151.9037 | 151.9037 | 151.9037 | 0 | 0 | 0 |  |  |  | 2033 | 18967.2601 | 7453.2648 | 7277.9422 | 7453.2648 | 0 | 0 | 0 |  | 2033 | 4595.7601 | 176.3204 | 0.99787 | 176.3204 | 0 | 0 | 0 |  | 2033 | 14371.5 | 7276.9444 | 7276.9444 | 7276.9444 | 0 | 0 | 0
2034 | 114.4278 | 24.4663 | 0.067812 | 24.4663 | 0 | 0 | 0 |  | 2034 | 114.4278 | 24.4663 | 0.067812 | 24.4663 | 0 | 0 | 0 |  | 2034 | [10 empty] | 2034 | 5481.6632 | 1172.0597 | 3.2485 | 1172.0597 | 0 | 0 | 0 |  | 2034 | 5481.6632 | 1172.0597 | 3.2485 | 1172.0597 | 0 | 0 | 0 |  | 2034 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | Cap | 300 | for benefits moderation

## Costs
PV Risk Mitigation Option Costs and Timing |  |  |  | Evaluation Period |  | 20 | years
CAPEX PV RESULTS $m |  |  | Option | Capex Costs | [6 empty] | Option | Opex Costs | [5 empty] | Option | EUE Costs
| Year | Ratio | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7
|  | PV $m | 0 | 56.8891 | 44.4089 | 35.4386 | 0 | 0 | 0 |  | 0 | 8.027 | 6.4968 | 5.3718 | 0 | 0 | 0 | 154.9963 | 25.7354 | 15.1825 | 16.0564 | 3.9692 | 3.9692 | 3.9692
|  | Sum $m | 0 | 73.966 | 51.966 | 36.78 | 0 | 0 | 0 |  | 0 | 10.6262 | 8.6462 | 7.0808 | 0 | 0 | 0 | 199.2595 | 34.056 | 19.7984 | 21.1634 | 3.9692 | 3.9692 | 3.9692
0 | 2025 | 1 | 0 | 12.762 | 12.762 | 12.762 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9692 | 3.9692 | 3.9692 | 3.9692 | 3.9692 | 3.9692 | 3.9692
1 | 2026 | 0.95075 |  | 15.64 | 15.64 | 22.454 | [5 empty] | 0.12762 | 0.12762 | 0.12762 | 0 | 0 | 0 | 10.7218 | 0.49562 | 0.49562 | 0.49562 | 0 | 0 | 0
2 | 2027 | 0.90393 |  | 0 | 0 | 0 | [5 empty] | 0.28402 | 0.28402 | 0.35216 | 0 | 0 | 0 | 15.2836 | 0.0002658 | 0.0002658 | 0.0002658 | 0 | 0 | 0
3 | 2028 | 0.85941 |  | 1.194 | 1.194 | 1.194 | [5 empty] | 0.28402 | 0.28402 | 0.35216 | 0 | 0 | 0 | 15.795 | 0.18454 | 0.18454 | 0.18454 | 0 | 0 | 0
4 | 2029 | 0.81709 |  | 0.37 | 0.37 | 0.37 | [5 empty] | 0.29596 | 0.29596 | 0.3641 | 0 | 0 | 0 | 16.2559 | 0.27877 | 0.27865 | 0.27877 | 0 | 0 | 0
5 | 2030 | 0.77684 |  | 0 | 0 | 0 | [5 empty] | 0.29966 | 0.29966 | 0.3678 | 0 | 0 | 0 | 16.8569 | 1.127 | 1.1254 | 1.127 | 0 | 0 | 0
6 | 2031 | 0.73859 |  | 0 | 0 | 0 | [5 empty] | 0.29966 | 0.29966 | 0.3678 | 0 | 0 | 0 | 17.4634 | 2.246 | 2.2406 | 2.246 | 0 | 0 | 0
7 | 2032 | 0.70221 |  | 0 | 22 | 0 | [5 empty] | 0.29966 | 0.29966 | 0.3678 | 0 | 0 | 0 | 18.1665 | 4.2367 | 4.223 | 4.2367 | 0 | 0 | 0
8 | 2033 | 0.66763 |  | 0 | 0 | 0 | [5 empty] | 0.29966 | 0.51966 | 0.3678 | 0 | 0 | 0 | 18.9673 | 7.4533 | 7.2779 | 7.4533 | 0 | 0 | 0
9 | 2034 | 0.63475 |  | 44 | 0 | 0 | [5 empty] | 0.29966 | 0.51966 | 0.3678 | 0 | 0 | 0 | 5.4817 | 1.1721 | 0.0032485 | 1.1721 | 0 | 0 | 0
10 | 2035 | 0.60349 | [9 empty] | 0.73966 | 0.51966 | 0.3678 | 0 | 0 | 0 | 5.4817 | 1.1721 | 0 | 0 | 0 | 0 | 0
Solutions |  |  |  |  | Ref. | Capex $m | Annualised $k | Network Limitation | Optimum Timing | Option
New feeder SHM-013 |  |  |  |  | 8.1.1 | 4.388 | 227.2984 | SHM14 | 2026 | 2,3,4
Load transfer SBY24 to SBY35 |  |  |  |  | 8.1.2 | 0 | 0 | SBY24 | 2028 | 2,3,4
Install Regulator - SBY13 |  |  |  |  | 8.1.3 | 0.29 | 15.022 | ACR51070 | 2026 | 2,3,4
Augment steel section - SBY24 |  |  |  |  | 8.1.4 | 0.7761 | 40.202 | SW51196 | 2029 | 2,3,4
Augment steel section - SBY24 |  |  |  |  | 8.1.4 | 0.4179 | 21.6472 | SW56781 | 2029 | 2,3,4
Install Regulator - SBY23 |  |  |  |  | 8.1.5 | 0.37 | 19.166 | ACR55612 | 2030 | 2,3,4
New feeder SBY-022 |  |  |  |  | 8.1.6 | 2.626 | 136.0268 | SHM11 | 2026 | 2,3,4
New feeder SBY-014 |  |  |  |  | 8.1.7 | 5.458 | 282.7244 | SBY23 | 2026 | 2,3,4
New feeder SBY-015 |  |  |  |  | 8.1.8 | 3.932 | 203.6776 | SBY24 | 2027 | 2,3,4
New 66/22 kV zone substation at PLN |  |  |  |  | 8.2.1 | 34.4 | 1781.92 | SHM | 2035 | 2
New feeders PLN11 and PLN12 |  |  |  |  | 8.2.2 | 9.6 | 724.5784 | SHM14 | 2035 | 2
3rd 66/22 kV transformer at SHM |  |  |  |  | 8.3.1 | 10 | 518 | SHM | 2033 | 3
New feeders SHM31 and SHM32 |  |  |  |  | 8.3.2 | 12 | 848.8984 | SHM14 | 2033 | 3
Upgrade SBY No.1 transformer to 20/33MVA |  |  |  |  | 8.4.1 | 5.854 | 303.2372 | SBY | 2027 | 2,3,4
Upgrade SBY No.3 transformer to 20/33MVA |  |  |  |  | 8.4.2 | 5.854 | 606.4744 | SBY | 2027 | 2,3,4
New feeder SBY-031 |  |  |  |  | 8.4.3 | 6.814 | 580.2636 | SHM14 | 2027 | 4
0
0
[7 empty] | 0 |  |  | 36.78
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## NPV
Base Case NPV ($ million)
Option | PV of Project Capital Cost | PV of Annual O&M Cost | PV of EUE Cost | PV of Total Costs | Ranking |  | Option | PV of Capital and O&M Cost | PV of EUE Benefit | NPV | PVR | Ranking
Option 1 | 0 | 0 | 154.9963 | 154.9963 | 6 |  | Option 1 | 0 | 0 | 0 | 1 | 6
Option 2 | 56.8891 | 8.027 | 25.7354 | 90.6516 | 3 |  | Option 2 | 64.9162 | 129.2609 | 64.3447 | 1.9912 | 3
Option 3 | 44.4089 | 6.4968 | 15.1825 | 66.0881 | 2 |  | Option 3 | 50.9056 | 139.8138 | 88.9082 | 2.7465 | 2
Option 4 | 35.4386 | 5.3718 | 16.0564 | 56.8668 | 1 |  | Option 4 | 40.8105 | 138.9399 | 98.1295 | 3.4045 | 1
Option 5 | 0 | 72.508 | 79.9963 | 152.5043 | 5 |  | Option 5 | 72.508 | 75 | 2.492 | 1.0344 | 5
Option 6 | 0 | 33.0032 | 79.9963 | 112.9995 | 4 |  | Option 6 | 33.0032 | 75 | 41.9968 | 2.2725 | 4
Option 7 | [6 empty] | Option 7
Sensitivity NPV ($ million)
Option | Baseline | Customer Benefit 10% Lower | Customer Benefit 10% Higher | Discount Rate 1% Higher | Discount Rate 1% Lower | Capital Costs 30% Higher | Capital Costs 30% Lower
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 64.3447 | 51.4186 | 77.2708 | 61.6176 | 67.197 | 44.8698 | 83.8195
3 | 88.9082 | 74.9268 | 102.8896 | 84.2706 | 93.0155 | 73.6365 | 104.1799
4 | 98.1295 | 84.2355 | 112.0235 | 92.5681 | 104.0919 | 85.8863 | 110.3726
5 | 2.492 | -5.008 | 9.992 |  |  | -19.2605 | 24.2444
6 | 41.9968 | 34.4968 | 49.4968 |  |  | 32.0958 | 51.8977
7 | 0 | 0 | 0 |  |  | 0 | 0
Sensitivity Rank |  |  | Yellow highlights copied from Sensitivities sheet
Option | Baseline | Customer Benefit 10% Lower | Customer Benefit 10% Higher | Discount Rate 1% Higher | Discount Rate 1% Lower | Capital Costs 30% Higher | Capital Costs 30% Lower
1 | 6 | 5 | 6 | 4 | 4 | 5 | 6
2 | 3 | 3 | 3 | 3 | 3 | 3 | 3
3 | 2 | 2 | 2 | 2 | 2 | 2 | 2
4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
5 | 5 | 7 | 5 | 4 | 4 | 7 | 5
6
7