## Ratings
Zone Substation (MVA) | Summer (N) | Winter (N) | Summer (N-1) | Winter (N-1) | Feeder (MVA) | Summer | Winter
ST | 95.2 | 95.2 | 79.7 | 89.3 | BD 01 | 14.2894 | 14.2894
KLO | 66 | 66 | 49.1 | 49.1 | BD 02 | 22.482 | 22.482
BD | 123 | 123 | 123.7 | 125.1 | BD 04 | 11.6 | 11.6
COO | 46.5 | 47.6 | 38 | 39.6 | BD 06 | 22.482 | 22.482
[5 empty] | BD 08 | 11.6221 | 11.6221
BMS | 66 | 66 | 38 | 39.6 | BD 09 | 13.1463 | 13.1463
[5 empty] | BD 13 | 12.0031 | 12.0031
CBN | 66 | 66 | 38 | 39.6 | BD 14 | 12.0031 | 12.0031
GVE | 66 | 66 | 38 | 39.6 | COO11 | 10.86 | 10.86
[5 empty] | COO12 | 14.3 | 14.3
[5 empty] | COO13 | 12.0031 | 12.0031
[5 empty] | COO14 | 12.0031 | 12.0031
[5 empty] | COO21 | 14.2894 | 14.2894
[5 empty] | COO22 | 12.0031 | 12.0031
[5 empty] | COO23 | 14.2894 | 14.2894
[5 empty] | COO24 | 12.1936 | 12.1936
[5 empty] | KLO13 | 14.2894 | 14.5
[5 empty] | KLO21 | 14.2894 | 14.5
[5 empty] | KLO22 | 14.2894 | 14.2894
Sub-transmission Loop (MVA) | Summer | Winter | Line |  | KLO23 | 14.2894 | 14.2894
|  |  | Overall N Rating |  | ST 11 | 22.482 | 22.6
|  |  | Overall N-1 Rating |  | ST 12 | 14.2894 | 14.6
[5 empty] | ST 13 | 14.2894 | 14.2894
[5 empty] | ST 14 | 14.2894 | 14.2894
|  |  | Overall N Rating |  | ST 21 | 14.2894 | 14.2894
|  |  | Overall N-1 Rating |  | ST 22 | 22.482 | 22.482
[5 empty] | ST 23 | 22.482 | 22.482
[5 empty] | ST 24 | 14.2894 | 14.2894
|  |  | Overall N Rating |  | ST 31 | 22.482 | 22.482
|  |  | Overall N-1 Rating |  | ST 32 | 12.3842 | 12.6
[5 empty] | ST 33 | 12.5 | 12.5
[5 empty] | ST 34 | 14.2894 | 14.2894
[5 empty] | COO21 Option 3 | 12.7 | 12.7
[5 empty] | GVE11 new | 12.7 | 12.7
SMTS-ST-SSS-SMTS |  |  | Overall N Rating |  | GVE12 new | 13.7 | 14.5
| 117.2 | 126.3 | Overall N-1 Rating |  | GVE13 new | 13.7 | 13.7
| 117.2 | 126.3 | SMTS-SSS |  | GVE21 new | 13.7 | 13.7
| 117.2 | 126.3 | SMTS-ST |  | GVE22 new | 13.7 | 14.5
| 142 | 182 | SSS-ST |  | GVE23 new | 0 | 0
|  |  | Overall N Rating |  | CBN11 new | 14.3 | 14.3
|  |  | Overall N-1 Rating |  | CBN12 new | 14.3 | 14.3
[5 empty] | CBN13 new | 12.7 | 12.7
[5 empty] | CBN21 new | 12.7 | 12.7
[5 empty] | CBN22 new | 12.7 | 12.7
[5 empty] | CBN23 new | 14.3 | 14.3
TTS-COO-VCO-BD-BMS-TTS |  |  | Overall N Rating |  | KLO23 reconfigured | 24 | 24
| 196.3 | 217.339 | Overall N-1 Rating
| 101.7 | 104.6 | TTS-BMS
| 117.2 | 126.3 | TTS-BD
| 101.7 | 112.6 | TTS-COO
| 89.7 | 93.1 | BMS-BD
| 90.3 | 98 | COO-VCO
| 89.7 | 93.1 | BD-VCO
Overall N Rating
Overall N-1 Rating
Overall N Rating
Overall N-1 Rating
Overall N Rating
Overall N-1 Rating
Overall N Rating
Overall N-1 Rating
Overall N Rating
Overall N-1 Rating

## Customers
Feeder | Actual 2022
COO11 | 3283
COO12 | 3502
COO13 | 1
COO14 | 0
COO21 | 1
COO22 | 3714
COO23 | 3374
COO24 | 3572
ST 11 | 3614
ST 12 | 440
ST 13 | 505
ST 14 | 170
ST 21 | 2
ST 22 | 4522
ST 23 | 154
ST 24 | 1
ST 31 | 1
ST 32 | 5780
ST 33 | 3681
ST 34 | 461
BD 01 | 141
BD 02 | 1
BD 04 | 574
BD 06 | 1
BD 08 | 832
BD 09 | 687
BD 13 | 315
BD 14 | 2036
KLO13 | 5057
KLO21 | 7
KLO22 | 5691
KLO23 | 1
TOTAL | 52121

## Population
Suburb | Actual 2022 | Forecast 2046 | Increase | % Increase | % Increase (pa)
Mickleham | 17689 | 52919 | 35230 | 199.2% | 8.298%
Craigieburn | 66088 | 78040 | 11952 | 18.08% | 0.7535%
Somerton / Campbellfield | 5332 | 5988 | 656 | 12.3% | 0.5126%
Meadow Heights | 15078 | 16073 | 995 | 6.599% | 0.275%
Roxburgh Park | 24412 | 23365 | -1047 | -4.289% | -0.1787%
Greenvale / Yuroke | 21961 | 31651 | 9690 | 44.12% | 1.838%
Coolaroo | 3237 | 3575 | 338 | 10.44% | 0.4351%
TOTAL | 153797 | 211611 | 57814 | 37.59% | 1.566%

## Historical
Network Asset (MVA) | N-1 Rating | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Feeder (A) | Rating | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
ST | 79.7 | 72.3922 | 76.3545 | 65.594 | 71.0606 | 70.438 |  | BD 01 | 14.2894 | 5.8301 | 5.8301 | 7.24 | 7.2781 | 7.0113
KLO | 49.1 | [6 empty] | BD 02 | 22.482 | 1.7071 | 1.5623 | 0.64779 | 0.7621 | 0
BD | 123.7 | 76.9933 | 72.4206 | 64.049 | 68.024 | 70.5138 |  | BD 04 | 11.6 | 3.6505 | 3.4295 | 3.0865 | 3.5057 | 3.0103
COO | 38 | 42.4176 | 43.6848 | 40.8001 | 44.2556 | 36.9997 |  | BD 06 | 22.482 | 1.4632 | 1.3337 | 0.7621 | 0.34295 | 0
BMS | 38 | 29.2226 | 29.0561 | 27.6586 | 31.1247 | 32.476 |  | BD 08 | 11.6221 | 8.7185 | 8.4974 | 8.4593 | 8.345 | 8.3069
SMTS-ST-SSS-SMTS | 117.2 | 72.3922 | 76.3545 | 65.594 | 71.0606 | 70.438 |  | BD 09 | 13.1463 | 5.3042 | 4.9918 | 4.6107 | 4.2297 | 11.4696
TTS-COO-VCO-BD-BMS-TTS | 196.3 | 177.4133 | 169.5153 | 156.8175 | 169.1326 | 166.4849 |  | BD 13 | 12.0031 | 8.1621 | 7.2781 | 7.5448 | 7.6972 | 7.8115
VCO |  | 28.7798 | 24.3538 | 24.3098 | 25.7282 | 26.4953 |  | BD 14 | 12.0031 | 7.6058 | 7.24 | 6.7065 | 7.3924 | 8.345
[8 empty] | COO11 | 10.86 | 10.0598 | 12.1936 | 9.4882 | 10.3646 | 6.0206
[8 empty] | COO12 | 14.3 | 4.8775 | 6.5922 | 4.8393 | 5.2966 | 4.2297
[8 empty] | COO13 | 12.0031 | 7.2781 | 7.5067 | 6.3636 | 6.5541 | 5.449
[8 empty] | COO14 | 12.0031 | 7.1638 | 9.0309 | 8.2307 | 7.621 | 6.8208
[8 empty] | COO21 | 14.2894 | 8.9166 | 8.688 | 7.5448 | 9.8311 | 4.8775
[8 empty] | COO22 | 12.0031 | 7.964 | 10.2884 | 10.0216 | 10.2122 | 6.1349
[8 empty] | COO23 | 14.2894 | 0 | 0 | 0 | 0 | 10.136
[8 empty] | COO24 | 12.1936 | 0 | 0 | 0 | 0 | 7.7734
[8 empty] | KLO13 | 14.2894 | 3.0865 | 5.2585 | 5.7158 | 8.1545 | 9.9835
[8 empty] | KLO21 | 14.2894 | 0.95263 | 0.99073 | 1.0669 | 2.172 | 2.0958
[8 empty] | KLO22 | 14.2894 | 7.1257 | 6.7827 | 7.4686 | 8.9928 | 9.7549
[8 empty] | KLO23 | 14.2894 | 0 | 0 | 0.60968 | 0.95263 | 1.2194
[8 empty] | ST 11 | 22.482 | 9.8692 | 11.965 | 13.4511 | 14.4418 | 16.2328
[8 empty] | ST 12 | 14.2894 | 8.1545 | 8.2307 | 6.516 | 6.9732 | 7.0113
[8 empty] | ST 13 | 14.2894 | 7.6591 | 7.7353 | 7.3162 | 7.8115 | 7.4305
[8 empty] | ST 14 | 14.2894 | 7.9259 | 7.6591 | 7.4305 | 7.5067 | 6.6684
[8 empty] | ST 21 | 14.2894 | 1.4861 | 1.448 | 1.1813 | 1.2575 | 1.2194
[8 empty] | ST 22 | 22.482 | 15.7374 | 13.3368 | 11.584 | 11.6221 | 12.0793
[8 empty] | ST 23 | 22.482 | 7.7353 | 9.412 | 9.069 | 7.621 | 7.5067
[8 empty] | ST 24 | 14.2894 | 1.829 | 1.9434 | 2.4006 | 2.4006 | 2.4006
[8 empty] | ST 31 | 22.482 | 0.7621 | 2.3244 | 2.2863 | 2.7817 | 2.4006
[8 empty] | ST 32 | 12.3842 | 10.3951 | 9.0766 | 8.4365 | 10.0216 | 10.6694
[8 empty] | ST 33 | 12.5 | 12.0793 | 11.6221 | 11.1267 | 10.5551 | 11.1648
[8 empty] | ST 34 | 14.2894 | 9.3053 | 9.1605 | 8.787 | 9.0309 | 9.793

## Summer 10PoE
Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 3.734% | Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
ST | 79.7 | 80.658 | 85.3108 | 90.573 | 94.9504 | 98.1886 | 100.5649 | 103.2501 | 105.9993 | 108.7212 | 111.0872 | 9.152% | BD 01 | 14.2894 | 7.6985 | 9.1507 | 10.5338 | 11.0319 | 11.0846 | 11.2235 | 11.3913 | 11.5609 | 11.7224 | 11.8419
KLO | 49.1 | 26.652 | 31.2028 | 34.7195 | 37.7554 | 39.6397 | 41.2582 | 43.0454 | 44.9069 | 46.8068 | 48.6051 | 2.177% | BD 02 | 22.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BD | 123.7 | 75.4032 | 78.7292 | 81.7286 | 83.7367 | 84.3173 | 85.3908 | 86.6886 | 88.0007 | 89.2516 | 90.1771 | 2.369% | BD 04 | 11.6 | 6.3146 | 6.6101 | 7.001 | 7.3074 | 7.4156 | 7.5835 | 7.7737 | 7.9681 | 8.1601 | 8.3255
COO | 38 | 46.7694 | 48.2541 | 49.4777 | 50.3317 | 50.9369 | 52.0079 | 53.2309 | 54.4789 | 55.705 | 56.7422 | 0.917% | BD 06 | 22.482 | 0 | 0.81424 | 1.8919 | 2.7138 | 2.7268 | 2.7609 | 2.8022 | 2.844 | 2.8837 | 2.9131
BMS | 38 | 36.6407 | 36.6996 | 36.9188 | 37.1299 | 37.29 | 37.7241 | 38.2554 | 38.7917 | 39.2999 | 39.6647 |  | BD 08 | 11.6221 | 9.0449 | 9.475 | 9.8627 | 10.0209 | 10.0687 | 10.1949 | 10.3474 | 10.5014 | 10.6481 | 10.7566
SMTS-ST-SSS-SMTS | 117.2 | 80.658 | 85.3108 | 90.573 | 94.9504 | 98.1886 | 100.5649 | 103.2501 | 105.9993 | 108.7212 | 111.4431 |  | BD 09 | 13.1463 | 4.158 | 4.3706 | 4.5495 | 4.5685 | 4.5903 | 4.6479 | 4.7174 | 4.7876 | 4.8545 | 4.9039
TTS-COO-VCO-BD-BMS-TTS | 196.3 | 185.0247 | 189.6026 | 193.9504 | 197.1108 | 198.5542 | 201.4063 | 204.7982 | 208.237 | 211.5444 | 214.8518 |  | BD 13 | 12.0031 | 8.0659 | 8.2246 | 8.3349 | 8.4715 | 8.5119 | 8.6186 | 8.7475 | 8.8777 | 9.0018 | 9.0935
VCO |  | 26.2113 | 25.9197 | 25.8253 | 25.9124 | 26.01 | 26.2835 | 26.6233 | 26.9657 | 27.2879 | 27.5109 |  | BD 14 | 12.0031 | 9.1221 | 9.0242 | 8.9967 | 9.0343 | 9.0774 | 9.1912 | 9.3286 | 9.4675 | 9.5998 | 9.6976
COO Bus No.1 | 33 | 11.3937 | 11.9354 | 12.3604 | 12.3926 | 12.4664 | 12.666 | 12.9283 | 13.1947 | 13.4538 | 13.6655 | N | COO11 | 10.86 | 5.502 | 5.6364 | 5.7166 | 5.7729 | 5.8268 | 5.9469 | 6.084 | 6.2239 | 6.3613 | 6.4774
COO Bus No.2 | 33 | 35.3757 | 36.3187 | 37.1174 | 37.9391 | 38.4705 | 39.3419 | 40.3026 | 41.2842 | 42.2512 | 43.0767 | 43.4688 | COO12 | 14.3 | 6.6841 | 7.5274 | 8.1832 | 8.2858 | 8.3818 | 8.5546 | 8.7518 | 8.953 | 9.1506 | 9.3177
Feeder - ZSS Diversity Factor |  | 0.93569 | 0.90731 | 0.88983 | 0.88207 | 0.87797 | 0.874 | 0.872 | 0.86997 | 0.8679 | 0.86575 |  | COO13 | 12.0031 | 0.0055236 | 0.0054681 | 0.0054674 | 0.0055125 | 0.0056008 | 0.0057187 | 0.0058535 | 0.0059939 | 0.0061185 | 0.006243
[13 empty] | COO14 | 12.0031 | -0.014764 | -0.014615 | -0.014613 | -0.014734 | -0.01497 | -0.015285 | -0.015645 | -0.016021 | -0.016353 | -0.016686
[13 empty] | COO21 | 14.2894 | 4.6219 | 4.5723 | 4.5584 | 4.5774 | 4.5993 | 4.6569 | 4.7265 | 4.7969 | 4.8639 | 4.9135
[13 empty] | COO22 | 12.0031 | 9.1029 | 9.1192 | 9.1613 | 9.229 | 9.3101 | 9.5021 | 9.7212 | 9.9447 | 10.1641 | 10.3497
[13 empty] | COO23 | 14.2894 | 13.7786 | 16.1232 | 17.7791 | 18.9106 | 19.5236 | 20.2554 | 20.9277 | 21.6207 | 22.3167 | 22.9491
[13 empty] | COO24 | 12.1936 | 10.3037 | 10.2143 | 10.2141 | 10.2945 | 10.3849 | 10.599 | 10.8434 | 11.0927 | 11.3375 | 11.5445
[13 empty] | KLO13 | 14.2894 | 11.773 | 15.0398 | 16.2804 | 16.8558 | 17.1731 | 17.8742 | 18.6485 | 19.4549 | 20.278 | 21.0571
[13 empty] | KLO21 | 14.2894 | 11.2076 | 13.9223 | 16.5488 | 18.641 | 19.9404 | 21.355 | 22.28 | 23.2436 | 24.2269 | 25.1577
[13 empty] | KLO22 | 14.2894 | 10.0323 | 13.0303 | 16.0339 | 19.215 | 21.2698 | 23.5415 | 25.8086 | 27.9404 | 30.1036 | 31.8672
[13 empty] | KLO23 | 14.2894 | 1.1247 | 1.1189 | 1.1248 | 1.1422 | 1.1637 | 1.2112 | 1.2636 | 1.3183 | 1.3741 | 1.4268
[13 empty] | ST 11 | 22.482 | 13.9044 | 14.6191 | 15.5504 | 15.9416 | 16.1617 | 16.6582 | 17.211 | 17.781 | 18.3534 | 18.8735
[13 empty] | ST 12 | 14.2894 | 13.6486 | 16.0775 | 19.341 | 22.3886 | 25.2307 | 27.5776 | 29.3876 | 30.8109 | 32.2278 | 33.466
[13 empty] | ST 13 | 14.2894 | 8.7794 | 9.7205 | 10.6131 | 10.9767 | 11.0731 | 11.3015 | 11.562 | 11.8278 | 12.0889 | 12.3095
[13 empty] | ST 14 | 14.2894 | 7.5549 | 7.4798 | 7.466 | 8.2482 | 9.0459 | 9.9455 | 10.1345 | 10.3264 | 10.5125 | 10.662
[13 empty] | ST 21 | 14.2894 | 1.3082 | 1.2937 | 1.289 | 1.2933 | 1.2982 | 1.3118 | 1.3288 | 1.3459 | 1.362 | 1.3731
[13 empty] | ST 22 | 22.482 | 14.5515 | 17.6441 | 20.6991 | 23.0297 | 24.6875 | 25.6955 | 26.8086 | 27.9679 | 29.1512 | 30.2711
[13 empty] | ST 23 | 22.482 | 10.9752 | 12.0664 | 13.3538 | 13.6832 | 13.769 | 13.9834 | 14.235 | 14.4901 | 14.7366 | 14.9313
[13 empty] | ST 24 | 14.2894 | 6.9523 | 7.3153 | 7.7273 | 8.1935 | 8.2244 | 8.3108 | 8.4183 | 8.5266 | 8.6284 | 8.699
[13 empty] | ST 31 | 22.482 | 1.7194 | 1.7003 | 1.6941 | 1.6998 | 1.7062 | 1.7241 | 1.7464 | 1.7689 | 1.79 | 1.8046
[13 empty] | ST 32 | 12.3842 | 8.0173 | 8.2189 | 8.2626 | 8.39 | 8.5479 | 8.8969 | 9.2823 | 9.6837 | 10.0934 | 10.4812
[13 empty] | ST 33 | 12.5 | 9.9018 | 9.9056 | 9.9696 | 10.0433 | 10.1315 | 10.3404 | 10.5788 | 10.822 | 11.0609 | 11.2628
[13 empty] | ST 34 | 14.2894 | 11.9585 | 12.5384 | 12.7555 | 12.992 | 13.1061 | 13.3764 | 13.6848 | 13.9994 | 14.3083 | 14.5695
ZSS/SubT Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 |  | Feeder Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2034 do nothing check
Option 2 | [12 empty] | Option 2
ST | 79.7 |  | 59.955 | 62.2387 | 63.9371 | 65.2745 | 66.3908 | 67.9057 | 69.6191 | 71.3024 | 72.7413 |  | CBN11 new | 14.3 | 4.6 | 9.4232 | 10.4023 | 11.3166 | 12.1692 | 12.8733 | 13.4163 | 13.8433 | 14.2683 | 14.6398
KLO | 49.1 |  | 23.9718 | 25.8906 | 27.1796 | 27.9406 | 28.3212 | 28.8531 | 29.5422 | 30.2583 | 31.1052 |  | CBN22 new | 12.7 | 4.2 | 7.9146 | 8.7045 | 9.4798 | 10.1116 | 10.6908 | 11.189 | 11.6157 | 12.0445 | 12.4066
BD | 123.7 |  | 85.0371 | 88.238 | 90.5527 | 91.5109 | 92.579 | 93.9356 | 95.3244 | 96.6518 | 97.6472 |  | CBN13 new | 12.7 | 2.5 | 5.7576 | 6.5085 | 7.3038 | 7.8174 | 8.3854 | 8.9522 | 9.4851 | 10.0259 | 10.4668
COO | 38 |  | 41.1676 | 41.9821 | 42.4753 | 42.6074 | 43.9368 | 44.9995 | 46.0902 | 47.1249 | 47.8628 |  | CBN21 new | 12.7 | KLO22 | 3.9091 | 4.8102 | 5.7645 | 6.3809 | 7.0624 | 7.7426 | 8.3821 | 9.0311 | 9.5602
BMS | 38 |  | 36.6996 | 36.9188 | 37.1299 | 37.29 | 37.7241 | 38.2554 | 38.7917 | 39.2999 | 39.6647 |  | COO21 | 14.2894 | COO23 | 8.0671 | 8.895 | 9.4608 | 9.7674 | 10.1334 | 10.4697 | 10.8164 | 11.1644 | 11.4808 | 4.9135
SMTS-ST-SSS-SMTS | 117.2 |  | 95.129 | 101.5913 | 107.3505 | 111.7519 | 115.4593 | 119.5038 | 123.5321 | 127.5457 | 130.9663 |  | ST 11 | 22.482 | -4 | 10.6191 | 11.5504 | 11.9416 | 12.1617 | 12.6582 | 13.211 | 13.781 | 14.3534 | 14.8735 | 18.8735
TTS-COO-VCO-BD-BMS-TTS | 196.3 |  | 188.824 | 192.9641 | 196.0704 | 197.4182 | 200.5233 | 203.8138 | 207.172 | 210.3644 | 212.6855 |  | ST 12 | 14.2894 | CBN11/22 | 7.2349 | 8.7034 | 10.0749 | 11.3538 | 12.4099 | 13.2244 | 13.8649 | 14.5025 | 15.0597 | 33.466
CBN | 38 |  | 35.174 | 39.3526 | 43.4134 | 46.4773 | 49.0685 | 51.598 | 53.913 | 56.2433 | 58.225 |  | ST 22 | 22.482 | CBN | 1.6814 | 2.6997 | 3.4766 | 4.0292 | 4.3652 | 4.7362 | 5.1226 | 5.5171 | 5.8904 | 30.2711
COO Bus No.1 | 33 |  | 15.6253 | 15.9668 | 15.9843 | 16.0605 | 16.2941 | 16.6087 | 16.9276 | 17.236 | 17.481 | N | ST 32 | 12.3842 | Nil | 8.2189 | 8.2626 | 8.39 | 8.5479 | 8.8969 | 9.2823 | 9.6837 | 10.0934 | 10.4812 | 10.4812
COO Bus No.2 | 33 |  | 23.4044 | 24.4456 | 25.2958 | 25.7917 | 26.4925 | 27.22 | 27.9654 | 28.7045 | 29.3509 | 52.6544 | ST 33 | 12.5 | -3.1 | 8.4134 | 8.8037 | 9.1821 | 9.5546 | 9.9982 | 10.4176 | 10.8031 | 11.1836 | 11.5094 | 11.2628
[13 empty] | CBN12 new | 14.3 | ST22 | 5.8814 | 6.8997 | 7.6766 | 8.2292 | 8.5652 | 8.9362 | 9.3226 | 9.7171 | 10.0904
Option 3 | [12 empty] | CBN23 new | 14.3 | ST22 | 5.8814 | 6.8997 | 7.6766 | 8.2292 | 8.5652 | 8.9362 | 9.3226 | 9.7171 | 10.0904
ST | 79.7 |  | 66.6223 | 68.8491 | 70.3062 | 71.2126 | 71.7068 | 72.8239 | 74.2874 | 75.7323 | 76.9884 |  | KLO22 | 14.2894 | COO11 | 5.0606 | 6.1118 | 7.2253 | 7.9444 | 8.7395 | 9.533 | 10.2791 | 11.0363 | 11.6535 | 31.8672
KLO | 49.1 |  | 24.4929 | 26.5444 | 27.818 | 28.5964 | 28.8525 | 29.2808 | 29.8924 | 30.5314 | 31.3425 |  | BD 08 | 14.3 | BD13 | 9.475 | 9.8627 | 10.0209 | 10.0687 | 10.1949 | 10.3474 | 10.5014 | 10.6481 | 10.7566
BD | 123.7 |  | 85.0371 | 88.238 | 90.5527 | 91.5109 | 92.579 | 93.9356 | 95.3244 | 96.6518 | 97.6472
COO | 38 |  | 36.8699 | 38.1499 | 39.1097 | 39.9634 | 41.0884 | 42.2577 | 43.3766 | 44.4783 | 45.4147
BMS | 38 |  | 36.6996 | 36.9188 | 37.1299 | 37.29 | 37.7241 | 38.2554 | 38.7917 | 39.2999 | 39.6647
SMTS-ST-SSS-SMTS | 117.2 |  | 96.7727 | 103.2048 | 108.8874 | 112.9896 | 116.6314 | 120.6522 | 124.7035 | 128.7401 | 132.1516
TTS-COO-VCO-BD-BMS-TTS | 196.3 |  | 184.5263 | 189.1319 | 192.7047 | 194.7743 | 197.6749 | 201.0721 | 204.4584 | 207.7178 | 210.2374
GVE | 38 |  | 30.1504 | 34.3557 | 38.5812 | 41.7771 | 44.9246 | 47.8284 | 50.4161 | 53.0078 | 55.1632
COO Bus No.1 | 33 |  | 15.6253 | 15.9668 | 15.9843 | 16.0605 | 16.2941 | 16.6087 | 16.9276 | 17.236 | 17.481 | N
COO Bus No.2 | 33 |  | 21.2446 | 22.1832 | 23.1254 | 23.903 | 24.7942 | 25.649 | 26.449 | 27.2423 | 27.9337 | 53.6516
Option 3
[13 empty] | GVE11 new | 12.7 | COO21 new | 8.0671 | 8.895 | 9.4608 | 9.7674 | 10.1334 | 10.4697 | 10.8164 | 11.1644 | 11.4808
[13 empty] | GVE21 new | 13.7 | ST12/32/33 | 8.3082 | 9.1509 | 9.9513 | 10.7085 | 11.4032 | 11.9777 | 12.4588 | 12.9376 | 13.3566
[13 empty] | GVE13 new | 13.7 | ST12 | 6.431 | 7.7364 | 8.9554 | 10.0923 | 11.031 | 11.755 | 12.3244 | 12.8911 | 13.3864
[13 empty] | COO21 Option 3 | 12.7 | ST32/12 | 5.6866 | 6.3524 | 7.0002 | 7.6161 | 8.1903 | 8.6681 | 9.0733 | 9.4797 | 9.8438 | 4.9135
[13 empty] | ST 11 | 22.482 | ST12/22 | 14.2333 | 14.8853 | 15.1591 | 15.3132 | 15.6607 | 16.0477 | 16.4467 | 16.8474 | 17.2114 | 18.8735
[13 empty] | ST 12 | 14.2894 | GVE13/21/COO21/ST11/KLO22 | 7.7973 | 8.5663 | 9.1408 | 9.6331 | 10.1341 | 10.5715 | 10.9559 | 11.3402 | 11.6819 | 33.466
[13 empty] | ST 22 | 22.482 | KLO22/ST11/33 | 9.2331 | 11.5243 | 13.2723 | 14.5157 | 15.2716 | 16.1064 | 16.9759 | 17.8634 | 18.7033 | 30.2711
[13 empty] | ST 32 | 12.3842 | GVE21/COO21 | 4.9313 | 4.9576 | 5.034 | 5.1287 | 5.3381 | 5.5694 | 5.8102 | 6.056 | 6.2887 | 10.4812
[13 empty] | ST 33 | 12.5 | GVE21/ST22 | 7.3209 | 7.5152 | 7.6796 | 7.8199 | 8.006 | 8.2167 | 8.4327 | 8.6471 | 8.8344 | 11.2628
[13 empty] | GVE12 new | 13.7 | KLO22 | 5.2121 | 6.4135 | 7.686 | 8.5079 | 9.4166 | 10.3234 | 11.1762 | 12.0414 | 12.7469
[13 empty] | GVE22 new | 13.7 | KLO22 | 5.2121 | 6.4135 | 7.686 | 8.5079 | 9.4166 | 10.3234 | 11.1762 | 12.0414 | 12.7469
[13 empty] | KLO22 | 14.2894 | COO11/GVE12/22/ST22/12 | 5.6349 | 6.8466 | 7.9489 | 8.6915 | 9.3474 | 10.0234 | 10.6817 | 11.351 | 11.9277 | 31.8672
[13 empty] | BD 08 | 14.3 | BD13 | 9.475 | 9.8627 | 10.0209 | 10.0687 | 10.1949 | 10.3474 | 10.5014 | 10.6481 | 10.7566
Option 2 & 3
[13 empty] | BD 08 | 11.6221 | BD 13 | 8.475 | 8.8627 | 9.0209 | 9.0687 | 9.1949 | 9.3474 | 9.5014 | 9.6481 | 9.7566 | 10.7566
[13 empty] | BD 09 | 13.1463 | ST 24 | 11.3229 | 11.8648 | 12.2958 | 12.7838 | 12.8722 | 13.0282 | 13.2059 | 13.381 | 13.5324 | 4.9039
[13 empty] | BD 13 | 12.0031 | BD 08 | 9.2246 | 9.3349 | 9.4715 | 9.5119 | 9.6186 | 9.7475 | 9.8777 | 10.0018 | 10.0935 | 9.0935
[13 empty] | COO11 | 10.86 | KLO22 | 5.1364 | 5.2166 | 5.2729 | 5.3268 | 5.4469 | 5.584 | 5.7239 | 5.8613 | 5.9774 | 6.4774
[13 empty] | COO13 | 12.0031 | COO21 | 4.5723 | 4.5584 | 4.5774 | 4.5993 | 4.6569 | 4.7265 | 4.7969 | 4.8639 | 4.9135 | 0.006243
[13 empty] | COO22 | 12.0031 | ST 21 | 4.5596 | 4.5807 | 4.6145 | 4.6551 | 4.751 | 4.8606 | 4.9723 | 5.0821 | 5.1748 | 10.3497
[13 empty] | COO23 | 14.2894 | COO21 | 8.0616 | 8.8895 | 9.4553 | 9.7618 | 10.1277 | 10.4638 | 10.8104 | 11.1583 | 11.4745 | 22.9491
[13 empty] | COO24 | 12.1936 | ST 21 | 5.1072 | 5.1071 | 5.1472 | 5.1925 | 5.2995 | 5.4217 | 5.5464 | 5.6688 | 5.7722 | 11.5445
[13 empty] | KLO13 | 14.2894 | KLO23 | 9.0239 | 9.7682 | 10.1135 | 10.3038 | 10.7245 | 11.1891 | 11.673 | 12.1668 | 12.6343 | 21.0571
[13 empty] | KLO21 | 14.2894 | KLO13 | 6.9612 | 8.2744 | 9.3205 | 9.9702 | 10.6775 | 11.14 | 11.6218 | 12.1135 | 12.5789 | 25.1577
[13 empty] | KLO23 reconfigured | 24 | KLO13/21 | 14.0959 | 15.9114 | 17.205 | 18.0031 | 19.0384 | 19.863 | 20.722 | 21.5987 | 22.4285 | 1.4268
[13 empty] | ST 24 | 14.2894 | BD 09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.699
[13 empty] | ST 21 | 14.2894 | COO24/22 | 10.9604 | 10.9767 | 11.0551 | 11.1457 | 11.3624 | 11.6111 | 11.8646 | 12.1128 | 12.3202 | 1.3731

## Winter 10PoE
Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 4.411% | Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
ST | 89.3 | 82.0015 | 87.8877 | 93.9279 | 98.6593 | 102.3469 | 104.7825 | 107.0161 | 109.2417 | 111.4937 | 113.763 | 11.54% | BD 01 | 14.2894 | 8.0394 | 9.7546 | 11.3786 | 11.9932 | 12.127 | 12.2822 | 12.4345 | 12.5835 | 12.7348 | 12.8867
KLO | 49.1 | 26.4381 | 31.8228 | 36.1756 | 40.0066 | 42.7226 | 45.15 | 47.2752 | 49.4444 | 51.6522 | 53.9031 | 2.479% | BD 02 | 22.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BD | 125.1 | 78.3879 | 83.1142 | 87.0781 | 89.5606 | 90.6427 | 91.7146 | 92.7645 | 93.7892 | 94.8314 | 95.878 | 3.593% | BD 04 | 11.6 | 5.7052 | 6.1348 | 6.6244 | 6.9999 | 7.19 | 7.3961 | 7.6039 | 7.8132 | 8.0275 | 8.2458
COO | 39.6 | 34.7182 | 37.0658 | 38.8933 | 40.0795 | 41.0264 | 42.1167 | 42.9255 | 43.9217 | 44.9292 | 45.9442 | 1.039% | BD 06 | 22.482 | 0 | 0.78947 | 1.8773 | 2.7446 | 2.8103 | 2.8982 | 2.9527 | 3.0043 | 3.0522 | 3.0967
BMS | 39.6 | 35.2306 | 35.9454 | 36.5646 | 36.9316 | 37.2496 | 37.614 | 37.9684 | 37.835 | 38.18 | 38.5258 |  | BD 08 | 11.6221 | 10.191 | 10.7176 | 11.1369 | 11.2532 | 11.2573 | 11.2809 | 11.3015 | 11.3186 | 11.3373 | 11.3562
SMTS-ST-SSS-SMTS | 126.3 | 82.0015 | 87.8877 | 93.9279 | 98.6593 | 102.3469 | 104.7825 | 107.0161 | 109.2417 | 111.4937 | 113.7456 |  | BD 09 | 13.1463 | 4.9382 | 5.2988 | 5.5893 | 5.6487 | 5.7117 | 5.7848 | 5.8566 | 5.9267 | 5.998 | 6.0695
TTS-COO-VCO-BD-BMS-TTS | 217.339 | 177.4421 | 185.1824 | 191.5535 | 195.5579 | 197.8863 | 200.416 | 202.6239 | 204.4973 | 206.8821 | 209.2668 |  | BD 13 | 12.0031 | 9.2482 | 9.6265 | 9.8858 | 10.1123 | 10.2252 | 10.3561 | 10.4845 | 10.6101 | 10.7377 | 10.8657
VCO |  | 29.1054 | 29.057 | 29.0175 | 28.9861 | 28.9677 | 28.9707 | 28.9655 | 28.9514 | 28.9415 | 28.9319 |  | BD 14 | 12.0031 | 9.2479 | 9.3392 | 9.4351 | 9.5353 | 9.6417 | 9.7652 | 9.8863 | 10.0047 | 10.125 | 10.2457
COO Bus No.1 | 33 | 9.3287 | 10.1391 | 10.77 | 10.9451 | 11.1441 | 11.3732 | 11.588 | 11.8545 | 12.1278 | 12.4058 | N | COO11 | 10.86 | 5.0987 | 5.3654 | 5.5479 | 5.672 | 5.7946 | 5.9488 | 6.1039 | 6.2596 | 6.4185 | 6.5801
COO Bus No.2 | 33 | 25.3895 | 26.9267 | 28.1233 | 29.1344 | 29.8822 | 30.7435 | 31.3375 | 32.0672 | 32.8014 | 33.5384 | 45.2067 | COO12 | 14.3 | 7.5258 | 8.7052 | 9.6479 | 9.8898 | 10.1261 | 10.3957 | 10.6667 | 10.9387 | 11.2165 | 11.4988
Feeder - ZSS Diversity Factor |  | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 |  | COO13 | 12.0031 | -0.0062741 | -0.0064802 | -0.0067381 | -0.0070387 | -0.0073578 | -0.007687 | -0.0079125 | -0.0081418 | -0.0083563 | -0.0085708
[13 empty] | COO14 | 12.0031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | COO21 | 14.2894 | 7.445 | 7.4356 | 7.4299 | 7.4278 | 7.4305 | 7.4462 | 7.4597 | 7.471 | 7.4834 | 7.4959
[13 empty] | COO22 | 12.0031 | 7.9301 | 8.1632 | 8.3624 | 8.5286 | 8.7082 | 8.94 | 9.1731 | 9.407 | 9.6459 | 9.8886
[13 empty] | COO23 | 14.2894 | 10.2157 | 12.8395 | 14.7845 | 16.1772 | 17.0656 | 18.0566 | 18.727 | 19.3966 | 20.0594 | 20.718
[13 empty] | COO24 | 12.1936 | 8.7516 | 8.912 | 9.0859 | 9.2709 | 9.4661 | 9.7182 | 9.9715 | 10.2257 | 10.4855 | 10.7493
[13 empty] | KLO13 | 14.5 | 9.1773 | 12.0708 | 13.3701 | 14.1076 | 14.6471 | 15.5273 | 16.2617 | 17.0082 | 17.7619 | 18.5249
[13 empty] | KLO21 | 14.5 | 12.1617 | 15.5658 | 18.9349 | 21.7375 | 23.6956 | 25.8461 | 27.0685 | 28.3112 | 29.5657 | 30.8357
[13 empty] | KLO22 | 14.2894 | 9.7295 | 13.0114 | 16.3782 | 19.9981 | 22.5558 | 25.4248 | 27.9781 | 30.3654 | 32.7785 | 34.8504
[13 empty] | KLO23 | 14.2894 | 1.3546 | 1.3843 | 1.4188 | 1.4586 | 1.5041 | 1.5747 | 1.6478 | 1.7232 | 1.802 | 1.8839
[13 empty] | ST 11 | 22.6 | 17.2695 | 18.6496 | 20.2231 | 20.9882 | 21.5369 | 22.3292 | 23.1381 | 23.963 | 24.8149 | 25.6912
[13 empty] | ST 12 | 14.6 | 13.1991 | 16.0204 | 19.7231 | 23.2684 | 26.7215 | 29.7473 | 31.8204 | 33.4466 | 35.0519 | 36.5576
[13 empty] | ST 13 | 14.2894 | 10.023 | 11.2025 | 12.2583 | 12.6218 | 12.6768 | 12.8049 | 12.9306 | 13.0536 | 13.1796 | 13.307
[13 empty] | ST 14 | 14.2894 | 7.0288 | 7.0255 | 7.0285 | 7.73 | 8.4401 | 9.1835 | 9.2369 | 9.2878 | 9.3404 | 9.3933
[13 empty] | ST 21 | 14.2894 | 1.4759 | 1.4734 | 1.4714 | 1.4698 | 1.4689 | 1.469 | 1.4688 | 1.4681 | 1.4676 | 1.4671
[13 empty] | ST 22 | 22.482 | 15.0684 | 18.7593 | 22.43 | 25.2606 | 27.4062 | 28.693 | 30.024 | 31.3992 | 32.8343 | 34.3271
[13 empty] | ST 23 | 22.482 | 11.0335 | 12.3825 | 13.886 | 14.3197 | 14.5012 | 14.7308 | 14.9582 | 15.1827 | 15.4112 | 15.6417
[13 empty] | ST 24 | 14.2894 | 7.3793 | 7.8388 | 8.2993 | 8.761 | 8.7554 | 8.7563 | 8.7548 | 8.7505 | 8.7475 | 8.7446
[13 empty] | ST 31 | 22.482 | 2.3135 | 2.3097 | 2.3065 | 2.304 | 2.3026 | 2.3028 | 2.3024 | 2.3013 | 2.3005 | 2.2997
[13 empty] | ST 32 | 12.6 | 7.3001 | 7.7104 | 7.9331 | 8.21 | 8.524 | 9.0362 | 9.4636 | 9.8981 | 10.3366 | 10.7807
[13 empty] | ST 33 | 12.5 | 8.964 | 9.2115 | 9.452 | 9.6399 | 9.8429 | 10.105 | 10.3684 | 10.6328 | 10.9028 | 11.1772
[13 empty] | ST 34 | 14.2894 | 13.1951 | 13.9667 | 14.2409 | 14.4404 | 14.5034 | 14.6499 | 14.7937 | 14.9344 | 15.0786 | 15.2244
ZSS/SubT Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 |  | Feeder Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2034 do nothing check
Option 2 | [12 empty] | Option 2
ST | 89.3 |  | 62.1186 | 64.4295 | 65.9576 | 67.2727 | 68.0267 | 68.9211 | 69.9565 | 70.9957 | 72.0609 |  | CBN11 new | 14.3 | 4.6 | 9.4061 | 10.5169 | 11.5805 | 12.6165 | 13.5242 | 14.1461 | 14.634 | 15.1156 | 15.5673
KLO | 49.1 |  | 25.0591 | 27.5516 | 29.3827 | 30.6856 | 31.5278 | 32.2424 | 33.0925 | 33.9671 | 35.0732 |  | CBN22 new | 12.7 | 4.2 | 7.9042 | 8.7963 | 9.6901 | 10.4638 | 11.2046 | 11.7709 | 12.2535 | 12.7356 | 13.1687
BD | 125.1 |  | 89.3866 | 93.7411 | 96.6151 | 98.0896 | 99.1568 | 100.2074 | 101.2308 | 102.2693 | 103.3134 |  | CBN13 new | 12.7 | 2.5 | 5.7528 | 6.5946 | 7.4995 | 8.139 | 8.8562 | 9.4945 | 10.0914 | 10.6946 | 11.2126
COO | 39.6 |  | 32.167 | 33.1733 | 33.6755 | 34.0572 | 35.1597 | 35.4905 | 36.2786 | 37.0811 | 37.8862 |  | CBN21 new | 12.7 | KLO22 | 3.9034 | 4.9135 | 5.9994 | 6.7667 | 7.6274 | 8.3934 | 9.1096 | 9.8335 | 10.4551
BMS | 39.6 |  | 35.9454 | 36.5646 | 36.9316 | 37.2496 | 37.614 | 37.9684 | 37.835 | 38.18 | 38.5258 |  | COO21 | 14.2894 | COO23 | 6.4133 | 7.3855 | 8.0816 | 8.5254 | 9.0206 | 9.3556 | 9.6902 | 10.0213 | 10.3504 | 7.4959
SMTS-ST-SSS-SMTS | 126.3 |  | 95.6704 | 103.3379 | 109.8261 | 115.0909 | 119.3166 | 123.1689 | 126.9246 | 130.7242 | 134.356 |  | ST 11 | 22.6 | -4 | 14.6496 | 16.2231 | 16.9882 | 17.5369 | 18.3292 | 19.1381 | 19.963 | 20.8149 | 21.6912 | 25.6912
TTS-COO-VCO-BD-BMS-TTS | 217.339 |  | 186.556 | 192.4965 | 196.2084 | 198.3641 | 200.9012 | 202.6317 | 204.2957 | 206.4719 | 208.6574 |  | ST 12 | 14.6 | CBN11/22 | 7.2092 | 8.8754 | 10.4708 | 12.0247 | 13.3863 | 14.3192 | 15.051 | 15.7733 | 16.4509 | 36.5576
CBN | 39.6 |  | 33.5519 | 38.9084 | 43.8685 | 47.8183 | 51.2899 | 54.2478 | 56.9681 | 59.7285 | 62.2951 |  | ST 22 | 22.482 | CBN | 2.0531 | 3.2767 | 4.2202 | 4.9354 | 5.3643 | 5.808 | 6.2664 | 6.7448 | 7.2424 | 34.3271
COO Bus No.1 | 33 |  | 17.8552 | 18.8069 | 19.1162 | 19.4235 | 19.7971 | 20.1708 | 20.5439 | 20.9257 | 21.3135 | N | ST 32 | 12.6 | Nil | 7.7104 | 7.9331 | 8.21 | 8.524 | 9.0362 | 9.4636 | 9.8981 | 10.3366 | 10.7807 | 10.7807
COO Bus No.2 | 33 |  | 18.165 | 19.9766 | 21.3094 | 22.2236 | 23.2713 | 24.0477 | 24.8241 | 25.5992 | 26.3741 | 59.668 | ST 33 | 12.5 | -3.1 | 7.7135 | 8.3244 | 8.8667 | 9.4151 | 9.9797 | 10.4504 | 10.8774 | 11.308 | 11.7329 | 11.1772
[13 empty] | CBN12 new | 14.3 | ST22 | 6.2531 | 7.4767 | 8.4202 | 9.1354 | 9.5643 | 10.008 | 10.4664 | 10.9448 | 11.4424
Option 3 | [12 empty] | CBN23 new | 14.3 | ST22 | 6.2531 | 7.4767 | 8.4202 | 9.1354 | 9.5643 | 10.008 | 10.4664 | 10.9448 | 11.4424
ST | 89.3 |  | 69.2059 | 71.5667 | 72.8621 | 73.687 | 73.6706 | 74.1644 | 74.9661 | 75.7992 | 76.7121 |  | KLO22 | 14.2894 | COO11 | 5.054 | 6.2324 | 7.4993 | 8.3945 | 9.3987 | 10.2923 | 11.1279 | 11.9725 | 12.6976 | 34.8504
KLO | 49.1 |  | 25.7392 | 28.4265 | 30.2772 | 31.6187 | 32.314 | 32.9292 | 33.7087 | 34.5197 | 35.6154 |  | BD 08 | 14.3 | BD13 | 10.7176 | 11.1369 | 11.2532 | 11.2573 | 11.2809 | 11.3015 | 11.3186 | 11.3373 | 11.3562
BD | 125.1 |  | 89.3866 | 93.7411 | 96.6151 | 98.0896 | 99.1568 | 100.2074 | 101.2308 | 102.2693 | 103.3134
COO | 39.6 |  | 28.6167 | 30.1452 | 31.2636 | 32.3407 | 33.4491 | 34.2278 | 35.1192 | 36.0178 | 36.9068
BMS | 39.6 |  | 35.9454 | 36.5646 | 36.9316 | 37.2496 | 37.614 | 37.9684 | 37.835 | 38.18 | 38.5258
SMTS-ST-SSS-SMTS | 126.3 |  | 95.752 | 103.3649 | 109.7517 | 114.6881 | 118.8367 | 122.6116 | 126.3351 | 130.0951 | 133.6479
TTS-COO-VCO-BD-BMS-TTS | 217.339 |  | 183.0057 | 189.4684 | 193.7965 | 196.6475 | 199.1906 | 201.369 | 203.1364 | 205.4086 | 207.678
GVE | 39.6 |  | 26.5461 | 31.7982 | 36.8896 | 41.001 | 45.1661 | 48.4471 | 51.369 | 54.2959 | 56.9358
COO Bus No.1 | 33 |  | 17.8552 | 18.8069 | 19.1162 | 19.4235 | 19.7971 | 20.1708 | 20.5439 | 20.9257 | 21.3135 | N
COO Bus No.2 | 33 |  | 17.3978 | 19.0691 | 20.4833 | 21.687 | 22.9585 | 23.9114 | 24.7905 | 25.6686 | 26.5328 | 59.5085
Option 3
[13 empty] | GVE11 new | 12.7 | COO21 new | 6.4133 | 7.3855 | 8.0816 | 8.5254 | 9.0206 | 9.3556 | 9.6902 | 10.0213 | 10.3504
[13 empty] | GVE21 new | 13.7 | ST12/32/33 | 8.0002 | 9.0323 | 10.0121 | 10.9778 | 11.8772 | 12.5304 | 13.0729 | 13.6126 | 14.1295
[13 empty] | GVE13 new | 13.7 | ST12 | 6.4082 | 7.8892 | 9.3074 | 10.6886 | 11.8989 | 12.7281 | 13.3786 | 14.0208 | 14.623
[13 empty] | COO21 Option 3 | 12.7 | ST32/12 | 5.5107 | 6.3178 | 7.1097 | 7.8941 | 8.6526 | 9.1952 | 9.6506 | 10.103 | 10.5372 | 7.4959
[13 empty] | ST 11 | 22.6 | ST12/22 | 17.0547 | 18.1562 | 18.6918 | 19.0758 | 19.6304 | 20.1967 | 20.7741 | 21.3704 | 21.9839 | 25.6912
[13 empty] | ST 12 | 14.6 | GVE13/21/COO21/ST11/KLO22 | 8.9979 | 10.0254 | 10.7867 | 11.4693 | 12.1609 | 12.7145 | 13.2059 | 13.7022 | 14.191 | 36.5576
[13 empty] | ST 22 | 22.482 | KLO22/ST11/33 | 10.0695 | 12.8225 | 14.9455 | 16.5547 | 17.5198 | 18.518 | 19.5494 | 20.6257 | 21.7453 | 34.3271
[13 empty] | ST 32 | 12.6 | GVE21/COO21 | 4.6262 | 4.7599 | 4.926 | 5.1144 | 5.4217 | 5.6782 | 5.9388 | 6.202 | 6.4684 | 10.7807
[13 empty] | ST 33 | 12.5 | GVE21/ST22 | 6.9254 | 7.2653 | 7.529 | 7.7682 | 8.0029 | 8.2407 | 8.4813 | 8.7285 | 8.9815 | 11.1772
[13 empty] | GVE12 new | 13.7 | KLO22 | 5.2046 | 6.5513 | 7.9992 | 9.0223 | 10.1699 | 11.1912 | 12.1462 | 13.1114 | 13.9401
[13 empty] | GVE22 new | 14.5 | KLO22 | 5.2046 | 6.5513 | 7.9992 | 9.0223 | 10.1699 | 11.1912 | 12.1462 | 13.1114 | 13.9401
[13 empty] | KLO22 | 14.2894 | COO11/GVE12/22/ST22/12 | 5.8541 | 7.2616 | 8.5517 | 9.4924 | 10.3236 | 11.1004 | 11.8529 | 12.6225 | 13.3355 | 34.8504
[13 empty] | BD 08 | 14.3 | BD13 | 10.7176 | 11.1369 | 11.2532 | 11.2573 | 11.2809 | 11.3015 | 11.3186 | 11.3373 | 11.3562
Option 2 & 3
[13 empty] | BD 08 | 11.6221 | BD 13 | 9.7176 | 10.1369 | 10.2532 | 10.2573 | 10.2809 | 10.3015 | 10.3186 | 10.3373 | 10.3562 | 11.3562
[13 empty] | BD 09 | 13.1463 | ST 24 | 12.6781 | 13.4281 | 13.948 | 14.4727 | 14.5403 | 14.6129 | 14.6815 | 14.7485 | 14.817 | 6.0695
[13 empty] | BD 13 | 12.0031 | BD 08 | 10.6265 | 10.8858 | 11.1123 | 11.2252 | 11.3561 | 11.4845 | 11.6101 | 11.7377 | 11.8657 | 10.8657
[13 empty] | COO11 | 10.86 | KLO22 | 4.8654 | 5.0479 | 5.172 | 5.2946 | 5.4488 | 5.6039 | 5.7596 | 5.9185 | 6.0801 | 6.5801
[13 empty] | COO13 | 12.0031 | COO21 | 7.4356 | 7.4299 | 7.4278 | 7.4305 | 7.4462 | 7.4597 | 7.471 | 7.4834 | 7.4959 | -0.0085708
[13 empty] | COO22 | 12.0031 | ST 21 | 4.0816 | 4.1812 | 4.2643 | 4.3541 | 4.47 | 4.5865 | 4.7035 | 4.8229 | 4.9443 | 9.8886
[13 empty] | COO23 | 14.2894 | COO21 | 6.4197 | 7.3922 | 8.0886 | 8.5328 | 9.0283 | 9.3635 | 9.6983 | 10.0297 | 10.359 | 20.718
[13 empty] | COO24 | 12.1936 | ST 21 | 4.456 | 4.543 | 4.6354 | 4.7331 | 4.8591 | 4.9857 | 5.1129 | 5.2427 | 5.3747 | 10.7493
[13 empty] | KLO13 | 14.5 | KLO23 | 7.2425 | 8.0221 | 8.4646 | 8.7883 | 9.3164 | 9.757 | 10.2049 | 10.6571 | 11.1149 | 18.5249
[13 empty] | KLO21 | 14.5 | KLO13 | 7.7829 | 9.4675 | 10.8688 | 11.8478 | 12.9231 | 13.5343 | 14.1556 | 14.7828 | 15.4179 | 30.8357
[13 empty] | KLO23 reconfigured | 24 | KLO13/21 | 13.9955 | 16.2344 | 17.9704 | 19.2108 | 20.7087 | 21.6867 | 22.6821 | 23.6896 | 24.7117 | 1.8839
[13 empty] | ST 24 | 14.2894 | BD 09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7446
[13 empty] | ST 21 | 14.2894 | COO24/22 | 10.011 | 10.1955 | 10.3695 | 10.556 | 10.7981 | 11.0411 | 11.2844 | 11.5332 | 11.786 | 1.4671

## Summer 50PoE
Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 3.859% | Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
ST | 79.7 | 77.495 | 82.1532 | 87.1991 | 91.6347 | 94.7408 | 96.9857 | 99.4867 | 102.2509 | 104.8863 | 107.5035 | 9.295% | BD 01 | 14.2894 | 7.5856 | 9.0369 | 10.4003 | 10.9179 | 10.9678 | 11.0998 | 11.256 | 11.4361 | 11.5969 | 11.7508
KLO | 49.1 | 25.6297 | 30.0735 | 33.4549 | 36.4663 | 38.2787 | 39.8222 | 41.5109 | 43.3536 | 45.1917 | 47.071 | 2.267% | BD 02 | 22.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BD | 123.7 | 71.7808 | 75.1083 | 77.9443 | 80.0467 | 80.5843 | 81.5683 | 82.7324 | 84.0761 | 85.2768 | 86.4267 | 2.465% | BD 04 | 11.6 | 6.222 | 6.5279 | 6.9122 | 7.2318 | 7.3374 | 7.4999 | 7.6813 | 7.8821 | 8.0727 | 8.2615
COO | 38 | 42.6229 | 44.0752 | 45.1811 | 46.071 | 46.6152 | 47.5712 | 48.646 | 49.8418 | 50.9678 | 52.078 | 1.002% | BD 06 | 22.482 | 0 | 0.80411 | 1.8679 | 2.6858 | 2.698 | 2.7305 | 2.7689 | 2.8132 | 2.8528 | 2.8907
BMS | 38 | 34.8794 | 35.0148 | 35.2153 | 35.5011 | 35.6468 | 36.0438 | 36.5189 | 37.0715 | 37.5601 | 38.0253 |  | BD 08 | 11.6221 | 8.9123 | 9.3571 | 9.7377 | 9.9173 | 9.9626 | 10.0826 | 10.2244 | 10.388 | 10.534 | 10.6738
SMTS-ST-SSS-SMTS | 117.2 | 77.495 | 82.1532 | 87.1991 | 91.6347 | 94.7408 | 96.9857 | 99.4867 | 102.2509 | 104.8863 | 107.5217 |  | BD 09 | 13.1463 | 4.097 | 4.3162 | 4.4919 | 4.5213 | 4.5419 | 4.5966 | 4.6613 | 4.7359 | 4.8025 | 4.8662
TTS-COO-VCO-BD-BMS-TTS | 196.3 | 175.1101 | 179.7955 | 183.8387 | 187.2633 | 188.5823 | 191.1772 | 194.2041 | 197.6639 | 200.8002 | 203.9365 |  | BD 13 | 12.0031 | 7.9476 | 8.1223 | 8.2292 | 8.3839 | 8.4222 | 8.5237 | 8.6436 | 8.7819 | 8.9053 | 9.0235
VCO |  | 25.8271 | 25.5973 | 25.4979 | 25.6445 | 25.7359 | 25.9939 | 26.3069 | 26.6745 | 26.9955 | 27.2992 |  | BD 14 | 12.0031 | 8.9883 | 8.9119 | 8.8827 | 8.9409 | 8.9817 | 9.0899 | 9.2178 | 9.3652 | 9.4969 | 9.6229
COO Bus No.1 | 33 | 10.3338 | 10.8534 | 11.2393 | 11.2967 | 11.3622 | 11.5389 | 11.7677 | 12.0241 | 12.2618 | 12.4939 | N | COO11 | 10.86 | 5.1521 | 5.29 | 5.3639 | 5.4296 | 5.4791 | 5.5894 | 5.7133 | 5.851 | 5.9807 | 6.1084
COO Bus No.2 | 33 | 32.2891 | 33.2219 | 33.9417 | 34.7743 | 35.253 | 36.0323 | 36.8782 | 37.8177 | 38.706 | 39.584 | 43.4158 | COO12 | 14.3 | 6.2619 | 7.0678 | 7.6818 | 7.7964 | 7.8852 | 8.0439 | 8.2222 | 8.4204 | 8.607 | 8.7908
Feeder - ZSS Diversity Factor |  | 0.90604 | 0.87887 | 0.8621 | 0.85469 | 0.85075 | 0.84694 | 0.845 | 0.84308 | 0.84111 | 0.83911 |  | COO13 | 12.0031 | 0.0052948 | 0.0052458 | 0.0052459 | 0.0052874 | 0.0053799 | 0.0054946 | 0.0056194 | 0.0057491 | 0.0058687 | 0.0059883
[13 empty] | COO14 | 12.0031 | -0.01393 | -0.0138 | -0.013801 | -0.01391 | -0.014153 | -0.014455 | -0.014783 | -0.015124 | -0.015439 | -0.015754
[13 empty] | COO21 | 14.2894 | 4.5541 | 4.5154 | 4.5006 | 4.5301 | 4.5508 | 4.6056 | 4.6704 | 4.7451 | 4.8118 | 4.8757
[13 empty] | COO22 | 12.0031 | 8.528 | 8.5624 | 8.6 | 8.684 | 8.7586 | 8.9348 | 9.1328 | 9.353 | 9.5603 | 9.7645
[13 empty] | COO23 | 14.2894 | 12.9025 | 15.132 | 16.6822 | 17.7859 | 18.3587 | 19.0377 | 19.6523 | 20.3254 | 20.9814 | 21.6418
[13 empty] | COO24 | 12.1936 | 9.6528 | 9.5907 | 9.5882 | 9.6865 | 9.7697 | 9.9663 | 10.1872 | 10.4328 | 10.6639 | 10.8917
[13 empty] | KLO13 | 14.2894 | 10.8607 | 13.9056 | 15.0492 | 15.6179 | 15.9087 | 16.5502 | 17.252 | 18.0178 | 18.7817 | 19.5628
[13 empty] | KLO21 | 14.2894 | 10.3392 | 12.8725 | 15.2973 | 17.272 | 18.4722 | 19.7731 | 20.6116 | 21.5266 | 22.4392 | 23.3724
[13 empty] | KLO22 | 14.2894 | 9.2549 | 12.0477 | 14.8213 | 17.8038 | 19.7038 | 21.7976 | 23.8759 | 25.8765 | 27.8823 | 29.6057
[13 empty] | KLO23 | 14.2894 | 1.1082 | 1.1049 | 1.1106 | 1.1304 | 1.1514 | 1.1978 | 1.2486 | 1.304 | 1.3593 | 1.4159
[13 empty] | ST 11 | 22.482 | 13.7005 | 14.4372 | 15.3534 | 15.7768 | 15.9914 | 16.4747 | 17.0065 | 17.589 | 18.1568 | 18.7282
[13 empty] | ST 12 | 14.2894 | 12.591 | 14.8651 | 17.8783 | 20.7443 | 23.3731 | 25.5348 | 27.1869 | 28.5349 | 29.8497 | 31.091
[13 empty] | ST 13 | 14.2894 | 8.6507 | 9.5996 | 10.4786 | 10.8632 | 10.9565 | 11.1769 | 11.4247 | 11.7001 | 11.9594 | 12.2148
[13 empty] | ST 14 | 14.2894 | 7.4441 | 7.3868 | 7.3713 | 8.1629 | 8.9506 | 9.8359 | 10.0141 | 10.2149 | 10.3999 | 10.58
[13 empty] | ST 21 | 14.2894 | 1.2891 | 1.2776 | 1.2726 | 1.2799 | 1.2845 | 1.2974 | 1.313 | 1.3313 | 1.3474 | 1.3625
[13 empty] | ST 22 | 22.482 | 13.9865 | 16.9972 | 19.9354 | 22.2325 | 23.8282 | 24.789 | 25.8402 | 26.9873 | 28.1314 | 29.3013
[13 empty] | ST 23 | 22.482 | 10.8143 | 11.9163 | 13.1845 | 13.5417 | 13.6239 | 13.8293 | 14.0658 | 14.3337 | 14.5787 | 14.8164
[13 empty] | ST 24 | 14.2894 | 6.8504 | 7.2242 | 7.6293 | 8.1088 | 8.1377 | 8.2193 | 8.3183 | 8.4345 | 8.536 | 8.632
[13 empty] | ST 31 | 22.482 | 1.6942 | 1.6791 | 1.6726 | 1.6822 | 1.6882 | 1.7051 | 1.7257 | 1.7498 | 1.7708 | 1.7908
[13 empty] | ST 32 | 12.3842 | 7.3961 | 7.5991 | 7.6377 | 7.7738 | 7.9186 | 8.2379 | 8.5872 | 8.9684 | 9.3486 | 9.7374
[13 empty] | ST 33 | 12.5 | 9.1881 | 9.2123 | 9.2696 | 9.3602 | 9.4405 | 9.6305 | 9.8439 | 10.0813 | 10.3047 | 10.5248
[13 empty] | ST 34 | 14.2894 | 11.7832 | 12.3824 | 12.5938 | 12.8577 | 12.968 | 13.229 | 13.5222 | 13.8482 | 14.1551 | 14.4574
ZSS/SubT Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 |  | Feeder Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2034 do nothing check
Option 2 | [12 empty] | Option 2
ST | 79.7 |  | 58.0119 | 60.3268 | 62.2504 | 63.6231 | 64.7298 | 66.1773 | 67.9594 | 69.6347 | 71.3134 |  | CBN11 new | 14.3 | 4.6 | 9.0595 | 9.9635 | 10.8233 | 11.6119 | 12.2604 | 12.7561 | 13.1605 | 13.5549 | 13.9273
KLO | 49.1 |  | 23.6304 | 25.5807 | 27.0028 | 27.8082 | 28.2459 | 28.8195 | 29.5947 | 30.3683 | 31.3429 |  | CBN22 new | 12.7 | 4.2 | 7.6345 | 8.3639 | 9.092 | 9.6763 | 10.21 | 10.6656 | 11.0679 | 11.4657 | 11.8242
BD | 123.7 |  | 81.1289 | 84.1723 | 86.5674 | 87.4829 | 88.4604 | 89.6777 | 91.0891 | 92.3711 | 93.5894 |  | CBN13 new | 12.7 | 2.5 | 5.5119 | 6.2053 | 6.951 | 7.4259 | 7.9494 | 8.469 | 8.9691 | 9.4706 | 9.9014
COO | 38 |  | 37.6809 | 38.3277 | 38.9736 | 38.9897 | 40.1745 | 41.0936 | 42.2192 | 43.1276 | 44.0694 |  | CBN21 new | 12.7 | KLO22 | 3.6143 | 4.4464 | 5.3411 | 5.9111 | 6.5393 | 7.1628 | 7.7629 | 8.3647 | 8.8817
BMS | 38 |  | 35.0148 | 35.2153 | 35.5011 | 35.6468 | 36.0438 | 36.5189 | 37.0715 | 37.5601 | 38.0253 |  | COO21 | 14.2894 | COO23 | 7.5713 | 8.3463 | 8.8982 | 9.1847 | 9.5243 | 9.8318 | 10.1684 | 10.4966 | 10.8269 | 4.8757
SMTS-ST-SSS-SMTS | 117.2 |  | 90.6636 | 96.7672 | 102.4456 | 106.595 | 110.0282 | 113.7344 | 117.6609 | 121.4559 | 125.0744 |  | ST 11 | 22.482 | -4 | 10.4372 | 11.3534 | 11.7768 | 11.9914 | 12.4747 | 13.0065 | 13.589 | 14.1568 | 14.7282 | 18.7282
TTS-COO-VCO-BD-BMS-TTS | 196.3 |  | 179.4218 | 183.2133 | 186.6866 | 187.8553 | 190.6726 | 193.5971 | 197.0543 | 200.0544 | 202.9833 |  | ST 12 | 14.2894 | CBN11/22 | 6.6893 | 8.0452 | 9.335 | 10.5179 | 11.4907 | 12.2341 | 12.8407 | 13.4324 | 13.991 | 31.091
CBN | 38 |  | 32.6517 | 36.4403 | 40.1952 | 42.9719 | 45.2985 | 47.557 | 49.7015 | 51.8212 | 53.761 |  | ST 22 | 22.482 | CBN | 1.4657 | 2.4451 | 3.2108 | 3.7427 | 4.063 | 4.4134 | 4.7958 | 5.1771 | 5.5671 | 29.3013
COO Bus No.1 | 33 |  | 14.3778 | 14.6837 | 14.7367 | 14.8038 | 15.0114 | 15.287 | 15.5983 | 15.8836 | 16.1606 | N | ST 32 | 12.3842 | Nil | 7.5991 | 7.6377 | 7.7738 | 7.9186 | 8.2379 | 8.5872 | 8.9684 | 9.3486 | 9.7374 | 9.7374
COO Bus No.2 | 33 |  | 21.2809 | 22.2263 | 23.0564 | 23.5046 | 24.1323 | 24.7737 | 25.4814 | 26.1582 | 26.8314 | 52.876 | ST 33 | 12.5 | -3.1 | 7.5988 | 7.9574 | 8.3346 | 8.6778 | 9.084 | 9.4626 | 9.8348 | 10.1896 | 10.5339 | 10.5248
[13 empty] | CBN12 new | 14.3 | ST22 | 5.6657 | 6.6451 | 7.4108 | 7.9427 | 8.263 | 8.6134 | 8.9958 | 9.3771 | 9.7671
Option 3 | [12 empty] | CBN23 new | 14.3 | ST22 | 5.6657 | 6.6451 | 7.4108 | 7.9427 | 8.263 | 8.6134 | 8.9958 | 9.3771 | 9.7671
ST | 79.7 |  | 65.0623 | 67.355 | 69.081 | 70.0879 | 70.6486 | 71.7575 | 73.3251 | 74.8009 | 76.3136 |  | KLO22 | 14.2894 | COO11 | 4.7167 | 5.6874 | 6.7313 | 7.3963 | 8.1292 | 8.8566 | 9.5568 | 10.2588 | 10.862 | 29.6057
KLO | 49.1 |  | 24.151 | 26.2392 | 27.666 | 28.4974 | 28.8288 | 29.3152 | 30.0297 | 30.7417 | 31.6948 |  | BD 08 | 14.3 | BD13 | 9.3571 | 9.7377 | 9.9173 | 9.9626 | 10.0826 | 10.2244 | 10.388 | 10.534 | 10.6738
BD | 123.7 |  | 81.1289 | 84.1723 | 86.5674 | 87.4829 | 88.4604 | 89.6777 | 91.0891 | 92.3711 | 93.5894
COO | 38 |  | 33.6256 | 34.7771 | 35.7317 | 36.497 | 37.5003 | 38.5291 | 39.5915 | 40.5983 | 41.581
BMS | 38 |  | 35.0148 | 35.2153 | 35.5011 | 35.6468 | 36.0438 | 36.5189 | 37.0715 | 37.5601 | 38.0253
SMTS-ST-SSS-SMTS | 117.2 |  | 92.1807 | 98.2461 | 103.8484 | 107.7218 | 111.0936 | 114.775 | 118.7189 | 122.5309 | 126.1384
TTS-COO-VCO-BD-BMS-TTS | 196.3 |  | 175.3665 | 179.6627 | 183.4447 | 185.3627 | 187.9984 | 191.0326 | 194.4266 | 197.5251 | 200.4949
GVE | 38 |  | 27.1184 | 30.8911 | 34.7674 | 37.6339 | 40.445 | 43.0175 | 45.3939 | 47.7301 | 49.8248
COO Bus No.1 | 33 |  | 14.3778 | 14.6837 | 14.7367 | 14.8038 | 15.0114 | 15.287 | 15.5983 | 15.8836 | 16.1606 | N
COO Bus No.2 | 33 |  | 19.2478 | 20.0933 | 20.995 | 21.6932 | 22.4888 | 23.2421 | 23.9932 | 24.7147 | 25.4204 | 53.9792
Option 3
[13 empty] | GVE11 new | 12.7 | COO21 new | 7.5713 | 8.3463 | 8.8982 | 9.1847 | 9.5243 | 9.8318 | 10.1684 | 10.4966 | 10.8269
[13 empty] | GVE21 new | 13.7 | ST12/32/33 | 7.7005 | 8.4777 | 9.2395 | 9.9393 | 10.5782 | 11.1008 | 11.559 | 12.0039 | 12.4302
[13 empty] | GVE13 new | 13.7 | ST12 | 5.946 | 7.1513 | 8.2977 | 9.3492 | 10.2139 | 10.8748 | 11.414 | 11.9399 | 12.4364
[13 empty] | COO21 Option 3 | 12.7 | ST32/12 | 5.258 | 5.8722 | 6.4863 | 7.0556 | 7.5838 | 8.0192 | 8.4033 | 8.7804 | 9.1454 | 4.8757
[13 empty] | ST 11 | 22.482 | ST12/22 | 14.106 | 14.7473 | 15.0437 | 15.194 | 15.5323 | 15.9046 | 16.3123 | 16.7097 | 17.1097 | 18.7282
[13 empty] | ST 12 | 14.2894 | GVE13/21/COO21/ST11/KLO22 | 7.5609 | 8.2877 | 8.8447 | 9.3034 | 9.7726 | 10.18 | 10.557 | 10.9245 | 11.2821 | 31.091
[13 empty] | ST 22 | 22.482 | KLO22/ST11/33 | 8.7479 | 10.9515 | 12.6744 | 13.8711 | 14.5918 | 15.3801 | 16.2405 | 17.0986 | 17.976 | 29.3013
[13 empty] | ST 32 | 12.3842 | GVE21/COO21 | 4.5595 | 4.5826 | 4.6643 | 4.7511 | 4.9427 | 5.1523 | 5.381 | 5.6092 | 5.8424 | 9.7374
[13 empty] | ST 33 | 12.5 | GVE21/ST22 | 6.8378 | 7.022 | 7.1957 | 7.3277 | 7.4993 | 7.6906 | 7.9022 | 8.1046 | 8.3062 | 10.5248
[13 empty] | GVE12 new | 13.7 | KLO22 | 4.8191 | 5.9285 | 7.1215 | 7.8815 | 8.7191 | 9.5504 | 10.3506 | 11.1529 | 11.8423
[13 empty] | GVE22 new | 13.7 | KLO22 | 4.8191 | 5.9285 | 7.1215 | 7.8815 | 8.7191 | 9.5504 | 10.3506 | 11.1529 | 11.8423
[13 empty] | KLO22 | 14.2894 | COO11/GVE12/22/ST22/12 | 5.309 | 6.4513 | 7.5073 | 8.2064 | 8.8173 | 9.4432 | 10.0727 | 10.7027 | 11.2814 | 29.6057
[13 empty] | BD 08 | 14.3 | BD13 | 9.3571 | 9.7377 | 9.9173 | 9.9626 | 10.0826 | 10.2244 | 10.388 | 10.534 | 10.6738
Option 2 & 3
[13 empty] | BD 08 | 11.6221 | BD 13 | 8.3571 | 8.7377 | 8.9173 | 8.9626 | 9.0826 | 9.2244 | 9.388 | 9.534 | 9.6738 | 10.6738
[13 empty] | BD 09 | 13.1463 | ST 24 | 11.1666 | 11.7161 | 12.1506 | 12.6508 | 12.7344 | 12.8806 | 13.0542 | 13.237 | 13.4022 | 4.8662
[13 empty] | BD 13 | 12.0031 | BD 08 | 9.1223 | 9.2292 | 9.3839 | 9.4222 | 9.5237 | 9.6436 | 9.7819 | 9.9053 | 10.0235 | 9.0235
[13 empty] | COO11 | 10.86 | KLO22 | 4.79 | 4.8639 | 4.9296 | 4.9791 | 5.0894 | 5.2133 | 5.351 | 5.4807 | 5.6084 | 6.1084
[13 empty] | COO13 | 12.0031 | COO21 | 4.5154 | 4.5006 | 4.5301 | 4.5508 | 4.6056 | 4.6704 | 4.7451 | 4.8118 | 4.8757 | 0.0059883
[13 empty] | COO22 | 12.0031 | ST 21 | 4.2812 | 4.3 | 4.342 | 4.3793 | 4.4674 | 4.5664 | 4.6765 | 4.7801 | 4.8822 | 9.7645
[13 empty] | COO23 | 14.2894 | COO21 | 7.566 | 8.3411 | 8.8929 | 9.1794 | 9.5188 | 9.8261 | 10.1627 | 10.4907 | 10.8209 | 21.6418
[13 empty] | COO24 | 12.1936 | ST 21 | 4.7953 | 4.7941 | 4.8433 | 4.8848 | 4.9831 | 5.0936 | 5.2164 | 5.332 | 5.4459 | 10.8917
[13 empty] | KLO13 | 14.2894 | KLO23 | 8.3434 | 9.0295 | 9.3707 | 9.5452 | 9.9301 | 10.3512 | 10.8107 | 11.269 | 11.7377 | 19.5628
[13 empty] | KLO21 | 14.2894 | KLO13 | 6.4362 | 7.6486 | 8.636 | 9.2361 | 9.8866 | 10.3058 | 10.7633 | 11.2196 | 11.6862 | 23.3724
[13 empty] | KLO23 reconfigured | 24 | KLO13/21 | 13.1034 | 14.7789 | 16.0135 | 16.751 | 17.7045 | 18.4552 | 19.2745 | 20.0916 | 20.9271 | 1.4159
[13 empty] | ST 24 | 14.2894 | BD 09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.632
[13 empty] | ST 21 | 14.2894 | COO24/22 | 10.3541 | 10.3667 | 10.4652 | 10.5486 | 10.7479 | 10.973 | 11.2243 | 11.4595 | 11.6906 | 1.3625

## Winter 50PoE
Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 4.489% | Option 1 - Do Nothing | Rating | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
ST | 89.3 | 78.4801 | 84.0416 | 89.936 | 94.5664 | 98.1622 | 100.4868 | 102.6465 | 104.8319 | 107.0288 | 109.2432 | 11.68% | BD 01 | 14.2894 | 7.6751 | 9.3284 | 10.8965 | 11.4976 | 11.6334 | 11.7811 | 11.9294 | 12.0783 | 12.2277 | 12.3776
KLO | 49.1 | 25.2401 | 30.4324 | 34.6428 | 38.3535 | 40.9837 | 43.3079 | 45.3548 | 47.459 | 49.5953 | 51.7738 | 2.558% | BD 02 | 22.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BD | 125.1 | 74.8055 | 79.4407 | 83.3388 | 85.806 | 86.898 | 87.9154 | 88.9371 | 89.963 | 90.9933 | 92.0278 | 3.687% | BD 04 | 11.6 | 5.4466 | 5.8667 | 6.3437 | 6.7107 | 6.8974 | 7.0943 | 7.295 | 7.4995 | 7.7078 | 7.9201
COO | 39.6 | 33.1319 | 35.4323 | 37.231 | 38.4088 | 39.3417 | 40.3832 | 41.3614 | 42.1566 | 43.1371 | 44.1252 | 1.267% | BD 06 | 22.482 | 0 | 0.75497 | 1.7978 | 2.6312 | 2.6959 | 2.7799 | 2.8328 | 2.8837 | 2.9306 | 2.9744
BMS | 39.6 | 33.6341 | 34.3748 | 35.0153 | 35.4055 | 35.7333 | 36.0794 | 36.426 | 36.7733 | 37.1213 | 37.4699 |  | BD 08 | 11.6221 | 9.7292 | 10.2493 | 10.665 | 10.7882 | 10.799 | 10.8207 | 10.8424 | 10.8641 | 10.8858 | 10.9077
SMTS-ST-SSS-SMTS | 126.3 | 78.4801 | 84.0416 | 89.936 | 94.5664 | 98.1622 | 100.4868 | 102.6465 | 104.8319 | 107.0288 | 109.2258 |  | BD 09 | 13.1463 | 4.7144 | 5.0673 | 5.3525 | 5.4153 | 5.4792 | 5.5488 | 5.6186 | 5.6888 | 5.7591 | 5.8297
TTS-COO-VCO-BD-BMS-TTS | 217.339 | 169.3581 | 177.0352 | 183.3731 | 187.4086 | 189.7616 | 192.1666 | 194.5132 | 196.6818 | 199.0406 | 201.3994 |  | BD 13 | 12.0031 | 8.8291 | 9.2059 | 9.4669 | 9.6945 | 9.809 | 9.9335 | 10.0586 | 10.1841 | 10.3101 | 10.4365
VCO |  | 27.7866 | 27.7874 | 27.788 | 27.7884 | 27.7886 | 27.7887 | 27.7888 | 27.7889 | 27.789 | 27.7891 |  | BD 14 | 12.0031 | 8.8289 | 8.9312 | 9.0353 | 9.1413 | 9.2493 | 9.3667 | 9.4846 | 9.603 | 9.7218 | 9.841
COO Bus No.1 | 33 | 8.9026 | 9.6925 | 10.3098 | 10.4891 | 10.6867 | 10.9052 | 11.166 | 11.3783 | 11.6442 | 11.9148 | N | COO11 | 10.86 | 4.8676 | 5.131 | 5.3128 | 5.4376 | 5.5587 | 5.7061 | 5.856 | 6.0082 | 6.1629 | 6.3201
COO Bus No.2 | 33 | 24.2293 | 25.7399 | 26.9211 | 27.9197 | 28.655 | 29.4779 | 30.1954 | 30.7783 | 31.4929 | 32.2104 | 45.2069 | COO12 | 14.3 | 7.1848 | 8.3248 | 9.2391 | 9.4811 | 9.7139 | 9.9716 | 10.2334 | 10.4995 | 10.7698 | 11.0445
Feeder - ZSS Diversity Factor |  | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 |  | COO13 | 12.0031 | -0.0056974 | -0.0058972 | -0.0061409 | -0.0064164 | -0.0067208 | -0.0070682 | -0.0072721 | -0.0074961 | -0.0077083 | -0.0079205
[13 empty] | COO14 | 12.0031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | COO21 | 14.2894 | 7.1076 | 7.1107 | 7.1151 | 7.1209 | 7.1281 | 7.1424 | 7.1567 | 7.171 | 7.1854 | 7.1998
[13 empty] | COO22 | 12.0031 | 7.5708 | 7.8065 | 8.0081 | 8.1762 | 8.3537 | 8.5753 | 8.8005 | 9.0293 | 9.2618 | 9.498
[13 empty] | COO23 | 14.2894 | 9.7528 | 12.2785 | 14.1581 | 15.5087 | 16.371 | 17.3199 | 17.9663 | 18.6178 | 19.2606 | 19.8996
[13 empty] | COO24 | 12.1936 | 8.3551 | 8.5226 | 8.7009 | 8.8878 | 9.0808 | 9.3217 | 9.5664 | 9.8151 | 10.0679 | 10.3247
[13 empty] | KLO13 | 14.5 | 8.7614 | 11.5434 | 12.8036 | 13.5247 | 14.0509 | 14.8938 | 15.6011 | 16.3253 | 17.0545 | 17.7931
[13 empty] | KLO21 | 14.5 | 11.6106 | 14.8857 | 18.1327 | 20.8393 | 22.7311 | 24.7916 | 25.9689 | 27.1744 | 28.3883 | 29.6177
[13 empty] | KLO22 | 14.2894 | 9.2887 | 12.4429 | 15.6843 | 19.1717 | 21.6377 | 24.3874 | 26.8415 | 29.1462 | 31.4731 | 33.4737
[13 empty] | KLO23 | 14.2894 | 1.2932 | 1.3238 | 1.3587 | 1.3983 | 1.4429 | 1.5105 | 1.5808 | 1.6541 | 1.7302 | 1.8095
[13 empty] | ST 11 | 22.6 | 16.4869 | 17.8347 | 19.3662 | 20.1209 | 20.6602 | 21.4182 | 22.1982 | 23.0008 | 23.8267 | 24.6764
[13 empty] | ST 12 | 14.6 | 12.601 | 15.3204 | 18.8874 | 22.3069 | 25.6338 | 28.5336 | 30.5277 | 32.1036 | 33.656 | 35.1135
[13 empty] | ST 13 | 14.2894 | 9.5688 | 10.713 | 11.7389 | 12.1002 | 12.1608 | 12.2825 | 12.4053 | 12.5294 | 12.6548 | 12.7814
[13 empty] | ST 14 | 14.2894 | 6.7103 | 6.7185 | 6.7307 | 7.4106 | 8.0965 | 8.8088 | 8.8617 | 8.9149 | 8.9684 | 9.0222
[13 empty] | ST 21 | 14.2894 | 1.409 | 1.409 | 1.4091 | 1.4091 | 1.4091 | 1.4091 | 1.4091 | 1.4091 | 1.4091 | 1.4091
[13 empty] | ST 22 | 22.482 | 14.3856 | 17.9396 | 21.4797 | 24.2168 | 26.2907 | 27.5224 | 28.8043 | 30.1384 | 31.5267 | 32.9711
[13 empty] | ST 23 | 22.482 | 10.5335 | 11.8415 | 13.2976 | 13.728 | 13.911 | 14.1298 | 14.3505 | 14.5731 | 14.7975 | 15.0238
[13 empty] | ST 24 | 14.2894 | 7.0449 | 7.4963 | 7.9477 | 8.399 | 8.3991 | 8.3991 | 8.3991 | 8.3991 | 8.3992 | 8.3992
[13 empty] | ST 31 | 22.482 | 2.2087 | 2.2087 | 2.2088 | 2.2088 | 2.2088 | 2.2089 | 2.2089 | 2.2089 | 2.2089 | 2.2089
[13 empty] | ST 32 | 12.6 | 6.9693 | 7.3735 | 7.597 | 7.8708 | 8.177 | 8.6676 | 9.0792 | 9.5006 | 9.925 | 10.3548
[13 empty] | ST 33 | 12.5 | 8.5578 | 8.809 | 9.0516 | 9.2416 | 9.4423 | 9.6927 | 9.9472 | 10.2058 | 10.4686 | 10.7357
[13 empty] | ST 34 | 14.2894 | 12.5972 | 13.3564 | 13.6375 | 13.8437 | 13.913 | 14.0522 | 14.1928 | 14.3348 | 14.4781 | 14.623
ZSS/SubT Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 |  | Feeder Solutions Applied | Rating | Xfer | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2034 do nothing check
Option 2 | [12 empty] | Option 2
ST | 89.3 |  | 58.9787 | 61.2806 | 62.8192 | 64.1246 | 64.8387 | 65.7089 | 66.7384 | 67.7611 | 68.809 |  | CBN11 new | 14.3 | 4.6 | 9.1961 | 10.2662 | 11.2921 | 12.2902 | 13.1601 | 13.7583 | 14.2311 | 14.6968 | 15.1341
KLO | 49.1 |  | 23.9827 | 26.4023 | 28.1861 | 29.4538 | 30.2588 | 30.9498 | 31.7807 | 32.6313 | 33.7046 |  | CBN22 new | 12.7 | 4.2 | 7.7423 | 8.6015 | 9.4632 | 10.2088 | 10.9188 | 11.4633 | 11.9302 | 12.3957 | 12.8144
BD | 125.1 |  | 85.4289 | 89.7106 | 92.5615 | 94.0372 | 95.0546 | 96.0763 | 97.1023 | 98.1326 | 99.1671 |  | CBN13 new | 12.7 | 2.5 | 5.6107 | 6.4211 | 7.2929 | 7.9094 | 8.5969 | 9.2104 | 9.7865 | 10.3683 | 10.8684
COO | 39.6 |  | 30.7833 | 31.7834 | 32.2921 | 32.6637 | 33.6888 | 34.2186 | 34.8238 | 35.5993 | 36.3835 |  | CBN21 new | 12.7 | KLO22 | 3.7329 | 4.7053 | 5.7515 | 6.4913 | 7.3162 | 8.0525 | 8.7439 | 9.4419 | 10.0421
BMS | 39.6 |  | 34.3748 | 35.0153 | 35.4055 | 35.7333 | 36.0794 | 36.426 | 36.7733 | 37.1213 | 37.4699 |  | COO21 | 14.2894 | COO23 | 6.1333 | 7.0729 | 7.7479 | 8.1788 | 8.6529 | 8.9759 | 9.3014 | 9.6226 | 9.9419 | 7.1998
SMTS-ST-SSS-SMTS | 126.3 |  | 91.4842 | 98.9474 | 105.2718 | 110.3875 | 114.4278 | 118.1431 | 121.8047 | 125.4935 | 129.0228 |  | ST 11 | 22.6 | -4 | 13.8347 | 15.3662 | 16.1209 | 16.6602 | 17.4182 | 18.1982 | 19.0008 | 19.8267 | 20.6764 | 24.6764
TTS-COO-VCO-BD-BMS-TTS | 217.339 |  | 178.3744 | 184.2973 | 188.0475 | 190.2228 | 192.6114 | 194.5097 | 196.4883 | 198.6422 | 200.8096 |  | ST 12 | 14.6 | CBN11/22 | 6.8942 | 8.4993 | 10.0381 | 11.5352 | 12.8401 | 13.7375 | 14.4466 | 15.1452 | 15.8011 | 35.1135
CBN | 39.6 |  | 32.5055 | 37.6668 | 42.4526 | 46.2628 | 49.5892 | 52.4342 | 55.0663 | 57.7324 | 60.2138 |  | ST 22 | 22.482 | CBN | 1.7799 | 2.9599 | 3.8723 | 4.5636 | 4.9741 | 5.4014 | 5.8461 | 6.3089 | 6.7904 | 32.9711
COO Bus No.1 | 33 |  | 17.0565 | 17.992 | 18.3087 | 18.6156 | 18.9721 | 19.3341 | 19.7019 | 20.0754 | 20.4548 | N | ST 32 | 12.6 | Nil | 7.3735 | 7.597 | 7.8708 | 8.177 | 8.6676 | 9.0792 | 9.5006 | 9.925 | 10.3548 | 10.3548
COO Bus No.2 | 33 |  | 17.3716 | 19.1305 | 20.4291 | 21.3193 | 22.3221 | 23.0711 | 23.8276 | 24.58 | 25.3326 | 59.6459 | ST 33 | 12.5 | -3.1 | 7.2411 | 7.8403 | 8.3722 | 8.9057 | 9.4461 | 9.9 | 10.3162 | 10.7342 | 11.147 | 10.7357
[13 empty] | CBN12 new | 14.3 | ST22 | 5.9799 | 7.1599 | 8.0723 | 8.7636 | 9.1741 | 9.6014 | 10.0461 | 10.5089 | 10.9904
Option 3 | [12 empty] | CBN23 new | 14.3 | ST22 | 5.9799 | 7.1599 | 8.0723 | 8.7636 | 9.1741 | 9.6014 | 10.0461 | 10.5089 | 10.9904
ST | 89.3 |  | 66.2132 | 68.5583 | 69.8704 | 70.7035 | 70.6789 | 71.164 | 71.9666 | 72.7897 | 73.6895 |  | KLO22 | 14.2894 | COO11 | 4.855 | 5.9895 | 7.2101 | 8.0732 | 9.0356 | 9.8945 | 10.7012 | 11.5156 | 12.2158 | 33.4737
KLO | 49.1 |  | 24.596 | 27.2041 | 29.0085 | 30.3144 | 30.9782 | 31.5743 | 32.3381 | 33.1281 | 34.1917 |  | BD 08 | 14.3 | BD13 | 10.2493 | 10.665 | 10.7882 | 10.799 | 10.8207 | 10.8424 | 10.8641 | 10.8858 | 10.9077
BD | 125.1 |  | 85.4289 | 89.7106 | 92.5615 | 94.0372 | 95.0546 | 96.0763 | 97.1023 | 98.1326 | 99.1671
COO | 39.6 |  | 27.3338 | 28.8356 | 29.9396 | 30.9923 | 32.0519 | 32.9997 | 33.6904 | 34.5636 | 35.428
BMS | 39.6 |  | 34.3748 | 35.0153 | 35.4055 | 35.7333 | 36.0794 | 36.426 | 36.7733 | 37.1213 | 37.4699
SMTS-ST-SSS-SMTS | 126.3 |  | 91.5996 | 99.0095 | 105.2358 | 110.0359 | 114.0024 | 117.6433 | 121.2732 | 124.9236 | 128.3764
TTS-COO-VCO-BD-BMS-TTS | 217.339 |  | 174.9249 | 181.3495 | 185.695 | 188.5513 | 190.9746 | 193.2908 | 195.3549 | 197.6064 | 199.8541
GVE | 39.6 |  | 25.3864 | 30.4511 | 35.3655 | 39.3324 | 43.3236 | 46.4793 | 49.3066 | 52.1339 | 54.6869
COO Bus No.1 | 33 |  | 17.0565 | 17.992 | 18.3087 | 18.6156 | 18.9721 | 19.3341 | 19.7019 | 20.0754 | 20.4548 | N
COO Bus No.2 | 33 |  | 16.6379 | 18.2614 | 19.6371 | 20.8045 | 22.0221 | 22.9403 | 23.7953 | 24.6467 | 25.485 | 59.4865
Option 3
[13 empty] | GVE11 new | 12.7 | COO21 new | 6.1333 | 7.0729 | 7.7479 | 8.1788 | 8.6529 | 8.9759 | 9.3014 | 9.6226 | 9.9419
[13 empty] | GVE21 new | 13.7 | ST12/32/33 | 7.6506 | 8.6496 | 9.5983 | 10.531 | 11.3926 | 12.0214 | 12.548 | 13.0705 | 13.5713
[13 empty] | GVE13 new | 13.7 | ST12 | 6.1282 | 7.555 | 8.9228 | 10.2535 | 11.4134 | 12.2111 | 12.8414 | 13.4624 | 14.0454
[13 empty] | COO21 Option 3 | 12.7 | ST32/12 | 5.2702 | 6.0504 | 6.8162 | 7.5732 | 8.2999 | 8.822 | 9.2634 | 9.701 | 10.1212 | 7.1998
[13 empty] | ST 11 | 22.6 | ST12/22 | 16.4843 | 17.5563 | 18.0847 | 18.4622 | 18.9927 | 19.5387 | 20.1006 | 20.6787 | 21.2735 | 24.6764
[13 empty] | ST 12 | 14.6 | GVE13/21/COO21/ST11/KLO22 | 8.6485 | 9.643 | 10.3823 | 11.0431 | 11.7055 | 12.2386 | 12.7158 | 13.1964 | 13.6699 | 35.1135
[13 empty] | ST 22 | 22.482 | KLO22/ST11/33 | 9.4547 | 12.1097 | 14.1626 | 15.718 | 16.6418 | 17.6033 | 18.6038 | 19.645 | 20.7283 | 32.9711
[13 empty] | ST 32 | 12.6 | GVE21/COO21 | 4.4241 | 4.5582 | 4.7225 | 4.9062 | 5.2005 | 5.4475 | 5.7004 | 5.955 | 6.2129 | 10.3548
[13 empty] | ST 33 | 12.5 | GVE21/ST22 | 6.6228 | 6.9575 | 7.2179 | 7.452 | 7.6764 | 7.9059 | 8.1407 | 8.3809 | 8.6267 | 10.7357
[13 empty] | GVE12 new | 13.7 | KLO22 | 4.9771 | 6.2737 | 7.6687 | 8.6551 | 9.755 | 10.7366 | 11.6585 | 12.5893 | 13.3895
[13 empty] | GVE22 new | 14.5 | KLO22 | 4.9771 | 6.2737 | 7.6687 | 8.6551 | 9.755 | 10.7366 | 11.6585 | 12.5893 | 13.3895
[13 empty] | KLO22 | 14.2894 | COO11/GVE12/22/ST22/12 | 5.5765 | 6.9328 | 8.1777 | 9.0857 | 9.882 | 10.6292 | 11.3569 | 12.1 | 12.789 | 33.4737
[13 empty] | BD 08 | 14.3 | BD013 | 10.2493 | 10.665 | 10.7882 | 10.799 | 10.8207 | 10.8424 | 10.8641 | 10.8858 | 10.9077
Option 2 & 3
[13 empty] | BD 08 | 11.6221 | BD 13 | 9.2493 | 9.665 | 9.7882 | 9.799 | 9.8207 | 9.8424 | 9.8641 | 9.8858 | 9.9077 | 10.9077
[13 empty] | BD 09 | 13.1463 | ST 24 | 12.1122 | 12.8488 | 13.3629 | 13.8782 | 13.9479 | 14.0177 | 14.0879 | 14.1583 | 14.2289 | 5.8297
[13 empty] | BD 13 | 12.0031 | BD 08 | 10.2059 | 10.4669 | 10.6945 | 10.809 | 10.9335 | 11.0586 | 11.1841 | 11.3101 | 11.4365 | 10.4365
[13 empty] | COO11 | 10.86 | KLO22 | 4.631 | 4.8128 | 4.9376 | 5.0587 | 5.2061 | 5.356 | 5.5082 | 5.6629 | 5.8201 | 6.3201
[13 empty] | COO13 | 12.0031 | COO21 | 7.1107 | 7.1151 | 7.1209 | 7.1281 | 7.1424 | 7.1567 | 7.171 | 7.1854 | 7.1998 | -0.0079205
[13 empty] | COO22 | 12.0031 | ST 21 | 3.9032 | 4.004 | 4.0881 | 4.1769 | 4.2876 | 4.4002 | 4.5146 | 4.6309 | 4.749 | 9.498
[13 empty] | COO23 | 14.2894 | COO21 | 6.1392 | 7.079 | 7.7544 | 8.1855 | 8.66 | 8.9831 | 9.3089 | 9.6303 | 9.9498 | 19.8996
[13 empty] | COO24 | 12.1936 | ST 21 | 4.2613 | 4.3505 | 4.4439 | 4.5404 | 4.6608 | 4.7832 | 4.9076 | 5.0339 | 5.1623 | 10.3247
[13 empty] | KLO13 | 14.5 | KLO23 | 6.926 | 7.6822 | 8.1148 | 8.4306 | 8.9363 | 9.3606 | 9.7952 | 10.2327 | 10.6759 | 17.7931
[13 empty] | KLO21 | 14.5 | KLO13 | 7.4429 | 9.0663 | 10.4196 | 11.3656 | 12.3958 | 12.9845 | 13.5872 | 14.1941 | 14.8088 | 29.6177
[13 empty] | KLO23 reconfigured | 24 | KLO13/21 | 13.384 | 15.5465 | 17.2278 | 18.4288 | 19.8638 | 20.8057 | 21.7714 | 22.7462 | 23.7356 | 1.8095
[13 empty] | ST 24 | 14.2894 | BD 09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3992
[13 empty] | ST 21 | 14.2894 | COO24/22 | 9.5736 | 9.7636 | 9.941 | 10.1264 | 10.3576 | 10.5925 | 10.8313 | 11.0739 | 11.3205 | 1.4091

## REFCL
EDPR Forecasts for Ico at COO
Option 1 - Do Nothing | U/G Length (km)
JEN Feeders (August 2023) | 2023 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Rating
COO-011 | 21.1 | 68.3569 | 70.0369 | 71.7169 | 73.3969 | 75.0769 | 76.7569 | 78.4369 | 80.1169 | 81.7969 | 83.4769
COO-012 | 13 | 42.9963 | 44.7264 | 46.4535 | 48.1776 | 49.8986 | 51.6166 | 53.3315 | 55.0434 | 56.7523 | 58.4612
COO-013 | 0 | 0.075241 | 0.092273 | 0.1111 | 0.13172 | 0.15413 | 0.17833 | 0.20433 | 0.23211 | 0.2617 | 0.29128
COO-014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COO Bus No.1 |  | 111.4284 | 114.8556 | 118.2815 | 121.7062 | 125.1296 | 128.5518 | 131.9727 | 135.3924 | 138.8109 | 142.2293 | 120
COO-021 | 0.6 | 2.0235 | 2.0561 | 2.0922 | 2.1316 | 2.1744 | 2.2206 | 2.2702 | 2.3232 | 2.3795 | 2.4359
COO-022 | 29.5 | 106.2942 | 109.0481 | 111.8864 | 114.8089 | 117.8159 | 120.9073 | 124.083 | 127.3431 | 130.6876 | 134.0321
COO-023 | 25.6 | 103.5468 | 111.9446 | 120.7255 | 129.8895 | 139.4366 | 149.3668 | 159.6802 | 170.3766 | 181.4562 | 192.5358
COO-024 | 18.1 | 63.8959 | 63.8959 | 63.8959 | 63.8959 | 63.8959 | 63.8959 | 63.8959 | 63.8959 | 63.8959 | 63.8959
COO Bus No.2 |  | 275.7604 | 286.9447 | 298.5998 | 310.7259 | 323.3227 | 336.3905 | 349.9292 | 363.9387 | 378.4192 | 392.8996 | 300
Option 2 - CBN | Share
JEN Feeders (August 2023) |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Rating
COO-011 | 55.92% | 38.228 | 39.1675 | 40.1071 | 41.0466 | 41.9861 | 42.9256 | 43.8652 | 44.8047 | 45.7442 | 46.6838 |  | To KLO22
COO-012 | 80.77% | 34.7278 | 36.1252 | 37.5201 | 38.9126 | 40.3027 | 41.6903 | 43.0754 | 44.4581 | 45.8384 | 47.2186 |  | To CLO21
COO-013 | 100% | 2.0235 | 2.0561 | 2.0922 | 2.1316 | 2.1744 | 2.2206 | 2.2702 | 2.3232 | 2.3795 | 2.4359 |  | from COO21
COO-014 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | No change
COO Bus No.1 |  | 74.9793 | 77.3489 | 79.7194 | 82.0908 | 84.4632 | 86.8366 | 89.2108 | 91.586 | 93.9621 | 96.3383 | 120
COO-021 | 34.62% | 66.6567 | 71.4545 | 76.4428 | 81.6216 | 86.9909 | 92.5507 | 98.301 | 104.2418 | 110.3731 | 116.5045 |  | From COO23 + new exit cable (part of COO12 cable)
COO-022 | 44% | 46.7695 | 47.9812 | 49.23 | 50.5159 | 51.839 | 53.1992 | 54.5965 | 56.031 | 57.5025 | 58.9741 |  | To ST21
COO-023 | 50% | 51.7734 | 55.9723 | 60.3627 | 64.9447 | 69.7183 | 74.6834 | 79.8401 | 85.1883 | 90.7281 | 96.2679 |  | To COO21
COO-024 | 44% | 28.1142 | 28.1142 | 28.1142 | 28.1142 | 28.1142 | 28.1142 | 28.1142 | 28.1142 | 28.1142 | 28.1142 |  | To ST21
COO Bus No.2 |  | 193.3138 | 203.5222 | 214.1497 | 225.1964 | 236.6623 | 248.5475 | 260.8518 | 273.5753 | 286.7179 | 299.8606 | 300
Option 3 - GVE | Share
JEN Feeders (August 2023) |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Rating
COO-011 |  | 38.228 | 39.1675 | 40.1071 | 41.0466 | 41.9861 | 42.9256 | 43.8652 | 44.8047 | 45.7442 | 46.6838 |  | As above
COO-012 |  | 34.7278 | 36.1252 | 37.5201 | 38.9126 | 40.3027 | 41.6903 | 43.0754 | 44.4581 | 45.8384 | 47.2186 |  | As above
COO-013 |  | 2.0235 | 2.0561 | 2.0922 | 2.1316 | 2.1744 | 2.2206 | 2.2702 | 2.3232 | 2.3795 | 2.4359 |  | As above
COO-014 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | As above
COO Bus No.1 |  | 74.9793 | 77.3489 | 79.7194 | 82.0908 | 84.4632 | 86.8366 | 89.2108 | 91.586 | 93.9621 | 96.3383 | 120
COO-021 | 54.24% | 57.6511 | 59.1447 | 60.6841 | 62.2693 | 63.9002 | 65.5768 | 67.2992 | 69.0674 | 70.8814 | 72.6954 |  | Moved to GVE11, Pick up ST21
COO-022 |  | 46.7695 | 47.9812 | 49.23 | 50.5159 | 51.839 | 53.1992 | 54.5965 | 56.031 | 57.5025 | 58.9741 |  | As above
COO-023 |  | 51.7734 | 55.9723 | 60.3627 | 64.9447 | 69.7183 | 74.6834 | 79.8401 | 85.1883 | 90.7281 | 96.2679 |  | As above
COO-024 |  | 28.1142 | 28.1142 | 28.1142 | 28.1142 | 28.1142 | 28.1142 | 28.1142 | 28.1142 | 28.1142 | 28.1142 |  | As above
COO Bus No.2 |  | 184.3081 | 191.2124 | 198.391 | 205.8441 | 213.5716 | 221.5736 | 229.85 | 238.4009 | 247.2262 | 256.0515 | 300

## EUE
Results from EUE modellling | [5 empty] | VCR | 47905.2881 | $/MWh |  | WACC | 5.18% |  | O&M | 1% |  | Asset Life | 45 | years |  | Discount Rate | 5.18%
Expected Unserved Energy for each Option (MWh) – Feeder (N) Overload (from NDS FDR EUE model) | [28 empty] | Value of Expected Unserved Energy for each Option ($k) – Feeder (N) Overload
Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7
FDR | COO23 | [6 empty] | KLO13 | [6 empty] | KLO21 | [6 empty] | KLO22 | [6 empty] | FDR | COO23 | 0 | 0 | 0 | 0 | 0 | 0 | KLO13 | 0 | 0 | 0 | 0 | 0 | 0 | KLO21 | 0 | 0 | 0 | 0 | 0 | 0 | KLO22 | 0 | 0 | 0 | 0 | 0 | 0
Solution Applied | Nil | [6 empty] | Nil | [20 empty] | Solution Applied | Nil | 0 | 0 | 0 | 0 | 0 | 0 | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 0 | [6 empty] | 23.9831 | [6 empty] | 3.7686 | [6 empty] | 0 | [6 empty] | 2025 | 0 | [6 empty] | 1148.9161 | [6 empty] | 180.5338 | [6 empty] | 0
2026 | 2.093 | 2.093 | 2.093 |  |  |  |  | 31.7491 | 0 | 0 |  |  |  |  | 10.2755 | 0 | 0 |  |  |  |  | 0.10735 | 0 | 0 |  |  |  |  | 2026 | 100.2659 | 100.2659 | 100.2659 | 0 | 0 | 0 | 0 | 1520.95 | 0 | 0 | 0 | 0 | 0 | 0 | 492.2528 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1429 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 11.5938 | 0 | 0 |  |  |  |  | 40.284 | 0 | 0 |  |  |  |  | 72.4384 | 0 | 0 |  |  |  |  | 21.05 | 0 | 0 |  |  |  |  | 2027 | 555.404 | 0 | 0 | 0 | 0 | 0 | 0 | 1929.8158 | 0 | 0 | 0 | 0 | 0 | 0 | 3470.1812 | 0 | 0 | 0 | 0 | 0 | 0 | 1008.4062 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 44.8798 | 0 | 0 |  |  |  |  | 49.3559 | 0 | 0 |  |  |  |  | 325.1303 | 0 | 0 |  |  |  |  | 260.8977 | 0 | 0 |  |  |  |  | 2028 | 2149.9818 | 0 | 0 | 0 | 0 | 0 | 0 | 2364.4088 | 0 | 0 | 0 | 0 | 0 | 0 | 15575.4615 | 0 | 0 | 0 | 0 | 0 | 0 | 12498.3774 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 115.397 | 0 | 0 |  |  |  |  | 55.9827 | 0 | 0 |  |  |  |  | 748.8693 | 0 | 0 |  |  |  |  | 704.9729 | 0 | 0 |  |  |  |  | 2029 | 5528.1284 | 0 | 0 | 0 | 0 | 0 | 0 | 2681.8685 | 0 | 0 | 0 | 0 | 0 | 0 | 35874.801 | 0 | 0 | 0 | 0 | 0 | 0 | 33771.9282 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 294.7108 | 0 | 0 |  |  |  |  | 77.6462 | 0 | 0 |  |  |  |  | 1792.9419 | 0 | 0 |  |  |  |  | 1978.623 | 0 | 0 |  |  |  |  | 2030 | 14118.2051 | 0 | 0 | 0 | 0 | 0 | 0 | 3719.6636 | 0 | 0 | 0 | 0 | 0 | 0 | 85891.3982 | 0 | 0 | 0 | 0 | 0 | 0 | 94786.5052 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 496.2716 | 0 | 0 | 0 |  |  |  | 113.1162 | 0 | 0 | 0 |  |  |  | 2825.1631 | 0 | 0 | 0 |  |  |  | 4689.4474 | 0 | 0 | 0 |  |  |  | 2031 | 23774.0323 | 0 | 0 | 0 | 0 | 0 | 0 | 5418.862 | 0 | 0 | 0 | 0 | 0 | 0 | 135340.2524 | 0 | 0 | 0 | 0 | 0 | 0 | 224649.3304 | 0 | 0 | 0 | 0 | 0 | 0
2032 | 697.8323 | 0 | 0 | 0 |  |  |  | 148.5861 | 0 | 0 | 0 |  |  |  | 3857.3843 | 0 | 0 | 0 |  |  |  | 7400.2719 | 0 | 0 | 0 |  |  |  | 2032 | 33429.8594 | 0 | 0 | 0 | 0 | 0 | 0 | 7118.0604 | 0 | 0 | 0 | 0 | 0 | 0 | 184789.1066 | 0 | 0 | 0 | 0 | 0 | 0 | 354512.1556 | 0 | 0 | 0 | 0 | 0 | 0
2033 | 899.3931 | 0 | 0 | 0 |  |  |  | 184.0561 | 0 | 0 | 0 |  |  |  | 4889.6055 | 0 | 0 | 0 |  |  |  | 10111.0963 | 0 | 0 | 0 |  |  |  | 2033 | 43085.6866 | 0 | 0 | 0 | 0 | 0 | 0 | 8817.2588 | 0 | 0 | 0 | 0 | 0 | 0 | 234237.9608 | 0 | 0 | 0 | 0 | 0 | 0 | 484374.9809 | 0 | 0 | 0 | 0 | 0 | 0
2034 | 1100.9539 | 0 | 0 | 0 |  |  |  | 219.526 | 0 | 0 | 0 |  |  |  | 5921.8267 | 0 | 0 | 0 |  |  |  | 12821.9207 | 0 | 0 | 0 |  |  |  | 2034 | 52741.5137 | 0 | 0 | 0 | 0 | 0 | 0 | 10516.4572 | 0 | 0 | 0 | 0 | 0 | 0 | 283686.8151 | 0 | 0 | 0 | 0 | 0 | 0 | 614237.8061 | 0 | 0 | 0 | 0 | 0 | 0
Expected Unserved Energy for each Option (MWh) – Feeder (N) Overload (from NDS FDR EUE model) | [28 empty] | Value of Expected Unserved Energy for each Option ($k) – Feeder (N) Overload
Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7
FDR | KLO23 | [6 empty] | ST 11 | [6 empty] | ST 12 | [6 empty] | ST 22 | [6 empty] | FDR | KLO23 | 0 | 0 | 0 | 0 | 0 | 0 | ST 11 | 0 | 0 | 0 | 0 | 0 | 0 | ST 12 | 0 | 0 | 0 | 0 | 0 | 0 | ST 22 | 0 | 0 | 0 | 0 | 0 | 0
Solution Applied | Nil | [6 empty] | Nil | [20 empty] | Solution Applied | Nil | 0 | 0 | 0 | 0 | 0 | 0 | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 0 | [6 empty] | 1.8838 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 2025 | 0 | [6 empty] | 90.242 | [6 empty] | 0 | [6 empty] | 0
2026 | 0 | 0 | 0 |  |  |  |  | 13.6838 | 13.6838 | 13.6838 |  |  |  |  | 53.7658 | 53.7658 | 53.7658 |  |  |  |  | 1.1985 | 1.1985 | 1.1985 |  |  |  |  | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655.5258 | 655.5258 | 655.5258 | 0 | 0 | 0 | 0 | 2575.6642 | 2575.6642 | 2575.6642 | 0 | 0 | 0 | 0 | 57.4168 | 57.4168 | 57.4168 | 0 | 0 | 0 | 0
2027 | 0 | 0 | 0 |  |  |  |  | 40.7162 | 0 | 0 |  |  |  |  | 2532.3232 | 0 | 0 |  |  |  |  | 16.5595 | 0 | 0 |  |  |  |  | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1950.5211 | 0 | 0 | 0 | 0 | 0 | 0 | 121311.6717 | 0 | 0 | 0 | 0 | 0 | 0 | 793.2887 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 0 | 0 | 0 |  |  |  |  | 63.3214 | 0 | 0 |  |  |  |  | 9100.5743 | 0 | 0 |  |  |  |  | 116.8481 | 0 | 0 |  |  |  |  | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3033.4311 | 0 | 0 | 0 | 0 | 0 | 0 | 435965.633 | 0 | 0 | 0 | 0 | 0 | 0 | 5597.6412 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 0 | 0 | 0 |  |  |  |  | 75.8965 | 0 | 0 |  |  |  |  | 18071.6027 | 0 | 0 |  |  |  |  | 747.9415 | 0 | 0 |  |  |  |  | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3635.8436 | 0 | 0 | 0 | 0 | 0 | 0 | 865725.3346 | 0 | 0 | 0 | 0 | 0 | 0 | 35830.3517 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 0 | 0 | 0 |  |  |  |  | 91.381 | 0 | 0 |  |  |  |  | 27504.9992 | 0 | 0 |  |  |  |  | 1540.2472 | 0 | 0 |  |  |  |  | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4377.6327 | 0 | 0 | 0 | 0 | 0 | 0 | 1317634.9088 | 0 | 0 | 0 | 0 | 0 | 0 | 73785.9837 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 0 | 0 | 0 | 0 |  |  |  | 101.0563 | 0 | 0 | 0 |  |  |  | 35105.6896 | 0 | 0 | 0 |  |  |  | 2714.0349 | 0 | 0 | 0 |  |  |  | 2031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4841.1327 | 0 | 0 | 0 | 0 | 0 | 0 | 1681748.176 | 0 | 0 | 0 | 0 | 0 | 0 | 130016.6241 | 0 | 0 | 0 | 0 | 0 | 0
2032 | 0 | 0 | 0 | 0 |  |  |  | 110.7317 | 0 | 0 | 0 |  |  |  | 42706.3801 | 0 | 0 | 0 |  |  |  | 3887.8227 | 0 | 0 | 0 |  |  |  | 2032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5304.6327 | 0 | 0 | 0 | 0 | 0 | 0 | 2045861.4432 | 0 | 0 | 0 | 0 | 0 | 0 | 186247.2646 | 0 | 0 | 0 | 0 | 0 | 0
2033 | 0 | 0 | 0 | 0 |  |  |  | 120.407 | 0 | 0 | 0 |  |  |  | 50307.0706 | 0 | 0 | 0 |  |  |  | 5061.6104 | 0 | 0 | 0 |  |  |  | 2033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5768.1328 | 0 | 0 | 0 | 0 | 0 | 0 | 2409974.7104 | 0 | 0 | 0 | 0 | 0 | 0 | 242477.905 | 0 | 0 | 0 | 0 | 0 | 0
2034 | 0 | 0 | 0 | 0 |  |  |  | 130.0824 | 0 | 0 | 0 |  |  |  | 57907.7611 | 0 | 0 | 0 |  |  |  | 6235.3982 | 0 | 0 | 0 |  |  |  | 2034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6231.6328 | 0 | 0 | 0 | 0 | 0 | 0 | 2774087.9775 | 0 | 0 | 0 | 0 | 0 | 0 | 298708.5454 | 0 | 0 | 0 | 0 | 0 | 0
Expected Unserved Energy for each Option (MWh) – Feeder (N) Overload (from NDS FDR EUE model) | [28 empty] | Value of Expected Unserved Energy for each Option ($k) – Feeder (N) Overload
Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7
FDR | ST 32 | [6 empty] | ST 33 | [6 empty] | ST 34 | [13 empty] | FDR | ST 32 | 0 | 0 | 0 | 0 | 0 | 0 | ST 33 | 0 | 0 | 0 | 0 | 0 | 0 | ST 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solution Applied | Nil | [6 empty] | Nil | [6 empty] | Nil | [6 empty] | Nil | [6 empty] | Solution Applied | Nil | 0 | 0 | 0 | 0 | 0 | 0 | Nil | 0 | 0 | 0 | 0 | 0 | 0 | Nil | 0 | 0 | 0 | 0 | 0 | 0 | Nil | 0 | 0 | 0 | 0 | 0 | 0
2025 | 0 | [6 empty] | 0 | [6 empty] | 1.8796e-05 | [13 empty] | 2025 | 0 | [6 empty] | 0 | [6 empty] | 0.00090043 | [6 empty] | 0
2026 | 0 | 0 | 0 |  |  |  |  | 0.018047 | 0.018047 | 0.018047 |  |  |  |  | 0.23679 | 0 | 0 | [11 empty] | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86456 | 0.86456 | 0.86456 | 0 | 0 | 0 | 0 | 11.3435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 0 | 0 | 0 |  |  |  |  | 2.8928 | 0 | 0 |  |  |  |  | 1.9325 | 0 | 0 | [11 empty] | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138.5808 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 0.014917 | 0 | 0 |  |  |  |  | 7.906 | 0 | 0 |  |  |  |  | 3.2671 | 0 | 0 | [11 empty] | 2028 | 0.71461 | 0 | 0 | 0 | 0 | 0 | 0 | 378.7385 | 0 | 0 | 0 | 0 | 0 | 0 | 156.5119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 0.044755 | 0 | 0 |  |  |  |  | 10.4805 | 0 | 0 |  |  |  |  | 3.8131 | 0 | 0 | [11 empty] | 2029 | 2.144 | 0 | 0 | 0 | 0 | 0 | 0 | 502.0709 | 0 | 0 | 0 | 0 | 0 | 0 | 182.6684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 0.4413 | 0 | 0 |  |  |  |  | 14.9912 | 0 | 0 |  |  |  |  | 4.8067 | 0 | 0 | [11 empty] | 2030 | 21.1407 | 0 | 0 | 0 | 0 | 0 | 0 | 718.1577 | 0 | 0 | 0 | 0 | 0 | 0 | 230.2651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 2.0309 | 0 | 0 | 0 | 0 |  |  | 20.373 | 0 | 0 | 0 | 0 |  |  | 6.1333 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2031 | 97.2906 | 0 | 0 | 0 | 0 | 0 | 0 | 975.9767 | 0 | 0 | 0 | 0 | 0 | 0 | 293.8194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2032 | 3.6205 | 0 | 0 | 0 | 0 |  |  | 25.7549 | 0 | 0 | 0 | 0 |  |  | 7.46 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2032 | 173.4404 | 0 | 0 | 0 | 0 | 0 | 0 | 1233.7957 | 0 | 0 | 0 | 0 | 0 | 0 | 357.3737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2033 | 5.2101 | 0 | 0 | 0 | 0 |  |  | 31.1367 | 0 | 0 | 0 | 0 |  |  | 8.7867 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2033 | 249.5903 | 0 | 0 | 0 | 0 | 0 | 0 | 1491.6147 | 0 | 0 | 0 | 0 | 0 | 0 | 420.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2034 | 6.7997 | 0 | 0 | 0 | 0 |  |  | 36.5186 | 0 | 0 | 0 | 0 |  |  | 10.1133 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 2034 | 325.7401 | 0 | 0 | 0 | 0 | 0 | 0 | 1749.4336 | 0 | 0 | 0 | 0 | 0 | 0 | 484.4823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Expected Unserved Energy for each Option (MWh) – Zone Substations Overload (from NDS ZSS EUE model) | [28 empty] | Value of Expected Unserved Energy for each Option ($k) – Zone Substations Overload
Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7
ZSS | ST | [6 empty] | COO | [6 empty] | COO Bus No.1 REFCL | [6 empty] | COO Bus No.2 REFCL | [6 empty] | ZSS | ST | 0 | 0 | 0 | 0 | 0 | 0 | COO | 0 | 0 | 0 | 0 | 0 | 0 | COO Bus No.1 REFCL | 0 | 0 | 0 | 0 | 0 | 0 | COO Bus No.2 REFCL | 0 | 0 | 0 | 0 | 0 | 0 | REFCL1 + (COO23 + COO)/2 | REFCL2 + (COO23 + COO)/2 | KLO13+KLO21 | ST & Other Feeders
Solution Applied | xfers to BD | [6 empty] | Nil | [6 empty] | Nil | [6 empty] | Nil | [6 empty] | Solution Applied | xfers to BD | 0 | 0 | 0 | 0 | 0 | 0 | Nil | 0 | 0 | 0 | 0 | 0 | 0 | Nil | 0 | 0 | 0 | 0 | 0 | 0 | Nil | 0 | 0 | 0 | 0 | 0 | 0
2025 | 0 | [6 empty] | 0.48828 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 2025 | 0 | [6 empty] | 23.3912 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 11.6956 | 11.6956 | 1329.4498 | 90.242
2026 | 0 | 0 | 0 |  |  |  |  | 0.74081 | 0.74081 | 0.74081 |  |  |  |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  |  |  | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.4887 | 35.4887 | 35.4887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.8773 | 67.8773 | 2013.2028 | 3294.6143
2027 | 0.045494 | 0.045494 | 0.045494 |  |  |  |  | 1.5234 | 0.066123 | 0.012989 |  |  |  |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  |  |  | 2027 | 2.1794 | 2.1794 | 2.1794 | 0 | 0 | 0 | 0 | 72.9807 | 3.1676 | 0.62225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314.1924 | 314.1924 | 5399.997 | 125204.6479
2028 | 0.29417 | 0 | 0 |  |  |  |  | 2.0874 | 0.16932 | 0.064855 |  |  |  |  | 0.078824 | 0 | 0 |  |  |  |  | 0.53054 | 0 | 0 |  |  |  |  | 2028 | 14.0925 | 0 | 0 | 0 | 0 | 0 | 0 | 99.9954 | 8.1115 | 3.1069 | 0 | 0 | 0 | 0 | 3.7761 | 0 | 0 | 0 | 0 | 0 | 0 | 25.4156 | 0 | 0 | 0 | 0 | 0 | 0 | 1128.7647 | 1150.4042 | 17939.8702 | 457488.6282
2029 | 0.73854 | 0 | 0 |  |  |  |  | 2.689 | 0.39545 | 0.189 |  |  |  |  | 0.23723 | 0 | 0 |  |  |  |  | 1.4308 | 0 | 0 |  |  |  |  | 2029 | 35.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 128.8156 | 18.9443 | 9.0543 | 0 | 0 | 0 | 0 | 11.3644 | 0 | 0 | 0 | 0 | 0 | 0 | 68.5406 | 0 | 0 | 0 | 0 | 0 | 0 | 2839.8364 | 2897.0126 | 38556.6695 | 939503.0532
2030 | 1.6161 | 0 | 0 |  |  |  |  | 4.669 | 0.73038 | 0.4109 |  |  |  |  | 0.5373 | 0 | 0 |  |  |  |  | 3.0835 | 0 | 0 |  |  |  |  | 2030 | 77.4219 | 0 | 0 | 0 | 0 | 0 | 0 | 223.672 | 34.9892 | 19.6844 | 0 | 0 | 0 | 0 | 25.7394 | 0 | 0 | 0 | 0 | 0 | 0 | 147.7181 | 0 | 0 | 0 | 0 | 0 | 0 | 7196.678 | 7318.6567 | 89611.0618 | 1491401.7508
2031 | 5.2267 | 0 | 0 |  |  |  |  | 7.5747 | 1.2255 | 0.81184 |  |  |  |  | 0.84568 | 0 | 0 |  |  |  |  | 6.1535 | 0 | 0 |  |  |  |  | 2031 | 250.3845 | 0 | 0 | 0 | 0 | 0 | 0 | 362.8664 | 58.7076 | 38.8916 | 0 | 0 | 0 | 0 | 40.5125 | 0 | 0 | 0 | 0 | 0 | 0 | 294.7865 | 0 | 0 | 0 | 0 | 0 | 0 | 12108.9618 | 12363.2359 | 140759.1144 | 2042578.915
2032 | 19.2468 | 0 | 0 |  |  |  |  | 11.9916 | 1.9801 | 1.4442 |  |  |  |  | 1.2804 | 0 | 0 |  |  |  |  | 11.8529 | 0 | 0 |  |  |  |  | 2032 | 922.0228 | 0 | 0 | 0 | 0 | 0 | 0 | 574.4601 | 94.8576 | 69.1845 | 0 | 0 | 0 | 0 | 61.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 567.8153 | 0 | 0 | 0 | 0 | 0 | 0 | 17063.4954 | 17569.9751 | 191907.1671 | 2594254.7551
2033 | 67.7193 | 0 | 0 |  |  |  |  | 17.6939 | 3.0552 | 2.3956 |  |  |  |  | 2.0782 | 0 | 0 |  |  |  |  | 20.5644 | 0 | 0 |  |  |  |  | 2033 | 3244.115 | 0 | 0 | 0 | 0 | 0 | 0 | 847.6325 | 146.36 | 114.7607 | 0 | 0 | 0 | 0 | 99.5553 | 0 | 0 | 0 | 0 | 0 | 0 | 985.1455 | 0 | 0 | 0 | 0 | 0 | 0 | 22066.2148 | 22951.8051 | 243055.2197 | 3147581.0489
2034 | 192.8072 | 0 | 0.0053504 |  |  |  |  | 24.76 | 4.474 | 3.7343 |  |  |  |  | 3.4256 | 0 | 0 |  |  |  |  | 34.0232 | 0 | 0 |  |  |  |  | 2034 | 9236.4851 | 0 | 0.25631 | 0 | 0 | 0 | 0 | 1186.1328 | 214.3293 | 178.8904 | 0 | 0 | 0 | 0 | 164.1024 | 0 | 0 | 0 | 0 | 0 | 0 | 1629.8901 | 0 | 0 | 0 | 0 | 0 | 0 | 27127.9256 | 28593.7133 | 294203.2723 | 3704577.6206
Expected Unserved Energy for each Option (MWh) – SubT Overload (from NDS SUBT EUE model) | [28 empty] | Value of Expected Unserved Energy for each Option ($k) – SubT Overload
Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7
ZSS | CBN | [6 empty] | GVE | [20 empty] | ZSS | CBN | 0 | 0 | 0 | 0 | 0 | 0 | GVE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solution Applied | Nil | CBN | Nil | 2 tx | Nil |  |  | Nil | Nil | GVE | Nil | 2 tx | [16 empty] | Solution Applied | Nil | CBN | Nil | 2 tx | Nil | 0 | 0 | Nil | Nil | GVE | Nil | 2 tx | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 0 | [6 empty] | 0 | [20 empty] | 2025 | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
2026 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | [16 empty] | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | [16 empty] | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 0 | 0.034013 | 0 | 0.034013 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | [16 empty] | 2028 | 0 | 1.6294 | 0 | 1.6294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 0 | 0.39124 | 0 | 0.39124 | 0 |  |  | 0 | 0 | 0.00071261 | 0 | 0.00071261 | [16 empty] | 2029 | 0 | 18.7425 | 0 | 18.7425 | 0 | 0 | 0 | 0 | 0 | 0.034138 | 0 | 0.034138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 0 | 1.4655 | 0 | 1.4655 | 0 |  |  | 0 | 0 | 0.044441 | 0 | 0.044441 | [16 empty] | 2030 | 0 | 70.2053 | 0 | 70.2053 | 0 | 0 | 0 | 0 | 0 | 2.129 | 0 | 2.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 0 | 3.4309 | 0 | 3.4309 | 0 |  |  | 0 | 0 | 0.30059 | 0 | 0.30059 | [16 empty] | 2031 | 0 | 164.3603 | 0 | 164.3603 | 0 | 0 | 0 | 0 | 0 | 14.3999 | 0 | 14.3999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2032 | 0 | 6.8437 | 0 | 6.8437 | 0 |  |  | 0 | 0 | 1.3259 | 0 | 1.3259 | [16 empty] | 2032 | 0 | 327.8482 | 0 | 327.8482 | 0 | 0 | 0 | 0 | 0 | 63.5186 | 0 | 63.5186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2033 | 0 | 0 | 0 | 11.8726 | 0 |  |  | 0 | 0 | 3.8007 | 0 | 3.8007 | [16 empty] | 2033 | 0 | 0 | 0 | 568.7585 | 0 | 0 | 0 | 0 | 0 | 182.0758 | 0 | 182.0758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2034 | 0 | 0 | 0 | 18.4783 | 0 |  |  | 0 | 0 | 8.1391 | 0 | 8.1391 | [16 empty] | 2034 | 0 | 0 | 0 | 885.2059 | 0 | 0 | 0 | 0 | 0 | 389.9082 | 0 | 389.9082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) | [8 empty] | Total EUE (MWh) - Zone Substations and Sub-Transmission | [8 empty] | Total EUE (MWh) - Distribution Feeders | [10 empty] | Total EUE ($k) | [8 empty] | Total EUE ($k) - Zone Substations and Sub-Transmission | [8 empty] | Total EUE ($k) - Distribution Feeders
Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  |  |  | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7
2025 | 30.1237 | 30.1237 | 30.1237 | 30.1237 | 30.1237 | 30.1237 | 30.1237 |  | 2025 | 0.48828 | 0.48828 | 0.48828 | 0.48828 | 0.48828 | 0.48828 | 0.48828 |  | 2025 | 29.6354 | 29.6354 | 29.6354 | 29.6354 | 29.6354 | 29.6354 | 29.6354 |  |  |  | 2025 | 1443.0839 | 1443.0839 | 1443.0839 | 1443.0839 | 1443.0839 | 1443.0839 | 1443.0839 |  | 2025 | 23.3912 | 23.3912 | 23.3912 | 23.3912 | 23.3912 | 23.3912 | 23.3912 |  | 2025 | 1419.6927 | 1419.6927 | 1419.6927 | 1419.6927 | 1419.6927 | 1419.6927 | 1419.6927
2026 | 113.8687 | 71.5 | 71.5 | 0 | 0 | 0 | 0 |  | 2026 | 0.74081 | 0.74081 | 0.74081 | 0 | 0 | 0 | 0 |  | 2026 | 113.1279 | 70.7591 | 70.7591 | 0 | 0 | 0 | 0 |  |  |  | 2026 | 5454.9152 | 3425.226 | 3425.226 | 0 | 0 | 0 | 0 |  | 2026 | 35.4887 | 35.4887 | 35.4887 | 0 | 0 | 0 | 0 |  | 2026 | 5419.4264 | 3389.7373 | 3389.7373 | 0 | 0 | 0 | 0
2027 | 1432.5689 | 0.11162 | 0.058483 | 0 | 0 | 0 | 0 |  | 2027 | 1.5689 | 0.11162 | 0.058483 | 0 | 0 | 0 | 0 |  | 2027 | 1431 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2027 | 68627.6274 | 5.347 | 2.8017 | 0 | 0 | 0 | 0 |  | 2027 | 75.1601 | 5.347 | 2.8017 | 0 | 0 | 0 | 0 |  | 2027 | 68552.4673 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 1433.9909 | 0.20334 | 0.064855 | 0.034013 | 0 | 0 | 0 |  | 2028 | 2.9909 | 0.20334 | 0.064855 | 0.034013 | 0 | 0 | 0 |  | 2028 | 1431 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2028 | 68695.7469 | 9.741 | 3.1069 | 1.6294 | 0 | 0 | 0 |  | 2028 | 143.2796 | 9.741 | 3.1069 | 1.6294 | 0 | 0 | 0 |  | 2028 | 68552.4673 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 1436.0955 | 0.7867 | 0.18972 | 0.39124 | 0.00071261 | 0 | 0 |  | 2029 | 5.0955 | 0.7867 | 0.18972 | 0.39124 | 0.00071261 | 0 | 0 |  | 2029 | 1431 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2029 | 68796.5681 | 37.6869 | 9.0884 | 18.7425 | 0.034138 | 0 | 0 |  | 2029 | 244.1008 | 37.6869 | 9.0884 | 18.7425 | 0.034138 | 0 | 0 |  | 2029 | 68552.4673 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 1440.906 | 2.1959 | 0.45534 | 1.4655 | 0.044441 | 0 | 0 |  | 2030 | 9.906 | 2.1959 | 0.45534 | 1.4655 | 0.044441 | 0 | 0 |  | 2030 | 1431 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2030 | 69027.0187 | 105.1945 | 21.8133 | 70.2053 | 2.129 | 0 | 0 |  | 2030 | 474.5514 | 105.1945 | 21.8133 | 70.2053 | 2.129 | 0 | 0 |  | 2030 | 68552.4673 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 1450.8005 | 4.6564 | 1.1124 | 3.4309 | 0.30059 | 0 | 0 |  | 2031 | 19.8005 | 4.6564 | 1.1124 | 3.4309 | 0.30059 | 0 | 0 |  | 2031 | 1431 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2031 | 69501.0171 | 223.0679 | 53.2915 | 164.3603 | 14.3999 | 0 | 0 |  | 2031 | 948.5498 | 223.0679 | 53.2915 | 164.3603 | 14.3999 | 0 | 0 |  | 2031 | 68552.4673 | 0 | 0 | 0 | 0 | 0 | 0
2032 | 1475.3716 | 8.8238 | 2.7701 | 6.8437 | 1.3259 | 0 | 0 |  | 2032 | 44.3716 | 8.8238 | 2.7701 | 6.8437 | 1.3259 | 0 | 0 |  | 2032 | 1431 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2032 | 70678.1012 | 422.7057 | 132.7032 | 327.8482 | 63.5186 | 0 | 0 |  | 2032 | 2125.6339 | 422.7057 | 132.7032 | 327.8482 | 63.5186 | 0 | 0 |  | 2032 | 68552.4673 | 0 | 0 | 0 | 0 | 0 | 0
2033 | 1539.0559 | 3.0552 | 6.1963 | 11.8726 | 3.8007 | 0 | 0 |  | 2033 | 108.0559 | 3.0552 | 6.1963 | 11.8726 | 3.8007 | 0 | 0 |  | 2033 | 1431 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2033 | 73728.9155 | 146.36 | 296.8365 | 568.7585 | 182.0758 | 0 | 0 |  | 2033 | 5176.4483 | 146.36 | 296.8365 | 568.7585 | 182.0758 | 0 | 0 |  | 2033 | 68552.4673 | 0 | 0 | 0 | 0 | 0 | 0
2034 | 255.0159 | 4.474 | 11.8787 | 18.4783 | 8.1391 | 0 | 0 |  | 2034 | 255.0159 | 4.474 | 11.8787 | 18.4783 | 8.1391 | 0 | 0 |  | 2034 | [10 empty] | 2034 | 12216.6103 | 214.3293 | 569.0549 | 885.2059 | 389.9082 | 0 | 0 |  | 2034 | 12216.6103 | 214.3293 | 569.0549 | 885.2059 | 389.9082 | 0 | 0 |  | 2034 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | Cap | 1431 | for benefits moderation

## Costs
PV Risk Mitigation Option Costs and Timing |  |  |  | Evaluation Period |  | 20 | years
CAPEX PV RESULTS $m |  |  | Option | Capex Costs | [6 empty] | Option | Opex Costs | [5 empty] | Option | EUE Costs
| Year | Ratio | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7
|  | PV $m | 0 | 44.9131 | 56.2558 | 0 | 0 | 0 | 0 |  | 0 | 6.7055 | 8.3958 | 0 | 0 | 0 | 0 | 496.3657 | 7.2906 | 5.4211 | 2.8076 | 1.8691 | 1.4431 | 1.4431
|  | Sum $m | 0 | 49.178 | 61.676 | 0 | 0 | 0 | 0 |  | 0 | 8.8933 | 11.108 | 0 | 0 | 0 | 0 | 642.5523 | 8.3904 | 5.957 | 3.4798 | 2.0951 | 1.4431 | 1.4431
0 | 2025 | 1 | 0 | 2.951 | 2.951 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4431 | 1.4431 | 1.4431 | 1.4431 | 1.4431 | 1.4431 | 1.4431
1 | 2026 | 0.95075 |  | 38.227 | 50.725 | [6 empty] | 0.02951 | 0.02951 | 0 | 0 | 0 | 0 | 5.4549 | 3.4252 | 3.4252 | 0 | 0 | 0 | 0
2 | 2027 | 0.90393 |  | 0 | 0 | [6 empty] | 0.41178 | 0.53676 | 0 | 0 | 0 | 0 | 68.6276 | 0.005347 | 0.0028017 | 0 | 0 | 0 | 0
3 | 2028 | 0.85941 |  | 0 | 0 | [6 empty] | 0.41178 | 0.53676 | 0 | 0 | 0 | 0 | 68.6957 | 0.009741 | 0.0031069 | 0.0016294 | 0 | 0 | 0
4 | 2029 | 0.81709 |  | 0 | 0 | [6 empty] | 0.41178 | 0.53676 | 0 | 0 | 0 | 0 | 68.7966 | 0.037687 | 0.0090884 | 0.018743 | 3.4138e-05 | 0 | 0
5 | 2030 | 0.77684 |  | 0 | 0 | [6 empty] | 0.41178 | 0.53676 | 0 | 0 | 0 | 0 | 69.027 | 0.10519 | 0.021813 | 0.070205 | 0.002129 | 0 | 0
6 | 2031 | 0.73859 |  | 0 | 0 | [6 empty] | 0.41178 | 0.53676 | 0 | 0 | 0 | 0 | 69.501 | 0.22307 | 0.053291 | 0.16436 | 0.0144 | 0 | 0
7 | 2032 | 0.70221 |  | 8 | 0 | [6 empty] | 0.41178 | 0.53676 | 0 | 0 | 0 | 0 | 70.6781 | 0.42271 | 0.1327 | 0.32785 | 0.063519 | 0 | 0
8 | 2033 | 0.66763 |  | 0 | 0 | [6 empty] | 0.49178 | 0.53676 | 0 | 0 | 0 | 0 | 73.7289 | 0.14636 | 0.29684 | 0.56876 | 0.18208 | 0 | 0
9 | 2034 | 0.63475 |  | 0 | 8 | [6 empty] | 0.49178 | 0.53676 | 0 | 0 | 0 | 0 | 12.2166 | 0.21433 | 0.56905 | 0.88521 | 0.38991 | 0 | 0
10 | 2035 | 0.60349 | [9 empty] | 0.49178 | 0.61676 | 0 | 0 | 0 | 0 | 12.2166 | 0.21433 | 0 | 0 | 0 | 0 | 0
Solutions |  |  |  |  | Ref. | Capex $m | Annualised $k | Network Limitation | Lead Time Years | Optimum Timing | Options
Coolaroo No.1 bus cable transfers |  |  |  |  | 8.1.1 | xxx | xxx | REFCL1/COO23/COO | 1 | 2027 | 2,3
Coolaroo No.2 bus feeders |  |  |  |  | 8.1.2 | xxx | xxx | REFCL2/COO23/COO | 1 | 2027 | 2,3
New feeder KLO-023 |  |  |  |  | 8.1.3 | xxx | xxx | KLO13/21 | 2 | 2026 | 2,3
Establish new Craigieburn (CBN) zone substation - zone substation works |  |  |  |  | 8.2.1 | xxx | xxx | ST/OTHER FDRS | 2 | 2027 | 2
Establish new Craigieburn (CBN) zone substation - HV feeder works |  |  |  |  | 8.2.2 | xxx | xxx | ST/OTHER FDRS | 2 | 2027 | 2
New 66/22 kV zone substation at GVE |  |  |  |  | 8.3.1 | xxx | xxx | ST/OTHER FDRS | 2 | 2027 | 3
New 22 kV feeders at GVE |  |  |  |  | 8.3.2 | xxx | xxx | ST/OTHER FDRS | 2 | 2027 | 3
Third 66/22 kV transformer at CBN |  |  |  |  | - | xxx | xxx | CBN | 1 | 2033 | 2b
Third 66/22 kV transformer at GVE |  |  |  |  | - | xxx | xxx | GVE | 1 | 2035 | 3b
Augment feeder BD0-008 |  |  |  |  | 8.1.4 | xxx | xxx | ST, ST34 | 1 | 2026 | 2,3
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## NPV
Base Case NPV ($ million)
Table 5‑4: Summary of Option Costs ($M Real 2024)
Option | PV of Project Capital Cost | PV of Annual O&M Cost | PV of EUE Cost | PV of Total Costs | Ranking |  | Option | PV of Capital and O&M Cost | PV of EUE Benefit | NPV | PVR | Ranking | Capital Cost | Option 1 | Option 2 | Option 3
Option 1 | 0 | 0 | 496.3657 | 496.3657 | 5 |  | Option 1 | 0 | 0 | 0 | 1 | 5 | Option total capital cost | 0 | 49.178 | 61.676
Option 2 | 44.9131 | 6.7055 | 7.2906 | 58.9092 | 1 |  | Option 2 | 51.6185 | 489.0751 | 437.4565 | 9.4748 | 1 | PV of total capital cost | 0 | 44.9131 | 56.2558
Option 3 | 56.2558 | 8.3958 | 5.4211 | 70.0728 | 2 |  | Option 3 | 64.6517 | 490.9446 | 426.2929 | 7.5937 | 2 | PV of O&M cost | 0 | 6.7055 | 8.3958
Option 4 | 0 | 255.2302 | 7.2906 | 262.5209 | 4 |  | Option 4 | 255.2302 | 489.0751 | 233.8449 | 1.9162 | 4 | PV of option total capital and O&M cost | 0 | 51.6185 | 64.6517
Option 5 | 0 | 106.0921 | 7.2906 | 113.3827 | 3 |  | Option 5 | 106.0921 | 489.0751 | 382.983 | 4.6099 | 3
Option 6 | [6 empty] | Option 6
Option 7 | [6 empty] | Option 7
Sensitivity NPV ($ million) | [12 empty] | Table ES-1: Summary of Cost-Benefit Analysis ($M Real 2024)
Table 6‑1: Summary of NPV Cost-Benefit Analysis ($M Real 2024)
Option | Baseline | Customer Benefit 10% Lower | Customer Benefit 10% Higher | Discount Rate 1% Higher | Discount Rate 1% Lower | Capital Costs 30% Higher | Capital Costs 30% Lower | [5 empty] | Option | Total Capital Cost | Present Value of Capital and O&M Cost | Present Value of Reliability Benefit | Net Present Value (NPV) | Ranking
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | Option 1 - Do Nothing | 0 | 0 | 0 | 0 | 5
2 | 437.4565 | 388.549 | 486.3641 | 415.9683 | 460.4522 | 421.971 | 452.9421 | [5 empty] | Option 2 – Craigieburn Plan | 49.178 | 51.6185 | 489.0751 | 437.4565 | 1
3 | 426.2929 | 377.1985 | 475.3874 | 404.9647 | 448.8273 | 406.8974 | 445.6884 | [5 empty] | Option 3 - Greenvale Plan | 61.676 | 64.6517 | 490.9446 | 426.2929 | 2
4 | 233.8449 | 184.9374 | 282.7524 | 0 | 0 | 157.2758 | 310.4139 | [6 empty] | 0 | 255.2302 | 489.0751 | 233.8449 | 4
5 | 382.983 | 334.0755 | 431.8905 | 0 | 0 | 351.1554 | 414.8106 | [6 empty] | 0 | 106.0921 | 489.0751 | 382.983 | 3
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensitivity Rank |  |  | Yellow highlights copied from Sensitivities sheet
Table 4‑3: Zone Substation and Sub-transmission Value of Expected Unserved Energy ($k, Real 2024) – Option 1
Option | Baseline | Customer Benefit 10% Lower | Customer Benefit 10% Higher | Discount Rate 1% Higher | Discount Rate 1% Lower | Capital Costs 30% Higher | Capital Costs 30% Lower | [5 empty] | Asset | ST | COO | COO Bus No.1 REFCL | COO Bus No.2 REFCL | Total
1 | 5 | 5 | 5 | 3 | 3 | 5 | 5 | [5 empty] | 2025 | 0 | 23.3912 | 0 | 0 | 23.3912
2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | 2026 | 0 | 35.4887 | 0 | 0 | 35.4887
3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [5 empty] | 2027 | 2.1794 | 72.9807 | 0 | 0 | 75.1601
4 | 4 | 4 | 4 | 3 | 3 | 4 | 4 | [5 empty] | 2028 | 14.0925 | 99.9954 | 3.7761 | 25.4156 | 143.2796
5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | 2029 | 35.3801 | 128.8156 | 11.3644 | 68.5406 | 244.1008
6 | [12 empty] | 2030 | 77.4219 | 223.672 | 25.7394 | 147.7181 | 474.5514
7 | [12 empty] | 2031 | 250.3845 | 362.8664 | 40.5125 | 294.7865 | 948.5498
[13 empty] | 2032 | 922.0228 | 574.4601 | 61.3357 | 567.8153 | 2125.6339
[13 empty] | 2033 | 3244.115 | 847.6325 | 99.5553 | 985.1455 | 5176.4483
[13 empty] | 2034 | 9236.4851 | 1186.1328 | 164.1024 | 1629.8901 | 12216.6103
Table 4‑4: Distribution Feeder Value of Expected Unserved Energy ($k, Real 2024) – Option 1
[13 empty] | Asset | COO23 | KLO13 | KLO21 | KLO22 | ST 11 | ST 12 | ST 22 | ST 32 | ST 33 | ST 34 | Total
[13 empty] | 2025 | 0 | 1148.9161 | 180.5338 | 0 | 90.242 | 0 | 0 | 0 | 0 | 0.00090043 | 1419.6927
[13 empty] | 2026 | 100.2659 | 1520.95 | 492.2528 | 5.1429 | 655.5258 | 2575.6642 | 57.4168 | 0 | 0.86456 | 11.3435 | 5419.4264
[13 empty] | 2027 | 555.404 | 1929.8158 | 3470.1812 | 1008.4062 | 1950.5211 | 121311.6717 | 793.2887 | 0 | 138.5808 | 92.5753 | 131250.4449
[13 empty] | 2028 | 2149.9818 | 2364.4088 | 15575.4615 | 12498.3774 | 3033.4311 | 435965.633 | 5597.6412 | 0.71461 | 378.7385 | 156.5119 | 477720.8997
[13 empty] | 2029 | 5528.1284 | 2681.8685 | 35874.801 | 33771.9282 | 3635.8436 | 865725.3346 | 35830.3517 | 2.144 | 502.0709 | 182.6684 | 983735.1392
[13 empty] | 2030 | 14118.2051 | 3719.6636 | 85891.3982 | 94786.5052 | 4377.6327 | 1317634.9088 | 73785.9837 | 21.1407 | 718.1577 | 230.2651 | 1595283.8609

## Non-Network Options
OPTION 2
NPV Capx+Opex | 51.6185 | M
NPV Benefits Option 2 | 489.0751 | M
Network Augmentation deferral benefits |  |  | 2.6738 | M
STORAGE OPTION |  |  |  | DEMAND RESPONSE
Storage Cost | XXX | XXX |  | Dispatch Cost | XXX | XXX
| XXX | XXX |  |  | XXX | XXX
Installed cost | XXX | XXX |  | Annual cost | XXX | XXX