## Cover
Powercor
Regulatory proposal 2026-31
Greater western Melbourne supply area
| Model number: | 3.01
2025-01-31
12

## Summary
Powercor
Melton & Wyndham Transformation Capacity Project
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Southern capacity priority |  | -76.1885 | 659.3519 | 583.1634
| Option 3 | Northern capacity priority |  | -75.4637 | 658.1773 | 582.7136
| Option 4 | Lean investment, Northern capacity priority |  | -62.5758 | 625.6405 | 563.0647
| Option 5 | Lean investment, Southern capacity priority |  | -59.1707 | 613.1808 | 554.0101
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | Southern capacity priority |  | 583.1634
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 30.9873 | 21.101 | 35.44 | 44.1655 | 15.2636 |  | 146.9573
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
| Capex and risk ($M, 2026) |  | Value of expected unserved energy ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 583.1634 | 582.7136 | 563.0647 | 554.0101 |  | Option 2
| Capex 10% higher |  | 0 | 575.5446 | 575.1673 | 556.8071 | 548.093 |  | Option 2
| Capex 10% lower |  | 0 | 590.7823 | 590.26 | 569.3223 | 559.9272 |  | Option 2
| Total benefits 10% higher |  | 0 | 649.0986 | 648.5314 | 625.6287 | 615.3282 |  | Option 2
| Total benefits 10% lower |  | 0 | 517.2282 | 516.8959 | 500.5006 | 492.692 |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  | 0 | 509.6094 | 509.3495 | 494.2431 | 486.7749 |  | Option 2
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
Powercor
Melton & Wyndham Transformation Capacity Project
Project
|  | Business: | Powercor
|  | Descripton: | Melton & Wyndham Transformation Capacity Project
|  | Date of cost inputs: | December |  | 2023
|  | Option | Description
|  | Option 1 (base case) | No change to existing practices
|  | Option 2 | Southern capacity priority
|  | Option 3 | Northern capacity priority
|  | Option 4 | Lean investment, Northern capacity priority
|  | Option 5 | Lean investment, Southern capacity priority
|  | Compliance project | No
|  | Expenditure starts | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  | 3.5% | [real_disc]
|  | VCR date |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  | 20 | [years]\
|  | Output dollars |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | Region average |  | Melton/Wyndham | 42566 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  | 1
|  | Harm to property from bushfire |  |  | 1
|  | Harm to environment |  |  | 1
|  | Safety - Public trespass |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  | 3
|  | Safety from bushfire in HBRA |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  | 10
^ Public or employee
|  | Incident type |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  | 20%
Other benefits
| ENVIRONMENTAL | [7 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  | Value
|  | Reliability in worst-served areas |  |  | 151432.8174 | 2023-12-31 | per MWh
|  | Network resilience |  |  | 24590 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  | 88.3577 | 2023-12-31 | per MWh
|  | Aesthetics |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Communication |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[5 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  | 10% | -10%

## Option1 (base case)
Powercor
Melton & Wyndham Transformation Capacity Project
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| No change to existing practices |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 126.0532 | 212.094 | 277.7192 | 346.3475 | 444.0343 | 610.404 | 880.1971 | 1170.6152 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117
| Energy at risk value | $/MWh | 42566 | 2023-12-31 |  | 5365580.8534 | 9027994.7538 | 11821395.6394 | 14742628.4452 | 18900763.3738 | 25982456.0076 | 37466470.2508 | 49828408.5789 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445
| Safety consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 5365580.8534 | 9027994.7538 | 11821395.6394 | 14742628.4452 | 18900763.3738 | 25982456.0076 | 37466470.2508 | 49828408.5789 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445 | 62083006.9445
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| No change to existing practices |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| No change to existing practices |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - No change to existing practices |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
Powercor
Melton & Wyndham Transformation Capacity Project
OPTION 2 | Southern capacity priority
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| MTC 3rd Tx |  | 50 | 2023-12-31 | 14291649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH Rebuild |  | 50 | 2023-12-31 | 13551742.6667 | 13551742.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PCK Stage 1 |  | 50 | 2023-12-31 | 0 | 5408395.3 | 24162535.9333 | 22120559.4333 | 0 | 0 | 0 | 0 | 0 | 10425980.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New RBE ZSS |  | 50 | 2023-12-31 | 0 | 0 | 7681809 | 17564061.24 | 13715016.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 27843391.6667 | 18960137.9667 | 31844344.9333 | 39684620.6733 | 13715016.89 | 0 | 0 | 0 | 0 | 10425980.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 126.0532 | 22.5372 | 14.2358 | 21.2845 | 19.7706 | 6.9911 | 11.4878 | 17.2624 | 17.2624 | 17.2624 | 17.2624 | 17.2624 | 17.2624 | 17.2624 | 17.2624 | 17.2624 | 17.2624 | 17.2624 | 17.2624 | 17.2624 | 17.2624 | 17.2624 | 17.2624 | 17.2624 | 17.2624
| Energy at risk value | $/MWh | 42566 | 2023-12-31 | 5365580.8534 | 959318.6804 | 605960.0808 | 905995.8295 | 841554.6678 | 297584.3794 | 488989.2632 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 5365580.8534 | 959318.6804 | 605960.0808 | 905995.8295 | 841554.6678 | 297584.3794 | 488989.2632 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993 | 734791.5993
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 8068676.0735 | 11215435.5586 | 13836632.6156 | 18059208.706 | 25684871.6282 | 36977480.9876 | 49093616.9796 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452
Capital expenditure
| MTC 3rd Tx |  |  | 2023-12-31 | -14291649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH Rebuild |  |  | 2023-12-31 | -13551742.6667 | -13551742.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PCK Stage 1 |  |  | 2023-12-31 | 0 | -5408395.3 | -24162535.9333 | -22120559.4333 | 0 | 0 | 0 | 0 | 0 | -10425980.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New RBE ZSS |  |  | 2023-12-31 | 0 | 0 | -7681809 | -17564061.24 | -13715016.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| MTC 3rd Tx |  |  | 2023-12-31 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649
| BMH Rebuild |  |  | 2023-12-31 | -13551742.6667 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333
| PCK Stage 1 |  |  | 2023-12-31 | 0 | -5408395.3 | -29570931.2333 | -51691490.6667 | -51691490.6667 | -51691490.6667 | -51691490.6667 | -51691490.6667 | -51691490.6667 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471
| New RBE ZSS |  |  | 2023-12-31 | 0 | 0 | -7681809 | -25245870.24 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13 | -38960887.13
Annualised capex
| Annualised capex - MTC 3rd Tx |  |  | 2023-12-31 | 0 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127
| Annualised capex - BMH Rebuild |  |  | 2023-12-31 | 0 | -577761.061 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219
| Annualised capex - PCK Stage 1 |  |  | 2023-12-31 | 0 | 0 | -230579.9544 | -1260718.4938 | -2203800.0001 | -2203800.0001 | -2203800.0001 | -2203800.0001 | -2203800.0001 | -2203800.0001 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176
| Annualised capex - New RBE ZSS |  |  | 2023-12-31 | 0 | 0 | 0 | -327504.0139 | -1076325.0996 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464 | -1661047.1464
| Total annualised capex |  |  | 2023-12-31 | 0 | -1187067.0737 | -1995408.0891 | -3353050.6423 | -5044953.2343 | -5629675.2811 | -5629675.2811 | -5629675.2811 | -5629675.2811 | -5629675.2811 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986
| Annualised capex |  |  | 2023-12-31 | 0 | -1187067.0737 | -1995408.0891 | -3353050.6423 | -5044953.2343 | -5629675.2811 | -5629675.2811 | -5629675.2811 | -5629675.2811 | -5629675.2811 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 8068676.0735 | 11215435.5586 | 13836632.6156 | 18059208.706 | 25684871.6282 | 36977480.9876 | 49093616.9796 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 6881608.9998 | 9220027.4696 | 10483581.9733 | 13014255.4717 | 20055196.347 | 31347805.7065 | 43463941.6984 | 55718540.0641 | 55718540.0641 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | 6881608.9998 | 9220027.4696 | 10483581.9733 | 13014255.4717 | 20055196.347 | 31347805.7065 | 43463941.6984 | 55718540.0641 | 55718540.0641 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466
| Total annualised capex |  |  |  | 0 | -1187067.0737 | -1995408.0891 | -3353050.6423 | -5044953.2343 | -5629675.2811 | -5629675.2811 | -5629675.2811 | -5629675.2811 | -5629675.2811 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986 | -6074173.4986
| Total benefits |  |  |  | 0 | 8068676.0735 | 11215435.5586 | 13836632.6156 | 18059208.706 | 25684871.6282 | 36977480.9876 | 49093616.9796 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452 | 61348215.3452
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | 6762902.2924 | 9020486.6607 | 10148276.9091 | 12509760.1482 | 19492228.8189 | 30784838.1784 | 42900974.1703 | 55155572.5359 | 55155572.5359 | 54666624.4967 | 54666624.4967 | 54666624.4967 | 54666624.4967 | 54666624.4967 | 54666624.4967 | 54666624.4967 | 54666624.4967 | 54666624.4967 | 54666624.4967 | 54666624.4967 | 54666624.4967 | 54666624.4967 | 54666624.4967 | 54666624.4967
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | 7000315.7072 | 9419568.2785 | 10818887.0376 | 13518750.7951 | 20618163.8751 | 31910773.2346 | 44026909.2265 | 56281507.5922 | 56281507.5922 | 55881459.1964 | 55881459.1964 | 55881459.1964 | 55881459.1964 | 55881459.1964 | 55881459.1964 | 55881459.1964 | 55881459.1964 | 55881459.1964 | 55881459.1964 | 55881459.1964 | 55881459.1964 | 55881459.1964 | 55881459.1964 | 55881459.1964
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | 7688476.6071 | 10341571.0254 | 11867245.2349 | 14820176.3423 | 22623683.5098 | 35045553.8052 | 48373303.3964 | 61853361.5986 | 61853361.5986 | 61408863.3811 | 61408863.3811 | 61408863.3811 | 61408863.3811 | 61408863.3811 | 61408863.3811 | 61408863.3811 | 61408863.3811 | 61408863.3811 | 61408863.3811 | 61408863.3811 | 61408863.3811 | 61408863.3811 | 61408863.3811 | 61408863.3811
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | 6074741.3924 | 8098483.9137 | 9099918.7118 | 11208334.6011 | 17486709.1842 | 27650057.6077 | 38554580.0005 | 49583718.5295 | 49583718.5295 | 49139220.3121 | 49139220.3121 | 49139220.3121 | 49139220.3121 | 49139220.3121 | 49139220.3121 | 49139220.3121 | 49139220.3121 | 49139220.3121 | 49139220.3121 | 49139220.3121 | 49139220.3121 | 49139220.3121 | 49139220.3121 | 49139220.3121
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | 5956034.6851 | 7898943.1048 | 8764613.6475 | 10703839.2776 | 16923741.6561 | 27087090.0796 | 37991612.4723 | 49020751.0014 | 49020751.0014 | 48531802.9622 | 48531802.9622 | 48531802.9622 | 48531802.9622 | 48531802.9622 | 48531802.9622 | 48531802.9622 | 48531802.9622 | 48531802.9622 | 48531802.9622 | 48531802.9622 | 48531802.9622 | 48531802.9622 | 48531802.9622 | 48531802.9622
sens | 0 | 0% | 0% | Option 2sens | 0 | 6881608.9998 | 9220027.4696 | 10483581.9733 | 13014255.4717 | 20055196.347 | 31347805.7065 | 43463941.6984 | 55718540.0641 | 55718540.0641 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466
sens | 0 | 0% | 0% | Option 2sens | 0 | 6881608.9998 | 9220027.4696 | 10483581.9733 | 13014255.4717 | 20055196.347 | 31347805.7065 | 43463941.6984 | 55718540.0641 | 55718540.0641 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466
sens | 0 | 0% | 0% | Option 2sens | 0 | 6881608.9998 | 9220027.4696 | 10483581.9733 | 13014255.4717 | 20055196.347 | 31347805.7065 | 43463941.6984 | 55718540.0641 | 55718540.0641 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466 | 55274041.8466

## Option3
Powercor
Melton & Wyndham Transformation Capacity Project
OPTION 3 | Northern capacity priority
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| MTC 3rd Tx |  | 50 | 2023-12-31 | 14291649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH Rebuild |  | 50 | 2023-12-31 | 13551742.6667 | 13551742.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New RBE ZSS |  | 50 | 2023-12-31 | 0 | 5291808.87 | 17564061.24 | 16105016.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PCK Stage 1 |  | 50 | 2023-12-31 | 0 | 0 | 5408395.3 | 24162535.9333 | 22120559.4333 | 0 | 0 | 0 | 0 | 10425980.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 27843391.6667 | 18843551.5367 | 22972456.54 | 40267552.8233 | 22120559.4333 | 0 | 0 | 0 | 0 | 10425980.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 126.0532 | 22.5354 | 14.2301 | 21.2724 | 10.2581 | 6.6998 | 12.5319 | 21.1913 | 21.1913 | 21.1913 | 21.1913 | 21.1913 | 21.1913 | 21.1913 | 21.1913 | 21.1913 | 21.1913 | 21.1913 | 21.1913 | 21.1913 | 21.1913 | 21.1913 | 21.1913 | 21.1913 | 21.1913
| Energy at risk value | $/MWh | 42566 | 2023-12-31 | 5365580.8534 | 959241.3088 | 605718.4011 | 905482.242 | 436644.5037 | 285184.6456 | 533431.9039 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 5365580.8534 | 959241.3088 | 605718.4011 | 905482.242 | 436644.5037 | 285184.6456 | 533431.9039 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186 | 902027.8186
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 8068753.445 | 11215677.2383 | 13837146.2032 | 18464118.87 | 25697271.362 | 36933038.3469 | 48926380.7603 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259
Capital expenditure
| MTC 3rd Tx |  |  | 2023-12-31 | -14291649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH Rebuild |  |  | 2023-12-31 | -13551742.6667 | -13551742.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New RBE ZSS |  |  | 2023-12-31 | 0 | -5291808.87 | -17564061.24 | -16105016.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PCK Stage 1 |  |  | 2023-12-31 | 0 | 0 | -5408395.3 | -24162535.9333 | -22120559.4333 | 0 | 0 | 0 | 0 | -10425980.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| MTC 3rd Tx |  |  | 2023-12-31 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649
| BMH Rebuild |  |  | 2023-12-31 | -13551742.6667 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333
| New RBE ZSS |  |  | 2023-12-31 | 0 | -5291808.87 | -22855870.11 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887
| PCK Stage 1 |  |  | 2023-12-31 | 0 | 0 | -5408395.3 | -29570931.2333 | -51691490.6667 | -51691490.6667 | -51691490.6667 | -51691490.6667 | -51691490.6667 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471
Annualised capex
| Annualised capex - MTC 3rd Tx |  |  | 2023-12-31 | 0 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127
| Annualised capex - BMH Rebuild |  |  | 2023-12-31 | 0 | -577761.061 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219
| Annualised capex - New RBE ZSS |  |  | 2023-12-31 | 0 | 0 | -225609.4424 | -974430.5282 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408
| Annualised capex - PCK Stage 1 |  |  | 2023-12-31 | 0 | 0 | 0 | -230579.9544 | -1260718.4938 | -2203800.0001 | -2203800.0001 | -2203800.0001 | -2203800.0001 | -2203800.0001 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176
| Total annualised capex |  |  | 2023-12-31 | 0 | -1187067.0737 | -1990437.5771 | -2969838.6172 | -4686593.7693 | -5629675.2756 | -5629675.2756 | -5629675.2756 | -5629675.2756 | -5629675.2756 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931
| Annualised capex |  |  | 2023-12-31 | 0 | -1187067.0737 | -1990437.5771 | -2969838.6172 | -4686593.7693 | -5629675.2756 | -5629675.2756 | -5629675.2756 | -5629675.2756 | -5629675.2756 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 8068753.445 | 11215677.2383 | 13837146.2032 | 18464118.87 | 25697271.362 | 36933038.3469 | 48926380.7603 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 6881686.3713 | 9225239.6613 | 10867307.5859 | 13777525.1008 | 20067596.0864 | 31303363.0713 | 43296705.4847 | 55551303.8503 | 55551303.8503 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | 6881686.3713 | 9225239.6613 | 10867307.5859 | 13777525.1008 | 20067596.0864 | 31303363.0713 | 43296705.4847 | 55551303.8503 | 55551303.8503 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329
| Total annualised capex |  |  |  | 0 | -1187067.0737 | -1990437.5771 | -2969838.6172 | -4686593.7693 | -5629675.2756 | -5629675.2756 | -5629675.2756 | -5629675.2756 | -5629675.2756 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931 | -6074173.4931
| Total benefits |  |  |  | 0 | 8068753.445 | 11215677.2383 | 13837146.2032 | 18464118.87 | 25697271.362 | 36933038.3469 | 48926380.7603 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259 | 61180979.1259
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | 6762979.664 | 9026195.9036 | 10570323.7242 | 13308865.7238 | 19504628.5589 | 30740395.5437 | 42733737.9571 | 54988336.3228 | 54988336.3228 | 54499388.2836 | 54499388.2836 | 54499388.2836 | 54499388.2836 | 54499388.2836 | 54499388.2836 | 54499388.2836 | 54499388.2836 | 54499388.2836 | 54499388.2836 | 54499388.2836 | 54499388.2836 | 54499388.2836 | 54499388.2836 | 54499388.2836
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | 7000393.0787 | 9424283.419 | 11164291.4476 | 14246184.4777 | 20630563.614 | 31866330.5988 | 43859673.0123 | 56114271.3779 | 56114271.3779 | 55714222.9822 | 55714222.9822 | 55714222.9822 | 55714222.9822 | 55714222.9822 | 55714222.9822 | 55714222.9822 | 55714222.9822 | 55714222.9822 | 55714222.9822 | 55714222.9822 | 55714222.9822 | 55714222.9822 | 55714222.9822 | 55714222.9822
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | 7688561.7158 | 10346807.3851 | 12251022.2062 | 15623936.9878 | 22637323.2226 | 34996666.9059 | 48189343.5607 | 61669401.7629 | 61669401.7629 | 61224903.5455 | 61224903.5455 | 61224903.5455 | 61224903.5455 | 61224903.5455 | 61224903.5455 | 61224903.5455 | 61224903.5455 | 61224903.5455 | 61224903.5455 | 61224903.5455 | 61224903.5455 | 61224903.5455 | 61224903.5455 | 61224903.5455
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | 6074811.0268 | 8103671.9374 | 9483592.9656 | 11931113.2138 | 17497868.9502 | 27610059.2366 | 38404067.4087 | 49433205.9377 | 49433205.9377 | 48988707.7203 | 48988707.7203 | 48988707.7203 | 48988707.7203 | 48988707.7203 | 48988707.7203 | 48988707.7203 | 48988707.7203 | 48988707.7203 | 48988707.7203 | 48988707.7203 | 48988707.7203 | 48988707.7203 | 48988707.7203 | 48988707.7203
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | 5956104.3195 | 7904628.1797 | 9186609.1039 | 11462453.8368 | 16934901.4227 | 27047091.709 | 37841099.8811 | 48870238.4102 | 48870238.4102 | 48381290.371 | 48381290.371 | 48381290.371 | 48381290.371 | 48381290.371 | 48381290.371 | 48381290.371 | 48381290.371 | 48381290.371 | 48381290.371 | 48381290.371 | 48381290.371 | 48381290.371 | 48381290.371 | 48381290.371
sens | 0 | 0% | 0% | Option 3sens | 0 | 6881686.3713 | 9225239.6613 | 10867307.5859 | 13777525.1008 | 20067596.0864 | 31303363.0713 | 43296705.4847 | 55551303.8503 | 55551303.8503 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329
sens | 0 | 0% | 0% | Option 3sens | 0 | 6881686.3713 | 9225239.6613 | 10867307.5859 | 13777525.1008 | 20067596.0864 | 31303363.0713 | 43296705.4847 | 55551303.8503 | 55551303.8503 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329
sens | 0 | 0% | 0% | Option 3sens | 0 | 6881686.3713 | 9225239.6613 | 10867307.5859 | 13777525.1008 | 20067596.0864 | 31303363.0713 | 43296705.4847 | 55551303.8503 | 55551303.8503 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329 | 55106805.6329

## Option4
Powercor
Melton & Wyndham Transformation Capacity Project
OPTION 4 | Lean investment, Northern capacity priority
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| MTC 3rd Tx |  | 50 | 2023-12-31 | 14291649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New RBE ZSS |  | 50 | 2023-12-31 | 5291808.87 | 17564061.24 | 16105016.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PCK Stage 1 |  | 50 | 2023-12-31 | 0 | 5408395.3 | 24162535.9333 | 22120559.4333 | 0 | 0 | 0 | 0 | 0 | 10425980.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 19583457.87 | 22972456.54 | 40267552.8233 | 22120559.4333 | 0 | 0 | 0 | 0 | 0 | 10425980.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 126.0532 | 22.5354 | 53.3133 | 22.7281 | 22.8741 | 34.5662 | 58.8615 | 91.4439 | 91.4439 | 91.4439 | 91.4439 | 91.4439 | 91.4439 | 91.4439 | 91.4439 | 91.4439 | 91.4439 | 91.4439 | 91.4439 | 91.4439 | 91.4439 | 91.4439 | 91.4439 | 91.4439 | 91.4439
| Energy at risk value | $/MWh | 42566 | 2023-12-31 | 5365580.8534 | 959241.3088 | 2269332.9881 | 967443.2567 | 973657.6247 | 1471344.6013 | 2505499.1337 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 5365580.8534 | 959241.3088 | 2269332.9881 | 967443.2567 | 973657.6247 | 1471344.6013 | 2505499.1337 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128 | 3892400.5128
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 8068753.445 | 9552062.6513 | 13775185.1884 | 17927105.749 | 24511111.4063 | 34960971.1171 | 45936008.0661 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317
Capital expenditure
| MTC 3rd Tx |  |  | 2023-12-31 | -14291649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New RBE ZSS |  |  | 2023-12-31 | -5291808.87 | -17564061.24 | -16105016.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PCK Stage 1 |  |  | 2023-12-31 | 0 | -5408395.3 | -24162535.9333 | -22120559.4333 | 0 | 0 | 0 | 0 | 0 | -10425980.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| MTC 3rd Tx |  |  | 2023-12-31 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649
| New RBE ZSS |  |  | 2023-12-31 | -5291808.87 | -22855870.11 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887 | -38960887
| PCK Stage 1 |  |  | 2023-12-31 | 0 | -5408395.3 | -29570931.2333 | -51691490.6667 | -51691490.6667 | -51691490.6667 | -51691490.6667 | -51691490.6667 | -51691490.6667 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - MTC 3rd Tx |  |  | 2023-12-31 | 0 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127
| Annualised capex - New RBE ZSS |  |  | 2023-12-31 | 0 | -225609.4424 | -974430.5282 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408 | -1661047.1408
| Annualised capex - PCK Stage 1 |  |  | 2023-12-31 | 0 | 0 | -230579.9544 | -1260718.4938 | -2203800.0001 | -2203800.0001 | -2203800.0001 | -2203800.0001 | -2203800.0001 | -2203800.0001 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -834915.4551 | -1814316.4953 | -3531071.6473 | -4474153.1537 | -4474153.1537 | -4474153.1537 | -4474153.1537 | -4474153.1537 | -4474153.1537 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711
| Annualised capex |  |  | 2023-12-31 | 0 | -834915.4551 | -1814316.4953 | -3531071.6473 | -4474153.1537 | -4474153.1537 | -4474153.1537 | -4474153.1537 | -4474153.1537 | -4474153.1537 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 8068753.445 | 9552062.6513 | 13775185.1884 | 17927105.749 | 24511111.4063 | 34960971.1171 | 45936008.0661 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 7233837.9899 | 7737746.156 | 10244113.5411 | 13452952.5954 | 20036958.2526 | 30486817.9635 | 41461854.9124 | 53716453.2781 | 53716453.2781 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | 7233837.9899 | 7737746.156 | 10244113.5411 | 13452952.5954 | 20036958.2526 | 30486817.9635 | 41461854.9124 | 53716453.2781 | 53716453.2781 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606
| Total annualised capex |  |  |  | 0 | -834915.4551 | -1814316.4953 | -3531071.6473 | -4474153.1537 | -4474153.1537 | -4474153.1537 | -4474153.1537 | -4474153.1537 | -4474153.1537 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711 | -4918651.3711
| Total benefits |  |  |  | 0 | 8068753.445 | 9552062.6513 | 13775185.1884 | 17927105.749 | 24511111.4063 | 34960971.1171 | 45936008.0661 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317 | 58190606.4317
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | 7150346.4443 | 7556314.5064 | 9891006.3764 | 13005537.28 | 19589542.9373 | 30039402.6481 | 41014439.5971 | 53269037.9627 | 53269037.9627 | 52780089.9235 | 52780089.9235 | 52780089.9235 | 52780089.9235 | 52780089.9235 | 52780089.9235 | 52780089.9235 | 52780089.9235 | 52780089.9235 | 52780089.9235 | 52780089.9235 | 52780089.9235 | 52780089.9235 | 52780089.9235 | 52780089.9235
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | 7317329.5354 | 7919177.8055 | 10597220.7058 | 13900367.9108 | 20484373.568 | 30934233.2788 | 41909270.2278 | 54163868.5934 | 54163868.5934 | 53763820.1977 | 53763820.1977 | 53763820.1977 | 53763820.1977 | 53763820.1977 | 53763820.1977 | 53763820.1977 | 53763820.1977 | 53763820.1977 | 53763820.1977 | 53763820.1977 | 53763820.1977 | 53763820.1977 | 53763820.1977 | 53763820.1977
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | 8040713.3343 | 8692952.4211 | 11621632.0599 | 15245663.1703 | 22488069.3933 | 33982915.0752 | 46055455.719 | 59535513.9212 | 59535513.9212 | 59091015.7037 | 59091015.7037 | 59091015.7037 | 59091015.7037 | 59091015.7037 | 59091015.7037 | 59091015.7037 | 59091015.7037 | 59091015.7037 | 59091015.7037 | 59091015.7037 | 59091015.7037 | 59091015.7037 | 59091015.7037 | 59091015.7037
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | 6426962.6454 | 6782539.8908 | 8866595.0223 | 11660242.0205 | 17585847.112 | 26990720.8517 | 36868254.1058 | 47897392.6349 | 47897392.6349 | 47452894.4174 | 47452894.4174 | 47452894.4174 | 47452894.4174 | 47452894.4174 | 47452894.4174 | 47452894.4174 | 47452894.4174 | 47452894.4174 | 47452894.4174 | 47452894.4174 | 47452894.4174 | 47452894.4174 | 47452894.4174 | 47452894.4174
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | 6343471.0998 | 6601108.2413 | 8513487.8575 | 11212826.7051 | 17138431.7966 | 26543305.5364 | 36420838.7904 | 47449977.3195 | 47449977.3195 | 46961029.2803 | 46961029.2803 | 46961029.2803 | 46961029.2803 | 46961029.2803 | 46961029.2803 | 46961029.2803 | 46961029.2803 | 46961029.2803 | 46961029.2803 | 46961029.2803 | 46961029.2803 | 46961029.2803 | 46961029.2803 | 46961029.2803
sens | 0 | 0% | 0% | Option 4sens | 0 | 7233837.9899 | 7737746.156 | 10244113.5411 | 13452952.5954 | 20036958.2526 | 30486817.9635 | 41461854.9124 | 53716453.2781 | 53716453.2781 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606
sens | 0 | 0% | 0% | Option 4sens | 0 | 7233837.9899 | 7737746.156 | 10244113.5411 | 13452952.5954 | 20036958.2526 | 30486817.9635 | 41461854.9124 | 53716453.2781 | 53716453.2781 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606
sens | 0 | 0% | 0% | Option 4sens | 0 | 7233837.9899 | 7737746.156 | 10244113.5411 | 13452952.5954 | 20036958.2526 | 30486817.9635 | 41461854.9124 | 53716453.2781 | 53716453.2781 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606 | 53271955.0606

## Option5
Powercor
Melton & Wyndham Transformation Capacity Project
OPTION 5 | Lean investment, Southern capacity priority
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| MTC 3rd Tx |  | 50 | 2023-12-31 | 14291649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH Rebuild |  | 50 | 2023-12-31 | 13551742.6667 | 13551742.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PCK Stage 1 |  | 50 | 2023-12-31 | 0 | 5483395.3 | 29525526.1 | 27108549.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 27843391.6667 | 19035137.9667 | 29525526.1 | 27108549.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 126.0532 | 22.5354 | 14.2301 | 21.2724 | 18.0455 | 36.3792 | 77.0458 | 126.4342 | 126.4342 | 126.4342 | 126.4342 | 126.4342 | 126.4342 | 126.4342 | 126.4342 | 126.4342 | 126.4342 | 126.4342 | 126.4342 | 126.4342 | 126.4342 | 126.4342 | 126.4342 | 126.4342 | 126.4342
| Energy at risk value | $/MWh | 42566 | 2023-12-31 | 5365580.8534 | 959241.3088 | 605718.4011 | 905482.242 | 768123.7302 | 1548516.1941 | 3279533.1157 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 5365580.8534 | 959241.3088 | 605718.4011 | 905482.242 | 768123.7302 | 1548516.1941 | 3279533.1157 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487 | 5381799.8487
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 8068753.445 | 11215677.2383 | 13837146.2032 | 18132639.6435 | 24433939.8135 | 34186937.1351 | 44446608.7302 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959
Capital expenditure
| MTC 3rd Tx |  |  | 2023-12-31 | -14291649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BMH Rebuild |  |  | 2023-12-31 | -13551742.6667 | -13551742.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PCK Stage 1 |  |  | 2023-12-31 | 0 | -5483395.3 | -29525526.1 | -27108549.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| MTC 3rd Tx |  |  | 2023-12-31 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649 | -14291649
| BMH Rebuild |  |  | 2023-12-31 | -13551742.6667 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333 | -27103485.3333
| PCK Stage 1 |  |  | 2023-12-31 | 0 | -5483395.3 | -35008921.4 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471 | -62117471
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - MTC 3rd Tx |  |  | 2023-12-31 | 0 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127 | -609306.0127
| Annualised capex - BMH Rebuild |  |  | 2023-12-31 | 0 | -577761.061 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219 | -1155522.1219
| Annualised capex - PCK Stage 1 |  |  | 2023-12-31 | 0 | 0 | -233777.4827 | -1492560.1872 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176 | -2648298.2176
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -1187067.0737 | -1998605.6173 | -3257388.3218 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523
| Annualised capex |  |  | 2023-12-31 | 0 | -1187067.0737 | -1998605.6173 | -3257388.3218 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 8068753.445 | 11215677.2383 | 13837146.2032 | 18132639.6435 | 24433939.8135 | 34186937.1351 | 44446608.7302 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 6881686.3713 | 9217071.621 | 10579757.8813 | 13719513.2913 | 20020813.4612 | 29773810.7829 | 40033482.378 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 6881686.3713 | 9217071.621 | 10579757.8813 | 13719513.2913 | 20020813.4612 | 29773810.7829 | 40033482.378 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436
| Total annualised capex |  |  |  | 0 | -1187067.0737 | -1998605.6173 | -3257388.3218 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523 | -4413126.3523
| Total benefits |  |  |  | 0 | 8068753.445 | 11215677.2383 | 13837146.2032 | 18132639.6435 | 24433939.8135 | 34186937.1351 | 44446608.7302 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959 | 56701207.0959
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 6762979.664 | 9017211.0593 | 10254019.0491 | 13278200.6561 | 19579500.826 | 29332498.1476 | 39592169.7428 | 51846768.1084 | 51846768.1084 | 51846768.1084 | 51846768.1084 | 51846768.1084 | 51846768.1084 | 51846768.1084 | 51846768.1084 | 51846768.1084 | 51846768.1084 | 51846768.1084 | 51846768.1084 | 51846768.1084 | 51846768.1084 | 51846768.1084 | 51846768.1084 | 51846768.1084
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 7000393.0787 | 9416932.1828 | 10905496.7135 | 14160825.9265 | 20462126.0964 | 30215123.4181 | 40474795.0132 | 52729393.3788 | 52729393.3788 | 52729393.3788 | 52729393.3788 | 52729393.3788 | 52729393.3788 | 52729393.3788 | 52729393.3788 | 52729393.3788 | 52729393.3788 | 52729393.3788 | 52729393.3788 | 52729393.3788 | 52729393.3788 | 52729393.3788 | 52729393.3788 | 52729393.3788
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 7688561.7158 | 10338639.3449 | 11963472.5016 | 15532777.2556 | 22464207.4425 | 33192504.4964 | 44478143.251 | 57958201.4532 | 57958201.4532 | 57958201.4532 | 57958201.4532 | 57958201.4532 | 57958201.4532 | 57958201.4532 | 57958201.4532 | 57958201.4532 | 57958201.4532 | 57958201.4532 | 57958201.4532 | 57958201.4532 | 57958201.4532 | 57958201.4532 | 57958201.4532 | 57958201.4532
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 6074811.0268 | 8095503.8972 | 9196043.261 | 11906249.3269 | 17577419.4798 | 26355117.0693 | 35588821.505 | 46617960.034 | 46617960.034 | 46617960.034 | 46617960.034 | 46617960.034 | 46617960.034 | 46617960.034 | 46617960.034 | 46617960.034 | 46617960.034 | 46617960.034 | 46617960.034 | 46617960.034 | 46617960.034 | 46617960.034 | 46617960.034 | 46617960.034
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 5956104.3195 | 7895643.3355 | 8870304.4288 | 11464936.6917 | 17136106.8446 | 25913804.4341 | 35147508.8697 | 46176647.3988 | 46176647.3988 | 46176647.3988 | 46176647.3988 | 46176647.3988 | 46176647.3988 | 46176647.3988 | 46176647.3988 | 46176647.3988 | 46176647.3988 | 46176647.3988 | 46176647.3988 | 46176647.3988 | 46176647.3988 | 46176647.3988 | 46176647.3988 | 46176647.3988
sens | 0 | 0% | 0% | Option 5sens | 0 | 6881686.3713 | 9217071.621 | 10579757.8813 | 13719513.2913 | 20020813.4612 | 29773810.7829 | 40033482.378 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436
sens | 0 | 0% | 0% | Option 5sens | 0 | 6881686.3713 | 9217071.621 | 10579757.8813 | 13719513.2913 | 20020813.4612 | 29773810.7829 | 40033482.378 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436
sens | 0 | 0% | 0% | Option 5sens | 0 | 6881686.3713 | 9217071.621 | 10579757.8813 | 13719513.2913 | 20020813.4612 | 29773810.7829 | 40033482.378 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436 | 52288080.7436

## Consol
Powercor
Melton & Wyndham Transformation Capacity Project
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 835496363.9831 | 2026-06-30 |  | 5971422.7871 | 10047369.5333 | 13156180.7054 | 16407257.638 | 21034898.5856 | 28916203.8758 | 41696908.5587 | 55454666.0583 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 675996692.6109 | 2026-06-30 |  | 5971422.7871 | 10047369.5333 | 13156180.7054 | 16407257.638 | 21034898.5856 | 28916203.8758 | 41696908.5587 | 55454666.0583 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561 | 69092963.5561
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 18532523.9247 | 2026-06-30 |  | 5971422.7871 | 1067637.8913 | 674380.6371 | 1008294.2163 | 936576.8324 | 331185.4192 | 544202.335 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634
Option 2 | Capital expenditure | Option 2Capital expenditure | -143616359.5211 | 2026-06-30 |  | -30987262.705 | -21100977.3209 | -35439974.1932 | -44165516.2156 | -15263615.7427 | 0 | 0 | 0 | 0 | -11603205.3643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 16644744.5726 | 2026-06-30 |  | 5971422.7871 | 1067637.8913 | 674380.6371 | 1008294.2163 | 936576.8324 | 331185.4192 | 544202.335 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 817758.8634 | 0 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -76188514.8265 | 2026-06-30 |  | 0 | -1321101.9584 | -2220714.8971 | -3731652.4639 | -5614592.2551 | -6265336.8156 | -6265336.8156 | -6265336.8156 | -6265336.8156 | -6265336.8156 | -6760024.5031 | -6760024.5031 | -6760024.5031 | -6760024.5031 | -6760024.5031 | -6760024.5031 | -6760024.5031 | -6760024.5031 | -6760024.5031 | -6760024.5031 | 0 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 659351948.0382 | 2026-06-30 |  | 0 | 8979731.642 | 12481800.0683 | 15398963.4218 | 20098321.7532 | 28585018.4566 | 41152706.2237 | 54636907.1949 | 68275204.6927 | 68275204.6927 | 68275204.6927 | 68275204.6927 | 68275204.6927 | 68275204.6927 | 68275204.6927 | 68275204.6927 | 68275204.6927 | 68275204.6927 | 68275204.6927 | 68275204.6927 | 0 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | 7658629.6836 | 10261085.1712 | 11667310.9579 | 14483729.4981 | 22319681.641 | 34887369.4082 | 48371570.3793 | 62009867.8772 | 62009867.8772 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 583163433.2117 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -76188514.8265 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 659351948.0382 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 20136786.1806 | 2026-06-30 |  | 5971422.7871 | 1067551.7836 | 674111.6687 | 1007722.6382 | 485947.1902 | 317385.5986 | 593663.1119 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667
Option 3 | Capital expenditure | Option 3Capital expenditure | -143021335.7284 | 2026-06-30 |  | -30987262.705 | -20971226.8086 | -25566337.4026 | -44814268.7773 | -24618250.3392 | 0 | 0 | 0 | 0 | -11603205.3643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 17819354.2823 | 2026-06-30 |  | 5971422.7871 | 1067551.7836 | 674111.6687 | 1007722.6382 | 485947.1902 | 317385.5986 | 593663.1119 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 1003878.1667 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -75463712.872 | 2026-06-30 |  | 0 | -1321101.9584 | -2215183.1514 | -3305170.9549 | -5215769.4744 | -6265336.8094 | -6265336.8094 | -6265336.8094 | -6265336.8094 | -6265336.8094 | -6760024.497 | -6760024.497 | -6760024.497 | -6760024.497 | -6760024.497 | -6760024.497 | -6760024.497 | -6760024.497 | -6760024.497 | -6760024.497 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 658177338.3286 | 2026-06-30 |  | 0 | 8979817.7497 | 12482069.0367 | 15399534.9998 | 20548951.3954 | 28598818.2772 | 41103245.4468 | 54450787.8915 | 68089085.3894 | 68089085.3894 | 68089085.3894 | 68089085.3894 | 68089085.3894 | 68089085.3894 | 68089085.3894 | 68089085.3894 | 68089085.3894 | 68089085.3894 | 68089085.3894 | 68089085.3894 | 0 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | 7658715.7913 | 10266885.8852 | 12094364.0449 | 15333181.921 | 22333481.4678 | 34837908.6374 | 48185451.0821 | 61823748.58 | 61823748.58 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | 582713625.4566 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -75463712.872 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 658177338.3286 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 60356344.0602 | 2026-06-30 |  | 5971422.7871 | 1067551.7836 | 2525569.3814 | 1076679.8351 | 1083595.8839 | 1637478.014 | 2788401.6715 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556
Option 4 | Capital expenditure | Option 4Capital expenditure | -117018719.1259 | 2026-06-30 |  | -21794677.9241 | -25566337.4026 | -44814268.7773 | -24618250.3392 | 0 | 0 | 0 | 0 | 0 | -11603205.3643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 50356238.8269 | 2026-06-30 |  | 5971422.7871 | 1067551.7836 | 2525569.3814 | 1076679.8351 | 1083595.8839 | 1637478.014 | 2788401.6715 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 4331901.7556 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | -62575776.7481 | 2026-06-30 |  | 0 | -929187.9687 | -2019175.7722 | -3929774.2917 | -4979341.6267 | -4979341.6267 | -4979341.6267 | -4979341.6267 | -4979341.6267 | -4979341.6267 | -5474029.3142 | -5474029.3142 | -5474029.3142 | -5474029.3142 | -5474029.3142 | -5474029.3142 | -5474029.3142 | -5474029.3142 | -5474029.3142 | -5474029.3142 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 625640453.784 | 2026-06-30 |  | 0 | 8979817.7497 | 10630611.324 | 15330577.8029 | 19951302.7018 | 27278725.8618 | 38908506.8872 | 51122764.3026 | 64761061.8005 | 64761061.8005 | 64761061.8005 | 64761061.8005 | 64761061.8005 | 64761061.8005 | 64761061.8005 | 64761061.8005 | 64761061.8005 | 64761061.8005 | 64761061.8005 | 64761061.8005 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | 8050629.781 | 8611435.5517 | 11400803.5112 | 14971961.075 | 22299384.2351 | 33929165.2605 | 46143422.6759 | 59781720.1738 | 59781720.1738 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 563064677.0359 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | -62575776.7481 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 625640453.784 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 76642424.9492 | 2026-06-30 |  | 5971422.7871 | 1067551.7836 | 674111.6687 | 1007722.6382 | 854854.6134 | 1723363.2556 | 3649833.8788 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121
Option 5 | Capital expenditure | Option 5Capital expenditure | -107476316.8861 | 2026-06-30 |  | -30987262.705 | -21184445.7694 | -32859331.3888 | -30169447.6759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 62815850.6658 | 2026-06-30 |  | 5971422.7871 | 1067551.7836 | 674111.6687 | 1007722.6382 | 854854.6134 | 1723363.2556 | 3649833.8788 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 5989473.1121 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | -59170738.7919 | 2026-06-30 |  | 0 | -1321101.9584 | -2224273.4667 | -3625188.6577 | -4911424.1277 | -4911424.1277 | -4911424.1277 | -4911424.1277 | -4911424.1277 | -4911424.1277 | -4911424.1277 | -4911424.1277 | -4911424.1277 | -4911424.1277 | -4911424.1277 | -4911424.1277 | -4911424.1277 | -4911424.1277 | -4911424.1277 | -4911424.1277 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 613180841.945 | 2026-06-30 |  | 0 | 8979817.7497 | 12482069.0367 | 15399534.9998 | 20180043.9722 | 27192840.6202 | 38047074.6799 | 49465192.9462 | 63103490.4441 | 63103490.4441 | 63103490.4441 | 63103490.4441 | 63103490.4441 | 63103490.4441 | 63103490.4441 | 63103490.4441 | 63103490.4441 | 63103490.4441 | 63103490.4441 | 63103490.4441 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 7658715.7913 | 10257795.57 | 11774346.3421 | 15268619.8445 | 22281416.4925 | 33135650.5523 | 44553768.8186 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 554010103.1531 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | -59170738.7919 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 613180841.945 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 6.76 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 5.9714 | 10.0474 | 13.1562 | 16.4073 | 21.0349 | 28.9162 | 41.6969 | 55.4547 | 69.093 | 69.093 | 69.093 | 69.093 | 69.093 | 69.093 | 69.093 | 69.093 | 69.093 | 69.093 | 69.093 | 69.093 | 69.093 | 69.093 | 69.093 | 69.093 | 69.093
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 1458.5117 |  |  | Energy at risk energy at risk (weighted) | 126.0532 | 212.094 | 277.7192 | 346.3475 | 444.0343 | 610.404 | 880.1971 | 1170.6152 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117 | 1458.5117
Option 1 (base case) | Energy at risk value | 62.083 |  |  | Option 1 (base case) risk cost | 5.3656 | 9.028 | 11.8214 | 14.7426 | 18.9008 | 25.9825 | 37.4665 | 49.8284 | 62.083 | 62.083 | 62.083 | 62.083 | 62.083 | 62.083 | 62.083 | 62.083 | 62.083 | 62.083 | 62.083 | 62.083 | 62.083 | 62.083 | 62.083 | 62.083 | 62.083

## Sensitivity_calcs
Powercor
Melton & Wyndham Transformation Capacity Project
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
[7 empty] | 46203 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 61515180.1896 | 61515180.1896 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 583163433.2117 |  | 0 | 0 | 7658629.6836 | 10261085.1712 | 11667310.9579 | 14483729.4981 | 22319681.641 | 34887369.4082 | 48371570.3793 | 62009867.8772 | 62009867.8772 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 0 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 575544581.729 |  | 0 | 0 | 7526519.4877 | 10039013.6815 | 11294145.7115 | 13922270.2726 | 21693147.9594 | 34260835.7266 | 47745036.6977 | 61383334.1956 | 61383334.1956 | 60839177.7393 | 60839177.7393 | 60839177.7393 | 60839177.7393 | 60839177.7393 | 60839177.7393 | 60839177.7393 | 60839177.7393 | 60839177.7393 | 60839177.7393 | 0 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 590782284.6943 |  | 0 | 0 | 7790739.8794 | 10483156.6609 | 12040476.2043 | 15045188.7236 | 22946215.3225 | 35513903.0897 | 48998104.0608 | 62636401.5587 | 62636401.5587 | 62191182.6399 | 62191182.6399 | 62191182.6399 | 62191182.6399 | 62191182.6399 | 62191182.6399 | 62191182.6399 | 62191182.6399 | 62191182.6399 | 62191182.6399 | 0 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 649098628.0155 |  | 0 | 0 | 8556602.8478 | 11509265.178 | 13207207.3001 | 16493561.6734 | 25178183.4866 | 39002640.0305 | 53835261.0988 | 68837388.3464 | 68837388.3464 | 68342700.6589 | 68342700.6589 | 68342700.6589 | 68342700.6589 | 68342700.6589 | 68342700.6589 | 68342700.6589 | 68342700.6589 | 68342700.6589 | 68342700.6589 | 0 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 517228238.4079 |  | 0 | 0 | 6760656.5194 | 9012905.1644 | 10127414.6157 | 12473897.3228 | 19461179.7953 | 30772098.7858 | 42907879.6598 | 55182347.4079 | 55182347.4079 | 54687659.7203 | 54687659.7203 | 54687659.7203 | 54687659.7203 | 54687659.7203 | 54687659.7203 | 54687659.7203 | 54687659.7203 | 54687659.7203 | 54687659.7203 | 0 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 509609386.9252 |  | 0 | 0 | 6628546.3235 | 8790833.6746 | 9754249.3693 | 11912438.0973 | 18834646.1138 | 30145565.1042 | 42281345.9782 | 54555813.7263 | 54555813.7263 | 54011657.27 | 54011657.27 | 54011657.27 | 54011657.27 | 54011657.27 | 54011657.27 | 54011657.27 | 54011657.27 | 54011657.27 | 54011657.27 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 583163433.2117 |  | 0 | 0 | 7658629.6836 | 10261085.1712 | 11667310.9579 | 14483729.4981 | 22319681.641 | 34887369.4082 | 48371570.3793 | 62009867.8772 | 62009867.8772 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 583163433.2117 |  | 0 | 0 | 7658629.6836 | 10261085.1712 | 11667310.9579 | 14483729.4981 | 22319681.641 | 34887369.4082 | 48371570.3793 | 62009867.8772 | 62009867.8772 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 583163433.2117 |  | 0 | 0 | 7658629.6836 | 10261085.1712 | 11667310.9579 | 14483729.4981 | 22319681.641 | 34887369.4082 | 48371570.3793 | 62009867.8772 | 62009867.8772 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 61515180.1896 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 7658715.7913 | 10266885.8852 | 12094364.0449 | 15333181.921 | 22333481.4678 | 34837908.6374 | 48185451.0821 | 61823748.58 | 61823748.58 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 582713625.4566 |  | 0 | 0 | 7658715.7913 | 10266885.8852 | 12094364.0449 | 15333181.921 | 22333481.4678 | 34837908.6374 | 48185451.0821 | 61823748.58 | 61823748.58 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 0 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 575167254.1694 |  | 0 | 0 | 7526605.5955 | 10045367.5701 | 11763846.9494 | 14811604.9735 | 21706947.7868 | 34211374.9564 | 47558917.4012 | 61197214.899 | 61197214.899 | 60653058.4427 | 60653058.4427 | 60653058.4427 | 60653058.4427 | 60653058.4427 | 60653058.4427 | 60653058.4427 | 60653058.4427 | 60653058.4427 | 60653058.4427 | 0 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 590259996.7438 |  | 0 | 0 | 7790825.9872 | 10488404.2004 | 12424881.1404 | 15854758.8684 | 22960015.1487 | 35464442.3183 | 48811984.763 | 62450282.2609 | 62450282.2609 | 62005063.3421 | 62005063.3421 | 62005063.3421 | 62005063.3421 | 62005063.3421 | 62005063.3421 | 62005063.3421 | 62005063.3421 | 62005063.3421 | 62005063.3421 | 0 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 648531359.2894 |  | 0 | 0 | 8556697.5663 | 11515092.7889 | 13634317.5448 | 17388077.0605 | 25193363.2955 | 38948233.1821 | 53630529.8713 | 68632657.1189 | 68632657.1189 | 68137969.4314 | 68137969.4314 | 68137969.4314 | 68137969.4314 | 68137969.4314 | 68137969.4314 | 68137969.4314 | 68137969.4314 | 68137969.4314 | 68137969.4314 | 0 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | 516895891.6237 |  | 0 | 0 | 6760734.0163 | 9018678.9816 | 10554410.5449 | 13278286.7814 | 19473599.64 | 30727584.0927 | 42740372.2929 | 55014840.041 | 55014840.041 | 54520152.3535 | 54520152.3535 | 54520152.3535 | 54520152.3535 | 54520152.3535 | 54520152.3535 | 54520152.3535 | 54520152.3535 | 54520152.3535 | 54520152.3535 | 0 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | 509349520.3365 |  | 0 | 0 | 6628623.8205 | 8797160.6664 | 10223893.4494 | 12756709.834 | 18847065.9591 | 30101050.4118 | 42113838.612 | 54388306.3601 | 54388306.3601 | 53844149.9038 | 53844149.9038 | 53844149.9038 | 53844149.9038 | 53844149.9038 | 53844149.9038 | 53844149.9038 | 53844149.9038 | 53844149.9038 | 53844149.9038 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 582713625.4566 |  | 0 | 0 | 7658715.7913 | 10266885.8852 | 12094364.0449 | 15333181.921 | 22333481.4678 | 34837908.6374 | 48185451.0821 | 61823748.58 | 61823748.58 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 582713625.4566 |  | 0 | 0 | 7658715.7913 | 10266885.8852 | 12094364.0449 | 15333181.921 | 22333481.4678 | 34837908.6374 | 48185451.0821 | 61823748.58 | 61823748.58 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 582713625.4566 |  | 0 | 0 | 7658715.7913 | 10266885.8852 | 12094364.0449 | 15333181.921 | 22333481.4678 | 34837908.6374 | 48185451.0821 | 61823748.58 | 61823748.58 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 61329060.8924 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 563064677.0359 |  | 0 | 0 | 8050629.781 | 8611435.5517 | 11400803.5112 | 14971961.075 | 22299384.2351 | 33929165.2605 | 46143422.6759 | 59781720.1738 | 59781720.1738 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 556807099.3611 |  | 0 | 0 | 7957710.9842 | 8409517.9745 | 11007826.0821 | 14474026.9124 | 21801450.0724 | 33431231.0979 | 45645488.5132 | 59283786.0111 | 59283786.0111 | 58739629.5548 | 58739629.5548 | 58739629.5548 | 58739629.5548 | 58739629.5548 | 58739629.5548 | 58739629.5548 | 58739629.5548 | 58739629.5548 | 58739629.5548 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 569322254.7107 |  | 0 | 0 | 8143548.5779 | 8813353.129 | 11793780.9404 | 15469895.2377 | 22797318.3977 | 34427099.4232 | 46641356.8386 | 60279654.3365 | 60279654.3365 | 59834435.4177 | 59834435.4177 | 59834435.4177 | 59834435.4177 | 59834435.4177 | 59834435.4177 | 59834435.4177 | 59834435.4177 | 59834435.4177 | 59834435.4177 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 625628722.4143 |  | 0 | 0 | 8948611.556 | 9674496.6841 | 12933861.2915 | 16967091.3452 | 25027256.8212 | 37820015.9492 | 51255699.1062 | 66257826.3538 | 66257826.3538 | 65763138.6663 | 65763138.6663 | 65763138.6663 | 65763138.6663 | 65763138.6663 | 65763138.6663 | 65763138.6663 | 65763138.6663 | 65763138.6663 | 65763138.6663 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 500500631.6575 |  | 0 | 0 | 7152648.0061 | 7548374.4193 | 9867745.7309 | 12976830.8049 | 19571511.6489 | 30038314.5718 | 41031146.2457 | 53305613.9937 | 53305613.9937 | 52810926.3062 | 52810926.3062 | 52810926.3062 | 52810926.3062 | 52810926.3062 | 52810926.3062 | 52810926.3062 | 52810926.3062 | 52810926.3062 | 52810926.3062 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 494243053.9827 |  | 0 | 0 | 7059729.2092 | 7346456.8421 | 9474768.3018 | 12478896.6422 | 19073577.4862 | 29540380.4091 | 40533212.083 | 52807679.8311 | 52807679.8311 | 52263523.3748 | 52263523.3748 | 52263523.3748 | 52263523.3748 | 52263523.3748 | 52263523.3748 | 52263523.3748 | 52263523.3748 | 52263523.3748 | 52263523.3748 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 563064677.0359 |  | 0 | 0 | 8050629.781 | 8611435.5517 | 11400803.5112 | 14971961.075 | 22299384.2351 | 33929165.2605 | 46143422.6759 | 59781720.1738 | 59781720.1738 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 563064677.0359 |  | 0 | 0 | 8050629.781 | 8611435.5517 | 11400803.5112 | 14971961.075 | 22299384.2351 | 33929165.2605 | 46143422.6759 | 59781720.1738 | 59781720.1738 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 563064677.0359 |  | 0 | 0 | 8050629.781 | 8611435.5517 | 11400803.5112 | 14971961.075 | 22299384.2351 | 33929165.2605 | 46143422.6759 | 59781720.1738 | 59781720.1738 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 59287032.4863 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 554010103.1531 |  | 0 | 0 | 7658715.7913 | 10257795.57 | 11774346.3421 | 15268619.8445 | 22281416.4925 | 33135650.5523 | 44553768.8186 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 548093029.2739 |  | 0 | 0 | 7526605.5955 | 10035368.2233 | 11411827.4764 | 14777477.4318 | 21790274.0797 | 32644508.1395 | 44062626.4058 | 57700923.9037 | 57700923.9037 | 57700923.9037 | 57700923.9037 | 57700923.9037 | 57700923.9037 | 57700923.9037 | 57700923.9037 | 57700923.9037 | 57700923.9037 | 57700923.9037 | 57700923.9037 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 559927177.0323 |  | 0 | 0 | 7790825.9872 | 10480222.9167 | 12136865.2079 | 15759762.2573 | 22772558.9053 | 33626792.965 | 45044911.2313 | 58683208.7292 | 58683208.7292 | 58683208.7292 | 58683208.7292 | 58683208.7292 | 58683208.7292 | 58683208.7292 | 58683208.7292 | 58683208.7292 | 58683208.7292 | 58683208.7292 | 58683208.7292 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 615328187.3476 |  | 0 | 0 | 8556697.5663 | 11506002.4737 | 13314299.8421 | 17286624.2418 | 25000700.5545 | 36940358.0202 | 49500288.1132 | 64502415.3608 | 64502415.3608 | 64502415.3608 | 64502415.3608 | 64502415.3608 | 64502415.3608 | 64502415.3608 | 64502415.3608 | 64502415.3608 | 64502415.3608 | 64502415.3608 | 64502415.3608 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 492692018.9586 |  | 0 | 0 | 6760734.0163 | 9009588.6663 | 10234392.8422 | 13250615.4473 | 19562132.4305 | 29330943.0843 | 39607249.5239 | 51881717.272 | 51881717.272 | 51881717.272 | 51881717.272 | 51881717.272 | 51881717.272 | 51881717.272 | 51881717.272 | 51881717.272 | 51881717.272 | 51881717.272 | 51881717.272 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 486774945.0794 |  | 0 | 0 | 6628623.8205 | 8787161.3197 | 9871873.9764 | 12759473.0346 | 19070990.0177 | 28839800.6715 | 39116107.1112 | 51390574.8593 | 51390574.8593 | 51390574.8593 | 51390574.8593 | 51390574.8593 | 51390574.8593 | 51390574.8593 | 51390574.8593 | 51390574.8593 | 51390574.8593 | 51390574.8593 | 51390574.8593 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 554010103.1531 |  | 0 | 0 | 7658715.7913 | 10257795.57 | 11774346.3421 | 15268619.8445 | 22281416.4925 | 33135650.5523 | 44553768.8186 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 554010103.1531 |  | 0 | 0 | 7658715.7913 | 10257795.57 | 11774346.3421 | 15268619.8445 | 22281416.4925 | 33135650.5523 | 44553768.8186 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 554010103.1531 |  | 0 | 0 | 7658715.7913 | 10257795.57 | 11774346.3421 | 15268619.8445 | 22281416.4925 | 33135650.5523 | 44553768.8186 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 58192066.3164 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 0 | 0 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 583.1634 | 582.7136 | 563.0647 | 554.0101 |  | 2026-27: #NAME?; 2028-29: Option 2
sens1 | Capex 10% higher | 0 | 575.5446 | 575.1673 | 556.8071 | 548.093 |  | 2026-27: #NAME?; 2028-29: Option 2
sens2 | Capex 10% lower | 0 | 590.7823 | 590.26 | 569.3223 | 559.9272 |  | 2026-27: #NAME?; 2028-29: Option 2
sens3 | Total benefits 10% higher | 0 | 649.0986 | 648.5314 | 625.6287 | 615.3282 |  | 2026-27: #NAME?; 2028-29: Option 2
sens4 | Total benefits 10% lower | 0 | 517.2282 | 516.8959 | 500.5006 | 492.692 |  | 2026-27: #NAME?; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 509.6094 | 509.3495 | 494.2431 | 486.7749 |  | 2026-27: #NAME?; 2028-29: Option 2
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Misc_calcs
Powercor
Melton & Wyndham Transformation Capacity Project
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 1 | TRUE
| Option 3 | 1 | TRUE
| Option 4 | 1 | TRUE
| Option 5 | 1 | TRUE
| First year | 1
Region average
| PAL:Region average | #VALUE!
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
Powercor
Melton & Wyndham Transformation Capacity Project
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | FALSE |  |  | FALSE
Option5 | Option 5 | FALSE |  |  | FALSE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
Powercor
| Reliability in worst-served areas | per MWh | 151432.8174
| Network resilience | per MWh | 24590
| Enabling solar exports | per MWh | 88.3577
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.35181
| Customer value of time - business | per minute customer time | 0.35181
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020