## Cover
Powercor
Regulatory proposal 2026-31
Northern Murray harmonics management
| Model number: | 3.02
2025-01-31
14

## Summary
Powercor
Northern Murray harmonics management
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | -0.33384 | 0 | -0.28788
| Option 2 | Active harmonic filters |  | -5.2616 | 0.33924 | -4.9223
| Option 3 | Passive harmonic filters |  | -5.3544 | 0.33924 | -5.0151
| Option 4 | SOFIA harmonic filters |  | -6.3046 | 0.33924 | -5.9653
| Option 5 | STATCOMs |  | -7.8413 | 0.33924 | -7.502
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | Active harmonic filters |  | -4.9223 |  | Compliance project
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 2.431 | 2.9345 | 2.3476 | 0 | 0 |  | 7.7131
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  |  | -4.9223 | -5.0151 | -5.9653 | -7.502 |  | Option 2
| Capex 10% higher |  |  | -5.4485 | -5.5506 | -6.5958 | -8.2862 |  | Option 2
| Capex 10% lower |  |  | -4.3962 | -4.4797 | -5.3349 | -6.7179 |  | Option 2
| Total benefits 10% higher |  |  | -4.8884 | -4.9812 | -5.9314 | -7.4681 |  | Option 2
| Total benefits 10% lower |  |  | -4.9563 | -5.0491 | -5.9993 | -7.536 |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  |  | -5.4824 | -5.5845 | -6.6297 | -8.3201 |  | Option 2
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
Powercor
Northern Murray harmonics management
Project
|  | Business: |  | Powercor
|  | Descripton: |  | Northern Murray harmonics management
|  | Date of cost inputs: |  | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Active harmonic filters
|  | Option 3 |  | Passive harmonic filters
|  | Option 4 |  | SOFIA harmonic filters
|  | Option 5 |  | STATCOMs
|  | Compliance project |  | Yes
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | Network average |  | Network average | 43815.4862 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 151432.8174 | 2023-12-31 | per MWh
|  | Network resilience |  |  |  | 24590 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 88.3577 | 2023-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
Powercor
Northern Murray harmonics management
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890 | 17890
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reduction of utilization factors of transformers and lines due to high harmonics. |  |  | 2023-12-31 |  | 8773.41 | 9036.6123 | 9307.7107 | 9586.942 | 9874.5503 | 10170.7868 | 10475.9104 | 10790.1877 | 11113.8933 | 11447.3101 | 11790.7294 | 12144.4513 | 12508.7848 | 12884.0484 | 13270.5698 | 13668.6869 | 14078.7475 | 14501.11 | 14936.1433 | 15384.2276 | 15845.7544 | 16321.127 | 16810.7608 | 17315.0837 | 17834.5362
| Additional losses in transformers and lines due to high harmonics. |  |  | 2023-12-31 |  | 1570 | 1617.1 | 1665.613 | 1715.5814 | 1767.0488 | 1820.0603 | 1874.6621 | 1930.902 | 1988.829 | 2048.4939 | 2109.9487 | 2173.2472 | 2238.4446 | 2305.5979 | 2374.7659 | 2446.0088 | 2519.3891 | 2594.9708 | 2672.8199 | 2753.0045 | 2835.5946 | 2920.6625 | 3008.2824 | 3098.5308 | 3191.4867
| Reduction of the lifetime of line assets due to high harmonics. | (after DF) |  | 2023-12-31 |  | 2593.5374 | 2671.3435 | 2751.4838 | 2834.0284 | 2919.0492 | 3006.6207 | 3096.8193 | 3189.7239 | 3285.4156 | 3383.9781 | 3485.4974 | 3590.0623 | 3697.7642 | 3808.6971 | 3922.958 | 4040.6468 | 4161.8662 | 4286.7222 | 4415.3238 | 4547.7836 | 4684.2171 | 4824.7436 | 4969.4859 | 5118.5705 | 5272.1276
|  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 12936.9474 | 13325.0558 | 13724.8075 | 14136.5517 | 14560.6483 | 14997.4678 | 15447.3918 | 15910.8135 | 16388.1379 | 16879.7821 | 17386.1755 | 17907.7608 | 18444.9936 | 18998.3434 | 19568.2937 | 20155.3426 | 20760.0028 | 21382.8029 | 22024.287 | 22685.0156 | 23365.5661 | 24066.5331 | 24788.5291 | 25532.1849 | 26298.1505
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890 | -17890

## Option2
Powercor
Northern Murray harmonics management
OPTION 2 | Active harmonic filters
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| 1 X 500A harmonic filter at MBN31 |  | 30 | 2023-12-31 | 527348.1653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6 X 500A harmonic filters + a HV cap at BBD |  | 30 | 2023-12-31 | 602348.1653 | 1582044.4959 | 1054696.3306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6 X 500A harmonic filters at WMN |  | 30 | 2023-12-31 | 1054696.3306 | 1054696.3306 | 1054696.3306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 2184392.6612 | 2636740.8265 | 2109392.6612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - residential | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - business | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer benefits |  |  | 2023-12-31 | 0 | 0 | 3900 | 4017 | 4137.51 | 4261.6353 | 4389.4844 | 4521.1689 | 4656.804 | 4796.5081 | 4940.4033 | 5088.6154 | 5241.2739 | 5398.5121 | 5560.4675 | 5727.2815 | 5899.0999 | 6076.0729 | 6258.3551 | 6446.1058 | 6639.4889 | 6838.6736 | 7043.8338 | 7255.1488 | 7472.8033
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 3900 | 4017 | 4137.51 | 4261.6353 | 4389.4844 | 4521.1689 | 4656.804 | 4796.5081 | 4940.4033 | 5088.6154 | 5241.2739 | 5398.5121 | 5560.4675 | 5727.2815 | 5899.0999 | 6076.0729 | 6258.3551 | 6446.1058 | 6639.4889 | 6838.6736 | 7043.8338 | 7255.1488 | 7472.8033
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 12936.9474 | 13325.0558 | 13724.8075 | 14136.5517 | 14560.6483 | 14997.4678 | 15447.3918 | 15910.8135 | 16388.1379 | 16879.7821 | 17386.1755 | 17907.7608 | 18444.9936 | 18998.3434 | 19568.2937 | 20155.3426 | 20760.0028 | 21382.8029 | 22024.287 | 22685.0156 | 23365.5661 | 24066.5331 | 24788.5291 | 25532.1849 | 26298.1505
Capital expenditure
| 1 X 500A harmonic filter at MBN31 |  |  | 2023-12-31 | -527348.1653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6 X 500A harmonic filters + a HV cap at BBD |  |  | 2023-12-31 | -602348.1653 | -1582044.4959 | -1054696.3306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6 X 500A harmonic filters at WMN |  |  | 2023-12-31 | -1054696.3306 | -1054696.3306 | -1054696.3306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| 1 X 500A harmonic filter at MBN31 |  |  | 2023-12-31 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653 | -527348.1653
| 6 X 500A harmonic filters + a HV cap at BBD |  |  | 2023-12-31 | -602348.1653 | -2184392.6612 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918 | -3239088.9918
| 6 X 500A harmonic filters at WMN |  |  | 2023-12-31 | -1054696.3306 | -2109392.6612 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918 | -3164088.9918
Annualised capex
| Annualised capex - 1 X 500A harmonic filter at MBN31 |  |  | 2023-12-31 | 0 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622 | -28672.622
| Annualised capex - 6 X 500A harmonic filters + a HV cap at BBD |  |  | 2023-12-31 | 0 | -32750.4718 | -118768.3377 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817 | -176113.5817
| Annualised capex - 6 X 500A harmonic filters at WMN |  |  | 2023-12-31 | 0 | -57345.2439 | -114690.4879 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318 | -172035.7318
| Total annualised capex |  |  | 2023-12-31 | 0 | -118768.3377 | -262131.4476 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355
| Annualised capex |  |  | 2023-12-31 | 0 | -118768.3377 | -262131.4476 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 12936.9474 | 13325.0558 | 13724.8075 | 14136.5517 | 14560.6483 | 14997.4678 | 15447.3918 | 15910.8135 | 16388.1379 | 16879.7821 | 17386.1755 | 17907.7608 | 18444.9936 | 18998.3434 | 19568.2937 | 20155.3426 | 20760.0028 | 21382.8029 | 22024.287 | 22685.0156 | 23365.5661 | 24066.5331 | 24788.5291 | 25532.1849 | 26298.1505
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 3900 | 4017 | 4137.51 | 4261.6353 | 4389.4844 | 4521.1689 | 4656.804 | 4796.5081 | 4940.4033 | 5088.6154 | 5241.2739 | 5398.5121 | 5560.4675 | 5727.2815 | 5899.0999 | 6076.0729 | 6258.3551 | 6446.1058 | 6639.4889 | 6838.6736 | 7043.8338 | 7255.1488 | 7472.8033
| Net benefits |  |  | 2023-12-31 | 12936.9474 | -105443.2819 | -244506.6401 | -358668.3837 | -358123.7772 | -357562.8324 | -356985.0593 | -356389.953 | -355776.9936 | -355145.6453 | -354495.3566 | -353825.5592 | -353135.6679 | -352425.0799 | -351693.1743 | -350939.3114 | -350162.8327 | -349363.0596 | -348539.2933 | -347690.8141 | -346816.8804 | -345916.7288 | -344989.5726 | -344034.6017 | -343050.9817
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 12936.9474 | -105443.2819 | -244506.6401 | -358668.3837 | -358123.7772 | -357562.8324 | -356985.0593 | -356389.953 | -355776.9936 | -355145.6453 | -354495.3566 | -353825.5592 | -353135.6679 | -352425.0799 | -351693.1743 | -350939.3114 | -350162.8327 | -349363.0596 | -348539.2933 | -347690.8141 | -346816.8804 | -345916.7288 | -344989.5726 | -344034.6017 | -343050.9817
| Total annualised capex |  |  |  | 0 | -118768.3377 | -262131.4476 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355 | -376821.9355
| Total benefits |  |  |  | 12936.9474 | 13325.0558 | 17624.8075 | 18153.5517 | 18698.1583 | 19259.1031 | 19836.8761 | 20431.9824 | 21044.9419 | 21676.2902 | 22326.5789 | 22996.3762 | 23686.2675 | 24396.8555 | 25128.7612 | 25882.624 | 26659.1028 | 27458.8758 | 28282.6421 | 29131.1214 | 30005.055 | 30905.2067 | 31832.3629 | 32787.3338 | 33770.9538
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 12936.9474 | -117320.1157 | -270719.7848 | -396350.5773 | -395805.9707 | -395245.026 | -394667.2529 | -394072.1466 | -393459.1871 | -392827.8388 | -392177.5501 | -391507.7528 | -390817.8615 | -390107.2735 | -389375.3678 | -388621.505 | -387845.0262 | -387045.2532 | -386221.4869 | -385373.0076 | -384499.074 | -383598.9223 | -382671.7661 | -381716.7952 | -380733.1752
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 12936.9474 | -93566.4481 | -218293.4953 | -320986.1902 | -320441.5836 | -319880.6389 | -319302.8658 | -318707.7595 | -318094.8 | -317463.4518 | -316813.163 | -316143.3657 | -315453.4744 | -314742.8864 | -314010.9807 | -313257.1179 | -312480.6391 | -311680.8661 | -310857.0998 | -310008.6205 | -309134.6869 | -308234.5352 | -307307.379 | -306352.4081 | -305368.7881
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 14230.6422 | -104110.7763 | -242744.1593 | -356853.0285 | -356253.9613 | -355636.9221 | -355001.3717 | -354346.7548 | -353672.4994 | -352978.0163 | -352262.6987 | -351525.9216 | -350767.0412 | -349985.3944 | -349180.2981 | -348351.049 | -347496.9224 | -346617.172 | -345711.0291 | -344777.7019 | -343816.3749 | -342826.2081 | -341806.3363 | -340755.8683 | -339673.8863
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 11643.2527 | -106775.7875 | -246269.1208 | -360483.7389 | -359993.593 | -359488.7427 | -358968.7469 | -358433.1513 | -357881.4877 | -357313.2743 | -356728.0145 | -356125.1969 | -355504.2947 | -354864.7655 | -354206.0504 | -353527.5738 | -352828.743 | -352108.9472 | -351367.5575 | -350603.9262 | -349817.3859 | -349007.2494 | -348172.8089 | -347313.3351 | -346428.0771
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 11643.2527 | -118652.6213 | -272482.2656 | -398165.9324 | -397675.7865 | -397170.9363 | -396650.9405 | -396115.3448 | -395563.6813 | -394995.4679 | -394410.208 | -393807.3904 | -393186.4882 | -392546.959 | -391888.2439 | -391209.7674 | -390510.9365 | -389791.1407 | -389049.7511 | -388286.1198 | -387499.5795 | -386689.443 | -385855.0024 | -384995.5286 | -384110.2706
sens | 0 | 0% | 0% | Option 2sens | 12936.9474 | -105443.2819 | -244506.6401 | -358668.3837 | -358123.7772 | -357562.8324 | -356985.0593 | -356389.953 | -355776.9936 | -355145.6453 | -354495.3566 | -353825.5592 | -353135.6679 | -352425.0799 | -351693.1743 | -350939.3114 | -350162.8327 | -349363.0596 | -348539.2933 | -347690.8141 | -346816.8804 | -345916.7288 | -344989.5726 | -344034.6017 | -343050.9817
sens | 0 | 0% | 0% | Option 2sens | 12936.9474 | -105443.2819 | -244506.6401 | -358668.3837 | -358123.7772 | -357562.8324 | -356985.0593 | -356389.953 | -355776.9936 | -355145.6453 | -354495.3566 | -353825.5592 | -353135.6679 | -352425.0799 | -351693.1743 | -350939.3114 | -350162.8327 | -349363.0596 | -348539.2933 | -347690.8141 | -346816.8804 | -345916.7288 | -344989.5726 | -344034.6017 | -343050.9817
sens | 0 | 0% | 0% | Option 2sens | 12936.9474 | -105443.2819 | -244506.6401 | -358668.3837 | -358123.7772 | -357562.8324 | -356985.0593 | -356389.953 | -355776.9936 | -355145.6453 | -354495.3566 | -353825.5592 | -353135.6679 | -352425.0799 | -351693.1743 | -350939.3114 | -350162.8327 | -349363.0596 | -348539.2933 | -347690.8141 | -346816.8804 | -345916.7288 | -344989.5726 | -344034.6017 | -343050.9817

## Option3
Powercor
Northern Murray harmonics management
OPTION 3 | Passive harmonic filters
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| 1 X 2MVA filters at MBN31 |  | 30 | 2023-12-31 | 927180.5899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 X 2MVA filters at BBD feeders |  | 30 | 2023-12-31 | 927180.5899 | 927180.5899 | 927180.5899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| A 4MVA at ZSS + 2 X 2MVA filters at WMN feeders |  | 30 | 2023-12-31 | 1390770.8849 | 927180.5899 | 927180.5899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 3245132.0647 | 1854361.1798 | 1854361.1798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer benefits |  |  | 2023-12-31 | 0 | 0 | 3900 | 4017 | 4137.51 | 4261.6353 | 4389.4844 | 4521.1689 | 4656.804 | 4796.5081 | 4940.4033 | 5088.6154 | 5241.2739 | 5398.5121 | 5560.4675 | 5727.2815 | 5899.0999 | 6076.0729 | 6258.3551 | 6446.1058 | 6639.4889 | 6838.6736 | 7043.8338 | 7255.1488 | 7472.8033
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 3900 | 4017 | 4137.51 | 4261.6353 | 4389.4844 | 4521.1689 | 4656.804 | 4796.5081 | 4940.4033 | 5088.6154 | 5241.2739 | 5398.5121 | 5560.4675 | 5727.2815 | 5899.0999 | 6076.0729 | 6258.3551 | 6446.1058 | 6639.4889 | 6838.6736 | 7043.8338 | 7255.1488 | 7472.8033
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 12936.9474 | 13325.0558 | 13724.8075 | 14136.5517 | 14560.6483 | 14997.4678 | 15447.3918 | 15910.8135 | 16388.1379 | 16879.7821 | 17386.1755 | 17907.7608 | 18444.9936 | 18998.3434 | 19568.2937 | 20155.3426 | 20760.0028 | 21382.8029 | 22024.287 | 22685.0156 | 23365.5661 | 24066.5331 | 24788.5291 | 25532.1849 | 26298.1505
Capital expenditure
| 1 X 2MVA filters at MBN31 |  |  | 2023-12-31 | -927180.5899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 X 2MVA filters at BBD feeders |  |  | 2023-12-31 | -927180.5899 | -927180.5899 | -927180.5899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| A 4MVA at ZSS + 2 X 2MVA filters at WMN feeders |  |  | 2023-12-31 | -1390770.8849 | -927180.5899 | -927180.5899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| 1 X 2MVA filters at MBN31 |  |  | 2023-12-31 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899 | -927180.5899
| 3 X 2MVA filters at BBD feeders |  |  | 2023-12-31 | -927180.5899 | -1854361.1798 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697 | -2781541.7697
| A 4MVA at ZSS + 2 X 2MVA filters at WMN feeders |  |  | 2023-12-31 | -1390770.8849 | -2317951.4748 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647 | -3245132.0647
Annualised capex
| Annualised capex - 1 X 2MVA filters at MBN31 |  |  | 2023-12-31 | 0 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433 | -50412.0433
| Annualised capex - 3 X 2MVA filters at BBD feeders |  |  | 2023-12-31 | 0 | -50412.0433 | -100824.0866 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299 | -151236.1299
| Annualised capex - A 4MVA at ZSS + 2 X 2MVA filters at WMN feeders |  |  | 2023-12-31 | 0 | -75618.065 | -126030.1083 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516 | -176442.1516
| Total annualised capex |  |  | 2023-12-31 | 0 | -176442.1516 | -277266.2382 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249
| Annualised capex |  |  | 2023-12-31 | 0 | -176442.1516 | -277266.2382 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 12936.9474 | 13325.0558 | 13724.8075 | 14136.5517 | 14560.6483 | 14997.4678 | 15447.3918 | 15910.8135 | 16388.1379 | 16879.7821 | 17386.1755 | 17907.7608 | 18444.9936 | 18998.3434 | 19568.2937 | 20155.3426 | 20760.0028 | 21382.8029 | 22024.287 | 22685.0156 | 23365.5661 | 24066.5331 | 24788.5291 | 25532.1849 | 26298.1505
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 3900 | 4017 | 4137.51 | 4261.6353 | 4389.4844 | 4521.1689 | 4656.804 | 4796.5081 | 4940.4033 | 5088.6154 | 5241.2739 | 5398.5121 | 5560.4675 | 5727.2815 | 5899.0999 | 6076.0729 | 6258.3551 | 6446.1058 | 6639.4889 | 6838.6736 | 7043.8338 | 7255.1488 | 7472.8033
| Net benefits |  |  | 2023-12-31 | 12936.9474 | -163117.0957 | -259641.4307 | -359936.7731 | -359392.1665 | -358831.2218 | -358253.4487 | -357658.3424 | -357045.383 | -356414.0347 | -355763.746 | -355093.9486 | -354404.0573 | -353693.4693 | -352961.5636 | -352207.7008 | -351431.2221 | -350631.449 | -349807.6827 | -348959.2035 | -348085.2698 | -347185.1182 | -346257.962 | -345302.9911 | -344319.3711
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 12936.9474 | -163117.0957 | -259641.4307 | -359936.7731 | -359392.1665 | -358831.2218 | -358253.4487 | -357658.3424 | -357045.383 | -356414.0347 | -355763.746 | -355093.9486 | -354404.0573 | -353693.4693 | -352961.5636 | -352207.7008 | -351431.2221 | -350631.449 | -349807.6827 | -348959.2035 | -348085.2698 | -347185.1182 | -346257.962 | -345302.9911 | -344319.3711
| Total annualised capex |  |  |  | 0 | -176442.1516 | -277266.2382 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249 | -378090.3249
| Total benefits |  |  |  | 12936.9474 | 13325.0558 | 17624.8075 | 18153.5517 | 18698.1583 | 19259.1031 | 19836.8761 | 20431.9824 | 21044.9419 | 21676.2902 | 22326.5789 | 22996.3762 | 23686.2675 | 24396.8555 | 25128.7612 | 25882.624 | 26659.1028 | 27458.8758 | 28282.6421 | 29131.1214 | 30005.055 | 30905.2067 | 31832.3629 | 32787.3338 | 33770.9538
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 12936.9474 | -180761.3109 | -287368.0545 | -397745.8056 | -397201.199 | -396640.2543 | -396062.4812 | -395467.3749 | -394854.4154 | -394223.0672 | -393572.7785 | -392902.9811 | -392213.0898 | -391502.5018 | -390770.5961 | -390016.7333 | -389240.2546 | -388440.4815 | -387616.7152 | -386768.236 | -385894.3023 | -384994.1507 | -384066.9945 | -383112.0236 | -382128.4036
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 12936.9474 | -145472.8806 | -231914.8069 | -322127.7406 | -321583.1341 | -321022.1893 | -320444.4162 | -319849.3099 | -319236.3505 | -318605.0022 | -317954.7135 | -317284.9161 | -316595.0249 | -315884.4368 | -315152.5312 | -314398.6683 | -313622.1896 | -312822.4165 | -311998.6502 | -311150.171 | -310276.2373 | -309376.0857 | -308448.9295 | -307493.9586 | -306510.3386
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 14230.6422 | -161784.5902 | -257878.9499 | -358121.4179 | -357522.3507 | -356905.3115 | -356269.7611 | -355615.1442 | -354940.8888 | -354246.4057 | -353531.0881 | -352794.311 | -352035.4306 | -351253.7838 | -350448.6875 | -349619.4384 | -348765.3118 | -347885.5614 | -346979.4185 | -346046.0913 | -345084.7643 | -344094.5975 | -343074.7257 | -342024.2577 | -340942.2757
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 11643.2527 | -164449.6013 | -261403.9115 | -361752.1283 | -361261.9824 | -360757.1321 | -360237.1363 | -359701.5407 | -359149.8771 | -358581.6637 | -357996.4039 | -357393.5862 | -356772.6841 | -356133.1549 | -355474.4398 | -354795.9632 | -354097.1324 | -353377.3366 | -352635.9469 | -351872.3156 | -351085.7753 | -350275.6388 | -349441.1983 | -348581.7245 | -347696.4665
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 11643.2527 | -182093.8165 | -289130.5353 | -399561.1608 | -399071.0149 | -398566.1646 | -398046.1688 | -397510.5732 | -396958.9096 | -396390.6962 | -395805.4364 | -395202.6187 | -394581.7166 | -393942.1874 | -393283.4723 | -392604.9957 | -391906.1648 | -391186.3691 | -390444.9794 | -389681.3481 | -388894.8078 | -388084.6713 | -387250.2307 | -386390.7569 | -385505.4989
sens | 0 | 0% | 0% | Option 3sens | 12936.9474 | -163117.0957 | -259641.4307 | -359936.7731 | -359392.1665 | -358831.2218 | -358253.4487 | -357658.3424 | -357045.383 | -356414.0347 | -355763.746 | -355093.9486 | -354404.0573 | -353693.4693 | -352961.5636 | -352207.7008 | -351431.2221 | -350631.449 | -349807.6827 | -348959.2035 | -348085.2698 | -347185.1182 | -346257.962 | -345302.9911 | -344319.3711
sens | 0 | 0% | 0% | Option 3sens | 12936.9474 | -163117.0957 | -259641.4307 | -359936.7731 | -359392.1665 | -358831.2218 | -358253.4487 | -357658.3424 | -357045.383 | -356414.0347 | -355763.746 | -355093.9486 | -354404.0573 | -353693.4693 | -352961.5636 | -352207.7008 | -351431.2221 | -350631.449 | -349807.6827 | -348959.2035 | -348085.2698 | -347185.1182 | -346257.962 | -345302.9911 | -344319.3711
sens | 0 | 0% | 0% | Option 3sens | 12936.9474 | -163117.0957 | -259641.4307 | -359936.7731 | -359392.1665 | -358831.2218 | -358253.4487 | -357658.3424 | -357045.383 | -356414.0347 | -355763.746 | -355093.9486 | -354404.0573 | -353693.4693 | -352961.5636 | -352207.7008 | -351431.2221 | -350631.449 | -349807.6827 | -348959.2035 | -348085.2698 | -347185.1182 | -346257.962 | -345302.9911 | -344319.3711

## Option4
Powercor
Northern Murray harmonics management
OPTION 4 | SOFIA harmonic filters
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| 1 filters at MBN31 (300A) |  | 30 | 2023-12-31 | 767474.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 filters at BBD feeders (300A, 600A, 900A) + a HV cap at BBD |  | 30 | 2023-12-31 | 1609949.16 | 1151211.87 | 767474.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 filters at WMN feeders (300A, 900A, 900A) |  | 30 | 2023-12-31 | 1534949.16 | 1534949.16 | 767474.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 3912372.9 | 2686161.03 | 1534949.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer benefits |  |  | 2023-12-31 | 0 | 0 | 3900 | 4017 | 4137.51 | 4261.6353 | 4389.4844 | 4521.1689 | 4656.804 | 4796.5081 | 4940.4033 | 5088.6154 | 5241.2739 | 5398.5121 | 5560.4675 | 5727.2815 | 5899.0999 | 6076.0729 | 6258.3551 | 6446.1058 | 6639.4889 | 6838.6736 | 7043.8338 | 7255.1488 | 7472.8033
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 3900 | 4017 | 4137.51 | 4261.6353 | 4389.4844 | 4521.1689 | 4656.804 | 4796.5081 | 4940.4033 | 5088.6154 | 5241.2739 | 5398.5121 | 5560.4675 | 5727.2815 | 5899.0999 | 6076.0729 | 6258.3551 | 6446.1058 | 6639.4889 | 6838.6736 | 7043.8338 | 7255.1488 | 7472.8033
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 12936.9474 | 13325.0558 | 13724.8075 | 14136.5517 | 14560.6483 | 14997.4678 | 15447.3918 | 15910.8135 | 16388.1379 | 16879.7821 | 17386.1755 | 17907.7608 | 18444.9936 | 18998.3434 | 19568.2937 | 20155.3426 | 20760.0028 | 21382.8029 | 22024.287 | 22685.0156 | 23365.5661 | 24066.5331 | 24788.5291 | 25532.1849 | 26298.1505
Capital expenditure
| 1 filters at MBN31 (300A) |  |  | 2023-12-31 | -767474.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 filters at BBD feeders (300A, 600A, 900A) + a HV cap at BBD |  |  | 2023-12-31 | -1609949.16 | -1151211.87 | -767474.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 filters at WMN feeders (300A, 900A, 900A) |  |  | 2023-12-31 | -1534949.16 | -1534949.16 | -767474.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| 1 filters at MBN31 (300A) |  |  | 2023-12-31 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58 | -767474.58
| 3 filters at BBD feeders (300A, 600A, 900A) + a HV cap at BBD |  |  | 2023-12-31 | -1609949.16 | -2761161.03 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61 | -3528635.61
| 3 filters at WMN feeders (300A, 900A, 900A) |  |  | 2023-12-31 | -1534949.16 | -3069898.32 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9 | -3837372.9
Annualised capex
| Annualised capex - 1 filters at MBN31 (300A) |  |  | 2023-12-31 | 0 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149 | -41728.6149
| Annualised capex - 3 filters at BBD feeders (300A, 600A, 900A) + a HV cap at BBD |  |  | 2023-12-31 | 0 | -87535.0796 | -150128.002 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169 | -191856.6169
| Annualised capex - 3 filters at WMN feeders (300A, 900A, 900A) |  |  | 2023-12-31 | 0 | -83457.2298 | -166914.4596 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744 | -208643.0744
| Total annualised capex |  |  | 2023-12-31 | 0 | -212720.9243 | -358771.0764 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062
| Annualised capex |  |  | 2023-12-31 | 0 | -212720.9243 | -358771.0764 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 12936.9474 | 13325.0558 | 13724.8075 | 14136.5517 | 14560.6483 | 14997.4678 | 15447.3918 | 15910.8135 | 16388.1379 | 16879.7821 | 17386.1755 | 17907.7608 | 18444.9936 | 18998.3434 | 19568.2937 | 20155.3426 | 20760.0028 | 21382.8029 | 22024.287 | 22685.0156 | 23365.5661 | 24066.5331 | 24788.5291 | 25532.1849 | 26298.1505
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 3900 | 4017 | 4137.51 | 4261.6353 | 4389.4844 | 4521.1689 | 4656.804 | 4796.5081 | 4940.4033 | 5088.6154 | 5241.2739 | 5398.5121 | 5560.4675 | 5727.2815 | 5899.0999 | 6076.0729 | 6258.3551 | 6446.1058 | 6639.4889 | 6838.6736 | 7043.8338 | 7255.1488 | 7472.8033
| Net benefits |  |  | 2023-12-31 | 12936.9474 | -199395.8685 | -341146.2689 | -424074.7545 | -423530.1479 | -422969.2032 | -422391.4301 | -421796.3238 | -421183.3643 | -420552.0161 | -419901.7273 | -419231.93 | -418542.0387 | -417831.4507 | -417099.545 | -416345.6822 | -415569.2034 | -414769.4304 | -413945.6641 | -413097.1848 | -412223.2512 | -411323.0995 | -410395.9433 | -409440.9724 | -408457.3524
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 12936.9474 | -199395.8685 | -341146.2689 | -424074.7545 | -423530.1479 | -422969.2032 | -422391.4301 | -421796.3238 | -421183.3643 | -420552.0161 | -419901.7273 | -419231.93 | -418542.0387 | -417831.4507 | -417099.545 | -416345.6822 | -415569.2034 | -414769.4304 | -413945.6641 | -413097.1848 | -412223.2512 | -411323.0995 | -410395.9433 | -409440.9724 | -408457.3524
| Total annualised capex |  |  |  | 0 | -212720.9243 | -358771.0764 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062 | -442228.3062
| Total benefits |  |  |  | 12936.9474 | 13325.0558 | 17624.8075 | 18153.5517 | 18698.1583 | 19259.1031 | 19836.8761 | 20431.9824 | 21044.9419 | 21676.2902 | 22326.5789 | 22996.3762 | 23686.2675 | 24396.8555 | 25128.7612 | 25882.624 | 26659.1028 | 27458.8758 | 28282.6421 | 29131.1214 | 30005.055 | 30905.2067 | 31832.3629 | 32787.3338 | 33770.9538
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 12936.9474 | -220667.9609 | -377023.3766 | -468297.5851 | -467752.9785 | -467192.0338 | -466614.2607 | -466019.1544 | -465406.1949 | -464774.8467 | -464124.558 | -463454.7606 | -462764.8693 | -462054.2813 | -461322.3756 | -460568.5128 | -459792.0341 | -458992.261 | -458168.4947 | -457320.0154 | -456446.0818 | -455545.9302 | -454618.774 | -453663.8031 | -452680.1831
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 12936.9474 | -178123.776 | -305269.1613 | -379851.9238 | -379307.3173 | -378746.3725 | -378168.5994 | -377573.4932 | -376960.5337 | -376329.1854 | -375678.8967 | -375009.0994 | -374319.2081 | -373608.62 | -372876.7144 | -372122.8515 | -371346.3728 | -370546.5997 | -369722.8335 | -368874.3542 | -368000.4206 | -367100.2689 | -366173.1127 | -365218.1418 | -364234.5218
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 14230.6422 | -198063.3629 | -339383.7882 | -422259.3993 | -421660.3321 | -421043.2929 | -420407.7425 | -419753.1255 | -419078.8701 | -418384.387 | -417669.0695 | -416932.2924 | -416173.4119 | -415391.7651 | -414586.6689 | -413757.4198 | -412903.2932 | -412023.5428 | -411117.3999 | -410184.0727 | -409222.7457 | -408232.5789 | -407212.707 | -406162.2391 | -405080.2571
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 11643.2527 | -200728.3741 | -342908.7497 | -425890.1096 | -425399.9637 | -424895.1135 | -424375.1177 | -423839.522 | -423287.8585 | -422719.6451 | -422134.3852 | -421531.5676 | -420910.6654 | -420271.1362 | -419612.4211 | -418933.9446 | -418235.1137 | -417515.3179 | -416773.9283 | -416010.297 | -415223.7567 | -414413.6202 | -413579.1796 | -412719.7058 | -411834.4478
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 11643.2527 | -222000.4665 | -378785.8573 | -470112.9403 | -469622.7944 | -469117.9441 | -468597.9483 | -468062.3526 | -467510.6891 | -466942.4757 | -466357.2159 | -465754.3982 | -465133.4961 | -464493.9668 | -463835.2517 | -463156.7752 | -462457.9443 | -461738.1486 | -460996.7589 | -460233.1276 | -459446.5873 | -458636.4508 | -457802.0102 | -456942.5364 | -456057.2784
sens | 0 | 0% | 0% | Option 4sens | 12936.9474 | -199395.8685 | -341146.2689 | -424074.7545 | -423530.1479 | -422969.2032 | -422391.4301 | -421796.3238 | -421183.3643 | -420552.0161 | -419901.7273 | -419231.93 | -418542.0387 | -417831.4507 | -417099.545 | -416345.6822 | -415569.2034 | -414769.4304 | -413945.6641 | -413097.1848 | -412223.2512 | -411323.0995 | -410395.9433 | -409440.9724 | -408457.3524
sens | 0 | 0% | 0% | Option 4sens | 12936.9474 | -199395.8685 | -341146.2689 | -424074.7545 | -423530.1479 | -422969.2032 | -422391.4301 | -421796.3238 | -421183.3643 | -420552.0161 | -419901.7273 | -419231.93 | -418542.0387 | -417831.4507 | -417099.545 | -416345.6822 | -415569.2034 | -414769.4304 | -413945.6641 | -413097.1848 | -412223.2512 | -411323.0995 | -410395.9433 | -409440.9724 | -408457.3524
sens | 0 | 0% | 0% | Option 4sens | 12936.9474 | -199395.8685 | -341146.2689 | -424074.7545 | -423530.1479 | -422969.2032 | -422391.4301 | -421796.3238 | -421183.3643 | -420552.0161 | -419901.7273 | -419231.93 | -418542.0387 | -417831.4507 | -417099.545 | -416345.6822 | -415569.2034 | -414769.4304 | -413945.6641 | -413097.1848 | -412223.2512 | -411323.0995 | -410395.9433 | -409440.9724 | -408457.3524

## Option5
Powercor
Northern Murray harmonics management
OPTION 5 | STATCOMs
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| 1 STATCOMs at BBD feeders |  | 30 | 2023-12-31 | 1357820.28 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 STATCOMs at BBD feeders |  | 30 | 2023-12-31 | 1357820.28 | 1357820.28 | 1357820.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 STATCOMs at WMN feeders |  | 30 | 2023-12-31 | 2036730.42 | 1357820.28 | 1357820.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 4752370.98 | 2715640.56 | 2715640.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer benefits |  |  | 2023-12-31 | 0 | 0 | 3900 | 4017 | 4137.51 | 4261.6353 | 4389.4844 | 4521.1689 | 4656.804 | 4796.5081 | 4940.4033 | 5088.6154 | 5241.2739 | 5398.5121 | 5560.4675 | 5727.2815 | 5899.0999 | 6076.0729 | 6258.3551 | 6446.1058 | 6639.4889 | 6838.6736 | 7043.8338 | 7255.1488 | 7472.8033
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 3900 | 4017 | 4137.51 | 4261.6353 | 4389.4844 | 4521.1689 | 4656.804 | 4796.5081 | 4940.4033 | 5088.6154 | 5241.2739 | 5398.5121 | 5560.4675 | 5727.2815 | 5899.0999 | 6076.0729 | 6258.3551 | 6446.1058 | 6639.4889 | 6838.6736 | 7043.8338 | 7255.1488 | 7472.8033
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 12936.9474 | 13325.0558 | 13724.8075 | 14136.5517 | 14560.6483 | 14997.4678 | 15447.3918 | 15910.8135 | 16388.1379 | 16879.7821 | 17386.1755 | 17907.7608 | 18444.9936 | 18998.3434 | 19568.2937 | 20155.3426 | 20760.0028 | 21382.8029 | 22024.287 | 22685.0156 | 23365.5661 | 24066.5331 | 24788.5291 | 25532.1849 | 26298.1505
Capital expenditure
| 1 STATCOMs at BBD feeders |  |  | 2023-12-31 | -1357820.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 STATCOMs at BBD feeders |  |  | 2023-12-31 | -1357820.28 | -1357820.28 | -1357820.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 STATCOMs at WMN feeders |  |  | 2023-12-31 | -2036730.42 | -1357820.28 | -1357820.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| 1 STATCOMs at BBD feeders |  |  | 2023-12-31 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28 | -1357820.28
| 3 STATCOMs at BBD feeders |  |  | 2023-12-31 | -1357820.28 | -2715640.56 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84 | -4073460.84
| 4 STATCOMs at WMN feeders |  |  | 2023-12-31 | -2036730.42 | -3394550.7 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98 | -4752370.98
Annualised capex
| Annualised capex - 1 STATCOMs at BBD feeders |  |  | 2023-12-31 | 0 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967 | -73826.4967
| Annualised capex - 3 STATCOMs at BBD feeders |  |  | 2023-12-31 | 0 | -73826.4967 | -147652.9934 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901 | -221479.4901
| Annualised capex - 4 STATCOMs at WMN feeders |  |  | 2023-12-31 | 0 | -110739.7451 | -184566.2418 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385 | -258392.7385
| Total annualised capex |  |  | 2023-12-31 | 0 | -258392.7385 | -406045.7319 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253
| Annualised capex |  |  | 2023-12-31 | 0 | -258392.7385 | -406045.7319 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 12936.9474 | 13325.0558 | 13724.8075 | 14136.5517 | 14560.6483 | 14997.4678 | 15447.3918 | 15910.8135 | 16388.1379 | 16879.7821 | 17386.1755 | 17907.7608 | 18444.9936 | 18998.3434 | 19568.2937 | 20155.3426 | 20760.0028 | 21382.8029 | 22024.287 | 22685.0156 | 23365.5661 | 24066.5331 | 24788.5291 | 25532.1849 | 26298.1505
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 3900 | 4017 | 4137.51 | 4261.6353 | 4389.4844 | 4521.1689 | 4656.804 | 4796.5081 | 4940.4033 | 5088.6154 | 5241.2739 | 5398.5121 | 5560.4675 | 5727.2815 | 5899.0999 | 6076.0729 | 6258.3551 | 6446.1058 | 6639.4889 | 6838.6736 | 7043.8338 | 7255.1488 | 7472.8033
| Net benefits |  |  | 2023-12-31 | 12936.9474 | -245067.6826 | -388420.9244 | -535545.1736 | -535000.567 | -534439.6223 | -533861.8492 | -533266.7429 | -532653.7834 | -532022.4351 | -531372.1464 | -530702.3491 | -530012.4578 | -529301.8698 | -528569.9641 | -527816.1013 | -527039.6225 | -526239.8495 | -525416.0832 | -524567.6039 | -523693.6703 | -522793.5186 | -521866.3624 | -520911.3915 | -519927.7715
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 12936.9474 | -245067.6826 | -388420.9244 | -535545.1736 | -535000.567 | -534439.6223 | -533861.8492 | -533266.7429 | -532653.7834 | -532022.4351 | -531372.1464 | -530702.3491 | -530012.4578 | -529301.8698 | -528569.9641 | -527816.1013 | -527039.6225 | -526239.8495 | -525416.0832 | -524567.6039 | -523693.6703 | -522793.5186 | -521866.3624 | -520911.3915 | -519927.7715
| Total annualised capex |  |  |  | 0 | -258392.7385 | -406045.7319 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253 | -553698.7253
| Total benefits |  |  |  | 12936.9474 | 13325.0558 | 17624.8075 | 18153.5517 | 18698.1583 | 19259.1031 | 19836.8761 | 20431.9824 | 21044.9419 | 21676.2902 | 22326.5789 | 22996.3762 | 23686.2675 | 24396.8555 | 25128.7612 | 25882.624 | 26659.1028 | 27458.8758 | 28282.6421 | 29131.1214 | 30005.055 | 30905.2067 | 31832.3629 | 32787.3338 | 33770.9538
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 12936.9474 | -270906.9565 | -429025.4976 | -590915.0461 | -590370.4395 | -589809.4948 | -589231.7217 | -588636.6154 | -588023.6559 | -587392.3077 | -586742.019 | -586072.2216 | -585382.3303 | -584671.7423 | -583939.8366 | -583185.9738 | -582409.4951 | -581609.722 | -580785.9557 | -579937.4764 | -579063.5428 | -578163.3912 | -577236.235 | -576281.2641 | -575297.6441
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 12936.9474 | -219228.4088 | -347816.3512 | -480175.301 | -479630.6945 | -479069.7497 | -478491.9766 | -477896.8703 | -477283.9109 | -476652.5626 | -476002.2739 | -475332.4765 | -474642.5853 | -473931.9972 | -473200.0916 | -472446.2287 | -471669.75 | -470869.9769 | -470046.2107 | -469197.7314 | -468323.7977 | -467423.6461 | -466496.4899 | -465541.519 | -464557.899
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 14230.6422 | -243735.177 | -386658.4436 | -533729.8184 | -533130.7512 | -532513.7119 | -531878.1615 | -531223.5446 | -530549.2892 | -529854.8061 | -529139.4886 | -528402.7115 | -527643.831 | -526862.1842 | -526057.088 | -525227.8389 | -524373.7123 | -523493.9619 | -522587.819 | -521654.4918 | -520693.1648 | -519702.998 | -518683.1261 | -517632.6582 | -516550.6761
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 11643.2527 | -246400.1882 | -390183.4051 | -537360.5287 | -536870.3828 | -536365.5326 | -535845.5368 | -535309.9411 | -534758.2776 | -534190.0642 | -533604.8043 | -533001.9867 | -532381.0845 | -531741.5553 | -531082.8402 | -530404.3637 | -529705.5328 | -528985.737 | -528244.3474 | -527480.7161 | -526694.1758 | -525884.0393 | -525049.5987 | -524190.1249 | -523304.8669
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 11643.2527 | -272239.4621 | -430787.9783 | -592730.4013 | -592240.2554 | -591735.4051 | -591215.4093 | -590679.8136 | -590128.1501 | -589559.9367 | -588974.6769 | -588371.8592 | -587750.9571 | -587111.4278 | -586452.7127 | -585774.2362 | -585075.4053 | -584355.6096 | -583614.2199 | -582850.5886 | -582064.0483 | -581253.9118 | -580419.4712 | -579559.9974 | -578674.7394
sens | 0 | 0% | 0% | Option 5sens | 12936.9474 | -245067.6826 | -388420.9244 | -535545.1736 | -535000.567 | -534439.6223 | -533861.8492 | -533266.7429 | -532653.7834 | -532022.4351 | -531372.1464 | -530702.3491 | -530012.4578 | -529301.8698 | -528569.9641 | -527816.1013 | -527039.6225 | -526239.8495 | -525416.0832 | -524567.6039 | -523693.6703 | -522793.5186 | -521866.3624 | -520911.3915 | -519927.7715
sens | 0 | 0% | 0% | Option 5sens | 12936.9474 | -245067.6826 | -388420.9244 | -535545.1736 | -535000.567 | -534439.6223 | -533861.8492 | -533266.7429 | -532653.7834 | -532022.4351 | -531372.1464 | -530702.3491 | -530012.4578 | -529301.8698 | -528569.9641 | -527816.1013 | -527039.6225 | -526239.8495 | -525416.0832 | -524567.6039 | -523693.6703 | -522793.5186 | -521866.3624 | -520911.3915 | -519927.7715
sens | 0 | 0% | 0% | Option 5sens | 12936.9474 | -245067.6826 | -388420.9244 | -535545.1736 | -535000.567 | -534439.6223 | -533861.8492 | -533266.7429 | -532653.7834 | -532022.4351 | -531372.1464 | -530702.3491 | -530012.4578 | -529301.8698 | -528569.9641 | -527816.1013 | -527039.6225 | -526239.8495 | -525416.0832 | -524567.6039 | -523693.6703 | -522793.5186 | -521866.3624 | -520911.3915 | -519927.7715

## Consol
Powercor
Northern Murray harmonics management
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 270422.1925 | 2026-06-30 |  | 14397.6924 | 14829.6232 | 15274.5119 | 15732.7472 | 16204.7296 | 16690.8715 | 17191.5977 | 17707.3456 | 18238.566 | 18785.7229 | 19349.2946 | 19929.7735 | 20527.6667 | 21143.4967 | 21777.8016 | 22431.1356 | 23104.0697 | 23797.1918 | 24511.1075 | 25246.4408 | 26003.834 | 26783.949 | 27587.4675 | 28415.0915 | 29267.5442
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | -333840.2618 | 2026-06-30 |  | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072
Option 1 (base case) | NPV | Option 1 (base case)NPV | -287878.4236 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | -333840.2618 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Capital expenditure | Option 2Capital expenditure | -7330567.2481 | 2026-06-30 |  | -2431038.2174 | -2934462.2111 | -2347569.7689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -5261574.3378 | 2026-06-30 |  | 0 | -132178.7851 | -291729.403 | -419369.8974 | -419369.8974 | -419369.8974 | -419369.8974 | -419369.8974 | -419369.8974 | -419369.8974 | -419369.8974 | -419369.8974 | -419369.8974 | -419369.8974 | -419369.8974 | -419369.8974 | -419369.8974 | -419369.8974 | -419369.8974 | -419369.8974 | 0 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 270422.1925 | 2026-06-30 |  | 14397.6924 | 14829.6232 | 15274.5119 | 15732.7472 | 16204.7296 | 16690.8715 | 17191.5977 | 17707.3456 | 18238.566 | 18785.7229 | 19349.2946 | 19929.7735 | 20527.6667 | 21143.4967 | 21777.8016 | 22431.1356 | 23104.0697 | 23797.1918 | 24511.1075 | 25246.4408 | 0 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 68818.9135 | 2026-06-30 |  | 0 | 0 | 4340.3593 | 4470.5701 | 4604.6872 | 4742.8278 | 4885.1127 | 5031.666 | 5182.616 | 5338.0945 | 5498.2373 | 5663.1845 | 5833.08 | 6008.0724 | 6188.3146 | 6373.964 | 6565.1829 | 6762.1384 | 6965.0026 | 7173.9526 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 14397.6924 | -117349.1619 | -272114.5319 | -399166.5801 | -398560.4806 | -397936.1981 | -397293.1871 | -396630.8858 | -395948.7154 | -395246.08 | -394522.3654 | -393776.9395 | -393009.1508 | -392218.3284 | -391403.7813 | -390564.7978 | -389700.6448 | -388810.5672 | -387893.7873 | -386949.504 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | -4922333.2319 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -5261574.3378 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 339241.106 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Capital expenditure | Option 3Capital expenditure | -7403579.0169 | 2026-06-30 |  | -3611548.514 | -2063742.008 | -2063742.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -5354374.7263 | 2026-06-30 |  | 0 | -196364.7019 | -308573.1029 | -420781.504 | -420781.504 | -420781.504 | -420781.504 | -420781.504 | -420781.504 | -420781.504 | -420781.504 | -420781.504 | -420781.504 | -420781.504 | -420781.504 | -420781.504 | -420781.504 | -420781.504 | -420781.504 | -420781.504 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 270422.1925 | 2026-06-30 |  | 14397.6924 | 14829.6232 | 15274.5119 | 15732.7472 | 16204.7296 | 16690.8715 | 17191.5977 | 17707.3456 | 18238.566 | 18785.7229 | 19349.2946 | 19929.7735 | 20527.6667 | 21143.4967 | 21777.8016 | 22431.1356 | 23104.0697 | 23797.1918 | 24511.1075 | 25246.4408 | 0 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 68818.9135 | 2026-06-30 |  | 0 | 0 | 4340.3593 | 4470.5701 | 4604.6872 | 4742.8278 | 4885.1127 | 5031.666 | 5182.616 | 5338.0945 | 5498.2373 | 5663.1845 | 5833.08 | 6008.0724 | 6188.3146 | 6373.964 | 6565.1829 | 6762.1384 | 6965.0026 | 7173.9526 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 14397.6924 | -181535.0787 | -288958.2318 | -400578.1867 | -399972.0872 | -399347.8047 | -398704.7937 | -398042.4924 | -397360.322 | -396657.6866 | -395933.972 | -395188.5461 | -394420.7574 | -393629.935 | -392815.3879 | -391976.4044 | -391112.2514 | -390222.1738 | -389305.3939 | -388361.1106 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | -5015133.6204 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -5354374.7263 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 339241.106 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | -8686475.9611 | 2026-06-30 |  | -4354129.2779 | -2989462.5806 | -1708264.3318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | -6304583.1896 | 2026-06-30 |  | 0 | -236739.8068 | -399280.8681 | -492161.4746 | -492161.4746 | -492161.4746 | -492161.4746 | -492161.4746 | -492161.4746 | -492161.4746 | -492161.4746 | -492161.4746 | -492161.4746 | -492161.4746 | -492161.4746 | -492161.4746 | -492161.4746 | -492161.4746 | -492161.4746 | -492161.4746 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 270422.1925 | 2026-06-30 |  | 14397.6924 | 14829.6232 | 15274.5119 | 15732.7472 | 16204.7296 | 16690.8715 | 17191.5977 | 17707.3456 | 18238.566 | 18785.7229 | 19349.2946 | 19929.7735 | 20527.6667 | 21143.4967 | 21777.8016 | 22431.1356 | 23104.0697 | 23797.1918 | 24511.1075 | 25246.4408 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 68818.9135 | 2026-06-30 |  | 0 | 0 | 4340.3593 | 4470.5701 | 4604.6872 | 4742.8278 | 4885.1127 | 5031.666 | 5182.616 | 5338.0945 | 5498.2373 | 5663.1845 | 5833.08 | 6008.0724 | 6188.3146 | 6373.964 | 6565.1829 | 6762.1384 | 6965.0026 | 7173.9526 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 14397.6924 | -221910.1837 | -379665.9969 | -471958.1573 | -471352.0577 | -470727.7752 | -470084.7643 | -469422.4629 | -468740.2926 | -468037.6571 | -467313.9426 | -466568.5167 | -465800.7279 | -465009.9055 | -464195.3584 | -463356.375 | -462492.222 | -461602.1444 | -460685.3645 | -459741.0812 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | -5965342.0836 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | -6304583.1896 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 339241.106 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | -10842256.4527 | 2026-06-30 |  | -5288973.7641 | -3022270.7223 | -3022270.7223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | -7841275.658 | 2026-06-30 |  | 0 | -287568.5464 | -451893.43 | -616218.3137 | -616218.3137 | -616218.3137 | -616218.3137 | -616218.3137 | -616218.3137 | -616218.3137 | -616218.3137 | -616218.3137 | -616218.3137 | -616218.3137 | -616218.3137 | -616218.3137 | -616218.3137 | -616218.3137 | -616218.3137 | -616218.3137 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 270422.1925 | 2026-06-30 |  | 14397.6924 | 14829.6232 | 15274.5119 | 15732.7472 | 16204.7296 | 16690.8715 | 17191.5977 | 17707.3456 | 18238.566 | 18785.7229 | 19349.2946 | 19929.7735 | 20527.6667 | 21143.4967 | 21777.8016 | 22431.1356 | 23104.0697 | 23797.1918 | 24511.1075 | 25246.4408 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 68818.9135 | 2026-06-30 |  | 0 | 0 | 4340.3593 | 4470.5701 | 4604.6872 | 4742.8278 | 4885.1127 | 5031.666 | 5182.616 | 5338.0945 | 5498.2373 | 5663.1845 | 5833.08 | 6008.0724 | 6188.3146 | 6373.964 | 6565.1829 | 6762.1384 | 6965.0026 | 7173.9526 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 14397.6924 | -272738.9232 | -432278.5589 | -596014.9964 | -595408.8969 | -594784.6144 | -594141.6034 | -593479.3021 | -592797.1317 | -592094.4963 | -591370.7817 | -590625.3558 | -589857.567 | -589066.7446 | -588252.1976 | -587413.2141 | -586549.0611 | -585658.9835 | -584742.2036 | -583797.9203 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | -7502034.552 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | -7841275.658 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 339241.106 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0.41937 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 0.014398 | 0.01483 | 0.015275 | 0.015733 | 0.016205 | 0.016691 | 0.017192 | 0.017707 | 0.018239 | 0.018786 | 0.019349 | 0.01993 | 0.020528 | 0.021143 | 0.021778 | 0.022431 | 0.023104 | 0.023797 | 0.024511 | 0.025246 | 0.026004 | 0.026784 | 0.027587 | 0.028415 | 0.029268
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 0 |  |  | Energy at risk energy at risk (weighted) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Energy at risk value | 0 |  |  | Option 1 (base case) risk cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Sensitivity_calcs
Powercor
Northern Murray harmonics management
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
[7 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | -387893.7873 | -386949.504 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | -325269.2351 |  | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | -287878.4236 |  | 0 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | -287878.4236 |  | 0 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | -287878.4236 |  | 0 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | -287878.4236 |  | 0 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | -287878.4236 |  | 0 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | -287878.4236 |  | 0 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | -287878.4236 |  | 0 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | -287878.4236 |  | 0 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | -19910.0072 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | -4922333.2319 |  | 0 | 14397.6924 | -117349.1619 | -272114.5319 | -399166.5801 | -398560.4806 | -397936.1981 | -397293.1871 | -396630.8858 | -395948.7154 | -395246.08 | -394522.3654 | -393776.9395 | -393009.1508 | -392218.3284 | -391403.7813 | -390564.7978 | -389700.6448 | -388810.5672 | -387893.7873 | -386949.504 | 0 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | -5448490.6656 |  | 0 | 14397.6924 | -130567.0404 | -301287.4722 | -441103.5698 | -440497.4703 | -439873.1878 | -439230.1768 | -438567.8755 | -437885.7052 | -437183.0697 | -436459.3552 | -435713.9292 | -434946.1405 | -434155.3181 | -433340.771 | -432501.7875 | -431637.6346 | -430747.557 | -429830.7771 | -428886.4938 | 0 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | -4396175.7981 |  | 0 | 14397.6924 | -104131.2834 | -242941.5916 | -357229.5904 | -356623.4908 | -355999.2083 | -355356.1973 | -354693.896 | -354011.7257 | -353309.0902 | -352585.3757 | -351839.9497 | -351072.161 | -350281.3386 | -349466.7915 | -348627.8081 | -347763.6551 | -346873.5775 | -345956.7976 | -345012.5143 | 0 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | -4888409.1213 |  | 0 | 15837.4616 | -115866.1996 | -270153.0447 | -397146.2484 | -396479.5389 | -395792.8281 | -395085.5161 | -394356.9846 | -393606.5972 | -392833.6982 | -392037.6123 | -391217.6437 | -390373.0761 | -389503.1714 | -388607.1697 | -387684.2878 | -386733.7195 | -385754.6342 | -384746.1763 | -383707.4647 | 0 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | -4956257.3425 |  | 0 | 12957.9232 | -118832.1242 | -274076.019 | -401186.9118 | -400641.4223 | -400079.568 | -399500.8581 | -398904.7869 | -398290.8336 | -397658.4617 | -397007.1186 | -396336.2353 | -395645.2254 | -394933.4853 | -394200.3929 | -393445.3078 | -392667.5701 | -391866.5002 | -391041.3983 | -390191.5434 | 0 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | -5482414.7762 |  | 0 | 12957.9232 | -132050.0027 | -303248.9593 | -443123.9016 | -442578.412 | -442016.5577 | -441437.8479 | -440841.7767 | -440227.8234 | -439595.4515 | -438944.1084 | -438273.225 | -437582.2152 | -436870.475 | -436137.3826 | -435382.2975 | -434604.5598 | -433803.49 | -432978.3881 | -432128.5331 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | -4922333.2319 |  | 0 | 14397.6924 | -117349.1619 | -272114.5319 | -399166.5801 | -398560.4806 | -397936.1981 | -397293.1871 | -396630.8858 | -395948.7154 | -395246.08 | -394522.3654 | -393776.9395 | -393009.1508 | -392218.3284 | -391403.7813 | -390564.7978 | -389700.6448 | -388810.5672 | -387893.7873 | -386949.504 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | -4922333.2319 |  | 0 | 14397.6924 | -117349.1619 | -272114.5319 | -399166.5801 | -398560.4806 | -397936.1981 | -397293.1871 | -396630.8858 | -395948.7154 | -395246.08 | -394522.3654 | -393776.9395 | -393009.1508 | -392218.3284 | -391403.7813 | -390564.7978 | -389700.6448 | -388810.5672 | -387893.7873 | -386949.504 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | -4922333.2319 |  | 0 | 14397.6924 | -117349.1619 | -272114.5319 | -399166.5801 | -398560.4806 | -397936.1981 | -397293.1871 | -396630.8858 | -395948.7154 | -395246.08 | -394522.3654 | -393776.9395 | -393009.1508 | -392218.3284 | -391403.7813 | -390564.7978 | -389700.6448 | -388810.5672 | -387893.7873 | -386949.504 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 14397.6924 | -181535.0787 | -288958.2318 | -400578.1867 | -399972.0872 | -399347.8047 | -398704.7937 | -398042.4924 | -397360.322 | -396657.6866 | -395933.972 | -395188.5461 | -394420.7574 | -393629.935 | -392815.3879 | -391976.4044 | -391112.2514 | -390222.1738 | -389305.3939 | -388361.1106 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | -5015133.6204 |  | 0 | 14397.6924 | -181535.0787 | -288958.2318 | -400578.1867 | -399972.0872 | -399347.8047 | -398704.7937 | -398042.4924 | -397360.322 | -396657.6866 | -395933.972 | -395188.5461 | -394420.7574 | -393629.935 | -392815.3879 | -391976.4044 | -391112.2514 | -390222.1738 | -389305.3939 | -388361.1106 | 0 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | -5550571.093 |  | 0 | 14397.6924 | -201171.5489 | -319815.5421 | -442656.3371 | -442050.2376 | -441425.9551 | -440782.9441 | -440120.6428 | -439438.4724 | -438735.837 | -438012.1224 | -437266.6965 | -436498.9078 | -435708.0854 | -434893.5383 | -434054.5548 | -433190.4018 | -432300.3242 | -431383.5443 | -430439.261 | 0 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | -4479696.1477 |  | 0 | 14397.6924 | -161898.6085 | -258100.9215 | -358500.0363 | -357893.9368 | -357269.6543 | -356626.6433 | -355964.342 | -355282.1716 | -354579.5362 | -353855.8216 | -353110.3957 | -352342.6069 | -351551.7845 | -350737.2375 | -349898.254 | -349034.101 | -348144.0234 | -347227.2435 | -346282.9602 | 0 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | -4981209.5098 |  | 0 | 15837.4616 | -180052.1164 | -286996.7446 | -398557.855 | -397891.1455 | -397204.4347 | -396497.1227 | -395768.5912 | -395018.2038 | -394245.3048 | -393449.2189 | -392629.2503 | -391784.6827 | -390914.778 | -390018.7763 | -389095.8944 | -388145.3261 | -387166.2408 | -386157.7829 | -385119.0713 | 0 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | -5049057.731 |  | 0 | 12957.9232 | -183018.041 | -290919.7189 | -402598.5184 | -402053.0289 | -401491.1746 | -400912.4647 | -400316.3935 | -399702.4402 | -399070.0683 | -398418.7252 | -397747.8419 | -397056.832 | -396345.0919 | -395611.9995 | -394856.9144 | -394079.1767 | -393278.1068 | -392453.0049 | -391603.15 | 0 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | -5584495.2036 |  | 0 | 12957.9232 | -202654.5112 | -321777.0292 | -444676.6688 | -444131.1793 | -443569.325 | -442990.6151 | -442394.5439 | -441780.5906 | -441148.2187 | -440496.8756 | -439825.9923 | -439134.9824 | -438423.2423 | -437690.1499 | -436935.0648 | -436157.3271 | -435356.2572 | -434531.1553 | -433681.3004 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -5015133.6204 |  | 0 | 14397.6924 | -181535.0787 | -288958.2318 | -400578.1867 | -399972.0872 | -399347.8047 | -398704.7937 | -398042.4924 | -397360.322 | -396657.6866 | -395933.972 | -395188.5461 | -394420.7574 | -393629.935 | -392815.3879 | -391976.4044 | -391112.2514 | -390222.1738 | -389305.3939 | -388361.1106 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -5015133.6204 |  | 0 | 14397.6924 | -181535.0787 | -288958.2318 | -400578.1867 | -399972.0872 | -399347.8047 | -398704.7937 | -398042.4924 | -397360.322 | -396657.6866 | -395933.972 | -395188.5461 | -394420.7574 | -393629.935 | -392815.3879 | -391976.4044 | -391112.2514 | -390222.1738 | -389305.3939 | -388361.1106 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -5015133.6204 |  | 0 | 14397.6924 | -181535.0787 | -288958.2318 | -400578.1867 | -399972.0872 | -399347.8047 | -398704.7937 | -398042.4924 | -397360.322 | -396657.6866 | -395933.972 | -395188.5461 | -394420.7574 | -393629.935 | -392815.3879 | -391976.4044 | -391112.2514 | -390222.1738 | -389305.3939 | -388361.1106 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | -5965342.0836 |  | 0 | 14397.6924 | -221910.1837 | -379665.9969 | -471958.1573 | -471352.0577 | -470727.7752 | -470084.7643 | -469422.4629 | -468740.2926 | -468037.6571 | -467313.9426 | -466568.5167 | -465800.7279 | -465009.9055 | -464195.3584 | -463356.375 | -462492.222 | -461602.1444 | -460685.3645 | -459741.0812 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | -6595800.4026 |  | 0 | 14397.6924 | -245584.1643 | -419594.0838 | -521174.3047 | -520568.2052 | -519943.9227 | -519300.9117 | -518638.6104 | -517956.4401 | -517253.8046 | -516530.0901 | -515784.6641 | -515016.8754 | -514226.053 | -513411.5059 | -512572.5224 | -511708.3694 | -510818.2919 | -509901.512 | -508957.2286 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | -5334883.7647 |  | 0 | 14397.6924 | -198236.203 | -339737.9101 | -422742.0098 | -422135.9103 | -421511.6278 | -420868.6168 | -420206.3155 | -419524.1451 | -418821.5097 | -418097.7952 | -417352.3692 | -416584.5805 | -415793.7581 | -414979.211 | -414140.2275 | -413276.0745 | -412385.9969 | -411469.217 | -410524.9337 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | -5931417.973 |  | 0 | 15837.4616 | -220427.2213 | -377704.5098 | -469937.8255 | -469271.1161 | -468584.4053 | -467877.0932 | -467148.5618 | -466398.1744 | -465625.2754 | -464829.1894 | -464009.2209 | -463164.6533 | -462294.7486 | -461398.7468 | -460475.865 | -459525.2967 | -458546.2114 | -457537.7535 | -456499.0419 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | -5999266.1942 |  | 0 | 12957.9232 | -223393.146 | -381627.4841 | -473978.489 | -473432.9994 | -472871.1452 | -472292.4353 | -471696.3641 | -471082.4108 | -470450.0389 | -469798.6958 | -469127.8125 | -468436.8026 | -467725.0624 | -466991.9701 | -466236.8849 | -465459.1472 | -464658.0774 | -463832.9755 | -462983.1205 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | -6629724.5132 |  | 0 | 12957.9232 | -247067.1267 | -421555.5709 | -523194.6365 | -522649.1469 | -522087.2926 | -521508.5828 | -520912.5116 | -520298.5583 | -519666.1863 | -519014.8433 | -518343.9599 | -517652.95 | -516941.2099 | -516208.1175 | -515453.0324 | -514675.2947 | -513874.2249 | -513049.123 | -512199.268 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | -5965342.0836 |  | 0 | 14397.6924 | -221910.1837 | -379665.9969 | -471958.1573 | -471352.0577 | -470727.7752 | -470084.7643 | -469422.4629 | -468740.2926 | -468037.6571 | -467313.9426 | -466568.5167 | -465800.7279 | -465009.9055 | -464195.3584 | -463356.375 | -462492.222 | -461602.1444 | -460685.3645 | -459741.0812 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | -5965342.0836 |  | 0 | 14397.6924 | -221910.1837 | -379665.9969 | -471958.1573 | -471352.0577 | -470727.7752 | -470084.7643 | -469422.4629 | -468740.2926 | -468037.6571 | -467313.9426 | -466568.5167 | -465800.7279 | -465009.9055 | -464195.3584 | -463356.375 | -462492.222 | -461602.1444 | -460685.3645 | -459741.0812 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | -5965342.0836 |  | 0 | 14397.6924 | -221910.1837 | -379665.9969 | -471958.1573 | -471352.0577 | -470727.7752 | -470084.7643 | -469422.4629 | -468740.2926 | -468037.6571 | -467313.9426 | -466568.5167 | -465800.7279 | -465009.9055 | -464195.3584 | -463356.375 | -462492.222 | -461602.1444 | -460685.3645 | -459741.0812 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | -7502034.552 |  | 0 | 14397.6924 | -272738.9232 | -432278.5589 | -596014.9964 | -595408.8969 | -594784.6144 | -594141.6034 | -593479.3021 | -592797.1317 | -592094.4963 | -591370.7817 | -590625.3558 | -589857.567 | -589066.7446 | -588252.1976 | -587413.2141 | -586549.0611 | -585658.9835 | -584742.2036 | -583797.9203 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | -8286162.1178 |  | 0 | 14397.6924 | -301495.7779 | -477467.9019 | -657636.8277 | -657030.7282 | -656406.4457 | -655763.4347 | -655101.1334 | -654418.9631 | -653716.3276 | -652992.6131 | -652247.1871 | -651479.3984 | -650688.576 | -649874.0289 | -649035.0454 | -648170.8925 | -647280.8149 | -646364.035 | -645419.7517 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | -6717906.9862 |  | 0 | 14397.6924 | -243982.0686 | -387089.2159 | -534393.165 | -533787.0655 | -533162.783 | -532519.772 | -531857.4707 | -531175.3003 | -530472.6649 | -529748.9504 | -529003.5244 | -528235.7357 | -527444.9133 | -526630.3662 | -525791.3827 | -524927.2297 | -524037.1521 | -523120.3722 | -522176.0889 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | -7468110.4414 |  | 0 | 15837.4616 | -271255.9609 | -430317.0717 | -593994.6646 | -593327.9552 | -592641.2444 | -591933.9323 | -591205.4009 | -590455.0135 | -589682.1145 | -588886.0285 | -588066.06 | -587221.4924 | -586351.5877 | -585455.5859 | -584532.7041 | -583582.1358 | -582603.0505 | -581594.5926 | -580555.881 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | -7535958.6626 |  | 0 | 12957.9232 | -274221.8855 | -434240.046 | -598035.3281 | -597489.8385 | -596927.9843 | -596349.2744 | -595753.2032 | -595139.2499 | -594506.878 | -593855.5349 | -593184.6516 | -592493.6417 | -591781.9015 | -591048.8092 | -590293.724 | -589515.9863 | -588714.9165 | -587889.8146 | -587039.9596 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | -8320086.2284 |  | 0 | 12957.9232 | -302978.7402 | -479429.389 | -659657.1595 | -659111.6699 | -658549.8157 | -657971.1058 | -657375.0346 | -656761.0813 | -656128.7094 | -655477.3663 | -654806.4829 | -654115.4731 | -653403.7329 | -652670.6405 | -651915.5554 | -651137.8177 | -650336.7479 | -649511.646 | -648661.791 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | -7502034.552 |  | 0 | 14397.6924 | -272738.9232 | -432278.5589 | -596014.9964 | -595408.8969 | -594784.6144 | -594141.6034 | -593479.3021 | -592797.1317 | -592094.4963 | -591370.7817 | -590625.3558 | -589857.567 | -589066.7446 | -588252.1976 | -587413.2141 | -586549.0611 | -585658.9835 | -584742.2036 | -583797.9203 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | -7502034.552 |  | 0 | 14397.6924 | -272738.9232 | -432278.5589 | -596014.9964 | -595408.8969 | -594784.6144 | -594141.6034 | -593479.3021 | -592797.1317 | -592094.4963 | -591370.7817 | -590625.3558 | -589857.567 | -589066.7446 | -588252.1976 | -587413.2141 | -586549.0611 | -585658.9835 | -584742.2036 | -583797.9203 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | -7502034.552 |  | 0 | 14397.6924 | -272738.9232 | -432278.5589 | -596014.9964 | -595408.8969 | -594784.6144 | -594141.6034 | -593479.3021 | -592797.1317 | -592094.4963 | -591370.7817 | -590625.3558 | -589857.567 | -589066.7446 | -588252.1976 | -587413.2141 | -586549.0611 | -585658.9835 | -584742.2036 | -583797.9203 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 1 | 0 | 0 | 0 | 0 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None |  | -4.9223 | -5.0151 | -5.9653 | -7.502 |  | 2026-27: #NAME?; 2028-29: Option 2
sens1 | Capex 10% higher |  | -5.4485 | -5.5506 | -6.5958 | -8.2862 |  | 2026-27: #NAME?; 2028-29: Option 2
sens2 | Capex 10% lower |  | -4.3962 | -4.4797 | -5.3349 | -6.7179 |  | 2026-27: #NAME?; 2028-29: Option 2
sens3 | Total benefits 10% higher |  | -4.8884 | -4.9812 | -5.9314 | -7.4681 |  | 2026-27: #NAME?; 2028-29: Option 2
sens4 | Total benefits 10% lower |  | -4.9563 | -5.0491 | -5.9993 | -7.536 |  | 2026-27: #NAME?; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower |  | -5.4824 | -5.5845 | -6.6297 | -8.3201 |  | 2026-27: #NAME?; 2028-29: Option 2
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Workings_risks
Powercor
Northern Murray harmonics management
WORKINGS - RISKS
Option 1 (base case)
Extra losses in transformers and lines due to high harmonics.
|  |  | Total losses estimated (rate $0.1 per kwh) |  | 15700 | kwh
|  |  |  | 0.1 | 1570 | per year
Reduction of the lifetime of line assets due to high harmonics.
|  |  | Tx life without harmonic |  | 36 | Years
|  |  | Tx life with harmonic |  | 28 | Years
|  |  | Cost for Tx replacement (considering mix of Kiosk & pole top Tx) |  | 75000 | per MVA
|  |  | Extra loss due to harmonic |  | 595.2381 | per 1 MVA Tx
|  |  | The nameplate rating of the DSS in the high harmonic area |  | 122 | MVA
|  |  | Extra cost due to harmonic |  | 2593.5374 | per year
Risks due to high harmonic
Reduction of the utilization factors of transformers and other line assets due to high harmonics.
|  |  | Load of the network in the Mallee region increased due to high harmonic (based on UOW calc sheet) |  | 3.5 | %
|  |  | Total MD in high harmonic area of BBD, MBN and WMN |  | 58 | MVA
|  |  | Reduction of utilisation of Tx due to harmonic |  | 2.03 | MVA
|  |  | Cost of additional Tx (mix of Kiosk & pole top as well as different sizes) |  | 75000 | per MVA
|  |  | Cost for additional Tx due to harmonic |  | 155000 | entire life of the Tx
|  |  | The average Tx life in Mallee region |  | 28 | Years
|  |  | Cost for additional Tx due to harmonic |  | 8773.41 | per year
[7 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | Continued worsening of harmonics |  |  | 3% |  | 1 | 1.03 | 1.0609 | 1.0927 | 1.1255 | 1.1593 | 1.1941 | 1.2299 | 1.2668 | 1.3048 | 1.3439 | 1.3842 | 1.4258 | 1.4685 | 1.5126 | 1.558 | 1.6047 | 1.6528 | 1.7024 | 1.7535 | 1.8061 | 1.8603 | 1.9161 | 1.9736 | 2.0328

## Workings_benefits
Powercor
Northern Murray harmonics management
WORKINGS - BENEFITS
Options 2 - 5
Reduction in production losses
|  |  | Production losses ($500 per year) |  |  |  | 500 | per year
Reduced motor losses and reduction in asset life of customer assets
|  |  | 3000 kwh/year loss (rate $0.1) | 0.1 | 3000 | kwh | 300 | per year
|  | Asset failure due to high harmonic |  |  |  |  | 500 | per year
|  | Total customer benefit |  |  |  |  | 3900 | per year

## Misc_calcs
Powercor
Northern Murray harmonics management
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 1 | TRUE
| Option 3 | 1 | TRUE
| Option 4 | 1 | TRUE
| Option 5 | 1 | TRUE
| First year | 1
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
Powercor
Northern Murray harmonics management
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | TRUE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | FALSE |  |  | FALSE
Option5 | Option 5 | FALSE |  |  | FALSE
Compliance project |  |  | Yes | TRUE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
Powercor
| Reliability in worst-served areas | per MWh | 151432.8174
| Network resilience | per MWh | 24590
| Enabling solar exports | per MWh | 88.3577
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.35181
| Customer value of time - business | per minute customer time | 0.35181
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020