## Cover
Powercor
Regulatory proposal 2026-31
REFCL BAE compliance
| Model number: | 3.12
2025-01-31
13

## Summary
Powercor
REFCL BAE compliance
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Isolating substations, REFCL mini grids, deferred Ballarat East substation |  | -12.0559 | 44.3175 | 32.2616
| Option 3 | Ballarat East zone substation 2nd transformer and REFCL, isolating substations |  | -9.5249 | 44.3175 | 34.7926
| Option 4 | Mini zone substation, REFCL mini grid, isolating substations |  | -19.5603 | 44.3175 | 24.7572
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 3 | Ballarat East zone substation 2nd transformer and REFCL, isolating substations |  | 34.7926
PREFERRED OPTION
Preferred Option
Option 3
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 0.73174 | 13.1713 | 0.73174 | 0 | 0 |  | 14.6348
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  |  | 32.2616 | 34.7926 | 24.7572 |  |  | Option 3
| Capex 10% higher |  |  | 31.056 | 33.8401 | 22.8012 |  |  | Option 3
| Capex 10% lower |  |  | 33.4672 | 35.7451 | 26.7133 |  |  | Option 3
| Total benefits 10% higher |  |  | 36.6933 | 39.2244 | 29.189 |  |  | Option 3
| Total benefits 10% lower |  |  | 27.8298 | 30.3609 | 20.3255 |  |  | Option 3
| Capex 10% higher & Total benefits 10% lower |  |  | 26.6242 | 29.4084 | 18.3695 |  |  | Option 3
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
Powercor
REFCL BAE compliance
Project
|  | Business: | select > | Powercor
|  | Descripton: |  | REFCL BAE compliance
|  | Date of cost inputs: | select > | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Isolating substations, REFCL mini grids, deferred Ballarat East substation
|  | Option 3 |  | Ballarat East zone substation 2nd transformer and REFCL, isolating substations
|  | Option 4 |  | Mini zone substation, REFCL mini grid, isolating substations
Option 5
|  | Compliance project |  | Yes
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | BAN |  | Ballarat North | 44753.327 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 151432.8174 | 2023-12-31 | per MWh
|  | Network resilience |  |  |  | 24590 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 88.3577 | 2023-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
Powercor
REFCL BAE compliance
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 44753.327 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| REFCL civil penalties |  |  | 2023-12-31 |  | 0 | 0 | 18000000 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500
|  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 0 | 0 | 18000000 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
Powercor
REFCL BAE compliance
OPTION 2 | Isolating substations, REFCL mini grids, deferred Ballarat East substation
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Isolating substations x 4 |  | 50 | 2023-12-31 | 0 | 1600000 |  | 1600000 |  | 1600000 |  | 1600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| REFCL mini grid |  | 50 | 2023-12-31 | 2000000 | 6000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ballarat East 2nd transformer and REFCL, feeder transfers |  | 50 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 657500 | 11835000 | 657500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 2000000 | 7600000 | 0 | 1600000 | 0 | 1600000 | 0 | 2257500 | 11835000 | 657500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 44753.327 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| REFCL civil penalties |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 18000000 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500
Capital expenditure
| Isolating substations x 4 |  |  | 2023-12-31 | 0 | -1600000 | 0 | -1600000 | 0 | -1600000 | 0 | -1600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| REFCL mini grid |  |  | 2023-12-31 | -2000000 | -6000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ballarat East 2nd transformer and REFCL, feeder transfers |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -657500 | -11835000 | -657500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Isolating substations x 4 |  |  | 2023-12-31 | 0 | -1600000 | -1600000 | -3200000 | -3200000 | -4800000 | -4800000 | -6400000 | -6400000 | -6400000 | -6400000 | -6400000 | -6400000 | -6400000 | -6400000 | -6400000 | -6400000 | -6400000 | -6400000 | -6400000 | -6400000 | -6400000 | -6400000 | -6400000 | -6400000
| REFCL mini grid |  |  | 2023-12-31 | -2000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000
| Ballarat East 2nd transformer and REFCL, feeder transfers |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -657500 | -12492500 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000
Annualised capex
| Annualised capex - Isolating substations x 4 |  |  | 2023-12-31 | 0 | 0 | -68213.9353 | -68213.9353 | -136427.8706 | -136427.8706 | -204641.8059 | -204641.8059 | -272855.7412 | -272855.7412 | -272855.7412 | -272855.7412 | -272855.7412 | -272855.7412 | -272855.7412 | -272855.7412 | -272855.7412 | -272855.7412 | -272855.7412 | -272855.7412 | -272855.7412 | -272855.7412 | -272855.7412 | -272855.7412 | -272855.7412
| Annualised capex - REFCL mini grid |  |  | 2023-12-31 | 0 | -85267.4191 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765
| Annualised capex - Ballarat East 2nd transformer and REFCL, feeder transfers |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -28031.664 | -532601.6168 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808
| Total annualised capex |  |  | 2023-12-31 | 0 | -85267.4191 | -409283.6118 | -409283.6118 | -477497.5471 | -477497.5471 | -545711.4825 | -545711.4825 | -641957.0818 | -1146527.0345 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986
| Annualised capex |  |  | 2023-12-31 | 0 | -85267.4191 | -409283.6118 | -409283.6118 | -477497.5471 | -477497.5471 | -545711.4825 | -545711.4825 | -641957.0818 | -1146527.0345 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 18000000 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | -85267.4191 | 17590716.3882 | 1598216.3882 | 1530002.4529 | 1530002.4529 | 1461788.5175 | 1461788.5175 | 1365542.9182 | 860972.9655 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | -85267.4191 | 17590716.3882 | 1598216.3882 | 1530002.4529 | 1530002.4529 | 1461788.5175 | 1461788.5175 | 1365542.9182 | 860972.9655 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014
| Total annualised capex |  |  |  | 0 | -85267.4191 | -409283.6118 | -409283.6118 | -477497.5471 | -477497.5471 | -545711.4825 | -545711.4825 | -641957.0818 | -1146527.0345 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986 | -1174558.6986
| Total benefits |  |  |  | 0 | 0 | 18000000 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | -93794.161 | 17549788.027 | 1557288.027 | 1482252.6981 | 1482252.6981 | 1407217.3693 | 1407217.3693 | 1301347.21 | 746320.262 | 715485.4316 | 715485.4316 | 715485.4316 | 715485.4316 | 715485.4316 | 715485.4316 | 715485.4316 | 715485.4316 | 715485.4316 | 715485.4316 | 715485.4316 | 715485.4316 | 715485.4316 | 715485.4316 | 715485.4316
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | -76740.6772 | 17631644.7493 | 1639144.7493 | 1577752.2076 | 1577752.2076 | 1516359.6658 | 1516359.6658 | 1429738.6264 | 975625.6689 | 950397.1713 | 950397.1713 | 950397.1713 | 950397.1713 | 950397.1713 | 950397.1713 | 950397.1713 | 950397.1713 | 950397.1713 | 950397.1713 | 950397.1713 | 950397.1713 | 950397.1713 | 950397.1713 | 950397.1713
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | -85267.4191 | 19390716.3882 | 1798966.3882 | 1730752.4529 | 1730752.4529 | 1662538.5175 | 1662538.5175 | 1566292.9182 | 1061722.9655 | 1033691.3014 | 1033691.3014 | 1033691.3014 | 1033691.3014 | 1033691.3014 | 1033691.3014 | 1033691.3014 | 1033691.3014 | 1033691.3014 | 1033691.3014 | 1033691.3014 | 1033691.3014 | 1033691.3014 | 1033691.3014 | 1033691.3014
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | -85267.4191 | 15790716.3882 | 1397466.3882 | 1329252.4529 | 1329252.4529 | 1261038.5175 | 1261038.5175 | 1164792.9182 | 660222.9655 | 632191.3014 | 632191.3014 | 632191.3014 | 632191.3014 | 632191.3014 | 632191.3014 | 632191.3014 | 632191.3014 | 632191.3014 | 632191.3014 | 632191.3014 | 632191.3014 | 632191.3014 | 632191.3014 | 632191.3014
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | -93794.161 | 15749788.027 | 1356538.027 | 1281502.6981 | 1281502.6981 | 1206467.3693 | 1206467.3693 | 1100597.21 | 545570.262 | 514735.4316 | 514735.4316 | 514735.4316 | 514735.4316 | 514735.4316 | 514735.4316 | 514735.4316 | 514735.4316 | 514735.4316 | 514735.4316 | 514735.4316 | 514735.4316 | 514735.4316 | 514735.4316 | 514735.4316
sens | 0 | 0% | 0% | Option 2sens | 0 | -85267.4191 | 17590716.3882 | 1598216.3882 | 1530002.4529 | 1530002.4529 | 1461788.5175 | 1461788.5175 | 1365542.9182 | 860972.9655 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014
sens | 0 | 0% | 0% | Option 2sens | 0 | -85267.4191 | 17590716.3882 | 1598216.3882 | 1530002.4529 | 1530002.4529 | 1461788.5175 | 1461788.5175 | 1365542.9182 | 860972.9655 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014
sens | 0 | 0% | 0% | Option 2sens | 0 | -85267.4191 | 17590716.3882 | 1598216.3882 | 1530002.4529 | 1530002.4529 | 1461788.5175 | 1461788.5175 | 1365542.9182 | 860972.9655 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014 | 832941.3014

## Option3
Powercor
REFCL BAE compliance
OPTION 3 | Ballarat East zone substation 2nd transformer and REFCL, isolating substations
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Ballarat East 2nd transformer and REFCL, feeder transfers |  | 50 | 2023-12-31 | 657500 | 11835000 | 657500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Isolating substations x 3 |  | 50 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 1600000 |  | 1600000 |  | 1600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 657500 | 11835000 | 657500 | 0 | 0 | 1600000 | 0 | 1600000 | 0 | 1600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 44753.327 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| REFCL civil penalties |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 18000000 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500
Capital expenditure
| Ballarat East 2nd transformer and REFCL, feeder transfers |  |  | 2023-12-31 | -657500 | -11835000 | -657500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Isolating substations x 3 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | -1600000 | 0 | -1600000 | 0 | -1600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Ballarat East 2nd transformer and REFCL, feeder transfers |  |  | 2023-12-31 | -657500 | -12492500 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000 | -13150000
| Isolating substations x 3 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | -1600000 | -1600000 | -3200000 | -3200000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Ballarat East 2nd transformer and REFCL, feeder transfers |  |  | 2023-12-31 | 0 | -28031.664 | -532601.6168 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808 | -560633.2808
| Annualised capex - Isolating substations x 3 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | -68213.9353 | -68213.9353 | -136427.8706 | -136427.8706 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -28031.664 | -532601.6168 | -560633.2808 | -560633.2808 | -560633.2808 | -628847.2161 | -628847.2161 | -697061.1514 | -697061.1514 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867
| Annualised capex |  |  | 2023-12-31 | 0 | -28031.664 | -532601.6168 | -560633.2808 | -560633.2808 | -560633.2808 | -628847.2161 | -628847.2161 | -697061.1514 | -697061.1514 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 18000000 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | -28031.664 | 17467398.3832 | 1446866.7192 | 1446866.7192 | 1446866.7192 | 1378652.7839 | 1378652.7839 | 1310438.8486 | 1310438.8486 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | -28031.664 | 17467398.3832 | 1446866.7192 | 1446866.7192 | 1446866.7192 | 1378652.7839 | 1378652.7839 | 1310438.8486 | 1310438.8486 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133
| Total annualised capex |  |  |  | 0 | -28031.664 | -532601.6168 | -560633.2808 | -560633.2808 | -560633.2808 | -628847.2161 | -628847.2161 | -697061.1514 | -697061.1514 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867 | -765275.0867
| Total benefits |  |  |  | 0 | 0 | 18000000 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | -30834.8304 | 17414138.2216 | 1390803.3911 | 1390803.3911 | 1390803.3911 | 1315768.0623 | 1315768.0623 | 1240732.7334 | 1240732.7334 | 1165697.4046 | 1165697.4046 | 1165697.4046 | 1165697.4046 | 1165697.4046 | 1165697.4046 | 1165697.4046 | 1165697.4046 | 1165697.4046 | 1165697.4046 | 1165697.4046 | 1165697.4046 | 1165697.4046 | 1165697.4046 | 1165697.4046
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | -25228.4976 | 17520658.5449 | 1502930.0473 | 1502930.0473 | 1502930.0473 | 1441537.5055 | 1441537.5055 | 1380144.9637 | 1380144.9637 | 1318752.422 | 1318752.422 | 1318752.422 | 1318752.422 | 1318752.422 | 1318752.422 | 1318752.422 | 1318752.422 | 1318752.422 | 1318752.422 | 1318752.422 | 1318752.422 | 1318752.422 | 1318752.422 | 1318752.422
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | -28031.664 | 19267398.3832 | 1647616.7192 | 1647616.7192 | 1647616.7192 | 1579402.7839 | 1579402.7839 | 1511188.8486 | 1511188.8486 | 1442974.9133 | 1442974.9133 | 1442974.9133 | 1442974.9133 | 1442974.9133 | 1442974.9133 | 1442974.9133 | 1442974.9133 | 1442974.9133 | 1442974.9133 | 1442974.9133 | 1442974.9133 | 1442974.9133 | 1442974.9133 | 1442974.9133
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | -28031.664 | 15667398.3832 | 1246116.7192 | 1246116.7192 | 1246116.7192 | 1177902.7839 | 1177902.7839 | 1109688.8486 | 1109688.8486 | 1041474.9133 | 1041474.9133 | 1041474.9133 | 1041474.9133 | 1041474.9133 | 1041474.9133 | 1041474.9133 | 1041474.9133 | 1041474.9133 | 1041474.9133 | 1041474.9133 | 1041474.9133 | 1041474.9133 | 1041474.9133 | 1041474.9133
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | -30834.8304 | 15614138.2216 | 1190053.3911 | 1190053.3911 | 1190053.3911 | 1115018.0623 | 1115018.0623 | 1039982.7334 | 1039982.7334 | 964947.4046 | 964947.4046 | 964947.4046 | 964947.4046 | 964947.4046 | 964947.4046 | 964947.4046 | 964947.4046 | 964947.4046 | 964947.4046 | 964947.4046 | 964947.4046 | 964947.4046 | 964947.4046 | 964947.4046
sens | 0 | 0% | 0% | Option 3sens | 0 | -28031.664 | 17467398.3832 | 1446866.7192 | 1446866.7192 | 1446866.7192 | 1378652.7839 | 1378652.7839 | 1310438.8486 | 1310438.8486 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133
sens | 0 | 0% | 0% | Option 3sens | 0 | -28031.664 | 17467398.3832 | 1446866.7192 | 1446866.7192 | 1446866.7192 | 1378652.7839 | 1378652.7839 | 1310438.8486 | 1310438.8486 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133
sens | 0 | 0% | 0% | Option 3sens | 0 | -28031.664 | 17467398.3832 | 1446866.7192 | 1446866.7192 | 1446866.7192 | 1378652.7839 | 1378652.7839 | 1310438.8486 | 1310438.8486 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133 | 1242224.9133

## Option4
Powercor
REFCL BAE compliance
OPTION 4 | Mini zone substation, REFCL mini grid, isolating substations
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Mini zone substation |  | 50 | 2023-12-31 | 10209325.4424 | 10721863.2805 | 193811.4452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| REFCL mini grid |  | 50 | 2023-12-31 | 2000000 | 6000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Isolating substations x 3 |  | 50 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 1600000 |  | 1600000 |  | 1600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 12209325.4424 | 16721863.2805 | 193811.4452 | 0 | 0 | 1600000 | 0 | 1600000 | 0 | 1600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 44753.327 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| REFCL civil penalties |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 18000000 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500
Capital expenditure
| Mini zone substation |  |  | 2023-12-31 | -10209325.4424 | -10721863.2805 | -193811.4452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| REFCL mini grid |  |  | 2023-12-31 | -2000000 | -6000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Isolating substations x 3 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | -1600000 | 0 | -1600000 | 0 | -1600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Mini zone substation |  |  | 2023-12-31 | -10209325.4424 | -20931188.7229 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681 | -21125000.1681
| REFCL mini grid |  |  | 2023-12-31 | -2000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000 | -8000000
| Isolating substations x 3 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | -1600000 | -1600000 | -3200000 | -3200000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000 | -4800000
Annualised capex
| Annualised capex - Mini zone substation |  |  | 2023-12-31 | 0 | -435261.4158 | -892374.2209 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218 | -900637.1218
| Annualised capex - REFCL mini grid |  |  | 2023-12-31 | 0 | -85267.4191 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765 | -341069.6765
| Annualised capex - Isolating substations x 3 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | -68213.9353 | -68213.9353 | -136427.8706 | -136427.8706 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059 | -204641.8059
| Total annualised capex |  |  | 2023-12-31 | 0 | -520528.8349 | -1233443.8974 | -1241706.7983 | -1241706.7983 | -1241706.7983 | -1309920.7336 | -1309920.7336 | -1378134.6689 | -1378134.6689 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042
| Annualised capex |  |  | 2023-12-31 | 0 | -520528.8349 | -1233443.8974 | -1241706.7983 | -1241706.7983 | -1241706.7983 | -1309920.7336 | -1309920.7336 | -1378134.6689 | -1378134.6689 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 18000000 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | -520528.8349 | 16766556.1026 | 765793.2017 | 765793.2017 | 765793.2017 | 697579.2664 | 697579.2664 | 629365.3311 | 629365.3311 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | -520528.8349 | 16766556.1026 | 765793.2017 | 765793.2017 | 765793.2017 | 697579.2664 | 697579.2664 | 629365.3311 | 629365.3311 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958
| Total annualised capex |  |  |  | 0 | -520528.8349 | -1233443.8974 | -1241706.7983 | -1241706.7983 | -1241706.7983 | -1309920.7336 | -1309920.7336 | -1378134.6689 | -1378134.6689 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042 | -1446348.6042
| Total benefits |  |  |  | 0 | 0 | 18000000 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500 | 2007500
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | -572581.7184 | 16643211.7128 | 641622.5219 | 641622.5219 | 641622.5219 | 566587.193 | 566587.193 | 491551.8642 | 491551.8642 | 416516.5354 | 416516.5354 | 416516.5354 | 416516.5354 | 416516.5354 | 416516.5354 | 416516.5354 | 416516.5354 | 416516.5354 | 416516.5354 | 416516.5354 | 416516.5354 | 416516.5354 | 416516.5354 | 416516.5354
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | -468475.9514 | 16889900.4923 | 889963.8815 | 889963.8815 | 889963.8815 | 828571.3398 | 828571.3398 | 767178.798 | 767178.798 | 705786.2562 | 705786.2562 | 705786.2562 | 705786.2562 | 705786.2562 | 705786.2562 | 705786.2562 | 705786.2562 | 705786.2562 | 705786.2562 | 705786.2562 | 705786.2562 | 705786.2562 | 705786.2562 | 705786.2562
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | -520528.8349 | 18566556.1026 | 966543.2017 | 966543.2017 | 966543.2017 | 898329.2664 | 898329.2664 | 830115.3311 | 830115.3311 | 761901.3958 | 761901.3958 | 761901.3958 | 761901.3958 | 761901.3958 | 761901.3958 | 761901.3958 | 761901.3958 | 761901.3958 | 761901.3958 | 761901.3958 | 761901.3958 | 761901.3958 | 761901.3958 | 761901.3958
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | -520528.8349 | 14966556.1026 | 565043.2017 | 565043.2017 | 565043.2017 | 496829.2664 | 496829.2664 | 428615.3311 | 428615.3311 | 360401.3958 | 360401.3958 | 360401.3958 | 360401.3958 | 360401.3958 | 360401.3958 | 360401.3958 | 360401.3958 | 360401.3958 | 360401.3958 | 360401.3958 | 360401.3958 | 360401.3958 | 360401.3958 | 360401.3958
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | -572581.7184 | 14843211.7128 | 440872.5219 | 440872.5219 | 440872.5219 | 365837.193 | 365837.193 | 290801.8642 | 290801.8642 | 215766.5354 | 215766.5354 | 215766.5354 | 215766.5354 | 215766.5354 | 215766.5354 | 215766.5354 | 215766.5354 | 215766.5354 | 215766.5354 | 215766.5354 | 215766.5354 | 215766.5354 | 215766.5354 | 215766.5354
sens | 0 | 0% | 0% | Option 4sens | 0 | -520528.8349 | 16766556.1026 | 765793.2017 | 765793.2017 | 765793.2017 | 697579.2664 | 697579.2664 | 629365.3311 | 629365.3311 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958
sens | 0 | 0% | 0% | Option 4sens | 0 | -520528.8349 | 16766556.1026 | 765793.2017 | 765793.2017 | 765793.2017 | 697579.2664 | 697579.2664 | 629365.3311 | 629365.3311 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958
sens | 0 | 0% | 0% | Option 4sens | 0 | -520528.8349 | 16766556.1026 | 765793.2017 | 765793.2017 | 765793.2017 | 697579.2664 | 697579.2664 | 629365.3311 | 629365.3311 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958 | 561151.3958

## Option5
Powercor
REFCL BAE compliance
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 44753.327 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| REFCL civil penalties |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
Powercor
REFCL BAE compliance
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 44317492.0858 | 2026-06-30 |  | 0 | 0 | 20032427.6355 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Capital expenditure | Option 2Capital expenditure | -25573646.9831 | 2026-06-30 |  | -2225825.2928 | -8458136.1128 | 0 | -1780660.2343 | 0 | -1780660.2343 | 0 | -2512400.2993 | -13171321.1703 | -731740.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -12055916.7722 | 2026-06-30 |  | 0 | -94895.1891 | -455496.9076 | -455496.9076 | -531413.0589 | -531413.0589 | -607329.2101 | -607329.2101 | -714442.1548 | -1275984.4362 | -1307181.2296 | -1307181.2296 | -1307181.2296 | -1307181.2296 | -1307181.2296 | -1307181.2296 | -1307181.2296 | -1307181.2296 | -1307181.2296 | -1307181.2296 | 0 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 44317492.0858 | 2026-06-30 |  | 0 | 0 | 20032427.6355 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 0 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | -94895.1891 | 19576930.7279 | 1778675.2301 | 1702759.0788 | 1702759.0788 | 1626842.9276 | 1626842.9276 | 1519729.9829 | 958187.7015 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 32261575.3135 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -12055916.7722 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 44317492.0858 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Capital expenditure | Option 3Capital expenditure | -18033250.1417 | 2026-06-30 |  | -731740.065 | -13171321.1703 | -731740.065 | 0 | 0 | -1780660.2343 | 0 | -1780660.2343 | 0 | -1780660.2343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -9524880.0795 | 2026-06-30 |  | 0 | -31196.7934 | -592739.0748 | -623935.8682 | -623935.8682 | -623935.8682 | -699852.0195 | -699852.0195 | -775768.1707 | -775768.1707 | -851684.322 | -851684.322 | -851684.322 | -851684.322 | -851684.322 | -851684.322 | -851684.322 | -851684.322 | -851684.322 | -851684.322 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 44317492.0858 | 2026-06-30 |  | 0 | 0 | 20032427.6355 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 0 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | -31196.7934 | 19439688.5607 | 1610236.2695 | 1610236.2695 | 1610236.2695 | 1534320.1182 | 1534320.1182 | 1458403.9669 | 1458403.9669 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | 34792612.0063 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -9524880.0795 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 44317492.0858 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | -35361784.1924 | 2026-06-30 |  | -13587912.689 | -18609973.1166 | -215695.2084 | 0 | 0 | -1780660.2343 | 0 | -1780660.2343 | 0 | -1780660.2343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | -19560256.0015 | 2026-06-30 |  | 0 | -579303.1232 | -1372715.3121 | -1381911.199 | -1381911.199 | -1381911.199 | -1457827.3502 | -1457827.3502 | -1533743.5015 | -1533743.5015 | -1609659.6528 | -1609659.6528 | -1609659.6528 | -1609659.6528 | -1609659.6528 | -1609659.6528 | -1609659.6528 | -1609659.6528 | -1609659.6528 | -1609659.6528 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 44317492.0858 | 2026-06-30 |  | 0 | 0 | 20032427.6355 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 2234172.1377 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | -579303.1232 | 18659712.3234 | 852260.9387 | 852260.9387 | 852260.9387 | 776344.7875 | 776344.7875 | 700428.6362 | 700428.6362 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 24757236.0843 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | -19560256.0015 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 44317492.0858 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 3 | Annualised capex | -1 |  |  | Option 3 annualised capex | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0.85168 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 0 | 0 | 20.0324 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342 | 2.2342
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 0 |  |  | Energy at risk energy at risk (weighted) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Energy at risk value | 0 |  |  | Option 1 (base case) risk cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Sensitivity_calcs
Powercor
REFCL BAE compliance
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
[7 empty] | 46203 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 926990.9081 | 926990.9081 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 32261575.3135 |  | 0 | 0 | -94895.1891 | 19576930.7279 | 1778675.2301 | 1702759.0788 | 1702759.0788 | 1626842.9276 | 1626842.9276 | 1519729.9829 | 958187.7015 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 0 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 31055983.6363 |  | 0 | 0 | -104384.708 | 19531381.0372 | 1733125.5393 | 1649617.7729 | 1649617.7729 | 1566110.0066 | 1566110.0066 | 1448285.7674 | 830589.2579 | 796272.7851 | 796272.7851 | 796272.7851 | 796272.7851 | 796272.7851 | 796272.7851 | 796272.7851 | 796272.7851 | 796272.7851 | 796272.7851 | 0 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 33467166.9908 |  | 0 | 0 | -85405.6702 | 19622480.4187 | 1824224.9209 | 1755900.3847 | 1755900.3847 | 1687575.8486 | 1687575.8486 | 1591174.1984 | 1085786.1451 | 1057709.0311 | 1057709.0311 | 1057709.0311 | 1057709.0311 | 1057709.0311 | 1057709.0311 | 1057709.0311 | 1057709.0311 | 1057709.0311 | 1057709.0311 | 0 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 36693324.5221 |  | 0 | 0 | -94895.1891 | 21580173.4915 | 2002092.4439 | 1926176.2926 | 1926176.2926 | 1850260.1413 | 1850260.1413 | 1743147.1967 | 1181604.9153 | 1150408.1219 | 1150408.1219 | 1150408.1219 | 1150408.1219 | 1150408.1219 | 1150408.1219 | 1150408.1219 | 1150408.1219 | 1150408.1219 | 1150408.1219 | 0 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 27829826.105 |  | 0 | 0 | -94895.1891 | 17573687.9644 | 1555258.0163 | 1479341.8651 | 1479341.8651 | 1403425.7138 | 1403425.7138 | 1296312.7691 | 734770.4877 | 703573.6943 | 703573.6943 | 703573.6943 | 703573.6943 | 703573.6943 | 703573.6943 | 703573.6943 | 703573.6943 | 703573.6943 | 703573.6943 | 0 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 26624234.4277 |  | 0 | 0 | -104384.708 | 17528138.2736 | 1509708.3256 | 1426200.5592 | 1426200.5592 | 1342692.7928 | 1342692.7928 | 1224868.5536 | 607172.0441 | 572855.5714 | 572855.5714 | 572855.5714 | 572855.5714 | 572855.5714 | 572855.5714 | 572855.5714 | 572855.5714 | 572855.5714 | 572855.5714 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 32261575.3135 |  | 0 | 0 | -94895.1891 | 19576930.7279 | 1778675.2301 | 1702759.0788 | 1702759.0788 | 1626842.9276 | 1626842.9276 | 1519729.9829 | 958187.7015 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 32261575.3135 |  | 0 | 0 | -94895.1891 | 19576930.7279 | 1778675.2301 | 1702759.0788 | 1702759.0788 | 1626842.9276 | 1626842.9276 | 1519729.9829 | 958187.7015 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 32261575.3135 |  | 0 | 0 | -94895.1891 | 19576930.7279 | 1778675.2301 | 1702759.0788 | 1702759.0788 | 1626842.9276 | 1626842.9276 | 1519729.9829 | 958187.7015 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 926990.9081 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | -31196.7934 | 19439688.5607 | 1610236.2695 | 1610236.2695 | 1610236.2695 | 1534320.1182 | 1534320.1182 | 1458403.9669 | 1458403.9669 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 34792612.0063 |  | 0 | 0 | -31196.7934 | 19439688.5607 | 1610236.2695 | 1610236.2695 | 1610236.2695 | 1534320.1182 | 1534320.1182 | 1458403.9669 | 1458403.9669 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 0 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 33840123.9984 |  | 0 | 0 | -34316.4728 | 19380414.6532 | 1547842.6827 | 1547842.6827 | 1547842.6827 | 1464334.9163 | 1464334.9163 | 1380827.1499 | 1380827.1499 | 1297319.3835 | 1297319.3835 | 1297319.3835 | 1297319.3835 | 1297319.3835 | 1297319.3835 | 1297319.3835 | 1297319.3835 | 1297319.3835 | 1297319.3835 | 0 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 35745100.0143 |  | 0 | 0 | -28077.1141 | 19498962.4682 | 1672629.8563 | 1672629.8563 | 1672629.8563 | 1604305.3202 | 1604305.3202 | 1535980.784 | 1535980.784 | 1467656.2479 | 1467656.2479 | 1467656.2479 | 1467656.2479 | 1467656.2479 | 1467656.2479 | 1467656.2479 | 1467656.2479 | 1467656.2479 | 1467656.2479 | 0 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 39224361.2149 |  | 0 | 0 | -31196.7934 | 21442931.3243 | 1833653.4832 | 1833653.4832 | 1833653.4832 | 1757737.332 | 1757737.332 | 1681821.1807 | 1681821.1807 | 1605905.0295 | 1605905.0295 | 1605905.0295 | 1605905.0295 | 1605905.0295 | 1605905.0295 | 1605905.0295 | 1605905.0295 | 1605905.0295 | 1605905.0295 | 0 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | 30360862.7977 |  | 0 | 0 | -31196.7934 | 17436445.7972 | 1386819.0557 | 1386819.0557 | 1386819.0557 | 1310902.9044 | 1310902.9044 | 1234986.7532 | 1234986.7532 | 1159070.6019 | 1159070.6019 | 1159070.6019 | 1159070.6019 | 1159070.6019 | 1159070.6019 | 1159070.6019 | 1159070.6019 | 1159070.6019 | 1159070.6019 | 0 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | 29408374.7898 |  | 0 | 0 | -34316.4728 | 17377171.8897 | 1324425.4689 | 1324425.4689 | 1324425.4689 | 1240917.7025 | 1240917.7025 | 1157409.9361 | 1157409.9361 | 1073902.1697 | 1073902.1697 | 1073902.1697 | 1073902.1697 | 1073902.1697 | 1073902.1697 | 1073902.1697 | 1073902.1697 | 1073902.1697 | 1073902.1697 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 34792612.0063 |  | 0 | 0 | -31196.7934 | 19439688.5607 | 1610236.2695 | 1610236.2695 | 1610236.2695 | 1534320.1182 | 1534320.1182 | 1458403.9669 | 1458403.9669 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 34792612.0063 |  | 0 | 0 | -31196.7934 | 19439688.5607 | 1610236.2695 | 1610236.2695 | 1610236.2695 | 1534320.1182 | 1534320.1182 | 1458403.9669 | 1458403.9669 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 34792612.0063 |  | 0 | 0 | -31196.7934 | 19439688.5607 | 1610236.2695 | 1610236.2695 | 1610236.2695 | 1534320.1182 | 1534320.1182 | 1458403.9669 | 1458403.9669 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 1382487.8157 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 24757236.0843 |  | 0 | 0 | -579303.1232 | 18659712.3234 | 852260.9387 | 852260.9387 | 852260.9387 | 776344.7875 | 776344.7875 | 700428.6362 | 700428.6362 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 22801210.4841 |  | 0 | 0 | -637233.4355 | 18522440.7922 | 714069.8188 | 714069.8188 | 714069.8188 | 630562.0524 | 630562.0524 | 547054.286 | 547054.286 | 463546.5197 | 463546.5197 | 463546.5197 | 463546.5197 | 463546.5197 | 463546.5197 | 463546.5197 | 463546.5197 | 463546.5197 | 463546.5197 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 26713261.6844 |  | 0 | 0 | -521372.8109 | 18796983.8546 | 990452.0586 | 990452.0586 | 990452.0586 | 922127.5225 | 922127.5225 | 853802.9863 | 853802.9863 | 785478.4502 | 785478.4502 | 785478.4502 | 785478.4502 | 785478.4502 | 785478.4502 | 785478.4502 | 785478.4502 | 785478.4502 | 785478.4502 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 29188985.2928 |  | 0 | 0 | -579303.1232 | 20662955.087 | 1075678.1525 | 1075678.1525 | 1075678.1525 | 999762.0012 | 999762.0012 | 923845.85 | 923845.85 | 847929.6987 | 847929.6987 | 847929.6987 | 847929.6987 | 847929.6987 | 847929.6987 | 847929.6987 | 847929.6987 | 847929.6987 | 847929.6987 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 20325486.8757 |  | 0 | 0 | -579303.1232 | 16656469.5599 | 628843.725 | 628843.725 | 628843.725 | 552927.5737 | 552927.5737 | 477011.4224 | 477011.4224 | 401095.2712 | 401095.2712 | 401095.2712 | 401095.2712 | 401095.2712 | 401095.2712 | 401095.2712 | 401095.2712 | 401095.2712 | 401095.2712 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 18369461.2755 |  | 0 | 0 | -637233.4355 | 16519198.0286 | 490652.6051 | 490652.6051 | 490652.6051 | 407144.8387 | 407144.8387 | 323637.0723 | 323637.0723 | 240129.3059 | 240129.3059 | 240129.3059 | 240129.3059 | 240129.3059 | 240129.3059 | 240129.3059 | 240129.3059 | 240129.3059 | 240129.3059 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 24757236.0843 |  | 0 | 0 | -579303.1232 | 18659712.3234 | 852260.9387 | 852260.9387 | 852260.9387 | 776344.7875 | 776344.7875 | 700428.6362 | 700428.6362 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 24757236.0843 |  | 0 | 0 | -579303.1232 | 18659712.3234 | 852260.9387 | 852260.9387 | 852260.9387 | 776344.7875 | 776344.7875 | 700428.6362 | 700428.6362 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 24757236.0843 |  | 0 | 0 | -579303.1232 | 18659712.3234 | 852260.9387 | 852260.9387 | 852260.9387 | 776344.7875 | 776344.7875 | 700428.6362 | 700428.6362 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 624512.4849 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 1 | 0 | 0 | 0 | 1 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None |  | 32.2616 | 34.7926 | 24.7572 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens1 | Capex 10% higher |  | 31.056 | 33.8401 | 22.8012 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens2 | Capex 10% lower |  | 33.4672 | 35.7451 | 26.7133 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens3 | Total benefits 10% higher |  | 36.6933 | 39.2244 | 29.189 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens4 | Total benefits 10% lower |  | 27.8298 | 30.3609 | 20.3255 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens5 | Capex 10% higher & Total benefits 10% lower |  | 26.6242 | 29.4084 | 18.3695 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Workings_risks
Powercor
REFCL BAE compliance
WORKINGS - RISKS
REFCL civil penalty benefits
| Original penalty for non-compliance | 18000000 | per year | Ongoing compliance penalty
| $2,000,000 per point |  |  | $5,500 per day | 2007500 | per year
BAN is a 4 point station, BAS is a 5 point station

## Misc_calcs
Powercor
REFCL BAE compliance
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR | bar: 2021-06-30 to 2025-06-30
| Option | First year | Option included
| Option 2 | 1 | TRUE
| Option 3 | 1 | TRUE
| Option 4 | 1 | TRUE
| Option 5 | Not used | FALSE
| First year | 1
FLAGS | bar: 2021-06-30 to 2025-06-30
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
Powercor
REFCL BAE compliance
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | TRUE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | FALSE |  |  | FALSE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | TRUE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
Powercor
| Reliability in worst-served areas | per MWh | 151432.8174
| Network resilience | per MWh | 24590
| Enabling solar exports | per MWh | 88.3577
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.35181
| Customer value of time - business | per minute customer time | 0.35181
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020