## Cover
Powercor
Regulatory proposal 2026-31
Worst served customers BAN-WND
| Model number: | 3.25
2025-01-31
16

## Summary
Powercor
BAN003-WND024 Tie upgrade
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Install diesel generator microgrid in Trentham township |  | -3.3347 | 8.953 | 5.6184
| Option 3 | Install BESS + diesel generator microgrid in Trentham township |  | -7.4151 | 8.953 | 1.5379
| Option 4 | Install BAN003 to WND024 tie line |  | -1.9036 | 19.6225 | 17.7188
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 4 | Install BAN003 to WND024 tie line |  | 17.7188
PREFERRED OPTION
Preferred Option
Option 4
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 0.55646 | 2.9659 | 0 | 0 | 0 |  | 3.5224
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
| Capex and risk ($M, 2026) |  | Value of expected unserved energy ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 5.6184 | 1.5379 | 17.7188 |  |  | Option 4
| Capex 10% higher |  | 0 | 5.3803 | 1.0112 | 17.5285 |  |  | Option 4
| Capex 10% lower |  | 0 | 5.8564 | 2.0647 | 17.9092 |  |  | Option 4
| Total benefits 10% higher |  | 0 | 6.5137 | 2.4332 | 19.6811 |  |  | Option 4
| Total benefits 10% lower |  | 0 | 4.7231 | 0.64263 | 15.7566 |  |  | Option 4
| Capex 10% higher & Total benefits 10% lower |  | 0 | 4.485 | 0.11591 | 15.5662 |  |  | Option 4
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
Powercor
BAN003-WND024 Tie upgrade
Project
|  | Business: | select > | Powercor
|  | Descripton: |  | BAN003-WND024 Tie upgrade
|  | Date of cost inputs: | select > | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Install diesel generator microgrid in Trentham township
|  | Option 3 |  | Install BESS + diesel generator microgrid in Trentham township
|  | Option 4 |  | Install BAN003 to WND024 tie line
Option 5
|  | Compliance project |  | No
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | BAN weighted average |  |  |  | 44753.327 | 2023 VCR ($/MWh)
|  | Ballarat North |  |  |  | VCR | Proportion
|  | Domestic |  |  |  | 19880 | 36.52%
|  | Commercial |  |  |  | 52200 | 42.35%
|  | Industrial |  |  |  | 74790 | 19.76%
|  | Agricultural |  |  |  | 44400 | 1.366%
|  | Others |  |  |  | 52200 | 0%
Outage tiers
|  | 12<t<24 |  |  |  | 12
|  | >24 |  |  |  | 24
|  | >72 |  |  |  | 72
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 67500 | 2023-12-31 | per MWh
|  | Network resilience |  |  |  | 67129.9906 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 10 | 2023-12-31 | per MWh
|  | Customer value per kWh of storage capacity in local community: |  |  |  | 51130 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.73 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 4.45 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0.28 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0.17 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
Powercor
BAN003-WND024 Tie upgrade
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 79.1016 | 81.0377 | 82.9738 | 84.91 | 86.8461 | 86.2411 | 85.6361 | 85.031 | 84.426 | 83.8209 | 83.2159 | 82.6108 | 82.0058 | 81.4007 | 80.7957 | 80.1906 | 79.5856 | 78.9805 | 78.3755 | 77.7704 | 77.1654 | 76.5603 | 75.9554 | 75.3503 | 74.7453
| Energy at risk value | $/MWh | 44753.327 | 2023-12-31 |  | 3540058.1483 | 3626708.1516 | 3713354.6148 | 3800004.027 | 3886652.6567 | 3859574.9608 | 3832498.8119 | 3805420.9071 | 3778343.0023 | 3751265.0976 | 3724187.1928 | 3697109.288 | 3670031.3832 | 3642953.4784 | 3615875.5737 | 3588797.6689 | 3561719.7641 | 3534641.8593 | 3507563.9546 | 3480486.0498 | 3453408.145 | 3426330.2402 | 3399255.8755 | 3372177.9707 | 3345100.066
| Safety consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 3540058.1483 | 3626708.1516 | 3713354.6148 | 3800004.027 | 3886652.6567 | 3859574.9608 | 3832498.8119 | 3805420.9071 | 3778343.0023 | 3751265.0976 | 3724187.1928 | 3697109.288 | 3670031.3832 | 3642953.4784 | 3615875.5737 | 3588797.6689 | 3561719.7641 | 3534641.8593 | 3507563.9546 | 3480486.0498 | 3453408.145 | 3426330.2402 | 3399255.8755 | 3372177.9707 | 3345100.066
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental reliability in worst-served areas | $/MWh | 22746.673 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (domestic) | $/MWh | 19880 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (commercial) | $/MWh | 52200 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (industrial) | $/customer | 74790 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (agricultural) | $/customer min | 44400 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (others) | $/customer min | 52200 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0.28 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0.17 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
Powercor
BAN003-WND024 Tie upgrade
OPTION 2 | Install diesel generator microgrid in Trentham township
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Diesel generator microgrid |  | 20 | 2023-12-31 | 0 | 0 | 0 | 2834718.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 2834718.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 68.5214 | 68.3881 | 68.1383 | 67.979 | 67.7963 | 67.8758 | 67.9554 | 68.0349 | 68.1145 | 68.194 | 68.2736 | 68.3531 | 68.4327 | 68.5122 | 68.5918 | 68.6713 | 68.7509 | 68.8304 | 68.91 | 68.9895 | 69.0691
| Energy at risk value | $/MWh | 44753.327 | 2023-12-31 | 3540058.1483 | 3540058.1483 | 3540058.1483 | 3540058.1483 | 3066559.6802 | 3060593.5721 | 3049417.5635 | 3042286.5091 | 3034108.7378 | 3037668.9316 | 3041229.1253 | 3044789.3191 | 3048349.5129 | 3051909.7066 | 3055469.9004 | 3059030.0942 | 3062590.2879 | 3066150.4817 | 3069710.6755 | 3073270.8692 | 3076831.063 | 3080391.2567 | 3083950.9826 | 3087511.1764 | 3091071.3702
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 3540058.1483 | 3540058.1483 | 3540058.1483 | 3540058.1483 | 3066559.6802 | 3060593.5721 | 3049417.5635 | 3042286.5091 | 3034108.7378 | 3037668.9316 | 3041229.1253 | 3044789.3191 | 3048349.5129 | 3051909.7066 | 3055469.9004 | 3059030.0942 | 3062590.2879 | 3066150.4817 | 3069710.6755 | 3073270.8692 | 3076831.063 | 3080391.2567 | 3083950.9826 | 3087511.1764 | 3091071.3702
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental reliability in worst-served areas | $/MWh | 22746.673 | MWh | 0 | 0 | 0 | 0 | 2.0775 | 2.063 | 2.0485 | 2.0341 | 2.0196 | 2.0051 | 1.9906 | 1.9762 | 1.9617 | 1.9472 | 1.9327 | 1.9183 | 1.9038 | 1.8893 | 1.8749 | 1.8604 | 1.8459 | 1.8314 | 1.817 | 1.8025 | 1.788
| Incremental network resilience (domestic) | $/MWh | 19880 | MWh | 0 | 0 | 0 | 0 | 0.52958 | 0.52608 | 0.52259 | 0.51909 | 0.5156 | 0.5121 | 0.50861 | 0.50511 | 0.50162 | 0.49812 | 0.49463 | 0.49113 | 0.48764 | 0.48414 | 0.48064 | 0.47715 | 0.47365 | 0.47016 | 0.46666 | 0.46317 | 0.45967
| Incremental network resilience (commercial) | $/MWh | 52200 | MWh | 0 | 0 | 0 | 0 | 0.011463 | 0.011495 | 0.011528 | 0.011561 | 0.011594 | 0.011626 | 0.011659 | 0.011692 | 0.011724 | 0.011757 | 0.01179 | 0.011822 | 0.011855 | 0.011888 | 0.01192 | 0.011953 | 0.011986 | 0.012018 | 0.012051 | 0.012084 | 0.012117
| Incremental network resilience (industrial) | $/MWh | 74790 | customers | 0 | 0 | 0 | 0 | 0.0053494 | 0.0053647 | 0.0053799 | 0.0053952 | 0.0054104 | 0.0054257 | 0.0054409 | 0.0054562 | 0.0054714 | 0.0054867 | 0.0055019 | 0.0055172 | 0.0055324 | 0.0055477 | 0.0055629 | 0.0055782 | 0.0055935 | 0.0056087 | 0.005624 | 0.0056392 | 0.0056545
| Incremental network resilience (agricultural) | $/MWh | 44400 | mins | 0 | 0 | 0 | 0 | 0.00036978 | 0.00037083 | 0.00037188 | 0.00037294 | 0.00037399 | 0.00037505 | 0.0003761 | 0.00037716 | 0.00037821 | 0.00037927 | 0.00038032 | 0.00038137 | 0.00038243 | 0.00038348 | 0.00038454 | 0.00038559 | 0.00038665 | 0.0003877 | 0.00038876 | 0.00038981 | 0.00039086
| Incremental network resilience (others) | $/MWh | 52200 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0.28 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0.17 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 58798.6748 | 58402.8573 | 58007.0626 | 57611.2421 | 57215.4215 | 56819.6009 | 56423.7803 | 56027.9597 | 55632.1391 | 55236.3185 | 54840.4979 | 54444.6773 | 54048.8567 | 53653.0361 | 53257.2155 | 52861.3949 | 52465.5743 | 52069.7537 | 51673.9854 | 51278.1648 | 50882.3442
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 820092.9765 | 798981.3887 | 783081.2484 | 763134.398 | 744234.2645 | 713596.166 | 682958.0674 | 652319.9689 | 621681.8703 | 591043.7718 | 560405.6733 | 529767.5747 | 499129.4762 | 468491.3776 | 437853.2791 | 407215.1806 | 376577.082 | 345938.9835 | 315304.8929 | 284666.7943 | 254028.6958
Capital expenditure
| Diesel generator microgrid |  |  | 2023-12-31 | 0 | 0 | 0 | -2834718.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Diesel generator microgrid |  |  | 2023-12-31 | 0 | 0 | 0 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | -2834718.1175 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Diesel generator microgrid |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000 | -80000
| Risk mitigated |  |  | 2023-12-31 | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 820092.9765 | 798981.3887 | 783081.2484 | 763134.398 | 744234.2645 | 713596.166 | 682958.0674 | 652319.9689 | 621681.8703 | 591043.7718 | 560405.6733 | 529767.5747 | 499129.4762 | 468491.3776 | 437853.2791 | 407215.1806 | 376577.082 | 345938.9835 | 315304.8929 | 284666.7943 | 254028.6958
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 58798.6748 | 58402.8573 | 58007.0626 | 57611.2421 | 57215.4215 | 56819.6009 | 56423.7803 | 56027.9597 | 55632.1391 | 55236.3185 | 54840.4979 | 54444.6773 | 54048.8567 | 53653.0361 | 53257.2155 | 52861.3949 | 52465.5743 | 52069.7537 | 51673.9854 | 51278.1648 | 50882.3442
| Net benefits |  |  | 2023-12-31 | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 599437.8322 | 577930.4269 | 561634.4919 | 541291.8209 | 521995.8668 | 490961.9477 | 459928.0286 | 428894.1094 | 397860.1903 | 366826.2712 | 335792.352 | 304758.4329 | 273724.5138 | 242690.5946 | 211656.6755 | 180622.7564 | 149588.8372 | 118554.9181 | 87525.0592 | 56491.14 | 224911.04
| First capex year |  |  | 4
| First year |  |  | 4
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 599437.8322 | 577930.4269 | 561634.4919 | 541291.8209 | 521995.8668 | 490961.9477 | 459928.0286 | 428894.1094 | 397860.1903 | 366826.2712 | 335792.352 | 304758.4329 | 273724.5138 | 242690.5946 | 211656.6755 | 180622.7564 | 149588.8372 | 118554.9181 | 87525.0592 | 56491.14 | 224911.04
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | -199453.8191 | 0
| Total benefits |  |  |  | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 878891.6513 | 857384.246 | 841088.311 | 820745.6401 | 801449.686 | 770415.7668 | 739381.8477 | 708347.9286 | 677314.0094 | 646280.0903 | 615246.1712 | 584212.252 | 553178.3329 | 522144.4138 | 491110.4946 | 460076.5755 | 429042.6564 | 398008.7372 | 366978.8783 | 335944.9592 | 304911.04
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 579492.4503 | 557985.045 | 541689.11 | 521346.439 | 502050.4849 | 471016.5658 | 439982.6467 | 408948.7275 | 377914.8084 | 346880.8893 | 315846.9701 | 284813.051 | 253779.1319 | 222745.2127 | 191711.2936 | 160677.3745 | 129643.4553 | 98609.5362 | 67579.6773 | 36545.7581 | 224911.04
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 619383.2141 | 597875.8088 | 581579.8738 | 561237.2028 | 541941.2488 | 510907.3296 | 479873.4105 | 448839.4914 | 417805.5722 | 386771.6531 | 355737.734 | 324703.8148 | 293669.8957 | 262635.9766 | 231602.0574 | 200568.1383 | 169534.2191 | 138500.3 | 107470.4411 | 76436.522 | 224911.04
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | 95315.0036 | 190626.1132 | 285940.4665 | 687326.9974 | 663668.8515 | 645743.323 | 623366.3849 | 602140.8354 | 568003.5244 | 533866.2133 | 499728.9023 | 465591.5913 | 431454.2802 | 397316.9692 | 363179.6581 | 329042.3471 | 294905.036 | 260767.725 | 226630.4139 | 192493.1029 | 158355.7918 | 124222.947 | 90085.636 | 255402.144
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | 77985.003 | 155966.8199 | 233951.2908 | 511548.6671 | 492192.0023 | 477525.6608 | 459217.2569 | 441850.8983 | 413920.371 | 385989.8438 | 358059.3166 | 330128.7894 | 302198.2621 | 274267.7349 | 246337.2077 | 218406.6805 | 190476.1533 | 162545.626 | 134615.0988 | 106684.5716 | 78754.0444 | 50827.1713 | 22896.6441 | 194419.936
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | 77985.003 | 155966.8199 | 233951.2908 | 491603.2852 | 472246.6204 | 457580.2789 | 439271.875 | 421905.5163 | 393974.9891 | 366044.4619 | 338113.9347 | 310183.4075 | 282252.8802 | 254322.353 | 226391.8258 | 198461.2986 | 170530.7714 | 142600.2441 | 114669.7169 | 86739.1897 | 58808.6625 | 30881.7894 | 2951.2622 | 194419.936
sens | 0 | 0% | 0% | Option 2sens | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 599437.8322 | 577930.4269 | 561634.4919 | 541291.8209 | 521995.8668 | 490961.9477 | 459928.0286 | 428894.1094 | 397860.1903 | 366826.2712 | 335792.352 | 304758.4329 | 273724.5138 | 242690.5946 | 211656.6755 | 180622.7564 | 149588.8372 | 118554.9181 | 87525.0592 | 56491.14 | 224911.04
sens | 0 | 0% | 0% | Option 2sens | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 599437.8322 | 577930.4269 | 561634.4919 | 541291.8209 | 521995.8668 | 490961.9477 | 459928.0286 | 428894.1094 | 397860.1903 | 366826.2712 | 335792.352 | 304758.4329 | 273724.5138 | 242690.5946 | 211656.6755 | 180622.7564 | 149588.8372 | 118554.9181 | 87525.0592 | 56491.14 | 224911.04
sens | 0 | 0% | 0% | Option 2sens | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 599437.8322 | 577930.4269 | 561634.4919 | 541291.8209 | 521995.8668 | 490961.9477 | 459928.0286 | 428894.1094 | 397860.1903 | 366826.2712 | 335792.352 | 304758.4329 | 273724.5138 | 242690.5946 | 211656.6755 | 180622.7564 | 149588.8372 | 118554.9181 | 87525.0592 | 56491.14 | 224911.04

## Option3
Powercor
BAN003-WND024 Tie upgrade
OPTION 3 | Install BESS + diesel generator microgrid in Trentham township
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Microgrid CAPEX (exc BESS) |  | 20 | 2023-12-31 | 0 | 0 | 0 | 4557799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BESS CAPEX |  | 20 | 2023-12-31 | 0 | 0 | 0 | 1715596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 6273395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000 | 180000
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 68.5214 | 68.3881 | 68.1383 | 67.979 | 67.7963 | 67.8758 | 67.9554 | 68.0349 | 68.1145 | 68.194 | 68.2736 | 68.3531 | 68.4327 | 68.5122 | 68.5918 | 68.6713 | 68.7509 | 68.8304 | 68.91 | 68.9895 | 69.0691
| Energy at risk value | $/MWh | 44753.327 | 2023-12-31 | 3540058.1483 | 3540058.1483 | 3540058.1483 | 3540058.1483 | 3066559.6802 | 3060593.5721 | 3049417.5635 | 3042286.5091 | 3034108.7378 | 3037668.9316 | 3041229.1253 | 3044789.3191 | 3048349.5129 | 3051909.7066 | 3055469.9004 | 3059030.0942 | 3062590.2879 | 3066150.4817 | 3069710.6755 | 3073270.8692 | 3076831.063 | 3080391.2567 | 3083950.9826 | 3087511.1764 | 3091071.3702
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 3540058.1483 | 3540058.1483 | 3540058.1483 | 3540058.1483 | 3066559.6802 | 3060593.5721 | 3049417.5635 | 3042286.5091 | 3034108.7378 | 3037668.9316 | 3041229.1253 | 3044789.3191 | 3048349.5129 | 3051909.7066 | 3055469.9004 | 3059030.0942 | 3062590.2879 | 3066150.4817 | 3069710.6755 | 3073270.8692 | 3076831.063 | 3080391.2567 | 3083950.9826 | 3087511.1764 | 3091071.3702
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental reliability in worst-served areas | $/MWh | 22746.673 | MWh | 0 | 0 | 0 | 0 | 2.0775 | 2.063 | 2.0485 | 2.0341 | 2.0196 | 2.0051 | 1.9906 | 1.9762 | 1.9617 | 1.9472 | 1.9327 | 1.9183 | 1.9038 | 1.8893 | 1.8749 | 1.8604 | 1.8459 | 1.8314 | 1.817 | 1.8025 | 1.788
| Incremental network resilience (domestic) | $/MWh | 19880 | MWh | 0 | 0 | 0 | 0 | 0.52958 | 0.52608 | 0.52259 | 0.51909 | 0.5156 | 0.5121 | 0.50861 | 0.50511 | 0.50162 | 0.49812 | 0.49463 | 0.49113 | 0.48764 | 0.48414 | 0.48064 | 0.47715 | 0.47365 | 0.47016 | 0.46666 | 0.46317 | 0.45967
| Incremental network resilience (commercial) | $/MWh | 52200 | MWh | 0 | 0 | 0 | 0 | 0.011463 | 0.011495 | 0.011528 | 0.011561 | 0.011594 | 0.011626 | 0.011659 | 0.011692 | 0.011724 | 0.011757 | 0.01179 | 0.011822 | 0.011855 | 0.011888 | 0.01192 | 0.011953 | 0.011986 | 0.012018 | 0.012051 | 0.012084 | 0.012117
| Incremental network resilience (industrial) | $/customer | 74790 | customers | 0 | 0 | 0 | 0 | 0.0053494 | 0.0053647 | 0.0053799 | 0.0053952 | 0.0054104 | 0.0054257 | 0.0054409 | 0.0054562 | 0.0054714 | 0.0054867 | 0.0055019 | 0.0055172 | 0.0055324 | 0.0055477 | 0.0055629 | 0.0055782 | 0.0055935 | 0.0056087 | 0.005624 | 0.0056392 | 0.0056545
| Incremental network resilience (agricultural) | $/customer min | 44400 | mins | 0 | 0 | 0 | 0 | 0.00036978 | 0.00037083 | 0.00037188 | 0.00037294 | 0.00037399 | 0.00037505 | 0.0003761 | 0.00037716 | 0.00037821 | 0.00037927 | 0.00038032 | 0.00038137 | 0.00038243 | 0.00038348 | 0.00038454 | 0.00038559 | 0.00038665 | 0.0003877 | 0.00038876 | 0.00038981 | 0.00039086
| Incremental network resilience (others) | $/customer min | 52200 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0.28 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BESS lease | $/customer | 0.17 | customers | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 58798.8448 | 58403.0273 | 58007.2326 | 57611.4121 | 57215.5915 | 56819.7709 | 56423.9503 | 56028.1297 | 55632.3091 | 55236.4885 | 54840.6679 | 54444.8473 | 54049.0267 | 53653.2061 | 53257.3855 | 52861.5649 | 52465.7443 | 52069.9237 | 51674.1554 | 51278.3348 | 50882.5142
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 820092.9765 | 798981.3887 | 783081.2484 | 763134.398 | 744234.2645 | 713596.166 | 682958.0674 | 652319.9689 | 621681.8703 | 591043.7718 | 560405.6733 | 529767.5747 | 499129.4762 | 468491.3776 | 437853.2791 | 407215.1806 | 376577.082 | 345938.9835 | 315304.8929 | 284666.7943 | 254028.6958
Capital expenditure
| Microgrid CAPEX (exc BESS) |  |  | 2023-12-31 | 0 | 0 | 0 | -4557799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BESS CAPEX |  |  | 2023-12-31 | 0 | 0 | 0 | -1715596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Microgrid CAPEX (exc BESS) |  |  | 2023-12-31 | 0 | 0 | 0 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | -4557799 | 0 | 0
| BESS CAPEX |  |  | 2023-12-31 | 0 | 0 | 0 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | -1715596 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Microgrid CAPEX (exc BESS) |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | -320691.6454 | 0
| Annualised capex - BESS CAPEX |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | -120711.1819 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000 | -180000
| Risk mitigated |  |  | 2023-12-31 | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 820092.9765 | 798981.3887 | 783081.2484 | 763134.398 | 744234.2645 | 713596.166 | 682958.0674 | 652319.9689 | 621681.8703 | 591043.7718 | 560405.6733 | 529767.5747 | 499129.4762 | 468491.3776 | 437853.2791 | 407215.1806 | 376577.082 | 345938.9835 | 315304.8929 | 284666.7943 | 254028.6958
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 58798.8448 | 58403.0273 | 58007.2326 | 57611.4121 | 57215.5915 | 56819.7709 | 56423.9503 | 56028.1297 | 55632.3091 | 55236.4885 | 54840.6679 | 54444.8473 | 54049.0267 | 53653.2061 | 53257.3855 | 52861.5649 | 52465.7443 | 52069.9237 | 51674.1554 | 51278.3348 | 50882.5142
| Net benefits |  |  | 2023-12-31 | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 257488.9941 | 235981.5887 | 219685.6537 | 199342.9828 | 180047.0287 | 149013.1096 | 117979.1904 | 86945.2713 | 55911.3521 | 24877.433 | -6156.4861 | -37190.4053 | -68224.3244 | -99258.2435 | -130292.1627 | -161326.0818 | -192360.0009 | -223393.9201 | -254423.779 | -285457.6981 | 124911.21
| First capex year |  |  | 4
| First year |  |  | 4
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 257488.9941 | 235981.5887 | 219685.6537 | 199342.9828 | 180047.0287 | 149013.1096 | 117979.1904 | 86945.2713 | 55911.3521 | 24877.433 | -6156.4861 | -37190.4053 | -68224.3244 | -99258.2435 | -130292.1627 | -161326.0818 | -192360.0009 | -223393.9201 | -254423.779 | -285457.6981 | 124911.21
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | -441402.8273 | 0
| Total benefits |  |  |  | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 878891.8213 | 857384.416 | 841088.481 | 820745.8101 | 801449.856 | 770415.9368 | 739382.0177 | 708348.0986 | 677314.1794 | 646280.2603 | 615246.3412 | 584212.422 | 553178.5029 | 522144.5838 | 491110.6646 | 460076.7455 | 429042.8264 | 398008.9072 | 366979.0483 | 335945.1292 | 304911.21
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 213348.7113 | 191841.306 | 175545.371 | 155202.7 | 135906.746 | 104872.8268 | 73838.9077 | 42804.9886 | 11771.0694 | -19262.8497 | -50296.7688 | -81330.688 | -112364.6071 | -143398.5263 | -174432.4454 | -205466.3645 | -236500.2837 | -267534.2028 | -298564.0617 | -329597.9809 | 124911.21
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 301629.2768 | 280121.8714 | 263825.9365 | 243483.2655 | 224187.3114 | 193153.3923 | 162119.4731 | 131085.554 | 100051.6349 | 69017.7157 | 37983.7966 | 6949.8775 | -24084.0417 | -55117.9608 | -86151.8799 | -117185.7991 | -148219.7182 | -179253.6373 | -210283.4963 | -241317.4154 | 124911.21
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | 95315.0036 | 190626.1132 | 285940.4665 | 345378.1762 | 321720.0303 | 303794.5018 | 281417.5638 | 260192.0143 | 226054.7032 | 191917.3922 | 157780.0811 | 123642.7701 | 89505.459 | 55368.148 | 21230.8369 | -12906.4741 | -47043.7851 | -81181.0962 | -115318.4072 | -149455.7183 | -183593.0293 | -217725.8742 | -251863.1852 | 155402.331
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | 77985.003 | 155966.8199 | 233951.2908 | 169599.8119 | 150243.1471 | 135576.8056 | 117268.4018 | 99902.0431 | 71971.5159 | 44040.9886 | 16110.4614 | -11820.0658 | -39750.593 | -67681.1202 | -95611.6475 | -123542.1747 | -151472.7019 | -179403.2291 | -207333.7563 | -235264.2836 | -263194.8108 | -291121.6838 | -319052.211 | 94420.089
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | 77985.003 | 155966.8199 | 233951.2908 | 125459.5292 | 106102.8644 | 91436.5229 | 73128.119 | 55761.7604 | 27831.2331 | -99.2941 | -28029.8213 | -55960.3485 | -83890.8757 | -111821.403 | -139751.9302 | -167682.4574 | -195612.9846 | -223543.5118 | -251474.0391 | -279404.5663 | -307335.0935 | -335261.9665 | -363192.4938 | 94420.089
sens | 0 | 0% | 0% | Option 3sens | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 257488.9941 | 235981.5887 | 219685.6537 | 199342.9828 | 180047.0287 | 149013.1096 | 117979.1904 | 86945.2713 | 55911.3521 | 24877.433 | -6156.4861 | -37190.4053 | -68224.3244 | -99258.2435 | -130292.1627 | -161326.0818 | -192360.0009 | -223393.9201 | -254423.779 | -285457.6981 | 124911.21
sens | 0 | 0% | 0% | Option 3sens | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 257488.9941 | 235981.5887 | 219685.6537 | 199342.9828 | 180047.0287 | 149013.1096 | 117979.1904 | 86945.2713 | 55911.3521 | 24877.433 | -6156.4861 | -37190.4053 | -68224.3244 | -99258.2435 | -130292.1627 | -161326.0818 | -192360.0009 | -223393.9201 | -254423.779 | -285457.6981 | 124911.21
sens | 0 | 0% | 0% | Option 3sens | 0 | 86650.0033 | 173296.4665 | 259945.8786 | 257488.9941 | 235981.5887 | 219685.6537 | 199342.9828 | 180047.0287 | 149013.1096 | 117979.1904 | 86945.2713 | 55911.3521 | 24877.433 | -6156.4861 | -37190.4053 | -68224.3244 | -99258.2435 | -130292.1627 | -161326.0818 | -192360.0009 | -223393.9201 | -254423.779 | -285457.6981 | 124911.21

## Option4
Powercor
BAN003-WND024 Tie upgrade
OPTION 4 | Install BAN003 to WND024 tie line
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| No change to existing practices |  | 50 | 2023-12-31 | 500000 | 2665000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 500000 | 2665000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 79.1016 | 61.5682 | 63.0391 | 64.5101 | 65.9811 | 65.5214 | 65.0618 | 64.6021 | 64.1424 | 63.6827 | 63.223 | 62.7634 | 62.3037 | 61.844 | 61.3843 | 60.9246 | 60.4649 | 60.0053 | 59.5456 | 59.0859 | 58.6262 | 58.1665 | 57.7069 | 57.2472 | 56.7875
| Energy at risk value | $/MWh | 44753.327 | 2023-12-31 | 3540058.1483 | 2755381.7437 | 2821211.1607 | 2887042.818 | 2952873.8809 | 2932301.6744 | 2911730.6432 | 2891158.2781 | 2870585.9129 | 2850013.5477 | 2829441.1825 | 2808868.8174 | 2788296.4522 | 2767724.087 | 2747151.7218 | 2726579.3567 | 2706006.9915 | 2685434.6263 | 2664862.2611 | 2644289.896 | 2623717.5308 | 2603145.1656 | 2582575.49 | 2562003.1248 | 2541430.7596
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 3540058.1483 | 2755381.7437 | 2821211.1607 | 2887042.818 | 2952873.8809 | 2932301.6744 | 2911730.6432 | 2891158.2781 | 2870585.9129 | 2850013.5477 | 2829441.1825 | 2808868.8174 | 2788296.4522 | 2767724.087 | 2747151.7218 | 2726579.3567 | 2706006.9915 | 2685434.6263 | 2664862.2611 | 2644289.896 | 2623717.5308 | 2603145.1656 | 2582575.49 | 2562003.1248 | 2541430.7596
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental reliability in worst-served areas | $/MWh | 22746.673 | MWh | 0 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927 | 13.5927
| Incremental network resilience (domestic) | $/MWh | 19880 | MWh | 0 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008 | 0.89008
| Incremental network resilience (commercial) | $/MWh | 52200 | MWh | 0 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032 | 1.032
| Incremental network resilience (industrial) | $/customer | 74790 | customers | 0 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161 | 0.48161
| Incremental network resilience (agricultural) | $/customer min | 44400 | mins | 0 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291 | 0.033291
| Incremental network resilience (others) | $/customer min | 52200 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0.28 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0.17 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 871326.4079 | 892143.4542 | 912961.209 | 933778.7758 | 927273.2864 | 920768.1686 | 914262.629 | 907757.0894 | 901251.5498 | 894746.0102 | 888240.4706 | 881734.931 | 875229.3914 | 868723.8518 | 862218.3122 | 855712.7726 | 849207.233 | 842701.6934 | 836196.1538 | 829690.6142 | 823185.0746 | 816680.3855 | 810174.8459 | 803669.3063
Capital expenditure
| No change to existing practices |  |  | 2023-12-31 | -500000 | -2665000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| No change to existing practices |  |  | 2023-12-31 | -500000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000 | -3165000
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - No change to existing practices |  |  | 2023-12-31 | 0 | -21316.8548 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -21316.8548 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908
| Annualised capex |  |  | 2023-12-31 | 0 | -21316.8548 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 871326.4079 | 892143.4542 | 912961.209 | 933778.7758 | 927273.2864 | 920768.1686 | 914262.629 | 907757.0894 | 901251.5498 | 894746.0102 | 888240.4706 | 881734.931 | 875229.3914 | 868723.8518 | 862218.3122 | 855712.7726 | 849207.233 | 842701.6934 | 836196.1538 | 829690.6142 | 823185.0746 | 816680.3855 | 810174.8459 | 803669.3063
| Other benefits value |  |  | 2023-12-31 | 0 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182 | 418252.182
| Net benefits |  |  | 2023-12-31 | 0 | 1268261.7351 | 1175459.9454 | 1196277.7002 | 1217095.267 | 1210589.7776 | 1204084.6599 | 1197579.1203 | 1191073.5807 | 1184568.0411 | 1178062.5015 | 1171556.9619 | 1165051.4223 | 1158545.8827 | 1152040.3431 | 1145534.8034 | 1139029.2638 | 1132523.7242 | 1126018.1846 | 1119512.645 | 1113007.1054 | 1106501.5658 | 1099996.8768 | 1093491.3372 | 1086985.7975
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | 1268261.7351 | 1175459.9454 | 1196277.7002 | 1217095.267 | 1210589.7776 | 1204084.6599 | 1197579.1203 | 1191073.5807 | 1184568.0411 | 1178062.5015 | 1171556.9619 | 1165051.4223 | 1158545.8827 | 1152040.3431 | 1145534.8034 | 1139029.2638 | 1132523.7242 | 1126018.1846 | 1119512.645 | 1113007.1054 | 1106501.5658 | 1099996.8768 | 1093491.3372 | 1086985.7975
| Total annualised capex |  |  |  | 0 | -21316.8548 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908 | -134935.6908
| Total benefits |  |  |  | 0 | 1289578.5899 | 1310395.6362 | 1331213.391 | 1352030.9578 | 1345525.4684 | 1339020.3506 | 1332514.811 | 1326009.2714 | 1319503.7318 | 1312998.1922 | 1306492.6526 | 1299987.113 | 1293481.5734 | 1286976.0338 | 1280470.4942 | 1273964.9546 | 1267459.415 | 1260953.8754 | 1254448.3358 | 1247942.7962 | 1241437.2566 | 1234932.5675 | 1228427.0279 | 1221921.4883
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | 1266130.0496 | 1161966.3763 | 1182784.1311 | 1203601.698 | 1197096.2085 | 1190591.0908 | 1184085.5512 | 1177580.0116 | 1171074.472 | 1164568.9324 | 1158063.3928 | 1151557.8532 | 1145052.3136 | 1138546.774 | 1132041.2344 | 1125535.6948 | 1119030.1552 | 1112524.6156 | 1106019.076 | 1099513.5364 | 1093007.9968 | 1086503.3077 | 1079997.7681 | 1073492.2285
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | 1270393.4206 | 1188953.5145 | 1209771.2693 | 1230588.8361 | 1224083.3467 | 1217578.2289 | 1211072.6893 | 1204567.1497 | 1198061.6101 | 1191556.0705 | 1185050.5309 | 1178544.9913 | 1172039.4517 | 1165533.9121 | 1159028.3725 | 1152522.8329 | 1146017.2933 | 1139511.7537 | 1133006.2141 | 1126500.6745 | 1119995.1349 | 1113490.4458 | 1106984.9062 | 1100479.3666
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | 1397219.5941 | 1306499.509 | 1329399.0393 | 1352298.3628 | 1345142.3244 | 1337986.6949 | 1330830.6014 | 1323674.5078 | 1316518.4142 | 1309362.3207 | 1302206.2271 | 1295050.1336 | 1287894.04 | 1280737.9464 | 1273581.8529 | 1266425.7593 | 1259269.6658 | 1252113.5722 | 1244957.4786 | 1237801.3851 | 1230645.2915 | 1223490.1335 | 1216334.0399 | 1209177.9464
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | 1139303.8761 | 1044420.3818 | 1063156.3611 | 1081892.1712 | 1076037.2308 | 1070182.6248 | 1064327.6392 | 1058472.6535 | 1052617.6679 | 1046762.6822 | 1040907.6966 | 1035052.7109 | 1029197.7253 | 1023342.7397 | 1017487.754 | 1011632.7684 | 1005777.7827 | 999922.7971 | 994067.8115 | 988212.8258 | 982357.8402 | 976503.62 | 970648.6344 | 964793.6487
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | 1137172.1906 | 1030926.8127 | 1049662.792 | 1068398.6022 | 1062543.6617 | 1056689.0557 | 1050834.0701 | 1044979.0844 | 1039124.0988 | 1033269.1132 | 1027414.1275 | 1021559.1419 | 1015704.1562 | 1009849.1706 | 1003994.1849 | 998139.1993 | 992284.2137 | 986429.228 | 980574.2424 | 974719.2567 | 968864.2711 | 963010.0509 | 957155.0653 | 951300.0796
sens | 0 | 0% | 0% | Option 4sens | 0 | 1268261.7351 | 1175459.9454 | 1196277.7002 | 1217095.267 | 1210589.7776 | 1204084.6599 | 1197579.1203 | 1191073.5807 | 1184568.0411 | 1178062.5015 | 1171556.9619 | 1165051.4223 | 1158545.8827 | 1152040.3431 | 1145534.8034 | 1139029.2638 | 1132523.7242 | 1126018.1846 | 1119512.645 | 1113007.1054 | 1106501.5658 | 1099996.8768 | 1093491.3372 | 1086985.7975
sens | 0 | 0% | 0% | Option 4sens | 0 | 1268261.7351 | 1175459.9454 | 1196277.7002 | 1217095.267 | 1210589.7776 | 1204084.6599 | 1197579.1203 | 1191073.5807 | 1184568.0411 | 1178062.5015 | 1171556.9619 | 1165051.4223 | 1158545.8827 | 1152040.3431 | 1145534.8034 | 1139029.2638 | 1132523.7242 | 1126018.1846 | 1119512.645 | 1113007.1054 | 1106501.5658 | 1099996.8768 | 1093491.3372 | 1086985.7975
sens | 0 | 0% | 0% | Option 4sens | 0 | 1268261.7351 | 1175459.9454 | 1196277.7002 | 1217095.267 | 1210589.7776 | 1204084.6599 | 1197579.1203 | 1191073.5807 | 1184568.0411 | 1178062.5015 | 1171556.9619 | 1165051.4223 | 1158545.8827 | 1152040.3431 | 1145534.8034 | 1139029.2638 | 1132523.7242 | 1126018.1846 | 1119512.645 | 1113007.1054 | 1106501.5658 | 1099996.8768 | 1093491.3372 | 1086985.7975

## Option5
Powercor
BAN003-WND024 Tie upgrade
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 44753.327 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental reliability in worst-served areas | $/MWh | 22746.673 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (domestic) | $/MWh | 19880 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (commercial) | $/MWh | 52200 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (industrial) | $/customer | 74790 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (agricultural) | $/customer min | 44400 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience (others) | $/customer min | 52200 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0.28 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0.17 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
Powercor
BAN003-WND024 Tie upgrade
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 68175628.0418 | 2026-06-30 |  | 3939775.4823 | 4036209.3668 | 4132639.3115 | 4229072.538 | 4325504.8939 | 4295369.7837 | 4265236.3951 | 4235101.0525 | 4204965.7098 | 4174830.3671 | 4144695.0245 | 4114559.6818 | 4084424.3391 | 4054288.9965 | 4024153.6538 | 3994018.3111 | 3963882.9685 | 3933747.6258 | 3903612.2832 | 3873476.9405 | 3843341.5978 | 3813206.2552 | 3783074.8523 | 3752939.5096 | 3722804.1669
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 59437698.2007 | 2026-06-30 |  | 3939775.4823 | 4036209.3668 | 4132639.3115 | 4229072.538 | 4325504.8939 | 4295369.7837 | 4265236.3951 | 4235101.0525 | 4204965.7098 | 4174830.3671 | 4144695.0245 | 4114559.6818 | 4084424.3391 | 4054288.9965 | 4024153.6538 | 3994018.3111 | 3963882.9685 | 3933747.6258 | 3903612.2832 | 3873476.9405 | 3843341.5978 | 3813206.2552 | 3783074.8523 | 3752939.5096 | 3722804.1669
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 59076771.0107 | 2026-06-30 |  | 3939775.4823 | 3939775.4823 | 3939775.4823 | 3939775.4823 | 3412813.0491 | 3406173.2919 | 3393735.3706 | 3385799.13 | 3376697.9849 | 3380660.1696 | 3384622.3543 | 3388584.5389 | 3392546.7236 | 3396508.9082 | 3400471.0929 | 3404433.2776 | 3408395.4622 | 3412357.6469 | 3416319.8316 | 3420282.0162 | 3424244.2009 | 3428206.3855 | 3432168.0495 | 3436130.2342 | 3440092.4188
Option 2 | Capital expenditure | Option 2Capital expenditure | -2796917.9917 | 2026-06-30 |  | 0 | 0 | 0 | -3154793.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 51154310.8367 | 2026-06-30 |  | 3939775.4823 | 3939775.4823 | 3939775.4823 | 3939775.4823 | 3412813.0491 | 3406173.2919 | 3393735.3706 | 3385799.13 | 3376697.9849 | 3380660.1696 | 3384622.3543 | 3388584.5389 | 3392546.7236 | 3396508.9082 | 3400471.0929 | 3404433.2776 | 3408395.4622 | 3412357.6469 | 3416319.8316 | 3420282.0162 | 0 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -2380051.5772 | 2026-06-30 |  | 0 | 0 | 0 | 0 | -221974.6777 | -221974.6777 | -221974.6777 | -221974.6777 | -221974.6777 | -221974.6777 | -221974.6777 | -221974.6777 | -221974.6777 | -221974.6777 | -221974.6777 | -221974.6777 | -221974.6777 | -221974.6777 | -221974.6777 | -221974.6777 | 0 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | -954627.6276 | 2026-06-30 |  | 0 | 0 | 0 | 0 | -89033.0117 | -89033.0117 | -89033.0117 | -89033.0117 | -89033.0117 | -89033.0117 | -89033.0117 | -89033.0117 | -89033.0117 | -89033.0117 | -89033.0117 | -89033.0117 | -89033.0117 | -89033.0117 | -89033.0117 | -89033.0117 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 8283387.364 | 2026-06-30 |  | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 912691.8448 | 889196.4917 | 871501.0245 | 849301.9225 | 828267.7249 | 794170.1975 | 760072.6702 | 725975.1429 | 691877.6156 | 657780.0882 | 623682.5609 | 589585.0336 | 555487.5063 | 521389.9789 | 487292.4516 | 453194.9243 | 0 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 669646.7663 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 65437.7888 | 64997.2785 | 64556.7936 | 64116.2799 | 63675.7661 | 63235.2524 | 62794.7386 | 62354.2249 | 61913.7111 | 61473.1974 | 61032.6836 | 60592.1699 | 60151.6562 | 59711.1424 | 59270.6287 | 58830.1149 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 667121.9442 | 643186.0808 | 625050.1287 | 602410.5129 | 580935.8016 | 546397.7605 | 511859.7194 | 477321.6784 | 442783.6373 | 408245.5962 | 373707.5552 | 339169.5141 | 304631.473 | 270093.4319 | 235555.3909 | 201017.3498 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 5618354.9254 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -3334679.2048 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 8953034.1302 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 59076771.0107 | 2026-06-30 |  | 3939775.4823 | 3939775.4823 | 3939775.4823 | 3939775.4823 | 3412813.0491 | 3406173.2919 | 3393735.3706 | 3385799.13 | 3376697.9849 | 3380660.1696 | 3384622.3543 | 3388584.5389 | 3392546.7236 | 3396508.9082 | 3400471.0929 | 3404433.2776 | 3408395.4622 | 3412357.6469 | 3416319.8316 | 3420282.0162 | 3424244.2009 | 3428206.3855 | 3432168.0495 | 3436130.2342 | 3440092.4188
Option 3 | Capital expenditure | Option 3Capital expenditure | -6189741.1372 | 2026-06-30 |  | 0 | 0 | 0 | -6981740.6315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 51154310.8367 | 2026-06-30 |  | 3939775.4823 | 3939775.4823 | 3939775.4823 | 3939775.4823 | 3412813.0491 | 3406173.2919 | 3393735.3706 | 3385799.13 | 3376697.9849 | 3380660.1696 | 3384622.3543 | 3388584.5389 | 3392546.7236 | 3396508.9082 | 3400471.0929 | 3404433.2776 | 3408395.4622 | 3412357.6469 | 3416319.8316 | 3420282.0162 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -5267191.673 | 2026-06-30 |  | 0 | 0 | 0 | 0 | -491242.7886 | -491242.7886 | -491242.7886 | -491242.7886 | -491242.7886 | -491242.7886 | -491242.7886 | -491242.7886 | -491242.7886 | -491242.7886 | -491242.7886 | -491242.7886 | -491242.7886 | -491242.7886 | -491242.7886 | -491242.7886 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | -2147912.1622 | 2026-06-30 |  | 0 | 0 | 0 | 0 | -200324.2764 | -200324.2764 | -200324.2764 | -200324.2764 | -200324.2764 | -200324.2764 | -200324.2764 | -200324.2764 | -200324.2764 | -200324.2764 | -200324.2764 | -200324.2764 | -200324.2764 | -200324.2764 | -200324.2764 | -200324.2764 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 8283387.364 | 2026-06-30 |  | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 912691.8448 | 889196.4917 | 871501.0245 | 849301.9225 | 828267.7249 | 794170.1975 | 760072.6702 | 725975.1429 | 691877.6156 | 657780.0882 | 623682.5609 | 589585.0336 | 555487.5063 | 521389.9789 | 487292.4516 | 453194.9243 | 0 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 669648.7948 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 65437.978 | 64997.4677 | 64556.9828 | 64116.4691 | 63675.9553 | 63235.4416 | 62794.9278 | 62354.4141 | 61913.9003 | 61473.3866 | 61032.8728 | 60592.3591 | 60151.8453 | 59711.3316 | 59270.8179 | 58830.3041 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 286562.7578 | 262626.8944 | 244490.9423 | 221851.3265 | 200376.6152 | 165838.5741 | 131300.533 | 96762.492 | 62224.4509 | 27686.4098 | -6851.6313 | -41389.6723 | -75927.7134 | -110465.7545 | -145003.7955 | -179541.8366 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | 1537932.3236 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -7415103.8352 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 8953036.1588 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 52726649.3731 | 2026-06-30 |  | 3939775.4823 | 3066499.1883 | 3139761.5789 | 3213026.4629 | 3286290.6853 | 3263395.6166 | 3240501.8558 | 3217606.6105 | 3194711.3651 | 3171816.1197 | 3148920.8743 | 3126025.629 | 3103130.3836 | 3080235.1382 | 3057339.8929 | 3034444.6475 | 3011549.4021 | 2988654.1568 | 2965758.9114 | 2942863.666 | 2919968.4206 | 2897073.1753 | 2874180.9231 | 2851285.6778 | 2828390.4324
Option 4 | Capital expenditure | Option 4Capital expenditure | -3363713.2436 | 2026-06-30 |  | -556456.3232 | -2965912.2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 46088030.7261 | 2026-06-30 |  | 3939775.4823 | 3066499.1883 | 3139761.5789 | 3213026.4629 | 3286290.6853 | 3263395.6166 | 3240501.8558 | 3217606.6105 | 3194711.3651 | 3171816.1197 | 3148920.8743 | 3126025.629 | 3103130.3836 | 3080235.1382 | 3057339.8929 | 3034444.6475 | 3011549.4021 | 2988654.1568 | 2965758.9114 | 2942863.666 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | -1903629.8769 | 2026-06-30 |  | 0 | -23723.7973 | -150171.6367 | -150171.6367 | -150171.6367 | -150171.6367 | -150171.6367 | -150171.6367 | -150171.6367 | -150171.6367 | -150171.6367 | -150171.6367 | -150171.6367 | -150171.6367 | -150171.6367 | -150171.6367 | -150171.6367 | -150171.6367 | -150171.6367 | -150171.6367 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 13349667.4746 | 2026-06-30 |  | 0 | 969710.1785 | 992877.7326 | 1016046.0752 | 1039214.2085 | 1031974.1671 | 1024734.5393 | 1017494.442 | 1010254.3447 | 1003014.2474 | 995774.1501 | 988534.0528 | 981293.9555 | 974053.8582 | 966813.7609 | 959573.6636 | 952333.5664 | 945093.4691 | 937853.3718 | 930613.2745 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 6272799.7353 | 2026-06-30 |  | 0 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 465478.1427 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | 1411464.5239 | 1308184.2386 | 1331352.5812 | 1354520.7146 | 1347280.6731 | 1340041.0453 | 1332800.948 | 1325560.8507 | 1318320.7534 | 1311080.6561 | 1303840.5588 | 1296600.4616 | 1289360.3643 | 1282120.267 | 1274880.1697 | 1267640.0724 | 1260399.9751 | 1253159.8778 | 1245919.7805 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 17718837.333 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | -1903629.8769 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 19622467.2098 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 4 | Annualised capex | -1 |  |  | Option 4 annualised capex | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0.15017 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 3.9398 | 4.0362 | 4.1326 | 4.2291 | 4.3255 | 4.2954 | 4.2652 | 4.2351 | 4.205 | 4.1748 | 4.1447 | 4.1146 | 4.0844 | 4.0543 | 4.0242 | 3.994 | 3.9639 | 3.9337 | 3.9036 | 3.8735 | 3.8433 | 3.8132 | 3.7831 | 3.7529 | 3.7228
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 86.8461 |  |  | Energy at risk energy at risk (weighted) | 79.1016 | 81.0377 | 82.9738 | 84.91 | 86.8461 | 86.2411 | 85.6361 | 85.031 | 84.426 | 83.8209 | 83.2159 | 82.6108 | 82.0058 | 81.4007 | 80.7957 | 80.1906 | 79.5856 | 78.9805 | 78.3755 | 77.7704 | 77.1654 | 76.5603 | 75.9554 | 75.3503 | 74.7453
Option 1 (base case) | Energy at risk value | 3.8867 |  |  | Option 1 (base case) risk cost | 3.5401 | 3.6267 | 3.7134 | 3.8 | 3.8867 | 3.8596 | 3.8325 | 3.8054 | 3.7783 | 3.7513 | 3.7242 | 3.6971 | 3.67 | 3.643 | 3.6159 | 3.5888 | 3.5617 | 3.5346 | 3.5076 | 3.4805 | 3.4534 | 3.4263 | 3.3993 | 3.3722 | 3.3451

## Sensitivity_calcs
Powercor
BAN003-WND024 Tie upgrade
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
[7 empty] | 46203 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 235555.3909 | 201017.3498 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 5618354.9254 |  | 0 | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 667121.9442 | 643186.0808 | 625050.1287 | 602410.5129 | 580935.8016 | 546397.7605 | 511859.7194 | 477321.6784 | 442783.6373 | 408245.5962 | 373707.5552 | 339169.5141 | 304631.473 | 270093.4319 | 235555.3909 | 201017.3498 | 0 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 5380349.7677 |  | 0 | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 644924.4765 | 620988.6131 | 602852.6609 | 580213.0452 | 558738.3338 | 524200.2928 | 489662.2517 | 455124.2106 | 420586.1695 | 386048.1285 | 351510.0874 | 316972.0463 | 282434.0052 | 247895.9642 | 213357.9231 | 178819.882 | 0 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 5856360.0831 |  | 0 | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 689319.412 | 665383.5486 | 647247.5965 | 624607.9807 | 603133.2694 | 568595.2283 | 534057.1872 | 499519.1461 | 464981.1051 | 430443.064 | 395905.0229 | 361366.9819 | 326828.9408 | 292290.8997 | 257752.8586 | 223214.8176 | 0 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 6513658.3385 |  | 0 | 0 | 106077.2729 | 212150.2121 | 318226.7613 | 764934.9076 | 738605.4578 | 718655.9105 | 693752.3332 | 670130.1507 | 632138.3055 | 594146.4603 | 556154.6152 | 518162.77 | 480170.9248 | 442179.0796 | 404187.2344 | 366195.3893 | 328203.5441 | 290211.6989 | 252219.8537 | 0 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 4723051.5124 |  | 0 | 0 | 86790.496 | 173577.4463 | 260367.3502 | 569308.9809 | 547766.7038 | 531444.3469 | 511068.6927 | 491741.4525 | 460657.2155 | 429572.9786 | 398488.7416 | 367404.5046 | 336320.2677 | 305236.0307 | 274151.7937 | 243067.5568 | 211983.3198 | 180899.0828 | 149814.8459 | 0 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 4485046.3547 |  | 0 | 0 | 86790.496 | 173577.4463 | 260367.3502 | 547111.5131 | 525569.236 | 509246.8791 | 488871.2249 | 469543.9847 | 438459.7478 | 407375.5108 | 376291.2738 | 345207.0369 | 314122.7999 | 283038.5629 | 251954.326 | 220870.089 | 189785.852 | 158701.6151 | 127617.3781 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 5618354.9254 |  | 0 | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 667121.9442 | 643186.0808 | 625050.1287 | 602410.5129 | 580935.8016 | 546397.7605 | 511859.7194 | 477321.6784 | 442783.6373 | 408245.5962 | 373707.5552 | 339169.5141 | 304631.473 | 270093.4319 | 235555.3909 | 201017.3498 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 5618354.9254 |  | 0 | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 667121.9442 | 643186.0808 | 625050.1287 | 602410.5129 | 580935.8016 | 546397.7605 | 511859.7194 | 477321.6784 | 442783.6373 | 408245.5962 | 373707.5552 | 339169.5141 | 304631.473 | 270093.4319 | 235555.3909 | 201017.3498 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 5618354.9254 |  | 0 | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 667121.9442 | 643186.0808 | 625050.1287 | 602410.5129 | 580935.8016 | 546397.7605 | 511859.7194 | 477321.6784 | 442783.6373 | 408245.5962 | 373707.5552 | 339169.5141 | 304631.473 | 270093.4319 | 235555.3909 | 201017.3498 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 286562.7578 | 262626.8944 | 244490.9423 | 221851.3265 | 200376.6152 | 165838.5741 | 131300.533 | 96762.492 | 62224.4509 | 27686.4098 | -6851.6313 | -41389.6723 | -75927.7134 | -110465.7545 | -145003.7955 | -179541.8366 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 1537932.3236 |  | 0 | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 286562.7578 | 262626.8944 | 244490.9423 | 221851.3265 | 200376.6152 | 165838.5741 | 131300.533 | 96762.492 | 62224.4509 | 27686.4098 | -6851.6313 | -41389.6723 | -75927.7134 | -110465.7545 | -145003.7955 | -179541.8366 | 0 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 1011213.1563 |  | 0 | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 237438.4789 | 213502.6155 | 195366.6634 | 172727.0476 | 151252.3363 | 116714.2952 | 82176.2542 | 47638.2131 | 13100.172 | -21437.8691 | -55975.9101 | -90513.9512 | -125051.9923 | -159590.0333 | -194128.0744 | -228666.1155 | 0 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 2064651.4909 |  | 0 | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 335687.0367 | 311751.1733 | 293615.2211 | 270975.6054 | 249500.894 | 214962.853 | 180424.8119 | 145886.7708 | 111348.7298 | 76810.6887 | 42272.6476 | 7734.6065 | -26803.4345 | -61341.4756 | -95879.5167 | -130417.5578 | 0 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 2433235.9395 |  | 0 | 0 | 106077.2729 | 212150.2121 | 318226.7613 | 384375.7401 | 358046.2903 | 338096.743 | 313193.1657 | 289570.9832 | 251579.138 | 213587.2928 | 175595.4477 | 137603.6025 | 99611.7573 | 61619.9121 | 23628.0669 | -14363.7782 | -52355.6234 | -90347.4686 | -128339.3138 | 0 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | 642628.7077 |  | 0 | 0 | 86790.496 | 173577.4463 | 260367.3502 | 188749.7755 | 167207.4985 | 150885.1415 | 130509.4874 | 111182.2472 | 80098.0102 | 49013.7732 | 17929.5363 | -13154.7007 | -44238.9377 | -75323.1746 | -106407.4116 | -137491.6486 | -168575.8855 | -199660.1225 | -230744.3595 | 0 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | 115909.5404 |  | 0 | 0 | 86790.496 | 173577.4463 | 260367.3502 | 139625.4967 | 118083.2196 | 101760.8627 | 81385.2085 | 62057.9683 | 30973.7313 | -110.5056 | -31194.7426 | -62278.9796 | -93363.2165 | -124447.4535 | -155531.6905 | -186615.9274 | -217700.1644 | -248784.4014 | -279868.6383 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 1537932.3236 |  | 0 | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 286562.7578 | 262626.8944 | 244490.9423 | 221851.3265 | 200376.6152 | 165838.5741 | 131300.533 | 96762.492 | 62224.4509 | 27686.4098 | -6851.6313 | -41389.6723 | -75927.7134 | -110465.7545 | -145003.7955 | -179541.8366 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 1537932.3236 |  | 0 | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 286562.7578 | 262626.8944 | 244490.9423 | 221851.3265 | 200376.6152 | 165838.5741 | 131300.533 | 96762.492 | 62224.4509 | 27686.4098 | -6851.6313 | -41389.6723 | -75927.7134 | -110465.7545 | -145003.7955 | -179541.8366 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 1537932.3236 |  | 0 | 0 | 96433.8845 | 192863.8292 | 289297.0557 | 286562.7578 | 262626.8944 | 244490.9423 | 221851.3265 | 200376.6152 | 165838.5741 | 131300.533 | 96762.492 | 62224.4509 | 27686.4098 | -6851.6313 | -41389.6723 | -75927.7134 | -110465.7545 | -145003.7955 | -179541.8366 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 17718837.333 |  | 0 | 0 | 1411464.5239 | 1308184.2386 | 1331352.5812 | 1354520.7146 | 1347280.6731 | 1340041.0453 | 1332800.948 | 1325560.8507 | 1318320.7534 | 1311080.6561 | 1303840.5588 | 1296600.4616 | 1289360.3643 | 1282120.267 | 1274880.1697 | 1267640.0724 | 1260399.9751 | 1253159.8778 | 1245919.7805 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 17528474.3453 |  | 0 | 0 | 1409092.1442 | 1293167.0749 | 1316335.4175 | 1339503.5509 | 1332263.5095 | 1325023.8816 | 1317783.7843 | 1310543.6871 | 1303303.5898 | 1296063.4925 | 1288823.3952 | 1281583.2979 | 1274343.2006 | 1267103.1033 | 1259863.006 | 1252622.9087 | 1245382.8114 | 1238142.7141 | 1230902.6168 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 17909200.3207 |  | 0 | 0 | 1413836.9037 | 1323201.4023 | 1346369.7449 | 1369537.8782 | 1362297.8368 | 1355058.209 | 1347818.1117 | 1340578.0144 | 1333337.9171 | 1326097.8198 | 1318857.7225 | 1311617.6252 | 1304377.5279 | 1297137.4306 | 1289897.3333 | 1282657.236 | 1275417.1388 | 1268177.0415 | 1260936.9442 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 19681084.054 |  | 0 | 0 | 1554983.3561 | 1454019.8261 | 1479505.003 | 1504989.9497 | 1497025.9041 | 1489062.3135 | 1481098.2065 | 1473134.0995 | 1465169.9924 | 1457205.8854 | 1449241.7784 | 1441277.6714 | 1433313.5644 | 1425349.4573 | 1417385.3503 | 1409421.2433 | 1401457.1363 | 1393493.0292 | 1385528.9222 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 15756590.612 |  | 0 | 0 | 1267945.6918 | 1162348.6511 | 1183200.1594 | 1204051.4794 | 1197535.4421 | 1191019.7771 | 1184503.6895 | 1177987.602 | 1171471.5144 | 1164955.4269 | 1158439.3393 | 1151923.2517 | 1145407.1642 | 1138891.0766 | 1132374.989 | 1125858.9015 | 1119342.8139 | 1112826.7263 | 1106310.6388 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 15566227.6243 |  | 0 | 0 | 1265573.3121 | 1147331.4874 | 1168182.9957 | 1189034.3158 | 1182518.2785 | 1176002.6134 | 1169486.5259 | 1162970.4383 | 1156454.3507 | 1149938.2632 | 1143422.1756 | 1136906.0881 | 1130390.0005 | 1123873.9129 | 1117357.8254 | 1110841.7378 | 1104325.6502 | 1097809.5627 | 1091293.4751 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 17718837.333 |  | 0 | 0 | 1411464.5239 | 1308184.2386 | 1331352.5812 | 1354520.7146 | 1347280.6731 | 1340041.0453 | 1332800.948 | 1325560.8507 | 1318320.7534 | 1311080.6561 | 1303840.5588 | 1296600.4616 | 1289360.3643 | 1282120.267 | 1274880.1697 | 1267640.0724 | 1260399.9751 | 1253159.8778 | 1245919.7805 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 17718837.333 |  | 0 | 0 | 1411464.5239 | 1308184.2386 | 1331352.5812 | 1354520.7146 | 1347280.6731 | 1340041.0453 | 1332800.948 | 1325560.8507 | 1318320.7534 | 1311080.6561 | 1303840.5588 | 1296600.4616 | 1289360.3643 | 1282120.267 | 1274880.1697 | 1267640.0724 | 1260399.9751 | 1253159.8778 | 1245919.7805 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 17718837.333 |  | 0 | 0 | 1411464.5239 | 1308184.2386 | 1331352.5812 | 1354520.7146 | 1347280.6731 | 1340041.0453 | 1332800.948 | 1325560.8507 | 1318320.7534 | 1311080.6561 | 1303840.5588 | 1296600.4616 | 1289360.3643 | 1282120.267 | 1274880.1697 | 1267640.0724 | 1260399.9751 | 1253159.8778 | 1245919.7805 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 0 | 1 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 5.6184 | 1.5379 | 17.7188 |  |  | 2026-27: #NAME?; 2028-29: Option 4
sens1 | Capex 10% higher | 0 | 5.3803 | 1.0112 | 17.5285 |  |  | 2026-27: #NAME?; 2028-29: Option 4
sens2 | Capex 10% lower | 0 | 5.8564 | 2.0647 | 17.9092 |  |  | 2026-27: #NAME?; 2028-29: Option 4
sens3 | Total benefits 10% higher | 0 | 6.5137 | 2.4332 | 19.6811 |  |  | 2026-27: #NAME?; 2028-29: Option 4
sens4 | Total benefits 10% lower | 0 | 4.7231 | 0.64263 | 15.7566 |  |  | 2026-27: #NAME?; 2028-29: Option 4
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 4.485 | 0.11591 | 15.5662 |  |  | 2026-27: #NAME?; 2028-29: Option 4
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Workings_costs
Powercor
BAN003-WND024 Tie upgrade
WORKINGS - COSTS
1. Scope of Works
It is proposed to install a tie line between BAN003 and WND024 feeder to allow for the transfer of customers between the two feeders. The transfer will be completed using remote controlled switch equipment on the two feeders. Works will include the installation of 3km of new overhead HV, 5.2km of upgrades to existing HV overhead lines, the installation of one voltage regulator and the installation of 3 remote controllable switch devices.
· Install new HV OH line to link BAN003 and WND024. Lyonville Pole 181A to Trentham P258A, approximately - 3km.
· Upgrade existing OH line Lyonville Pole 166 to Pole 184, approximately - 3.7km.
· Upgrade existing OH line Trentham Pole 244 to Trentham Pole 262 approximately - 1.5km.
· Upgrade existing HV UG cable Lyonville Pole 124 to Pole 125A – approximately 300 metres.
· Install one voltage regulator on WND024 near Trentham Pole 182.
· Replace RCSW Trentham P215 S# 26444 with NOJA ACR
· New NOJA ACR on open point between BAN003 and WND024.
· New NOJA at Lyonville Pole 136 SW# 65072.
2. Cost Build Up
|  |  | Volume | Cost per Unit | Indicative Cost
|  | New Line - km | 3 | 297000 | 891000
|  | New U/G - km | 0.3 | 1870000 | 561000
|  | Reconductor Line - km | 5.2 | 179300 | 932360
|  | No. remote Sw |  | 93500 | 0
|  | No. Remote ACR's | 3 | 132000 | 396000
|  | No. Regulator | 1 | 385000 | 385000
|  | Total |  |  | 3165360
Capex profile
|  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31
|  | 500000 | 2665000 | 0 | 0 | 0

## Workings_risks
Powercor
BAN003-WND024 Tie upgrade
WORKINGS - RISKS
1. Worst Served Customer History
Worst-served customers are often those located in isolated pockets of the network, and towards the end of long radial rural lines, where no alternate back feed supply is available. We have identified customers who are consistently among our worst served, experiencing high numbers of interruptions and extended outage durations.
Worst served customers are defined as those experiencing 8 outages or more, and 700 minutes (~12 hours) off supply on average p.a. over a three-year period. This is roughly 3 times more than the typical rural customer. The thresholds used to identify worst served customers includeds the impacts of MED’s.
Note: the GSL level for reliability is approximately 9 outages and 18 hours – a high bar, meaning many worst-served customers are often not eligible to receive compensation through the GSL scheme
| Thresholds | Rural Short | Rural Long
| SAIFI | 8 | 8
| SAIDI | 700 | 700
All data is averaged over 5 Years.
Customers In Benefit Area
| Feeder | Feeder Category | No of NMI's | 5 Yr Avg SAIFI | 5 Yr Avg SAIDI | 5 Yr Avg Cust Int | 5 Yr Avg CMOS | Avg CAIDI | Energy Not Supplied |  | Total Energy Not Supplied
| BAN003 | Rural Long | 1185 | 11.0356 | 1754.6577 | 13077.2 | 2079269.4 | 158.9996 | 49.5762 | 149.6089 | 79.1016
| WND024 | Rural Long | 933 | 6.2009 | 1497.5113 | 5785.4 | 1397178 | 241.5007 | 29.5254 | 134.9948
All WSC Outages
| Feeder | Feeder Category | No of NMI's | 5 Yr Avg SAIFI | 5 Yr Avg SAIDI | 5 Yr Avg Cust Int | 5 Yr Avg CMOS | Avg CAIDI | Energy Not Supplied
| BAN003 | Rural Long | 3966 | 9.8488 | 1285.2088 | 39060.2 | 5097138.2 | 130.4944 | 130.367 | 149.6089
| WND024 | Rural Long | 2451 | 6.4734 | 1652.237 | 15866.4 | 4049632.8 | 255.2332 | 84.4391 | 134.9948
Resilience Outages > 12 Hrs
| Feeder | Feeder Category | No of NMI's |  |  | 5 Yr Avg Cust Int | 5 Yr Avg CMOS |  | Energy Not Supplied
| BAN003 | Rural Long | 736 |  |  | 1644 | 1046169 |  | 18.7163
| WND024 | Rural Long | 489 |  |  | 790 | 1933374 |  | 31.752
Microgrid energy at risk
[7 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
| Solar generation demand modifier | 0% | hours
| Network average outage duration due to bushfire | 25.1
hours
| 5 year average historical outages (hours/annum, total) | 28.86 | MW
| Microgrid average daily demand (MW) | 0.282 | MW
| Solar corrected average daily demand (MW) | 0.282
| Wind escalation | [5 empty] | 1 | 1.0245 | 1.049 | 1.0734 | 1.0979 | 1.0903 | 1.0826 | 1.075 | 1.0673 | 1.0597 | 1.052 | 1.0444 | 1.0367 | 1.0291 | 1.0214 | 1.0138 | 1.0061 | 0.99847 | 0.99082 | 0.98317 | 0.97552 | 0.96787 | 0.96023 | 0.95258 | 0.94493
| Annual likelihood that fire will cause outage | [5 empty] | 0.015692 | 0.015768 | 0.015845 | 0.015921 | 0.015998 | 0.016043 | 0.016089 | 0.016135 | 0.01618 | 0.016226 | 0.016272 | 0.016317 | 0.016363 | 0.016408 | 0.016454 | 0.0165 | 0.016545 | 0.016591 | 0.016636 | 0.016682 | 0.016728 | 0.016773 | 0.016819 | 0.016865 | 0.01691
| Ratio to 2022 | [5 empty] | 1.0787 | 1.0974 | 1.1228 | 1.152 | 1.1693 | 1.1922 | 1.2284 | 1.255 | 1.2846 | 1.2846 | 1.2846 | 1.2846 | 1.2846 | 1.2846 | 1.2846 | 1.2846 | 1.2846 | 1.2846 | 1.2846 | 1.2846 | 1.2846 | 1.2846 | 1.2846 | 1.2846 | 1.2846
| Option 1 (base case) |  | MWh |  |  |  | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016 | 79.1016
| Reduction due to microgrid |  | MWh |  |  |  | 8.8992 | 9.2723 | 9.7113 | 10.1942 | 10.5802 | 10.7135 | 10.9632 | 11.1226 | 11.3053 | 11.2257 | 11.1462 | 11.0666 | 10.9871 | 10.9075 | 10.828 | 10.7484 | 10.6689 | 10.5893 | 10.5098 | 10.4302 | 10.3507 | 10.2711 | 10.1916 | 10.112 | 10.0325

## Workings_benefits
Powercor
BAN003-WND024 Tie upgrade
WORKINGS - BENEFITS
1. MWh Reliability Calulator - Converts Cust Affected and Customer Minutes to Energy Lost
2021-2026 Incentive Rate Calculation
|  |  | Urban | Rural Short | Rural Long
|  | VCR $/MWh | 41210 | 41210 | 41210
|  | CPI | 0.020906 | 0.020906 | 0.020906
|  | w_n | 1.5 | 1.5 | 1.5
|  | Energy Supplied MWh | 4166180.3851 | 4425570.7123 | 2740818.2368
|  | Revenue $ | 650149950.3204 | 650149950.3204 | 650149950.3204
|  | SAIDI | 69.2269 | 104.1416 | 240.9159
|  | SAIFI | 0.82319 | 1.1472 | 2.0249
|  | MAIFI | 1.1996 | 2.5076 | 4.3933
Incentive Rate
|  | ir - SAIDI | 0.030755 | 0.03267 | 0.020233
|  | ir - SAIFI | 1.7242 | 1.9771 | 1.6048
|  | ir - MAIFI (% of SAIFI) | 0.13794 | 0.15817 | 0.12838
8%
Value of Reliability Calulations
|  | 2022-2026 Smoothed Revenue $m | 689.8989 | 689.8989 | 689.8989
$ per Unit
|  | SAIDI | 212176.28 | 225386.5757 | 139585.0789
|  | SAIFI | 11895374.2503 | 13639737.9637 | 11071500.2137
|  | MAIFI | 951629.94 | 1091179.0371 | 885720.0171
|  | Cust | 320111 | 356763 | 212928
$ per Outage Type
|  | SAIDI - $ per CMOS | 0.66282 | 0.63175 | 0.65555
|  | SAIFI - $ per Sustained Cust | 37.1602 | 38.2319 | 51.9965
|  | MAIFI - $ per Momentary Cust | 2.9728 | 3.0586 | 4.1597
MWh by Outage Type
|  |  | Urban | Rural Short | Rural Long
|  | MWh per CMOS | 1.6084e-05 | 1.533e-05 | 1.5908e-05
|  | MWh per Sustained Cust | 0.00090173 | 0.00092773 | 0.0012617
|  | MWh per Momentary Cust Int | 7.2138e-05 | 7.4219e-05 | 0.00010094
2. Worst Served Customer Improvements
It is proposed to install a tie line between BAN003 and WND024 feeder to allow for the transfer of customers between the two feeders. The transfer will be completed using remote controlled switch equipment on the two feeders. Works will include the installation of 3km of new overhead HV, 5.2km of upgrades to existing HV overhead lines, the installation of one voltage regulator and the installation of 3 remote controllable switch devices.
SAIDI/SAIFI Improvement from installing the tie line is influnenced by a number of factors. These include l;ocation of fault, capacity of tie to pick up load tranmsfer, operational restictions due temprary network re-configurations, REFCl opeerating mode and restictions.
|  | Factors to consider |  |  |  |  | BAN003 |  | WND024
[7 empty] | SAIDI | SAIFI | SAIDI | SAIFI
|  | Fault Location Fault is within transfer zone |  |  |  |  | 50% | 50% | 50% | 50%
|  | Transfer Capacity Ability of healthy tie feeder to pickup transfer. (% time unable to transfer) |  |  |  |  | 10% | 10% | 10% | 10%
|  | Operational Constraints Restriction on the ability to transfer customers as the system is switch abormally. Reclose suppression for tree clearing or live line work. Ability to complete auto transfer between Zone Substations. (% time restriction in place) |  |  |  |  | 5% | 25% | 5% | 25%
|  | REFCL Operation Mode (Fire v's Non Fire season) Electricity safety Acr specifies requirement for certain sections of the network to be protected by REFCL's during the declared fire danger period. This restrictions limits duration/time of temporary transfers. (% Time restriction in place) |  |  |  |  | 40% | 40% | 40% | 40%
[7 empty] | 25.65% | 20.25% | 25.65% | 20.25%
Reliability Improvement
|  | Feeder | Feeder Category | No. Customers to Benefit | SAIFI Improvements | SAIDI Improvements | Cust Int saving | CMOS Saving | Energy Not Supplied Saved
|  | BAN003 | Rural Long | 1185 | 20.25% | 25.65% | 2648.133 | 533332.6011 | 11.8253
|  | WND024 | Rural Long | 933 | 20.25% | 25.65% | 1171.5435 | 358376.157 | 7.1791
WSC
|  | Feeder | Feeder Category | No. Customers to Benefit | SAIFI Improvements | SAIDI Improvements | Cust Int saving | CMOS Saving | Energy Not Supplied Saved
|  | BAN003 | Rural Long | 1146 | 20.25% | 25.65% | 2285.5535 | 377785.8489 | 8.8934
|  | WND024 | Rural Long | 850 | 20.25% | 25.65% | 1114.2408 | 360228.9642 | 7.1363
Resilience Outages > 12 Hrs Improvement
|  | Feeder |  | No. Customers to Benefit | SAIFI Improvements | SAIDI Improvements | Cust Int saving | CMOS Saving | Energy Not Supplied Saved
|  | BAN003 | Rural Long | 212.6717 | 20.25% | 25.65% | 96.1964 | 34713.3978 | 0.67358
|  | WND024 | Rural Long | 169.5838 | 20.25% | 25.65% | 55.4789 | 106453.6669 | 1.7634
Reliability Improvement
|  |  |  | No. Customers to Benefit |  |  | Cust Int saving | CMOS Saving | Energy Not Supplied Saved
|  | BAN003 - WND024 Tie | Rural Long | 2118 |  |  | 3819.6765 | 891708.7581 | 19.0044
WSC Benefits
|  |  |  | No. Customers to Benefit |  |  | Cust Int saving | CMOS Saving | Energy Not Supplied Saved
|  | BAN003 - WND024 Tie | Rural Long | 1996 |  |  | 3399.7943 | 738014.8131 | 16.0297
Resilience Outages > 12 Hrs benefits
|  |  |  | No. Customers to Benefit |  |  | Cust Int saving | CMOS Saving | Energy Not Supplied Saved
|  | BAN003 - WND024 Tie | Rural Long | 382.2556 |  |  | 151.6753 | 141167.0647 | 2.437
Benefit Summary
|  |  |  | WSC Cust Benefit | Resilience Benefit | Reliability Benefit
|  |  |  | 13.5927 | 2.437 | 19.0044
|  | Network average outage duration due to bushfire |  | 25.1 |  | hours

## Microgrid_reliability
Powercor
BAN003-WND024 Tie upgrade
Microgrid reliability data
Supply Point | NMI | Order | Order Type | Order Location | Customer Substation | Cust Int Start Time | Cust Int End Time | Cause | SubCause | Order Comments | Order Count | Unplanned Ord Count Sust | Ord Count Momentary | Cust Int Duration | Unplanned Cust Int Dur | Inside Micrograd | Year | ESC Exclusions | Average reliability (used for energy at risk)
33787181 | 62032751888 | F-11395-b | switching | WND024 fdr CB | MARKET ST P3 | 10/02/2018 18:31 | 10/02/2018 19:07 | Weather | Lightning | WND24 unknown. WND23 wire down Redesdale P55,crew reports 3 bays down in the the paddocks. Approx 2-3 bays HV Conductor down ATL getting extra resources. COMPLETE . . . . .. | 1 | 1 | 0 | 108 | 108 | Out | 2018 | No | Annual outage mintues | 1731.6
33787181 | 62032751888 | F-11472-b | switching | 13340-59 22kV ACR TRENTHAM P147 ACR | MARKET ST P3 | 19/02/2018 18:07 | 20/02/2018 01:30 | Vegetation | Tree Council Resp- code compliant | Trees down across O/H conductors at Trentham P225 . . . . . . .. | 1 | 1 | 0 | 443 | 443 | Out | #VALUE! | No
33787181 | 62032751888 | F-11563-b | switching | WND024 fdr CB | MARKET ST P3 | 26/02/2018 11:55 | 26/02/2018 13:12 | Weather | Vegetation | Branch Centre phase and road side phase East Tylden P18 Lis# 980543 . . . . . .. | 1 | 1 | 0 | 77 | 77 | Out | #VALUE! | No
33787181 | 62032751888 | F-11563-b | switching | WND024 fdr CB | MARKET ST P3 | 26/02/2018 13:51 | 26/02/2018 13:55 | Weather | Vegetation | Branch Centre phase and road side phase East Tylden P18 Lis# 980543 . . . . . .. |  |  | 0 | 4 | 4 | Out | #VALUE! | No
33787181 | 62032751888 | F-11563-b | switching | WND024 fdr CB | MARKET ST P3 | 26/02/2018 14:26 | 26/02/2018 14:35 | Weather | Vegetation | Branch Centre phase and road side phase East Tylden P18 Lis# 980543 . . . . . .. |  |  | 0 | 9 | 9 | Out | #VALUE! | No
33787181 | 62032751888 | F-11769-b | switching | WND024 fdr CB | MARKET ST P3 | 17/03/2018 03:18 | 17/03/2018 04:57 | Unknown | No Cause Found | COMPLETE . . . . . . .. | 1 | 1 | 0 | 198 | 198 | Out | #VALUE! | AER MED SAIDI Exceeded 17 Mar 2018 Powercor | Worst served
33787181 | 62032751888 | F-12198-b | switching | WND024 fdr CB | MARKET ST P3 | 14/04/2018 15:14 | 14/04/2018 15:49 | Weather | Vegetation | ETR:Tree through power line at KYNETON train stationREJECT:A dditional Resource RequiredSend job to Jay REARDONETR:Tree t hrough power line at KYNETON train stationETR:Tree through p ower line at KYNETON train station . . . .. | 1 | 1 | 0 | 70 | 70 | Out | #VALUE! | No | Annual outage minutes for outages <12h | 902.6
33787181 | 62032751888 | F-250-d | switching | 21609-59 GIS on KYNETON LOCAL P5 | MARKET ST P3 | 17/12/2018 17:43 | 17/12/2018 18:30 | Third Party | Vehicle impact | Car into pole Kyneton Springhill Rd, broken ties, leaning po le, public safety.Kyneton Springhill Rd P3 lis 982978 . . . . . .. | 1 | 1 | 0 | 47 | 47 | Out | #VALUE! | No | Annual outage minutes for outages <12h exceeding 500 mins | 402.6
33787181 | 62032751888 | F-15217-b | switching | WND024 fdr CB | MARKET ST P3 | 18/01/2019 14:11 | 18/01/2019 17:55 | Third Party | Vehicle impact | ETR:Truck trailer hit pole Trentham Rd KYNETON SouthREJECT:E TR:Truck trailer hit pole Trentham Rd KYNETON SouthETR:Truck trailer hit pole Trentham Rd KYNETON SouthETR:Truck trailer hit pole Trentham Rd KYNETON SouthETR:Truck trailer hit pol e Trentham Rd KYNETON South . . .. | 1 | 1 | 0 | 224 | 224 | Out | #VALUE! | No | Annual outage hours for outages <12h exceeding 500 mins | 6.71
33787181 | 62032751888 | F-15434-b | switching | WND024 fdr CB | MARKET ST P3 | 30/01/2019 16:18 | 30/01/2019 16:53 | Weather | Vegetation | REJECT:Additional Resource RequiredPass on to Ross BakerTREE BROUGHT DOWN WIRE OFF XARM AT LIS 908192REJECT:Additional R esource Required Pole 8 lis 908192 fiddlers green req fog in s steel tie flex and reconnect servicRelated to 1223854-1 (W ire down)REPAIR:Replaced hv insulator and flex at txCOMPLETE :Replaced hv insulator and hv flex. Tied conductor back in a ll ok. .. | 1 | 1 | 0 | 35 | 35 | Out | #VALUE! | No
33787181 | 62032751888 | F-15461-b | switching | 13340-59 22kV ACR TRENTHAM P147 ACR | MARKET ST P3 | 30/01/2019 17:40 | 30/01/2019 20:06 | Weather | Storm activity | COMPLETE . . . . . . .. | 1 | 1 | 0 | 146 | 146 | Out | #VALUE! | No
33787181 | 62032751888 | F-15935-b | switching | WND024 fdr CB | MARKET ST P3 | 09/02/2019 19:13 | 09/02/2019 19:35 | Equip Fail | Insulation Failure | REPAIR:Changed HV insulated dropper burnt outCOMPLETE . . . . . . .. | 1 | 1 | 0 | 22 | 22 | Out | 2019 | No | Resilience
33787181 | 62032751888 | F-16071-b | switching | 13340-59 22kV ACR TRENTHAM P147 ACR | MARKET ST P3 | 20/02/2019 17:18 | 20/02/2019 18:05 | Equip Fail | U/G cable, Joint, Termination failure | REJECT:Additional Resource RequiredAppear to have U/G fault. Req more resources ..Phil Robinson and esc manager advise c ustomers will be off supply till 11.00 21/2. Generator being organised for tomorow 21/2.Spoken with phil 9:30 - still aw aiting gennieJob issued to Derek Russell.As per Phil Robinso n they have not located the fault yet and the customers coul d be off until 22/02. Phil has advised to move the ETR out t o 2000 21/02. Crew will keep us informed if its going to run over. | 1 | 1 | 0 | 47 | 47 | Out | #VALUE! | No | Annual outage minutes for outages >=12h | 829
33787181 | 62032751888 | F-16599-b | switching | WND024 fdr CB | MARKET ST P3 | 29/03/2019 18:02 | 29/03/2019 21:34 | Equip Fail | Loose connection | Burnt D 41625 GAC SW EAST TYLDEN P2 lis 905812COMPLETE . . . . . . .. | 1 | 1 | 0 | 212 | 212 | Out | #VALUE! | No | Annual outage minutes 12>t>24 hours | 0
33787181 | 62032751888 | F-17323-b | switching | 13340-59 22kV ACR TRENTHAM P147 ACR | MARKET ST P3 | 29/05/2019 09:13 | 29/05/2019 11:52 | Vegetation | Bark/Branch | Bark across 22KV O/H in Cosmo Rd P9 LIS 916927 HV LLC burnt off at Park Cnr of Drummond St LIS 906993. . . . . . .. | 1 | 1 | 0 | 159 | 159 | Inside Micrograd | #VALUE! | No | Annual outage minutes >24 hours | 541
33787181 | 62032751888 | J-192735-b | switching | 13340-59 22kV ACR TRENTHAM P147 ACR | MARKET ST P3 | 31/05/2019 17:22 | 31/05/2019 17:27 | Equip Fail | Loose connection | TEMP FIXED D LOOP . CREW RETURNING TO REPLACE G AND B 1/5 . . . . . . .. | 1 | 1 | 0 | 5 | 5 | Out | #VALUE! | No | Annual outage minutes >72 hours | 0
33787181 | 62032751888 | F-17878-b | switching | 13340-59 22kV ACR TRENTHAM P147 ACR | MARKET ST P3 | 22/07/2019 13:49 | 22/07/2019 22:06 | Weather | Wind | Trentham P147 ACR tripped to lockout. Large tree brought dow n conductors at Trentham P220, LIS 906715.REJECT:REPAIR:Repl aced p218 & p220 Trentham line and replaced 5 bays of hv con ductor from p217 to p222 Trentham line.COMPLETE . . . .. | 1 | 1 | 0 | 497 | 497 | Out | #VALUE! | No
33787181 | 62032751888 | F-18723-b | switching | WND022 fdr CB | MARKET ST P3 | 13/10/2019 18:45 | 13/10/2019 19:25 | Equip Fail | Conductor clashing | Poss HVI, LEI Phil Clayden 0416 146 599 will attend . . . . . . .. | 1 | 1 | 0 | 80 | 80 | Out | #VALUE! | No | Residential resilience hours at 2x VCR (12-24h) | 0
33787181 | 62032751888 | F-19346-b | switching | WND024 fdr CB | MARKET ST P3 | 21/11/2019 14:54 | 21/11/2019 18:21 | Weather | Wind | . . . . . . . .. | 1 | 1 | 0 | 207 | 207 | Out | #VALUE! | ESC: MED SAIFI & SAIDI Exceeded 21 Nov 2019 Powercor | Residential resilience hours at 1.5x VCR (>24h) | 9.0167
33787181 | 62032751888 | F-20182-b | switching | WND024 fdr CB | MARKET ST P3 | 07/01/2020 02:39 | 07/01/2020 02:57 | Unknown | Auto Resolved | REPAIR:Line restored by opsCOMPLETE . . . . . . .. | 1 | 1 | 0 | 18 | 18 | Out | 2020 | AER: REFCL Bush fire Mitigation Jan 2020
33787181 | 62032751888 | F-20354-b | restoration | WND024 fdr CB | MARKET ST P3 | 15/01/2020 16:21 | 15/01/2020 18:03 | Weather | Lightning | Outage Split for REFCL Bush fire Mitigation Exclusion - Ord er F-20354-b covers WND024 to18336-Trentham Kyneton Tie P18 ACR and Order 1436483-1 covers 18336-Trentham Kyneton Tie P1 8 ACRto End . . . .. | 1 | 1 | 0 | 102 | 102 | Out | #VALUE! | AER: REFCL Bush fire Mitigation Jan 2020 | Business resilience hours at 1.5x VCR (12-24h) | 0
33787181 | 62032751888 | F-20354-b | restoration | WND024 fdr CB | MARKET ST P3 | 15/01/2020 19:13 | 15/01/2020 19:17 | Weather | Lightning | Outage Split for REFCL Bush fire Mitigation Exclusion - Ord er F-20354-b covers WND024 to18336-Trentham Kyneton Tie P18 ACR and Order 1436483-1 covers 18336-Trentham Kyneton Tie P1 8 ACRto End . . . .. | 1 | 1 | 0 | 4 | 4 | Out | #VALUE! | AER: REFCL Bush fire Mitigation Jan 2020 | Business resilience hours at 0.5x VCR (>72 hours) | 0
33787181 | 62032751888 | 1391103-1 | switching | 626 BLACKWOOD ROAD,NEWBURY,VIC,3458 | MARKET ST P3 | 01/02/2020 10:29 | 01/02/2020 10:56 | Vegetation | Bark/Branch | Related to F-20981-b. Outage Split for REFCL Busfire Mitigat ion Exclusion - this outage covers WND024 CB to 13883 Blackw ood ACR P18 and Order F-20981-b cover 13883 Blackwood ACR P1 8 to END . . . .. | 1 | 1 | 0 | 27 | 27 | Out | 2020 | AER: REFCL Bush fire Mitigation Feb 2020
33787181 | 62032751888 | F-21805-b | switching | WND024 fdr CB | MARKET ST P3 | 01/03/2020 02:36 | 01/03/2020 02:47 | Unknown | No Cause Found | . . . . . . . .. | 1 | 1 | 0 | 11 | 11 | Out | 2020 | AER: REFCL Bush fire Mitigation Mar 2020
33787181 | 62032751888 | F-22000-b | switching | WND024 fdr CB | MARKET ST P3 | 15/03/2020 00:18 | 15/03/2020 00:37 | Unknown | No Cause Found | ETR:Feeder stayed in when tried by Operations Complete recei ved but not processed as no Restore . . . . . .. | 1 | 1 | 0 | 19 | 19 | Out | #VALUE! | AER: REFCL Bush fire Mitigation Mar 2020
33787181 | 62032751888 | F-22621-b | switching | WND024 fdr CB | MARKET ST P3 | 01/05/2020 10:20 | 01/05/2020 10:31 | Pole Fire | Salt/dust pollution | Pole fire Caddys iso due to faulty HV Earths. See F-22620- b & F-22621-b . . . . . .. | 1 | 1 | 0 | 11 | 11 | Out | 2020 | No
33787181 | 62032751888 | F-22621-b | switching | WND024 fdr CB | MARKET ST P3 | 01/05/2020 11:21 | 01/05/2020 11:23 | Pole Fire | Salt/dust pollution | Pole fire Caddys iso due to faulty HV Earths. See F-22620- b & F-22621-b . . . . . .. |  |  | 0 | 2 | 2 | Out | 2020 | No
33787181 | 62032751888 | F-22621-b | switching | WND024 fdr CB | MARKET ST P3 | 01/05/2020 11:24 | 01/05/2020 11:34 | Pole Fire | Salt/dust pollution | Pole fire Caddys iso due to faulty HV Earths. See F-22620- b & F-22621-b . . . . . .. |  |  | 0 | 10 | 10 | Out | 2020 | No
33787181 | 62032751888 | F-26356-b | switching | WND024 fdr CB | MARKET ST P3 | 23/01/2021 15:09 | 23/01/2021 16:05 | Unknown | No Cause Found | COMPLETE . . . . . . .. | 1 | 1 | 0 | 56 | 56 | Out | #VALUE! | AER: REFCL Bush fire Mitigation Jan 2021
33787181 | 62032751888 | F-26356-b | switching | WND024 fdr CB | MARKET ST P3 | 23/01/2021 16:07 | 23/01/2021 16:20 | Unknown | No Cause Found | COMPLETE . . . . . . .. |  |  | 0 | 13 | 13 | Out | #VALUE! | AER: REFCL Bush fire Mitigation Jan 2021
33787181 | 62032751888 | F-26356-b | switching | WND024 fdr CB | MARKET ST P3 | 23/01/2021 16:21 | 23/01/2021 16:38 | Unknown | No Cause Found | COMPLETE . . . . . . .. | 1 | 1 | 0 | 17 | 17 | Out | #VALUE! | AER: REFCL Bush fire Mitigation Jan 2021
33787181 | 62032751888 | F-28060-b | switching | WND024 fdr CB | MARKET ST P3 | 09/06/2021 16:15 | 09/06/2021 17:10 | Vegetation | Bark/Branch | Complete received but not processed as no RestoreConductors replaced between P98-105. Crew currently removing trees on T ylden Line - In process of energising backbone up to SW 2644 4 - Line being patrolled from ACR 2899 (Top end of Kyneton)W ork complete. . . .. | 1 | 1 | 0 | 55 | 55 | Out | 2021 | AER: MED SAIDI Exceeded 9 Jun 2021 Powercor
33787181 | 62032751888 | F-28060-b | switching | WND024 fdr CB | MARKET ST P3 | 09/06/2021 17:50 | 09/06/2021 17:53 | Vegetation | Bark/Branch | Complete received but not processed as no RestoreConductors replaced between P98-105. Crew currently removing trees on T ylden Line - In process of energising backbone up to SW 2644 4 - Line being patrolled from ACR 2899 (Top end of Kyneton)W ork complete. . . .. |  |  | 0 | 3 | 3 | Out | 2021 | AER: MED SAIDI Exceeded 9 Jun 2021 Powercor
33787181 | 62032751888 | F-28060-b | switching | WND024 fdr CB | MARKET ST P3 | 09/06/2021 19:22 | 12/06/2021 16:27 | Vegetation | Bark/Branch | Complete received but not processed as no RestoreConductors replaced between P98-105. Crew currently removing trees on T ylden Line - In process of energising backbone up to SW 2644 4 - Line being patrolled from ACR 2899 (Top end of Kyneton)W ork complete. . . .. |  |  | 0 | 4145 | 4145 | Out | 2021 | AER: MED SAIDI Exceeded 9 Jun 2021 Powercor
33787181 | 62032751888 | F-29436-b | switching | WND024 fdr CB | MARKET ST P3 | 30/09/2021 19:02 | 30/09/2021 20:38 | Weather | Storm activity | Patrolled, no cause found. Storm activity in area. . IT fron t door request submitted to close this job. . . . . . .. | 1 | 1 | 0 | 192 | 192 | Out | #VALUE! | No
33787181 | 62032751888 | F-30031-b | switching | WND024 fdr CB | MARKET ST P3 | 29/10/2021 06:10 | 29/10/2021 15:50 | Weather | Storm activity | . . . . . . . .. | 1 | 1 | 0 | 580 | 580 | Out | #VALUE! | ESC: MED SAIDI Exceeded 29th Oct Powercor
33787181 | 62032751888 | F-30761-b | switching | WND024 fdr CB | MARKET ST P3 | 01/12/2021 22:41 | 02/12/2021 01:56 | Weather | Storm activity | COMPLETE . . . . . . .. | 1 | 1 | 0 | 195 | 195 | Out | 2021 | No
33787181 | 62032751888 | F-31390-b | switching | WND024 fdr CB | MARKET ST P3 | 05/01/2022 01:24 | 05/01/2022 03:42 | Unknown | No Cause Found | COMPLETE:Patrolled Line. No apparent cause. Supply back on . . . . . . .. | 1 | 1 | 0 | 138 | 138 | Out | 2022 | ESC: MED SAIDI Exceeded 5th Jan 2022 Powercor
33787181 | 62032751888 | F-31914-b | switching | WND024 fdr CB | MARKET ST P3 | 13/01/2022 20:23 | 13/01/2022 23:44 | Weather | Lightning | LLFlex found burnt off Red phase incomming isol Trentham P14 7 ACR . . . . . .. | 1 | 1 | 0 | 201 | 201 | Out | #VALUE! | No
33787181 | 62032751888 | F-32501-b | switching | WND024 fdr CB | MARKET ST P3 | 27/01/2022 20:24 | 27/01/2022 23:24 | Weather | Storm activity | COMPLETE:Patrolled and patrolled. Turned REFCL off and the f dr stayed in. . . . . . .. | 1 | 1 | 0 | 180 | 180 | Out | #VALUE! | ESC: MED SAIDI Exceeded 27th Jan 2022 Powercor
33787181 | 62032751888 | 1714703-1 | switching | SPECIAL SCHOOL,MARTIN STREET,BLACKWOOD,VIC,3458 | MARKET ST P3 | 09/02/2022 15:36 | 09/02/2022 17:26 | Vegetation | Bark/Branch | Order Split for REFCL Bushfire Mitigation Exemption refer to Order F-33041-b . . . . . .. Bark flashed over at RAHILLS RD 14. No damage. | 1 | 1 | 0 | 110 | 110 | Inside Micrograd | 2022 | No
33787181 | 62032751888 | F-33236-b | switching | WND024 fdr CB | MARKET ST P3 | 23/02/2022 21:34 | 23/02/2022 23:12 | Equip Fail | Insulation Failure | Order split for REFCL Bushfire Mitigation Exemption - refer Order 1720734-1 for split outage.COMPLETE:Patrolled Feeder n othing found ,switched Feeder back in conjunction with Opera tionsloosen tie on LIS 907222 / SIMMONS REEF 8" . . . .. | 1 | 1 | 0 | 98 | 98 | Out | #VALUE! | AER: REFCL Bushfire Mitigation Feb 2022
33787181 | 62032751888 | F-33326-b | switching | WND024 fdr CB | MARKET ST P3 | 27/02/2022 22:45 | 27/02/2022 23:13 | Equip Fail | Insulation Failure | Order split for REFCL Bushfire Mitigation Exemption - refer Order 1721204-1 for split outage.Sectionalised and restored with no Cause found.loosen tie on LIS 907222 / SIMMONS REEF 8" . . . .. |  |  | 0 | 28 | 28 | Out | #VALUE! | AER: REFCL Bushfire Mitigation Feb 2022
33787181 | 62032751888 | F-33353-b | switching | WND024 fdr CB | MARKET ST P3 | 01/03/2022 03:39 | 01/03/2022 04:13 | Equip Fail | Insulation Failure | Order split for REFCL Bushfire Mitigation Exemption - refer Order 1724267-1. Sectionalised and Restored....Unknown; Day time Patrol Required; 3rd Lockout in 1 weekETR:Patrolling Fe eder for OperationsREPAIR:Disconnected 2 x Blown LA s at Tre ntham-Kyneton Tie P6 S/S, also removed bark at Blue Mount P5 LIS#906955. Operations made aware of both findings after a Patrol of WND024 backbone & unfused spurs.COMPLETE - Repaire d surge divertor at LIS 907236loosen tie on LIS 907222 / SIMMONS REEF 8" | 1 | 1 | 0 | 34 | 34 | Out | 2022 | AER: REFCL Bushfire Mitigation Mar 2022
33787181 | 62032751888 | F-33406-b | switching | WND024 fdr CB | MARKET ST P3 | 01/03/2022 21:43 | 01/03/2022 21:59 | Equip Fail | Insulation Failure | Order split for REFCL Bushfire Mitigation Exemption - refer Order 1724352-1 for split outage. . . . . . .. | 1 | 1 | 0 | 16 | 16 | Out | 2022 | AER: REFCL Bushfire Mitigation Mar 2022
33787181 | 62032751888 | F-33483-b | switching | WND024 fdr CB | MARKET ST P3 | 04/03/2022 20:59 | 04/03/2022 21:16 | Equip Fail | Insulation Failure | Order split for REFCL Bushfire Mitigation Exemption - refer Order 1726157-1 for split outage. SCHEDULE:Order not receive d in Click; try again. If problem persists, contact Service Desk.ETR:Storm around Blackwood. Sectionalise and see what w e can findCOMPLETE:Ongoing fault that doesn t want to be loc ated. Holds in when switched.loosen tie on LIS 907222 / SIMM ONS REEF 8" .. | 1 | 1 | 0 | 17 | 17 | Out | 2022 | AER: REFCL Bushfire Mitigation Mar 2022
33787181 | 62032751888 | F-33483-b | switching | WND024 fdr CB | MARKET ST P3 | 04/03/2022 21:22 | 04/03/2022 21:37 | Equip Fail | Insulation Failure | Order split for REFCL Bushfire Mitigation Exemption - refer Order 1726157-1 for split outage. SCHEDULE:Order not receive d in Click; try again. If problem persists, contact Service Desk.ETR:Storm around Blackwood. Sectionalise and see what w e can findCOMPLETE:Ongoing fault that doesn t want to be loc ated. Holds in when switched.loosen tie on LIS 907222 / SIMM ONS REEF 8" .. | 1 | 1 | 0 | 15 | 15 | Out | 2022 | AER: REFCL Bushfire Mitigation Mar 2022
33787181 | 62032751888 | F-33512-b-S | switching | WND024 fdr CB | MARKET ST P3 | 05/03/2022 21:37 | 05/03/2022 21:55 | Equip Fail | Insulation Failure | Order split for REFCL Bushfire Mitigation Exemption - refer Order 1726490-1 for split outage.loosen tie on LIS 907222 / SIMMONS REEF 8 . . . . .. | 1 | 1 | 0 | 18 | 18 | Out | 2022 | AER: REFCL Bushfire Mitigation Mar 2022
33787181 | 62032751888 | F-33539-b | switching | WND024 fdr CB | MARKET ST P3 | 07/03/2022 23:10 | 08/03/2022 01:01 | Equip Fail | Insulation Failure | Order split for REFCL Bushfire Mitigation Exemption - refer Order 1727215-1 for split outage.COMPLETE:Patrolled WND24 Fd r no apparent cause found supply restored.loosen tie on LIS 907222 / SIMMONS REEF 8 . . . .. | 1 | 1 | 0 | 111 | 111 | Out | 2022 | AER: REFCL Bushfire Mitigation Mar 2022
33787181 | 62032751888 | F-35900-b | switching | WND024 fdr CB | MARKET ST P3 | 17/09/2022 06:10 | 17/09/2022 06:31 | Unknown | No Cause Found | AER: REFCL Bush fire Mitigation Excemption Sept 2022 order s plit see for sub fault at Central Rd P5, oms 1805501-1, blo wn red phase fuse, ncf. . . . . .. | 1 | 1 | 0 | 21 | 21 | Out | #VALUE! | No
33787181 | 62032751888 | F-36211-b | switching | 13340-59 22kV ACR TRENTHAM P147 ACR | MARKET ST P3 | 12/10/2022 10:23 | 12/10/2022 10:51 | Vegetation | Tree Council Resp- code compliant | NAO informed - tree down on conductor LIS 917607 . . . . . . .. | 1 | 1 | 0 | 28 | 28 | Inside Micrograd | 2022 | No
33787181 | 62032751888 | F-36211-b | switching | 13340-59 22kV ACR TRENTHAM P147 ACR | MARKET ST P3 | 12/10/2022 10:51 | 12/10/2022 14:28 | Vegetation | Tree Council Resp- code compliant | NAO informed - tree down on conductor LIS 917607 . . . . . . .. | 1 | 1 | 0 | 217 | 217 | Inside Micrograd | 2022 | No
33787181 | 62032751888 | 1815256-1 | restoration | WND024 fdr CB | MARKET ST P3 | 13/10/2022 12:36 | 13/10/2022 14:12 | Weather | Storm activity | Related F-36248-b, 1815251-1,1815253-1,1815252-1, 1815255-1, 1815249-1 . . . . . .. | 1 | 1 | 0 | 96 | 96 | Out | #VALUE! | No
33787181 | 62032751888 | F-38525-b | switching | WND024 fdr CB | MARKET ST P3 | 02/02/2023 16:53 | 02/02/2023 17:18 | Vegetation | Bark/Branch | COMPLETE:Removed bark at pole 221. Lis 906710 . . . . . . .. | 1 | 1 | 0 | 25 | 25 | Inside Micrograd | 2023 | No
33787181 | 62032751888 | F-38525-b | switching | WND024 fdr CB | MARKET ST P3 | 02/02/2023 17:19 | 02/02/2023 19:08 | Vegetation | Bark/Branch | COMPLETE:Removed bark at pole 221. Lis 906710 . . . . . . .. | 1 | 1 | 0 | 109 | 109 | Inside Micrograd | 2023 | No
33787181 | 62032751888 | F-38525-b | switching | WND024 fdr CB | MARKET ST P3 | 02/02/2023 19:09 | 02/02/2023 19:25 | Vegetation | Bark/Branch | COMPLETE:Removed bark at pole 221. Lis 906710 . . . . . . .. | 1 | 1 | 0 | 16 | 16 | Inside Micrograd | 2023 | No
33787181 | 62032751888 | F-41294-b | switching | 13340-59 22kV ACR TRENTHAM P147 ACR | MARKET ST P3 | 08/09/2023 09:29 | 08/09/2023 10:55 | Weather | Vegetation | COMPLETE . . . . . . .. | 1 | 1 | 0 | 86 | 86 | Out | 2023 | ESC: MED 8/9/23

## Misc_calcs
Powercor
BAN003-WND024 Tie upgrade
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 4 | TRUE
| Option 3 | 4 | TRUE
| Option 4 | 1 | TRUE
| Option 5 | Not used | FALSE
| First year | 1
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
Powercor
BAN003-WND024 Tie upgrade
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | FALSE |  |  | FALSE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
Powercor
| Reliability in worst-served areas | per MWh | 67500
| Network resilience | per MWh | 67129.9906
| Enabling solar exports | per MWh | 10
| Customer value per kWh of storage capacity in local community: | per customer impacted | 51130
| Customer value of time - residential | per minute customer time | 0.73
| Customer value of time - business | per minute customer time | 4.45
| Communication | per customer impacted | 0.28
| Information accessibility | per customer impacted | 0.17
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020