## Cover
Powercor
Regulatory proposal 2026-31
Regional and rural SWER upgrades
| Model number: | 3.3
2025-01-31
16

## Summary
Powercor
Regional and rural supply upgrades
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Limited SWER upgrades |  | -40.3851 | 554.2919 | 513.9068
| Option 3 | Economic SWER upgrades |  | -57.3274 | 599.8738 | 542.5465
| Option 4 | Accelerated SWER upgrades |  | -109.9088 | 646.6525 | 536.7437
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 3 | Economic SWER upgrades |  | 542.5465
PREFERRED OPTION
Preferred Option
Option 3
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 10.684 | 7.3452 | 12.6872 | 15.5808 | 16.805 |  | 63.1021
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
Capex and risk ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 513.9068 | 542.5465 | 536.7437 |  |  | Option 3
| Capex 10% higher |  | 0 | 509.8683 | 536.8137 | 525.7529 |  |  | Option 3
| Capex 10% lower |  | 0 | 517.9453 | 548.2792 | 547.7346 |  |  | Option 3
| Total benefits 10% higher |  | 0 | 569.336 | 602.5339 | 601.409 |  |  | Option 3
| Total benefits 10% lower |  | 0 | 458.4776 | 482.5591 | 472.0785 |  |  | Option 3
| Capex 10% higher & Total benefits 10% lower |  | 0 | 454.4391 | 476.8263 | 461.0876 |  |  | Option 3
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
Powercor
Regional and rural supply upgrades
Project
|  | Business: |  | Powercor
|  | Descripton: |  | Regional and rural supply upgrades
|  | Date of cost inputs: |  | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Limited SWER upgrades
|  | Option 3 |  | Economic SWER upgrades
|  | Option 4 |  | Accelerated SWER upgrades
Option 5
|  | Compliance project |  | No
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | Network average |  | Network average | 43815.4862 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 151432.8174 | 2023-12-31 | per MWh
|  | Network resilience |  |  |  | 24590 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 88.3577 | 2023-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
Powercor
Regional and rural supply upgrades
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value (CECV + CO2 + VCR) | $/MWh | 43815.4862 | 2023-12-31 |  | 43929947.0411 | 49988716.7362 | 52690343.3273 | 53585767.7148 | 54058138.6687 | 56646621.3435 | 57424173.2902 | 59134679.1394 | 59492948.7658 | 59492948.7658 | 59492948.7658 | 59492948.7658 | 59492948.7658 | 59492948.7658 | 59492948.7658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 43929947.0411 | 49988716.7362 | 52690343.3273 | 53585767.7148 | 54058138.6687 | 56646621.3435 | 57424173.2902 | 59134679.1394 | 59492948.7658 | 59492948.7658 | 59492948.7658 | 59492948.7658 | 59492948.7658 | 59492948.7658 | 59492948.7658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
Powercor
Regional and rural supply upgrades
OPTION 2 | Limited SWER upgrades
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| SWER upgrades |  | 15 | 2023-12-31 | 7900000 | 7900000 | 7900000 | 7900000 | 7900000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 7900000 | 7900000 | 7900000 | 7900000 | 7900000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 10705064.4231 | 11266246.7363 | 11515808.4439 | 12077045.5195 | 12304963.958 | 12405383.6465 | 12938748.7564 | 14454713.0208 | 14706932.9132 | 14706932.9132 | 14706932.9132 | 14706932.9132 | 14706932.9132 | 14706932.9132 | 14706932.9132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 10705064.4231 | 11266246.7363 | 11515808.4439 | 12077045.5195 | 12304963.958 | 12405383.6465 | 12938748.7564 | 14454713.0208 | 14706932.9132 | 14706932.9132 | 14706932.9132 | 14706932.9132 | 14706932.9132 | 14706932.9132 | 14706932.9132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - residential | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - business | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 33224882.618 | 38722469.9999 | 41174534.8835 | 41508722.1954 | 41753174.7107 | 44241237.697 | 44485424.5337 | 44679966.1186 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| SWER upgrades |  |  | 2023-12-31 | -7900000 | -7900000 | -7900000 | -7900000 | -7900000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| SWER upgrades |  |  | 2023-12-31 | -7900000 | -15800000 | -23700000 | -31600000 | -39500000 | -39500000 | -39500000 | -39500000 | -39500000 | -39500000 | -39500000 | -39500000 | -39500000 | -39500000 | -39500000 | -31600000 | -23700000 | -15800000 | -7900000 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - SWER upgrades |  |  | 2023-12-31 | 0 | -685918.048 | -1371836.096 | -2057754.144 | -2743672.192 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -2743672.192 | -2057754.144 | -1371836.096 | -685918.048 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -685918.048 | -1371836.096 | -2057754.144 | -2743672.192 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -2743672.192 | -2057754.144 | -1371836.096 | -685918.048 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | -685918.048 | -1371836.096 | -2057754.144 | -2743672.192 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -2743672.192 | -2057754.144 | -1371836.096 | -685918.048 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 33224882.618 | 38722469.9999 | 41174534.8835 | 41508722.1954 | 41753174.7107 | 44241237.697 | 44485424.5337 | 44679966.1186 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 33224882.618 | 38036551.9519 | 39802698.7875 | 39450968.0514 | 39009502.5187 | 40811647.4571 | 41055834.2938 | 41250375.8787 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | -3429590.24 | -2743672.192 | -2057754.144 | -1371836.096 | -685918.048 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 33224882.618 | 38036551.9519 | 39802698.7875 | 39450968.0514 | 39009502.5187 | 40811647.4571 | 41055834.2938 | 41250375.8787 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | -3429590.24 | -2743672.192 | -2057754.144 | -1371836.096 | -685918.048 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | -685918.048 | -1371836.096 | -2057754.144 | -2743672.192 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -3429590.24 | -2743672.192 | -2057754.144 | -1371836.096 | -685918.048 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 33224882.618 | 38722469.9999 | 41174534.8835 | 41508722.1954 | 41753174.7107 | 44241237.697 | 44485424.5337 | 44679966.1186 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 33224882.618 | 37967960.1471 | 39665515.1779 | 39245192.637 | 38735135.2995 | 40468688.4331 | 40712875.2698 | 40907416.8547 | 41013466.5887 | 41013466.5887 | 41013466.5887 | 41013466.5887 | 41013466.5887 | 41013466.5887 | 41013466.5887 | -3772549.264 | -3018039.4112 | -2263529.5584 | -1509019.7056 | -754509.8528 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 33224882.618 | 38105143.7567 | 39939882.3971 | 39656743.4658 | 39283869.7379 | 41154606.4811 | 41398793.3178 | 41593334.9027 | 41699384.6367 | 41699384.6367 | 41699384.6367 | 41699384.6367 | 41699384.6367 | 41699384.6367 | 41699384.6367 | -3086631.216 | -2469304.9728 | -1851978.7296 | -1234652.4864 | -617326.2432 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 36547370.8798 | 41908798.9518 | 43920152.2758 | 43601840.2709 | 43184819.9898 | 45235771.2268 | 45504376.7471 | 45718372.4905 | 45835027.198 | 45835027.198 | 45835027.198 | 45835027.198 | 45835027.198 | 45835027.198 | 45835027.198 | -3429590.24 | -2743672.192 | -2057754.144 | -1371836.096 | -685918.048 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 29902394.3562 | 34164304.9519 | 35685245.2991 | 35300095.8319 | 34834185.0477 | 36387523.6874 | 36607291.8404 | 36782379.2668 | 36877824.0274 | 36877824.0274 | 36877824.0274 | 36877824.0274 | 36877824.0274 | 36877824.0274 | 36877824.0274 | -3429590.24 | -2743672.192 | -2057754.144 | -1371836.096 | -685918.048 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 29902394.3562 | 34095713.1471 | 35548061.6895 | 35094320.4175 | 34559817.8285 | 36044564.6634 | 36264332.8164 | 36439420.2428 | 36534865.0034 | 36534865.0034 | 36534865.0034 | 36534865.0034 | 36534865.0034 | 36534865.0034 | 36534865.0034 | -3772549.264 | -3018039.4112 | -2263529.5584 | -1509019.7056 | -754509.8528 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 2sens | 33224882.618 | 38036551.9519 | 39802698.7875 | 39450968.0514 | 39009502.5187 | 40811647.4571 | 41055834.2938 | 41250375.8787 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | -3429590.24 | -2743672.192 | -2057754.144 | -1371836.096 | -685918.048 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 2sens | 33224882.618 | 38036551.9519 | 39802698.7875 | 39450968.0514 | 39009502.5187 | 40811647.4571 | 41055834.2938 | 41250375.8787 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | -3429590.24 | -2743672.192 | -2057754.144 | -1371836.096 | -685918.048 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 2sens | 33224882.618 | 38036551.9519 | 39802698.7875 | 39450968.0514 | 39009502.5187 | 40811647.4571 | 41055834.2938 | 41250375.8787 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | 41356425.6127 | -3429590.24 | -2743672.192 | -2057754.144 | -1371836.096 | -685918.048 | 0 | 0 | 0 | 0 | 0

## Option3
Powercor
Regional and rural supply upgrades
OPTION 3 | Economic SWER upgrades
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| SWER upgrades |  | 15 | 2023-12-31 | 9600000 | 6600000 | 11400000 | 14000000 | 15100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 9600000 | 6600000 | 11400000 | 14000000 | 15100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 7613374.1453 | 8123960.7362 | 8335125.949 | 8717156.0779 | 8930431.0279 | 9063023.444 | 9469903.2361 | 10748497.816 | 10951036.9405 | 10951036.9405 | 10951036.9405 | 10951036.9405 | 10951036.9405 | 10951036.9405 | 10951036.9405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 7613374.1453 | 8123960.7362 | 8335125.949 | 8717156.0779 | 8930431.0279 | 9063023.444 | 9469903.2361 | 10748497.816 | 10951036.9405 | 10951036.9405 | 10951036.9405 | 10951036.9405 | 10951036.9405 | 10951036.9405 | 10951036.9405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 36316572.8958 | 41864756 | 44355217.3784 | 44868611.6369 | 45127707.6408 | 47583597.8995 | 47954270.0541 | 48386181.3234 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| SWER upgrades |  |  | 2023-12-31 | -9600000 | -6600000 | -11400000 | -14000000 | -15100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| SWER upgrades |  |  | 2023-12-31 | -9600000 | -16200000 | -27600000 | -41600000 | -56700000 | -56700000 | -56700000 | -56700000 | -56700000 | -56700000 | -56700000 | -56700000 | -56700000 | -56700000 | -56700000 | -47100000 | -40500000 | -29100000 | -15100000 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - SWER upgrades |  |  | 2023-12-31 | 0 | -833520.6659 | -1406566.1237 | -2396371.9145 | -3611922.8856 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4089460.7671 | -3516415.3093 | -2526609.5186 | -1311058.5474 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -833520.6659 | -1406566.1237 | -2396371.9145 | -3611922.8856 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4089460.7671 | -3516415.3093 | -2526609.5186 | -1311058.5474 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | -833520.6659 | -1406566.1237 | -2396371.9145 | -3611922.8856 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4089460.7671 | -3516415.3093 | -2526609.5186 | -1311058.5474 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 36316572.8958 | 41864756 | 44355217.3784 | 44868611.6369 | 45127707.6408 | 47583597.8995 | 47954270.0541 | 48386181.3234 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 36316572.8958 | 41031235.3341 | 42948651.2546 | 42472239.7224 | 41515784.7552 | 42660616.4664 | 43031288.621 | 43463199.8904 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | -4922981.4331 | -4089460.7671 | -3516415.3093 | -2526609.5186 | -1311058.5474 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 36316572.8958 | 41031235.3341 | 42948651.2546 | 42472239.7224 | 41515784.7552 | 42660616.4664 | 43031288.621 | 43463199.8904 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | -4922981.4331 | -4089460.7671 | -3516415.3093 | -2526609.5186 | -1311058.5474 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | -833520.6659 | -1406566.1237 | -2396371.9145 | -3611922.8856 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4922981.4331 | -4089460.7671 | -3516415.3093 | -2526609.5186 | -1311058.5474 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 36316572.8958 | 41864756 | 44355217.3784 | 44868611.6369 | 45127707.6408 | 47583597.8995 | 47954270.0541 | 48386181.3234 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 36316572.8958 | 40947883.2675 | 42807994.6423 | 42232602.5309 | 41154592.4666 | 42168318.3231 | 42538990.4777 | 42970901.7471 | 43126632.2489 | 43126632.2489 | 43126632.2489 | 43126632.2489 | 43126632.2489 | 43126632.2489 | 43126632.2489 | -5415279.5764 | -4498406.8439 | -3868056.8403 | -2779270.4704 | -1442164.4022 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 36316572.8958 | 41114587.4007 | 43089307.867 | 42711876.9138 | 41876977.0437 | 43152914.6098 | 43523586.7643 | 43955498.0337 | 44111228.5355 | 44111228.5355 | 44111228.5355 | 44111228.5355 | 44111228.5355 | 44111228.5355 | 44111228.5355 | -4430683.2897 | -3680514.6904 | -3164773.7784 | -2273948.5667 | -1179952.6927 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 39948230.1854 | 45217710.9341 | 47384172.9925 | 46959100.8861 | 46028555.5192 | 47418976.2564 | 47826715.6264 | 48301818.0227 | 48473121.5748 | 48473121.5748 | 48473121.5748 | 48473121.5748 | 48473121.5748 | 48473121.5748 | 48473121.5748 | -4922981.4331 | -4089460.7671 | -3516415.3093 | -2526609.5186 | -1311058.5474 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 32684915.6062 | 36844759.7341 | 38513129.5168 | 37985378.5587 | 37003013.9911 | 37902256.6765 | 38235861.6156 | 38624581.758 | 38764739.2097 | 38764739.2097 | 38764739.2097 | 38764739.2097 | 38764739.2097 | 38764739.2097 | 38764739.2097 | -4922981.4331 | -4089460.7671 | -3516415.3093 | -2526609.5186 | -1311058.5474 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 32684915.6062 | 36761407.6675 | 38372472.9044 | 37745741.3673 | 36641821.7025 | 37409958.5332 | 37743563.4723 | 38132283.6147 | 38272441.0664 | 38272441.0664 | 38272441.0664 | 38272441.0664 | 38272441.0664 | 38272441.0664 | 38272441.0664 | -5415279.5764 | -4498406.8439 | -3868056.8403 | -2779270.4704 | -1442164.4022 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 3sens | 36316572.8958 | 41031235.3341 | 42948651.2546 | 42472239.7224 | 41515784.7552 | 42660616.4664 | 43031288.621 | 43463199.8904 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | -4922981.4331 | -4089460.7671 | -3516415.3093 | -2526609.5186 | -1311058.5474 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 3sens | 36316572.8958 | 41031235.3341 | 42948651.2546 | 42472239.7224 | 41515784.7552 | 42660616.4664 | 43031288.621 | 43463199.8904 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | -4922981.4331 | -4089460.7671 | -3516415.3093 | -2526609.5186 | -1311058.5474 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 3sens | 36316572.8958 | 41031235.3341 | 42948651.2546 | 42472239.7224 | 41515784.7552 | 42660616.4664 | 43031288.621 | 43463199.8904 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | 43618930.3922 | -4922981.4331 | -4089460.7671 | -3516415.3093 | -2526609.5186 | -1311058.5474 | 0 | 0 | 0 | 0 | 0

## Option4
Powercor
Regional and rural supply upgrades
OPTION 4 | Accelerated SWER upgrades
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| SWER upgrades |  | 15 | 2023-12-31 | 21500000 | 21500000 | 21500000 | 21500000 | 21500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 21500000 | 21500000 | 21500000 | 21500000 | 21500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 4974406.4937 | 5341268.6157 | 5544429.7412 | 5703083.1117 | 5734836.7765 | 5868885.9449 | 5959525.2533 | 6610675.6274 | 6679570.9754 | 6679570.9754 | 6679570.9754 | 6679570.9754 | 6679570.9754 | 6679570.9754 | 6679570.9754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 4974406.4937 | 5341268.6157 | 5544429.7412 | 5703083.1117 | 5734836.7765 | 5868885.9449 | 5959525.2533 | 6610675.6274 | 6679570.9754 | 6679570.9754 | 6679570.9754 | 6679570.9754 | 6679570.9754 | 6679570.9754 | 6679570.9754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 38955540.5474 | 44647448.1205 | 47145913.5861 | 47882684.6032 | 48323301.8923 | 50777735.3986 | 51464648.0368 | 52524003.512 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| SWER upgrades |  |  | 2023-12-31 | -21500000 | -21500000 | -21500000 | -21500000 | -21500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| SWER upgrades |  |  | 2023-12-31 | -21500000 | -43000000 | -64500000 | -86000000 | -107500000 | -107500000 | -107500000 | -107500000 | -107500000 | -107500000 | -107500000 | -107500000 | -107500000 | -107500000 | -107500000 | -86000000 | -64500000 | -43000000 | -21500000 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - SWER upgrades |  |  | 2023-12-31 | 0 | -1866738.9914 | -3733477.9827 | -5600216.9741 | -7466955.9655 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -7466955.9655 | -5600216.9741 | -3733477.9827 | -1866738.9914 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -1866738.9914 | -3733477.9827 | -5600216.9741 | -7466955.9655 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -7466955.9655 | -5600216.9741 | -3733477.9827 | -1866738.9914 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | -1866738.9914 | -3733477.9827 | -5600216.9741 | -7466955.9655 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -7466955.9655 | -5600216.9741 | -3733477.9827 | -1866738.9914 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 38955540.5474 | 44647448.1205 | 47145913.5861 | 47882684.6032 | 48323301.8923 | 50777735.3986 | 51464648.0368 | 52524003.512 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 38955540.5474 | 42780709.1291 | 43412435.6034 | 42282467.629 | 40856345.9268 | 41444040.4418 | 42130953.08 | 43190308.5551 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | -9333694.9568 | -7466955.9655 | -5600216.9741 | -3733477.9827 | -1866738.9914 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 38955540.5474 | 42780709.1291 | 43412435.6034 | 42282467.629 | 40856345.9268 | 41444040.4418 | 42130953.08 | 43190308.5551 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | -9333694.9568 | -7466955.9655 | -5600216.9741 | -3733477.9827 | -1866738.9914 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | -1866738.9914 | -3733477.9827 | -5600216.9741 | -7466955.9655 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -9333694.9568 | -7466955.9655 | -5600216.9741 | -3733477.9827 | -1866738.9914 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 38955540.5474 | 44647448.1205 | 47145913.5861 | 47882684.6032 | 48323301.8923 | 50777735.3986 | 51464648.0368 | 52524003.512 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 38955540.5474 | 42594035.23 | 43039087.8051 | 41722445.9316 | 40109650.3302 | 40510670.9461 | 41197583.5843 | 42256939.0594 | 42546313.3379 | 42546313.3379 | 42546313.3379 | 42546313.3379 | 42546313.3379 | 42546313.3379 | 42546313.3379 | -10267064.4525 | -8213651.562 | -6160238.6715 | -4106825.781 | -2053412.8905 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 38955540.5474 | 42967383.0282 | 43785783.4016 | 42842489.3265 | 41603041.5233 | 42377409.9374 | 43064322.5757 | 44123678.0508 | 44413052.3292 | 44413052.3292 | 44413052.3292 | 44413052.3292 | 44413052.3292 | 44413052.3292 | 44413052.3292 | -8400325.4612 | -6720260.3689 | -5040195.2767 | -3360130.1845 | -1680065.0922 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 42851094.6022 | 47245453.9411 | 48127026.962 | 47070736.0894 | 45688676.116 | 46521813.9816 | 47277417.8837 | 48442708.9063 | 48761020.6126 | 48761020.6126 | 48761020.6126 | 48761020.6126 | 48761020.6126 | 48761020.6126 | 48761020.6126 | -9333694.9568 | -7466955.9655 | -5600216.9741 | -3733477.9827 | -1866738.9914 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 35059986.4927 | 38315964.317 | 38697844.2447 | 37494199.1687 | 36024015.7376 | 36366266.9019 | 36984488.2763 | 37937908.2039 | 38198345.0545 | 38198345.0545 | 38198345.0545 | 38198345.0545 | 38198345.0545 | 38198345.0545 | 38198345.0545 | -9333694.9568 | -7466955.9655 | -5600216.9741 | -3733477.9827 | -1866738.9914 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 35059986.4927 | 38129290.4179 | 38324496.4465 | 36934177.4713 | 35277320.141 | 35432897.4062 | 36051118.7806 | 37004538.7082 | 37264975.5588 | 37264975.5588 | 37264975.5588 | 37264975.5588 | 37264975.5588 | 37264975.5588 | 37264975.5588 | -10267064.4525 | -8213651.562 | -6160238.6715 | -4106825.781 | -2053412.8905 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 38955540.5474 | 42780709.1291 | 43412435.6034 | 42282467.629 | 40856345.9268 | 41444040.4418 | 42130953.08 | 43190308.5551 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | -9333694.9568 | -7466955.9655 | -5600216.9741 | -3733477.9827 | -1866738.9914 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 38955540.5474 | 42780709.1291 | 43412435.6034 | 42282467.629 | 40856345.9268 | 41444040.4418 | 42130953.08 | 43190308.5551 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | -9333694.9568 | -7466955.9655 | -5600216.9741 | -3733477.9827 | -1866738.9914 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 38955540.5474 | 42780709.1291 | 43412435.6034 | 42282467.629 | 40856345.9268 | 41444040.4418 | 42130953.08 | 43190308.5551 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | 43479682.8336 | -9333694.9568 | -7466955.9655 | -5600216.9741 | -3733477.9827 | -1866738.9914 | 0 | 0 | 0 | 0 | 0

## Option5
Powercor
Regional and rural supply upgrades
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
Powercor
Regional and rural supply upgrades
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 726006024.6048 | 2026-06-30 |  | 48890193.6185 | 55633075.0339 | 58639749.433 | 59636278.5578 | 60161986.1662 | 63042741.27 | 63908088.6646 | 65811732.256 | 66210455.0541 | 66210455.0541 | 66210455.0541 | 66210455.0541 | 66210455.0541 | 66210455.0541 | 66210455.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 726006024.6048 | 2026-06-30 |  | 48890193.6185 | 55633075.0339 | 58639749.433 | 59636278.5578 | 60161986.1662 | 63042741.27 | 63908088.6646 | 65811732.256 | 66210455.0541 | 66210455.0541 | 66210455.0541 | 66210455.0541 | 66210455.0541 | 66210455.0541 | 66210455.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 171714133.2627 | 2026-06-30 |  | 11913801.5772 | 12538348.4705 | 12816088.8509 | 13440696.69 | 13694350.0026 | 13806108.3439 | 14399697.1199 | 16086832.9211 | 16367531.6291 | 16367531.6291 | 16367531.6291 | 16367531.6291 | 16367531.6291 | 16367531.6291 | 16367531.6291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Capital expenditure | Option 2Capital expenditure | -40385097.5492 | 2026-06-30 |  | -8792009.9067 | -8792009.9067 | -8792009.9067 | -8792009.9067 | -8792009.9067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 171714133.2627 | 2026-06-30 |  | 11913801.5772 | 12538348.4705 | 12816088.8509 | 13440696.69 | 13694350.0026 | 13806108.3439 | 14399697.1199 | 16086832.9211 | 16367531.6291 | 16367531.6291 | 16367531.6291 | 16367531.6291 | 16367531.6291 | 16367531.6291 | 16367531.6291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -40385097.5492 | 2026-06-30 |  | 0 | -763366.87 | -1526733.74 | -2290100.61 | -3053467.4801 | -3816834.3501 | -3816834.3501 | -3816834.3501 | -3816834.3501 | -3816834.3501 | -3816834.3501 | -3816834.3501 | -3816834.3501 | -3816834.3501 | -3816834.3501 | -3816834.3501 | -3053467.4801 | -2290100.61 | -1526733.74 | -763366.87 | 0 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 554291891.3422 | 2026-06-30 |  | 36976392.0413 | 43094726.5633 | 45823660.5821 | 46195581.8678 | 46467636.1636 | 49236632.9261 | 49508391.5448 | 49724899.3349 | 49842923.425 | 49842923.425 | 49842923.425 | 49842923.425 | 49842923.425 | 49842923.425 | 49842923.425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 36976392.0413 | 42331359.6933 | 44296926.8421 | 43905481.2578 | 43414168.6835 | 45419798.5761 | 45691557.1947 | 45908064.9848 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | -3816834.3501 | -3053467.4801 | -2290100.61 | -1526733.74 | -763366.87 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 513906793.793 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -40385097.5492 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 554291891.3422 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 126132180.8022 | 2026-06-30 |  | 8473020.3682 | 9041258.6423 | 9276267.0781 | 9701433.2399 | 9938789.629 | 10086353.4056 | 10539175.0718 | 11962139.1494 | 12187547.5025 | 12187547.5025 | 12187547.5025 | 12187547.5025 | 12187547.5025 | 12187547.5025 | 12187547.5025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Capital expenditure | Option 3Capital expenditure | -57327373.6519 | 2026-06-30 |  | -10683961.4056 | -7345223.4663 | -12687204.1691 | -15580777.0498 | -16804980.9609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 126132180.8022 | 2026-06-30 |  | 8473020.3682 | 9041258.6423 | 9276267.0781 | 9701433.2399 | 9938789.629 | 10086353.4056 | 10539175.0718 | 11962139.1494 | 12187547.5025 | 12187547.5025 | 12187547.5025 | 12187547.5025 | 12187547.5025 | 12187547.5025 | 12187547.5025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -57327373.6519 | 2026-06-30 |  | 0 | -927635.6901 | -1565385.2271 | -2666952.6092 | -4019754.6573 | -5478848.2949 | -5478848.2949 | -5478848.2949 | -5478848.2949 | -5478848.2949 | -5478848.2949 | -5478848.2949 | -5478848.2949 | -5478848.2949 | -5478848.2949 | -5478848.2949 | -4551212.6048 | -3913463.0678 | -2811895.6858 | -1459093.6376 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 599873843.8027 | 2026-06-30 |  | 40417173.2502 | 46591816.3915 | 49363482.3549 | 49934845.3179 | 50223196.5372 | 52956387.8644 | 53368913.5928 | 53849593.1067 | 54022907.5516 | 54022907.5516 | 54022907.5516 | 54022907.5516 | 54022907.5516 | 54022907.5516 | 54022907.5516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 40417173.2502 | 45664180.7014 | 47798097.1278 | 47267892.7087 | 46203441.8799 | 47477539.5694 | 47890065.2979 | 48370744.8117 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | -5478848.2949 | -4551212.6048 | -3913463.0678 | -2811895.6858 | -1459093.6376 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | 542546470.1508 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -57327373.6519 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 599873843.8027 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 79353476.7086 | 2026-06-30 |  | 5536079.8952 | 5944365.3904 | 6170465.9762 | 6347033.3185 | 6382372.3737 | 6531557.3885 | 6632431.0211 | 7357104.5071 | 7433779.0112 | 7433779.0112 | 7433779.0112 | 7433779.0112 | 7433779.0112 | 7433779.0112 | 7433779.0112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | -109908809.7857 | 2026-06-30 |  | -23927621.898 | -23927621.898 | -23927621.898 | -23927621.898 | -23927621.898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 79353476.7086 | 2026-06-30 |  | 5536079.8952 | 5944365.3904 | 6170465.9762 | 6347033.3185 | 6382372.3737 | 6531557.3885 | 6632431.0211 | 7357104.5071 | 7433779.0112 | 7433779.0112 | 7433779.0112 | 7433779.0112 | 7433779.0112 | 7433779.0112 | 7433779.0112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | -109908809.7857 | 2026-06-30 |  | 0 | -2077517.4311 | -4155034.8621 | -6232552.2932 | -8310069.7242 | -10387587.1553 | -10387587.1553 | -10387587.1553 | -10387587.1553 | -10387587.1553 | -10387587.1553 | -10387587.1553 | -10387587.1553 | -10387587.1553 | -10387587.1553 | -10387587.1553 | -8310069.7242 | -6232552.2932 | -4155034.8621 | -2077517.4311 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 646652547.8962 | 2026-06-30 |  | 43354113.7232 | 49688709.6435 | 52469283.4568 | 53289245.2392 | 53779613.7925 | 56511183.8815 | 57275657.6436 | 58454627.7489 | 58776676.0429 | 58776676.0429 | 58776676.0429 | 58776676.0429 | 58776676.0429 | 58776676.0429 | 58776676.0429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 43354113.7232 | 47611192.2124 | 48314248.5947 | 47056692.9461 | 45469544.0683 | 46123596.7262 | 46888070.4883 | 48067040.5936 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | -10387587.1553 | -8310069.7242 | -6232552.2932 | -4155034.8621 | -2077517.4311 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 536743738.1105 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | -109908809.7857 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 646652547.8962 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 3 | Annualised capex | -1 |  |  | Option 3 annualised capex | 5.4788 | 5.4788 | 5.4788 | 5.4788 | 5.4788 | 5.4788 | 5.4788 | 5.4788 | 5.4788 | 5.4788 | 5.4788 | 5.4788 | 5.4788 | 5.4788 | 5.4788 | 5.4788 | 4.5512 | 3.9135 | 2.8119 | 1.4591 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 48.8902 | 55.6331 | 58.6397 | 59.6363 | 60.162 | 63.0427 | 63.9081 | 65.8117 | 66.2105 | 66.2105 | 66.2105 | 66.2105 | 66.2105 | 66.2105 | 66.2105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 0 |  |  | Energy at risk energy at risk (weighted) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Energy at risk value | #N/A |  |  | Option 1 (base case) risk cost | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## Sensitivity_calcs
Powercor
Regional and rural supply upgrades
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
[7 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | -1526733.74 | -763366.87 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 513906793.793 |  | 0 | 36976392.0413 | 42331359.6933 | 44296926.8421 | 43905481.2578 | 43414168.6835 | 45419798.5761 | 45691557.1947 | 45908064.9848 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | -3816834.3501 | -3053467.4801 | -2290100.61 | -1526733.74 | -763366.87 | 0 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 509868284.0381 |  | 0 | 36976392.0413 | 42255023.0063 | 44144253.4681 | 43676471.1968 | 43108821.9355 | 45038115.1411 | 45309873.7597 | 45526381.5498 | 45644405.6399 | 45644405.6399 | 45644405.6399 | 45644405.6399 | 45644405.6399 | 45644405.6399 | 45644405.6399 | -4198517.7851 | -3358814.2281 | -2519110.6711 | -1679407.114 | -839703.557 | 0 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 517945303.5479 |  | 0 | 36976392.0413 | 42407696.3803 | 44449600.2161 | 44134491.3188 | 43719515.4315 | 45801482.0111 | 46073240.6297 | 46289748.4198 | 46407772.51 | 46407772.51 | 46407772.51 | 46407772.51 | 46407772.51 | 46407772.51 | 46407772.51 | -3435150.9151 | -2748120.7321 | -2061090.549 | -1374060.366 | -687030.183 | 0 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 569335982.9272 |  | 0 | 40674031.2454 | 46640832.3496 | 48879292.9003 | 48525039.4446 | 48060932.2999 | 50343461.8687 | 50642396.3492 | 50880554.9183 | 51010381.4174 | 51010381.4174 | 51010381.4174 | 51010381.4174 | 51010381.4174 | 51010381.4174 | 51010381.4174 | -3816834.3501 | -3053467.4801 | -2290100.61 | -1526733.74 | -763366.87 | 0 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 458477604.6588 |  | 0 | 33278752.8372 | 38021887.037 | 39714560.7839 | 39285923.071 | 38767405.0672 | 40496135.2835 | 40740718.0402 | 40935575.0513 | 41041796.7324 | 41041796.7324 | 41041796.7324 | 41041796.7324 | 41041796.7324 | 41041796.7324 | 41041796.7324 | -3816834.3501 | -3053467.4801 | -2290100.61 | -1526733.74 | -763366.87 | 0 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 454439094.9039 |  | 0 | 33278752.8372 | 37945550.35 | 39561887.4099 | 39056913.01 | 38462058.3192 | 40114451.8484 | 40359034.6052 | 40553891.6163 | 40660113.2974 | 40660113.2974 | 40660113.2974 | 40660113.2974 | 40660113.2974 | 40660113.2974 | 40660113.2974 | -4198517.7851 | -3358814.2281 | -2519110.6711 | -1679407.114 | -839703.557 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 513906793.793 |  | 0 | 36976392.0413 | 42331359.6933 | 44296926.8421 | 43905481.2578 | 43414168.6835 | 45419798.5761 | 45691557.1947 | 45908064.9848 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | -3816834.3501 | -3053467.4801 | -2290100.61 | -1526733.74 | -763366.87 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 513906793.793 |  | 0 | 36976392.0413 | 42331359.6933 | 44296926.8421 | 43905481.2578 | 43414168.6835 | 45419798.5761 | 45691557.1947 | 45908064.9848 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | -3816834.3501 | -3053467.4801 | -2290100.61 | -1526733.74 | -763366.87 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 513906793.793 |  | 0 | 36976392.0413 | 42331359.6933 | 44296926.8421 | 43905481.2578 | 43414168.6835 | 45419798.5761 | 45691557.1947 | 45908064.9848 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | 46026089.0749 | -3816834.3501 | -3053467.4801 | -2290100.61 | -1526733.74 | -763366.87 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 40417173.2502 | 45664180.7014 | 47798097.1278 | 47267892.7087 | 46203441.8799 | 47477539.5694 | 47890065.2979 | 48370744.8117 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | -5478848.2949 | -4551212.6048 | -3913463.0678 | -2811895.6858 | -1459093.6376 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 542546470.1508 |  | 0 | 40417173.2502 | 45664180.7014 | 47798097.1278 | 47267892.7087 | 46203441.8799 | 47477539.5694 | 47890065.2979 | 48370744.8117 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | -5478848.2949 | -4551212.6048 | -3913463.0678 | -2811895.6858 | -1459093.6376 | 0 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 536813732.7856 |  | 0 | 40417173.2502 | 45571417.1324 | 47641558.6051 | 47001197.4478 | 45801466.4142 | 46929654.7399 | 47342180.4684 | 47822859.9822 | 47996174.4272 | 47996174.4272 | 47996174.4272 | 47996174.4272 | 47996174.4272 | 47996174.4272 | 47996174.4272 | -6026733.1244 | -5006333.8653 | -4304809.3746 | -3093085.2543 | -1605003.0014 | 0 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 548279207.516 |  | 0 | 40417173.2502 | 45756944.2704 | 47954635.6505 | 47534587.9696 | 46605417.3457 | 48025424.3989 | 48437950.1274 | 48918629.6412 | 49091944.0862 | 49091944.0862 | 49091944.0862 | 49091944.0862 | 49091944.0862 | 49091944.0862 | 49091944.0862 | -4930963.4654 | -4096091.3443 | -3522116.761 | -2530706.1172 | -1313184.2739 | 0 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 602533854.531 |  | 0 | 44458890.5753 | 50323362.3405 | 52734445.3633 | 52261377.2405 | 51225761.5336 | 52773178.3559 | 53226956.6572 | 53755704.1224 | 53946350.0119 | 53946350.0119 | 53946350.0119 | 53946350.0119 | 53946350.0119 | 53946350.0119 | 53946350.0119 | -5478848.2949 | -4551212.6048 | -3913463.0678 | -2811895.6858 | -1459093.6376 | 0 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | 482559085.7705 |  | 0 | 36375455.9252 | 41004999.0622 | 42861748.8923 | 42274408.1769 | 41181122.2262 | 42181900.783 | 42553173.9386 | 42985785.5011 | 43141768.5015 | 43141768.5015 | 43141768.5015 | 43141768.5015 | 43141768.5015 | 43141768.5015 | 43141768.5015 | -5478848.2949 | -4551212.6048 | -3913463.0678 | -2811895.6858 | -1459093.6376 | 0 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | 476826348.4053 |  | 0 | 36375455.9252 | 40912235.4932 | 42705210.3696 | 42007712.916 | 40779146.7605 | 41634015.9535 | 42005289.1091 | 42437900.6716 | 42593883.672 | 42593883.672 | 42593883.672 | 42593883.672 | 42593883.672 | 42593883.672 | 42593883.672 | -6026733.1244 | -5006333.8653 | -4304809.3746 | -3093085.2543 | -1605003.0014 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 542546470.1508 |  | 0 | 40417173.2502 | 45664180.7014 | 47798097.1278 | 47267892.7087 | 46203441.8799 | 47477539.5694 | 47890065.2979 | 48370744.8117 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | -5478848.2949 | -4551212.6048 | -3913463.0678 | -2811895.6858 | -1459093.6376 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 542546470.1508 |  | 0 | 40417173.2502 | 45664180.7014 | 47798097.1278 | 47267892.7087 | 46203441.8799 | 47477539.5694 | 47890065.2979 | 48370744.8117 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | -5478848.2949 | -4551212.6048 | -3913463.0678 | -2811895.6858 | -1459093.6376 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 542546470.1508 |  | 0 | 40417173.2502 | 45664180.7014 | 47798097.1278 | 47267892.7087 | 46203441.8799 | 47477539.5694 | 47890065.2979 | 48370744.8117 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | 48544059.2567 | -5478848.2949 | -4551212.6048 | -3913463.0678 | -2811895.6858 | -1459093.6376 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 536743738.1105 |  | 0 | 43354113.7232 | 47611192.2124 | 48314248.5947 | 47056692.9461 | 45469544.0683 | 46123596.7262 | 46888070.4883 | 48067040.5936 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | -10387587.1553 | -8310069.7242 | -6232552.2932 | -4155034.8621 | -2077517.4311 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 525752857.132 |  | 0 | 43354113.7232 | 47403440.4693 | 47898745.1085 | 46433437.7168 | 44638537.0959 | 45084838.0107 | 45849311.7728 | 47028281.8781 | 47350330.1721 | 47350330.1721 | 47350330.1721 | 47350330.1721 | 47350330.1721 | 47350330.1721 | 47350330.1721 | -11426345.8708 | -9141076.6966 | -6855807.5225 | -4570538.3483 | -2285269.1742 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 547734619.0891 |  | 0 | 43354113.7232 | 47818943.9555 | 48729752.0809 | 47679948.1754 | 46300551.0407 | 47162355.4418 | 47926829.2038 | 49105799.3091 | 49427847.6032 | 49427847.6032 | 49427847.6032 | 49427847.6032 | 49427847.6032 | 49427847.6032 | 49427847.6032 | -9348828.4397 | -7479062.7518 | -5609297.0638 | -3739531.3759 | -1869765.6879 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 601408992.9002 |  | 0 | 47689525.0956 | 52580063.1768 | 53561176.9404 | 52385617.47 | 50847505.4475 | 51774715.1144 | 52615636.2527 | 53912503.3685 | 54266756.4919 | 54266756.4919 | 54266756.4919 | 54266756.4919 | 54266756.4919 | 54266756.4919 | 54266756.4919 | -10387587.1553 | -8310069.7242 | -6232552.2932 | -4155034.8621 | -2077517.4311 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 472078483.3209 |  | 0 | 39018702.3509 | 42642321.2481 | 43067320.249 | 41727768.4221 | 40091582.689 | 40472478.3381 | 41160504.7239 | 42221577.8187 | 42511421.2834 | 42511421.2834 | 42511421.2834 | 42511421.2834 | 42511421.2834 | 42511421.2834 | 42511421.2834 | -10387587.1553 | -8310069.7242 | -6232552.2932 | -4155034.8621 | -2077517.4311 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 461087602.3423 |  | 0 | 39018702.3509 | 42434569.505 | 42651816.7628 | 41104513.1928 | 39260575.7166 | 39433719.6226 | 40121746.0084 | 41182819.1032 | 41472662.5678 | 41472662.5678 | 41472662.5678 | 41472662.5678 | 41472662.5678 | 41472662.5678 | 41472662.5678 | -11426345.8708 | -9141076.6966 | -6855807.5225 | -4570538.3483 | -2285269.1742 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 536743738.1105 |  | 0 | 43354113.7232 | 47611192.2124 | 48314248.5947 | 47056692.9461 | 45469544.0683 | 46123596.7262 | 46888070.4883 | 48067040.5936 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | -10387587.1553 | -8310069.7242 | -6232552.2932 | -4155034.8621 | -2077517.4311 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 536743738.1105 |  | 0 | 43354113.7232 | 47611192.2124 | 48314248.5947 | 47056692.9461 | 45469544.0683 | 46123596.7262 | 46888070.4883 | 48067040.5936 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | -10387587.1553 | -8310069.7242 | -6232552.2932 | -4155034.8621 | -2077517.4311 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 536743738.1105 |  | 0 | 43354113.7232 | 47611192.2124 | 48314248.5947 | 47056692.9461 | 45469544.0683 | 46123596.7262 | 46888070.4883 | 48067040.5936 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | 48389088.8877 | -10387587.1553 | -8310069.7242 | -6232552.2932 | -4155034.8621 | -2077517.4311 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 0 | 1 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 513.9068 | 542.5465 | 536.7437 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens1 | Capex 10% higher | 0 | 509.8683 | 536.8137 | 525.7529 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens2 | Capex 10% lower | 0 | 517.9453 | 548.2792 | 547.7346 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens3 | Total benefits 10% higher | 0 | 569.336 | 602.5339 | 601.409 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens4 | Total benefits 10% lower | 0 | 458.4776 | 482.5591 | 472.0785 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 454.4391 | 476.8263 | 461.0876 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Workings_costs
Powercor
Regional and rural supply upgrades
WORKINGS - RISKS
|  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
| Option 2 | Capex | 7900000 | 7900000 | 7900000 | 7900000 | 7900000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option 3 | Capex | 9600000 | 6600000 | 11400000 | 14000000 | 15100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option 4 | Capex | 21500000 | 21500000 | 21500000 | 21500000 | 21500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## BaseCase_risk
Powercor
Regional and rural supply upgrades
RISK DATA
| iso_gis_id | Year | feeder | total_export_risk_kwh | total_export_risk_cost | total_import_risk_kwh | total_import_risk_cost | total_risk_kwh | agg_bushfire_risk | total_risk_cost
| 20090442 | 2028 | ART023 | 0 | 0 | 3208.8873 | 140212.9473 | 3208.8873 | 214.0202 | 140426.9675
| 20090442 | 2029 | ART023 | 0 | 0 | 3184.5956 | 139151.517 | 3184.5956 | 214.0202 | 139365.5372
| 20090442 | 2030 | ART023 | 0 | 0 | 3093.3982 | 135166.6287 | 3093.3982 | 214.0202 | 135380.6488
| 20090442 | 2031 | ART023 | 0 | 0 | 2978.9596 | 130166.2151 | 2978.9596 | 214.0202 | 130380.2353
| 20090442 | 2032 | ART023 | 0 | 0 | 2970.8094 | 129810.0877 | 2970.8094 | 214.0202 | 130024.1079
| 20090442 | 2033 | ART023 | 0 | 0 | 2939.5732 | 128445.2176 | 2939.5732 | 214.0202 | 128659.2377
| 20090442 | 2034 | ART023 | 0 | 0 | 2939.5732 | 128445.2176 | 2939.5732 | 214.0202 | 128659.2377
| 20090768 | 2023 | ART023 | 75.9851 | 0 | 678.7116 | 29656.4348 | 754.6967 | 3250.3038 | 32906.7387
| 20090768 | 2024 | ART023 | 2900.1079 | 61.7256 | 843.3666 | 36851.0653 | 3743.4745 | 3250.3038 | 40163.0948
| 20090768 | 2025 | ART023 | 4944.2009 | 92.6123 | 741.8501 | 32415.281 | 5686.051 | 3250.3038 | 35758.1971
| 20090768 | 2026 | ART023 | 10199.2469 | 94.3741 | 584.73 | 25549.8881 | 10783.9768 | 3250.3038 | 28894.5661
| 20090768 | 2027 | ART023 | 16301.4666 | 148.2687 | 545.6937 | 23844.1908 | 16847.1603 | 3250.3038 | 27242.7632
| 20090768 | 2028 | ART023 | 33158.791 | 323.7662 | 467.1784 | 20413.452 | 33625.9695 | 3250.3038 | 23987.522
| 20090768 | 2029 | ART023 | 37120.5737 | 296.5857 | 415.7118 | 18164.6077 | 37536.2855 | 3250.3038 | 21711.4972
| 20090768 | 2030 | ART023 | 48257.1091 | 438.1438 | 444.928 | 19441.2135 | 48702.0371 | 3250.3038 | 23129.6612
| 20090768 | 2031 | ART023 | 57213.2093 | 750.0878 | 394.7544 | 17248.8687 | 57607.9636 | 3250.3038 | 21249.2603
| 20090768 | 2032 | ART023 | 73355.8164 | 1309.1235 | 452.2508 | 19761.1877 | 73808.0672 | 3250.3038 | 24320.615
| 20090768 | 2033 | ART023 | 98585.9055 | 3360.2077 | 527.3861 | 23044.238 | 99113.2916 | 3250.3038 | 29654.7496
| 20090768 | 2034 | ART023 | 98585.9055 | 3360.2077 | 527.3861 | 23044.238 | 99113.2916 | 3250.3038 | 29654.7496
| 20108607 | 2023 | ART023 | 0 | 0 | 151.2784 | 6610.1376 | 151.2784 | 1834.477 | 8444.6147
| 20108607 | 2024 | ART023 | 0 | 0 | 166.2602 | 7264.7708 | 166.2602 | 1834.477 | 9099.2479
| 20108607 | 2025 | ART023 | 0 | 0 | 163.4139 | 7140.4001 | 163.4139 | 1834.477 | 8974.8771
| 20108607 | 2026 | ART023 | 0 | 0 | 149.0928 | 6514.6375 | 149.0928 | 1834.477 | 8349.1145
| 20108607 | 2027 | ART023 | 0 | 0 | 143.8125 | 6283.9139 | 143.8125 | 1834.477 | 8118.3909
| 20108607 | 2028 | ART023 | 0 | 0 | 155.728 | 6804.5646 | 155.728 | 1834.477 | 8639.0416
| 20108607 | 2029 | ART023 | 0 | 0 | 155.2722 | 6784.6477 | 155.2722 | 1834.477 | 8619.1247
| 20108607 | 2030 | ART023 | 0 | 0 | 147.9358 | 6464.0821 | 147.9358 | 1834.477 | 8298.5591
| 20108607 | 2031 | ART023 | 0 | 0 | 141.4988 | 6182.8188 | 141.4988 | 1834.477 | 8017.2958
| 20108607 | 2032 | ART023 | 0 | 0 | 147.9533 | 6464.8479 | 147.9533 | 1834.477 | 8299.3249
| 20108607 | 2033 | ART023 | 0 | 0 | 150.8124 | 6589.7768 | 150.8124 | 1834.477 | 8424.2538
| 20108607 | 2034 | ART023 | 0 | 0 | 150.8124 | 6589.7768 | 150.8124 | 1834.477 | 8424.2538
| 20106367 | 2023 | ART033 | 0 | 0 | 3.669 | 160.3166 | 3.669 | 540.7525 | 701.0691
| 20106367 | 2024 | ART033 | 0 | 0 | 3.8902 | 169.9837 | 3.8902 | 540.7525 | 710.7361
| 20106367 | 2025 | ART033 | 0 | 0 | 3.9145 | 171.043 | 3.9145 | 540.7525 | 711.7954
| 20106367 | 2026 | ART033 | 0 | 0 | 3.5554 | 155.3551 | 3.5554 | 540.7525 | 696.1076
| 20106367 | 2027 | ART033 | 0 | 0 | 3.5554 | 155.3551 | 3.5554 | 540.7525 | 696.1076
| 20106367 | 2028 | ART033 | 0 | 0 | 3.5554 | 155.3551 | 3.5554 | 540.7525 | 696.1076
| 20106367 | 2029 | ART033 | 0 | 0 | 3.5554 | 155.3551 | 3.5554 | 540.7525 | 696.1076
| 20106367 | 2030 | ART033 | 0 | 0 | 3.5554 | 155.3551 | 3.5554 | 540.7525 | 696.1076
| 20106367 | 2031 | ART033 | 0 | 0 | 3.5554 | 155.3551 | 3.5554 | 540.7525 | 696.1076
| 20106367 | 2032 | ART033 | 0 | 0 | 3.5554 | 155.3551 | 3.5554 | 540.7525 | 696.1076
| 20106367 | 2033 | ART033 | 0 | 0 | 3.5554 | 155.3551 | 3.5554 | 540.7525 | 696.1076
| 20106367 | 2034 | ART033 | 0 | 0 | 3.5554 | 155.3551 | 3.5554 | 540.7525 | 696.1076
| 20107962 | 2023 | ART033 | 1182.6348 | 0 | 10.5728 | 461.9812 | 1193.2076 | 1157.5203 | 1619.5015
| 20107962 | 2024 | ART033 | 1331.8609 | 28.1963 | 13.0328 | 569.4701 | 1344.8937 | 1157.5203 | 1755.1867
| 20107962 | 2025 | ART033 | 1325.8432 | 25.0099 | 12.9654 | 566.5257 | 1338.8086 | 1157.5203 | 1749.0559
| 20107962 | 2026 | ART033 | 1215.5665 | 10.2821 | 11.7273 | 512.4266 | 1227.2938 | 1157.5203 | 1680.229
| 20107962 | 2027 | ART033 | 1215.5665 | 10.2821 | 11.7273 | 512.4266 | 1227.2938 | 1157.5203 | 1680.229
| 20107962 | 2028 | ART033 | 1215.5665 | 10.2821 | 11.7273 | 512.4266 | 1227.2938 | 1157.5203 | 1680.229
| 20107962 | 2029 | ART033 | 1215.5665 | 10.2821 | 11.7273 | 512.4266 | 1227.2938 | 1157.5203 | 1680.229
| 20107962 | 2030 | ART033 | 1215.5665 | 10.2821 | 11.7273 | 512.4266 | 1227.2938 | 1157.5203 | 1680.229
| 20107962 | 2031 | ART033 | 1215.5665 | 10.2821 | 11.7273 | 512.4266 | 1227.2938 | 1157.5203 | 1680.229
| 20107962 | 2032 | ART033 | 1215.5665 | 10.2821 | 11.7273 | 512.4266 | 1227.2938 | 1157.5203 | 1680.229
| 20107962 | 2033 | ART033 | 1215.5665 | 10.2821 | 11.7273 | 512.4266 | 1227.2938 | 1157.5203 | 1680.229
| 20107962 | 2034 | ART033 | 1215.5665 | 10.2821 | 11.7273 | 512.4266 | 1227.2938 | 1157.5203 | 1680.229
| 20108504 | 2023 | ART033 | 0 | 0 | 23556.6229 | 1029311.1702 | 23556.6229 | 2203.1165 | 1031514.2866
| 20108504 | 2024 | ART033 | 0 | 0 | 24520.3826 | 1071422.8399 | 24520.3826 | 2203.1165 | 1073625.9563
| 20108504 | 2025 | ART033 | 0 | 0 | 24385.2782 | 1065519.4237 | 24385.2782 | 2203.1165 | 1067722.5402
| 20108504 | 2026 | ART033 | 0 | 0 | 23303.7935 | 1018263.742 | 23303.7935 | 2203.1165 | 1020466.8584
| 20108504 | 2027 | ART033 | 0 | 0 | 23303.7935 | 1018263.742 | 23303.7935 | 2203.1165 | 1020466.8584
| 20108504 | 2028 | ART033 | 0 | 0 | 23303.7935 | 1018263.742 | 23303.7935 | 2203.1165 | 1020466.8584
| 20108504 | 2029 | ART033 | 0 | 0 | 23303.7935 | 1018263.742 | 23303.7935 | 2203.1165 | 1020466.8584
| 20108504 | 2030 | ART033 | 0 | 0 | 23303.7935 | 1018263.742 | 23303.7935 | 2203.1165 | 1020466.8584
| 20108504 | 2031 | ART033 | 0 | 0 | 23303.7935 | 1018263.742 | 23303.7935 | 2203.1165 | 1020466.8584
| 20108504 | 2032 | ART033 | 0 | 0 | 23303.7935 | 1018263.742 | 23303.7935 | 2203.1165 | 1020466.8584
| 20108504 | 2033 | ART033 | 0 | 0 | 23303.7935 | 1018263.742 | 23303.7935 | 2203.1165 | 1020466.8584
| 20108504 | 2034 | ART033 | 0 | 0 | 23303.7935 | 1018263.742 | 23303.7935 | 2203.1165 | 1020466.8584
| 20151196 | 2023 | ART033 | 0 | 0 | 26.1682 | 1143.4261 | 26.1682 | 751.8491 | 1895.2751
| 20151196 | 2024 | ART033 | 0 | 0 | 26.1332 | 1141.8934 | 26.1332 | 751.8491 | 1893.7424
| 20151196 | 2025 | ART033 | 0 | 0 | 34.8199 | 1521.4612 | 34.8199 | 751.8491 | 2273.3102
| 20151196 | 2026 | ART033 | 0 | 0 | 33.3621 | 1457.7619 | 33.3621 | 751.8491 | 2209.611
| 20151196 | 2027 | ART033 | 0 | 0 | 33.3621 | 1457.7619 | 33.3621 | 751.8491 | 2209.611
| 20151196 | 2028 | ART033 | 0 | 0 | 33.3621 | 1457.7619 | 33.3621 | 751.8491 | 2209.611
| 20151196 | 2029 | ART033 | 0 | 0 | 33.3621 | 1457.7619 | 33.3621 | 751.8491 | 2209.611
| 20151196 | 2030 | ART033 | 0 | 0 | 33.3621 | 1457.7619 | 33.3621 | 751.8491 | 2209.611
| 20151196 | 2031 | ART033 | 0 | 0 | 33.3621 | 1457.7619 | 33.3621 | 751.8491 | 2209.611
| 20151196 | 2032 | ART033 | 0 | 0 | 33.3621 | 1457.7619 | 33.3621 | 751.8491 | 2209.611
| 20151196 | 2033 | ART033 | 0 | 0 | 33.3621 | 1457.7619 | 33.3621 | 751.8491 | 2209.611
| 20151196 | 2034 | ART033 | 0 | 0 | 33.3621 | 1457.7619 | 33.3621 | 751.8491 | 2209.611
| 20154279 | 2023 | ART033 | 0 | 0 | 0 | 0 | 0 | 562.109 | 562.109
| 20154279 | 2024 | ART033 | 0 | 0 | 0 | 0 | 0 | 562.109 | 562.109
| 20154279 | 2025 | ART033 | 0 | 0 | 0 | 0 | 0 | 562.109 | 562.109
| 20154279 | 2026 | ART033 | 0 | 0 | 0 | 0 | 0 | 562.109 | 562.109
| 20154279 | 2027 | ART033 | 0 | 0 | 0 | 0 | 0 | 562.109 | 562.109
| 20154279 | 2028 | ART033 | 0 | 0 | 0 | 0 | 0 | 562.109 | 562.109
| 20154279 | 2029 | ART033 | 0 | 0 | 0 | 0 | 0 | 562.109 | 562.109
| 20154279 | 2030 | ART033 | 0 | 0 | 0 | 0 | 0 | 562.109 | 562.109
| 20154279 | 2031 | ART033 | 0 | 0 | 0 | 0 | 0 | 562.109 | 562.109
| 20154279 | 2032 | ART033 | 0 | 0 | 0 | 0 | 0 | 562.109 | 562.109
| 20154279 | 2033 | ART033 | 0 | 0 | 0 | 0 | 0 | 562.109 | 562.109
| 20154279 | 2034 | ART033 | 0 | 0 | 0 | 0 | 0 | 562.109 | 562.109
| 20155756 | 2023 | ART033 | 0 | 0 | 2.978 | 130.1233 | 2.978 | 1957.8728 | 2087.9961
| 20155756 | 2024 | ART033 | 0 | 0 | 5.2316 | 228.5955 | 5.2316 | 1957.8728 | 2186.4682
| 20155756 | 2025 | ART033 | 0 | 0 | 4.0084 | 175.1485 | 4.0084 | 1957.8728 | 2133.0212
| 20155756 | 2026 | ART033 | 0 | 0 | 3.7409 | 163.4575 | 3.7409 | 1957.8728 | 2121.3303
| 20155756 | 2027 | ART033 | 0 | 0 | 3.7409 | 163.4575 | 3.7409 | 1957.8728 | 2121.3303
| 20155756 | 2028 | ART033 | 0 | 0 | 3.7409 | 163.4575 | 3.7409 | 1957.8728 | 2121.3303
| 20155756 | 2029 | ART033 | 0 | 0 | 3.7409 | 163.4575 | 3.7409 | 1957.8728 | 2121.3303
| 20155756 | 2030 | ART033 | 0 | 0 | 3.7409 | 163.4575 | 3.7409 | 1957.8728 | 2121.3303
| 20155756 | 2031 | ART033 | 0 | 0 | 3.7409 | 163.4575 | 3.7409 | 1957.8728 | 2121.3303
| 20155756 | 2032 | ART033 | 0 | 0 | 3.7409 | 163.4575 | 3.7409 | 1957.8728 | 2121.3303
| 20155756 | 2033 | ART033 | 0 | 0 | 3.7409 | 163.4575 | 3.7409 | 1957.8728 | 2121.3303
| 20155756 | 2034 | ART033 | 0 | 0 | 3.7409 | 163.4575 | 3.7409 | 1957.8728 | 2121.3303
| 20158553 | 2023 | ART033 | 0 | 0 | 0 | 0 | 0 | 861.4013 | 861.4013
| 20158553 | 2024 | ART033 | 0 | 0 | 0 | 0 | 0 | 861.4013 | 861.4013
| 20158553 | 2025 | ART033 | 0 | 0 | 0 | 0 | 0 | 861.4013 | 861.4013
| 20158553 | 2026 | ART033 | 0 | 0 | 0 | 0 | 0 | 861.4013 | 861.4013
| 20158553 | 2027 | ART033 | 0 | 0 | 0 | 0 | 0 | 861.4013 | 861.4013
| 20158553 | 2028 | ART033 | 0 | 0 | 0 | 0 | 0 | 861.4013 | 861.4013
| 20158553 | 2029 | ART033 | 0 | 0 | 0 | 0 | 0 | 861.4013 | 861.4013
| 20158553 | 2030 | ART033 | 0 | 0 | 0 | 0 | 0 | 861.4013 | 861.4013
| 20158553 | 2031 | ART033 | 0 | 0 | 0 | 0 | 0 | 861.4013 | 861.4013
| 20158553 | 2032 | ART033 | 0 | 0 | 0 | 0 | 0 | 861.4013 | 861.4013
| 20158553 | 2033 | ART033 | 0 | 0 | 0 | 0 | 0 | 861.4013 | 861.4013
| 20158553 | 2034 | ART033 | 0 | 0 | 0 | 0 | 0 | 861.4013 | 861.4013
| 20173929 | 2023 | ART033 | 0 | 0 | 40.9931 | 1791.2034 | 40.9931 | 820.9654 | 2612.1688
| 20173929 | 2024 | ART033 | 0 | 0 | 46.3345 | 2024.5941 | 46.3345 | 820.9654 | 2845.5595
| 20173929 | 2025 | ART033 | 0 | 0 | 43.7286 | 1910.7307 | 43.7286 | 820.9654 | 2731.6961
| 20173929 | 2026 | ART033 | 0 | 0 | 37.9437 | 1657.9593 | 37.9437 | 820.9654 | 2478.9247
| 20173929 | 2027 | ART033 | 0 | 0 | 37.9437 | 1657.9593 | 37.9437 | 820.9654 | 2478.9247
| 20173929 | 2028 | ART033 | 0 | 0 | 37.9437 | 1657.9593 | 37.9437 | 820.9654 | 2478.9247
| 20173929 | 2029 | ART033 | 0 | 0 | 37.9437 | 1657.9593 | 37.9437 | 820.9654 | 2478.9247
| 20173929 | 2030 | ART033 | 0 | 0 | 37.9437 | 1657.9593 | 37.9437 | 820.9654 | 2478.9247
| 20173929 | 2031 | ART033 | 0 | 0 | 37.9437 | 1657.9593 | 37.9437 | 820.9654 | 2478.9247
| 20173929 | 2032 | ART033 | 0 | 0 | 37.9437 | 1657.9593 | 37.9437 | 820.9654 | 2478.9247
| 20173929 | 2033 | ART033 | 0 | 0 | 37.9437 | 1657.9593 | 37.9437 | 820.9654 | 2478.9247
| 20173929 | 2034 | ART033 | 0 | 0 | 37.9437 | 1657.9593 | 37.9437 | 820.9654 | 2478.9247
| 20174332 | 2023 | ART033 | 0 | 0 | 0.80835 | 35.3212 | 0.80835 | 388.7744 | 424.0956
| 20174332 | 2024 | ART033 | 0 | 0 | 0.6773 | 29.5947 | 0.6773 | 388.7744 | 418.3691
| 20174332 | 2025 | ART033 | 0 | 0 | 0.75532 | 33.004 | 0.75532 | 388.7744 | 421.7784
| 20174332 | 2026 | ART033 | 0 | 0 | 0.53149 | 23.2235 | 0.53149 | 388.7744 | 411.998
| 20174332 | 2027 | ART033 | 0 | 0 | 0.53149 | 23.2235 | 0.53149 | 388.7744 | 411.998
| 20174332 | 2028 | ART033 | 0 | 0 | 0.53149 | 23.2235 | 0.53149 | 388.7744 | 411.998
| 20174332 | 2029 | ART033 | 0 | 0 | 0.53149 | 23.2235 | 0.53149 | 388.7744 | 411.998
| 20174332 | 2030 | ART033 | 0 | 0 | 0.53149 | 23.2235 | 0.53149 | 388.7744 | 411.998
| 20174332 | 2031 | ART033 | 0 | 0 | 0.53149 | 23.2235 | 0.53149 | 388.7744 | 411.998
| 20174332 | 2032 | ART033 | 0 | 0 | 0.53149 | 23.2235 | 0.53149 | 388.7744 | 411.998
| 20174332 | 2033 | ART033 | 0 | 0 | 0.53149 | 23.2235 | 0.53149 | 388.7744 | 411.998
| 20174332 | 2034 | ART033 | 0 | 0 | 0.53149 | 23.2235 | 0.53149 | 388.7744 | 411.998
| 20495755 | 2023 | ART033 | 0 | 0 | 10429.7977 | 455732.0176 | 10429.7977 | 3115.3797 | 458847.3973
| 20495755 | 2024 | ART033 | 0 | 0 | 10954.6692 | 478666.3794 | 10954.6692 | 3115.3797 | 481781.7591
| 20495755 | 2025 | ART033 | 0 | 0 | 10522.8145 | 459796.4072 | 10522.8145 | 3115.3797 | 462911.7869
| 20495755 | 2026 | ART033 | 0 | 0 | 12338.9449 | 539152.5748 | 12338.9449 | 3115.3797 | 542267.9545
| 20495755 | 2027 | ART033 | 0 | 0 | 12338.9449 | 539152.5748 | 12338.9449 | 3115.3797 | 542267.9545
| 20495755 | 2028 | ART033 | 0 | 0 | 12338.9449 | 539152.5748 | 12338.9449 | 3115.3797 | 542267.9545
| 20495755 | 2029 | ART033 | 0 | 0 | 12338.9449 | 539152.5748 | 12338.9449 | 3115.3797 | 542267.9545
| 20495755 | 2030 | ART033 | 0 | 0 | 12338.9449 | 539152.5748 | 12338.9449 | 3115.3797 | 542267.9545
| 20495755 | 2031 | ART033 | 0 | 0 | 12338.9449 | 539152.5748 | 12338.9449 | 3115.3797 | 542267.9545
| 20495755 | 2032 | ART033 | 0 | 0 | 12338.9449 | 539152.5748 | 12338.9449 | 3115.3797 | 542267.9545
| 20495755 | 2033 | ART033 | 0 | 0 | 12338.9449 | 539152.5748 | 12338.9449 | 3115.3797 | 542267.9545
| 20495755 | 2034 | ART033 | 0 | 0 | 12338.9449 | 539152.5748 | 12338.9449 | 3115.3797 | 542267.9545
| 20495844 | 2023 | ART033 | 0 | 0 | 0 | 0 | 0 | 3860.9477 | 3860.9477
| 20495844 | 2024 | ART033 | 0 | 0 | 0 | 0 | 0 | 3860.9477 | 3860.9477
| 20495844 | 2025 | ART033 | 1249.3867 | 23.9095 | 0 | 0 | 1249.3867 | 3860.9477 | 3884.8572
| 20495844 | 2026 | ART033 | 3844.2884 | 39.599 | 0 | 0 | 3844.2884 | 3860.9477 | 3900.5467
| 20495844 | 2027 | ART033 | 3844.2884 | 39.599 | 0 | 0 | 3844.2884 | 3860.9477 | 3900.5467
| 20495844 | 2028 | ART033 | 3844.2884 | 39.599 | 0 | 0 | 3844.2884 | 3860.9477 | 3900.5467
| 20495844 | 2029 | ART033 | 3844.2884 | 39.599 | 0 | 0 | 3844.2884 | 3860.9477 | 3900.5467
| 20495844 | 2030 | ART033 | 3844.2884 | 39.599 | 0 | 0 | 3844.2884 | 3860.9477 | 3900.5467
| 20495844 | 2031 | ART033 | 3844.2884 | 39.599 | 0 | 0 | 3844.2884 | 3860.9477 | 3900.5467
| 20495844 | 2032 | ART033 | 3844.2884 | 39.599 | 0 | 0 | 3844.2884 | 3860.9477 | 3900.5467
| 20495844 | 2033 | ART033 | 3844.2884 | 39.599 | 0 | 0 | 3844.2884 | 3860.9477 | 3900.5467
| 20495844 | 2034 | ART033 | 3844.2884 | 39.599 | 0 | 0 | 3844.2884 | 3860.9477 | 3900.5467
| 20495863 | 2023 | ART033 | 0 | 0 | 52492.5647 | 2293672.7187 | 52492.5647 | 3602.1936 | 2297274.9122
| 20495863 | 2024 | ART033 | 0 | 0 | 54560.7652 | 2384043.1394 | 54560.7652 | 3602.1936 | 2387645.333
| 20495863 | 2025 | ART033 | 0 | 0 | 56496.4775 | 2468624.4617 | 56496.4775 | 3602.1936 | 2472226.6553
| 20495863 | 2026 | ART033 | 0 | 0 | 53603.3524 | 2342208.8008 | 53603.3524 | 3602.1936 | 2345810.9944
| 20495863 | 2027 | ART033 | 0 | 0 | 53603.3524 | 2342208.8008 | 53603.3524 | 3602.1936 | 2345810.9944
| 20495863 | 2028 | ART033 | 0 | 0 | 53603.3524 | 2342208.8008 | 53603.3524 | 3602.1936 | 2345810.9944
| 20495863 | 2029 | ART033 | 0 | 0 | 53603.3524 | 2342208.8008 | 53603.3524 | 3602.1936 | 2345810.9944
| 20495863 | 2030 | ART033 | 0 | 0 | 53603.3524 | 2342208.8008 | 53603.3524 | 3602.1936 | 2345810.9944
| 20495863 | 2031 | ART033 | 0 | 0 | 53603.3524 | 2342208.8008 | 53603.3524 | 3602.1936 | 2345810.9944
| 20495863 | 2032 | ART033 | 0 | 0 | 53603.3524 | 2342208.8008 | 53603.3524 | 3602.1936 | 2345810.9944
| 20495863 | 2033 | ART033 | 0 | 0 | 53603.3524 | 2342208.8008 | 53603.3524 | 3602.1936 | 2345810.9944
| 20495863 | 2034 | ART033 | 0 | 0 | 53603.3524 | 2342208.8008 | 53603.3524 | 3602.1936 | 2345810.9944
| 20697522 | 2023 | ART033 | 0 | 0 | 0 | 0 | 0 | 4674.4363 | 4674.4363
| 20697522 | 2024 | ART033 | 0 | 0 | 0 | 0 | 0 | 4674.4363 | 4674.4363
| 20697522 | 2025 | ART033 | 0 | 0 | 0 | 0 | 0 | 4674.4363 | 4674.4363
| 20697522 | 2026 | ART033 | 889.9973 | 5.5353 | 0 | 0 | 889.9973 | 4674.4363 | 4679.9716
| 20697522 | 2027 | ART033 | 889.9973 | 5.5353 | 0 | 0 | 889.9973 | 4674.4363 | 4679.9716
| 20697522 | 2028 | ART033 | 889.9973 | 5.5353 | 0 | 0 | 889.9973 | 4674.4363 | 4679.9716
| 20697522 | 2029 | ART033 | 889.9973 | 5.5353 | 0 | 0 | 889.9973 | 4674.4363 | 4679.9716
| 20697522 | 2030 | ART033 | 889.9973 | 5.5353 | 0 | 0 | 889.9973 | 4674.4363 | 4679.9716
| 20697522 | 2031 | ART033 | 889.9973 | 5.5353 | 0 | 0 | 889.9973 | 4674.4363 | 4679.9716
| 20697522 | 2032 | ART033 | 889.9973 | 5.5353 | 0 | 0 | 889.9973 | 4674.4363 | 4679.9716
| 20697522 | 2033 | ART033 | 889.9973 | 5.5353 | 0 | 0 | 889.9973 | 4674.4363 | 4679.9716
| 20697522 | 2034 | ART033 | 889.9973 | 5.5353 | 0 | 0 | 889.9973 | 4674.4363 | 4679.9716
| 123245496 | 2023 | ART033 | 0 | 0 | 0 | 0 | 0 | 2648.483 | 2648.483
| 123245496 | 2024 | ART033 | 0 | 0 | 0 | 0 | 0 | 2648.483 | 2648.483
| 123245496 | 2025 | ART033 | 0 | 0 | 0 | 0 | 0 | 2648.483 | 2648.483
| 123245496 | 2026 | ART033 | 0 | 0 | 0 | 0 | 0 | 2648.483 | 2648.483
| 123245496 | 2027 | ART033 | 0 | 0 | 0 | 0 | 0 | 2648.483 | 2648.483
| 123245496 | 2028 | ART033 | 0 | 0 | 0 | 0 | 0 | 2648.483 | 2648.483
| 123245496 | 2029 | ART033 | 0 | 0 | 0 | 0 | 0 | 2648.483 | 2648.483
| 123245496 | 2030 | ART033 | 0 | 0 | 0 | 0 | 0 | 2648.483 | 2648.483
| 123245496 | 2031 | ART033 | 0 | 0 | 0 | 0 | 0 | 2648.483 | 2648.483
| 123245496 | 2032 | ART033 | 0 | 0 | 0 | 0 | 0 | 2648.483 | 2648.483
| 123245496 | 2033 | ART033 | 0 | 0 | 0 | 0 | 0 | 2648.483 | 2648.483
| 123245496 | 2034 | ART033 | 0 | 0 | 0 | 0 | 0 | 2648.483 | 2648.483
| 154671563 | 2023 | ART033 | 0 | 0 | 0 | 0 | 0 | 1908.8744 | 1908.8744
| 154671563 | 2024 | ART033 | 0 | 0 | 0 | 0 | 0 | 1908.8744 | 1908.8744
| 154671563 | 2025 | ART033 | 0 | 0 | 0 | 0 | 0 | 1908.8744 | 1908.8744
| 154671563 | 2026 | ART033 | 0 | 0 | 0 | 0 | 0 | 1908.8744 | 1908.8744
| 154671563 | 2027 | ART033 | 0 | 0 | 0 | 0 | 0 | 1908.8744 | 1908.8744
| 154671563 | 2028 | ART033 | 0 | 0 | 0 | 0 | 0 | 1908.8744 | 1908.8744
| 154671563 | 2029 | ART033 | 0 | 0 | 0 | 0 | 0 | 1908.8744 | 1908.8744
| 154671563 | 2030 | ART033 | 0 | 0 | 0 | 0 | 0 | 1908.8744 | 1908.8744
| 154671563 | 2031 | ART033 | 0 | 0 | 0 | 0 | 0 | 1908.8744 | 1908.8744
| 154671563 | 2032 | ART033 | 0 | 0 | 0 | 0 | 0 | 1908.8744 | 1908.8744
| 154671563 | 2033 | ART033 | 0 | 0 | 0 | 0 | 0 | 1908.8744 | 1908.8744
| 154671563 | 2034 | ART033 | 0 | 0 | 0 | 0 | 0 | 1908.8744 | 1908.8744
| 155078993 | 2023 | ART033 | 0 | 0 | 7.6061 | 332.3509 | 7.6061 | 1896.8296 | 2229.1806
| 155078993 | 2024 | ART033 | 0 | 0 | 9.8033 | 428.3554 | 9.8033 | 1896.8296 | 2325.185
| 155078993 | 2025 | ART033 | 0 | 0 | 7.6776 | 335.4753 | 7.6776 | 1896.8296 | 2232.305
| 155078993 | 2026 | ART033 | 0 | 0 | 10.502 | 458.8881 | 10.502 | 1896.8296 | 2355.7177
| 155078993 | 2027 | ART033 | 0 | 0 | 10.502 | 458.8881 | 10.502 | 1896.8296 | 2355.7177
| 155078993 | 2028 | ART033 | 0 | 0 | 10.502 | 458.8881 | 10.502 | 1896.8296 | 2355.7177
| 155078993 | 2029 | ART033 | 0 | 0 | 10.502 | 458.8881 | 10.502 | 1896.8296 | 2355.7177
| 155078993 | 2030 | ART033 | 0 | 0 | 10.502 | 458.8881 | 10.502 | 1896.8296 | 2355.7177
| 155078993 | 2031 | ART033 | 0 | 0 | 10.502 | 458.8881 | 10.502 | 1896.8296 | 2355.7177
| 155078993 | 2032 | ART033 | 0 | 0 | 10.502 | 458.8881 | 10.502 | 1896.8296 | 2355.7177
| 155078993 | 2033 | ART033 | 0 | 0 | 10.502 | 458.8881 | 10.502 | 1896.8296 | 2355.7177
| 155078993 | 2034 | ART033 | 0 | 0 | 10.502 | 458.8881 | 10.502 | 1896.8296 | 2355.7177
| 155091650 | 2023 | ART033 | 450.8747 | 0 | 6823.2518 | 298143.3011 | 7274.1265 | 4957.3221 | 303100.6232
| 155091650 | 2024 | ART033 | 455.7309 | 9.116 | 7115.6964 | 310921.7242 | 7571.4273 | 4957.3221 | 315888.1623
| 155091650 | 2025 | ART033 | 454.4309 | 8.2596 | 7251.2962 | 316846.7838 | 7705.7271 | 4957.3221 | 321812.3655
| 155091650 | 2026 | ART033 | 599.7972 | 3.6412 | 7231.296 | 315972.8693 | 7831.0932 | 4957.3221 | 320933.8325
| 155091650 | 2027 | ART033 | 599.7972 | 3.6412 | 7231.296 | 315972.8693 | 7831.0932 | 4957.3221 | 320933.8325
| 155091650 | 2028 | ART033 | 599.7972 | 3.6412 | 7231.296 | 315972.8693 | 7831.0932 | 4957.3221 | 320933.8325
| 155091650 | 2029 | ART033 | 599.7972 | 3.6412 | 7231.296 | 315972.8693 | 7831.0932 | 4957.3221 | 320933.8325
| 155091650 | 2030 | ART033 | 599.7972 | 3.6412 | 7231.296 | 315972.8693 | 7831.0932 | 4957.3221 | 320933.8325
| 155091650 | 2031 | ART033 | 599.7972 | 3.6412 | 7231.296 | 315972.8693 | 7831.0932 | 4957.3221 | 320933.8325
| 155091650 | 2032 | ART033 | 599.7972 | 3.6412 | 7231.296 | 315972.8693 | 7831.0932 | 4957.3221 | 320933.8325
| 155091650 | 2033 | ART033 | 599.7972 | 3.6412 | 7231.296 | 315972.8693 | 7831.0932 | 4957.3221 | 320933.8325
| 155091650 | 2034 | ART033 | 599.7972 | 3.6412 | 7231.296 | 315972.8693 | 7831.0932 | 4957.3221 | 320933.8325
| 156524856 | 2023 | ART033 | 0 | 0 | 600.8618 | 26254.7709 | 600.8618 | 1366.4189 | 27621.1898
| 156524856 | 2024 | ART033 | 0 | 0 | 625.8897 | 27348.371 | 625.8897 | 1366.4189 | 28714.79
| 156524856 | 2025 | ART033 | 0 | 0 | 657.019 | 28708.5735 | 657.019 | 1366.4189 | 30074.9924
| 156524856 | 2026 | ART033 | 0 | 0 | 632.403 | 27632.9689 | 632.403 | 1366.4189 | 28999.3878
| 156524856 | 2027 | ART033 | 0 | 0 | 632.403 | 27632.9689 | 632.403 | 1366.4189 | 28999.3878
| 156524856 | 2028 | ART033 | 0 | 0 | 632.403 | 27632.9689 | 632.403 | 1366.4189 | 28999.3878
| 156524856 | 2029 | ART033 | 0 | 0 | 632.403 | 27632.9689 | 632.403 | 1366.4189 | 28999.3878
| 156524856 | 2030 | ART033 | 0 | 0 | 632.403 | 27632.9689 | 632.403 | 1366.4189 | 28999.3878
| 156524856 | 2031 | ART033 | 0 | 0 | 632.403 | 27632.9689 | 632.403 | 1366.4189 | 28999.3878
| 156524856 | 2032 | ART033 | 0 | 0 | 632.403 | 27632.9689 | 632.403 | 1366.4189 | 28999.3878
| 156524856 | 2033 | ART033 | 0 | 0 | 632.403 | 27632.9689 | 632.403 | 1366.4189 | 28999.3878
| 156524856 | 2034 | ART033 | 0 | 0 | 632.403 | 27632.9689 | 632.403 | 1366.4189 | 28999.3878
| 156670377 | 2023 | ART033 | 0 | 0 | 36.7251 | 1604.7091 | 36.7251 | 5991.0412 | 7595.7503
| 156670377 | 2024 | ART033 | 0 | 0 | 42.1127 | 1840.1234 | 42.1127 | 5991.0412 | 7831.1646
| 156670377 | 2025 | ART033 | 0 | 0 | 43.7231 | 1910.4909 | 43.7231 | 5991.0412 | 7901.5321
| 156670377 | 2026 | ART033 | 0 | 0 | 44.1316 | 1928.3399 | 44.1316 | 5991.0412 | 7919.3812
| 156670377 | 2027 | ART033 | 0 | 0 | 44.1316 | 1928.3399 | 44.1316 | 5991.0412 | 7919.3812
| 156670377 | 2028 | ART033 | 0 | 0 | 44.1316 | 1928.3399 | 44.1316 | 5991.0412 | 7919.3812
| 156670377 | 2029 | ART033 | 0 | 0 | 44.1316 | 1928.3399 | 44.1316 | 5991.0412 | 7919.3812
| 156670377 | 2030 | ART033 | 0 | 0 | 44.1316 | 1928.3399 | 44.1316 | 5991.0412 | 7919.3812
| 156670377 | 2031 | ART033 | 0 | 0 | 44.1316 | 1928.3399 | 44.1316 | 5991.0412 | 7919.3812
| 156670377 | 2032 | ART033 | 0 | 0 | 44.1316 | 1928.3399 | 44.1316 | 5991.0412 | 7919.3812
| 156670377 | 2033 | ART033 | 0 | 0 | 44.1316 | 1928.3399 | 44.1316 | 5991.0412 | 7919.3812
| 156670377 | 2034 | ART033 | 0 | 0 | 44.1316 | 1928.3399 | 44.1316 | 5991.0412 | 7919.3812
| 156737644 | 2023 | ART033 | 0 | 0 | 12862.2697 | 562019.3521 | 12862.2697 | 3973.5552 | 565992.9072
| 156737644 | 2024 | ART033 | 0 | 0 | 13086.824 | 571831.2948 | 13086.824 | 3973.5552 | 575804.85
| 156737644 | 2025 | ART033 | 0 | 0 | 13038.1193 | 569703.1322 | 13038.1193 | 3973.5552 | 573676.6874
| 156737644 | 2026 | ART033 | 0 | 0 | 12495.9165 | 546011.4777 | 12495.9165 | 3973.5552 | 549985.0329
| 156737644 | 2027 | ART033 | 0 | 0 | 12495.9165 | 546011.4777 | 12495.9165 | 3973.5552 | 549985.0329
| 156737644 | 2028 | ART033 | 0 | 0 | 12495.9165 | 546011.4777 | 12495.9165 | 3973.5552 | 549985.0329
| 156737644 | 2029 | ART033 | 0 | 0 | 12495.9165 | 546011.4777 | 12495.9165 | 3973.5552 | 549985.0329
| 156737644 | 2030 | ART033 | 0 | 0 | 12495.9165 | 546011.4777 | 12495.9165 | 3973.5552 | 549985.0329
| 156737644 | 2031 | ART033 | 0 | 0 | 12495.9165 | 546011.4777 | 12495.9165 | 3973.5552 | 549985.0329
| 156737644 | 2032 | ART033 | 0 | 0 | 12495.9165 | 546011.4777 | 12495.9165 | 3973.5552 | 549985.0329
| 156737644 | 2033 | ART033 | 0 | 0 | 12495.9165 | 546011.4777 | 12495.9165 | 3973.5552 | 549985.0329
| 156737644 | 2034 | ART033 | 0 | 0 | 12495.9165 | 546011.4777 | 12495.9165 | 3973.5552 | 549985.0329
| 187173693 | 2023 | ART033 | 0 | 0 | 2324.5329 | 101570.9112 | 2324.5329 | 13502.0697 | 115072.981
| 187173693 | 2024 | ART033 | 0 | 0 | 2369.5462 | 103537.7766 | 2369.5462 | 13502.0697 | 117039.8464
| 187173693 | 2025 | ART033 | 0 | 0 | 2394.1662 | 104613.5549 | 2394.1662 | 13502.0697 | 118115.6246
| 187173693 | 2026 | ART033 | 0 | 0 | 2384.4856 | 104190.5557 | 2384.4856 | 13502.0697 | 117692.6254
| 187173693 | 2027 | ART033 | 0 | 0 | 2384.4856 | 104190.5557 | 2384.4856 | 13502.0697 | 117692.6254
| 187173693 | 2028 | ART033 | 0 | 0 | 2384.4856 | 104190.5557 | 2384.4856 | 13502.0697 | 117692.6254
| 187173693 | 2029 | ART033 | 0 | 0 | 2384.4856 | 104190.5557 | 2384.4856 | 13502.0697 | 117692.6254
| 187173693 | 2030 | ART033 | 0 | 0 | 2384.4856 | 104190.5557 | 2384.4856 | 13502.0697 | 117692.6254
| 187173693 | 2031 | ART033 | 0 | 0 | 2384.4856 | 104190.5557 | 2384.4856 | 13502.0697 | 117692.6254
| 187173693 | 2032 | ART033 | 0 | 0 | 2384.4856 | 104190.5557 | 2384.4856 | 13502.0697 | 117692.6254
| 187173693 | 2033 | ART033 | 0 | 0 | 2384.4856 | 104190.5557 | 2384.4856 | 13502.0697 | 117692.6254
| 187173693 | 2034 | ART033 | 0 | 0 | 2384.4856 | 104190.5557 | 2384.4856 | 13502.0697 | 117692.6254
| 199745387 | 2023 | ART033 | 0 | 0 | 8.4546 | 369.4274 | 8.4546 | 2523.6665 | 2893.0939
| 199745387 | 2024 | ART033 | 0 | 0 | 11.8882 | 519.4565 | 11.8882 | 2523.6665 | 3043.123
| 199745387 | 2025 | ART033 | 0 | 0 | 14.9754 | 654.3544 | 14.9754 | 2523.6665 | 3178.0209
| 199745387 | 2026 | ART033 | 0 | 0 | 11.8647 | 518.4323 | 11.8647 | 2523.6665 | 3042.0988
| 199745387 | 2027 | ART033 | 0 | 0 | 11.8647 | 518.4323 | 11.8647 | 2523.6665 | 3042.0988
| 199745387 | 2028 | ART033 | 0 | 0 | 11.8647 | 518.4323 | 11.8647 | 2523.6665 | 3042.0988
| 199745387 | 2029 | ART033 | 0 | 0 | 11.8647 | 518.4323 | 11.8647 | 2523.6665 | 3042.0988
| 199745387 | 2030 | ART033 | 0 | 0 | 11.8647 | 518.4323 | 11.8647 | 2523.6665 | 3042.0988
| 199745387 | 2031 | ART033 | 0 | 0 | 11.8647 | 518.4323 | 11.8647 | 2523.6665 | 3042.0988
| 199745387 | 2032 | ART033 | 0 | 0 | 11.8647 | 518.4323 | 11.8647 | 2523.6665 | 3042.0988
| 199745387 | 2033 | ART033 | 0 | 0 | 11.8647 | 518.4323 | 11.8647 | 2523.6665 | 3042.0988
| 199745387 | 2034 | ART033 | 0 | 0 | 11.8647 | 518.4323 | 11.8647 | 2523.6665 | 3042.0988
| 20239754 | 2025 | BAN003 | 10.0531 | 0.05657 | 5115.9998 | 228958.0143 | 5126.0529 | 681.6666 | 229639.7375
| 20239754 | 2026 | BAN003 | 10.0531 | 0.05657 | 5115.9998 | 228958.0143 | 5126.0529 | 681.6666 | 229639.7375
| 20239754 | 2027 | BAN003 | 10.0531 | 0.05657 | 5115.9998 | 228958.0143 | 5126.0529 | 681.6666 | 229639.7375
| 20239754 | 2028 | BAN003 | 10.0531 | 0.05657 | 5115.9998 | 228958.0143 | 5126.0529 | 681.6666 | 229639.7375
| 20239754 | 2029 | BAN003 | 10.0531 | 0.05657 | 5115.9998 | 228958.0143 | 5126.0529 | 681.6666 | 229639.7375
| 20239754 | 2030 | BAN003 | 10.0531 | 0.05657 | 5115.9998 | 228958.0143 | 5126.0529 | 681.6666 | 229639.7375
| 20239754 | 2031 | BAN003 | 10.0531 | 0.05657 | 5115.9998 | 228958.0143 | 5126.0529 | 681.6666 | 229639.7375
| 20239754 | 2032 | BAN003 | 10.0531 | 0.05657 | 5115.9998 | 228958.0143 | 5126.0529 | 681.6666 | 229639.7375
| 20239754 | 2033 | BAN003 | 10.0531 | 0.05657 | 5115.9998 | 228958.0143 | 5126.0529 | 681.6666 | 229639.7375
| 20239754 | 2034 | BAN003 | 10.0531 | 0.05657 | 5115.9998 | 228958.0143 | 5126.0529 | 681.6666 | 229639.7375
| 20401509 | 2025 | BAN003 | 0 | 0 | 218.7071 | 9787.8689 | 218.7071 | 3405.1201 | 13192.989
| 20401509 | 2026 | BAN003 | 0 | 0 | 218.7071 | 9787.8689 | 218.7071 | 3405.1201 | 13192.989
| 20401509 | 2027 | BAN003 | 0 | 0 | 218.7071 | 9787.8689 | 218.7071 | 3405.1201 | 13192.989
| 20401509 | 2028 | BAN003 | 0 | 0 | 218.7071 | 9787.8689 | 218.7071 | 3405.1201 | 13192.989
| 20401509 | 2029 | BAN003 | 0 | 0 | 218.7071 | 9787.8689 | 218.7071 | 3405.1201 | 13192.989
| 20401509 | 2030 | BAN003 | 0 | 0 | 218.7071 | 9787.8689 | 218.7071 | 3405.1201 | 13192.989
| 20401509 | 2031 | BAN003 | 0 | 0 | 218.7071 | 9787.8689 | 218.7071 | 3405.1201 | 13192.989
| 20401509 | 2032 | BAN003 | 0 | 0 | 218.7071 | 9787.8689 | 218.7071 | 3405.1201 | 13192.989
| 20401509 | 2033 | BAN003 | 0 | 0 | 218.7071 | 9787.8689 | 218.7071 | 3405.1201 | 13192.989
| 20401509 | 2034 | BAN003 | 0 | 0 | 218.7071 | 9787.8689 | 218.7071 | 3405.1201 | 13192.989
| 20483282 | 2025 | BAN003 | 0 | 0 | 300.2376 | 13436.6299 | 300.2376 | 5505.5016 | 18942.1314
| 20483282 | 2026 | BAN003 | 0 | 0 | 300.2376 | 13436.6299 | 300.2376 | 5505.5016 | 18942.1314
| 20483282 | 2027 | BAN003 | 0 | 0 | 300.2376 | 13436.6299 | 300.2376 | 5505.5016 | 18942.1314
| 20483282 | 2028 | BAN003 | 0 | 0 | 300.2376 | 13436.6299 | 300.2376 | 5505.5016 | 18942.1314
| 20483282 | 2029 | BAN003 | 0 | 0 | 300.2376 | 13436.6299 | 300.2376 | 5505.5016 | 18942.1314
| 20483282 | 2030 | BAN003 | 0 | 0 | 300.2376 | 13436.6299 | 300.2376 | 5505.5016 | 18942.1314
| 20483282 | 2031 | BAN003 | 0 | 0 | 300.2376 | 13436.6299 | 300.2376 | 5505.5016 | 18942.1314
| 20483282 | 2032 | BAN003 | 0 | 0 | 300.2376 | 13436.6299 | 300.2376 | 5505.5016 | 18942.1314
| 20483282 | 2033 | BAN003 | 0 | 0 | 300.2376 | 13436.6299 | 300.2376 | 5505.5016 | 18942.1314
| 20483282 | 2034 | BAN003 | 0 | 0 | 300.2376 | 13436.6299 | 300.2376 | 5505.5016 | 18942.1314
| 20498976 | 2025 | BAN003 | 0 | 0 | 223.5589 | 10005.0049 | 223.5589 | 609.2146 | 10614.2194
| 20498976 | 2026 | BAN003 | 0 | 0 | 223.5589 | 10005.0049 | 223.5589 | 609.2146 | 10614.2194
| 20498976 | 2027 | BAN003 | 0 | 0 | 223.5589 | 10005.0049 | 223.5589 | 609.2146 | 10614.2194
| 20498976 | 2028 | BAN003 | 0 | 0 | 223.5589 | 10005.0049 | 223.5589 | 609.2146 | 10614.2194
| 20498976 | 2029 | BAN003 | 0 | 0 | 223.5589 | 10005.0049 | 223.5589 | 609.2146 | 10614.2194
| 20498976 | 2030 | BAN003 | 0 | 0 | 223.5589 | 10005.0049 | 223.5589 | 609.2146 | 10614.2194
| 20498976 | 2031 | BAN003 | 0 | 0 | 223.5589 | 10005.0049 | 223.5589 | 609.2146 | 10614.2194
| 20498976 | 2032 | BAN003 | 0 | 0 | 223.5589 | 10005.0049 | 223.5589 | 609.2146 | 10614.2194
| 20498976 | 2033 | BAN003 | 0 | 0 | 223.5589 | 10005.0049 | 223.5589 | 609.2146 | 10614.2194
| 20498976 | 2034 | BAN003 | 0 | 0 | 223.5589 | 10005.0049 | 223.5589 | 609.2146 | 10614.2194
| 20519796 | 2025 | BAN003 | 1.6601 | 0.014666 | 119.2598 | 5337.2717 | 120.9198 | 1165.6416 | 6502.928
| 20519796 | 2026 | BAN003 | 1.6601 | 0.014666 | 119.2598 | 5337.2717 | 120.9198 | 1165.6416 | 6502.928
| 20519796 | 2027 | BAN003 | 1.6601 | 0.014666 | 119.2598 | 5337.2717 | 120.9198 | 1165.6416 | 6502.928
| 20519796 | 2028 | BAN003 | 1.6601 | 0.014666 | 119.2598 | 5337.2717 | 120.9198 | 1165.6416 | 6502.928
| 20519796 | 2029 | BAN003 | 1.6601 | 0.014666 | 119.2598 | 5337.2717 | 120.9198 | 1165.6416 | 6502.928
| 20519796 | 2030 | BAN003 | 1.6601 | 0.014666 | 119.2598 | 5337.2717 | 120.9198 | 1165.6416 | 6502.928
| 20519796 | 2031 | BAN003 | 1.6601 | 0.014666 | 119.2598 | 5337.2717 | 120.9198 | 1165.6416 | 6502.928
| 20519796 | 2032 | BAN003 | 1.6601 | 0.014666 | 119.2598 | 5337.2717 | 120.9198 | 1165.6416 | 6502.928
| 20519796 | 2033 | BAN003 | 1.6601 | 0.014666 | 119.2598 | 5337.2717 | 120.9198 | 1165.6416 | 6502.928
| 20519796 | 2034 | BAN003 | 1.6601 | 0.014666 | 119.2598 | 5337.2717 | 120.9198 | 1165.6416 | 6502.928
| 20519807 | 2025 | BAN003 | 39.4207 | 0.84786 | 7.5735 | 338.9385 | 46.9941 | 749.8044 | 1089.5908
| 20519807 | 2026 | BAN003 | 39.4207 | 0.84786 | 7.5735 | 338.9385 | 46.9941 | 749.8044 | 1089.5908
| 20519807 | 2027 | BAN003 | 39.4207 | 0.84786 | 7.5735 | 338.9385 | 46.9941 | 749.8044 | 1089.5908
| 20519807 | 2028 | BAN003 | 39.4207 | 0.84786 | 7.5735 | 338.9385 | 46.9941 | 749.8044 | 1089.5908
| 20519807 | 2029 | BAN003 | 39.4207 | 0.84786 | 7.5735 | 338.9385 | 46.9941 | 749.8044 | 1089.5908
| 20519807 | 2030 | BAN003 | 39.4207 | 0.84786 | 7.5735 | 338.9385 | 46.9941 | 749.8044 | 1089.5908
| 20519807 | 2031 | BAN003 | 39.4207 | 0.84786 | 7.5735 | 338.9385 | 46.9941 | 749.8044 | 1089.5908
| 20519807 | 2032 | BAN003 | 39.4207 | 0.84786 | 7.5735 | 338.9385 | 46.9941 | 749.8044 | 1089.5908
| 20519807 | 2033 | BAN003 | 39.4207 | 0.84786 | 7.5735 | 338.9385 | 46.9941 | 749.8044 | 1089.5908
| 20519807 | 2034 | BAN003 | 39.4207 | 0.84786 | 7.5735 | 338.9385 | 46.9941 | 749.8044 | 1089.5908
| 20575682 | 2025 | BAN003 | 0 | 0 | 269.2741 | 12050.9107 | 269.2741 | 620.9644 | 12671.8751
| 20575682 | 2026 | BAN003 | 0 | 0 | 269.2741 | 12050.9107 | 269.2741 | 620.9644 | 12671.8751
| 20575682 | 2027 | BAN003 | 0 | 0 | 269.2741 | 12050.9107 | 269.2741 | 620.9644 | 12671.8751
| 20575682 | 2028 | BAN003 | 0 | 0 | 269.2741 | 12050.9107 | 269.2741 | 620.9644 | 12671.8751
| 20575682 | 2029 | BAN003 | 0 | 0 | 269.2741 | 12050.9107 | 269.2741 | 620.9644 | 12671.8751
| 20575682 | 2030 | BAN003 | 0 | 0 | 269.2741 | 12050.9107 | 269.2741 | 620.9644 | 12671.8751
| 20575682 | 2031 | BAN003 | 0 | 0 | 269.2741 | 12050.9107 | 269.2741 | 620.9644 | 12671.8751
| 20575682 | 2032 | BAN003 | 0 | 0 | 269.2741 | 12050.9107 | 269.2741 | 620.9644 | 12671.8751
| 20575682 | 2033 | BAN003 | 0 | 0 | 269.2741 | 12050.9107 | 269.2741 | 620.9644 | 12671.8751
| 20575682 | 2034 | BAN003 | 0 | 0 | 269.2741 | 12050.9107 | 269.2741 | 620.9644 | 12671.8751
| 20604529 | 2025 | BAN003 | 0 | 0 | 80.9879 | 3624.4782 | 80.9879 | 2780.2609 | 6404.7391
| 20604529 | 2026 | BAN003 | 0 | 0 | 80.9879 | 3624.4782 | 80.9879 | 2780.2609 | 6404.7391
| 20604529 | 2027 | BAN003 | 0 | 0 | 80.9879 | 3624.4782 | 80.9879 | 2780.2609 | 6404.7391
| 20604529 | 2028 | BAN003 | 0 | 0 | 80.9879 | 3624.4782 | 80.9879 | 2780.2609 | 6404.7391
| 20604529 | 2029 | BAN003 | 0 | 0 | 80.9879 | 3624.4782 | 80.9879 | 2780.2609 | 6404.7391
| 20604529 | 2030 | BAN003 | 0 | 0 | 80.9879 | 3624.4782 | 80.9879 | 2780.2609 | 6404.7391
| 20604529 | 2031 | BAN003 | 0 | 0 | 80.9879 | 3624.4782 | 80.9879 | 2780.2609 | 6404.7391
| 20604529 | 2032 | BAN003 | 0 | 0 | 80.9879 | 3624.4782 | 80.9879 | 2780.2609 | 6404.7391
| 20604529 | 2033 | BAN003 | 0 | 0 | 80.9879 | 3624.4782 | 80.9879 | 2780.2609 | 6404.7391
| 20604529 | 2034 | BAN003 | 0 | 0 | 80.9879 | 3624.4782 | 80.9879 | 2780.2609 | 6404.7391
| 20612043 | 2025 | BAN003 | 0 | 0 | 415.4775 | 18594.0018 | 415.4775 | 7735.3605 | 26329.3623
| 20612043 | 2026 | BAN003 | 0 | 0 | 415.4775 | 18594.0018 | 415.4775 | 7735.3605 | 26329.3623
| 20612043 | 2027 | BAN003 | 0 | 0 | 415.4775 | 18594.0018 | 415.4775 | 7735.3605 | 26329.3623
| 20612043 | 2028 | BAN003 | 0 | 0 | 415.4775 | 18594.0018 | 415.4775 | 7735.3605 | 26329.3623
| 20612043 | 2029 | BAN003 | 0 | 0 | 415.4775 | 18594.0018 | 415.4775 | 7735.3605 | 26329.3623
| 20612043 | 2030 | BAN003 | 0 | 0 | 415.4775 | 18594.0018 | 415.4775 | 7735.3605 | 26329.3623
| 20612043 | 2031 | BAN003 | 0 | 0 | 415.4775 | 18594.0018 | 415.4775 | 7735.3605 | 26329.3623
| 20612043 | 2032 | BAN003 | 0 | 0 | 415.4775 | 18594.0018 | 415.4775 | 7735.3605 | 26329.3623
| 20612043 | 2033 | BAN003 | 0 | 0 | 415.4775 | 18594.0018 | 415.4775 | 7735.3605 | 26329.3623
| 20612043 | 2034 | BAN003 | 0 | 0 | 415.4775 | 18594.0018 | 415.4775 | 7735.3605 | 26329.3623
| 20647240 | 2025 | BAN003 | 4625.0145 | 92.5627 | 392.062 | 17546.0791 | 5017.0765 | 7598.6476 | 25237.2894
| 20647240 | 2026 | BAN003 | 4625.0145 | 92.5627 | 392.062 | 17546.0791 | 5017.0765 | 7598.6476 | 25237.2894
| 20647240 | 2027 | BAN003 | 4625.0145 | 92.5627 | 392.062 | 17546.0791 | 5017.0765 | 7598.6476 | 25237.2894
| 20647240 | 2028 | BAN003 | 4625.0145 | 92.5627 | 392.062 | 17546.0791 | 5017.0765 | 7598.6476 | 25237.2894
| 20647240 | 2029 | BAN003 | 4625.0145 | 92.5627 | 392.062 | 17546.0791 | 5017.0765 | 7598.6476 | 25237.2894
| 20647240 | 2030 | BAN003 | 4625.0145 | 92.5627 | 392.062 | 17546.0791 | 5017.0765 | 7598.6476 | 25237.2894
| 20647240 | 2031 | BAN003 | 4625.0145 | 92.5627 | 392.062 | 17546.0791 | 5017.0765 | 7598.6476 | 25237.2894
| 20647240 | 2032 | BAN003 | 4625.0145 | 92.5627 | 392.062 | 17546.0791 | 5017.0765 | 7598.6476 | 25237.2894
| 20647240 | 2033 | BAN003 | 4625.0145 | 92.5627 | 392.062 | 17546.0791 | 5017.0765 | 7598.6476 | 25237.2894
| 20647240 | 2034 | BAN003 | 4625.0145 | 92.5627 | 392.062 | 17546.0791 | 5017.0765 | 7598.6476 | 25237.2894
| 20648756 | 2025 | BAN003 | 55042.5528 | 1355.2439 | 0 | 0 | 55042.5528 | 2341.5764 | 3696.8203
| 20648756 | 2026 | BAN003 | 55042.5528 | 1355.2439 | 0 | 0 | 55042.5528 | 2341.5764 | 3696.8203
| 20648756 | 2027 | BAN003 | 55042.5528 | 1355.2439 | 0 | 0 | 55042.5528 | 2341.5764 | 3696.8203
| 20648756 | 2028 | BAN003 | 55042.5528 | 1355.2439 | 0 | 0 | 55042.5528 | 2341.5764 | 3696.8203
| 20648756 | 2029 | BAN003 | 55042.5528 | 1355.2439 | 0 | 0 | 55042.5528 | 2341.5764 | 3696.8203
| 20648756 | 2030 | BAN003 | 55042.5528 | 1355.2439 | 0 | 0 | 55042.5528 | 2341.5764 | 3696.8203
| 20648756 | 2031 | BAN003 | 55042.5528 | 1355.2439 | 0 | 0 | 55042.5528 | 2341.5764 | 3696.8203
| 20648756 | 2032 | BAN003 | 55042.5528 | 1355.2439 | 0 | 0 | 55042.5528 | 2341.5764 | 3696.8203
| 20648756 | 2033 | BAN003 | 55042.5528 | 1355.2439 | 0 | 0 | 55042.5528 | 2341.5764 | 3696.8203
| 20648756 | 2034 | BAN003 | 55042.5528 | 1355.2439 | 0 | 0 | 55042.5528 | 2341.5764 | 3696.8203
| 20655277 | 2025 | BAN003 | 6213.4021 | 150.098 | 7.3958 | 330.9845 | 6220.7979 | 2699.9833 | 3181.0658
| 20655277 | 2026 | BAN003 | 6213.4021 | 150.098 | 7.3958 | 330.9845 | 6220.7979 | 2699.9833 | 3181.0658
| 20655277 | 2027 | BAN003 | 6213.4021 | 150.098 | 7.3958 | 330.9845 | 6220.7979 | 2699.9833 | 3181.0658
| 20655277 | 2028 | BAN003 | 6213.4021 | 150.098 | 7.3958 | 330.9845 | 6220.7979 | 2699.9833 | 3181.0658
| 20655277 | 2029 | BAN003 | 6213.4021 | 150.098 | 7.3958 | 330.9845 | 6220.7979 | 2699.9833 | 3181.0658
| 20655277 | 2030 | BAN003 | 6213.4021 | 150.098 | 7.3958 | 330.9845 | 6220.7979 | 2699.9833 | 3181.0658
| 20655277 | 2031 | BAN003 | 6213.4021 | 150.098 | 7.3958 | 330.9845 | 6220.7979 | 2699.9833 | 3181.0658
| 20655277 | 2032 | BAN003 | 6213.4021 | 150.098 | 7.3958 | 330.9845 | 6220.7979 | 2699.9833 | 3181.0658
| 20655277 | 2033 | BAN003 | 6213.4021 | 150.098 | 7.3958 | 330.9845 | 6220.7979 | 2699.9833 | 3181.0658
| 20655277 | 2034 | BAN003 | 6213.4021 | 150.098 | 7.3958 | 330.9845 | 6220.7979 | 2699.9833 | 3181.0658
| 42784766 | 2025 | BAN003 | 38.5883 | 0.31147 | 9536.0466 | 426769.8103 | 9574.6349 | 962.4309 | 427732.5526
| 42784766 | 2026 | BAN003 | 38.5883 | 0.31147 | 9536.0466 | 426769.8103 | 9574.6349 | 962.4309 | 427732.5526
| 42784766 | 2027 | BAN003 | 38.5883 | 0.31147 | 9536.0466 | 426769.8103 | 9574.6349 | 962.4309 | 427732.5526
| 42784766 | 2028 | BAN003 | 38.5883 | 0.31147 | 9536.0466 | 426769.8103 | 9574.6349 | 962.4309 | 427732.5526
| 42784766 | 2029 | BAN003 | 38.5883 | 0.31147 | 9536.0466 | 426769.8103 | 9574.6349 | 962.4309 | 427732.5526
| 42784766 | 2030 | BAN003 | 38.5883 | 0.31147 | 9536.0466 | 426769.8103 | 9574.6349 | 962.4309 | 427732.5526
| 42784766 | 2031 | BAN003 | 38.5883 | 0.31147 | 9536.0466 | 426769.8103 | 9574.6349 | 962.4309 | 427732.5526
| 42784766 | 2032 | BAN003 | 38.5883 | 0.31147 | 9536.0466 | 426769.8103 | 9574.6349 | 962.4309 | 427732.5526
| 42784766 | 2033 | BAN003 | 38.5883 | 0.31147 | 9536.0466 | 426769.8103 | 9574.6349 | 962.4309 | 427732.5526
| 42784766 | 2034 | BAN003 | 38.5883 | 0.31147 | 9536.0466 | 426769.8103 | 9574.6349 | 962.4309 | 427732.5526
| 42784818 | 2025 | BAN003 | 67.6591 | 0.41337 | 39578.5752 | 1771272.9203 | 39646.2343 | 713.2642 | 1771986.598
| 42784818 | 2026 | BAN003 | 67.6591 | 0.41337 | 39578.5752 | 1771272.9203 | 39646.2343 | 713.2642 | 1771986.598
| 42784818 | 2027 | BAN003 | 67.6591 | 0.41337 | 39578.5752 | 1771272.9203 | 39646.2343 | 713.2642 | 1771986.598
| 42784818 | 2028 | BAN003 | 67.6591 | 0.41337 | 39578.5752 | 1771272.9203 | 39646.2343 | 713.2642 | 1771986.598
| 42784818 | 2029 | BAN003 | 67.6591 | 0.41337 | 39578.5752 | 1771272.9203 | 39646.2343 | 713.2642 | 1771986.598
| 42784818 | 2030 | BAN003 | 67.6591 | 0.41337 | 39578.5752 | 1771272.9203 | 39646.2343 | 713.2642 | 1771986.598
| 42784818 | 2031 | BAN003 | 67.6591 | 0.41337 | 39578.5752 | 1771272.9203 | 39646.2343 | 713.2642 | 1771986.598
| 42784818 | 2032 | BAN003 | 67.6591 | 0.41337 | 39578.5752 | 1771272.9203 | 39646.2343 | 713.2642 | 1771986.598
| 42784818 | 2033 | BAN003 | 67.6591 | 0.41337 | 39578.5752 | 1771272.9203 | 39646.2343 | 713.2642 | 1771986.598
| 42784818 | 2034 | BAN003 | 67.6591 | 0.41337 | 39578.5752 | 1771272.9203 | 39646.2343 | 713.2642 | 1771986.598
| 97730969 | 2025 | BAN003 | 0 | 0 | 1260.5241 | 56412.6477 | 1260.5241 | 3202.1742 | 59614.8219
| 97730969 | 2026 | BAN003 | 0 | 0 | 1260.5241 | 56412.6477 | 1260.5241 | 3202.1742 | 59614.8219
| 97730969 | 2027 | BAN003 | 0 | 0 | 1260.5241 | 56412.6477 | 1260.5241 | 3202.1742 | 59614.8219
| 97730969 | 2028 | BAN003 | 0 | 0 | 1260.5241 | 56412.6477 | 1260.5241 | 3202.1742 | 59614.8219
| 97730969 | 2029 | BAN003 | 0 | 0 | 1260.5241 | 56412.6477 | 1260.5241 | 3202.1742 | 59614.8219
| 97730969 | 2030 | BAN003 | 0 | 0 | 1260.5241 | 56412.6477 | 1260.5241 | 3202.1742 | 59614.8219
| 97730969 | 2031 | BAN003 | 0 | 0 | 1260.5241 | 56412.6477 | 1260.5241 | 3202.1742 | 59614.8219
| 97730969 | 2032 | BAN003 | 0 | 0 | 1260.5241 | 56412.6477 | 1260.5241 | 3202.1742 | 59614.8219
| 97730969 | 2033 | BAN003 | 0 | 0 | 1260.5241 | 56412.6477 | 1260.5241 | 3202.1742 | 59614.8219
| 97730969 | 2034 | BAN003 | 0 | 0 | 1260.5241 | 56412.6477 | 1260.5241 | 3202.1742 | 59614.8219
| 193634827 | 2025 | BAN003 | 1453.1086 | 27.597 | 28.0985 | 1257.4997 | 1481.2071 | 552.7844 | 1837.8811
| 193634827 | 2026 | BAN003 | 1453.1086 | 27.597 | 28.0985 | 1257.4997 | 1481.2071 | 552.7844 | 1837.8811
| 193634827 | 2027 | BAN003 | 1453.1086 | 27.597 | 28.0985 | 1257.4997 | 1481.2071 | 552.7844 | 1837.8811
| 193634827 | 2028 | BAN003 | 1453.1086 | 27.597 | 28.0985 | 1257.4997 | 1481.2071 | 552.7844 | 1837.8811
| 193634827 | 2029 | BAN003 | 1453.1086 | 27.597 | 28.0985 | 1257.4997 | 1481.2071 | 552.7844 | 1837.8811
| 193634827 | 2030 | BAN003 | 1453.1086 | 27.597 | 28.0985 | 1257.4997 | 1481.2071 | 552.7844 | 1837.8811
| 193634827 | 2031 | BAN003 | 1453.1086 | 27.597 | 28.0985 | 1257.4997 | 1481.2071 | 552.7844 | 1837.8811
| 193634827 | 2032 | BAN003 | 1453.1086 | 27.597 | 28.0985 | 1257.4997 | 1481.2071 | 552.7844 | 1837.8811
| 193634827 | 2033 | BAN003 | 1453.1086 | 27.597 | 28.0985 | 1257.4997 | 1481.2071 | 552.7844 | 1837.8811
| 193634827 | 2034 | BAN003 | 1453.1086 | 27.597 | 28.0985 | 1257.4997 | 1481.2071 | 552.7844 | 1837.8811
| 203377333 | 2025 | BAN003 | 0 | 0 | 1481.912 | 66320.4908 | 1481.912 | 919.2872 | 67239.778
| 203377333 | 2026 | BAN003 | 0 | 0 | 1481.912 | 66320.4908 | 1481.912 | 919.2872 | 67239.778
| 203377333 | 2027 | BAN003 | 0 | 0 | 1481.912 | 66320.4908 | 1481.912 | 919.2872 | 67239.778
| 203377333 | 2028 | BAN003 | 0 | 0 | 1481.912 | 66320.4908 | 1481.912 | 919.2872 | 67239.778
| 203377333 | 2029 | BAN003 | 0 | 0 | 1481.912 | 66320.4908 | 1481.912 | 919.2872 | 67239.778
| 203377333 | 2030 | BAN003 | 0 | 0 | 1481.912 | 66320.4908 | 1481.912 | 919.2872 | 67239.778
| 203377333 | 2031 | BAN003 | 0 | 0 | 1481.912 | 66320.4908 | 1481.912 | 919.2872 | 67239.778
| 203377333 | 2032 | BAN003 | 0 | 0 | 1481.912 | 66320.4908 | 1481.912 | 919.2872 | 67239.778
| 203377333 | 2033 | BAN003 | 0 | 0 | 1481.912 | 66320.4908 | 1481.912 | 919.2872 | 67239.778
| 203377333 | 2034 | BAN003 | 0 | 0 | 1481.912 | 66320.4908 | 1481.912 | 919.2872 | 67239.778
| 20407357 | 2023 | BAN006 | 0 | 0 | 231.5748 | 10363.7415 | 231.5748 | 4732.203 | 15095.9444
| 20407357 | 2024 | BAN006 | 0 | 0 | 251.4019 | 11251.0702 | 251.4019 | 4732.203 | 15983.2732
| 20407357 | 2025 | BAN006 | 0 | 0 | 251.4019 | 11251.0702 | 251.4019 | 4732.203 | 15983.2732
| 20407357 | 2026 | BAN006 | 0 | 0 | 251.4019 | 11251.0702 | 251.4019 | 4732.203 | 15983.2732
| 20407357 | 2027 | BAN006 | 0 | 0 | 251.4019 | 11251.0702 | 251.4019 | 4732.203 | 15983.2732
| 20407357 | 2028 | BAN006 | 0 | 0 | 251.4019 | 11251.0702 | 251.4019 | 4732.203 | 15983.2732
| 20407357 | 2029 | BAN006 | 0 | 0 | 251.4019 | 11251.0702 | 251.4019 | 4732.203 | 15983.2732
| 20407357 | 2030 | BAN006 | 0 | 0 | 251.4019 | 11251.0702 | 251.4019 | 4732.203 | 15983.2732
| 20407357 | 2031 | BAN006 | 0 | 0 | 251.4019 | 11251.0702 | 251.4019 | 4732.203 | 15983.2732
| 20407357 | 2032 | BAN006 | 0 | 0 | 251.4019 | 11251.0702 | 251.4019 | 4732.203 | 15983.2732
| 20407357 | 2033 | BAN006 | 0 | 0 | 251.4019 | 11251.0702 | 251.4019 | 4732.203 | 15983.2732
| 20407357 | 2034 | BAN006 | 0 | 0 | 251.4019 | 11251.0702 | 251.4019 | 4732.203 | 15983.2732
| 84646930 | 2023 | BAN006 | 0 | 0 | 0 | 0 | 0 | 1977.8776 | 1977.8776
| 84646930 | 2024 | BAN006 | 537.5995 | 9.0741 | 0 | 0 | 537.5995 | 1977.8776 | 1986.9517
| 84646930 | 2025 | BAN006 | 537.5995 | 9.0741 | 0 | 0 | 537.5995 | 1977.8776 | 1986.9517
| 84646930 | 2026 | BAN006 | 537.5995 | 9.0741 | 0 | 0 | 537.5995 | 1977.8776 | 1986.9517
| 84646930 | 2027 | BAN006 | 537.5995 | 9.0741 | 0 | 0 | 537.5995 | 1977.8776 | 1986.9517
| 84646930 | 2028 | BAN006 | 537.5995 | 9.0741 | 0 | 0 | 537.5995 | 1977.8776 | 1986.9517
| 84646930 | 2029 | BAN006 | 537.5995 | 9.0741 | 0 | 0 | 537.5995 | 1977.8776 | 1986.9517
| 84646930 | 2030 | BAN006 | 537.5995 | 9.0741 | 0 | 0 | 537.5995 | 1977.8776 | 1986.9517
| 84646930 | 2031 | BAN006 | 537.5995 | 9.0741 | 0 | 0 | 537.5995 | 1977.8776 | 1986.9517
| 84646930 | 2032 | BAN006 | 537.5995 | 9.0741 | 0 | 0 | 537.5995 | 1977.8776 | 1986.9517
| 84646930 | 2033 | BAN006 | 537.5995 | 9.0741 | 0 | 0 | 537.5995 | 1977.8776 | 1986.9517
| 84646930 | 2034 | BAN006 | 537.5995 | 9.0741 | 0 | 0 | 537.5995 | 1977.8776 | 1986.9517
| 84647461 | 2023 | BAN006 | 9932.0227 | 0 | 50.6522 | 2266.8534 | 9982.6748 | 4939.0115 | 7205.8649
| 84647461 | 2024 | BAN006 | 18200.7428 | 324.0539 | 65.7255 | 2941.4354 | 18266.4683 | 4939.0115 | 8204.5008
| 84647461 | 2025 | BAN006 | 18200.7428 | 324.0539 | 65.7255 | 2941.4354 | 18266.4683 | 4939.0115 | 8204.5008
| 84647461 | 2026 | BAN006 | 18200.7428 | 324.0539 | 65.7255 | 2941.4354 | 18266.4683 | 4939.0115 | 8204.5008
| 84647461 | 2027 | BAN006 | 18200.7428 | 324.0539 | 65.7255 | 2941.4354 | 18266.4683 | 4939.0115 | 8204.5008
| 84647461 | 2028 | BAN006 | 18200.7428 | 324.0539 | 65.7255 | 2941.4354 | 18266.4683 | 4939.0115 | 8204.5008
| 84647461 | 2029 | BAN006 | 18200.7428 | 324.0539 | 65.7255 | 2941.4354 | 18266.4683 | 4939.0115 | 8204.5008
| 84647461 | 2030 | BAN006 | 18200.7428 | 324.0539 | 65.7255 | 2941.4354 | 18266.4683 | 4939.0115 | 8204.5008
| 84647461 | 2031 | BAN006 | 18200.7428 | 324.0539 | 65.7255 | 2941.4354 | 18266.4683 | 4939.0115 | 8204.5008
| 84647461 | 2032 | BAN006 | 18200.7428 | 324.0539 | 65.7255 | 2941.4354 | 18266.4683 | 4939.0115 | 8204.5008
| 84647461 | 2033 | BAN006 | 18200.7428 | 324.0539 | 65.7255 | 2941.4354 | 18266.4683 | 4939.0115 | 8204.5008
| 84647461 | 2034 | BAN006 | 18200.7428 | 324.0539 | 65.7255 | 2941.4354 | 18266.4683 | 4939.0115 | 8204.5008
| 85222431 | 2023 | BAN006 | 840.4951 | 0 | 0 | 0 | 840.4951 | 3341.5244 | 3341.5244
| 85222431 | 2024 | BAN006 | 809.5129 | 13.4693 | 0 | 0 | 809.5129 | 3341.5244 | 3354.9936
| 85222431 | 2025 | BAN006 | 809.5129 | 13.4693 | 0 | 0 | 809.5129 | 3341.5244 | 3354.9936
| 85222431 | 2026 | BAN006 | 809.5129 | 13.4693 | 0 | 0 | 809.5129 | 3341.5244 | 3354.9936
| 85222431 | 2027 | BAN006 | 809.5129 | 13.4693 | 0 | 0 | 809.5129 | 3341.5244 | 3354.9936
| 85222431 | 2028 | BAN006 | 809.5129 | 13.4693 | 0 | 0 | 809.5129 | 3341.5244 | 3354.9936
| 85222431 | 2029 | BAN006 | 809.5129 | 13.4693 | 0 | 0 | 809.5129 | 3341.5244 | 3354.9936
| 85222431 | 2030 | BAN006 | 809.5129 | 13.4693 | 0 | 0 | 809.5129 | 3341.5244 | 3354.9936
| 85222431 | 2031 | BAN006 | 809.5129 | 13.4693 | 0 | 0 | 809.5129 | 3341.5244 | 3354.9936
| 85222431 | 2032 | BAN006 | 809.5129 | 13.4693 | 0 | 0 | 809.5129 | 3341.5244 | 3354.9936
| 85222431 | 2033 | BAN006 | 809.5129 | 13.4693 | 0 | 0 | 809.5129 | 3341.5244 | 3354.9936
| 85222431 | 2034 | BAN006 | 809.5129 | 13.4693 | 0 | 0 | 809.5129 | 3341.5244 | 3354.9936
| 182632546 | 2023 | BAN006 | 0 | 0 | 93110.0415 | 4166984.1379 | 93110.0415 | 10260.8937 | 4177245.0315
| 182632546 | 2024 | BAN006 | 0 | 0 | 94325.8236 | 4221394.4329 | 94325.8236 | 10260.8937 | 4231655.3265
| 182632546 | 2025 | BAN006 | 0 | 0 | 94325.8236 | 4221394.4329 | 94325.8236 | 10260.8937 | 4231655.3265
| 182632546 | 2026 | BAN006 | 0 | 0 | 94325.8236 | 4221394.4329 | 94325.8236 | 10260.8937 | 4231655.3265
| 182632546 | 2027 | BAN006 | 0 | 0 | 94325.8236 | 4221394.4329 | 94325.8236 | 10260.8937 | 4231655.3265
| 182632546 | 2028 | BAN006 | 0 | 0 | 94325.8236 | 4221394.4329 | 94325.8236 | 10260.8937 | 4231655.3265
| 182632546 | 2029 | BAN006 | 0 | 0 | 94325.8236 | 4221394.4329 | 94325.8236 | 10260.8937 | 4231655.3265
| 182632546 | 2030 | BAN006 | 0 | 0 | 94325.8236 | 4221394.4329 | 94325.8236 | 10260.8937 | 4231655.3265
| 182632546 | 2031 | BAN006 | 0 | 0 | 94325.8236 | 4221394.4329 | 94325.8236 | 10260.8937 | 4231655.3265
| 182632546 | 2032 | BAN006 | 0 | 0 | 94325.8236 | 4221394.4329 | 94325.8236 | 10260.8937 | 4231655.3265
| 182632546 | 2033 | BAN006 | 0 | 0 | 94325.8236 | 4221394.4329 | 94325.8236 | 10260.8937 | 4231655.3265
| 182632546 | 2034 | BAN006 | 0 | 0 | 94325.8236 | 4221394.4329 | 94325.8236 | 10260.8937 | 4231655.3265
| 20072996 | 2023 | BBD014 | 0 | 0 | 0 | 0 | 0 | 13532.8553 | 13532.8553
| 20072996 | 2024 | BBD014 | 0 | 0 | 0 | 0 | 0 | 13532.8553 | 13532.8553
| 20072996 | 2025 | BBD014 | 0 | 0 | 0 | 0 | 0 | 13532.8553 | 13532.8553
| 20072996 | 2026 | BBD014 | 0 | 0 | 0 | 0 | 0 | 13532.8553 | 13532.8553
| 20072996 | 2027 | BBD014 | 0 | 0 | 0 | 0 | 0 | 13532.8553 | 13532.8553
| 20072996 | 2028 | BBD014 | 0 | 0 | 0 | 0 | 0 | 13532.8553 | 13532.8553
| 20072996 | 2029 | BBD014 | 0 | 0 | 0 | 0 | 0 | 13532.8553 | 13532.8553
| 20072996 | 2030 | BBD014 | 0 | 0 | 0 | 0 | 0 | 13532.8553 | 13532.8553
| 20072996 | 2031 | BBD014 | 0 | 0 | 0 | 0 | 0 | 13532.8553 | 13532.8553
| 20072996 | 2032 | BBD014 | 0 | 0 | 0 | 0 | 0 | 13532.8553 | 13532.8553
| 20072996 | 2033 | BBD014 | 0 | 0 | 0 | 0 | 0 | 13532.8553 | 13532.8553
| 20072996 | 2034 | BBD014 | 0 | 0 | 0 | 0 | 0 | 13532.8553 | 13532.8553
| 20074279 | 2023 | BBD014 | 5856.9475 | 0 | 0 | 0 | 5856.9475 | 15885.3983 | 15885.3983
| 20074279 | 2024 | BBD014 | 5886.9416 | 149 | 0 | 0 | 5886.9416 | 15885.3983 | 16034.3984
| 20074279 | 2025 | BBD014 | 5816.4711 | 169.5025 | 0 | 0 | 5816.4711 | 15885.3983 | 16054.9009
| 20074279 | 2026 | BBD014 | 5784.1798 | 109.1467 | 0 | 0 | 5784.1798 | 15885.3983 | 15994.5451
| 20074279 | 2027 | BBD014 | 12982.1923 | 279.6819 | 0 | 0 | 12982.1923 | 15885.3983 | 16165.0803
| 20074279 | 2028 | BBD014 | 13043.3197 | 313.1682 | 0 | 0 | 13043.3197 | 15885.3983 | 16198.5665
| 20074279 | 2029 | BBD014 | 13241.6444 | 263.9631 | 0 | 0 | 13241.6444 | 15885.3983 | 16149.3615
| 20074279 | 2030 | BBD014 | 17898.1448 | 375.579 | 0 | 0 | 17898.1448 | 15885.3983 | 16260.9774
| 20074279 | 2031 | BBD014 | 17813.4118 | 409.8789 | 0 | 0 | 17813.4118 | 15885.3983 | 16295.2773
| 20074279 | 2032 | BBD014 | 23153.0147 | 667.6282 | 0 | 0 | 23153.0147 | 15885.3983 | 16553.0266
| 20074279 | 2033 | BBD014 | 23153.0147 | 908.646 | 0 | 0 | 23153.0147 | 15885.3983 | 16794.0444
| 20074279 | 2034 | BBD014 | 22995.1774 | 1003.1771 | 0 | 0 | 22995.1774 | 15885.3983 | 16888.5755
| 20209655 | 2023 | BET005 | 0 | 0 | 0 | 0 | 0 | 2762.501 | 2762.501
| 20209655 | 2024 | BET005 | 0 | 0 | 0 | 0 | 0 | 2762.501 | 2762.501
| 20209655 | 2025 | BET005 | 0 | 0 | 0 | 0 | 0 | 2762.501 | 2762.501
| 20209655 | 2026 | BET005 | 0 | 0 | 0 | 0 | 0 | 2762.501 | 2762.501
| 20209655 | 2027 | BET005 | 0 | 0 | 0 | 0 | 0 | 2762.501 | 2762.501
| 20209655 | 2028 | BET005 | 0 | 0 | 0 | 0 | 0 | 2762.501 | 2762.501
| 20209655 | 2029 | BET005 | 0 | 0 | 0 | 0 | 0 | 2762.501 | 2762.501
| 20209655 | 2030 | BET005 | 0 | 0 | 0 | 0 | 0 | 2762.501 | 2762.501
| 20209655 | 2031 | BET005 | 0 | 0 | 0 | 0 | 0 | 2762.501 | 2762.501
| 20209655 | 2032 | BET005 | 0 | 0 | 0 | 0 | 0 | 2762.501 | 2762.501
| 20209655 | 2033 | BET005 | 0 | 0 | 0 | 0 | 0 | 2762.501 | 2762.501
| 20209655 | 2034 | BET005 | 0 | 0 | 0 | 0 | 0 | 2762.501 | 2762.501
| 20218091 | 2023 | BET005 | 52.9341 | 0 | 0 | 0 | 52.9341 | 667.4963 | 667.4963
| 20218091 | 2024 | BET005 | 52.9669 | 0.6178 | 0 | 0 | 52.9669 | 667.4963 | 668.1141
| 20218091 | 2025 | BET005 | 33.5922 | 0.53211 | 0 | 0 | 33.5922 | 667.4963 | 668.0284
| 20218091 | 2026 | BET005 | 33.5922 | 0.53211 | 0 | 0 | 33.5922 | 667.4963 | 668.0284
| 20218091 | 2027 | BET005 | 33.5922 | 0.53211 | 0 | 0 | 33.5922 | 667.4963 | 668.0284
| 20218091 | 2028 | BET005 | 33.5922 | 0.53211 | 0 | 0 | 33.5922 | 667.4963 | 668.0284
| 20218091 | 2029 | BET005 | 33.5922 | 0.53211 | 0 | 0 | 33.5922 | 667.4963 | 668.0284
| 20218091 | 2030 | BET005 | 33.5922 | 0.53211 | 0 | 0 | 33.5922 | 667.4963 | 668.0284
| 20218091 | 2031 | BET005 | 33.5922 | 0.53211 | 0 | 0 | 33.5922 | 667.4963 | 668.0284
| 20218091 | 2032 | BET005 | 33.5922 | 0.53211 | 0 | 0 | 33.5922 | 667.4963 | 668.0284
| 20218091 | 2033 | BET005 | 33.5922 | 0.53211 | 0 | 0 | 33.5922 | 667.4963 | 668.0284
| 20218091 | 2034 | BET005 | 33.5922 | 0.53211 | 0 | 0 | 33.5922 | 667.4963 | 668.0284
| 20516133 | 2023 | BET005 | 0 | 0 | 0 | 0 | 0 | 3119.1262 | 3119.1262
| 20516133 | 2024 | BET005 | 0 | 0 | 0 | 0 | 0 | 3119.1262 | 3119.1262
| 20516133 | 2025 | BET005 | 0 | 0 | 6.4445 | 282.3694 | 6.4445 | 3119.1262 | 3401.4956
| 20516133 | 2026 | BET005 | 0 | 0 | 6.4445 | 282.3694 | 6.4445 | 3119.1262 | 3401.4956
| 20516133 | 2027 | BET005 | 0 | 0 | 6.4445 | 282.3694 | 6.4445 | 3119.1262 | 3401.4956
| 20516133 | 2028 | BET005 | 0 | 0 | 6.4445 | 282.3694 | 6.4445 | 3119.1262 | 3401.4956
| 20516133 | 2029 | BET005 | 0 | 0 | 6.4445 | 282.3694 | 6.4445 | 3119.1262 | 3401.4956
| 20516133 | 2030 | BET005 | 0 | 0 | 6.4445 | 282.3694 | 6.4445 | 3119.1262 | 3401.4956
| 20516133 | 2031 | BET005 | 0 | 0 | 6.4445 | 282.3694 | 6.4445 | 3119.1262 | 3401.4956
| 20516133 | 2032 | BET005 | 0 | 0 | 6.4445 | 282.3694 | 6.4445 | 3119.1262 | 3401.4956
| 20516133 | 2033 | BET005 | 0 | 0 | 6.4445 | 282.3694 | 6.4445 | 3119.1262 | 3401.4956
| 20516133 | 2034 | BET005 | 0 | 0 | 6.4445 | 282.3694 | 6.4445 | 3119.1262 | 3401.4956
| 20620160 | 2023 | BET005 | 0 | 0 | 26.212 | 1148.4927 | 26.212 | 4907.4375 | 6055.9302
| 20620160 | 2024 | BET005 | 0 | 0 | 30.2782 | 1326.6557 | 30.2782 | 4907.4375 | 6234.0932
| 20620160 | 2025 | BET005 | 0 | 0 | 37.0143 | 1621.8021 | 37.0143 | 4907.4375 | 6529.2396
| 20620160 | 2026 | BET005 | 0 | 0 | 37.0143 | 1621.8021 | 37.0143 | 4907.4375 | 6529.2396
| 20620160 | 2027 | BET005 | 0 | 0 | 37.0143 | 1621.8021 | 37.0143 | 4907.4375 | 6529.2396
| 20620160 | 2028 | BET005 | 0 | 0 | 37.0143 | 1621.8021 | 37.0143 | 4907.4375 | 6529.2396
| 20620160 | 2029 | BET005 | 0 | 0 | 37.0143 | 1621.8021 | 37.0143 | 4907.4375 | 6529.2396
| 20620160 | 2030 | BET005 | 0 | 0 | 37.0143 | 1621.8021 | 37.0143 | 4907.4375 | 6529.2396
| 20620160 | 2031 | BET005 | 0 | 0 | 37.0143 | 1621.8021 | 37.0143 | 4907.4375 | 6529.2396
| 20620160 | 2032 | BET005 | 0 | 0 | 37.0143 | 1621.8021 | 37.0143 | 4907.4375 | 6529.2396
| 20620160 | 2033 | BET005 | 0 | 0 | 37.0143 | 1621.8021 | 37.0143 | 4907.4375 | 6529.2396
| 20620160 | 2034 | BET005 | 0 | 0 | 37.0143 | 1621.8021 | 37.0143 | 4907.4375 | 6529.2396
| 20632173 | 2023 | BET005 | 2893.5717 | 0 | 0 | 0 | 2893.5717 | 4966.1549 | 4966.1549
| 20632173 | 2024 | BET005 | 3123.6523 | 64.7493 | 0 | 0 | 3123.6523 | 4966.1549 | 5030.9041
| 20632173 | 2025 | BET005 | 5441.4394 | 83.8841 | 0.0013144 | 0.057592 | 5441.4407 | 4966.1549 | 5050.0966
| 20632173 | 2026 | BET005 | 5441.4394 | 83.8841 | 0.0013144 | 0.057592 | 5441.4407 | 4966.1549 | 5050.0966
| 20632173 | 2027 | BET005 | 5441.4394 | 83.8841 | 0.0013144 | 0.057592 | 5441.4407 | 4966.1549 | 5050.0966
| 20632173 | 2028 | BET005 | 5441.4394 | 83.8841 | 0.0013144 | 0.057592 | 5441.4407 | 4966.1549 | 5050.0966
| 20632173 | 2029 | BET005 | 5441.4394 | 83.8841 | 0.0013144 | 0.057592 | 5441.4407 | 4966.1549 | 5050.0966
| 20632173 | 2030 | BET005 | 5441.4394 | 83.8841 | 0.0013144 | 0.057592 | 5441.4407 | 4966.1549 | 5050.0966
| 20632173 | 2031 | BET005 | 5441.4394 | 83.8841 | 0.0013144 | 0.057592 | 5441.4407 | 4966.1549 | 5050.0966
| 20632173 | 2032 | BET005 | 5441.4394 | 83.8841 | 0.0013144 | 0.057592 | 5441.4407 | 4966.1549 | 5050.0966
| 20632173 | 2033 | BET005 | 5441.4394 | 83.8841 | 0.0013144 | 0.057592 | 5441.4407 | 4966.1549 | 5050.0966
| 20632173 | 2034 | BET005 | 5441.4394 | 83.8841 | 0.0013144 | 0.057592 | 5441.4407 | 4966.1549 | 5050.0966
| 20632191 | 2023 | BET005 | 1795.9271 | 0 | 0 | 0 | 1795.9271 | 3553.2898 | 3553.2898
| 20632191 | 2024 | BET005 | 2194.9737 | 34.7482 | 0 | 0 | 2194.9737 | 3553.2898 | 3588.038
| 20632191 | 2025 | BET005 | 8570.757 | 165.6053 | 0 | 0 | 8570.757 | 3553.2898 | 3718.8951
| 20632191 | 2026 | BET005 | 8570.757 | 165.6053 | 0 | 0 | 8570.757 | 3553.2898 | 3718.8951
| 20632191 | 2027 | BET005 | 8570.757 | 165.6053 | 0 | 0 | 8570.757 | 3553.2898 | 3718.8951
| 20632191 | 2028 | BET005 | 8570.757 | 165.6053 | 0 | 0 | 8570.757 | 3553.2898 | 3718.8951
| 20632191 | 2029 | BET005 | 8570.757 | 165.6053 | 0 | 0 | 8570.757 | 3553.2898 | 3718.8951
| 20632191 | 2030 | BET005 | 8570.757 | 165.6053 | 0 | 0 | 8570.757 | 3553.2898 | 3718.8951
| 20632191 | 2031 | BET005 | 8570.757 | 165.6053 | 0 | 0 | 8570.757 | 3553.2898 | 3718.8951
| 20632191 | 2032 | BET005 | 8570.757 | 165.6053 | 0 | 0 | 8570.757 | 3553.2898 | 3718.8951
| 20632191 | 2033 | BET005 | 8570.757 | 165.6053 | 0 | 0 | 8570.757 | 3553.2898 | 3718.8951
| 20632191 | 2034 | BET005 | 8570.757 | 165.6053 | 0 | 0 | 8570.757 | 3553.2898 | 3718.8951
| 110828634 | 2023 | BET005 | 0 | 0 | 0 | 0 | 0 | 3545.0728 | 3545.0728
| 110828634 | 2024 | BET005 | 0 | 0 | 0 | 0 | 0 | 3545.0728 | 3545.0728
| 110828634 | 2025 | BET005 | 0 | 0 | 0 | 0 | 0 | 3545.0728 | 3545.0728
| 110828634 | 2026 | BET005 | 0 | 0 | 0 | 0 | 0 | 3545.0728 | 3545.0728
| 110828634 | 2027 | BET005 | 0 | 0 | 0 | 0 | 0 | 3545.0728 | 3545.0728
| 110828634 | 2028 | BET005 | 0 | 0 | 0 | 0 | 0 | 3545.0728 | 3545.0728
| 110828634 | 2029 | BET005 | 0 | 0 | 0 | 0 | 0 | 3545.0728 | 3545.0728
| 110828634 | 2030 | BET005 | 0 | 0 | 0 | 0 | 0 | 3545.0728 | 3545.0728
| 110828634 | 2031 | BET005 | 0 | 0 | 0 | 0 | 0 | 3545.0728 | 3545.0728
| 110828634 | 2032 | BET005 | 0 | 0 | 0 | 0 | 0 | 3545.0728 | 3545.0728
| 110828634 | 2033 | BET005 | 0 | 0 | 0 | 0 | 0 | 3545.0728 | 3545.0728
| 110828634 | 2034 | BET005 | 0 | 0 | 0 | 0 | 0 | 3545.0728 | 3545.0728
| 117327676 | 2023 | BET005 | 0 | 0 | 0 | 0 | 0 | 226.1183 | 226.1183
| 117327676 | 2024 | BET005 | 0 | 0 | 0 | 0 | 0 | 226.1183 | 226.1183
| 117327676 | 2025 | BET005 | 0 | 0 | 0 | 0 | 0 | 226.1183 | 226.1183
| 117327676 | 2026 | BET005 | 0 | 0 | 0 | 0 | 0 | 226.1183 | 226.1183
| 117327676 | 2027 | BET005 | 0 | 0 | 0 | 0 | 0 | 226.1183 | 226.1183
| 117327676 | 2028 | BET005 | 0 | 0 | 0 | 0 | 0 | 226.1183 | 226.1183
| 117327676 | 2029 | BET005 | 0 | 0 | 0 | 0 | 0 | 226.1183 | 226.1183
| 117327676 | 2030 | BET005 | 0 | 0 | 0 | 0 | 0 | 226.1183 | 226.1183
| 117327676 | 2031 | BET005 | 0 | 0 | 0 | 0 | 0 | 226.1183 | 226.1183
| 117327676 | 2032 | BET005 | 0 | 0 | 0 | 0 | 0 | 226.1183 | 226.1183
| 117327676 | 2033 | BET005 | 0 | 0 | 0 | 0 | 0 | 226.1183 | 226.1183
| 117327676 | 2034 | BET005 | 0 | 0 | 0 | 0 | 0 | 226.1183 | 226.1183
| 160958288 | 2023 | BET005 | 2592.5049 | 0 | 0 | 0 | 2592.5049 | 4978.0023 | 4978.0023
| 160958288 | 2024 | BET005 | 2631.7431 | 56.1378 | 0 | 0 | 2631.7431 | 4978.0023 | 5034.14
| 160958288 | 2025 | BET005 | 2599.481 | 58.0422 | 1.2511 | 54.8173 | 2600.7321 | 4978.0023 | 5090.8618
| 160958288 | 2026 | BET005 | 2599.481 | 58.0422 | 1.2511 | 54.8173 | 2600.7321 | 4978.0023 | 5090.8618
| 160958288 | 2027 | BET005 | 2599.481 | 58.0422 | 1.2511 | 54.8173 | 2600.7321 | 4978.0023 | 5090.8618
| 160958288 | 2028 | BET005 | 2599.481 | 58.0422 | 1.2511 | 54.8173 | 2600.7321 | 4978.0023 | 5090.8618
| 160958288 | 2029 | BET005 | 2599.481 | 58.0422 | 1.2511 | 54.8173 | 2600.7321 | 4978.0023 | 5090.8618
| 160958288 | 2030 | BET005 | 2599.481 | 58.0422 | 1.2511 | 54.8173 | 2600.7321 | 4978.0023 | 5090.8618
| 160958288 | 2031 | BET005 | 2599.481 | 58.0422 | 1.2511 | 54.8173 | 2600.7321 | 4978.0023 | 5090.8618
| 160958288 | 2032 | BET005 | 2599.481 | 58.0422 | 1.2511 | 54.8173 | 2600.7321 | 4978.0023 | 5090.8618
| 160958288 | 2033 | BET005 | 2599.481 | 58.0422 | 1.2511 | 54.8173 | 2600.7321 | 4978.0023 | 5090.8618
| 160958288 | 2034 | BET005 | 2599.481 | 58.0422 | 1.2511 | 54.8173 | 2600.7321 | 4978.0023 | 5090.8618
| 20242298 | 2023 | BET007 | 0 | 0 | 9.4731 | 415.0699 | 9.4731 | 1354.266 | 1769.3359
| 20242298 | 2024 | BET007 | 0 | 0 | 9.4731 | 415.0699 | 9.4731 | 1354.266 | 1769.3359
| 20242298 | 2025 | BET007 | 0 | 0 | 9.4731 | 415.0699 | 9.4731 | 1354.266 | 1769.3359
| 20242298 | 2026 | BET007 | 0 | 0 | 9.4731 | 415.0699 | 9.4731 | 1354.266 | 1769.3359
| 20242298 | 2027 | BET007 | 0 | 0 | 9.4731 | 415.0699 | 9.4731 | 1354.266 | 1769.3359
| 20242298 | 2028 | BET007 | 0 | 0 | 9.4731 | 415.0699 | 9.4731 | 1354.266 | 1769.3359
| 20242298 | 2029 | BET007 | 0 | 0 | 9.4731 | 415.0699 | 9.4731 | 1354.266 | 1769.3359
| 20242298 | 2030 | BET007 | 0 | 0 | 9.4731 | 415.0699 | 9.4731 | 1354.266 | 1769.3359
| 20242298 | 2031 | BET007 | 0 | 0 | 9.4731 | 415.0699 | 9.4731 | 1354.266 | 1769.3359
| 20242298 | 2032 | BET007 | 0 | 0 | 9.4731 | 415.0699 | 9.4731 | 1354.266 | 1769.3359
| 20242298 | 2033 | BET007 | 0 | 0 | 9.4731 | 415.0699 | 9.4731 | 1354.266 | 1769.3359
| 20242298 | 2034 | BET007 | 0 | 0 | 9.4731 | 415.0699 | 9.4731 | 1354.266 | 1769.3359
| 20330141 | 2023 | BET007 | 0 | 0 | 0.64463 | 28.2447 | 0.64463 | 579.9538 | 608.1985
| 20330141 | 2024 | BET007 | 0 | 0 | 0.64463 | 28.2447 | 0.64463 | 579.9538 | 608.1985
| 20330141 | 2025 | BET007 | 0 | 0 | 0.64463 | 28.2447 | 0.64463 | 579.9538 | 608.1985
| 20330141 | 2026 | BET007 | 0 | 0 | 0.64463 | 28.2447 | 0.64463 | 579.9538 | 608.1985
| 20330141 | 2027 | BET007 | 0 | 0 | 0.64463 | 28.2447 | 0.64463 | 579.9538 | 608.1985
| 20330141 | 2028 | BET007 | 0 | 0 | 0.64463 | 28.2447 | 0.64463 | 579.9538 | 608.1985
| 20330141 | 2029 | BET007 | 0 | 0 | 0.64463 | 28.2447 | 0.64463 | 579.9538 | 608.1985
| 20330141 | 2030 | BET007 | 0 | 0 | 0.64463 | 28.2447 | 0.64463 | 579.9538 | 608.1985
| 20330141 | 2031 | BET007 | 0 | 0 | 0.64463 | 28.2447 | 0.64463 | 579.9538 | 608.1985
| 20330141 | 2032 | BET007 | 0 | 0 | 0.64463 | 28.2447 | 0.64463 | 579.9538 | 608.1985
| 20330141 | 2033 | BET007 | 0 | 0 | 0.64463 | 28.2447 | 0.64463 | 579.9538 | 608.1985
| 20330141 | 2034 | BET007 | 0 | 0 | 0.64463 | 28.2447 | 0.64463 | 579.9538 | 608.1985
| 20491272 | 2023 | BET007 | 0 | 0 | 6720.3905 | 294457.6637 | 6720.3905 | 3211.6678 | 297669.3315
| 20491272 | 2024 | BET007 | 0 | 0 | 6720.3905 | 294457.6637 | 6720.3905 | 3211.6678 | 297669.3315
| 20491272 | 2025 | BET007 | 0 | 0 | 6720.3905 | 294457.6637 | 6720.3905 | 3211.6678 | 297669.3315
| 20491272 | 2026 | BET007 | 0 | 0 | 6720.3905 | 294457.6637 | 6720.3905 | 3211.6678 | 297669.3315
| 20491272 | 2027 | BET007 | 0 | 0 | 6720.3905 | 294457.6637 | 6720.3905 | 3211.6678 | 297669.3315
| 20491272 | 2028 | BET007 | 0 | 0 | 6720.3905 | 294457.6637 | 6720.3905 | 3211.6678 | 297669.3315
| 20491272 | 2029 | BET007 | 0 | 0 | 6720.3905 | 294457.6637 | 6720.3905 | 3211.6678 | 297669.3315
| 20491272 | 2030 | BET007 | 0 | 0 | 6720.3905 | 294457.6637 | 6720.3905 | 3211.6678 | 297669.3315
| 20491272 | 2031 | BET007 | 0 | 0 | 6720.3905 | 294457.6637 | 6720.3905 | 3211.6678 | 297669.3315
| 20491272 | 2032 | BET007 | 0 | 0 | 6720.3905 | 294457.6637 | 6720.3905 | 3211.6678 | 297669.3315
| 20491272 | 2033 | BET007 | 0 | 0 | 6720.3905 | 294457.6637 | 6720.3905 | 3211.6678 | 297669.3315
| 20491272 | 2034 | BET007 | 0 | 0 | 6720.3905 | 294457.6637 | 6720.3905 | 3211.6678 | 297669.3315
| 20491781 | 2023 | BET007 | 0 | 0 | 0.0028472 | 0.12475 | 0.0028472 | 2429.3649 | 2429.4897
| 20491781 | 2024 | BET007 | 0 | 0 | 0.0028472 | 0.12475 | 0.0028472 | 2429.3649 | 2429.4897
| 20491781 | 2025 | BET007 | 0 | 0 | 0.0028472 | 0.12475 | 0.0028472 | 2429.3649 | 2429.4897
| 20491781 | 2026 | BET007 | 0 | 0 | 0.0028472 | 0.12475 | 0.0028472 | 2429.3649 | 2429.4897
| 20491781 | 2027 | BET007 | 0 | 0 | 0.0028472 | 0.12475 | 0.0028472 | 2429.3649 | 2429.4897
| 20491781 | 2028 | BET007 | 0 | 0 | 0.0028472 | 0.12475 | 0.0028472 | 2429.3649 | 2429.4897
| 20491781 | 2029 | BET007 | 0 | 0 | 0.0028472 | 0.12475 | 0.0028472 | 2429.3649 | 2429.4897
| 20491781 | 2030 | BET007 | 0 | 0 | 0.0028472 | 0.12475 | 0.0028472 | 2429.3649 | 2429.4897
| 20491781 | 2031 | BET007 | 0 | 0 | 0.0028472 | 0.12475 | 0.0028472 | 2429.3649 | 2429.4897
| 20491781 | 2032 | BET007 | 0 | 0 | 0.0028472 | 0.12475 | 0.0028472 | 2429.3649 | 2429.4897
| 20491781 | 2033 | BET007 | 0 | 0 | 0.0028472 | 0.12475 | 0.0028472 | 2429.3649 | 2429.4897
| 20491781 | 2034 | BET007 | 0 | 0 | 0.0028472 | 0.12475 | 0.0028472 | 2429.3649 | 2429.4897
| 20499023 | 2023 | BET007 | 0 | 0 | 1752.5764 | 76790.1152 | 1752.5764 | 3738.4466 | 80528.5617
| 20499023 | 2024 | BET007 | 0 | 0 | 1752.5764 | 76790.1152 | 1752.5764 | 3738.4466 | 80528.5617
| 20499023 | 2025 | BET007 | 0 | 0 | 1752.5764 | 76790.1152 | 1752.5764 | 3738.4466 | 80528.5617
| 20499023 | 2026 | BET007 | 0 | 0 | 1752.5764 | 76790.1152 | 1752.5764 | 3738.4466 | 80528.5617
| 20499023 | 2027 | BET007 | 0 | 0 | 1752.5764 | 76790.1152 | 1752.5764 | 3738.4466 | 80528.5617
| 20499023 | 2028 | BET007 | 0 | 0 | 1752.5764 | 76790.1152 | 1752.5764 | 3738.4466 | 80528.5617
| 20499023 | 2029 | BET007 | 0 | 0 | 1752.5764 | 76790.1152 | 1752.5764 | 3738.4466 | 80528.5617
| 20499023 | 2030 | BET007 | 0 | 0 | 1752.5764 | 76790.1152 | 1752.5764 | 3738.4466 | 80528.5617
| 20499023 | 2031 | BET007 | 0 | 0 | 1752.5764 | 76790.1152 | 1752.5764 | 3738.4466 | 80528.5617
| 20499023 | 2032 | BET007 | 0 | 0 | 1752.5764 | 76790.1152 | 1752.5764 | 3738.4466 | 80528.5617
| 20499023 | 2033 | BET007 | 0 | 0 | 1752.5764 | 76790.1152 | 1752.5764 | 3738.4466 | 80528.5617
| 20499023 | 2034 | BET007 | 0 | 0 | 1752.5764 | 76790.1152 | 1752.5764 | 3738.4466 | 80528.5617
| 20588628 | 2023 | BET007 | 0 | 0 | 11.2493 | 492.8923 | 11.2493 | 5537.3325 | 6030.2248
| 20588628 | 2024 | BET007 | 0 | 0 | 11.2493 | 492.8923 | 11.2493 | 5537.3325 | 6030.2248
| 20588628 | 2025 | BET007 | 0 | 0 | 11.2493 | 492.8923 | 11.2493 | 5537.3325 | 6030.2248
| 20588628 | 2026 | BET007 | 0 | 0 | 11.2493 | 492.8923 | 11.2493 | 5537.3325 | 6030.2248
| 20588628 | 2027 | BET007 | 0 | 0 | 11.2493 | 492.8923 | 11.2493 | 5537.3325 | 6030.2248
| 20588628 | 2028 | BET007 | 0 | 0 | 11.2493 | 492.8923 | 11.2493 | 5537.3325 | 6030.2248
| 20588628 | 2029 | BET007 | 0 | 0 | 11.2493 | 492.8923 | 11.2493 | 5537.3325 | 6030.2248
| 20588628 | 2030 | BET007 | 0 | 0 | 11.2493 | 492.8923 | 11.2493 | 5537.3325 | 6030.2248
| 20588628 | 2031 | BET007 | 0 | 0 | 11.2493 | 492.8923 | 11.2493 | 5537.3325 | 6030.2248
| 20588628 | 2032 | BET007 | 0 | 0 | 11.2493 | 492.8923 | 11.2493 | 5537.3325 | 6030.2248
| 20588628 | 2033 | BET007 | 0 | 0 | 11.2493 | 492.8923 | 11.2493 | 5537.3325 | 6030.2248
| 20588628 | 2034 | BET007 | 0 | 0 | 11.2493 | 492.8923 | 11.2493 | 5537.3325 | 6030.2248
| 110330728 | 2023 | BET007 | 0 | 0 | 35.4185 | 1551.8818 | 35.4185 | 2268.2559 | 3820.1377
| 110330728 | 2024 | BET007 | 0 | 0 | 35.4185 | 1551.8818 | 35.4185 | 2268.2559 | 3820.1377
| 110330728 | 2025 | BET007 | 0 | 0 | 35.4185 | 1551.8818 | 35.4185 | 2268.2559 | 3820.1377
| 110330728 | 2026 | BET007 | 0 | 0 | 35.4185 | 1551.8818 | 35.4185 | 2268.2559 | 3820.1377
| 110330728 | 2027 | BET007 | 0 | 0 | 35.4185 | 1551.8818 | 35.4185 | 2268.2559 | 3820.1377
| 110330728 | 2028 | BET007 | 0 | 0 | 35.4185 | 1551.8818 | 35.4185 | 2268.2559 | 3820.1377
| 110330728 | 2029 | BET007 | 0 | 0 | 35.4185 | 1551.8818 | 35.4185 | 2268.2559 | 3820.1377
| 110330728 | 2030 | BET007 | 0 | 0 | 35.4185 | 1551.8818 | 35.4185 | 2268.2559 | 3820.1377
| 110330728 | 2031 | BET007 | 0 | 0 | 35.4185 | 1551.8818 | 35.4185 | 2268.2559 | 3820.1377
| 110330728 | 2032 | BET007 | 0 | 0 | 35.4185 | 1551.8818 | 35.4185 | 2268.2559 | 3820.1377
| 110330728 | 2033 | BET007 | 0 | 0 | 35.4185 | 1551.8818 | 35.4185 | 2268.2559 | 3820.1377
| 110330728 | 2034 | BET007 | 0 | 0 | 35.4185 | 1551.8818 | 35.4185 | 2268.2559 | 3820.1377
| 156484100 | 2023 | BET007 | 0 | 0 | 84.8264 | 3716.715 | 84.8264 | 1431.1278 | 5147.8428
| 156484100 | 2024 | BET007 | 0 | 0 | 84.8264 | 3716.715 | 84.8264 | 1431.1278 | 5147.8428
| 156484100 | 2025 | BET007 | 0 | 0 | 84.8264 | 3716.715 | 84.8264 | 1431.1278 | 5147.8428
| 156484100 | 2026 | BET007 | 0 | 0 | 84.8264 | 3716.715 | 84.8264 | 1431.1278 | 5147.8428
| 156484100 | 2027 | BET007 | 0 | 0 | 84.8264 | 3716.715 | 84.8264 | 1431.1278 | 5147.8428
| 156484100 | 2028 | BET007 | 0 | 0 | 84.8264 | 3716.715 | 84.8264 | 1431.1278 | 5147.8428
| 156484100 | 2029 | BET007 | 0 | 0 | 84.8264 | 3716.715 | 84.8264 | 1431.1278 | 5147.8428
| 156484100 | 2030 | BET007 | 0 | 0 | 84.8264 | 3716.715 | 84.8264 | 1431.1278 | 5147.8428
| 156484100 | 2031 | BET007 | 0 | 0 | 84.8264 | 3716.715 | 84.8264 | 1431.1278 | 5147.8428
| 156484100 | 2032 | BET007 | 0 | 0 | 84.8264 | 3716.715 | 84.8264 | 1431.1278 | 5147.8428
| 156484100 | 2033 | BET007 | 0 | 0 | 84.8264 | 3716.715 | 84.8264 | 1431.1278 | 5147.8428
| 156484100 | 2034 | BET007 | 0 | 0 | 84.8264 | 3716.715 | 84.8264 | 1431.1278 | 5147.8428
| 20210329 | 2023 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.0118 | 501.0118
| 20210329 | 2024 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.0118 | 501.0118
| 20210329 | 2025 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.0118 | 501.0118
| 20210329 | 2026 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.0118 | 501.0118
| 20210329 | 2027 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.0118 | 501.0118
| 20210329 | 2028 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.0118 | 501.0118
| 20210329 | 2029 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.0118 | 501.0118
| 20210329 | 2030 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.0118 | 501.0118
| 20210329 | 2031 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.0118 | 501.0118
| 20210329 | 2032 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.0118 | 501.0118
| 20210329 | 2033 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.0118 | 501.0118
| 20210329 | 2034 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.0118 | 501.0118
| 20368770 | 2023 | BGO023 | 0 | 0 | 0 | 0 | 0 | 2124.123 | 2124.123
| 20368770 | 2024 | BGO023 | 2668.6549 | 77.8544 | 0 | 0 | 2668.6549 | 2124.123 | 2201.9774
| 20368770 | 2025 | BGO023 | 753.788 | 21.1383 | 0 | 0 | 753.788 | 2124.123 | 2145.2613
| 20368770 | 2026 | BGO023 | 753.788 | 21.1383 | 0 | 0 | 753.788 | 2124.123 | 2145.2613
| 20368770 | 2027 | BGO023 | 753.788 | 21.1383 | 0 | 0 | 753.788 | 2124.123 | 2145.2613
| 20368770 | 2028 | BGO023 | 753.788 | 21.1383 | 0 | 0 | 753.788 | 2124.123 | 2145.2613
| 20368770 | 2029 | BGO023 | 753.788 | 21.1383 | 0 | 0 | 753.788 | 2124.123 | 2145.2613
| 20368770 | 2030 | BGO023 | 753.788 | 21.1383 | 0 | 0 | 753.788 | 2124.123 | 2145.2613
| 20368770 | 2031 | BGO023 | 753.788 | 21.1383 | 0 | 0 | 753.788 | 2124.123 | 2145.2613
| 20368770 | 2032 | BGO023 | 753.788 | 21.1383 | 0 | 0 | 753.788 | 2124.123 | 2145.2613
| 20368770 | 2033 | BGO023 | 753.788 | 21.1383 | 0 | 0 | 753.788 | 2124.123 | 2145.2613
| 20368770 | 2034 | BGO023 | 753.788 | 21.1383 | 0 | 0 | 753.788 | 2124.123 | 2145.2613
| 20496964 | 2023 | BGO023 | 2023.4191 | 0 | 0 | 0 | 2023.4191 | 5767.3719 | 5767.3719
| 20496964 | 2024 | BGO023 | 2065.4323 | 41.3837 | 0 | 0 | 2065.4323 | 5767.3719 | 5808.7556
| 20496964 | 2025 | BGO023 | 764.856 | 16.6996 | 0 | 0 | 764.856 | 5767.3719 | 5784.0715
| 20496964 | 2026 | BGO023 | 764.856 | 16.6996 | 0 | 0 | 764.856 | 5767.3719 | 5784.0715
| 20496964 | 2027 | BGO023 | 764.856 | 16.6996 | 0 | 0 | 764.856 | 5767.3719 | 5784.0715
| 20496964 | 2028 | BGO023 | 764.856 | 16.6996 | 0 | 0 | 764.856 | 5767.3719 | 5784.0715
| 20496964 | 2029 | BGO023 | 764.856 | 16.6996 | 0 | 0 | 764.856 | 5767.3719 | 5784.0715
| 20496964 | 2030 | BGO023 | 764.856 | 16.6996 | 0 | 0 | 764.856 | 5767.3719 | 5784.0715
| 20496964 | 2031 | BGO023 | 764.856 | 16.6996 | 0 | 0 | 764.856 | 5767.3719 | 5784.0715
| 20496964 | 2032 | BGO023 | 764.856 | 16.6996 | 0 | 0 | 764.856 | 5767.3719 | 5784.0715
| 20496964 | 2033 | BGO023 | 764.856 | 16.6996 | 0 | 0 | 764.856 | 5767.3719 | 5784.0715
| 20496964 | 2034 | BGO023 | 764.856 | 16.6996 | 0 | 0 | 764.856 | 5767.3719 | 5784.0715
| 20502519 | 2023 | BGO023 | 4180.2049 | 0 | 0 | 0 | 4180.2049 | 3398.2238 | 3398.2238
| 20502519 | 2024 | BGO023 | 4266.277 | 94.9903 | 0 | 0 | 4266.277 | 3398.2238 | 3493.2142
| 20502519 | 2025 | BGO023 | 1970.9598 | 53.1027 | 0 | 0 | 1970.9598 | 3398.2238 | 3451.3265
| 20502519 | 2026 | BGO023 | 1970.9598 | 53.1027 | 0 | 0 | 1970.9598 | 3398.2238 | 3451.3265
| 20502519 | 2027 | BGO023 | 1970.9598 | 53.1027 | 0 | 0 | 1970.9598 | 3398.2238 | 3451.3265
| 20502519 | 2028 | BGO023 | 1970.9598 | 53.1027 | 0 | 0 | 1970.9598 | 3398.2238 | 3451.3265
| 20502519 | 2029 | BGO023 | 1970.9598 | 53.1027 | 0 | 0 | 1970.9598 | 3398.2238 | 3451.3265
| 20502519 | 2030 | BGO023 | 1970.9598 | 53.1027 | 0 | 0 | 1970.9598 | 3398.2238 | 3451.3265
| 20502519 | 2031 | BGO023 | 1970.9598 | 53.1027 | 0 | 0 | 1970.9598 | 3398.2238 | 3451.3265
| 20502519 | 2032 | BGO023 | 1970.9598 | 53.1027 | 0 | 0 | 1970.9598 | 3398.2238 | 3451.3265
| 20502519 | 2033 | BGO023 | 1970.9598 | 53.1027 | 0 | 0 | 1970.9598 | 3398.2238 | 3451.3265
| 20502519 | 2034 | BGO023 | 1970.9598 | 53.1027 | 0 | 0 | 1970.9598 | 3398.2238 | 3451.3265
| 20513936 | 2023 | BGO023 | 998.9943 | 0 | 0 | 0 | 998.9943 | 9899.1522 | 9899.1522
| 20513936 | 2024 | BGO023 | 1308.1817 | 18.5651 | 0 | 0 | 1308.1817 | 9899.1522 | 9917.7172
| 20513936 | 2025 | BGO023 | 247.316 | 3.3967 | 5.5036 | 235.195 | 252.8196 | 9899.1522 | 10137.7439
| 20513936 | 2026 | BGO023 | 247.316 | 3.3967 | 5.5036 | 235.195 | 252.8196 | 9899.1522 | 10137.7439
| 20513936 | 2027 | BGO023 | 247.316 | 3.3967 | 5.5036 | 235.195 | 252.8196 | 9899.1522 | 10137.7439
| 20513936 | 2028 | BGO023 | 247.316 | 3.3967 | 5.5036 | 235.195 | 252.8196 | 9899.1522 | 10137.7439
| 20513936 | 2029 | BGO023 | 247.316 | 3.3967 | 5.5036 | 235.195 | 252.8196 | 9899.1522 | 10137.7439
| 20513936 | 2030 | BGO023 | 247.316 | 3.3967 | 5.5036 | 235.195 | 252.8196 | 9899.1522 | 10137.7439
| 20513936 | 2031 | BGO023 | 247.316 | 3.3967 | 5.5036 | 235.195 | 252.8196 | 9899.1522 | 10137.7439
| 20513936 | 2032 | BGO023 | 247.316 | 3.3967 | 5.5036 | 235.195 | 252.8196 | 9899.1522 | 10137.7439
| 20513936 | 2033 | BGO023 | 247.316 | 3.3967 | 5.5036 | 235.195 | 252.8196 | 9899.1522 | 10137.7439
| 20513936 | 2034 | BGO023 | 247.316 | 3.3967 | 5.5036 | 235.195 | 252.8196 | 9899.1522 | 10137.7439
| 20515866 | 2023 | BGO023 | 0.79972 | 0 | 0.69406 | 29.6606 | 1.4938 | 6421.1748 | 6450.8354
| 20515866 | 2024 | BGO023 | 1.6814 | 0.021042 | 0.9133 | 39.0297 | 2.5947 | 6421.1748 | 6460.2255
| 20515866 | 2025 | BGO023 | 0.11637 | 0.0018691 | 0.13718 | 5.8625 | 0.25356 | 6421.1748 | 6427.0392
| 20515866 | 2026 | BGO023 | 0.11637 | 0.0018691 | 0.13718 | 5.8625 | 0.25356 | 6421.1748 | 6427.0392
| 20515866 | 2027 | BGO023 | 0.11637 | 0.0018691 | 0.13718 | 5.8625 | 0.25356 | 6421.1748 | 6427.0392
| 20515866 | 2028 | BGO023 | 0.11637 | 0.0018691 | 0.13718 | 5.8625 | 0.25356 | 6421.1748 | 6427.0392
| 20515866 | 2029 | BGO023 | 0.11637 | 0.0018691 | 0.13718 | 5.8625 | 0.25356 | 6421.1748 | 6427.0392
| 20515866 | 2030 | BGO023 | 0.11637 | 0.0018691 | 0.13718 | 5.8625 | 0.25356 | 6421.1748 | 6427.0392
| 20515866 | 2031 | BGO023 | 0.11637 | 0.0018691 | 0.13718 | 5.8625 | 0.25356 | 6421.1748 | 6427.0392
| 20515866 | 2032 | BGO023 | 0.11637 | 0.0018691 | 0.13718 | 5.8625 | 0.25356 | 6421.1748 | 6427.0392
| 20515866 | 2033 | BGO023 | 0.11637 | 0.0018691 | 0.13718 | 5.8625 | 0.25356 | 6421.1748 | 6427.0392
| 20515866 | 2034 | BGO023 | 0.11637 | 0.0018691 | 0.13718 | 5.8625 | 0.25356 | 6421.1748 | 6427.0392
| 20632634 | 2023 | BGO023 | 2214.9307 | 0 | 0 | 0 | 2214.9307 | 10199.3478 | 10199.3478
| 20632634 | 2024 | BGO023 | 4867.3887 | 85.7752 | 0 | 0 | 4867.3887 | 10199.3478 | 10285.123
| 20632634 | 2025 | BGO023 | 1964.6861 | 35.9014 | 0.18492 | 7.9027 | 1964.871 | 10199.3478 | 10243.1518
| 20632634 | 2026 | BGO023 | 1964.6861 | 35.9014 | 0.18492 | 7.9027 | 1964.871 | 10199.3478 | 10243.1518
| 20632634 | 2027 | BGO023 | 1964.6861 | 35.9014 | 0.18492 | 7.9027 | 1964.871 | 10199.3478 | 10243.1518
| 20632634 | 2028 | BGO023 | 1964.6861 | 35.9014 | 0.18492 | 7.9027 | 1964.871 | 10199.3478 | 10243.1518
| 20632634 | 2029 | BGO023 | 1964.6861 | 35.9014 | 0.18492 | 7.9027 | 1964.871 | 10199.3478 | 10243.1518
| 20632634 | 2030 | BGO023 | 1964.6861 | 35.9014 | 0.18492 | 7.9027 | 1964.871 | 10199.3478 | 10243.1518
| 20632634 | 2031 | BGO023 | 1964.6861 | 35.9014 | 0.18492 | 7.9027 | 1964.871 | 10199.3478 | 10243.1518
| 20632634 | 2032 | BGO023 | 1964.6861 | 35.9014 | 0.18492 | 7.9027 | 1964.871 | 10199.3478 | 10243.1518
| 20632634 | 2033 | BGO023 | 1964.6861 | 35.9014 | 0.18492 | 7.9027 | 1964.871 | 10199.3478 | 10243.1518
| 20632634 | 2034 | BGO023 | 1964.6861 | 35.9014 | 0.18492 | 7.9027 | 1964.871 | 10199.3478 | 10243.1518
| 76723440 | 2023 | BGO023 | 5434.4554 | 0 | 0 | 0 | 5434.4554 | 7126.0957 | 7126.0957
| 76723440 | 2024 | BGO023 | 13286.7033 | 301.2333 | 0 | 0 | 13286.7033 | 7126.0957 | 7427.329
| 76723440 | 2025 | BGO023 | 5056.6804 | 123.5551 | 0 | 0 | 5056.6804 | 7126.0957 | 7249.6508
| 76723440 | 2026 | BGO023 | 5056.6804 | 123.5551 | 0 | 0 | 5056.6804 | 7126.0957 | 7249.6508
| 76723440 | 2027 | BGO023 | 5056.6804 | 123.5551 | 0 | 0 | 5056.6804 | 7126.0957 | 7249.6508
| 76723440 | 2028 | BGO023 | 5056.6804 | 123.5551 | 0 | 0 | 5056.6804 | 7126.0957 | 7249.6508
| 76723440 | 2029 | BGO023 | 5056.6804 | 123.5551 | 0 | 0 | 5056.6804 | 7126.0957 | 7249.6508
| 76723440 | 2030 | BGO023 | 5056.6804 | 123.5551 | 0 | 0 | 5056.6804 | 7126.0957 | 7249.6508
| 76723440 | 2031 | BGO023 | 5056.6804 | 123.5551 | 0 | 0 | 5056.6804 | 7126.0957 | 7249.6508
| 76723440 | 2032 | BGO023 | 5056.6804 | 123.5551 | 0 | 0 | 5056.6804 | 7126.0957 | 7249.6508
| 76723440 | 2033 | BGO023 | 5056.6804 | 123.5551 | 0 | 0 | 5056.6804 | 7126.0957 | 7249.6508
| 76723440 | 2034 | BGO023 | 5056.6804 | 123.5551 | 0 | 0 | 5056.6804 | 7126.0957 | 7249.6508
| 84633256 | 2023 | BGO023 | 0 | 0 | 0 | 0 | 0 | 3811.8681 | 3811.8681
| 84633256 | 2024 | BGO023 | 0 | 0 | 0 | 0 | 0 | 3811.8681 | 3811.8681
| 84633256 | 2025 | BGO023 | 0 | 0 | 0 | 0 | 0 | 3811.8681 | 3811.8681
| 84633256 | 2026 | BGO023 | 0 | 0 | 0 | 0 | 0 | 3811.8681 | 3811.8681
| 84633256 | 2027 | BGO023 | 0 | 0 | 0 | 0 | 0 | 3811.8681 | 3811.8681
| 84633256 | 2028 | BGO023 | 0 | 0 | 0 | 0 | 0 | 3811.8681 | 3811.8681
| 84633256 | 2029 | BGO023 | 0 | 0 | 0 | 0 | 0 | 3811.8681 | 3811.8681
| 84633256 | 2030 | BGO023 | 0 | 0 | 0 | 0 | 0 | 3811.8681 | 3811.8681
| 84633256 | 2031 | BGO023 | 0 | 0 | 0 | 0 | 0 | 3811.8681 | 3811.8681
| 84633256 | 2032 | BGO023 | 0 | 0 | 0 | 0 | 0 | 3811.8681 | 3811.8681
| 84633256 | 2033 | BGO023 | 0 | 0 | 0 | 0 | 0 | 3811.8681 | 3811.8681
| 84633256 | 2034 | BGO023 | 0 | 0 | 0 | 0 | 0 | 3811.8681 | 3811.8681
| 95621518 | 2023 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.3051 | 501.3051
| 95621518 | 2024 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.3051 | 501.3051
| 95621518 | 2025 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.3051 | 501.3051
| 95621518 | 2026 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.3051 | 501.3051
| 95621518 | 2027 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.3051 | 501.3051
| 95621518 | 2028 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.3051 | 501.3051
| 95621518 | 2029 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.3051 | 501.3051
| 95621518 | 2030 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.3051 | 501.3051
| 95621518 | 2031 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.3051 | 501.3051
| 95621518 | 2032 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.3051 | 501.3051
| 95621518 | 2033 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.3051 | 501.3051
| 95621518 | 2034 | BGO023 | 0 | 0 | 0 | 0 | 0 | 501.3051 | 501.3051
| 182432574 | 2023 | BGO023 | 0 | 0 | 0 | 0 | 0 | 2662.8343 | 2662.8343
| 182432574 | 2024 | BGO023 | 0 | 0 | 0 | 0 | 0 | 2662.8343 | 2662.8343
| 182432574 | 2025 | BGO023 | 0 | 0 | 0 | 0 | 0 | 2662.8343 | 2662.8343
| 182432574 | 2026 | BGO023 | 0 | 0 | 0 | 0 | 0 | 2662.8343 | 2662.8343
| 182432574 | 2027 | BGO023 | 0 | 0 | 0 | 0 | 0 | 2662.8343 | 2662.8343
| 182432574 | 2028 | BGO023 | 0 | 0 | 0 | 0 | 0 | 2662.8343 | 2662.8343
| 182432574 | 2029 | BGO023 | 0 | 0 | 0 | 0 | 0 | 2662.8343 | 2662.8343
| 182432574 | 2030 | BGO023 | 0 | 0 | 0 | 0 | 0 | 2662.8343 | 2662.8343
| 182432574 | 2031 | BGO023 | 0 | 0 | 0 | 0 | 0 | 2662.8343 | 2662.8343
| 182432574 | 2032 | BGO023 | 0 | 0 | 0 | 0 | 0 | 2662.8343 | 2662.8343
| 182432574 | 2033 | BGO023 | 0 | 0 | 0 | 0 | 0 | 2662.8343 | 2662.8343
| 182432574 | 2034 | BGO023 | 0 | 0 | 0 | 0 | 0 | 2662.8343 | 2662.8343
| 19998982 | 2023 | BMH003 | 0 | 0 | 0 | 0 | 0 | 937.9519 | 937.9519
| 19998982 | 2024 | BMH003 | 0 | 0 | 0 | 0 | 0 | 937.9519 | 937.9519
| 19998982 | 2025 | BMH003 | 0 | 0 | 0 | 0 | 0 | 937.9519 | 937.9519
| 19998982 | 2026 | BMH003 | 0 | 0 | 0 | 0 | 0 | 937.9519 | 937.9519
| 19998982 | 2027 | BMH003 | 0 | 0 | 0 | 0 | 0 | 937.9519 | 937.9519
| 19998982 | 2028 | BMH003 | 0 | 0 | 0 | 0 | 0 | 937.9519 | 937.9519
| 19998982 | 2029 | BMH003 | 0 | 0 | 0 | 0 | 0 | 937.9519 | 937.9519
| 19998982 | 2030 | BMH003 | 0 | 0 | 0 | 0 | 0 | 937.9519 | 937.9519
| 19998982 | 2031 | BMH003 | 0 | 0 | 0 | 0 | 0 | 937.9519 | 937.9519
| 19998982 | 2032 | BMH003 | 0 | 0 | 0 | 0 | 0 | 937.9519 | 937.9519
| 19998982 | 2033 | BMH003 | 0 | 0 | 0 | 0 | 0 | 937.9519 | 937.9519
| 19998982 | 2034 | BMH003 | 0 | 0 | 0 | 0 | 0 | 937.9519 | 937.9519
| 19999269 | 2023 | BMH003 | 0 | 0 | 0 | 0 | 0 | 461.5575 | 461.5575
| 19999269 | 2024 | BMH003 | 0 | 0 | 0 | 0 | 0 | 461.5575 | 461.5575
| 19999269 | 2025 | BMH003 | 0 | 0 | 0 | 0 | 0 | 461.5575 | 461.5575
| 19999269 | 2026 | BMH003 | 0 | 0 | 0 | 0 | 0 | 461.5575 | 461.5575
| 19999269 | 2027 | BMH003 | 0 | 0 | 0 | 0 | 0 | 461.5575 | 461.5575
| 19999269 | 2028 | BMH003 | 0 | 0 | 0 | 0 | 0 | 461.5575 | 461.5575
| 19999269 | 2029 | BMH003 | 0 | 0 | 0 | 0 | 0 | 461.5575 | 461.5575
| 19999269 | 2030 | BMH003 | 0 | 0 | 0 | 0 | 0 | 461.5575 | 461.5575
| 19999269 | 2031 | BMH003 | 0 | 0 | 0 | 0 | 0 | 461.5575 | 461.5575
| 19999269 | 2032 | BMH003 | 0 | 0 | 0 | 0 | 0 | 461.5575 | 461.5575
| 19999269 | 2033 | BMH003 | 0 | 0 | 0 | 0 | 0 | 461.5575 | 461.5575
| 19999269 | 2034 | BMH003 | 0 | 0 | 0 | 0 | 0 | 461.5575 | 461.5575
| 20384235 | 2023 | BMH003 | 649.4537 | 0 | 0 | 0 | 649.4537 | 3263.6181 | 3263.6181
| 20384235 | 2024 | BMH003 | 557.994 | 11.6026 | 0 | 0 | 557.994 | 3263.6181 | 3275.2206
| 20384235 | 2025 | BMH003 | 559.4179 | 11.0425 | 0 | 0 | 559.4179 | 3263.6181 | 3274.6606
| 20384235 | 2026 | BMH003 | 391.8796 | 4.2377 | 0 | 0 | 391.8796 | 3263.6181 | 3267.8557
| 20384235 | 2027 | BMH003 | 391.8796 | 4.2377 | 0 | 0 | 391.8796 | 3263.6181 | 3267.8557
| 20384235 | 2028 | BMH003 | 391.8796 | 4.2377 | 0 | 0 | 391.8796 | 3263.6181 | 3267.8557
| 20384235 | 2029 | BMH003 | 391.8796 | 4.2377 | 0 | 0 | 391.8796 | 3263.6181 | 3267.8557
| 20384235 | 2030 | BMH003 | 391.8796 | 4.2377 | 0 | 0 | 391.8796 | 3263.6181 | 3267.8557
| 20384235 | 2031 | BMH003 | 391.8796 | 4.2377 | 0 | 0 | 391.8796 | 3263.6181 | 3267.8557
| 20384235 | 2032 | BMH003 | 391.8796 | 4.2377 | 0 | 0 | 391.8796 | 3263.6181 | 3267.8557
| 20384235 | 2033 | BMH003 | 391.8796 | 4.2377 | 0 | 0 | 391.8796 | 3263.6181 | 3267.8557
| 20384235 | 2034 | BMH003 | 391.8796 | 4.2377 | 0 | 0 | 391.8796 | 3263.6181 | 3267.8557
| 20516744 | 2023 | BMH003 | 10627.365 | 0 | 0 | 0 | 10627.365 | 3231.7048 | 3231.7048
| 20516744 | 2024 | BMH003 | 10744.0821 | 258.1132 | 0 | 0 | 10744.0821 | 3231.7048 | 3489.8179
| 20516744 | 2025 | BMH003 | 10705.0015 | 271.8623 | 0 | 0 | 10705.0015 | 3231.7048 | 3503.5671
| 20516744 | 2026 | BMH003 | 14651.8389 | 217.6147 | 0 | 0 | 14651.8389 | 3231.7048 | 3449.3195
| 20516744 | 2027 | BMH003 | 14651.8389 | 217.6147 | 0 | 0 | 14651.8389 | 3231.7048 | 3449.3195
| 20516744 | 2028 | BMH003 | 14651.8389 | 217.6147 | 0 | 0 | 14651.8389 | 3231.7048 | 3449.3195
| 20516744 | 2029 | BMH003 | 14651.8389 | 217.6147 | 0 | 0 | 14651.8389 | 3231.7048 | 3449.3195
| 20516744 | 2030 | BMH003 | 14651.8389 | 217.6147 | 0 | 0 | 14651.8389 | 3231.7048 | 3449.3195
| 20516744 | 2031 | BMH003 | 14651.8389 | 217.6147 | 0 | 0 | 14651.8389 | 3231.7048 | 3449.3195
| 20516744 | 2032 | BMH003 | 14651.8389 | 217.6147 | 0 | 0 | 14651.8389 | 3231.7048 | 3449.3195
| 20516744 | 2033 | BMH003 | 14651.8389 | 217.6147 | 0 | 0 | 14651.8389 | 3231.7048 | 3449.3195
| 20516744 | 2034 | BMH003 | 14651.8389 | 217.6147 | 0 | 0 | 14651.8389 | 3231.7048 | 3449.3195
| 20654511 | 2023 | BMH003 | 2849 | 0 | 0 | 0 | 2849 | 3288.5967 | 3288.5967
| 20654511 | 2024 | BMH003 | 2933.8626 | 53.719 | 0 | 0 | 2933.8626 | 3288.5967 | 3342.3157
| 20654511 | 2025 | BMH003 | 2989.7745 | 62.0255 | 0 | 0 | 2989.7745 | 3288.5967 | 3350.6222
| 20654511 | 2026 | BMH003 | 3105.9729 | 37.0963 | 0 | 0 | 3105.9729 | 3288.5967 | 3325.693
| 20654511 | 2027 | BMH003 | 3105.9729 | 37.0963 | 0 | 0 | 3105.9729 | 3288.5967 | 3325.693
| 20654511 | 2028 | BMH003 | 3105.9729 | 37.0963 | 0 | 0 | 3105.9729 | 3288.5967 | 3325.693
| 20654511 | 2029 | BMH003 | 3105.9729 | 37.0963 | 0 | 0 | 3105.9729 | 3288.5967 | 3325.693
| 20654511 | 2030 | BMH003 | 3105.9729 | 37.0963 | 0 | 0 | 3105.9729 | 3288.5967 | 3325.693
| 20654511 | 2031 | BMH003 | 3105.9729 | 37.0963 | 0 | 0 | 3105.9729 | 3288.5967 | 3325.693
| 20654511 | 2032 | BMH003 | 3105.9729 | 37.0963 | 0 | 0 | 3105.9729 | 3288.5967 | 3325.693
| 20654511 | 2033 | BMH003 | 3105.9729 | 37.0963 | 0 | 0 | 3105.9729 | 3288.5967 | 3325.693
| 20654511 | 2034 | BMH003 | 3105.9729 | 37.0963 | 0 | 0 | 3105.9729 | 3288.5967 | 3325.693
| 20705668 | 2023 | BMH003 | 0 | 0 | 0 | 0 | 0 | 2852.6241 | 2852.6241
| 20705668 | 2024 | BMH003 | 1028.3119 | 17.4503 | 0 | 0 | 1028.3119 | 2852.6241 | 2870.0743
| 20705668 | 2025 | BMH003 | 1052.893 | 21.4179 | 0 | 0 | 1052.893 | 2852.6241 | 2874.042
| 20705668 | 2026 | BMH003 | 1146.3788 | 13.6185 | 0 | 0 | 1146.3788 | 2852.6241 | 2866.2425
| 20705668 | 2027 | BMH003 | 1146.3788 | 13.6185 | 0 | 0 | 1146.3788 | 2852.6241 | 2866.2425
| 20705668 | 2028 | BMH003 | 1146.3788 | 13.6185 | 0 | 0 | 1146.3788 | 2852.6241 | 2866.2425
| 20705668 | 2029 | BMH003 | 1146.3788 | 13.6185 | 0 | 0 | 1146.3788 | 2852.6241 | 2866.2425
| 20705668 | 2030 | BMH003 | 1146.3788 | 13.6185 | 0 | 0 | 1146.3788 | 2852.6241 | 2866.2425
| 20705668 | 2031 | BMH003 | 1146.3788 | 13.6185 | 0 | 0 | 1146.3788 | 2852.6241 | 2866.2425
| 20705668 | 2032 | BMH003 | 1146.3788 | 13.6185 | 0 | 0 | 1146.3788 | 2852.6241 | 2866.2425
| 20705668 | 2033 | BMH003 | 1146.3788 | 13.6185 | 0 | 0 | 1146.3788 | 2852.6241 | 2866.2425
| 20705668 | 2034 | BMH003 | 1146.3788 | 13.6185 | 0 | 0 | 1146.3788 | 2852.6241 | 2866.2425
| 41475395 | 2023 | BMH003 | 0 | 0 | 0 | 0 | 0 | 1586.1731 | 1586.1731
| 41475395 | 2024 | BMH003 | 840.8745 | 14.6065 | 0 | 0 | 840.8745 | 1586.1731 | 1600.7796
| 41475395 | 2025 | BMH003 | 1064.6505 | 20.7462 | 0 | 0 | 1064.6505 | 1586.1731 | 1606.9193
| 41475395 | 2026 | BMH003 | 1028.8763 | 11.5164 | 0 | 0 | 1028.8763 | 1586.1731 | 1597.6895
| 41475395 | 2027 | BMH003 | 1028.8763 | 11.5164 | 0 | 0 | 1028.8763 | 1586.1731 | 1597.6895
| 41475395 | 2028 | BMH003 | 1028.8763 | 11.5164 | 0 | 0 | 1028.8763 | 1586.1731 | 1597.6895
| 41475395 | 2029 | BMH003 | 1028.8763 | 11.5164 | 0 | 0 | 1028.8763 | 1586.1731 | 1597.6895
| 41475395 | 2030 | BMH003 | 1028.8763 | 11.5164 | 0 | 0 | 1028.8763 | 1586.1731 | 1597.6895
| 41475395 | 2031 | BMH003 | 1028.8763 | 11.5164 | 0 | 0 | 1028.8763 | 1586.1731 | 1597.6895
| 41475395 | 2032 | BMH003 | 1028.8763 | 11.5164 | 0 | 0 | 1028.8763 | 1586.1731 | 1597.6895
| 41475395 | 2033 | BMH003 | 1028.8763 | 11.5164 | 0 | 0 | 1028.8763 | 1586.1731 | 1597.6895
| 41475395 | 2034 | BMH003 | 1028.8763 | 11.5164 | 0 | 0 | 1028.8763 | 1586.1731 | 1597.6895
| 42433190 | 2023 | BMH003 | 0 | 0 | 0 | 0 | 0 | 1258.1432 | 1258.1432
| 42433190 | 2024 | BMH003 | 0 | 0 | 0 | 0 | 0 | 1258.1432 | 1258.1432
| 42433190 | 2025 | BMH003 | 0 | 0 | 0 | 0 | 0 | 1258.1432 | 1258.1432
| 42433190 | 2026 | BMH003 | 0 | 0 | 0 | 0 | 0 | 1258.1432 | 1258.1432
| 42433190 | 2027 | BMH003 | 0 | 0 | 0 | 0 | 0 | 1258.1432 | 1258.1432
| 42433190 | 2028 | BMH003 | 0 | 0 | 0 | 0 | 0 | 1258.1432 | 1258.1432
| 42433190 | 2029 | BMH003 | 0 | 0 | 0 | 0 | 0 | 1258.1432 | 1258.1432
| 42433190 | 2030 | BMH003 | 0 | 0 | 0 | 0 | 0 | 1258.1432 | 1258.1432
| 42433190 | 2031 | BMH003 | 0 | 0 | 0 | 0 | 0 | 1258.1432 | 1258.1432
| 42433190 | 2032 | BMH003 | 0 | 0 | 0 | 0 | 0 | 1258.1432 | 1258.1432
| 42433190 | 2033 | BMH003 | 0 | 0 | 0 | 0 | 0 | 1258.1432 | 1258.1432
| 42433190 | 2034 | BMH003 | 0 | 0 | 0 | 0 | 0 | 1258.1432 | 1258.1432
| 147434264 | 2023 | BMH003 | 512.9135 | 0 | 0 | 0 | 512.9135 | 832.5131 | 832.5131
| 147434264 | 2024 | BMH003 | 557.2451 | 9.7218 | 0 | 0 | 557.2451 | 832.5131 | 842.235
| 147434264 | 2025 | BMH003 | 540.485 | 9.6598 | 0 | 0 | 540.485 | 832.5131 | 842.173
| 147434264 | 2026 | BMH003 | 549.8949 | 5.138 | 0 | 0 | 549.8949 | 832.5131 | 837.6512
| 147434264 | 2027 | BMH003 | 549.8949 | 5.138 | 0 | 0 | 549.8949 | 832.5131 | 837.6512
| 147434264 | 2028 | BMH003 | 549.8949 | 5.138 | 0 | 0 | 549.8949 | 832.5131 | 837.6512
| 147434264 | 2029 | BMH003 | 549.8949 | 5.138 | 0 | 0 | 549.8949 | 832.5131 | 837.6512
| 147434264 | 2030 | BMH003 | 549.8949 | 5.138 | 0 | 0 | 549.8949 | 832.5131 | 837.6512
| 147434264 | 2031 | BMH003 | 549.8949 | 5.138 | 0 | 0 | 549.8949 | 832.5131 | 837.6512
| 147434264 | 2032 | BMH003 | 549.8949 | 5.138 | 0 | 0 | 549.8949 | 832.5131 | 837.6512
| 147434264 | 2033 | BMH003 | 549.8949 | 5.138 | 0 | 0 | 549.8949 | 832.5131 | 837.6512
| 147434264 | 2034 | BMH003 | 549.8949 | 5.138 | 0 | 0 | 549.8949 | 832.5131 | 837.6512
| 20271477 | 2023 | CDN001 | 0 | 0 | 0 | 0 | 0 | 740.5764 | 740.5764
| 20271477 | 2024 | CDN001 | 0 | 0 | 0 | 0 | 0 | 740.5764 | 740.5764
| 20271477 | 2025 | CDN001 | 0 | 0 | 0 | 0 | 0 | 740.5764 | 740.5764
| 20271477 | 2026 | CDN001 | 0 | 0 | 0 | 0 | 0 | 740.5764 | 740.5764
| 20271477 | 2027 | CDN001 | 0 | 0 | 0 | 0 | 0 | 740.5764 | 740.5764
| 20271477 | 2028 | CDN001 | 0 | 0 | 0 | 0 | 0 | 740.5764 | 740.5764
| 20271477 | 2029 | CDN001 | 0 | 0 | 0 | 0 | 0 | 740.5764 | 740.5764
| 20271477 | 2030 | CDN001 | 0 | 0 | 0 | 0 | 0 | 740.5764 | 740.5764
| 20271477 | 2031 | CDN001 | 0 | 0 | 0 | 0 | 0 | 740.5764 | 740.5764
| 20271477 | 2032 | CDN001 | 0 | 0 | 0 | 0 | 0 | 740.5764 | 740.5764
| 20271477 | 2033 | CDN001 | 0 | 0 | 0 | 0 | 0 | 740.5764 | 740.5764
| 20271477 | 2034 | CDN001 | 0 | 0 | 0 | 0 | 0 | 740.5764 | 740.5764
| 20566468 | 2023 | CDN001 | 0 | 0 | 0 | 0 | 0 | 354.5269 | 354.5269
| 20566468 | 2024 | CDN001 | 0 | 0 | 0 | 0 | 0 | 354.5269 | 354.5269
| 20566468 | 2025 | CDN001 | 0 | 0 | 0 | 0 | 0 | 354.5269 | 354.5269
| 20566468 | 2026 | CDN001 | 0 | 0 | 0 | 0 | 0 | 354.5269 | 354.5269
| 20566468 | 2027 | CDN001 | 0 | 0 | 96102.1434 | 4365849.1038 | 96102.1434 | 354.5269 | 4366203.6307
| 20566468 | 2028 | CDN001 | 0 | 0 | 97708.0999 | 4438806.5149 | 97708.0999 | 354.5269 | 4439161.0419
| 20566468 | 2029 | CDN001 | 0 | 0 | 97708.0999 | 4438806.5149 | 97708.0999 | 354.5269 | 4439161.0419
| 20566468 | 2030 | CDN001 | 0 | 0 | 97708.0999 | 4438806.5149 | 97708.0999 | 354.5269 | 4439161.0419
| 20566468 | 2031 | CDN001 | 0 | 0 | 97708.0999 | 4438806.5149 | 97708.0999 | 354.5269 | 4439161.0419
| 20566468 | 2032 | CDN001 | 0 | 0 | 97708.0999 | 4438806.5149 | 97708.0999 | 354.5269 | 4439161.0419
| 20566468 | 2033 | CDN001 | 0 | 0 | 97708.0999 | 4438806.5149 | 97708.0999 | 354.5269 | 4439161.0419
| 20566468 | 2034 | CDN001 | 0 | 0 | 97708.0999 | 4438806.5149 | 97708.0999 | 354.5269 | 4439161.0419
| 158379622 | 2023 | CDN001 | 0 | 0 | 0 | 0 | 0 | 2135.5989 | 2135.5989
| 158379622 | 2024 | CDN001 | 0 | 0 | 0 | 0 | 0 | 2135.5989 | 2135.5989
| 158379622 | 2025 | CDN001 | 0 | 0 | 0 | 0 | 0 | 2135.5989 | 2135.5989
| 158379622 | 2026 | CDN001 | 0 | 0 | 0 | 0 | 0 | 2135.5989 | 2135.5989
| 158379622 | 2027 | CDN001 | 6.2898 | 0.013179 | 0 | 0 | 6.2898 | 2135.5989 | 2135.6121
| 158379622 | 2028 | CDN001 | 107.9268 | 0.71412 | 0 | 0 | 107.9268 | 2135.5989 | 2136.313
| 158379622 | 2029 | CDN001 | 107.9268 | 0.71412 | 0 | 0 | 107.9268 | 2135.5989 | 2136.313
| 158379622 | 2030 | CDN001 | 107.9268 | 0.71412 | 0 | 0 | 107.9268 | 2135.5989 | 2136.313
| 158379622 | 2031 | CDN001 | 107.9268 | 0.71412 | 0 | 0 | 107.9268 | 2135.5989 | 2136.313
| 158379622 | 2032 | CDN001 | 107.9268 | 0.71412 | 0 | 0 | 107.9268 | 2135.5989 | 2136.313
| 158379622 | 2033 | CDN001 | 107.9268 | 0.71412 | 0 | 0 | 107.9268 | 2135.5989 | 2136.313
| 158379622 | 2034 | CDN001 | 107.9268 | 0.71412 | 0 | 0 | 107.9268 | 2135.5989 | 2136.313
| 160253147 | 2023 | CDN001 | 0 | 0 | 0 | 0 | 0 | 1229.6875 | 1229.6875
| 160253147 | 2024 | CDN001 | 0 | 0 | 0 | 0 | 0 | 1229.6875 | 1229.6875
| 160253147 | 2025 | CDN001 | 0 | 0 | 0 | 0 | 0 | 1229.6875 | 1229.6875
| 160253147 | 2026 | CDN001 | 0 | 0 | 0 | 0 | 0 | 1229.6875 | 1229.6875
| 160253147 | 2027 | CDN001 | 337.8147 | 2.3155 | 0 | 0 | 337.8147 | 1229.6875 | 1232.003
| 160253147 | 2028 | CDN001 | 780.1181 | 7.1654 | 0 | 0 | 780.1181 | 1229.6875 | 1236.8529
| 160253147 | 2029 | CDN001 | 780.1181 | 7.1654 | 0 | 0 | 780.1181 | 1229.6875 | 1236.8529
| 160253147 | 2030 | CDN001 | 780.1181 | 7.1654 | 0 | 0 | 780.1181 | 1229.6875 | 1236.8529
| 160253147 | 2031 | CDN001 | 780.1181 | 7.1654 | 0 | 0 | 780.1181 | 1229.6875 | 1236.8529
| 160253147 | 2032 | CDN001 | 780.1181 | 7.1654 | 0 | 0 | 780.1181 | 1229.6875 | 1236.8529
| 160253147 | 2033 | CDN001 | 780.1181 | 7.1654 | 0 | 0 | 780.1181 | 1229.6875 | 1236.8529
| 160253147 | 2034 | CDN001 | 780.1181 | 7.1654 | 0 | 0 | 780.1181 | 1229.6875 | 1236.8529
| 200307352 | 2023 | CDN001 | 0 | 0 | 0 | 0 | 0 | 190.9958 | 190.9958
| 200307352 | 2024 | CDN001 | 1661.9797 | 27.1723 | 0 | 0 | 1661.9797 | 190.9958 | 218.1681
| 200307352 | 2025 | CDN001 | 1656.3443 | 32.9267 | 0 | 0 | 1656.3443 | 190.9958 | 223.9225
| 200307352 | 2026 | CDN001 | 1644.5583 | 19.9749 | 0 | 0 | 1644.5583 | 190.9958 | 210.9706
| 200307352 | 2027 | CDN001 | 3455.7325 | 36.4193 | 0 | 0 | 3455.7325 | 190.9958 | 227.415
| 200307352 | 2028 | CDN001 | 5358.7756 | 72.1261 | 0 | 0 | 5358.7756 | 190.9958 | 263.1218
| 200307352 | 2029 | CDN001 | 5358.7756 | 72.1261 | 0 | 0 | 5358.7756 | 190.9958 | 263.1218
| 200307352 | 2030 | CDN001 | 5358.7756 | 72.1261 | 0 | 0 | 5358.7756 | 190.9958 | 263.1218
| 200307352 | 2031 | CDN001 | 5358.7756 | 72.1261 | 0 | 0 | 5358.7756 | 190.9958 | 263.1218
| 200307352 | 2032 | CDN001 | 5358.7756 | 72.1261 | 0 | 0 | 5358.7756 | 190.9958 | 263.1218
| 200307352 | 2033 | CDN001 | 5358.7756 | 72.1261 | 0 | 0 | 5358.7756 | 190.9958 | 263.1218
| 200307352 | 2034 | CDN001 | 5358.7756 | 72.1261 | 0 | 0 | 5358.7756 | 190.9958 | 263.1218
| 20271737 | 2023 | CDN002 | 0 | 0 | 0 | 0 | 0 | 970.3708 | 970.3708
| 20271737 | 2024 | CDN002 | 0 | 0 | 0 | 0 | 0 | 970.3708 | 970.3708
| 20271737 | 2025 | CDN002 | 0 | 0 | 0 | 0 | 0 | 970.3708 | 970.3708
| 20271737 | 2026 | CDN002 | 0 | 0 | 0 | 0 | 0 | 970.3708 | 970.3708
| 20271737 | 2027 | CDN002 | 0 | 0 | 0 | 0 | 0 | 970.3708 | 970.3708
| 20271737 | 2028 | CDN002 | 0 | 0 | 0 | 0 | 0 | 970.3708 | 970.3708
| 20271737 | 2029 | CDN002 | 0 | 0 | 0 | 0 | 0 | 970.3708 | 970.3708
| 20271737 | 2030 | CDN002 | 0 | 0 | 0 | 0 | 0 | 970.3708 | 970.3708
| 20271737 | 2031 | CDN002 | 0 | 0 | 0 | 0 | 0 | 970.3708 | 970.3708
| 20271737 | 2032 | CDN002 | 0 | 0 | 0 | 0 | 0 | 970.3708 | 970.3708
| 20271737 | 2033 | CDN002 | 0 | 0 | 0 | 0 | 0 | 970.3708 | 970.3708
| 20271737 | 2034 | CDN002 | 0 | 0 | 0 | 0 | 0 | 970.3708 | 970.3708
| 20278855 | 2023 | CDN002 | 0 | 0 | 0 | 0 | 0 | 360.6578 | 360.6578
| 20278855 | 2024 | CDN002 | 0 | 0 | 0 | 0 | 0 | 360.6578 | 360.6578
| 20278855 | 2025 | CDN002 | 0 | 0 | 0 | 0 | 0 | 360.6578 | 360.6578
| 20278855 | 2026 | CDN002 | 0 | 0 | 0 | 0 | 0 | 360.6578 | 360.6578
| 20278855 | 2027 | CDN002 | 0 | 0 | 0 | 0 | 0 | 360.6578 | 360.6578
| 20278855 | 2028 | CDN002 | 0 | 0 | 0 | 0 | 0 | 360.6578 | 360.6578
| 20278855 | 2029 | CDN002 | 0 | 0 | 0 | 0 | 0 | 360.6578 | 360.6578
| 20278855 | 2030 | CDN002 | 0 | 0 | 0 | 0 | 0 | 360.6578 | 360.6578
| 20278855 | 2031 | CDN002 | 0 | 0 | 0 | 0 | 0 | 360.6578 | 360.6578
| 20278855 | 2032 | CDN002 | 0 | 0 | 0 | 0 | 0 | 360.6578 | 360.6578
| 20278855 | 2033 | CDN002 | 0 | 0 | 0 | 0 | 0 | 360.6578 | 360.6578
| 20278855 | 2034 | CDN002 | 0 | 0 | 0 | 0 | 0 | 360.6578 | 360.6578
| 20464331 | 2023 | CDN002 | 0 | 0 | 0 | 0 | 0 | 2559.1941 | 2559.1941
| 20464331 | 2024 | CDN002 | 0 | 0 | 0 | 0 | 0 | 2559.1941 | 2559.1941
| 20464331 | 2025 | CDN002 | 0 | 0 | 0 | 0 | 0 | 2559.1941 | 2559.1941
| 20464331 | 2026 | CDN002 | 0 | 0 | 0 | 0 | 0 | 2559.1941 | 2559.1941
| 20464331 | 2027 | CDN002 | 0 | 0 | 0 | 0 | 0 | 2559.1941 | 2559.1941
| 20464331 | 2028 | CDN002 | 0 | 0 | 0 | 0 | 0 | 2559.1941 | 2559.1941
| 20464331 | 2029 | CDN002 | 0 | 0 | 0 | 0 | 0 | 2559.1941 | 2559.1941
| 20464331 | 2030 | CDN002 | 0 | 0 | 0 | 0 | 0 | 2559.1941 | 2559.1941
| 20464331 | 2031 | CDN002 | 0 | 0 | 0 | 0 | 0 | 2559.1941 | 2559.1941
| 20464331 | 2032 | CDN002 | 0 | 0 | 0 | 0 | 0 | 2559.1941 | 2559.1941
| 20464331 | 2033 | CDN002 | 0 | 0 | 0 | 0 | 0 | 2559.1941 | 2559.1941
| 20464331 | 2034 | CDN002 | 0 | 0 | 0 | 0 | 0 | 2559.1941 | 2559.1941
| 20464349 | 2023 | CDN002 | 0 | 0 | 0 | 0 | 0 | 289.241 | 289.241
| 20464349 | 2024 | CDN002 | 0 | 0 | 0 | 0 | 0 | 289.241 | 289.241
| 20464349 | 2025 | CDN002 | 0 | 0 | 0 | 0 | 0 | 289.241 | 289.241
| 20464349 | 2026 | CDN002 | 0 | 0 | 0 | 0 | 0 | 289.241 | 289.241
| 20464349 | 2027 | CDN002 | 0 | 0 | 0 | 0 | 0 | 289.241 | 289.241
| 20464349 | 2028 | CDN002 | 0 | 0 | 0 | 0 | 0 | 289.241 | 289.241
| 20464349 | 2029 | CDN002 | 0 | 0 | 0 | 0 | 0 | 289.241 | 289.241
| 20464349 | 2030 | CDN002 | 0 | 0 | 0 | 0 | 0 | 289.241 | 289.241
| 20464349 | 2031 | CDN002 | 0 | 0 | 0 | 0 | 0 | 289.241 | 289.241
| 20464349 | 2032 | CDN002 | 0 | 0 | 0 | 0 | 0 | 289.241 | 289.241
| 20464349 | 2033 | CDN002 | 0 | 0 | 0 | 0 | 0 | 289.241 | 289.241
| 20464349 | 2034 | CDN002 | 0 | 0 | 0 | 0 | 0 | 289.241 | 289.241
| 20464367 | 2023 | CDN002 | 0 | 0 | 0 | 0 | 0 | 30.7913 | 30.7913
| 20464367 | 2024 | CDN002 | 0 | 0 | 0 | 0 | 0 | 30.7913 | 30.7913
| 20464367 | 2025 | CDN002 | 0 | 0 | 0 | 0 | 0 | 30.7913 | 30.7913
| 20464367 | 2026 | CDN002 | 0 | 0 | 0 | 0 | 0 | 30.7913 | 30.7913
| 20464367 | 2027 | CDN002 | 0 | 0 | 0 | 0 | 0 | 30.7913 | 30.7913
| 20464367 | 2028 | CDN002 | 0 | 0 | 0 | 0 | 0 | 30.7913 | 30.7913
| 20464367 | 2029 | CDN002 | 0 | 0 | 0 | 0 | 0 | 30.7913 | 30.7913
| 20464367 | 2030 | CDN002 | 0 | 0 | 0 | 0 | 0 | 30.7913 | 30.7913
| 20464367 | 2031 | CDN002 | 0 | 0 | 0 | 0 | 0 | 30.7913 | 30.7913
| 20464367 | 2032 | CDN002 | 0 | 0 | 0 | 0 | 0 | 30.7913 | 30.7913
| 20464367 | 2033 | CDN002 | 0 | 0 | 0 | 0 | 0 | 30.7913 | 30.7913
| 20464367 | 2034 | CDN002 | 0 | 0 | 0 | 0 | 0 | 30.7913 | 30.7913
| 20504979 | 2023 | CDN002 | 0 | 0 | 0 | 0 | 0 | 187.1207 | 187.1207
| 20504979 | 2024 | CDN002 | 0 | 0 | 0 | 0 | 0 | 187.1207 | 187.1207
| 20504979 | 2025 | CDN002 | 0 | 0 | 0 | 0 | 0 | 187.1207 | 187.1207
| 20504979 | 2026 | CDN002 | 0 | 0 | 0 | 0 | 0 | 187.1207 | 187.1207
| 20504979 | 2027 | CDN002 | 0 | 0 | 0 | 0 | 0 | 187.1207 | 187.1207
| 20504979 | 2028 | CDN002 | 0 | 0 | 0 | 0 | 0 | 187.1207 | 187.1207
| 20504979 | 2029 | CDN002 | 0 | 0 | 0 | 0 | 0 | 187.1207 | 187.1207
| 20504979 | 2030 | CDN002 | 0 | 0 | 0 | 0 | 0 | 187.1207 | 187.1207
| 20504979 | 2031 | CDN002 | 0 | 0 | 0 | 0 | 0 | 187.1207 | 187.1207
| 20504979 | 2032 | CDN002 | 0 | 0 | 0 | 0 | 0 | 187.1207 | 187.1207
| 20504979 | 2033 | CDN002 | 0 | 0 | 0 | 0 | 0 | 187.1207 | 187.1207
| 20504979 | 2034 | CDN002 | 0 | 0 | 0 | 0 | 0 | 187.1207 | 187.1207
| 20051784 | 2023 | CHA003 | 0 | 0 | 0 | 0 | 0 | 927.696 | 927.696
| 20051784 | 2024 | CHA003 | 0 | 0 | 0 | 0 | 0 | 927.696 | 927.696
| 20051784 | 2025 | CHA003 | 0 | 0 | 0 | 0 | 0 | 927.696 | 927.696
| 20051784 | 2026 | CHA003 | 0 | 0 | 0 | 0 | 0 | 927.696 | 927.696
| 20051784 | 2027 | CHA003 | 0 | 0 | 0 | 0 | 0 | 927.696 | 927.696
| 20051784 | 2028 | CHA003 | 0 | 0 | 0 | 0 | 0 | 927.696 | 927.696
| 20051784 | 2029 | CHA003 | 0 | 0 | 0 | 0 | 0 | 927.696 | 927.696
| 20051784 | 2030 | CHA003 | 0 | 0 | 0 | 0 | 0 | 927.696 | 927.696
| 20051784 | 2031 | CHA003 | 0 | 0 | 0 | 0 | 0 | 927.696 | 927.696
| 20051784 | 2032 | CHA003 | 0 | 0 | 0 | 0 | 0 | 927.696 | 927.696
| 20051784 | 2033 | CHA003 | 0 | 0 | 0 | 0 | 0 | 927.696 | 927.696
| 20051784 | 2034 | CHA003 | 0 | 0 | 0 | 0 | 0 | 927.696 | 927.696
| 20497940 | 2023 | CHA003 | 0 | 0 | 0 | 0 | 0 | 1102.5455 | 1102.5455
| 20497940 | 2024 | CHA003 | 0 | 0 | 0 | 0 | 0 | 1102.5455 | 1102.5455
| 20497940 | 2025 | CHA003 | 0 | 0 | 0 | 0 | 0 | 1102.5455 | 1102.5455
| 20497940 | 2026 | CHA003 | 0 | 0 | 0 | 0 | 0 | 1102.5455 | 1102.5455
| 20497940 | 2027 | CHA003 | 0 | 0 | 0 | 0 | 0 | 1102.5455 | 1102.5455
| 20497940 | 2028 | CHA003 | 0 | 0 | 0 | 0 | 0 | 1102.5455 | 1102.5455
| 20497940 | 2029 | CHA003 | 0 | 0 | 0 | 0 | 0 | 1102.5455 | 1102.5455
| 20497940 | 2030 | CHA003 | 0 | 0 | 0 | 0 | 0 | 1102.5455 | 1102.5455
| 20497940 | 2031 | CHA003 | 0 | 0 | 0 | 0 | 0 | 1102.5455 | 1102.5455
| 20497940 | 2032 | CHA003 | 34.6362 | 0.21639 | 0 | 0 | 34.6362 | 1102.5455 | 1102.7619
| 20497940 | 2033 | CHA003 | 87.4601 | 2.4501 | 0 | 0 | 87.4601 | 1102.5455 | 1104.9957
| 20497940 | 2034 | CHA003 | 166.3589 | 3.4494 | 0 | 0 | 166.3589 | 1102.5455 | 1105.9949
| 19919777 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3771.0289 | 3771.0289
| 19919777 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3771.0289 | 3771.0289
| 19919777 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3771.0289 | 3771.0289
| 19919777 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3771.0289 | 3771.0289
| 19919777 | 2027 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3771.0289 | 3771.0289
| 19919777 | 2028 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3771.0289 | 3771.0289
| 19919777 | 2029 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3771.0289 | 3771.0289
| 19919777 | 2030 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3771.0289 | 3771.0289
| 19919777 | 2031 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3771.0289 | 3771.0289
| 19919777 | 2032 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3771.0289 | 3771.0289
| 19919777 | 2033 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3771.0289 | 3771.0289
| 19919777 | 2034 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3771.0289 | 3771.0289
| 19919905 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 8481.6042 | 8481.6042
| 19919905 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 8481.6042 | 8481.6042
| 19919905 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 8481.6042 | 8481.6042
| 19919905 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 8481.6042 | 8481.6042
| 19919905 | 2027 | CHM011 | 0 | 0 | 4082.1821 | 179306.9911 | 4082.1821 | 8481.6042 | 187788.5952
| 19919905 | 2028 | CHM011 | 0 | 0 | 4082.1821 | 179306.9911 | 4082.1821 | 8481.6042 | 187788.5952
| 19919905 | 2029 | CHM011 | 0 | 0 | 4082.1821 | 179306.9911 | 4082.1821 | 8481.6042 | 187788.5952
| 19919905 | 2030 | CHM011 | 0 | 0 | 4082.1821 | 179306.9911 | 4082.1821 | 8481.6042 | 187788.5952
| 19919905 | 2031 | CHM011 | 0 | 0 | 4082.1821 | 179306.9911 | 4082.1821 | 8481.6042 | 187788.5952
| 19919905 | 2032 | CHM011 | 0 | 0 | 4082.1821 | 179306.9911 | 4082.1821 | 8481.6042 | 187788.5952
| 19919905 | 2033 | CHM011 | 0 | 0 | 4082.1821 | 179306.9911 | 4082.1821 | 8481.6042 | 187788.5952
| 19919905 | 2034 | CHM011 | 0 | 0 | 4082.1821 | 179306.9911 | 4082.1821 | 8481.6042 | 187788.5952
| 20024176 | 2027 | CHM011 | 33334.3111 | 777.4539 | 0 | 0 | 33334.3111 | 4786.4301 | 5563.884
| 20024176 | 2028 | CHM011 | 33334.3111 | 777.4539 | 0 | 0 | 33334.3111 | 4786.4301 | 5563.884
| 20024176 | 2029 | CHM011 | 33334.3111 | 777.4539 | 0 | 0 | 33334.3111 | 4786.4301 | 5563.884
| 20024176 | 2030 | CHM011 | 33334.3111 | 777.4539 | 0 | 0 | 33334.3111 | 4786.4301 | 5563.884
| 20024176 | 2031 | CHM011 | 33334.3111 | 777.4539 | 0 | 0 | 33334.3111 | 4786.4301 | 5563.884
| 20024176 | 2032 | CHM011 | 33334.3111 | 777.4539 | 0 | 0 | 33334.3111 | 4786.4301 | 5563.884
| 20024176 | 2033 | CHM011 | 33334.3111 | 777.4539 | 0 | 0 | 33334.3111 | 4786.4301 | 5563.884
| 20024176 | 2034 | CHM011 | 33334.3111 | 777.4539 | 0 | 0 | 33334.3111 | 4786.4301 | 5563.884
| 20024833 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1274.3894 | 1274.3894
| 20024833 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1274.3894 | 1274.3894
| 20024833 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1274.3894 | 1274.3894
| 20024833 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1274.3894 | 1274.3894
| 20024833 | 2027 | CHM011 | 43.5177 | 0.11516 | 1.2068 | 53.0065 | 44.7244 | 1274.3894 | 1327.511
| 20024833 | 2028 | CHM011 | 43.5177 | 0.11516 | 1.2068 | 53.0065 | 44.7244 | 1274.3894 | 1327.511
| 20024833 | 2029 | CHM011 | 43.5177 | 0.11516 | 1.2068 | 53.0065 | 44.7244 | 1274.3894 | 1327.511
| 20024833 | 2030 | CHM011 | 43.5177 | 0.11516 | 1.2068 | 53.0065 | 44.7244 | 1274.3894 | 1327.511
| 20024833 | 2031 | CHM011 | 43.5177 | 0.11516 | 1.2068 | 53.0065 | 44.7244 | 1274.3894 | 1327.511
| 20024833 | 2032 | CHM011 | 43.5177 | 0.11516 | 1.2068 | 53.0065 | 44.7244 | 1274.3894 | 1327.511
| 20024833 | 2033 | CHM011 | 43.5177 | 0.11516 | 1.2068 | 53.0065 | 44.7244 | 1274.3894 | 1327.511
| 20024833 | 2034 | CHM011 | 43.5177 | 0.11516 | 1.2068 | 53.0065 | 44.7244 | 1274.3894 | 1327.511
| 20027247 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 9235.6048 | 9235.6048
| 20027247 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 9235.6048 | 9235.6048
| 20027247 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 9235.6048 | 9235.6048
| 20027247 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 9235.6048 | 9235.6048
| 20027247 | 2027 | CHM011 | 0 | 0 | 231.981 | 10189.6033 | 231.981 | 9235.6048 | 19425.2082
| 20027247 | 2028 | CHM011 | 0 | 0 | 231.981 | 10189.6033 | 231.981 | 9235.6048 | 19425.2082
| 20027247 | 2029 | CHM011 | 0 | 0 | 231.981 | 10189.6033 | 231.981 | 9235.6048 | 19425.2082
| 20027247 | 2030 | CHM011 | 0 | 0 | 231.981 | 10189.6033 | 231.981 | 9235.6048 | 19425.2082
| 20027247 | 2031 | CHM011 | 0 | 0 | 231.981 | 10189.6033 | 231.981 | 9235.6048 | 19425.2082
| 20027247 | 2032 | CHM011 | 0 | 0 | 231.981 | 10189.6033 | 231.981 | 9235.6048 | 19425.2082
| 20027247 | 2033 | CHM011 | 0 | 0 | 231.981 | 10189.6033 | 231.981 | 9235.6048 | 19425.2082
| 20027247 | 2034 | CHM011 | 0 | 0 | 231.981 | 10189.6033 | 231.981 | 9235.6048 | 19425.2082
| 20027738 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 923.2197 | 923.2197
| 20027738 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 923.2197 | 923.2197
| 20027738 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 923.2197 | 923.2197
| 20027738 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 923.2197 | 923.2197
| 20027738 | 2027 | CHM011 | 0 | 0 | 4.0206 | 176.6009 | 4.0206 | 923.2197 | 1099.8206
| 20027738 | 2028 | CHM011 | 0 | 0 | 4.0206 | 176.6009 | 4.0206 | 923.2197 | 1099.8206
| 20027738 | 2029 | CHM011 | 0 | 0 | 4.0206 | 176.6009 | 4.0206 | 923.2197 | 1099.8206
| 20027738 | 2030 | CHM011 | 0 | 0 | 4.0206 | 176.6009 | 4.0206 | 923.2197 | 1099.8206
| 20027738 | 2031 | CHM011 | 0 | 0 | 4.0206 | 176.6009 | 4.0206 | 923.2197 | 1099.8206
| 20027738 | 2032 | CHM011 | 0 | 0 | 4.0206 | 176.6009 | 4.0206 | 923.2197 | 1099.8206
| 20027738 | 2033 | CHM011 | 0 | 0 | 4.0206 | 176.6009 | 4.0206 | 923.2197 | 1099.8206
| 20027738 | 2034 | CHM011 | 0 | 0 | 4.0206 | 176.6009 | 4.0206 | 923.2197 | 1099.8206
| 20028837 | 2023 | CHM011 | 3559.0236 | 0 | 0 | 0 | 3559.0236 | 2768.7019 | 2768.7019
| 20028837 | 2024 | CHM011 | 3553.3045 | 76.7442 | 0 | 0 | 3553.3045 | 2768.7019 | 2845.4461
| 20028837 | 2025 | CHM011 | 6287.4356 | 152.4924 | 0 | 0 | 6287.4356 | 2768.7019 | 2921.1943
| 20028837 | 2026 | CHM011 | 6287.4356 | 152.4924 | 0 | 0 | 6287.4356 | 2768.7019 | 2921.1943
| 20028837 | 2027 | CHM011 | 3404.5701 | 43.8114 | 0 | 0 | 3404.5701 | 2768.7019 | 2812.5133
| 20028837 | 2028 | CHM011 | 3404.5701 | 43.8114 | 0 | 0 | 3404.5701 | 2768.7019 | 2812.5133
| 20028837 | 2029 | CHM011 | 3404.5701 | 43.8114 | 0 | 0 | 3404.5701 | 2768.7019 | 2812.5133
| 20028837 | 2030 | CHM011 | 3404.5701 | 43.8114 | 0 | 0 | 3404.5701 | 2768.7019 | 2812.5133
| 20028837 | 2031 | CHM011 | 3404.5701 | 43.8114 | 0 | 0 | 3404.5701 | 2768.7019 | 2812.5133
| 20028837 | 2032 | CHM011 | 3404.5701 | 43.8114 | 0 | 0 | 3404.5701 | 2768.7019 | 2812.5133
| 20028837 | 2033 | CHM011 | 3404.5701 | 43.8114 | 0 | 0 | 3404.5701 | 2768.7019 | 2812.5133
| 20028837 | 2034 | CHM011 | 3404.5701 | 43.8114 | 0 | 0 | 3404.5701 | 2768.7019 | 2812.5133
| 20028922 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1385.7636 | 1385.7636
| 20028922 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1385.7636 | 1385.7636
| 20028922 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1385.7636 | 1385.7636
| 20028922 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1385.7636 | 1385.7636
| 20028922 | 2027 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1385.7636 | 1385.7636
| 20028922 | 2028 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1385.7636 | 1385.7636
| 20028922 | 2029 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1385.7636 | 1385.7636
| 20028922 | 2030 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1385.7636 | 1385.7636
| 20028922 | 2031 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1385.7636 | 1385.7636
| 20028922 | 2032 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1385.7636 | 1385.7636
| 20028922 | 2033 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1385.7636 | 1385.7636
| 20028922 | 2034 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1385.7636 | 1385.7636
| 20029475 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 2672.4175 | 2672.4175
| 20029475 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 2672.4175 | 2672.4175
| 20029475 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 2672.4175 | 2672.4175
| 20029475 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 2672.4175 | 2672.4175
| 20029475 | 2027 | CHM011 | 1101.8527 | 9.9688 | 119.2485 | 5237.9089 | 1221.1013 | 2672.4175 | 7920.2952
| 20029475 | 2028 | CHM011 | 1101.8527 | 9.9688 | 119.2485 | 5237.9089 | 1221.1013 | 2672.4175 | 7920.2952
| 20029475 | 2029 | CHM011 | 1101.8527 | 9.9688 | 119.2485 | 5237.9089 | 1221.1013 | 2672.4175 | 7920.2952
| 20029475 | 2030 | CHM011 | 1101.8527 | 9.9688 | 119.2485 | 5237.9089 | 1221.1013 | 2672.4175 | 7920.2952
| 20029475 | 2031 | CHM011 | 1101.8527 | 9.9688 | 119.2485 | 5237.9089 | 1221.1013 | 2672.4175 | 7920.2952
| 20029475 | 2032 | CHM011 | 1101.8527 | 9.9688 | 119.2485 | 5237.9089 | 1221.1013 | 2672.4175 | 7920.2952
| 20029475 | 2033 | CHM011 | 1101.8527 | 9.9688 | 119.2485 | 5237.9089 | 1221.1013 | 2672.4175 | 7920.2952
| 20029475 | 2034 | CHM011 | 1101.8527 | 9.9688 | 119.2485 | 5237.9089 | 1221.1013 | 2672.4175 | 7920.2952
| 20037638 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1459.6786 | 1459.6786
| 20037638 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1459.6786 | 1459.6786
| 20037638 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1459.6786 | 1459.6786
| 20037638 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1459.6786 | 1459.6786
| 20037638 | 2027 | CHM011 | 0 | 0 | 1206.6738 | 53002.3006 | 1206.6738 | 1459.6786 | 54461.9792
| 20037638 | 2028 | CHM011 | 0 | 0 | 1206.6738 | 53002.3006 | 1206.6738 | 1459.6786 | 54461.9792
| 20037638 | 2029 | CHM011 | 0 | 0 | 1206.6738 | 53002.3006 | 1206.6738 | 1459.6786 | 54461.9792
| 20037638 | 2030 | CHM011 | 0 | 0 | 1206.6738 | 53002.3006 | 1206.6738 | 1459.6786 | 54461.9792
| 20037638 | 2031 | CHM011 | 0 | 0 | 1206.6738 | 53002.3006 | 1206.6738 | 1459.6786 | 54461.9792
| 20037638 | 2032 | CHM011 | 0 | 0 | 1206.6738 | 53002.3006 | 1206.6738 | 1459.6786 | 54461.9792
| 20037638 | 2033 | CHM011 | 0 | 0 | 1206.6738 | 53002.3006 | 1206.6738 | 1459.6786 | 54461.9792
| 20037638 | 2034 | CHM011 | 0 | 0 | 1206.6738 | 53002.3006 | 1206.6738 | 1459.6786 | 54461.9792
| 20495974 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 5288.2738 | 5288.2738
| 20495974 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 5288.2738 | 5288.2738
| 20495974 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 5288.2738 | 5288.2738
| 20495974 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 5288.2738 | 5288.2738
| 20495974 | 2027 | CHM011 | 61.7422 | 0.15083 | 625.9735 | 27495.4475 | 687.7157 | 5288.2738 | 32783.8722
| 20495974 | 2028 | CHM011 | 61.7422 | 0.15083 | 625.9735 | 27495.4475 | 687.7157 | 5288.2738 | 32783.8722
| 20495974 | 2029 | CHM011 | 61.7422 | 0.15083 | 625.9735 | 27495.4475 | 687.7157 | 5288.2738 | 32783.8722
| 20495974 | 2030 | CHM011 | 61.7422 | 0.15083 | 625.9735 | 27495.4475 | 687.7157 | 5288.2738 | 32783.8722
| 20495974 | 2031 | CHM011 | 61.7422 | 0.15083 | 625.9735 | 27495.4475 | 687.7157 | 5288.2738 | 32783.8722
| 20495974 | 2032 | CHM011 | 61.7422 | 0.15083 | 625.9735 | 27495.4475 | 687.7157 | 5288.2738 | 32783.8722
| 20495974 | 2033 | CHM011 | 61.7422 | 0.15083 | 625.9735 | 27495.4475 | 687.7157 | 5288.2738 | 32783.8722
| 20495974 | 2034 | CHM011 | 61.7422 | 0.15083 | 625.9735 | 27495.4475 | 687.7157 | 5288.2738 | 32783.8722
| 20496586 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1788.2788 | 1788.2788
| 20496586 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1788.2788 | 1788.2788
| 20496586 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1788.2788 | 1788.2788
| 20496586 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1788.2788 | 1788.2788
| 20496586 | 2027 | CHM011 | 0 | 0 | 0.048313 | 2.1221 | 0.048313 | 1788.2788 | 1790.401
| 20496586 | 2028 | CHM011 | 0 | 0 | 0.048313 | 2.1221 | 0.048313 | 1788.2788 | 1790.401
| 20496586 | 2029 | CHM011 | 0 | 0 | 0.048313 | 2.1221 | 0.048313 | 1788.2788 | 1790.401
| 20496586 | 2030 | CHM011 | 0 | 0 | 0.048313 | 2.1221 | 0.048313 | 1788.2788 | 1790.401
| 20496586 | 2031 | CHM011 | 0 | 0 | 0.048313 | 2.1221 | 0.048313 | 1788.2788 | 1790.401
| 20496586 | 2032 | CHM011 | 0 | 0 | 0.048313 | 2.1221 | 0.048313 | 1788.2788 | 1790.401
| 20496586 | 2033 | CHM011 | 0 | 0 | 0.048313 | 2.1221 | 0.048313 | 1788.2788 | 1790.401
| 20496586 | 2034 | CHM011 | 0 | 0 | 0.048313 | 2.1221 | 0.048313 | 1788.2788 | 1790.401
| 20496605 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 2710.8561 | 2710.8561
| 20496605 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 2710.8561 | 2710.8561
| 20496605 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 2710.8561 | 2710.8561
| 20496605 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 2710.8561 | 2710.8561
| 20496605 | 2027 | CHM011 | 0 | 0 | 706.4874 | 31031.9647 | 706.4874 | 2710.8561 | 33742.8207
| 20496605 | 2028 | CHM011 | 0 | 0 | 706.4874 | 31031.9647 | 706.4874 | 2710.8561 | 33742.8207
| 20496605 | 2029 | CHM011 | 0 | 0 | 706.4874 | 31031.9647 | 706.4874 | 2710.8561 | 33742.8207
| 20496605 | 2030 | CHM011 | 0 | 0 | 706.4874 | 31031.9647 | 706.4874 | 2710.8561 | 33742.8207
| 20496605 | 2031 | CHM011 | 0 | 0 | 706.4874 | 31031.9647 | 706.4874 | 2710.8561 | 33742.8207
| 20496605 | 2032 | CHM011 | 0 | 0 | 706.4874 | 31031.9647 | 706.4874 | 2710.8561 | 33742.8207
| 20496605 | 2033 | CHM011 | 0 | 0 | 706.4874 | 31031.9647 | 706.4874 | 2710.8561 | 33742.8207
| 20496605 | 2034 | CHM011 | 0 | 0 | 706.4874 | 31031.9647 | 706.4874 | 2710.8561 | 33742.8207
| 93688245 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 79.7994 | 79.7994
| 93688245 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 79.7994 | 79.7994
| 93688245 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 79.7994 | 79.7994
| 93688245 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 79.7994 | 79.7994
| 93688245 | 2027 | CHM011 | 3.9225 | 0.0069863 | 0 | 0 | 3.9225 | 79.7994 | 79.8064
| 93688245 | 2028 | CHM011 | 3.9225 | 0.0069863 | 0 | 0 | 3.9225 | 79.7994 | 79.8064
| 93688245 | 2029 | CHM011 | 3.9225 | 0.0069863 | 0 | 0 | 3.9225 | 79.7994 | 79.8064
| 93688245 | 2030 | CHM011 | 3.9225 | 0.0069863 | 0 | 0 | 3.9225 | 79.7994 | 79.8064
| 93688245 | 2031 | CHM011 | 3.9225 | 0.0069863 | 0 | 0 | 3.9225 | 79.7994 | 79.8064
| 93688245 | 2032 | CHM011 | 3.9225 | 0.0069863 | 0 | 0 | 3.9225 | 79.7994 | 79.8064
| 93688245 | 2033 | CHM011 | 3.9225 | 0.0069863 | 0 | 0 | 3.9225 | 79.7994 | 79.8064
| 93688245 | 2034 | CHM011 | 3.9225 | 0.0069863 | 0 | 0 | 3.9225 | 79.7994 | 79.8064
| 159372710 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1393.7762 | 1393.7762
| 159372710 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1393.7762 | 1393.7762
| 159372710 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1393.7762 | 1393.7762
| 159372710 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1393.7762 | 1393.7762
| 159372710 | 2027 | CHM011 | 0 | 0 | 106.6036 | 4682.4903 | 106.6036 | 1393.7762 | 6076.2665
| 159372710 | 2028 | CHM011 | 0 | 0 | 106.6036 | 4682.4903 | 106.6036 | 1393.7762 | 6076.2665
| 159372710 | 2029 | CHM011 | 0 | 0 | 106.6036 | 4682.4903 | 106.6036 | 1393.7762 | 6076.2665
| 159372710 | 2030 | CHM011 | 0 | 0 | 106.6036 | 4682.4903 | 106.6036 | 1393.7762 | 6076.2665
| 159372710 | 2031 | CHM011 | 0 | 0 | 106.6036 | 4682.4903 | 106.6036 | 1393.7762 | 6076.2665
| 159372710 | 2032 | CHM011 | 0 | 0 | 106.6036 | 4682.4903 | 106.6036 | 1393.7762 | 6076.2665
| 159372710 | 2033 | CHM011 | 0 | 0 | 106.6036 | 4682.4903 | 106.6036 | 1393.7762 | 6076.2665
| 159372710 | 2034 | CHM011 | 0 | 0 | 106.6036 | 4682.4903 | 106.6036 | 1393.7762 | 6076.2665
| 160318382 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3390.5969 | 3390.5969
| 160318382 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3390.5969 | 3390.5969
| 160318382 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3390.5969 | 3390.5969
| 160318382 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3390.5969 | 3390.5969
| 160318382 | 2027 | CHM011 | 0 | 0 | 350.898 | 15412.9482 | 350.898 | 3390.5969 | 18803.5451
| 160318382 | 2028 | CHM011 | 0 | 0 | 350.898 | 15412.9482 | 350.898 | 3390.5969 | 18803.5451
| 160318382 | 2029 | CHM011 | 0 | 0 | 350.898 | 15412.9482 | 350.898 | 3390.5969 | 18803.5451
| 160318382 | 2030 | CHM011 | 0 | 0 | 350.898 | 15412.9482 | 350.898 | 3390.5969 | 18803.5451
| 160318382 | 2031 | CHM011 | 0 | 0 | 350.898 | 15412.9482 | 350.898 | 3390.5969 | 18803.5451
| 160318382 | 2032 | CHM011 | 0 | 0 | 350.898 | 15412.9482 | 350.898 | 3390.5969 | 18803.5451
| 160318382 | 2033 | CHM011 | 0 | 0 | 350.898 | 15412.9482 | 350.898 | 3390.5969 | 18803.5451
| 160318382 | 2034 | CHM011 | 0 | 0 | 350.898 | 15412.9482 | 350.898 | 3390.5969 | 18803.5451
| 160864049 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 4469.8552 | 4469.8552
| 160864049 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 4469.8552 | 4469.8552
| 160864049 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 4469.8552 | 4469.8552
| 160864049 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 4469.8552 | 4469.8552
| 160864049 | 2027 | CHM011 | 0 | 0 | 0 | 0 | 0 | 4469.8552 | 4469.8552
| 160864049 | 2028 | CHM011 | 0 | 0 | 0 | 0 | 0 | 4469.8552 | 4469.8552
| 160864049 | 2029 | CHM011 | 0 | 0 | 0 | 0 | 0 | 4469.8552 | 4469.8552
| 160864049 | 2030 | CHM011 | 0 | 0 | 0 | 0 | 0 | 4469.8552 | 4469.8552
| 160864049 | 2031 | CHM011 | 0 | 0 | 0 | 0 | 0 | 4469.8552 | 4469.8552
| 160864049 | 2032 | CHM011 | 0 | 0 | 0 | 0 | 0 | 4469.8552 | 4469.8552
| 160864049 | 2033 | CHM011 | 0 | 0 | 0 | 0 | 0 | 4469.8552 | 4469.8552
| 160864049 | 2034 | CHM011 | 0 | 0 | 0 | 0 | 0 | 4469.8552 | 4469.8552
| 160909250 | 2023 | CHM011 | 1.1593 | 0 | 0 | 0 | 1.1593 | 2435.2907 | 2435.2907
| 160909250 | 2024 | CHM011 | 0.58742 | 0.012902 | 0 | 0 | 0.58742 | 2435.2907 | 2435.3036
| 160909250 | 2025 | CHM011 | 1.5731 | 0.037188 | 0 | 0 | 1.5731 | 2435.2907 | 2435.3279
| 160909250 | 2026 | CHM011 | 1.5731 | 0.037188 | 0 | 0 | 1.5731 | 2435.2907 | 2435.3279
| 160909250 | 2027 | CHM011 | 1063.4992 | 10.573 | 193.407 | 8495.2692 | 1256.9062 | 2435.2907 | 10941.1329
| 160909250 | 2028 | CHM011 | 1063.4992 | 10.573 | 193.407 | 8495.2692 | 1256.9062 | 2435.2907 | 10941.1329
| 160909250 | 2029 | CHM011 | 1063.4992 | 10.573 | 193.407 | 8495.2692 | 1256.9062 | 2435.2907 | 10941.1329
| 160909250 | 2030 | CHM011 | 1063.4992 | 10.573 | 193.407 | 8495.2692 | 1256.9062 | 2435.2907 | 10941.1329
| 160909250 | 2031 | CHM011 | 1063.4992 | 10.573 | 193.407 | 8495.2692 | 1256.9062 | 2435.2907 | 10941.1329
| 160909250 | 2032 | CHM011 | 1063.4992 | 10.573 | 193.407 | 8495.2692 | 1256.9062 | 2435.2907 | 10941.1329
| 160909250 | 2033 | CHM011 | 1063.4992 | 10.573 | 193.407 | 8495.2692 | 1256.9062 | 2435.2907 | 10941.1329
| 160909250 | 2034 | CHM011 | 1063.4992 | 10.573 | 193.407 | 8495.2692 | 1256.9062 | 2435.2907 | 10941.1329
| 162767233 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3602.3334 | 3602.3334
| 162767233 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3602.3334 | 3602.3334
| 162767233 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3602.3334 | 3602.3334
| 162767233 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 3602.3334 | 3602.3334
| 162767233 | 2027 | CHM011 | 2405.3035 | 26.2314 | 157.6364 | 6924.0705 | 2562.9399 | 3602.3334 | 10552.6353
| 162767233 | 2028 | CHM011 | 2405.3035 | 26.2314 | 157.6364 | 6924.0705 | 2562.9399 | 3602.3334 | 10552.6353
| 162767233 | 2029 | CHM011 | 2405.3035 | 26.2314 | 157.6364 | 6924.0705 | 2562.9399 | 3602.3334 | 10552.6353
| 162767233 | 2030 | CHM011 | 2405.3035 | 26.2314 | 157.6364 | 6924.0705 | 2562.9399 | 3602.3334 | 10552.6353
| 162767233 | 2031 | CHM011 | 2405.3035 | 26.2314 | 157.6364 | 6924.0705 | 2562.9399 | 3602.3334 | 10552.6353
| 162767233 | 2032 | CHM011 | 2405.3035 | 26.2314 | 157.6364 | 6924.0705 | 2562.9399 | 3602.3334 | 10552.6353
| 162767233 | 2033 | CHM011 | 2405.3035 | 26.2314 | 157.6364 | 6924.0705 | 2562.9399 | 3602.3334 | 10552.6353
| 162767233 | 2034 | CHM011 | 2405.3035 | 26.2314 | 157.6364 | 6924.0705 | 2562.9399 | 3602.3334 | 10552.6353
| 162814555 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 6482.4765 | 6482.4765
| 162814555 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 6482.4765 | 6482.4765
| 162814555 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 6482.4765 | 6482.4765
| 162814555 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 6482.4765 | 6482.4765
| 162814555 | 2027 | CHM011 | 0 | 0 | 0 | 0 | 0 | 6482.4765 | 6482.4765
| 162814555 | 2028 | CHM011 | 0 | 0 | 0 | 0 | 0 | 6482.4765 | 6482.4765
| 162814555 | 2029 | CHM011 | 0 | 0 | 0 | 0 | 0 | 6482.4765 | 6482.4765
| 162814555 | 2030 | CHM011 | 0 | 0 | 0 | 0 | 0 | 6482.4765 | 6482.4765
| 162814555 | 2031 | CHM011 | 0 | 0 | 0 | 0 | 0 | 6482.4765 | 6482.4765
| 162814555 | 2032 | CHM011 | 0 | 0 | 0 | 0 | 0 | 6482.4765 | 6482.4765
| 162814555 | 2033 | CHM011 | 0 | 0 | 0 | 0 | 0 | 6482.4765 | 6482.4765
| 162814555 | 2034 | CHM011 | 0 | 0 | 0 | 0 | 0 | 6482.4765 | 6482.4765
| 163186429 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 2214.4285 | 2214.4285
| 163186429 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 2214.4285 | 2214.4285
| 163186429 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 2214.4285 | 2214.4285
| 163186429 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 2214.4285 | 2214.4285
| 163186429 | 2027 | CHM011 | 0 | 0 | 209.0281 | 9181.4124 | 209.0281 | 2214.4285 | 11395.8409
| 163186429 | 2028 | CHM011 | 0 | 0 | 209.0281 | 9181.4124 | 209.0281 | 2214.4285 | 11395.8409
| 163186429 | 2029 | CHM011 | 0 | 0 | 209.0281 | 9181.4124 | 209.0281 | 2214.4285 | 11395.8409
| 163186429 | 2030 | CHM011 | 0 | 0 | 209.0281 | 9181.4124 | 209.0281 | 2214.4285 | 11395.8409
| 163186429 | 2031 | CHM011 | 0 | 0 | 209.0281 | 9181.4124 | 209.0281 | 2214.4285 | 11395.8409
| 163186429 | 2032 | CHM011 | 0 | 0 | 209.0281 | 9181.4124 | 209.0281 | 2214.4285 | 11395.8409
| 163186429 | 2033 | CHM011 | 0 | 0 | 209.0281 | 9181.4124 | 209.0281 | 2214.4285 | 11395.8409
| 163186429 | 2034 | CHM011 | 0 | 0 | 209.0281 | 9181.4124 | 209.0281 | 2214.4285 | 11395.8409
| 163310477 | 2023 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1892.4991 | 1892.4991
| 163310477 | 2024 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1892.4991 | 1892.4991
| 163310477 | 2025 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1892.4991 | 1892.4991
| 163310477 | 2026 | CHM011 | 0 | 0 | 0 | 0 | 0 | 1892.4991 | 1892.4991
| 163310477 | 2027 | CHM011 | 0 | 0 | 424.7936 | 18658.7625 | 424.7936 | 1892.4991 | 20551.2617
| 163310477 | 2028 | CHM011 | 0 | 0 | 424.7936 | 18658.7625 | 424.7936 | 1892.4991 | 20551.2617
| 163310477 | 2029 | CHM011 | 0 | 0 | 424.7936 | 18658.7625 | 424.7936 | 1892.4991 | 20551.2617
| 163310477 | 2030 | CHM011 | 0 | 0 | 424.7936 | 18658.7625 | 424.7936 | 1892.4991 | 20551.2617
| 163310477 | 2031 | CHM011 | 0 | 0 | 424.7936 | 18658.7625 | 424.7936 | 1892.4991 | 20551.2617
| 163310477 | 2032 | CHM011 | 0 | 0 | 424.7936 | 18658.7625 | 424.7936 | 1892.4991 | 20551.2617
| 163310477 | 2033 | CHM011 | 0 | 0 | 424.7936 | 18658.7625 | 424.7936 | 1892.4991 | 20551.2617
| 163310477 | 2034 | CHM011 | 0 | 0 | 424.7936 | 18658.7625 | 424.7936 | 1892.4991 | 20551.2617
| 20252909 | 2023 | CLC003 | 0 | 0 | 0 | 0 | 0 | 6075.1206 | 6075.1206
| 20252909 | 2024 | CLC003 | 23.4294 | 0.12777 | 0 | 0 | 23.4294 | 6075.1206 | 6075.2483
| 20252909 | 2025 | CLC003 | 43.1217 | 1.418 | 0 | 0 | 43.1217 | 6075.1206 | 6076.5385
| 20252909 | 2026 | CLC003 | 425.2796 | 0.69271 | 0 | 0 | 425.2796 | 6075.1206 | 6075.8133
| 20252909 | 2027 | CLC003 | 782.0284 | 1.4287 | 0 | 0 | 782.0284 | 6075.1206 | 6076.5493
| 20252909 | 2028 | CLC003 | 1202.5865 | 3.2132 | 0 | 0 | 1202.5865 | 6075.1206 | 6078.3338
| 20252909 | 2029 | CLC003 | 1202.5865 | 3.2132 | 0 | 0 | 1202.5865 | 6075.1206 | 6078.3338
| 20252909 | 2030 | CLC003 | 1202.5865 | 3.2132 | 0 | 0 | 1202.5865 | 6075.1206 | 6078.3338
| 20252909 | 2031 | CLC003 | 1202.5865 | 3.2132 | 0 | 0 | 1202.5865 | 6075.1206 | 6078.3338
| 20252909 | 2032 | CLC003 | 1202.5865 | 3.2132 | 0 | 0 | 1202.5865 | 6075.1206 | 6078.3338
| 20252909 | 2033 | CLC003 | 1202.5865 | 3.2132 | 0 | 0 | 1202.5865 | 6075.1206 | 6078.3338
| 20252909 | 2034 | CLC003 | 1202.5865 | 3.2132 | 0 | 0 | 1202.5865 | 6075.1206 | 6078.3338
| 20256392 | 2023 | CLC003 | 5.1292 | 0 | 0 | 0 | 5.1292 | 858.0772 | 858.0772
| 20256392 | 2024 | CLC003 | 52.8922 | 0.33889 | 0 | 0 | 52.8922 | 858.0772 | 858.4161
| 20256392 | 2025 | CLC003 | 71.3605 | 1.3077 | 0 | 0 | 71.3605 | 858.0772 | 859.3849
| 20256392 | 2026 | CLC003 | 227.579 | 0.37557 | 0 | 0 | 227.579 | 858.0772 | 858.4527
| 20256392 | 2027 | CLC003 | 670.283 | 1.3308 | 0 | 0 | 670.283 | 858.0772 | 859.408
| 20256392 | 2028 | CLC003 | 1143.3361 | 3.4061 | 0 | 0 | 1143.3361 | 858.0772 | 861.4832
| 20256392 | 2029 | CLC003 | 1143.3361 | 3.4061 | 0 | 0 | 1143.3361 | 858.0772 | 861.4832
| 20256392 | 2030 | CLC003 | 1143.3361 | 3.4061 | 0 | 0 | 1143.3361 | 858.0772 | 861.4832
| 20256392 | 2031 | CLC003 | 1143.3361 | 3.4061 | 0 | 0 | 1143.3361 | 858.0772 | 861.4832
| 20256392 | 2032 | CLC003 | 1143.3361 | 3.4061 | 0 | 0 | 1143.3361 | 858.0772 | 861.4832
| 20256392 | 2033 | CLC003 | 1143.3361 | 3.4061 | 0 | 0 | 1143.3361 | 858.0772 | 861.4832
| 20256392 | 2034 | CLC003 | 1143.3361 | 3.4061 | 0 | 0 | 1143.3361 | 858.0772 | 861.4832
| 20266524 | 2023 | CLC003 | 0 | 0 | 0 | 0 | 0 | 87.4008 | 87.4008
| 20266524 | 2024 | CLC003 | 0 | 0 | 0 | 0 | 0 | 87.4008 | 87.4008
| 20266524 | 2025 | CLC003 | 0 | 0 | 0 | 0 | 0 | 87.4008 | 87.4008
| 20266524 | 2026 | CLC003 | 0 | 0 | 0 | 0 | 0 | 87.4008 | 87.4008
| 20266524 | 2027 | CLC003 | 0 | 0 | 0 | 0 | 0 | 87.4008 | 87.4008
| 20266524 | 2028 | CLC003 | 0 | 0 | 0 | 0 | 0 | 87.4008 | 87.4008
| 20266524 | 2029 | CLC003 | 0 | 0 | 0 | 0 | 0 | 87.4008 | 87.4008
| 20266524 | 2030 | CLC003 | 0 | 0 | 0 | 0 | 0 | 87.4008 | 87.4008
| 20266524 | 2031 | CLC003 | 0 | 0 | 0 | 0 | 0 | 87.4008 | 87.4008
| 20266524 | 2032 | CLC003 | 0 | 0 | 0 | 0 | 0 | 87.4008 | 87.4008
| 20266524 | 2033 | CLC003 | 0 | 0 | 0 | 0 | 0 | 87.4008 | 87.4008
| 20266524 | 2034 | CLC003 | 0 | 0 | 0 | 0 | 0 | 87.4008 | 87.4008
| 20286294 | 2023 | CLC003 | 211.922 | 0 | 0 | 0 | 211.922 | 1638.6332 | 1638.6332
| 20286294 | 2024 | CLC003 | 113.1987 | 1.7998 | 0 | 0 | 113.1987 | 1638.6332 | 1640.433
| 20286294 | 2025 | CLC003 | 81.5824 | 1.5493 | 0 | 0 | 81.5824 | 1638.6332 | 1640.1825
| 20286294 | 2026 | CLC003 | 90.8839 | 1.0139 | 0 | 0 | 90.8839 | 1638.6332 | 1639.6471
| 20286294 | 2027 | CLC003 | 123.8588 | 1.1582 | 0 | 0 | 123.8588 | 1638.6332 | 1639.7914
| 20286294 | 2028 | CLC003 | 129.538 | 1.7574 | 0 | 0 | 129.538 | 1638.6332 | 1640.3906
| 20286294 | 2029 | CLC003 | 129.538 | 1.7574 | 0 | 0 | 129.538 | 1638.6332 | 1640.3906
| 20286294 | 2030 | CLC003 | 129.538 | 1.7574 | 0 | 0 | 129.538 | 1638.6332 | 1640.3906
| 20286294 | 2031 | CLC003 | 129.538 | 1.7574 | 0 | 0 | 129.538 | 1638.6332 | 1640.3906
| 20286294 | 2032 | CLC003 | 129.538 | 1.7574 | 0 | 0 | 129.538 | 1638.6332 | 1640.3906
| 20286294 | 2033 | CLC003 | 129.538 | 1.7574 | 0 | 0 | 129.538 | 1638.6332 | 1640.3906
| 20286294 | 2034 | CLC003 | 129.538 | 1.7574 | 0 | 0 | 129.538 | 1638.6332 | 1640.3906
| 20288867 | 2023 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1255.9723 | 1255.9723
| 20288867 | 2024 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1255.9723 | 1255.9723
| 20288867 | 2025 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1255.9723 | 1255.9723
| 20288867 | 2026 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1255.9723 | 1255.9723
| 20288867 | 2027 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1255.9723 | 1255.9723
| 20288867 | 2028 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1255.9723 | 1255.9723
| 20288867 | 2029 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1255.9723 | 1255.9723
| 20288867 | 2030 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1255.9723 | 1255.9723
| 20288867 | 2031 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1255.9723 | 1255.9723
| 20288867 | 2032 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1255.9723 | 1255.9723
| 20288867 | 2033 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1255.9723 | 1255.9723
| 20288867 | 2034 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1255.9723 | 1255.9723
| 20290293 | 2023 | CLC003 | 0 | 0 | 0 | 0 | 0 | 3405.9695 | 3405.9695
| 20290293 | 2024 | CLC003 | 0 | 0 | 0 | 0 | 0 | 3405.9695 | 3405.9695
| 20290293 | 2025 | CLC003 | 0 | 0 | 0 | 0 | 0 | 3405.9695 | 3405.9695
| 20290293 | 2026 | CLC003 | 0 | 0 | 0 | 0 | 0 | 3405.9695 | 3405.9695
| 20290293 | 2027 | CLC003 | 0 | 0 | 0 | 0 | 0 | 3405.9695 | 3405.9695
| 20290293 | 2028 | CLC003 | 0 | 0 | 0 | 0 | 0 | 3405.9695 | 3405.9695
| 20290293 | 2029 | CLC003 | 0 | 0 | 0 | 0 | 0 | 3405.9695 | 3405.9695
| 20290293 | 2030 | CLC003 | 0 | 0 | 0 | 0 | 0 | 3405.9695 | 3405.9695
| 20290293 | 2031 | CLC003 | 0 | 0 | 0 | 0 | 0 | 3405.9695 | 3405.9695
| 20290293 | 2032 | CLC003 | 0 | 0 | 0 | 0 | 0 | 3405.9695 | 3405.9695
| 20290293 | 2033 | CLC003 | 0 | 0 | 0 | 0 | 0 | 3405.9695 | 3405.9695
| 20290293 | 2034 | CLC003 | 0 | 0 | 0 | 0 | 0 | 3405.9695 | 3405.9695
| 20448521 | 2023 | CLC003 | 72.089 | 0 | 0 | 0 | 72.089 | 1310.143 | 1310.143
| 20448521 | 2024 | CLC003 | 74.6057 | 0.43581 | 0 | 0 | 74.6057 | 1310.143 | 1310.5788
| 20448521 | 2025 | CLC003 | 64.3199 | 1.9162 | 0 | 0 | 64.3199 | 1310.143 | 1312.0592
| 20448521 | 2026 | CLC003 | 99.3654 | 2.4026 | 0 | 0 | 99.3654 | 1310.143 | 1312.5456
| 20448521 | 2027 | CLC003 | 60.6248 | 1.0662 | 0 | 0 | 60.6248 | 1310.143 | 1311.2093
| 20448521 | 2028 | CLC003 | 25.2588 | 0.45641 | 0 | 0 | 25.2588 | 1310.143 | 1310.5994
| 20448521 | 2029 | CLC003 | 25.2588 | 0.45641 | 0 | 0 | 25.2588 | 1310.143 | 1310.5994
| 20448521 | 2030 | CLC003 | 25.2588 | 0.45641 | 0 | 0 | 25.2588 | 1310.143 | 1310.5994
| 20448521 | 2031 | CLC003 | 25.2588 | 0.45641 | 0 | 0 | 25.2588 | 1310.143 | 1310.5994
| 20448521 | 2032 | CLC003 | 25.2588 | 0.45641 | 0 | 0 | 25.2588 | 1310.143 | 1310.5994
| 20448521 | 2033 | CLC003 | 25.2588 | 0.45641 | 0 | 0 | 25.2588 | 1310.143 | 1310.5994
| 20448521 | 2034 | CLC003 | 25.2588 | 0.45641 | 0 | 0 | 25.2588 | 1310.143 | 1310.5994
| 20497210 | 2023 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1369.5874 | 1369.5874
| 20497210 | 2024 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1369.5874 | 1369.5874
| 20497210 | 2025 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1369.5874 | 1369.5874
| 20497210 | 2026 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1369.5874 | 1369.5874
| 20497210 | 2027 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1369.5874 | 1369.5874
| 20497210 | 2028 | CLC003 | 0 | 0 | 1.492 | 66.9993 | 1.492 | 1369.5874 | 1436.5867
| 20497210 | 2029 | CLC003 | 0 | 0 | 1.492 | 66.9993 | 1.492 | 1369.5874 | 1436.5867
| 20497210 | 2030 | CLC003 | 0 | 0 | 1.492 | 66.9993 | 1.492 | 1369.5874 | 1436.5867
| 20497210 | 2031 | CLC003 | 0 | 0 | 1.492 | 66.9993 | 1.492 | 1369.5874 | 1436.5867
| 20497210 | 2032 | CLC003 | 0 | 0 | 1.492 | 66.9993 | 1.492 | 1369.5874 | 1436.5867
| 20497210 | 2033 | CLC003 | 0 | 0 | 1.492 | 66.9993 | 1.492 | 1369.5874 | 1436.5867
| 20497210 | 2034 | CLC003 | 0 | 0 | 1.492 | 66.9993 | 1.492 | 1369.5874 | 1436.5867
| 20497221 | 2023 | CLC003 | 0 | 0 | 0 | 0 | 0 | 540.2483 | 540.2483
| 20497221 | 2024 | CLC003 | 0 | 0 | 0 | 0 | 0 | 540.2483 | 540.2483
| 20497221 | 2025 | CLC003 | 0 | 0 | 0 | 0 | 0 | 540.2483 | 540.2483
| 20497221 | 2026 | CLC003 | 0 | 0 | 0 | 0 | 0 | 540.2483 | 540.2483
| 20497221 | 2027 | CLC003 | 0 | 0 | 0 | 0 | 0 | 540.2483 | 540.2483
| 20497221 | 2028 | CLC003 | 0 | 0 | 0 | 0 | 0 | 540.2483 | 540.2483
| 20497221 | 2029 | CLC003 | 0 | 0 | 0 | 0 | 0 | 540.2483 | 540.2483
| 20497221 | 2030 | CLC003 | 0 | 0 | 0 | 0 | 0 | 540.2483 | 540.2483
| 20497221 | 2031 | CLC003 | 0 | 0 | 0 | 0 | 0 | 540.2483 | 540.2483
| 20497221 | 2032 | CLC003 | 0 | 0 | 0 | 0 | 0 | 540.2483 | 540.2483
| 20497221 | 2033 | CLC003 | 0 | 0 | 0 | 0 | 0 | 540.2483 | 540.2483
| 20497221 | 2034 | CLC003 | 0 | 0 | 0 | 0 | 0 | 540.2483 | 540.2483
| 20497724 | 2023 | CLC003 | 7660.7686 | 0 | 0 | 0 | 7660.7686 | 377.3773 | 377.3773
| 20497724 | 2024 | CLC003 | 9425.8103 | 220.0906 | 0 | 0 | 9425.8103 | 377.3773 | 597.4679
| 20497724 | 2025 | CLC003 | 9439.7298 | 197.0002 | 0 | 0 | 9439.7298 | 377.3773 | 574.3775
| 20497724 | 2026 | CLC003 | 11072.1156 | 126.449 | 0 | 0 | 11072.1156 | 377.3773 | 503.8263
| 20497724 | 2027 | CLC003 | 15271.2372 | 184.0612 | 0 | 0 | 15271.2372 | 377.3773 | 561.4384
| 20497724 | 2028 | CLC003 | 14057.2732 | 162.1289 | 5.9777 | 268.4336 | 14063.2509 | 377.3773 | 807.9397
| 20497724 | 2029 | CLC003 | 14057.2732 | 162.1289 | 5.9777 | 268.4336 | 14063.2509 | 377.3773 | 807.9397
| 20497724 | 2030 | CLC003 | 14057.2732 | 162.1289 | 5.9777 | 268.4336 | 14063.2509 | 377.3773 | 807.9397
| 20497724 | 2031 | CLC003 | 14057.2732 | 162.1289 | 5.9777 | 268.4336 | 14063.2509 | 377.3773 | 807.9397
| 20497724 | 2032 | CLC003 | 14057.2732 | 162.1289 | 5.9777 | 268.4336 | 14063.2509 | 377.3773 | 807.9397
| 20497724 | 2033 | CLC003 | 14057.2732 | 162.1289 | 5.9777 | 268.4336 | 14063.2509 | 377.3773 | 807.9397
| 20497724 | 2034 | CLC003 | 14057.2732 | 162.1289 | 5.9777 | 268.4336 | 14063.2509 | 377.3773 | 807.9397
| 20542217 | 2023 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2829.1047 | 2829.1047
| 20542217 | 2024 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2829.1047 | 2829.1047
| 20542217 | 2025 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2829.1047 | 2829.1047
| 20542217 | 2026 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2829.1047 | 2829.1047
| 20542217 | 2027 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2829.1047 | 2829.1047
| 20542217 | 2028 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2829.1047 | 2829.1047
| 20542217 | 2029 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2829.1047 | 2829.1047
| 20542217 | 2030 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2829.1047 | 2829.1047
| 20542217 | 2031 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2829.1047 | 2829.1047
| 20542217 | 2032 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2829.1047 | 2829.1047
| 20542217 | 2033 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2829.1047 | 2829.1047
| 20542217 | 2034 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2829.1047 | 2829.1047
| 20649027 | 2023 | CLC003 | 620.2166 | 0 | 0 | 0 | 620.2166 | 4857.8179 | 4857.8179
| 20649027 | 2024 | CLC003 | 1295.4243 | 11.3276 | 0 | 0 | 1295.4243 | 4857.8179 | 4869.1455
| 20649027 | 2025 | CLC003 | 1844.5286 | 20.133 | 0 | 0 | 1844.5286 | 4857.8179 | 4877.9509
| 20649027 | 2026 | CLC003 | 6428.8694 | 18.774 | 0 | 0 | 6428.8694 | 4857.8179 | 4876.5919
| 20649027 | 2027 | CLC003 | 9752.889 | 30.751 | 0 | 0 | 9752.889 | 4857.8179 | 4888.5689
| 20649027 | 2028 | CLC003 | 12809.0286 | 48.446 | 0 | 0 | 12809.0286 | 4857.8179 | 4906.2639
| 20649027 | 2029 | CLC003 | 12809.0286 | 48.446 | 0 | 0 | 12809.0286 | 4857.8179 | 4906.2639
| 20649027 | 2030 | CLC003 | 12809.0286 | 48.446 | 0 | 0 | 12809.0286 | 4857.8179 | 4906.2639
| 20649027 | 2031 | CLC003 | 12809.0286 | 48.446 | 0 | 0 | 12809.0286 | 4857.8179 | 4906.2639
| 20649027 | 2032 | CLC003 | 12809.0286 | 48.446 | 0 | 0 | 12809.0286 | 4857.8179 | 4906.2639
| 20649027 | 2033 | CLC003 | 12809.0286 | 48.446 | 0 | 0 | 12809.0286 | 4857.8179 | 4906.2639
| 20649027 | 2034 | CLC003 | 12809.0286 | 48.446 | 0 | 0 | 12809.0286 | 4857.8179 | 4906.2639
| 63340261 | 2023 | CLC003 | 359.168 | 0 | 0 | 0 | 359.168 | 2335.277 | 2335.277
| 63340261 | 2024 | CLC003 | 233.9029 | 3.1841 | 0 | 0 | 233.9029 | 2335.277 | 2338.4611
| 63340261 | 2025 | CLC003 | 253.3706 | 3.8821 | 0 | 0 | 253.3706 | 2335.277 | 2339.1591
| 63340261 | 2026 | CLC003 | 451.1508 | 2.9812 | 0 | 0 | 451.1508 | 2335.277 | 2338.2582
| 63340261 | 2027 | CLC003 | 449.9025 | 2.2082 | 0 | 0 | 449.9025 | 2335.277 | 2337.4852
| 63340261 | 2028 | CLC003 | 836.4499 | 4.5397 | 0 | 0 | 836.4499 | 2335.277 | 2339.8167
| 63340261 | 2029 | CLC003 | 836.4499 | 4.5397 | 0 | 0 | 836.4499 | 2335.277 | 2339.8167
| 63340261 | 2030 | CLC003 | 836.4499 | 4.5397 | 0 | 0 | 836.4499 | 2335.277 | 2339.8167
| 63340261 | 2031 | CLC003 | 836.4499 | 4.5397 | 0 | 0 | 836.4499 | 2335.277 | 2339.8167
| 63340261 | 2032 | CLC003 | 836.4499 | 4.5397 | 0 | 0 | 836.4499 | 2335.277 | 2339.8167
| 63340261 | 2033 | CLC003 | 836.4499 | 4.5397 | 0 | 0 | 836.4499 | 2335.277 | 2339.8167
| 63340261 | 2034 | CLC003 | 836.4499 | 4.5397 | 0 | 0 | 836.4499 | 2335.277 | 2339.8167
| 154908473 | 2023 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2997.9689 | 2997.9689
| 154908473 | 2024 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2997.9689 | 2997.9689
| 154908473 | 2025 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2997.9689 | 2997.9689
| 154908473 | 2026 | CLC003 | 0 | 0 | 0 | 0 | 0 | 2997.9689 | 2997.9689
| 154908473 | 2027 | CLC003 | 11.0482 | 0.018448 | 0 | 0 | 11.0482 | 2997.9689 | 2997.9873
| 154908473 | 2028 | CLC003 | 37.8062 | 0.097465 | 0 | 0 | 37.8062 | 2997.9689 | 2998.0664
| 154908473 | 2029 | CLC003 | 37.8062 | 0.097465 | 0 | 0 | 37.8062 | 2997.9689 | 2998.0664
| 154908473 | 2030 | CLC003 | 37.8062 | 0.097465 | 0 | 0 | 37.8062 | 2997.9689 | 2998.0664
| 154908473 | 2031 | CLC003 | 37.8062 | 0.097465 | 0 | 0 | 37.8062 | 2997.9689 | 2998.0664
| 154908473 | 2032 | CLC003 | 37.8062 | 0.097465 | 0 | 0 | 37.8062 | 2997.9689 | 2998.0664
| 154908473 | 2033 | CLC003 | 37.8062 | 0.097465 | 0 | 0 | 37.8062 | 2997.9689 | 2998.0664
| 154908473 | 2034 | CLC003 | 37.8062 | 0.097465 | 0 | 0 | 37.8062 | 2997.9689 | 2998.0664
| 184565263 | 2023 | CLC003 | 0 | 0 | 0 | 0 | 0 | 524.5037 | 524.5037
| 184565263 | 2024 | CLC003 | 0 | 0 | 0 | 0 | 0 | 524.5037 | 524.5037
| 184565263 | 2025 | CLC003 | 0 | 0 | 0 | 0 | 0 | 524.5037 | 524.5037
| 184565263 | 2026 | CLC003 | 0 | 0 | 0 | 0 | 0 | 524.5037 | 524.5037
| 184565263 | 2027 | CLC003 | 0 | 0 | 0 | 0 | 0 | 524.5037 | 524.5037
| 184565263 | 2028 | CLC003 | 0 | 0 | 9.8337 | 441.593 | 9.8337 | 524.5037 | 966.0966
| 184565263 | 2029 | CLC003 | 0 | 0 | 9.8337 | 441.593 | 9.8337 | 524.5037 | 966.0966
| 184565263 | 2030 | CLC003 | 0 | 0 | 9.8337 | 441.593 | 9.8337 | 524.5037 | 966.0966
| 184565263 | 2031 | CLC003 | 0 | 0 | 9.8337 | 441.593 | 9.8337 | 524.5037 | 966.0966
| 184565263 | 2032 | CLC003 | 0 | 0 | 9.8337 | 441.593 | 9.8337 | 524.5037 | 966.0966
| 184565263 | 2033 | CLC003 | 0 | 0 | 9.8337 | 441.593 | 9.8337 | 524.5037 | 966.0966
| 184565263 | 2034 | CLC003 | 0 | 0 | 9.8337 | 441.593 | 9.8337 | 524.5037 | 966.0966
| 202042623 | 2023 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1245.3082 | 1245.3082
| 202042623 | 2024 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1245.3082 | 1245.3082
| 202042623 | 2025 | CLC003 | 0 | 0 | 0 | 0 | 0 | 1245.3082 | 1245.3082
| 202042623 | 2026 | CLC003 | 35.2717 | 0.093147 | 0 | 0 | 35.2717 | 1245.3082 | 1245.4013
| 202042623 | 2027 | CLC003 | 200.1936 | 0.40642 | 0 | 0 | 200.1936 | 1245.3082 | 1245.7146
| 202042623 | 2028 | CLC003 | 3005.0214 | 13.6508 | 460.0979 | 20661.2385 | 3465.1193 | 1245.3082 | 21920.1975
| 202042623 | 2029 | CLC003 | 3005.0214 | 13.6508 | 460.0979 | 20661.2385 | 3465.1193 | 1245.3082 | 21920.1975
| 202042623 | 2030 | CLC003 | 3005.0214 | 13.6508 | 460.0979 | 20661.2385 | 3465.1193 | 1245.3082 | 21920.1975
| 202042623 | 2031 | CLC003 | 3005.0214 | 13.6508 | 460.0979 | 20661.2385 | 3465.1193 | 1245.3082 | 21920.1975
| 202042623 | 2032 | CLC003 | 3005.0214 | 13.6508 | 460.0979 | 20661.2385 | 3465.1193 | 1245.3082 | 21920.1975
| 202042623 | 2033 | CLC003 | 3005.0214 | 13.6508 | 460.0979 | 20661.2385 | 3465.1193 | 1245.3082 | 21920.1975
| 202042623 | 2034 | CLC003 | 3005.0214 | 13.6508 | 460.0979 | 20661.2385 | 3465.1193 | 1245.3082 | 21920.1975
| 20228425 | 2023 | CLC004 | 0 | 0 | 0 | 0 | 0 | 4541.5543 | 4541.5543
| 20228425 | 2024 | CLC004 | 0 | 0 | 0 | 0 | 0 | 4541.5543 | 4541.5543
| 20228425 | 2025 | CLC004 | 0 | 0 | 0 | 0 | 0 | 4541.5543 | 4541.5543
| 20228425 | 2026 | CLC004 | 0 | 0 | 0 | 0 | 0 | 4541.5543 | 4541.5543
| 20228425 | 2027 | CLC004 | 0 | 0 | 0 | 0 | 0 | 4541.5543 | 4541.5543
| 20228425 | 2028 | CLC004 | 0 | 0 | 0 | 0 | 0 | 4541.5543 | 4541.5543
| 20228425 | 2029 | CLC004 | 0 | 0 | 0 | 0 | 0 | 4541.5543 | 4541.5543
| 20228425 | 2030 | CLC004 | 0 | 0 | 0 | 0 | 0 | 4541.5543 | 4541.5543
| 20228425 | 2031 | CLC004 | 0 | 0 | 0 | 0 | 0 | 4541.5543 | 4541.5543
| 20228425 | 2032 | CLC004 | 0 | 0 | 0 | 0 | 0 | 4541.5543 | 4541.5543
| 20228425 | 2033 | CLC004 | 0 | 0 | 0 | 0 | 0 | 4541.5543 | 4541.5543
| 20228425 | 2034 | CLC004 | 0 | 0 | 0 | 0 | 0 | 4541.5543 | 4541.5543
| 20275564 | 2023 | CLC006 | 0 | 0 | 23.4295 | 1052.1302 | 23.4295 | 20344.1179 | 21396.2481
| 20275564 | 2024 | CLC006 | 0 | 0 | 30.307 | 1360.9696 | 30.307 | 20344.1179 | 21705.0875
| 20275564 | 2025 | CLC006 | 0 | 0 | 35.1928 | 1580.3746 | 35.1928 | 20344.1179 | 21924.4925
| 20275564 | 2026 | CLC006 | 0 | 0 | 35.1928 | 1580.3746 | 35.1928 | 20344.1179 | 21924.4925
| 20275564 | 2027 | CLC006 | 0 | 0 | 35.1928 | 1580.3746 | 35.1928 | 20344.1179 | 21924.4925
| 20275564 | 2028 | CLC006 | 0 | 0 | 35.1928 | 1580.3746 | 35.1928 | 20344.1179 | 21924.4925
| 20275564 | 2029 | CLC006 | 0 | 0 | 35.1928 | 1580.3746 | 35.1928 | 20344.1179 | 21924.4925
| 20275564 | 2030 | CLC006 | 0 | 0 | 35.1928 | 1580.3746 | 35.1928 | 20344.1179 | 21924.4925
| 20275564 | 2031 | CLC006 | 0 | 0 | 35.1928 | 1580.3746 | 35.1928 | 20344.1179 | 21924.4925
| 20275564 | 2032 | CLC006 | 0 | 0 | 35.1928 | 1580.3746 | 35.1928 | 20344.1179 | 21924.4925
| 20275564 | 2033 | CLC006 | 0 | 0 | 35.1928 | 1580.3746 | 35.1928 | 20344.1179 | 21924.4925
| 20275564 | 2034 | CLC006 | 0 | 0 | 35.1928 | 1580.3746 | 35.1928 | 20344.1179 | 21924.4925
| 20275582 | 2023 | CLC006 | 0 | 0 | 1.3265 | 59.5683 | 1.3265 | 18999.4934 | 19059.0617
| 20275582 | 2024 | CLC006 | 0 | 0 | 2.0143 | 90.4547 | 2.0143 | 18999.4934 | 19089.9481
| 20275582 | 2025 | CLC006 | 0 | 0 | 1.8084 | 81.2075 | 1.8084 | 18999.4934 | 19080.7008
| 20275582 | 2026 | CLC006 | 0 | 0 | 1.8084 | 81.2075 | 1.8084 | 18999.4934 | 19080.7008
| 20275582 | 2027 | CLC006 | 0 | 0 | 1.8084 | 81.2075 | 1.8084 | 18999.4934 | 19080.7008
| 20275582 | 2028 | CLC006 | 0 | 0 | 1.8084 | 81.2075 | 1.8084 | 18999.4934 | 19080.7008
| 20275582 | 2029 | CLC006 | 0 | 0 | 1.8084 | 81.2075 | 1.8084 | 18999.4934 | 19080.7008
| 20275582 | 2030 | CLC006 | 0 | 0 | 1.8084 | 81.2075 | 1.8084 | 18999.4934 | 19080.7008
| 20275582 | 2031 | CLC006 | 0 | 0 | 1.8084 | 81.2075 | 1.8084 | 18999.4934 | 19080.7008
| 20275582 | 2032 | CLC006 | 0 | 0 | 1.8084 | 81.2075 | 1.8084 | 18999.4934 | 19080.7008
| 20275582 | 2033 | CLC006 | 0 | 0 | 1.8084 | 81.2075 | 1.8084 | 18999.4934 | 19080.7008
| 20275582 | 2034 | CLC006 | 0 | 0 | 1.8084 | 81.2075 | 1.8084 | 18999.4934 | 19080.7008
| 20284964 | 2023 | CLC006 | 0 | 0 | 1.6728 | 75.117 | 1.6728 | 13182.0782 | 13257.1953
| 20284964 | 2024 | CLC006 | 0 | 0 | 2.4241 | 108.8577 | 2.4241 | 13182.0782 | 13290.9359
| 20284964 | 2025 | CLC006 | 4.1116 | 0.058637 | 2.597 | 116.6201 | 6.7086 | 13182.0782 | 13298.7569
| 20284964 | 2026 | CLC006 | 4.1116 | 0.058637 | 2.597 | 116.6201 | 6.7086 | 13182.0782 | 13298.7569
| 20284964 | 2027 | CLC006 | 4.1116 | 0.058637 | 2.597 | 116.6201 | 6.7086 | 13182.0782 | 13298.7569
| 20284964 | 2028 | CLC006 | 4.1116 | 0.058637 | 2.597 | 116.6201 | 6.7086 | 13182.0782 | 13298.7569
| 20284964 | 2029 | CLC006 | 4.1116 | 0.058637 | 2.597 | 116.6201 | 6.7086 | 13182.0782 | 13298.7569
| 20284964 | 2030 | CLC006 | 4.1116 | 0.058637 | 2.597 | 116.6201 | 6.7086 | 13182.0782 | 13298.7569
| 20284964 | 2031 | CLC006 | 4.1116 | 0.058637 | 2.597 | 116.6201 | 6.7086 | 13182.0782 | 13298.7569
| 20284964 | 2032 | CLC006 | 4.1116 | 0.058637 | 2.597 | 116.6201 | 6.7086 | 13182.0782 | 13298.7569
| 20284964 | 2033 | CLC006 | 4.1116 | 0.058637 | 2.597 | 116.6201 | 6.7086 | 13182.0782 | 13298.7569
| 20284964 | 2034 | CLC006 | 4.1116 | 0.058637 | 2.597 | 116.6201 | 6.7086 | 13182.0782 | 13298.7569
| 20285202 | 2023 | CLC006 | 0 | 0 | 0.0022383 | 0.10051 | 0.0022383 | 4387.0136 | 4387.1141
| 20285202 | 2024 | CLC006 | 0 | 0 | 0.0028255 | 0.12688 | 0.0028255 | 4387.0136 | 4387.1405
| 20285202 | 2025 | CLC006 | 0 | 0 | 0.003054 | 0.13715 | 0.003054 | 4387.0136 | 4387.1508
| 20285202 | 2026 | CLC006 | 0 | 0 | 0.003054 | 0.13715 | 0.003054 | 4387.0136 | 4387.1508
| 20285202 | 2027 | CLC006 | 0 | 0 | 0.003054 | 0.13715 | 0.003054 | 4387.0136 | 4387.1508
| 20285202 | 2028 | CLC006 | 0 | 0 | 0.003054 | 0.13715 | 0.003054 | 4387.0136 | 4387.1508
| 20285202 | 2029 | CLC006 | 0 | 0 | 0.003054 | 0.13715 | 0.003054 | 4387.0136 | 4387.1508
| 20285202 | 2030 | CLC006 | 0 | 0 | 0.003054 | 0.13715 | 0.003054 | 4387.0136 | 4387.1508
| 20285202 | 2031 | CLC006 | 0 | 0 | 0.003054 | 0.13715 | 0.003054 | 4387.0136 | 4387.1508
| 20285202 | 2032 | CLC006 | 0 | 0 | 0.003054 | 0.13715 | 0.003054 | 4387.0136 | 4387.1508
| 20285202 | 2033 | CLC006 | 0 | 0 | 0.003054 | 0.13715 | 0.003054 | 4387.0136 | 4387.1508
| 20285202 | 2034 | CLC006 | 0 | 0 | 0.003054 | 0.13715 | 0.003054 | 4387.0136 | 4387.1508
| 20285528 | 2023 | CLC006 | 0 | 0 | 0 | 0 | 0 | 1402.2353 | 1402.2353
| 20285528 | 2024 | CLC006 | 0 | 0 | 0 | 0 | 0 | 1402.2353 | 1402.2353
| 20285528 | 2025 | CLC006 | 0 | 0 | 0 | 0 | 0 | 1402.2353 | 1402.2353
| 20285528 | 2026 | CLC006 | 0 | 0 | 0 | 0 | 0 | 1402.2353 | 1402.2353
| 20285528 | 2027 | CLC006 | 0 | 0 | 0 | 0 | 0 | 1402.2353 | 1402.2353
| 20285528 | 2028 | CLC006 | 0 | 0 | 0 | 0 | 0 | 1402.2353 | 1402.2353
| 20285528 | 2029 | CLC006 | 0 | 0 | 0 | 0 | 0 | 1402.2353 | 1402.2353
| 20285528 | 2030 | CLC006 | 0 | 0 | 0 | 0 | 0 | 1402.2353 | 1402.2353
| 20285528 | 2031 | CLC006 | 0 | 0 | 0 | 0 | 0 | 1402.2353 | 1402.2353
| 20285528 | 2032 | CLC006 | 0 | 0 | 0 | 0 | 0 | 1402.2353 | 1402.2353
| 20285528 | 2033 | CLC006 | 0 | 0 | 0 | 0 | 0 | 1402.2353 | 1402.2353
| 20285528 | 2034 | CLC006 | 0 | 0 | 0 | 0 | 0 | 1402.2353 | 1402.2353
| 20333470 | 2023 | CLC006 | 34.889 | 0 | 0 | 0 | 34.889 | 15017.2868 | 15017.2868
| 20333470 | 2024 | CLC006 | 292.4046 | 4.0778 | 0 | 0 | 292.4046 | 15017.2868 | 15021.3646
| 20333470 | 2025 | CLC006 | 1213.7241 | 18.3061 | 0 | 0 | 1213.7241 | 15017.2868 | 15035.5929
| 20333470 | 2026 | CLC006 | 1213.7241 | 18.3061 | 0 | 0 | 1213.7241 | 15017.2868 | 15035.5929
| 20333470 | 2027 | CLC006 | 1213.7241 | 18.3061 | 0 | 0 | 1213.7241 | 15017.2868 | 15035.5929
| 20333470 | 2028 | CLC006 | 1213.7241 | 18.3061 | 0 | 0 | 1213.7241 | 15017.2868 | 15035.5929
| 20333470 | 2029 | CLC006 | 1213.7241 | 18.3061 | 0 | 0 | 1213.7241 | 15017.2868 | 15035.5929
| 20333470 | 2030 | CLC006 | 1213.7241 | 18.3061 | 0 | 0 | 1213.7241 | 15017.2868 | 15035.5929
| 20333470 | 2031 | CLC006 | 1213.7241 | 18.3061 | 0 | 0 | 1213.7241 | 15017.2868 | 15035.5929
| 20333470 | 2032 | CLC006 | 1213.7241 | 18.3061 | 0 | 0 | 1213.7241 | 15017.2868 | 15035.5929
| 20333470 | 2033 | CLC006 | 1213.7241 | 18.3061 | 0 | 0 | 1213.7241 | 15017.2868 | 15035.5929
| 20333470 | 2034 | CLC006 | 1213.7241 | 18.3061 | 0 | 0 | 1213.7241 | 15017.2868 | 15035.5929
| 20333752 | 2023 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4357.2511 | 4357.2511
| 20333752 | 2024 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4357.2511 | 4357.2511
| 20333752 | 2025 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4357.2511 | 4357.2511
| 20333752 | 2026 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4357.2511 | 4357.2511
| 20333752 | 2027 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4357.2511 | 4357.2511
| 20333752 | 2028 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4357.2511 | 4357.2511
| 20333752 | 2029 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4357.2511 | 4357.2511
| 20333752 | 2030 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4357.2511 | 4357.2511
| 20333752 | 2031 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4357.2511 | 4357.2511
| 20333752 | 2032 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4357.2511 | 4357.2511
| 20333752 | 2033 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4357.2511 | 4357.2511
| 20333752 | 2034 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4357.2511 | 4357.2511
| 20360521 | 2023 | CLC006 | 0 | 0 | 0 | 0 | 0 | 3178.7257 | 3178.7257
| 20360521 | 2024 | CLC006 | 0 | 0 | 0 | 0 | 0 | 3178.7257 | 3178.7257
| 20360521 | 2025 | CLC006 | 0 | 0 | 0 | 0 | 0 | 3178.7257 | 3178.7257
| 20360521 | 2026 | CLC006 | 0 | 0 | 0 | 0 | 0 | 3178.7257 | 3178.7257
| 20360521 | 2027 | CLC006 | 0 | 0 | 0 | 0 | 0 | 3178.7257 | 3178.7257
| 20360521 | 2028 | CLC006 | 0 | 0 | 0 | 0 | 0 | 3178.7257 | 3178.7257
| 20360521 | 2029 | CLC006 | 0 | 0 | 0 | 0 | 0 | 3178.7257 | 3178.7257
| 20360521 | 2030 | CLC006 | 0 | 0 | 0 | 0 | 0 | 3178.7257 | 3178.7257
| 20360521 | 2031 | CLC006 | 0 | 0 | 0 | 0 | 0 | 3178.7257 | 3178.7257
| 20360521 | 2032 | CLC006 | 0 | 0 | 0 | 0 | 0 | 3178.7257 | 3178.7257
| 20360521 | 2033 | CLC006 | 0 | 0 | 0 | 0 | 0 | 3178.7257 | 3178.7257
| 20360521 | 2034 | CLC006 | 0 | 0 | 0 | 0 | 0 | 3178.7257 | 3178.7257
| 20497634 | 2023 | CLC006 | 0 | 0 | 0 | 0 | 0 | 15459.0208 | 15459.0208
| 20497634 | 2024 | CLC006 | 0 | 0 | 0 | 0 | 0 | 15459.0208 | 15459.0208
| 20497634 | 2025 | CLC006 | 0 | 0 | 0 | 0 | 0 | 15459.0208 | 15459.0208
| 20497634 | 2026 | CLC006 | 0 | 0 | 0 | 0 | 0 | 15459.0208 | 15459.0208
| 20497634 | 2027 | CLC006 | 0 | 0 | 0 | 0 | 0 | 15459.0208 | 15459.0208
| 20497634 | 2028 | CLC006 | 0 | 0 | 0 | 0 | 0 | 15459.0208 | 15459.0208
| 20497634 | 2029 | CLC006 | 0 | 0 | 0 | 0 | 0 | 15459.0208 | 15459.0208
| 20497634 | 2030 | CLC006 | 0 | 0 | 0 | 0 | 0 | 15459.0208 | 15459.0208
| 20497634 | 2031 | CLC006 | 0 | 0 | 0 | 0 | 0 | 15459.0208 | 15459.0208
| 20497634 | 2032 | CLC006 | 0 | 0 | 0 | 0 | 0 | 15459.0208 | 15459.0208
| 20497634 | 2033 | CLC006 | 0 | 0 | 0 | 0 | 0 | 15459.0208 | 15459.0208
| 20497634 | 2034 | CLC006 | 0 | 0 | 0 | 0 | 0 | 15459.0208 | 15459.0208
| 20498041 | 2023 | CLC006 | 0 | 0 | 0.072684 | 3.264 | 0.072684 | 928.6502 | 931.9142
| 20498041 | 2024 | CLC006 | 0 | 0 | 0.22148 | 9.9457 | 0.22148 | 928.6502 | 938.5959
| 20498041 | 2025 | CLC006 | 0 | 0 | 0.2423 | 10.881 | 0.2423 | 928.6502 | 939.5312
| 20498041 | 2026 | CLC006 | 0 | 0 | 0.2423 | 10.881 | 0.2423 | 928.6502 | 939.5312
| 20498041 | 2027 | CLC006 | 0 | 0 | 0.2423 | 10.881 | 0.2423 | 928.6502 | 939.5312
| 20498041 | 2028 | CLC006 | 0 | 0 | 0.2423 | 10.881 | 0.2423 | 928.6502 | 939.5312
| 20498041 | 2029 | CLC006 | 0 | 0 | 0.2423 | 10.881 | 0.2423 | 928.6502 | 939.5312
| 20498041 | 2030 | CLC006 | 0 | 0 | 0.2423 | 10.881 | 0.2423 | 928.6502 | 939.5312
| 20498041 | 2031 | CLC006 | 0 | 0 | 0.2423 | 10.881 | 0.2423 | 928.6502 | 939.5312
| 20498041 | 2032 | CLC006 | 0 | 0 | 0.2423 | 10.881 | 0.2423 | 928.6502 | 939.5312
| 20498041 | 2033 | CLC006 | 0 | 0 | 0.2423 | 10.881 | 0.2423 | 928.6502 | 939.5312
| 20498041 | 2034 | CLC006 | 0 | 0 | 0.2423 | 10.881 | 0.2423 | 928.6502 | 939.5312
| 20669568 | 2023 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4207.921 | 4207.921
| 20669568 | 2024 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4207.921 | 4207.921
| 20669568 | 2025 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4207.921 | 4207.921
| 20669568 | 2026 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4207.921 | 4207.921
| 20669568 | 2027 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4207.921 | 4207.921
| 20669568 | 2028 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4207.921 | 4207.921
| 20669568 | 2029 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4207.921 | 4207.921
| 20669568 | 2030 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4207.921 | 4207.921
| 20669568 | 2031 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4207.921 | 4207.921
| 20669568 | 2032 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4207.921 | 4207.921
| 20669568 | 2033 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4207.921 | 4207.921
| 20669568 | 2034 | CLC006 | 0 | 0 | 0 | 0 | 0 | 4207.921 | 4207.921
| 181907744 | 2023 | CLC006 | 0 | 0 | 0 | 0 | 0 | 10972.7087 | 10972.7087
| 181907744 | 2024 | CLC006 | 0 | 0 | 0 | 0 | 0 | 10972.7087 | 10972.7087
| 181907744 | 2025 | CLC006 | 0 | 0 | 0 | 0 | 0 | 10972.7087 | 10972.7087
| 181907744 | 2026 | CLC006 | 0 | 0 | 0 | 0 | 0 | 10972.7087 | 10972.7087
| 181907744 | 2027 | CLC006 | 0 | 0 | 0 | 0 | 0 | 10972.7087 | 10972.7087
| 181907744 | 2028 | CLC006 | 0 | 0 | 0 | 0 | 0 | 10972.7087 | 10972.7087
| 181907744 | 2029 | CLC006 | 0 | 0 | 0 | 0 | 0 | 10972.7087 | 10972.7087
| 181907744 | 2030 | CLC006 | 0 | 0 | 0 | 0 | 0 | 10972.7087 | 10972.7087
| 181907744 | 2031 | CLC006 | 0 | 0 | 0 | 0 | 0 | 10972.7087 | 10972.7087
| 181907744 | 2032 | CLC006 | 0 | 0 | 0 | 0 | 0 | 10972.7087 | 10972.7087
| 181907744 | 2033 | CLC006 | 0 | 0 | 0 | 0 | 0 | 10972.7087 | 10972.7087
| 181907744 | 2034 | CLC006 | 0 | 0 | 0 | 0 | 0 | 10972.7087 | 10972.7087
| 20215213 | 2023 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2752.9428 | 2752.9428
| 20215213 | 2024 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2752.9428 | 2752.9428
| 20215213 | 2025 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2752.9428 | 2752.9428
| 20215213 | 2026 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2752.9428 | 2752.9428
| 20215213 | 2027 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2752.9428 | 2752.9428
| 20215213 | 2028 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2752.9428 | 2752.9428
| 20215213 | 2029 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2752.9428 | 2752.9428
| 20215213 | 2030 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2752.9428 | 2752.9428
| 20215213 | 2031 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2752.9428 | 2752.9428
| 20215213 | 2032 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2752.9428 | 2752.9428
| 20215213 | 2033 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2752.9428 | 2752.9428
| 20215213 | 2034 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2752.9428 | 2752.9428
| 20215481 | 2023 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1206.0269 | 1206.0269
| 20215481 | 2024 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1206.0269 | 1206.0269
| 20215481 | 2025 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1206.0269 | 1206.0269
| 20215481 | 2026 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1206.0269 | 1206.0269
| 20215481 | 2027 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1206.0269 | 1206.0269
| 20215481 | 2028 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1206.0269 | 1206.0269
| 20215481 | 2029 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1206.0269 | 1206.0269
| 20215481 | 2030 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1206.0269 | 1206.0269
| 20215481 | 2031 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1206.0269 | 1206.0269
| 20215481 | 2032 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1206.0269 | 1206.0269
| 20215481 | 2033 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1206.0269 | 1206.0269
| 20215481 | 2034 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1206.0269 | 1206.0269
| 20248340 | 2023 | CLC013 | 0.26718 | 0 | 0 | 0 | 0.26718 | 2914.9754 | 2914.9754
| 20248340 | 2024 | CLC013 | 0.084451 | 0 | 0 | 0 | 0.084451 | 2914.9754 | 2914.9754
| 20248340 | 2025 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2914.9754 | 2914.9754
| 20248340 | 2026 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2914.9754 | 2914.9754
| 20248340 | 2027 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2914.9754 | 2914.9754
| 20248340 | 2028 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2914.9754 | 2914.9754
| 20248340 | 2029 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2914.9754 | 2914.9754
| 20248340 | 2030 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2914.9754 | 2914.9754
| 20248340 | 2031 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2914.9754 | 2914.9754
| 20248340 | 2032 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2914.9754 | 2914.9754
| 20248340 | 2033 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2914.9754 | 2914.9754
| 20248340 | 2034 | CLC013 | 0 | 0 | 0 | 0 | 0 | 2914.9754 | 2914.9754
| 20265879 | 2023 | CLC013 | 6192.3735 | 0 | 0 | 0 | 6192.3735 | 3008.473 | 3008.473
| 20265879 | 2024 | CLC013 | 6367.1565 | 139.3418 | 0.040318 | 1.8105 | 6367.1968 | 3008.473 | 3149.6253
| 20265879 | 2025 | CLC013 | 6195.7158 | 146.5725 | 0.1959 | 8.797 | 6195.9117 | 3008.473 | 3163.8425
| 20265879 | 2026 | CLC013 | 6414.527 | 89.5435 | 0.44701 | 20.0735 | 6414.974 | 3008.473 | 3118.0899
| 20265879 | 2027 | CLC013 | 12165.1907 | 182.5674 | 2.5518 | 114.5923 | 12167.7426 | 3008.473 | 3305.6327
| 20265879 | 2028 | CLC013 | 13827.0001 | 208.016 | 18.9196 | 849.6078 | 13845.9197 | 3008.473 | 4066.0967
| 20265879 | 2029 | CLC013 | 13827.0001 | 208.016 | 18.9196 | 849.6078 | 13845.9197 | 3008.473 | 4066.0967
| 20265879 | 2030 | CLC013 | 13827.0001 | 208.016 | 18.9196 | 849.6078 | 13845.9197 | 3008.473 | 4066.0967
| 20265879 | 2031 | CLC013 | 13827.0001 | 208.016 | 18.9196 | 849.6078 | 13845.9197 | 3008.473 | 4066.0967
| 20265879 | 2032 | CLC013 | 13827.0001 | 208.016 | 18.9196 | 849.6078 | 13845.9197 | 3008.473 | 4066.0967
| 20265879 | 2033 | CLC013 | 13827.0001 | 208.016 | 18.9196 | 849.6078 | 13845.9197 | 3008.473 | 4066.0967
| 20265879 | 2034 | CLC013 | 13827.0001 | 208.016 | 18.9196 | 849.6078 | 13845.9197 | 3008.473 | 4066.0967
| 20451878 | 2023 | CLC013 | 0 | 0 | 1.8455 | 82.8739 | 1.8455 | 1200.8781 | 1283.752
| 20451878 | 2024 | CLC013 | 0 | 0 | 7.5688 | 339.888 | 7.5688 | 1200.8781 | 1540.7661
| 20451878 | 2025 | CLC013 | 0 | 0 | 35.2382 | 1582.4115 | 35.2382 | 1200.8781 | 2783.2896
| 20451878 | 2026 | CLC013 | 0 | 0 | 54.0079 | 2425.2907 | 54.0079 | 1200.8781 | 3626.1688
| 20451878 | 2027 | CLC013 | 0 | 0 | 89.6052 | 4023.8254 | 89.6052 | 1200.8781 | 5224.7035
| 20451878 | 2028 | CLC013 | 0 | 0 | 117.4586 | 5274.618 | 117.4586 | 1200.8781 | 6475.4961
| 20451878 | 2029 | CLC013 | 0 | 0 | 117.4586 | 5274.618 | 117.4586 | 1200.8781 | 6475.4961
| 20451878 | 2030 | CLC013 | 0 | 0 | 117.4586 | 5274.618 | 117.4586 | 1200.8781 | 6475.4961
| 20451878 | 2031 | CLC013 | 0 | 0 | 117.4586 | 5274.618 | 117.4586 | 1200.8781 | 6475.4961
| 20451878 | 2032 | CLC013 | 0 | 0 | 117.4586 | 5274.618 | 117.4586 | 1200.8781 | 6475.4961
| 20451878 | 2033 | CLC013 | 0 | 0 | 117.4586 | 5274.618 | 117.4586 | 1200.8781 | 6475.4961
| 20451878 | 2034 | CLC013 | 0 | 0 | 117.4586 | 5274.618 | 117.4586 | 1200.8781 | 6475.4961
| 20497652 | 2023 | CLC013 | 1700.2742 | 0 | 0 | 0 | 1700.2742 | 1483.181 | 1483.181
| 20497652 | 2024 | CLC013 | 1735.105 | 31.8129 | 0 | 0 | 1735.105 | 1483.181 | 1514.9939
| 20497652 | 2025 | CLC013 | 1734.3497 | 31.3625 | 0 | 0 | 1734.3497 | 1483.181 | 1514.5435
| 20497652 | 2026 | CLC013 | 1813.2596 | 16.1265 | 0 | 0 | 1813.2596 | 1483.181 | 1499.3074
| 20497652 | 2027 | CLC013 | 1879.6775 | 14.0103 | 0 | 0 | 1879.6775 | 1483.181 | 1497.1913
| 20497652 | 2028 | CLC013 | 1874.8277 | 15.8615 | 0 | 0 | 1874.8277 | 1483.181 | 1499.0425
| 20497652 | 2029 | CLC013 | 1874.8277 | 15.8615 | 0 | 0 | 1874.8277 | 1483.181 | 1499.0425
| 20497652 | 2030 | CLC013 | 1874.8277 | 15.8615 | 0 | 0 | 1874.8277 | 1483.181 | 1499.0425
| 20497652 | 2031 | CLC013 | 1874.8277 | 15.8615 | 0 | 0 | 1874.8277 | 1483.181 | 1499.0425
| 20497652 | 2032 | CLC013 | 1874.8277 | 15.8615 | 0 | 0 | 1874.8277 | 1483.181 | 1499.0425
| 20497652 | 2033 | CLC013 | 1874.8277 | 15.8615 | 0 | 0 | 1874.8277 | 1483.181 | 1499.0425
| 20497652 | 2034 | CLC013 | 1874.8277 | 15.8615 | 0 | 0 | 1874.8277 | 1483.181 | 1499.0425
| 20528023 | 2023 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1335.0313 | 1335.0313
| 20528023 | 2024 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1335.0313 | 1335.0313
| 20528023 | 2025 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1335.0313 | 1335.0313
| 20528023 | 2026 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1335.0313 | 1335.0313
| 20528023 | 2027 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1335.0313 | 1335.0313
| 20528023 | 2028 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1335.0313 | 1335.0313
| 20528023 | 2029 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1335.0313 | 1335.0313
| 20528023 | 2030 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1335.0313 | 1335.0313
| 20528023 | 2031 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1335.0313 | 1335.0313
| 20528023 | 2032 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1335.0313 | 1335.0313
| 20528023 | 2033 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1335.0313 | 1335.0313
| 20528023 | 2034 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1335.0313 | 1335.0313
| 120141457 | 2023 | CLC013 | 0 | 0 | 0 | 0 | 0 | 4399.5785 | 4399.5785
| 120141457 | 2024 | CLC013 | 0 | 0 | 0 | 0 | 0 | 4399.5785 | 4399.5785
| 120141457 | 2025 | CLC013 | 0 | 0 | 0 | 0 | 0 | 4399.5785 | 4399.5785
| 120141457 | 2026 | CLC013 | 0 | 0 | 0 | 0 | 0 | 4399.5785 | 4399.5785
| 120141457 | 2027 | CLC013 | 0 | 0 | 0.18069 | 8.1141 | 0.18069 | 4399.5785 | 4407.6926
| 120141457 | 2028 | CLC013 | 0 | 0 | 4.3937 | 197.3056 | 4.3937 | 4399.5785 | 4596.8841
| 120141457 | 2029 | CLC013 | 0 | 0 | 4.3937 | 197.3056 | 4.3937 | 4399.5785 | 4596.8841
| 120141457 | 2030 | CLC013 | 0 | 0 | 4.3937 | 197.3056 | 4.3937 | 4399.5785 | 4596.8841
| 120141457 | 2031 | CLC013 | 0 | 0 | 4.3937 | 197.3056 | 4.3937 | 4399.5785 | 4596.8841
| 120141457 | 2032 | CLC013 | 0 | 0 | 4.3937 | 197.3056 | 4.3937 | 4399.5785 | 4596.8841
| 120141457 | 2033 | CLC013 | 0 | 0 | 4.3937 | 197.3056 | 4.3937 | 4399.5785 | 4596.8841
| 120141457 | 2034 | CLC013 | 0 | 0 | 4.3937 | 197.3056 | 4.3937 | 4399.5785 | 4596.8841
| 155079261 | 2023 | CLC013 | 0 | 0 | 0.79153 | 35.5445 | 0.79153 | 186.0838 | 221.6283
| 155079261 | 2024 | CLC013 | 0 | 0 | 1.137 | 51.0563 | 1.137 | 186.0838 | 237.14
| 155079261 | 2025 | CLC013 | 0 | 0 | 2.5178 | 113.0659 | 2.5178 | 186.0838 | 299.1497
| 155079261 | 2026 | CLC013 | 0 | 0 | 3.5149 | 157.8389 | 3.5149 | 186.0838 | 343.9226
| 155079261 | 2027 | CLC013 | 0 | 0 | 5.7865 | 259.8508 | 5.7865 | 186.0838 | 445.9346
| 155079261 | 2028 | CLC013 | 0 | 0 | 8.6598 | 388.8778 | 8.6598 | 186.0838 | 574.9616
| 155079261 | 2029 | CLC013 | 0 | 0 | 8.6598 | 388.8778 | 8.6598 | 186.0838 | 574.9616
| 155079261 | 2030 | CLC013 | 0 | 0 | 8.6598 | 388.8778 | 8.6598 | 186.0838 | 574.9616
| 155079261 | 2031 | CLC013 | 0 | 0 | 8.6598 | 388.8778 | 8.6598 | 186.0838 | 574.9616
| 155079261 | 2032 | CLC013 | 0 | 0 | 8.6598 | 388.8778 | 8.6598 | 186.0838 | 574.9616
| 155079261 | 2033 | CLC013 | 0 | 0 | 8.6598 | 388.8778 | 8.6598 | 186.0838 | 574.9616
| 155079261 | 2034 | CLC013 | 0 | 0 | 8.6598 | 388.8778 | 8.6598 | 186.0838 | 574.9616
| 156871043 | 2023 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1865.3917 | 1865.3917
| 156871043 | 2024 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1865.3917 | 1865.3917
| 156871043 | 2025 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1865.3917 | 1865.3917
| 156871043 | 2026 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1865.3917 | 1865.3917
| 156871043 | 2027 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1865.3917 | 1865.3917
| 156871043 | 2028 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1865.3917 | 1865.3917
| 156871043 | 2029 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1865.3917 | 1865.3917
| 156871043 | 2030 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1865.3917 | 1865.3917
| 156871043 | 2031 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1865.3917 | 1865.3917
| 156871043 | 2032 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1865.3917 | 1865.3917
| 156871043 | 2033 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1865.3917 | 1865.3917
| 156871043 | 2034 | CLC013 | 0 | 0 | 0 | 0 | 0 | 1865.3917 | 1865.3917
| 201013189 | 2023 | CLC013 | 0 | 0 | 0 | 0 | 0 | 6805.2568 | 6805.2568
| 201013189 | 2024 | CLC013 | 0 | 0 | 0 | 0 | 0 | 6805.2568 | 6805.2568
| 201013189 | 2025 | CLC013 | 0 | 0 | 0.016483 | 0.74017 | 0.016483 | 6805.2568 | 6805.997
| 201013189 | 2026 | CLC013 | 0 | 0 | 0.073545 | 3.3026 | 0.073545 | 6805.2568 | 6808.5594
| 201013189 | 2027 | CLC013 | 0 | 0 | 0.47715 | 21.4271 | 0.47715 | 6805.2568 | 6826.6839
| 201013189 | 2028 | CLC013 | 0 | 0 | 1.1844 | 53.1859 | 1.1844 | 6805.2568 | 6858.4428
| 201013189 | 2029 | CLC013 | 0 | 0 | 1.1844 | 53.1859 | 1.1844 | 6805.2568 | 6858.4428
| 201013189 | 2030 | CLC013 | 0 | 0 | 1.1844 | 53.1859 | 1.1844 | 6805.2568 | 6858.4428
| 201013189 | 2031 | CLC013 | 0 | 0 | 1.1844 | 53.1859 | 1.1844 | 6805.2568 | 6858.4428
| 201013189 | 2032 | CLC013 | 0 | 0 | 1.1844 | 53.1859 | 1.1844 | 6805.2568 | 6858.4428
| 201013189 | 2033 | CLC013 | 0 | 0 | 1.1844 | 53.1859 | 1.1844 | 6805.2568 | 6858.4428
| 201013189 | 2034 | CLC013 | 0 | 0 | 1.1844 | 53.1859 | 1.1844 | 6805.2568 | 6858.4428
| 20644488 | 2023 | CME016 | 0 | 0 | 0 | 0 | 0 | 8263.1742 | 8263.1742
| 20644488 | 2024 | CME016 | 6.9992 | 0.098164 | 0 | 0 | 6.9992 | 8263.1742 | 8263.2723
| 20644488 | 2025 | CME016 | 9.8995 | 0.17079 | 0 | 0 | 9.8995 | 8263.1742 | 8263.345
| 20644488 | 2026 | CME016 | 209.8923 | 0.67015 | 4.3235 | 202.6656 | 214.2158 | 8263.1742 | 8466.5099
| 20644488 | 2027 | CME016 | 1111.2126 | 5.2067 | 183.2204 | 8588.5069 | 1294.4329 | 8263.1742 | 16856.8878
| 20644488 | 2028 | CME016 | 1111.2126 | 5.2067 | 183.2204 | 8588.5069 | 1294.4329 | 8263.1742 | 16856.8878
| 20644488 | 2029 | CME016 | 1111.2126 | 5.2067 | 183.2204 | 8588.5069 | 1294.4329 | 8263.1742 | 16856.8878
| 20644488 | 2030 | CME016 | 1111.2126 | 5.2067 | 183.2204 | 8588.5069 | 1294.4329 | 8263.1742 | 16856.8878
| 20644488 | 2031 | CME016 | 1111.2126 | 5.2067 | 183.2204 | 8588.5069 | 1294.4329 | 8263.1742 | 16856.8878
| 20644488 | 2032 | CME016 | 1111.2126 | 5.2067 | 183.2204 | 8588.5069 | 1294.4329 | 8263.1742 | 16856.8878
| 20644488 | 2033 | CME016 | 1111.2126 | 5.2067 | 183.2204 | 8588.5069 | 1294.4329 | 8263.1742 | 16856.8878
| 20644488 | 2034 | CME016 | 1111.2126 | 5.2067 | 183.2204 | 8588.5069 | 1294.4329 | 8263.1742 | 16856.8878
| 88138129 | 2023 | CME016 | 16604.821 | 0 | 0 | 0 | 16604.821 | 0 | 0
| 88138129 | 2024 | CME016 | 20663.6271 | 407.1505 | 0 | 0 | 20663.6271 | 0 | 407.1505
| 88138129 | 2025 | CME016 | 23219.7132 | 474.0235 | 0 | 0 | 23219.7132 | 0 | 474.0235
| 88138129 | 2026 | CME016 | 35051.668 | 383.556 | 27.9161 | 1308.5772 | 35079.5842 | 0 | 1692.1332
| 88138129 | 2027 | CME016 | 36048.7896 | 334.5117 | 453.5593 | 21260.7214 | 36502.3488 | 0 | 21595.2331
| 88138129 | 2028 | CME016 | 36048.7896 | 334.5117 | 453.5593 | 21260.7214 | 36502.3488 | 0 | 21595.2331
| 88138129 | 2029 | CME016 | 36048.7896 | 334.5117 | 453.5593 | 21260.7214 | 36502.3488 | 0 | 21595.2331
| 88138129 | 2030 | CME016 | 36048.7896 | 334.5117 | 453.5593 | 21260.7214 | 36502.3488 | 0 | 21595.2331
| 88138129 | 2031 | CME016 | 36048.7896 | 334.5117 | 453.5593 | 21260.7214 | 36502.3488 | 0 | 21595.2331
| 88138129 | 2032 | CME016 | 36048.7896 | 334.5117 | 453.5593 | 21260.7214 | 36502.3488 | 0 | 21595.2331
| 88138129 | 2033 | CME016 | 36048.7896 | 334.5117 | 453.5593 | 21260.7214 | 36502.3488 | 0 | 21595.2331
| 88138129 | 2034 | CME016 | 36048.7896 | 334.5117 | 453.5593 | 21260.7214 | 36502.3488 | 0 | 21595.2331
| 112029390 | 2023 | CME016 | 11452.1438 | 0 | 0 | 0 | 11452.1438 | 2723.1038 | 2723.1038
| 112029390 | 2024 | CME016 | 15010.4318 | 291.856 | 0 | 0 | 15010.4318 | 2723.1038 | 3014.9597
| 112029390 | 2025 | CME016 | 14568.2185 | 275.9898 | 0 | 0 | 14568.2185 | 2723.1038 | 2999.0935
| 112029390 | 2026 | CME016 | 16668.0581 | 154.496 | 0.20809 | 9.7543 | 16668.2662 | 2723.1038 | 2887.354
| 112029390 | 2027 | CME016 | 16837.0351 | 139.5563 | 2.212 | 103.6886 | 16839.2471 | 2723.1038 | 2966.3488
| 112029390 | 2028 | CME016 | 16837.0351 | 139.5563 | 2.212 | 103.6886 | 16839.2471 | 2723.1038 | 2966.3488
| 112029390 | 2029 | CME016 | 16837.0351 | 139.5563 | 2.212 | 103.6886 | 16839.2471 | 2723.1038 | 2966.3488
| 112029390 | 2030 | CME016 | 16837.0351 | 139.5563 | 2.212 | 103.6886 | 16839.2471 | 2723.1038 | 2966.3488
| 112029390 | 2031 | CME016 | 16837.0351 | 139.5563 | 2.212 | 103.6886 | 16839.2471 | 2723.1038 | 2966.3488
| 112029390 | 2032 | CME016 | 16837.0351 | 139.5563 | 2.212 | 103.6886 | 16839.2471 | 2723.1038 | 2966.3488
| 112029390 | 2033 | CME016 | 16837.0351 | 139.5563 | 2.212 | 103.6886 | 16839.2471 | 2723.1038 | 2966.3488
| 112029390 | 2034 | CME016 | 16837.0351 | 139.5563 | 2.212 | 103.6886 | 16839.2471 | 2723.1038 | 2966.3488
| 142932154 | 2023 | CME016 | 0 | 0 | 0.11353 | 5.3215 | 0.11353 | 5170.5301 | 5175.8517
| 142932154 | 2024 | CME016 | 0 | 0 | 0.27433 | 12.8591 | 0.27433 | 5170.5301 | 5183.3892
| 142932154 | 2025 | CME016 | 0 | 0 | 0.3887 | 18.2203 | 0.3887 | 5170.5301 | 5188.7504
| 142932154 | 2026 | CME016 | 0 | 0 | 0.50892 | 23.8558 | 0.50892 | 5170.5301 | 5194.3859
| 142932154 | 2027 | CME016 | 0 | 0 | 1.2152 | 56.9614 | 1.2152 | 5170.5301 | 5227.4915
| 142932154 | 2028 | CME016 | 0 | 0 | 1.2152 | 56.9614 | 1.2152 | 5170.5301 | 5227.4915
| 142932154 | 2029 | CME016 | 0 | 0 | 1.2152 | 56.9614 | 1.2152 | 5170.5301 | 5227.4915
| 142932154 | 2030 | CME016 | 0 | 0 | 1.2152 | 56.9614 | 1.2152 | 5170.5301 | 5227.4915
| 142932154 | 2031 | CME016 | 0 | 0 | 1.2152 | 56.9614 | 1.2152 | 5170.5301 | 5227.4915
| 142932154 | 2032 | CME016 | 0 | 0 | 1.2152 | 56.9614 | 1.2152 | 5170.5301 | 5227.4915
| 142932154 | 2033 | CME016 | 0 | 0 | 1.2152 | 56.9614 | 1.2152 | 5170.5301 | 5227.4915
| 142932154 | 2034 | CME016 | 0 | 0 | 1.2152 | 56.9614 | 1.2152 | 5170.5301 | 5227.4915
| 142932473 | 2023 | CME016 | 0 | 0 | 840.6715 | 39406.7185 | 840.6715 | 4201.4389 | 43608.1574
| 142932473 | 2024 | CME016 | 0 | 0 | 878.5155 | 41180.6688 | 878.5155 | 4201.4389 | 45382.1077
| 142932473 | 2025 | CME016 | 0 | 0 | 865.9687 | 40592.5305 | 865.9687 | 4201.4389 | 44793.9694
| 142932473 | 2026 | CME016 | 0 | 0 | 914.8066 | 42881.8223 | 914.8066 | 4201.4389 | 47083.2611
| 142932473 | 2027 | CME016 | 114.1172 | 0.21869 | 997.5967 | 46762.6313 | 1111.7139 | 4201.4389 | 50964.2889
| 142932473 | 2028 | CME016 | 114.1172 | 0.21869 | 997.5967 | 46762.6313 | 1111.7139 | 4201.4389 | 50964.2889
| 142932473 | 2029 | CME016 | 114.1172 | 0.21869 | 997.5967 | 46762.6313 | 1111.7139 | 4201.4389 | 50964.2889
| 142932473 | 2030 | CME016 | 114.1172 | 0.21869 | 997.5967 | 46762.6313 | 1111.7139 | 4201.4389 | 50964.2889
| 142932473 | 2031 | CME016 | 114.1172 | 0.21869 | 997.5967 | 46762.6313 | 1111.7139 | 4201.4389 | 50964.2889
| 142932473 | 2032 | CME016 | 114.1172 | 0.21869 | 997.5967 | 46762.6313 | 1111.7139 | 4201.4389 | 50964.2889
| 142932473 | 2033 | CME016 | 114.1172 | 0.21869 | 997.5967 | 46762.6313 | 1111.7139 | 4201.4389 | 50964.2889
| 142932473 | 2034 | CME016 | 114.1172 | 0.21869 | 997.5967 | 46762.6313 | 1111.7139 | 4201.4389 | 50964.2889
| 20316479 | 2023 | CMN003 | 2303.5587 | 0 | 0 | 0 | 2303.5587 | 3569.467 | 3569.467
| 20316479 | 2024 | CMN003 | 2841.245 | 44.1065 | 0 | 0 | 2841.245 | 3569.467 | 3613.5735
| 20316479 | 2025 | CMN003 | 4523.125 | 70.1614 | 0 | 0 | 4523.125 | 3569.467 | 3639.6284
| 20316479 | 2026 | CMN003 | 4712.1138 | 29.9857 | 0 | 0 | 4712.1138 | 3569.467 | 3599.4527
| 20316479 | 2027 | CMN003 | 4913.7568 | 30.8207 | 0 | 0 | 4913.7568 | 3569.467 | 3600.2876
| 20316479 | 2028 | CMN003 | 4619.1123 | 32.9367 | 0 | 0 | 4619.1123 | 3569.467 | 3602.4037
| 20316479 | 2029 | CMN003 | 7712.2659 | 54.0396 | 0 | 0 | 7712.2659 | 3569.467 | 3623.5066
| 20316479 | 2030 | CMN003 | 10690.9965 | 92.3545 | 0 | 0 | 10690.9965 | 3569.467 | 3661.8214
| 20316479 | 2031 | CMN003 | 10425.8505 | 123.2366 | 0 | 0 | 10425.8505 | 3569.467 | 3692.7036
| 20316479 | 2032 | CMN003 | 11570.7871 | 196.1205 | 0 | 0 | 11570.7871 | 3569.467 | 3765.5875
| 20316479 | 2033 | CMN003 | 14515.0544 | 442.4222 | 0 | 0 | 14515.0544 | 3569.467 | 4011.8892
| 20316479 | 2034 | CMN003 | 17851.4134 | 632.8949 | 0 | 0 | 17851.4134 | 3569.467 | 4202.3619
| 20632396 | 2023 | CMN003 | 0 | 0 | 0 | 0 | 0 | 1803.6668 | 1803.6668
| 20632396 | 2024 | CMN003 | 0 | 0 | 0 | 0 | 0 | 1803.6668 | 1803.6668
| 20632396 | 2025 | CMN003 | 0 | 0 | 0 | 0 | 0 | 1803.6668 | 1803.6668
| 20632396 | 2026 | CMN003 | 0 | 0 | 0 | 0 | 0 | 1803.6668 | 1803.6668
| 20632396 | 2027 | CMN003 | 0 | 0 | 0 | 0 | 0 | 1803.6668 | 1803.6668
| 20632396 | 2028 | CMN003 | 0 | 0 | 0 | 0 | 0 | 1803.6668 | 1803.6668
| 20632396 | 2029 | CMN003 | 0 | 0 | 0 | 0 | 0 | 1803.6668 | 1803.6668
| 20632396 | 2030 | CMN003 | 0 | 0 | 0 | 0 | 0 | 1803.6668 | 1803.6668
| 20632396 | 2031 | CMN003 | 0 | 0 | 0 | 0 | 0 | 1803.6668 | 1803.6668
| 20632396 | 2032 | CMN003 | 1266.3676 | 13.2472 | 0 | 0 | 1266.3676 | 1803.6668 | 1816.914
| 20632396 | 2033 | CMN003 | 3108.0153 | 76.6503 | 0 | 0 | 3108.0153 | 1803.6668 | 1880.3171
| 20632396 | 2034 | CMN003 | 3301.9437 | 100.1516 | 0 | 0 | 3301.9437 | 1803.6668 | 1903.8184
| 75645177 | 2023 | CMN003 | 1314.0339 | 0 | 0 | 0 | 1314.0339 | 1953.989 | 1953.989
| 75645177 | 2024 | CMN003 | 3095.7975 | 51.1721 | 0 | 0 | 3095.7975 | 1953.989 | 2005.161
| 75645177 | 2025 | CMN003 | 3344.923 | 46.258 | 0 | 0 | 3344.923 | 1953.989 | 2000.2469
| 75645177 | 2026 | CMN003 | 6363.5889 | 41.632 | 0 | 0 | 6363.5889 | 1953.989 | 1995.6209
| 75645177 | 2027 | CMN003 | 6952.864 | 55.5535 | 0 | 0 | 6952.864 | 1953.989 | 2009.5425
| 75645177 | 2028 | CMN003 | 8978.132 | 76.0795 | 0 | 0 | 8978.132 | 1953.989 | 2030.0684
| 75645177 | 2029 | CMN003 | 9179.0899 | 56.1725 | 0 | 0 | 9179.0899 | 1953.989 | 2010.1614
| 75645177 | 2030 | CMN003 | 16132.0145 | 119.8586 | 0 | 0 | 16132.0145 | 1953.989 | 2073.8475
| 75645177 | 2031 | CMN003 | 16637.5671 | 169.9674 | 0 | 0 | 16637.5671 | 1953.989 | 2123.9564
| 75645177 | 2032 | CMN003 | 24879.9472 | 407.234 | 0 | 0 | 24879.9472 | 1953.989 | 2361.223
| 75645177 | 2033 | CMN003 | 24772.4303 | 738.3226 | 0 | 0 | 24772.4303 | 1953.989 | 2692.3116
| 75645177 | 2034 | CMN003 | 25037.0501 | 887.6752 | 0 | 0 | 25037.0501 | 1953.989 | 2841.6641
| 128771645 | 2023 | CMN003 | 0 | 0 | 0 | 0 | 0 | 120.0934 | 120.0934
| 128771645 | 2024 | CMN003 | 0 | 0 | 0 | 0 | 0 | 120.0934 | 120.0934
| 128771645 | 2025 | CMN003 | 0 | 0 | 0 | 0 | 0 | 120.0934 | 120.0934
| 128771645 | 2026 | CMN003 | 0 | 0 | 0 | 0 | 0 | 120.0934 | 120.0934
| 128771645 | 2027 | CMN003 | 0 | 0 | 0 | 0 | 0 | 120.0934 | 120.0934
| 128771645 | 2028 | CMN003 | 0 | 0 | 0 | 0 | 0 | 120.0934 | 120.0934
| 128771645 | 2029 | CMN003 | 0 | 0 | 0 | 0 | 0 | 120.0934 | 120.0934
| 128771645 | 2030 | CMN003 | 0 | 0 | 0 | 0 | 0 | 120.0934 | 120.0934
| 128771645 | 2031 | CMN003 | 0 | 0 | 0 | 0 | 0 | 120.0934 | 120.0934
| 128771645 | 2032 | CMN003 | 0 | 0 | 0 | 0 | 0 | 120.0934 | 120.0934
| 128771645 | 2033 | CMN003 | 0 | 0 | 0 | 0 | 0 | 120.0934 | 120.0934
| 128771645 | 2034 | CMN003 | 0 | 0 | 0 | 0 | 0 | 120.0934 | 120.0934
| 20292536 | 2023 | COB011 | 0 | 0 | 0 | 0 | 0 | 37.3421 | 37.3421
| 20292536 | 2024 | COB011 | 0 | 0 | 0 | 0 | 0 | 37.3421 | 37.3421
| 20292536 | 2025 | COB011 | 0 | 0 | 0 | 0 | 0 | 37.3421 | 37.3421
| 20292536 | 2026 | COB011 | 0 | 0 | 0 | 0 | 0 | 37.3421 | 37.3421
| 20292536 | 2027 | COB011 | 0 | 0 | 0 | 0 | 0 | 37.3421 | 37.3421
| 20292536 | 2028 | COB011 | 0 | 0 | 0 | 0 | 0 | 37.3421 | 37.3421
| 20292536 | 2029 | COB011 | 0 | 0 | 0 | 0 | 0 | 37.3421 | 37.3421
| 20292536 | 2030 | COB011 | 0 | 0 | 0 | 0 | 0 | 37.3421 | 37.3421
| 20292536 | 2031 | COB011 | 0 | 0 | 0 | 0 | 0 | 37.3421 | 37.3421
| 20292536 | 2032 | COB011 | 0 | 0 | 0 | 0 | 0 | 37.3421 | 37.3421
| 20292536 | 2033 | COB011 | 0 | 0 | 0 | 0 | 0 | 37.3421 | 37.3421
| 20292536 | 2034 | COB011 | 0 | 0 | 0 | 0 | 0 | 37.3421 | 37.3421
| 20292686 | 2023 | COB011 | 0 | 0 | 0 | 0 | 0 | 150.2677 | 150.2677
| 20292686 | 2024 | COB011 | 0 | 0 | 0 | 0 | 0 | 150.2677 | 150.2677
| 20292686 | 2025 | COB011 | 0 | 0 | 0 | 0 | 0 | 150.2677 | 150.2677
| 20292686 | 2026 | COB011 | 0 | 0 | 0 | 0 | 0 | 150.2677 | 150.2677
| 20292686 | 2027 | COB011 | 0 | 0 | 0 | 0 | 0 | 150.2677 | 150.2677
| 20292686 | 2028 | COB011 | 0 | 0 | 0 | 0 | 0 | 150.2677 | 150.2677
| 20292686 | 2029 | COB011 | 0 | 0 | 0 | 0 | 0 | 150.2677 | 150.2677
| 20292686 | 2030 | COB011 | 0 | 0 | 0 | 0 | 0 | 150.2677 | 150.2677
| 20292686 | 2031 | COB011 | 0 | 0 | 0 | 0 | 0 | 150.2677 | 150.2677
| 20292686 | 2032 | COB011 | 0 | 0 | 0 | 0 | 0 | 150.2677 | 150.2677
| 20292686 | 2033 | COB011 | 0 | 0 | 0 | 0 | 0 | 150.2677 | 150.2677
| 20292686 | 2034 | COB011 | 0 | 0 | 0 | 0 | 0 | 150.2677 | 150.2677
| 20293918 | 2023 | COB011 | 1223.116 | 0 | 0 | 0 | 1223.116 | 82.7961 | 82.7961
| 20293918 | 2024 | COB011 | 2786.582 | 66.8566 | 0 | 0 | 2786.582 | 82.7961 | 149.6527
| 20293918 | 2025 | COB011 | 2382.8861 | 57.6316 | 0 | 0 | 2382.8861 | 82.7961 | 140.4277
| 20293918 | 2026 | COB011 | 2257.3708 | 35.3893 | 0 | 0 | 2257.3708 | 82.7961 | 118.1854
| 20293918 | 2027 | COB011 | 2372.084 | 35.2131 | 0 | 0 | 2372.084 | 82.7961 | 118.0092
| 20293918 | 2028 | COB011 | 2415.6283 | 41.1832 | 0 | 0 | 2415.6283 | 82.7961 | 123.9793
| 20293918 | 2029 | COB011 | 2345.6981 | 31.3588 | 0 | 0 | 2345.6981 | 82.7961 | 114.1549
| 20293918 | 2030 | COB011 | 2344.0255 | 34.2545 | 0 | 0 | 2344.0255 | 82.7961 | 117.0506
| 20293918 | 2031 | COB011 | 2376.3483 | 39.6848 | 0 | 0 | 2376.3483 | 82.7961 | 122.4809
| 20293918 | 2032 | COB011 | 2220.7894 | 52.0021 | 0 | 0 | 2220.7894 | 82.7961 | 134.7982
| 20293918 | 2033 | COB011 | 2713.1016 | 107.893 | 0 | 0 | 2713.1016 | 82.7961 | 190.6891
| 20293918 | 2034 | COB011 | 2870.3877 | 139.2853 | 0 | 0 | 2870.3877 | 82.7961 | 222.0814
| 20445270 | 2023 | COB011 | 0 | 0 | 0 | 0 | 0 | 239.0881 | 239.0881
| 20445270 | 2024 | COB011 | 0 | 0 | 0 | 0 | 0 | 239.0881 | 239.0881
| 20445270 | 2025 | COB011 | 0 | 0 | 0 | 0 | 0 | 239.0881 | 239.0881
| 20445270 | 2026 | COB011 | 0 | 0 | 0 | 0 | 0 | 239.0881 | 239.0881
| 20445270 | 2027 | COB011 | 0 | 0 | 0 | 0 | 0 | 239.0881 | 239.0881
| 20445270 | 2028 | COB011 | 0 | 0 | 0 | 0 | 0 | 239.0881 | 239.0881
| 20445270 | 2029 | COB011 | 0 | 0 | 0 | 0 | 0 | 239.0881 | 239.0881
| 20445270 | 2030 | COB011 | 0 | 0 | 0 | 0 | 0 | 239.0881 | 239.0881
| 20445270 | 2031 | COB011 | 0 | 0 | 0 | 0 | 0 | 239.0881 | 239.0881
| 20445270 | 2032 | COB011 | 0 | 0 | 0 | 0 | 0 | 239.0881 | 239.0881
| 20445270 | 2033 | COB011 | 0 | 0 | 0 | 0 | 0 | 239.0881 | 239.0881
| 20445270 | 2034 | COB011 | 0 | 0 | 0 | 0 | 0 | 239.0881 | 239.0881
| 20497251 | 2023 | COB011 | 0 | 0 | 0 | 0 | 0 | 20.5901 | 20.5901
| 20497251 | 2024 | COB011 | 0 | 0 | 0 | 0 | 0 | 20.5901 | 20.5901
| 20497251 | 2025 | COB011 | 0 | 0 | 0 | 0 | 0 | 20.5901 | 20.5901
| 20497251 | 2026 | COB011 | 0 | 0 | 0 | 0 | 0 | 20.5901 | 20.5901
| 20497251 | 2027 | COB011 | 0 | 0 | 0 | 0 | 0 | 20.5901 | 20.5901
| 20497251 | 2028 | COB011 | 0 | 0 | 0 | 0 | 0 | 20.5901 | 20.5901
| 20497251 | 2029 | COB011 | 0 | 0 | 0 | 0 | 0 | 20.5901 | 20.5901
| 20497251 | 2030 | COB011 | 0 | 0 | 0 | 0 | 0 | 20.5901 | 20.5901
| 20497251 | 2031 | COB011 | 0 | 0 | 0 | 0 | 0 | 20.5901 | 20.5901
| 20497251 | 2032 | COB011 | 0 | 0 | 0 | 0 | 0 | 20.5901 | 20.5901
| 20497251 | 2033 | COB011 | 0 | 0 | 0 | 0 | 0 | 20.5901 | 20.5901
| 20497251 | 2034 | COB011 | 0 | 0 | 0 | 0 | 0 | 20.5901 | 20.5901
| 20513731 | 2023 | COB011 | 0 | 0 | 0 | 0 | 0 | 181.9304 | 181.9304
| 20513731 | 2024 | COB011 | 0 | 0 | 0 | 0 | 0 | 181.9304 | 181.9304
| 20513731 | 2025 | COB011 | 0 | 0 | 0 | 0 | 0 | 181.9304 | 181.9304
| 20513731 | 2026 | COB011 | 0 | 0 | 0 | 0 | 0 | 181.9304 | 181.9304
| 20513731 | 2027 | COB011 | 0 | 0 | 0 | 0 | 0 | 181.9304 | 181.9304
| 20513731 | 2028 | COB011 | 0 | 0 | 0 | 0 | 0 | 181.9304 | 181.9304
| 20513731 | 2029 | COB011 | 0 | 0 | 0 | 0 | 0 | 181.9304 | 181.9304
| 20513731 | 2030 | COB011 | 0 | 0 | 0 | 0 | 0 | 181.9304 | 181.9304
| 20513731 | 2031 | COB011 | 0 | 0 | 0 | 0 | 0 | 181.9304 | 181.9304
| 20513731 | 2032 | COB011 | 0 | 0 | 0 | 0 | 0 | 181.9304 | 181.9304
| 20513731 | 2033 | COB011 | 0 | 0 | 0 | 0 | 0 | 181.9304 | 181.9304
| 20513731 | 2034 | COB011 | 0 | 0 | 0 | 0 | 0 | 181.9304 | 181.9304
| 42244921 | 2023 | COB011 | 0 | 0 | 0 | 0 | 0 | 266.9213 | 266.9213
| 42244921 | 2024 | COB011 | 0 | 0 | 0 | 0 | 0 | 266.9213 | 266.9213
| 42244921 | 2025 | COB011 | 0 | 0 | 0 | 0 | 0 | 266.9213 | 266.9213
| 42244921 | 2026 | COB011 | 0 | 0 | 0 | 0 | 0 | 266.9213 | 266.9213
| 42244921 | 2027 | COB011 | 0 | 0 | 0 | 0 | 0 | 266.9213 | 266.9213
| 42244921 | 2028 | COB011 | 0 | 0 | 0 | 0 | 0 | 266.9213 | 266.9213
| 42244921 | 2029 | COB011 | 0 | 0 | 0 | 0 | 0 | 266.9213 | 266.9213
| 42244921 | 2030 | COB011 | 0 | 0 | 0 | 0 | 0 | 266.9213 | 266.9213
| 42244921 | 2031 | COB011 | 0 | 0 | 0 | 0 | 0 | 266.9213 | 266.9213
| 42244921 | 2032 | COB011 | 0 | 0 | 0 | 0 | 0 | 266.9213 | 266.9213
| 42244921 | 2033 | COB011 | 0 | 0 | 0 | 0 | 0 | 266.9213 | 266.9213
| 42244921 | 2034 | COB011 | 0 | 0 | 0 | 0 | 0 | 266.9213 | 266.9213
| 163030146 | 2023 | COB011 | 0 | 0 | 780.746 | 40690.9961 | 780.746 | 156.4408 | 40847.4369
| 163030146 | 2024 | COB011 | 0 | 0 | 796.7509 | 41525.1439 | 796.7509 | 156.4408 | 41681.5847
| 163030146 | 2025 | COB011 | 0 | 0 | 808.9394 | 42160.3828 | 808.9394 | 156.4408 | 42316.8236
| 163030146 | 2026 | COB011 | 0 | 0 | 814.8745 | 42469.7117 | 814.8745 | 156.4408 | 42626.1525
| 163030146 | 2027 | COB011 | 0 | 0 | 823.3893 | 42913.4848 | 823.3893 | 156.4408 | 43069.9256
| 163030146 | 2028 | COB011 | 0 | 0 | 830.929 | 43306.4375 | 830.929 | 156.4408 | 43462.8783
| 163030146 | 2029 | COB011 | 0 | 0 | 867.7678 | 45226.4088 | 867.7678 | 156.4408 | 45382.8496
| 163030146 | 2030 | COB011 | 0 | 0 | 870.7737 | 45383.0696 | 870.7737 | 156.4408 | 45539.5104
| 163030146 | 2031 | COB011 | 0 | 0 | 887.9607 | 46278.8236 | 887.9607 | 156.4408 | 46435.2645
| 163030146 | 2032 | COB011 | 0 | 0 | 902.0785 | 47014.6152 | 902.0785 | 156.4408 | 47171.056
| 163030146 | 2033 | COB011 | 0 | 0 | 939.7215 | 48976.4969 | 939.7215 | 156.4408 | 49132.9377
| 163030146 | 2034 | COB011 | 0 | 0 | 934.232 | 48690.3955 | 934.232 | 156.4408 | 48846.8363
| 163520203 | 2023 | COB011 | 0 | 0 | 3.8091 | 198.5256 | 3.8091 | 401.0832 | 599.6088
| 163520203 | 2024 | COB011 | 0 | 0 | 3.8595 | 201.1502 | 3.8595 | 401.0832 | 602.2334
| 163520203 | 2025 | COB011 | 0 | 0 | 4.4255 | 230.6473 | 4.4255 | 401.0832 | 631.7305
| 163520203 | 2026 | COB011 | 0 | 0 | 4.84 | 252.2512 | 4.84 | 401.0832 | 653.3344
| 163520203 | 2027 | COB011 | 0 | 0 | 4.5875 | 239.092 | 4.5875 | 401.0832 | 640.1752
| 163520203 | 2028 | COB011 | 0 | 0 | 6.7666 | 352.6629 | 6.7666 | 401.0832 | 753.7461
| 163520203 | 2029 | COB011 | 0 | 0 | 6.4097 | 334.0621 | 6.4097 | 401.0832 | 735.1453
| 163520203 | 2030 | COB011 | 0 | 0 | 6.7584 | 352.2336 | 6.7584 | 401.0832 | 753.3168
| 163520203 | 2031 | COB011 | 0 | 0 | 7.0946 | 369.7553 | 7.0946 | 401.0832 | 770.8385
| 163520203 | 2032 | COB011 | 0 | 0 | 7.622 | 397.243 | 7.622 | 401.0832 | 798.3261
| 163520203 | 2033 | COB011 | 0 | 0 | 13.2389 | 689.9861 | 13.2389 | 401.0832 | 1091.0693
| 163520203 | 2034 | COB011 | 0 | 0 | 11.8749 | 618.8989 | 11.8749 | 401.0832 | 1019.9821
| 177012578 | 2023 | COB011 | 0 | 0 | 0 | 0 | 0 | 414.834 | 414.834
| 177012578 | 2024 | COB011 | 0 | 0 | 0 | 0 | 0 | 414.834 | 414.834
| 177012578 | 2025 | COB011 | 0 | 0 | 0 | 0 | 0 | 414.834 | 414.834
| 177012578 | 2026 | COB011 | 0 | 0 | 0 | 0 | 0 | 414.834 | 414.834
| 177012578 | 2027 | COB011 | 0 | 0 | 0 | 0 | 0 | 414.834 | 414.834
| 177012578 | 2028 | COB011 | 0 | 0 | 0 | 0 | 0 | 414.834 | 414.834
| 177012578 | 2029 | COB011 | 0 | 0 | 0 | 0 | 0 | 414.834 | 414.834
| 177012578 | 2030 | COB011 | 0 | 0 | 0 | 0 | 0 | 414.834 | 414.834
| 177012578 | 2031 | COB011 | 0 | 0 | 0 | 0 | 0 | 414.834 | 414.834
| 177012578 | 2032 | COB011 | 0 | 0 | 0 | 0 | 0 | 414.834 | 414.834
| 177012578 | 2033 | COB011 | 0 | 0 | 0 | 0 | 0 | 414.834 | 414.834
| 177012578 | 2034 | COB011 | 0 | 0 | 0 | 0 | 0 | 414.834 | 414.834
| 19985788 | 2023 | CTN001 | 0 | 0 | 0 | 0 | 0 | 20318.7775 | 20318.7775
| 19985788 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 20318.7775 | 20318.7775
| 19985788 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 20318.7775 | 20318.7775
| 19985788 | 2026 | CTN001 | 0 | 0 | 91.6074 | 4140.5291 | 91.6074 | 20318.7775 | 24459.3067
| 19985788 | 2027 | CTN001 | 0 | 0 | 91.6074 | 4140.5291 | 91.6074 | 20318.7775 | 24459.3067
| 19985788 | 2028 | CTN001 | 0 | 0 | 91.6074 | 4140.5291 | 91.6074 | 20318.7775 | 24459.3067
| 19985788 | 2029 | CTN001 | 0 | 0 | 91.6074 | 4140.5291 | 91.6074 | 20318.7775 | 24459.3067
| 19985788 | 2030 | CTN001 | 0 | 0 | 91.6074 | 4140.5291 | 91.6074 | 20318.7775 | 24459.3067
| 19985788 | 2031 | CTN001 | 0 | 0 | 91.6074 | 4140.5291 | 91.6074 | 20318.7775 | 24459.3067
| 19985788 | 2032 | CTN001 | 0 | 0 | 91.6074 | 4140.5291 | 91.6074 | 20318.7775 | 24459.3067
| 19985788 | 2033 | CTN001 | 0 | 0 | 91.6074 | 4140.5291 | 91.6074 | 20318.7775 | 24459.3067
| 19985788 | 2034 | CTN001 | 0 | 0 | 91.6074 | 4140.5291 | 91.6074 | 20318.7775 | 24459.3067
| 19985828 | 2023 | CTN001 | 0 | 0 | 0 | 0 | 0 | 23076.7741 | 23076.7741
| 19985828 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 23076.7741 | 23076.7741
| 19985828 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 23076.7741 | 23076.7741
| 19985828 | 2026 | CTN001 | 0 | 0 | 86.5282 | 3910.959 | 86.5282 | 23076.7741 | 26987.7331
| 19985828 | 2027 | CTN001 | 0 | 0 | 86.5282 | 3910.959 | 86.5282 | 23076.7741 | 26987.7331
| 19985828 | 2028 | CTN001 | 0 | 0 | 86.5282 | 3910.959 | 86.5282 | 23076.7741 | 26987.7331
| 19985828 | 2029 | CTN001 | 0 | 0 | 86.5282 | 3910.959 | 86.5282 | 23076.7741 | 26987.7331
| 19985828 | 2030 | CTN001 | 0 | 0 | 86.5282 | 3910.959 | 86.5282 | 23076.7741 | 26987.7331
| 19985828 | 2031 | CTN001 | 0 | 0 | 86.5282 | 3910.959 | 86.5282 | 23076.7741 | 26987.7331
| 19985828 | 2032 | CTN001 | 0 | 0 | 86.5282 | 3910.959 | 86.5282 | 23076.7741 | 26987.7331
| 19985828 | 2033 | CTN001 | 0 | 0 | 86.5282 | 3910.959 | 86.5282 | 23076.7741 | 26987.7331
| 19985828 | 2034 | CTN001 | 0 | 0 | 86.5282 | 3910.959 | 86.5282 | 23076.7741 | 26987.7331
| 19987733 | 2023 | CTN001 | 0 | 0 | 0 | 0 | 0 | 15229.3526 | 15229.3526
| 19987733 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 15229.3526 | 15229.3526
| 19987733 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 15229.3526 | 15229.3526
| 19987733 | 2026 | CTN001 | 1.0146 | 0.039733 | 43.0496 | 1945.7833 | 44.0642 | 15229.3526 | 17175.1756
| 19987733 | 2027 | CTN001 | 1.0146 | 0.039733 | 43.0496 | 1945.7833 | 44.0642 | 15229.3526 | 17175.1756
| 19987733 | 2028 | CTN001 | 1.0146 | 0.039733 | 43.0496 | 1945.7833 | 44.0642 | 15229.3526 | 17175.1756
| 19987733 | 2029 | CTN001 | 1.0146 | 0.039733 | 43.0496 | 1945.7833 | 44.0642 | 15229.3526 | 17175.1756
| 19987733 | 2030 | CTN001 | 1.0146 | 0.039733 | 43.0496 | 1945.7833 | 44.0642 | 15229.3526 | 17175.1756
| 19987733 | 2031 | CTN001 | 1.0146 | 0.039733 | 43.0496 | 1945.7833 | 44.0642 | 15229.3526 | 17175.1756
| 19987733 | 2032 | CTN001 | 1.0146 | 0.039733 | 43.0496 | 1945.7833 | 44.0642 | 15229.3526 | 17175.1756
| 19987733 | 2033 | CTN001 | 1.0146 | 0.039733 | 43.0496 | 1945.7833 | 44.0642 | 15229.3526 | 17175.1756
| 19987733 | 2034 | CTN001 | 1.0146 | 0.039733 | 43.0496 | 1945.7833 | 44.0642 | 15229.3526 | 17175.1756
| 19987751 | 2023 | CTN001 | 0 | 0 | 0 | 0 | 0 | 14372.8603 | 14372.8603
| 19987751 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 14372.8603 | 14372.8603
| 19987751 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 14372.8603 | 14372.8603
| 19987751 | 2026 | CTN001 | 0 | 0 | 394.371 | 17825.0343 | 394.371 | 14372.8603 | 32197.8946
| 19987751 | 2027 | CTN001 | 0 | 0 | 394.371 | 17825.0343 | 394.371 | 14372.8603 | 32197.8946
| 19987751 | 2028 | CTN001 | 0 | 0 | 394.371 | 17825.0343 | 394.371 | 14372.8603 | 32197.8946
| 19987751 | 2029 | CTN001 | 0 | 0 | 394.371 | 17825.0343 | 394.371 | 14372.8603 | 32197.8946
| 19987751 | 2030 | CTN001 | 0 | 0 | 394.371 | 17825.0343 | 394.371 | 14372.8603 | 32197.8946
| 19987751 | 2031 | CTN001 | 0 | 0 | 394.371 | 17825.0343 | 394.371 | 14372.8603 | 32197.8946
| 19987751 | 2032 | CTN001 | 0 | 0 | 394.371 | 17825.0343 | 394.371 | 14372.8603 | 32197.8946
| 19987751 | 2033 | CTN001 | 0 | 0 | 394.371 | 17825.0343 | 394.371 | 14372.8603 | 32197.8946
| 19987751 | 2034 | CTN001 | 0 | 0 | 394.371 | 17825.0343 | 394.371 | 14372.8603 | 32197.8946
| 19988381 | 2023 | CTN001 | 0 | 0 | 0 | 0 | 0 | 7107.6704 | 7107.6704
| 19988381 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 7107.6704 | 7107.6704
| 19988381 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 7107.6704 | 7107.6704
| 19988381 | 2026 | CTN001 | 0 | 0 | 0.0093933 | 0.42456 | 0.0093933 | 7107.6704 | 7108.0949
| 19988381 | 2027 | CTN001 | 0 | 0 | 0.0093933 | 0.42456 | 0.0093933 | 7107.6704 | 7108.0949
| 19988381 | 2028 | CTN001 | 0 | 0 | 0.0093933 | 0.42456 | 0.0093933 | 7107.6704 | 7108.0949
| 19988381 | 2029 | CTN001 | 0 | 0 | 0.0093933 | 0.42456 | 0.0093933 | 7107.6704 | 7108.0949
| 19988381 | 2030 | CTN001 | 0 | 0 | 0.0093933 | 0.42456 | 0.0093933 | 7107.6704 | 7108.0949
| 19988381 | 2031 | CTN001 | 0 | 0 | 0.0093933 | 0.42456 | 0.0093933 | 7107.6704 | 7108.0949
| 19988381 | 2032 | CTN001 | 0 | 0 | 0.0093933 | 0.42456 | 0.0093933 | 7107.6704 | 7108.0949
| 19988381 | 2033 | CTN001 | 0 | 0 | 0.0093933 | 0.42456 | 0.0093933 | 7107.6704 | 7108.0949
| 19988381 | 2034 | CTN001 | 0 | 0 | 0.0093933 | 0.42456 | 0.0093933 | 7107.6704 | 7108.0949
| 19988615 | 2023 | CTN001 | 0 | 0 | 0 | 0 | 0 | 1085.8942 | 1085.8942
| 19988615 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 1085.8942 | 1085.8942
| 19988615 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 1085.8942 | 1085.8942
| 19988615 | 2026 | CTN001 | 0 | 0 | 0 | 0 | 0 | 1085.8942 | 1085.8942
| 19988615 | 2027 | CTN001 | 0 | 0 | 0 | 0 | 0 | 1085.8942 | 1085.8942
| 19988615 | 2028 | CTN001 | 0 | 0 | 0 | 0 | 0 | 1085.8942 | 1085.8942
| 19988615 | 2029 | CTN001 | 0 | 0 | 0 | 0 | 0 | 1085.8942 | 1085.8942
| 19988615 | 2030 | CTN001 | 0 | 0 | 0 | 0 | 0 | 1085.8942 | 1085.8942
| 19988615 | 2031 | CTN001 | 0 | 0 | 0 | 0 | 0 | 1085.8942 | 1085.8942
| 19988615 | 2032 | CTN001 | 0 | 0 | 0 | 0 | 0 | 1085.8942 | 1085.8942
| 19988615 | 2033 | CTN001 | 0 | 0 | 0 | 0 | 0 | 1085.8942 | 1085.8942
| 19988615 | 2034 | CTN001 | 0 | 0 | 0 | 0 | 0 | 1085.8942 | 1085.8942
| 19988805 | 2023 | CTN001 | 0 | 0 | 0 | 0 | 0 | 18020.4324 | 18020.4324
| 19988805 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 18020.4324 | 18020.4324
| 19988805 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 18020.4324 | 18020.4324
| 19988805 | 2026 | CTN001 | 0 | 0 | 0 | 0 | 0 | 18020.4324 | 18020.4324
| 19988805 | 2027 | CTN001 | 0 | 0 | 0 | 0 | 0 | 18020.4324 | 18020.4324
| 19988805 | 2028 | CTN001 | 0 | 0 | 0 | 0 | 0 | 18020.4324 | 18020.4324
| 19988805 | 2029 | CTN001 | 0 | 0 | 0 | 0 | 0 | 18020.4324 | 18020.4324
| 19988805 | 2030 | CTN001 | 0 | 0 | 0 | 0 | 0 | 18020.4324 | 18020.4324
| 19988805 | 2031 | CTN001 | 0 | 0 | 0 | 0 | 0 | 18020.4324 | 18020.4324
| 19988805 | 2032 | CTN001 | 0 | 0 | 0 | 0 | 0 | 18020.4324 | 18020.4324
| 19988805 | 2033 | CTN001 | 0 | 0 | 0 | 0 | 0 | 18020.4324 | 18020.4324
| 19988805 | 2034 | CTN001 | 0 | 0 | 0 | 0 | 0 | 18020.4324 | 18020.4324
| 20497088 | 2023 | CTN001 | 0 | 0 | 0 | 0 | 0 | 7728.4608 | 7728.4608
| 20497088 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 7728.4608 | 7728.4608
| 20497088 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 7728.4608 | 7728.4608
| 20497088 | 2026 | CTN001 | 0 | 0 | 0 | 0 | 0 | 7728.4608 | 7728.4608
| 20497088 | 2027 | CTN001 | 0 | 0 | 0 | 0 | 0 | 7728.4608 | 7728.4608
| 20497088 | 2028 | CTN001 | 0 | 0 | 0 | 0 | 0 | 7728.4608 | 7728.4608
| 20497088 | 2029 | CTN001 | 0 | 0 | 0 | 0 | 0 | 7728.4608 | 7728.4608
| 20497088 | 2030 | CTN001 | 0 | 0 | 0 | 0 | 0 | 7728.4608 | 7728.4608
| 20497088 | 2031 | CTN001 | 0 | 0 | 0 | 0 | 0 | 7728.4608 | 7728.4608
| 20497088 | 2032 | CTN001 | 0 | 0 | 0 | 0 | 0 | 7728.4608 | 7728.4608
| 20497088 | 2033 | CTN001 | 0 | 0 | 0 | 0 | 0 | 7728.4608 | 7728.4608
| 20497088 | 2034 | CTN001 | 0 | 0 | 0 | 0 | 0 | 7728.4608 | 7728.4608
| 20497125 | 2023 | CTN001 | 0 | 0 | 0 | 0 | 0 | 3763.7396 | 3763.7396
| 20497125 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 3763.7396 | 3763.7396
| 20497125 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 3763.7396 | 3763.7396
| 20497125 | 2026 | CTN001 | 0 | 0 | 0 | 0 | 0 | 3763.7396 | 3763.7396
| 20497125 | 2027 | CTN001 | 0 | 0 | 0 | 0 | 0 | 3763.7396 | 3763.7396
| 20497125 | 2028 | CTN001 | 0 | 0 | 0 | 0 | 0 | 3763.7396 | 3763.7396
| 20497125 | 2029 | CTN001 | 0 | 0 | 0 | 0 | 0 | 3763.7396 | 3763.7396
| 20497125 | 2030 | CTN001 | 0 | 0 | 0 | 0 | 0 | 3763.7396 | 3763.7396
| 20497125 | 2031 | CTN001 | 0 | 0 | 0 | 0 | 0 | 3763.7396 | 3763.7396
| 20497125 | 2032 | CTN001 | 0 | 0 | 0 | 0 | 0 | 3763.7396 | 3763.7396
| 20497125 | 2033 | CTN001 | 0 | 0 | 0 | 0 | 0 | 3763.7396 | 3763.7396
| 20497125 | 2034 | CTN001 | 0 | 0 | 0 | 0 | 0 | 3763.7396 | 3763.7396
| 20516538 | 2023 | CTN001 | 0 | 0 | 0.54658 | 24.7046 | 0.54658 | 6787.0101 | 6811.7147
| 20516538 | 2024 | CTN001 | 0 | 0 | 0.40873 | 18.4743 | 0.40873 | 6787.0101 | 6805.4844
| 20516538 | 2025 | CTN001 | 0 | 0 | 1.5337 | 69.3198 | 1.5337 | 6787.0101 | 6856.3299
| 20516538 | 2026 | CTN001 | 0 | 0 | 0.98285 | 44.4234 | 0.98285 | 6787.0101 | 6831.4335
| 20516538 | 2027 | CTN001 | 0 | 0 | 0.98285 | 44.4234 | 0.98285 | 6787.0101 | 6831.4335
| 20516538 | 2028 | CTN001 | 0 | 0 | 0.98285 | 44.4234 | 0.98285 | 6787.0101 | 6831.4335
| 20516538 | 2029 | CTN001 | 0 | 0 | 0.98285 | 44.4234 | 0.98285 | 6787.0101 | 6831.4335
| 20516538 | 2030 | CTN001 | 0 | 0 | 0.98285 | 44.4234 | 0.98285 | 6787.0101 | 6831.4335
| 20516538 | 2031 | CTN001 | 0 | 0 | 0.98285 | 44.4234 | 0.98285 | 6787.0101 | 6831.4335
| 20516538 | 2032 | CTN001 | 0 | 0 | 0.98285 | 44.4234 | 0.98285 | 6787.0101 | 6831.4335
| 20516538 | 2033 | CTN001 | 0 | 0 | 0.98285 | 44.4234 | 0.98285 | 6787.0101 | 6831.4335
| 20516538 | 2034 | CTN001 | 0 | 0 | 0.98285 | 44.4234 | 0.98285 | 6787.0101 | 6831.4335
| 44508139 | 2023 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2433.5799 | 2433.5799
| 44508139 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2433.5799 | 2433.5799
| 44508139 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2433.5799 | 2433.5799
| 44508139 | 2026 | CTN001 | 0 | 0 | 29.1667 | 1318.2936 | 29.1667 | 2433.5799 | 3751.8735
| 44508139 | 2027 | CTN001 | 0 | 0 | 29.1667 | 1318.2936 | 29.1667 | 2433.5799 | 3751.8735
| 44508139 | 2028 | CTN001 | 0 | 0 | 29.1667 | 1318.2936 | 29.1667 | 2433.5799 | 3751.8735
| 44508139 | 2029 | CTN001 | 0 | 0 | 29.1667 | 1318.2936 | 29.1667 | 2433.5799 | 3751.8735
| 44508139 | 2030 | CTN001 | 0 | 0 | 29.1667 | 1318.2936 | 29.1667 | 2433.5799 | 3751.8735
| 44508139 | 2031 | CTN001 | 0 | 0 | 29.1667 | 1318.2936 | 29.1667 | 2433.5799 | 3751.8735
| 44508139 | 2032 | CTN001 | 0 | 0 | 29.1667 | 1318.2936 | 29.1667 | 2433.5799 | 3751.8735
| 44508139 | 2033 | CTN001 | 0 | 0 | 29.1667 | 1318.2936 | 29.1667 | 2433.5799 | 3751.8735
| 44508139 | 2034 | CTN001 | 0 | 0 | 29.1667 | 1318.2936 | 29.1667 | 2433.5799 | 3751.8735
| 48100058 | 2023 | CTN001 | 7833.0266 | 0 | 0 | 0 | 7833.0266 | 13893.254 | 13893.254
| 48100058 | 2024 | CTN001 | 8805.2342 | 159.877 | 0 | 0 | 8805.2342 | 13893.254 | 14053.1311
| 48100058 | 2025 | CTN001 | 11065.9352 | 209.1251 | 0 | 0 | 11065.9352 | 13893.254 | 14102.3791
| 48100058 | 2026 | CTN001 | 14165.752 | 168.7945 | 0 | 0 | 14165.752 | 13893.254 | 14062.0485
| 48100058 | 2027 | CTN001 | 14165.752 | 168.7945 | 0 | 0 | 14165.752 | 13893.254 | 14062.0485
| 48100058 | 2028 | CTN001 | 14165.752 | 168.7945 | 0 | 0 | 14165.752 | 13893.254 | 14062.0485
| 48100058 | 2029 | CTN001 | 14165.752 | 168.7945 | 0 | 0 | 14165.752 | 13893.254 | 14062.0485
| 48100058 | 2030 | CTN001 | 14165.752 | 168.7945 | 0 | 0 | 14165.752 | 13893.254 | 14062.0485
| 48100058 | 2031 | CTN001 | 14165.752 | 168.7945 | 0 | 0 | 14165.752 | 13893.254 | 14062.0485
| 48100058 | 2032 | CTN001 | 14165.752 | 168.7945 | 0 | 0 | 14165.752 | 13893.254 | 14062.0485
| 48100058 | 2033 | CTN001 | 14165.752 | 168.7945 | 0 | 0 | 14165.752 | 13893.254 | 14062.0485
| 48100058 | 2034 | CTN001 | 14165.752 | 168.7945 | 0 | 0 | 14165.752 | 13893.254 | 14062.0485
| 154671789 | 2023 | CTN001 | 0 | 0 | 0 | 0 | 0 | 1938.1292 | 1938.1292
| 154671789 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 1938.1292 | 1938.1292
| 154671789 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 1938.1292 | 1938.1292
| 154671789 | 2026 | CTN001 | 0 | 0 | 3.2988 | 149.1007 | 3.2988 | 1938.1292 | 2087.2299
| 154671789 | 2027 | CTN001 | 0 | 0 | 3.2988 | 149.1007 | 3.2988 | 1938.1292 | 2087.2299
| 154671789 | 2028 | CTN001 | 0 | 0 | 3.2988 | 149.1007 | 3.2988 | 1938.1292 | 2087.2299
| 154671789 | 2029 | CTN001 | 0 | 0 | 3.2988 | 149.1007 | 3.2988 | 1938.1292 | 2087.2299
| 154671789 | 2030 | CTN001 | 0 | 0 | 3.2988 | 149.1007 | 3.2988 | 1938.1292 | 2087.2299
| 154671789 | 2031 | CTN001 | 0 | 0 | 3.2988 | 149.1007 | 3.2988 | 1938.1292 | 2087.2299
| 154671789 | 2032 | CTN001 | 0 | 0 | 3.2988 | 149.1007 | 3.2988 | 1938.1292 | 2087.2299
| 154671789 | 2033 | CTN001 | 0 | 0 | 3.2988 | 149.1007 | 3.2988 | 1938.1292 | 2087.2299
| 154671789 | 2034 | CTN001 | 0 | 0 | 3.2988 | 149.1007 | 3.2988 | 1938.1292 | 2087.2299
| 154864394 | 2023 | CTN001 | 0 | 0 | 213.2844 | 9640.1664 | 213.2844 | 10132.0594 | 19772.2258
| 154864394 | 2024 | CTN001 | 0 | 0 | 193.9184 | 8764.8484 | 193.9184 | 10132.0594 | 18896.9078
| 154864394 | 2025 | CTN001 | 0 | 0 | 200.6499 | 9069.1033 | 200.6499 | 10132.0594 | 19201.1627
| 154864394 | 2026 | CTN001 | 0 | 0 | 235.6706 | 10651.989 | 235.6706 | 10132.0594 | 20784.0484
| 154864394 | 2027 | CTN001 | 0 | 0 | 235.6706 | 10651.989 | 235.6706 | 10132.0594 | 20784.0484
| 154864394 | 2028 | CTN001 | 0 | 0 | 235.6706 | 10651.989 | 235.6706 | 10132.0594 | 20784.0484
| 154864394 | 2029 | CTN001 | 0 | 0 | 235.6706 | 10651.989 | 235.6706 | 10132.0594 | 20784.0484
| 154864394 | 2030 | CTN001 | 0 | 0 | 235.6706 | 10651.989 | 235.6706 | 10132.0594 | 20784.0484
| 154864394 | 2031 | CTN001 | 0 | 0 | 235.6706 | 10651.989 | 235.6706 | 10132.0594 | 20784.0484
| 154864394 | 2032 | CTN001 | 0 | 0 | 235.6706 | 10651.989 | 235.6706 | 10132.0594 | 20784.0484
| 154864394 | 2033 | CTN001 | 0 | 0 | 235.6706 | 10651.989 | 235.6706 | 10132.0594 | 20784.0484
| 154864394 | 2034 | CTN001 | 0 | 0 | 235.6706 | 10651.989 | 235.6706 | 10132.0594 | 20784.0484
| 163266496 | 2023 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2272.2914 | 2272.2914
| 163266496 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2272.2914 | 2272.2914
| 163266496 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2272.2914 | 2272.2914
| 163266496 | 2026 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2272.2914 | 2272.2914
| 163266496 | 2027 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2272.2914 | 2272.2914
| 163266496 | 2028 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2272.2914 | 2272.2914
| 163266496 | 2029 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2272.2914 | 2272.2914
| 163266496 | 2030 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2272.2914 | 2272.2914
| 163266496 | 2031 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2272.2914 | 2272.2914
| 163266496 | 2032 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2272.2914 | 2272.2914
| 163266496 | 2033 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2272.2914 | 2272.2914
| 163266496 | 2034 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2272.2914 | 2272.2914
| 163810606 | 2023 | CTN001 | 0 | 0 | 0 | 0 | 0 | 4662.9435 | 4662.9435
| 163810606 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 4662.9435 | 4662.9435
| 163810606 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 4662.9435 | 4662.9435
| 163810606 | 2026 | CTN001 | 0 | 0 | 0 | 0 | 0 | 4662.9435 | 4662.9435
| 163810606 | 2027 | CTN001 | 0 | 0 | 0 | 0 | 0 | 4662.9435 | 4662.9435
| 163810606 | 2028 | CTN001 | 0 | 0 | 0 | 0 | 0 | 4662.9435 | 4662.9435
| 163810606 | 2029 | CTN001 | 0 | 0 | 0 | 0 | 0 | 4662.9435 | 4662.9435
| 163810606 | 2030 | CTN001 | 0 | 0 | 0 | 0 | 0 | 4662.9435 | 4662.9435
| 163810606 | 2031 | CTN001 | 0 | 0 | 0 | 0 | 0 | 4662.9435 | 4662.9435
| 163810606 | 2032 | CTN001 | 0 | 0 | 0 | 0 | 0 | 4662.9435 | 4662.9435
| 163810606 | 2033 | CTN001 | 0 | 0 | 0 | 0 | 0 | 4662.9435 | 4662.9435
| 163810606 | 2034 | CTN001 | 0 | 0 | 0 | 0 | 0 | 4662.9435 | 4662.9435
| 176947367 | 2023 | CTN001 | 0 | 0 | 0 | 0 | 0 | 17457.3476 | 17457.3476
| 176947367 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 17457.3476 | 17457.3476
| 176947367 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 17457.3476 | 17457.3476
| 176947367 | 2026 | CTN001 | 0 | 0 | 236.8791 | 10706.6146 | 236.8791 | 17457.3476 | 28163.9623
| 176947367 | 2027 | CTN001 | 0 | 0 | 236.8791 | 10706.6146 | 236.8791 | 17457.3476 | 28163.9623
| 176947367 | 2028 | CTN001 | 0 | 0 | 236.8791 | 10706.6146 | 236.8791 | 17457.3476 | 28163.9623
| 176947367 | 2029 | CTN001 | 0 | 0 | 236.8791 | 10706.6146 | 236.8791 | 17457.3476 | 28163.9623
| 176947367 | 2030 | CTN001 | 0 | 0 | 236.8791 | 10706.6146 | 236.8791 | 17457.3476 | 28163.9623
| 176947367 | 2031 | CTN001 | 0 | 0 | 236.8791 | 10706.6146 | 236.8791 | 17457.3476 | 28163.9623
| 176947367 | 2032 | CTN001 | 0 | 0 | 236.8791 | 10706.6146 | 236.8791 | 17457.3476 | 28163.9623
| 176947367 | 2033 | CTN001 | 0 | 0 | 236.8791 | 10706.6146 | 236.8791 | 17457.3476 | 28163.9623
| 176947367 | 2034 | CTN001 | 0 | 0 | 236.8791 | 10706.6146 | 236.8791 | 17457.3476 | 28163.9623
| 181894334 | 2023 | CTN001 | 0 | 0 | 0 | 0 | 0 | 12682.0762 | 12682.0762
| 181894334 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 12682.0762 | 12682.0762
| 181894334 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 12682.0762 | 12682.0762
| 181894334 | 2026 | CTN001 | 0 | 0 | 0 | 0 | 0 | 12682.0762 | 12682.0762
| 181894334 | 2027 | CTN001 | 0 | 0 | 0 | 0 | 0 | 12682.0762 | 12682.0762
| 181894334 | 2028 | CTN001 | 0 | 0 | 0 | 0 | 0 | 12682.0762 | 12682.0762
| 181894334 | 2029 | CTN001 | 0 | 0 | 0 | 0 | 0 | 12682.0762 | 12682.0762
| 181894334 | 2030 | CTN001 | 0 | 0 | 0 | 0 | 0 | 12682.0762 | 12682.0762
| 181894334 | 2031 | CTN001 | 0 | 0 | 0 | 0 | 0 | 12682.0762 | 12682.0762
| 181894334 | 2032 | CTN001 | 0 | 0 | 0 | 0 | 0 | 12682.0762 | 12682.0762
| 181894334 | 2033 | CTN001 | 0 | 0 | 0 | 0 | 0 | 12682.0762 | 12682.0762
| 181894334 | 2034 | CTN001 | 0 | 0 | 0 | 0 | 0 | 12682.0762 | 12682.0762
| 202969717 | 2023 | CTN001 | 0.4408 | 0 | 0 | 0 | 0.4408 | 2748.9673 | 2748.9673
| 202969717 | 2024 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2748.9673 | 2748.9673
| 202969717 | 2025 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2748.9673 | 2748.9673
| 202969717 | 2026 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2748.9673 | 2748.9673
| 202969717 | 2027 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2748.9673 | 2748.9673
| 202969717 | 2028 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2748.9673 | 2748.9673
| 202969717 | 2029 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2748.9673 | 2748.9673
| 202969717 | 2030 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2748.9673 | 2748.9673
| 202969717 | 2031 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2748.9673 | 2748.9673
| 202969717 | 2032 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2748.9673 | 2748.9673
| 202969717 | 2033 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2748.9673 | 2748.9673
| 202969717 | 2034 | CTN001 | 0 | 0 | 0 | 0 | 0 | 2748.9673 | 2748.9673
| 19989164 | 2023 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2883.2969 | 2883.2969
| 19989164 | 2024 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2883.2969 | 2883.2969
| 19989164 | 2025 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2883.2969 | 2883.2969
| 19989164 | 2026 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2883.2969 | 2883.2969
| 19989164 | 2027 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2883.2969 | 2883.2969
| 19989164 | 2028 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2883.2969 | 2883.2969
| 19989164 | 2029 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2883.2969 | 2883.2969
| 19989164 | 2030 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2883.2969 | 2883.2969
| 19989164 | 2031 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2883.2969 | 2883.2969
| 19989164 | 2032 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2883.2969 | 2883.2969
| 19989164 | 2033 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2883.2969 | 2883.2969
| 19989164 | 2034 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2883.2969 | 2883.2969
| 20202176 | 2023 | CTN002 | 2354.6754 | 0 | 0 | 0 | 2354.6754 | 17905.4212 | 17905.4212
| 20202176 | 2024 | CTN002 | 2519.4578 | 52.7325 | 0 | 0 | 2519.4578 | 17905.4212 | 17958.1537
| 20202176 | 2025 | CTN002 | 2569.2326 | 59.4328 | 0 | 0 | 2569.2326 | 17905.4212 | 17964.854
| 20202176 | 2026 | CTN002 | 5609.8949 | 78.8382 | 0 | 0 | 5609.8949 | 17905.4212 | 17984.2594
| 20202176 | 2027 | CTN002 | 7140.6487 | 87.6387 | 3.1981 | 144.5518 | 7143.8469 | 17905.4212 | 18137.6117
| 20202176 | 2028 | CTN002 | 7140.6487 | 87.6387 | 3.1981 | 144.5518 | 7143.8469 | 17905.4212 | 18137.6117
| 20202176 | 2029 | CTN002 | 7140.6487 | 87.6387 | 3.1981 | 144.5518 | 7143.8469 | 17905.4212 | 18137.6117
| 20202176 | 2030 | CTN002 | 7140.6487 | 87.6387 | 3.1981 | 144.5518 | 7143.8469 | 17905.4212 | 18137.6117
| 20202176 | 2031 | CTN002 | 7140.6487 | 87.6387 | 3.1981 | 144.5518 | 7143.8469 | 17905.4212 | 18137.6117
| 20202176 | 2032 | CTN002 | 7140.6487 | 87.6387 | 3.1981 | 144.5518 | 7143.8469 | 17905.4212 | 18137.6117
| 20202176 | 2033 | CTN002 | 7140.6487 | 87.6387 | 3.1981 | 144.5518 | 7143.8469 | 17905.4212 | 18137.6117
| 20202176 | 2034 | CTN002 | 7140.6487 | 87.6387 | 3.1981 | 144.5518 | 7143.8469 | 17905.4212 | 18137.6117
| 20202271 | 2023 | CTN002 | 9141.368 | 0 | 0 | 0 | 9141.368 | 12166.6336 | 12166.6336
| 20202271 | 2024 | CTN002 | 14862.71 | 292.845 | 0 | 0 | 14862.71 | 12166.6336 | 12459.4787
| 20202271 | 2025 | CTN002 | 14931.14 | 329.8091 | 0 | 0 | 14931.14 | 12166.6336 | 12496.4427
| 20202271 | 2026 | CTN002 | 20586.4529 | 282.1303 | 0 | 0 | 20586.4529 | 12166.6336 | 12448.7639
| 20202271 | 2027 | CTN002 | 24658.2607 | 288.8736 | 0 | 0 | 24658.2607 | 12166.6336 | 12455.5073
| 20202271 | 2028 | CTN002 | 24658.2607 | 288.8736 | 0 | 0 | 24658.2607 | 12166.6336 | 12455.5073
| 20202271 | 2029 | CTN002 | 24658.2607 | 288.8736 | 0 | 0 | 24658.2607 | 12166.6336 | 12455.5073
| 20202271 | 2030 | CTN002 | 24658.2607 | 288.8736 | 0 | 0 | 24658.2607 | 12166.6336 | 12455.5073
| 20202271 | 2031 | CTN002 | 24658.2607 | 288.8736 | 0 | 0 | 24658.2607 | 12166.6336 | 12455.5073
| 20202271 | 2032 | CTN002 | 24658.2607 | 288.8736 | 0 | 0 | 24658.2607 | 12166.6336 | 12455.5073
| 20202271 | 2033 | CTN002 | 24658.2607 | 288.8736 | 0 | 0 | 24658.2607 | 12166.6336 | 12455.5073
| 20202271 | 2034 | CTN002 | 24658.2607 | 288.8736 | 0 | 0 | 24658.2607 | 12166.6336 | 12455.5073
| 20299268 | 2023 | CTN002 | 9.1483 | 0 | 0 | 0 | 9.1483 | 13629.7801 | 13629.7801
| 20299268 | 2024 | CTN002 | 10.1231 | 0.31179 | 0 | 0 | 10.1231 | 13629.7801 | 13630.0919
| 20299268 | 2025 | CTN002 | 19.5664 | 0.79086 | 0 | 0 | 19.5664 | 13629.7801 | 13630.571
| 20299268 | 2026 | CTN002 | 18.7604 | 0.42276 | 0.063509 | 2.8705 | 18.8239 | 13629.7801 | 13633.0734
| 20299268 | 2027 | CTN002 | 37.5209 | 0.20073 | 45.0639 | 2036.8254 | 82.5848 | 13629.7801 | 15666.8062
| 20299268 | 2028 | CTN002 | 37.5209 | 0.20073 | 45.0639 | 2036.8254 | 82.5848 | 13629.7801 | 15666.8062
| 20299268 | 2029 | CTN002 | 37.5209 | 0.20073 | 45.0639 | 2036.8254 | 82.5848 | 13629.7801 | 15666.8062
| 20299268 | 2030 | CTN002 | 37.5209 | 0.20073 | 45.0639 | 2036.8254 | 82.5848 | 13629.7801 | 15666.8062
| 20299268 | 2031 | CTN002 | 37.5209 | 0.20073 | 45.0639 | 2036.8254 | 82.5848 | 13629.7801 | 15666.8062
| 20299268 | 2032 | CTN002 | 37.5209 | 0.20073 | 45.0639 | 2036.8254 | 82.5848 | 13629.7801 | 15666.8062
| 20299268 | 2033 | CTN002 | 37.5209 | 0.20073 | 45.0639 | 2036.8254 | 82.5848 | 13629.7801 | 15666.8062
| 20299268 | 2034 | CTN002 | 37.5209 | 0.20073 | 45.0639 | 2036.8254 | 82.5848 | 13629.7801 | 15666.8062
| 20299770 | 2023 | CTN002 | 1.9281 | 0 | 0 | 0 | 1.9281 | 9242.8938 | 9242.8938
| 20299770 | 2024 | CTN002 | 4.1545 | 0.16083 | 0 | 0 | 4.1545 | 9242.8938 | 9243.0546
| 20299770 | 2025 | CTN002 | 2.9174 | 0.15706 | 0 | 0 | 2.9174 | 9242.8938 | 9243.0508
| 20299770 | 2026 | CTN002 | 96.1563 | 0.94247 | 0 | 0 | 96.1563 | 9242.8938 | 9243.8362
| 20299770 | 2027 | CTN002 | 1935.7121 | 26.2896 | 0 | 0 | 1935.7121 | 9242.8938 | 9269.1834
| 20299770 | 2028 | CTN002 | 1935.7121 | 26.2896 | 0 | 0 | 1935.7121 | 9242.8938 | 9269.1834
| 20299770 | 2029 | CTN002 | 1935.7121 | 26.2896 | 0 | 0 | 1935.7121 | 9242.8938 | 9269.1834
| 20299770 | 2030 | CTN002 | 1935.7121 | 26.2896 | 0 | 0 | 1935.7121 | 9242.8938 | 9269.1834
| 20299770 | 2031 | CTN002 | 1935.7121 | 26.2896 | 0 | 0 | 1935.7121 | 9242.8938 | 9269.1834
| 20299770 | 2032 | CTN002 | 1935.7121 | 26.2896 | 0 | 0 | 1935.7121 | 9242.8938 | 9269.1834
| 20299770 | 2033 | CTN002 | 1935.7121 | 26.2896 | 0 | 0 | 1935.7121 | 9242.8938 | 9269.1834
| 20299770 | 2034 | CTN002 | 1935.7121 | 26.2896 | 0 | 0 | 1935.7121 | 9242.8938 | 9269.1834
| 20302437 | 2023 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2481.5881 | 2481.5881
| 20302437 | 2024 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2481.5881 | 2481.5881
| 20302437 | 2025 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2481.5881 | 2481.5881
| 20302437 | 2026 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2481.5881 | 2481.5881
| 20302437 | 2027 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2481.5881 | 2481.5881
| 20302437 | 2028 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2481.5881 | 2481.5881
| 20302437 | 2029 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2481.5881 | 2481.5881
| 20302437 | 2030 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2481.5881 | 2481.5881
| 20302437 | 2031 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2481.5881 | 2481.5881
| 20302437 | 2032 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2481.5881 | 2481.5881
| 20302437 | 2033 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2481.5881 | 2481.5881
| 20302437 | 2034 | CTN002 | 0 | 0 | 0 | 0 | 0 | 2481.5881 | 2481.5881
| 20497143 | 2023 | CTN002 | 3305.9655 | 0 | 0 | 0 | 3305.9655 | 6475.7613 | 6475.7613
| 20497143 | 2024 | CTN002 | 3245.0763 | 80.5346 | 0 | 0 | 3245.0763 | 6475.7613 | 6556.2959
| 20497143 | 2025 | CTN002 | 3234.4541 | 87.2833 | 0 | 0 | 3234.4541 | 6475.7613 | 6563.0446
| 20497143 | 2026 | CTN002 | 2984.1721 | 49.1633 | 0 | 0 | 2984.1721 | 6475.7613 | 6524.9246
| 20497143 | 2027 | CTN002 | 6006.729 | 81.3045 | 1.1828 | 53.4629 | 6007.9118 | 6475.7613 | 6610.5287
| 20497143 | 2028 | CTN002 | 6006.729 | 81.3045 | 1.1828 | 53.4629 | 6007.9118 | 6475.7613 | 6610.5287
| 20497143 | 2029 | CTN002 | 6006.729 | 81.3045 | 1.1828 | 53.4629 | 6007.9118 | 6475.7613 | 6610.5287
| 20497143 | 2030 | CTN002 | 6006.729 | 81.3045 | 1.1828 | 53.4629 | 6007.9118 | 6475.7613 | 6610.5287
| 20497143 | 2031 | CTN002 | 6006.729 | 81.3045 | 1.1828 | 53.4629 | 6007.9118 | 6475.7613 | 6610.5287
| 20497143 | 2032 | CTN002 | 6006.729 | 81.3045 | 1.1828 | 53.4629 | 6007.9118 | 6475.7613 | 6610.5287
| 20497143 | 2033 | CTN002 | 6006.729 | 81.3045 | 1.1828 | 53.4629 | 6007.9118 | 6475.7613 | 6610.5287
| 20497143 | 2034 | CTN002 | 6006.729 | 81.3045 | 1.1828 | 53.4629 | 6007.9118 | 6475.7613 | 6610.5287
| 20552151 | 2023 | CTN002 | 0 | 0 | 0 | 0 | 0 | 18086.2565 | 18086.2565
| 20552151 | 2024 | CTN002 | 7.0037 | 0.10284 | 0 | 0 | 7.0037 | 18086.2565 | 18086.3594
| 20552151 | 2025 | CTN002 | 7.0162 | 0.069258 | 0 | 0 | 7.0162 | 18086.2565 | 18086.3258
| 20552151 | 2026 | CTN002 | 3.3497 | 0.037633 | 0 | 0 | 3.3497 | 18086.2565 | 18086.2942
| 20552151 | 2027 | CTN002 | 120.7233 | 2.3176 | 0 | 0 | 120.7233 | 18086.2565 | 18088.5741
| 20552151 | 2028 | CTN002 | 120.7233 | 2.3176 | 0 | 0 | 120.7233 | 18086.2565 | 18088.5741
| 20552151 | 2029 | CTN002 | 120.7233 | 2.3176 | 0 | 0 | 120.7233 | 18086.2565 | 18088.5741
| 20552151 | 2030 | CTN002 | 120.7233 | 2.3176 | 0 | 0 | 120.7233 | 18086.2565 | 18088.5741
| 20552151 | 2031 | CTN002 | 120.7233 | 2.3176 | 0 | 0 | 120.7233 | 18086.2565 | 18088.5741
| 20552151 | 2032 | CTN002 | 120.7233 | 2.3176 | 0 | 0 | 120.7233 | 18086.2565 | 18088.5741
| 20552151 | 2033 | CTN002 | 120.7233 | 2.3176 | 0 | 0 | 120.7233 | 18086.2565 | 18088.5741
| 20552151 | 2034 | CTN002 | 120.7233 | 2.3176 | 0 | 0 | 120.7233 | 18086.2565 | 18088.5741
| 20614861 | 2023 | CTN002 | 0 | 0 | 0 | 0 | 0 | 12516.5959 | 12516.5959
| 20614861 | 2024 | CTN002 | 0 | 0 | 0 | 0 | 0 | 12516.5959 | 12516.5959
| 20614861 | 2025 | CTN002 | 0 | 0 | 0 | 0 | 0 | 12516.5959 | 12516.5959
| 20614861 | 2026 | CTN002 | 0 | 0 | 0 | 0 | 0 | 12516.5959 | 12516.5959
| 20614861 | 2027 | CTN002 | 0 | 0 | 0 | 0 | 0 | 12516.5959 | 12516.5959
| 20614861 | 2028 | CTN002 | 0 | 0 | 0 | 0 | 0 | 12516.5959 | 12516.5959
| 20614861 | 2029 | CTN002 | 0 | 0 | 0 | 0 | 0 | 12516.5959 | 12516.5959
| 20614861 | 2030 | CTN002 | 0 | 0 | 0 | 0 | 0 | 12516.5959 | 12516.5959
| 20614861 | 2031 | CTN002 | 0 | 0 | 0 | 0 | 0 | 12516.5959 | 12516.5959
| 20614861 | 2032 | CTN002 | 0 | 0 | 0 | 0 | 0 | 12516.5959 | 12516.5959
| 20614861 | 2033 | CTN002 | 0 | 0 | 0 | 0 | 0 | 12516.5959 | 12516.5959
| 20614861 | 2034 | CTN002 | 0 | 0 | 0 | 0 | 0 | 12516.5959 | 12516.5959
| 19984534 | 2023 | CTN003 | 6.8521 | 0 | 0 | 0 | 6.8521 | 3060.4326 | 3060.4326
| 19984534 | 2024 | CTN003 | 3.2506 | 0.054044 | 0 | 0 | 3.2506 | 3060.4326 | 3060.4866
| 19984534 | 2025 | CTN003 | 4.4744 | 0.12651 | 0 | 0 | 4.4744 | 3060.4326 | 3060.5591
| 19984534 | 2026 | CTN003 | 4.4744 | 0.12651 | 0 | 0 | 4.4744 | 3060.4326 | 3060.5591
| 19984534 | 2027 | CTN003 | 4.4744 | 0.12651 | 0 | 0 | 4.4744 | 3060.4326 | 3060.5591
| 19984534 | 2028 | CTN003 | 4.4744 | 0.12651 | 0 | 0 | 4.4744 | 3060.4326 | 3060.5591
| 19984534 | 2029 | CTN003 | 4.4744 | 0.12651 | 0 | 0 | 4.4744 | 3060.4326 | 3060.5591
| 19984534 | 2030 | CTN003 | 4.4744 | 0.12651 | 0 | 0 | 4.4744 | 3060.4326 | 3060.5591
| 19984534 | 2031 | CTN003 | 4.4744 | 0.12651 | 0 | 0 | 4.4744 | 3060.4326 | 3060.5591
| 19984534 | 2032 | CTN003 | 4.4744 | 0.12651 | 0 | 0 | 4.4744 | 3060.4326 | 3060.5591
| 19984534 | 2033 | CTN003 | 4.4744 | 0.12651 | 0 | 0 | 4.4744 | 3060.4326 | 3060.5591
| 19984534 | 2034 | CTN003 | 4.4744 | 0.12651 | 0 | 0 | 4.4744 | 3060.4326 | 3060.5591
| 19985318 | 2023 | CTN003 | 0 | 0 | 0 | 0 | 0 | 3889.6114 | 3889.6114
| 19985318 | 2024 | CTN003 | 0 | 0 | 0 | 0 | 0 | 3889.6114 | 3889.6114
| 19985318 | 2025 | CTN003 | 0 | 0 | 0 | 0 | 0 | 3889.6114 | 3889.6114
| 19985318 | 2026 | CTN003 | 0 | 0 | 0 | 0 | 0 | 3889.6114 | 3889.6114
| 19985318 | 2027 | CTN003 | 0 | 0 | 0 | 0 | 0 | 3889.6114 | 3889.6114
| 19985318 | 2028 | CTN003 | 0 | 0 | 0 | 0 | 0 | 3889.6114 | 3889.6114
| 19985318 | 2029 | CTN003 | 0 | 0 | 0 | 0 | 0 | 3889.6114 | 3889.6114
| 19985318 | 2030 | CTN003 | 0 | 0 | 0 | 0 | 0 | 3889.6114 | 3889.6114
| 19985318 | 2031 | CTN003 | 0 | 0 | 0 | 0 | 0 | 3889.6114 | 3889.6114
| 19985318 | 2032 | CTN003 | 0 | 0 | 0 | 0 | 0 | 3889.6114 | 3889.6114
| 19985318 | 2033 | CTN003 | 0 | 0 | 0 | 0 | 0 | 3889.6114 | 3889.6114
| 19985318 | 2034 | CTN003 | 0 | 0 | 0 | 0 | 0 | 3889.6114 | 3889.6114
| 19986641 | 2023 | CTN003 | 30.4655 | 0 | 0 | 0 | 30.4655 | 10584.8336 | 10584.8336
| 19986641 | 2024 | CTN003 | 30.5115 | 0.86815 | 0 | 0 | 30.5115 | 10584.8336 | 10585.7017
| 19986641 | 2025 | CTN003 | 28.8419 | 0.97517 | 0 | 0 | 28.8419 | 10584.8336 | 10585.8087
| 19986641 | 2026 | CTN003 | 28.8419 | 0.97517 | 0 | 0 | 28.8419 | 10584.8336 | 10585.8087
| 19986641 | 2027 | CTN003 | 28.8419 | 0.97517 | 0 | 0 | 28.8419 | 10584.8336 | 10585.8087
| 19986641 | 2028 | CTN003 | 28.8419 | 0.97517 | 0 | 0 | 28.8419 | 10584.8336 | 10585.8087
| 19986641 | 2029 | CTN003 | 28.8419 | 0.97517 | 0 | 0 | 28.8419 | 10584.8336 | 10585.8087
| 19986641 | 2030 | CTN003 | 28.8419 | 0.97517 | 0 | 0 | 28.8419 | 10584.8336 | 10585.8087
| 19986641 | 2031 | CTN003 | 28.8419 | 0.97517 | 0 | 0 | 28.8419 | 10584.8336 | 10585.8087
| 19986641 | 2032 | CTN003 | 28.8419 | 0.97517 | 0 | 0 | 28.8419 | 10584.8336 | 10585.8087
| 19986641 | 2033 | CTN003 | 28.8419 | 0.97517 | 0 | 0 | 28.8419 | 10584.8336 | 10585.8087
| 19986641 | 2034 | CTN003 | 28.8419 | 0.97517 | 0 | 0 | 28.8419 | 10584.8336 | 10585.8087
| 19986956 | 2023 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14667.9258 | 14667.9258
| 19986956 | 2024 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14667.9258 | 14667.9258
| 19986956 | 2025 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14667.9258 | 14667.9258
| 19986956 | 2026 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14667.9258 | 14667.9258
| 19986956 | 2027 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14667.9258 | 14667.9258
| 19986956 | 2028 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14667.9258 | 14667.9258
| 19986956 | 2029 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14667.9258 | 14667.9258
| 19986956 | 2030 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14667.9258 | 14667.9258
| 19986956 | 2031 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14667.9258 | 14667.9258
| 19986956 | 2032 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14667.9258 | 14667.9258
| 19986956 | 2033 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14667.9258 | 14667.9258
| 19986956 | 2034 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14667.9258 | 14667.9258
| 20011475 | 2023 | CTN003 | 2.486 | 0 | 0 | 0 | 2.486 | 5272.7719 | 5272.7719
| 20011475 | 2024 | CTN003 | 2.6306 | 0.10508 | 0 | 0 | 2.6306 | 5272.7719 | 5272.877
| 20011475 | 2025 | CTN003 | 2.1835 | 0.082044 | 0 | 0 | 2.1835 | 5272.7719 | 5272.854
| 20011475 | 2026 | CTN003 | 2.1835 | 0.082044 | 0 | 0 | 2.1835 | 5272.7719 | 5272.854
| 20011475 | 2027 | CTN003 | 2.1835 | 0.082044 | 0 | 0 | 2.1835 | 5272.7719 | 5272.854
| 20011475 | 2028 | CTN003 | 2.1835 | 0.082044 | 0 | 0 | 2.1835 | 5272.7719 | 5272.854
| 20011475 | 2029 | CTN003 | 2.1835 | 0.082044 | 0 | 0 | 2.1835 | 5272.7719 | 5272.854
| 20011475 | 2030 | CTN003 | 2.1835 | 0.082044 | 0 | 0 | 2.1835 | 5272.7719 | 5272.854
| 20011475 | 2031 | CTN003 | 2.1835 | 0.082044 | 0 | 0 | 2.1835 | 5272.7719 | 5272.854
| 20011475 | 2032 | CTN003 | 2.1835 | 0.082044 | 0 | 0 | 2.1835 | 5272.7719 | 5272.854
| 20011475 | 2033 | CTN003 | 2.1835 | 0.082044 | 0 | 0 | 2.1835 | 5272.7719 | 5272.854
| 20011475 | 2034 | CTN003 | 2.1835 | 0.082044 | 0 | 0 | 2.1835 | 5272.7719 | 5272.854
| 20011614 | 2023 | CTN003 | 3.975 | 0 | 0 | 0 | 3.975 | 15702.2166 | 15702.2166
| 20011614 | 2024 | CTN003 | 5.3262 | 0.13688 | 0 | 0 | 5.3262 | 15702.2166 | 15702.3535
| 20011614 | 2025 | CTN003 | 4.1123 | 0.16058 | 0 | 0 | 4.1123 | 15702.2166 | 15702.3772
| 20011614 | 2026 | CTN003 | 4.1123 | 0.16058 | 0 | 0 | 4.1123 | 15702.2166 | 15702.3772
| 20011614 | 2027 | CTN003 | 4.1123 | 0.16058 | 0 | 0 | 4.1123 | 15702.2166 | 15702.3772
| 20011614 | 2028 | CTN003 | 4.1123 | 0.16058 | 0 | 0 | 4.1123 | 15702.2166 | 15702.3772
| 20011614 | 2029 | CTN003 | 4.1123 | 0.16058 | 0 | 0 | 4.1123 | 15702.2166 | 15702.3772
| 20011614 | 2030 | CTN003 | 4.1123 | 0.16058 | 0 | 0 | 4.1123 | 15702.2166 | 15702.3772
| 20011614 | 2031 | CTN003 | 4.1123 | 0.16058 | 0 | 0 | 4.1123 | 15702.2166 | 15702.3772
| 20011614 | 2032 | CTN003 | 4.1123 | 0.16058 | 0 | 0 | 4.1123 | 15702.2166 | 15702.3772
| 20011614 | 2033 | CTN003 | 4.1123 | 0.16058 | 0 | 0 | 4.1123 | 15702.2166 | 15702.3772
| 20011614 | 2034 | CTN003 | 4.1123 | 0.16058 | 0 | 0 | 4.1123 | 15702.2166 | 15702.3772
| 20011643 | 2023 | CTN003 | 0 | 0 | 0 | 0 | 0 | 7954.8007 | 7954.8007
| 20011643 | 2024 | CTN003 | 0 | 0 | 0 | 0 | 0 | 7954.8007 | 7954.8007
| 20011643 | 2025 | CTN003 | 0 | 0 | 0 | 0 | 0 | 7954.8007 | 7954.8007
| 20011643 | 2026 | CTN003 | 0 | 0 | 0 | 0 | 0 | 7954.8007 | 7954.8007
| 20011643 | 2027 | CTN003 | 0 | 0 | 0 | 0 | 0 | 7954.8007 | 7954.8007
| 20011643 | 2028 | CTN003 | 0 | 0 | 0 | 0 | 0 | 7954.8007 | 7954.8007
| 20011643 | 2029 | CTN003 | 0 | 0 | 0 | 0 | 0 | 7954.8007 | 7954.8007
| 20011643 | 2030 | CTN003 | 0 | 0 | 0 | 0 | 0 | 7954.8007 | 7954.8007
| 20011643 | 2031 | CTN003 | 0 | 0 | 0 | 0 | 0 | 7954.8007 | 7954.8007
| 20011643 | 2032 | CTN003 | 0 | 0 | 0 | 0 | 0 | 7954.8007 | 7954.8007
| 20011643 | 2033 | CTN003 | 0 | 0 | 0 | 0 | 0 | 7954.8007 | 7954.8007
| 20011643 | 2034 | CTN003 | 0 | 0 | 0 | 0 | 0 | 7954.8007 | 7954.8007
| 20017143 | 2023 | CTN003 | 0 | 0 | 0 | 0 | 0 | 15696.8997 | 15696.8997
| 20017143 | 2024 | CTN003 | 0 | 0 | 0 | 0 | 0 | 15696.8997 | 15696.8997
| 20017143 | 2025 | CTN003 | 0 | 0 | 0 | 0 | 0 | 15696.8997 | 15696.8997
| 20017143 | 2026 | CTN003 | 0 | 0 | 0 | 0 | 0 | 15696.8997 | 15696.8997
| 20017143 | 2027 | CTN003 | 0 | 0 | 0 | 0 | 0 | 15696.8997 | 15696.8997
| 20017143 | 2028 | CTN003 | 0 | 0 | 0 | 0 | 0 | 15696.8997 | 15696.8997
| 20017143 | 2029 | CTN003 | 0 | 0 | 0 | 0 | 0 | 15696.8997 | 15696.8997
| 20017143 | 2030 | CTN003 | 0 | 0 | 0 | 0 | 0 | 15696.8997 | 15696.8997
| 20017143 | 2031 | CTN003 | 0 | 0 | 0 | 0 | 0 | 15696.8997 | 15696.8997
| 20017143 | 2032 | CTN003 | 0 | 0 | 0 | 0 | 0 | 15696.8997 | 15696.8997
| 20017143 | 2033 | CTN003 | 0 | 0 | 0 | 0 | 0 | 15696.8997 | 15696.8997
| 20017143 | 2034 | CTN003 | 0 | 0 | 0 | 0 | 0 | 15696.8997 | 15696.8997
| 20018539 | 2023 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1424.4174 | 1424.4174
| 20018539 | 2024 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1424.4174 | 1424.4174
| 20018539 | 2025 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1424.4174 | 1424.4174
| 20018539 | 2026 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1424.4174 | 1424.4174
| 20018539 | 2027 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1424.4174 | 1424.4174
| 20018539 | 2028 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1424.4174 | 1424.4174
| 20018539 | 2029 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1424.4174 | 1424.4174
| 20018539 | 2030 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1424.4174 | 1424.4174
| 20018539 | 2031 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1424.4174 | 1424.4174
| 20018539 | 2032 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1424.4174 | 1424.4174
| 20018539 | 2033 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1424.4174 | 1424.4174
| 20018539 | 2034 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1424.4174 | 1424.4174
| 20020939 | 2023 | CTN003 | 10324.3411 | 0 | 0 | 0 | 10324.3411 | 3952.0683 | 3952.0683
| 20020939 | 2024 | CTN003 | 10125.2991 | 201.9081 | 0 | 0 | 10125.2991 | 3952.0683 | 4153.9764
| 20020939 | 2025 | CTN003 | 10656.2226 | 249.0109 | 0 | 0 | 10656.2226 | 3952.0683 | 4201.0792
| 20020939 | 2026 | CTN003 | 10656.2226 | 249.0109 | 0 | 0 | 10656.2226 | 3952.0683 | 4201.0792
| 20020939 | 2027 | CTN003 | 10656.2226 | 249.0109 | 0 | 0 | 10656.2226 | 3952.0683 | 4201.0792
| 20020939 | 2028 | CTN003 | 10656.2226 | 249.0109 | 0 | 0 | 10656.2226 | 3952.0683 | 4201.0792
| 20020939 | 2029 | CTN003 | 10656.2226 | 249.0109 | 0 | 0 | 10656.2226 | 3952.0683 | 4201.0792
| 20020939 | 2030 | CTN003 | 10656.2226 | 249.0109 | 0 | 0 | 10656.2226 | 3952.0683 | 4201.0792
| 20020939 | 2031 | CTN003 | 10656.2226 | 249.0109 | 0 | 0 | 10656.2226 | 3952.0683 | 4201.0792
| 20020939 | 2032 | CTN003 | 10656.2226 | 249.0109 | 0 | 0 | 10656.2226 | 3952.0683 | 4201.0792
| 20020939 | 2033 | CTN003 | 10656.2226 | 249.0109 | 0 | 0 | 10656.2226 | 3952.0683 | 4201.0792
| 20020939 | 2034 | CTN003 | 10656.2226 | 249.0109 | 0 | 0 | 10656.2226 | 3952.0683 | 4201.0792
| 20021045 | 2023 | CTN003 | 0 | 0 | 0 | 0 | 0 | 18442.9806 | 18442.9806
| 20021045 | 2024 | CTN003 | 0 | 0 | 0 | 0 | 0 | 18442.9806 | 18442.9806
| 20021045 | 2025 | CTN003 | 0 | 0 | 0 | 0 | 0 | 18442.9806 | 18442.9806
| 20021045 | 2026 | CTN003 | 0 | 0 | 0 | 0 | 0 | 18442.9806 | 18442.9806
| 20021045 | 2027 | CTN003 | 0 | 0 | 0 | 0 | 0 | 18442.9806 | 18442.9806
| 20021045 | 2028 | CTN003 | 0 | 0 | 0 | 0 | 0 | 18442.9806 | 18442.9806
| 20021045 | 2029 | CTN003 | 0 | 0 | 0 | 0 | 0 | 18442.9806 | 18442.9806
| 20021045 | 2030 | CTN003 | 0 | 0 | 0 | 0 | 0 | 18442.9806 | 18442.9806
| 20021045 | 2031 | CTN003 | 0 | 0 | 0 | 0 | 0 | 18442.9806 | 18442.9806
| 20021045 | 2032 | CTN003 | 0 | 0 | 0 | 0 | 0 | 18442.9806 | 18442.9806
| 20021045 | 2033 | CTN003 | 0 | 0 | 0 | 0 | 0 | 18442.9806 | 18442.9806
| 20021045 | 2034 | CTN003 | 0 | 0 | 0 | 0 | 0 | 18442.9806 | 18442.9806
| 20496004 | 2023 | CTN003 | 0 | 0 | 0 | 0 | 0 | 11359.0718 | 11359.0718
| 20496004 | 2024 | CTN003 | 0 | 0 | 0 | 0 | 0 | 11359.0718 | 11359.0718
| 20496004 | 2025 | CTN003 | 0 | 0 | 0 | 0 | 0 | 11359.0718 | 11359.0718
| 20496004 | 2026 | CTN003 | 0 | 0 | 0 | 0 | 0 | 11359.0718 | 11359.0718
| 20496004 | 2027 | CTN003 | 0 | 0 | 0 | 0 | 0 | 11359.0718 | 11359.0718
| 20496004 | 2028 | CTN003 | 0 | 0 | 0 | 0 | 0 | 11359.0718 | 11359.0718
| 20496004 | 2029 | CTN003 | 0 | 0 | 0 | 0 | 0 | 11359.0718 | 11359.0718
| 20496004 | 2030 | CTN003 | 0 | 0 | 0 | 0 | 0 | 11359.0718 | 11359.0718
| 20496004 | 2031 | CTN003 | 0 | 0 | 0 | 0 | 0 | 11359.0718 | 11359.0718
| 20496004 | 2032 | CTN003 | 0 | 0 | 0 | 0 | 0 | 11359.0718 | 11359.0718
| 20496004 | 2033 | CTN003 | 0 | 0 | 0 | 0 | 0 | 11359.0718 | 11359.0718
| 20496004 | 2034 | CTN003 | 0 | 0 | 0 | 0 | 0 | 11359.0718 | 11359.0718
| 20516500 | 2023 | CTN003 | 0 | 0 | 0 | 0 | 0 | 9396.3253 | 9396.3253
| 20516500 | 2024 | CTN003 | 0 | 0 | 0 | 0 | 0 | 9396.3253 | 9396.3253
| 20516500 | 2025 | CTN003 | 0 | 0 | 0 | 0 | 0 | 9396.3253 | 9396.3253
| 20516500 | 2026 | CTN003 | 0 | 0 | 0 | 0 | 0 | 9396.3253 | 9396.3253
| 20516500 | 2027 | CTN003 | 0 | 0 | 0 | 0 | 0 | 9396.3253 | 9396.3253
| 20516500 | 2028 | CTN003 | 0 | 0 | 0 | 0 | 0 | 9396.3253 | 9396.3253
| 20516500 | 2029 | CTN003 | 0 | 0 | 0 | 0 | 0 | 9396.3253 | 9396.3253
| 20516500 | 2030 | CTN003 | 0 | 0 | 0 | 0 | 0 | 9396.3253 | 9396.3253
| 20516500 | 2031 | CTN003 | 0 | 0 | 0 | 0 | 0 | 9396.3253 | 9396.3253
| 20516500 | 2032 | CTN003 | 0 | 0 | 0 | 0 | 0 | 9396.3253 | 9396.3253
| 20516500 | 2033 | CTN003 | 0 | 0 | 0 | 0 | 0 | 9396.3253 | 9396.3253
| 20516500 | 2034 | CTN003 | 0 | 0 | 0 | 0 | 0 | 9396.3253 | 9396.3253
| 20516519 | 2023 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2535.9476 | 2535.9476
| 20516519 | 2024 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2535.9476 | 2535.9476
| 20516519 | 2025 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2535.9476 | 2535.9476
| 20516519 | 2026 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2535.9476 | 2535.9476
| 20516519 | 2027 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2535.9476 | 2535.9476
| 20516519 | 2028 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2535.9476 | 2535.9476
| 20516519 | 2029 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2535.9476 | 2535.9476
| 20516519 | 2030 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2535.9476 | 2535.9476
| 20516519 | 2031 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2535.9476 | 2535.9476
| 20516519 | 2032 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2535.9476 | 2535.9476
| 20516519 | 2033 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2535.9476 | 2535.9476
| 20516519 | 2034 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2535.9476 | 2535.9476
| 20586509 | 2023 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14717.2285 | 14717.2285
| 20586509 | 2024 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14717.2285 | 14717.2285
| 20586509 | 2025 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14717.2285 | 14717.2285
| 20586509 | 2026 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14717.2285 | 14717.2285
| 20586509 | 2027 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14717.2285 | 14717.2285
| 20586509 | 2028 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14717.2285 | 14717.2285
| 20586509 | 2029 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14717.2285 | 14717.2285
| 20586509 | 2030 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14717.2285 | 14717.2285
| 20586509 | 2031 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14717.2285 | 14717.2285
| 20586509 | 2032 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14717.2285 | 14717.2285
| 20586509 | 2033 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14717.2285 | 14717.2285
| 20586509 | 2034 | CTN003 | 0 | 0 | 0 | 0 | 0 | 14717.2285 | 14717.2285
| 20589644 | 2023 | CTN003 | 0 | 0 | 0 | 0 | 0 | 13035.661 | 13035.661
| 20589644 | 2024 | CTN003 | 0 | 0 | 0 | 0 | 0 | 13035.661 | 13035.661
| 20589644 | 2025 | CTN003 | 1.5236 | 0.028193 | 0 | 0 | 1.5236 | 13035.661 | 13035.6892
| 20589644 | 2026 | CTN003 | 1.5236 | 0.028193 | 0 | 0 | 1.5236 | 13035.661 | 13035.6892
| 20589644 | 2027 | CTN003 | 1.5236 | 0.028193 | 0 | 0 | 1.5236 | 13035.661 | 13035.6892
| 20589644 | 2028 | CTN003 | 1.5236 | 0.028193 | 0 | 0 | 1.5236 | 13035.661 | 13035.6892
| 20589644 | 2029 | CTN003 | 1.5236 | 0.028193 | 0 | 0 | 1.5236 | 13035.661 | 13035.6892
| 20589644 | 2030 | CTN003 | 1.5236 | 0.028193 | 0 | 0 | 1.5236 | 13035.661 | 13035.6892
| 20589644 | 2031 | CTN003 | 1.5236 | 0.028193 | 0 | 0 | 1.5236 | 13035.661 | 13035.6892
| 20589644 | 2032 | CTN003 | 1.5236 | 0.028193 | 0 | 0 | 1.5236 | 13035.661 | 13035.6892
| 20589644 | 2033 | CTN003 | 1.5236 | 0.028193 | 0 | 0 | 1.5236 | 13035.661 | 13035.6892
| 20589644 | 2034 | CTN003 | 1.5236 | 0.028193 | 0 | 0 | 1.5236 | 13035.661 | 13035.6892
| 40896748 | 2023 | CTN003 | 68.7817 | 0 | 0 | 0 | 68.7817 | 20834.2852 | 20834.2852
| 40896748 | 2024 | CTN003 | 78.7152 | 1.8627 | 0 | 0 | 78.7152 | 20834.2852 | 20836.1478
| 40896748 | 2025 | CTN003 | 61.6412 | 1.1948 | 0 | 0 | 61.6412 | 20834.2852 | 20835.48
| 40896748 | 2026 | CTN003 | 61.6412 | 1.1948 | 0 | 0 | 61.6412 | 20834.2852 | 20835.48
| 40896748 | 2027 | CTN003 | 61.6412 | 1.1948 | 0 | 0 | 61.6412 | 20834.2852 | 20835.48
| 40896748 | 2028 | CTN003 | 61.6412 | 1.1948 | 0 | 0 | 61.6412 | 20834.2852 | 20835.48
| 40896748 | 2029 | CTN003 | 61.6412 | 1.1948 | 0 | 0 | 61.6412 | 20834.2852 | 20835.48
| 40896748 | 2030 | CTN003 | 61.6412 | 1.1948 | 0 | 0 | 61.6412 | 20834.2852 | 20835.48
| 40896748 | 2031 | CTN003 | 61.6412 | 1.1948 | 0 | 0 | 61.6412 | 20834.2852 | 20835.48
| 40896748 | 2032 | CTN003 | 61.6412 | 1.1948 | 0 | 0 | 61.6412 | 20834.2852 | 20835.48
| 40896748 | 2033 | CTN003 | 61.6412 | 1.1948 | 0 | 0 | 61.6412 | 20834.2852 | 20835.48
| 40896748 | 2034 | CTN003 | 61.6412 | 1.1948 | 0 | 0 | 61.6412 | 20834.2852 | 20835.48
| 75521099 | 2023 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1868.9238 | 1868.9238
| 75521099 | 2024 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1868.9238 | 1868.9238
| 75521099 | 2025 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1868.9238 | 1868.9238
| 75521099 | 2026 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1868.9238 | 1868.9238
| 75521099 | 2027 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1868.9238 | 1868.9238
| 75521099 | 2028 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1868.9238 | 1868.9238
| 75521099 | 2029 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1868.9238 | 1868.9238
| 75521099 | 2030 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1868.9238 | 1868.9238
| 75521099 | 2031 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1868.9238 | 1868.9238
| 75521099 | 2032 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1868.9238 | 1868.9238
| 75521099 | 2033 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1868.9238 | 1868.9238
| 75521099 | 2034 | CTN003 | 0 | 0 | 0 | 0 | 0 | 1868.9238 | 1868.9238
| 88138666 | 2023 | CTN003 | 406.9398 | 0 | 0 | 0 | 406.9398 | 8969.342 | 8969.342
| 88138666 | 2024 | CTN003 | 488.9832 | 9.6273 | 0 | 0 | 488.9832 | 8969.342 | 8978.9692
| 88138666 | 2025 | CTN003 | 332.9141 | 5.6823 | 0 | 0 | 332.9141 | 8969.342 | 8975.0242
| 88138666 | 2026 | CTN003 | 332.9141 | 5.6823 | 0 | 0 | 332.9141 | 8969.342 | 8975.0242
| 88138666 | 2027 | CTN003 | 332.9141 | 5.6823 | 0 | 0 | 332.9141 | 8969.342 | 8975.0242
| 88138666 | 2028 | CTN003 | 332.9141 | 5.6823 | 0 | 0 | 332.9141 | 8969.342 | 8975.0242
| 88138666 | 2029 | CTN003 | 332.9141 | 5.6823 | 0 | 0 | 332.9141 | 8969.342 | 8975.0242
| 88138666 | 2030 | CTN003 | 332.9141 | 5.6823 | 0 | 0 | 332.9141 | 8969.342 | 8975.0242
| 88138666 | 2031 | CTN003 | 332.9141 | 5.6823 | 0 | 0 | 332.9141 | 8969.342 | 8975.0242
| 88138666 | 2032 | CTN003 | 332.9141 | 5.6823 | 0 | 0 | 332.9141 | 8969.342 | 8975.0242
| 88138666 | 2033 | CTN003 | 332.9141 | 5.6823 | 0 | 0 | 332.9141 | 8969.342 | 8975.0242
| 88138666 | 2034 | CTN003 | 332.9141 | 5.6823 | 0 | 0 | 332.9141 | 8969.342 | 8975.0242
| 156572639 | 2023 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2797.4824 | 2797.4824
| 156572639 | 2024 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2797.4824 | 2797.4824
| 156572639 | 2025 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2797.4824 | 2797.4824
| 156572639 | 2026 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2797.4824 | 2797.4824
| 156572639 | 2027 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2797.4824 | 2797.4824
| 156572639 | 2028 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2797.4824 | 2797.4824
| 156572639 | 2029 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2797.4824 | 2797.4824
| 156572639 | 2030 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2797.4824 | 2797.4824
| 156572639 | 2031 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2797.4824 | 2797.4824
| 156572639 | 2032 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2797.4824 | 2797.4824
| 156572639 | 2033 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2797.4824 | 2797.4824
| 156572639 | 2034 | CTN003 | 0 | 0 | 0 | 0 | 0 | 2797.4824 | 2797.4824
| 19995060 | 2023 | CTN004 | 4398.9582 | 0 | 0 | 0 | 4398.9582 | 10303.1462 | 10303.1462
| 19995060 | 2024 | CTN004 | 4454.8318 | 95.1396 | 0 | 0 | 4454.8318 | 10303.1462 | 10398.2858
| 19995060 | 2025 | CTN004 | 4454.8318 | 95.1396 | 0 | 0 | 4454.8318 | 10303.1462 | 10398.2858
| 19995060 | 2026 | CTN004 | 4454.8318 | 95.1396 | 0 | 0 | 4454.8318 | 10303.1462 | 10398.2858
| 19995060 | 2027 | CTN004 | 4454.8318 | 95.1396 | 0 | 0 | 4454.8318 | 10303.1462 | 10398.2858
| 19995060 | 2028 | CTN004 | 4454.8318 | 95.1396 | 0 | 0 | 4454.8318 | 10303.1462 | 10398.2858
| 19995060 | 2029 | CTN004 | 4454.8318 | 95.1396 | 0 | 0 | 4454.8318 | 10303.1462 | 10398.2858
| 19995060 | 2030 | CTN004 | 4454.8318 | 95.1396 | 0 | 0 | 4454.8318 | 10303.1462 | 10398.2858
| 19995060 | 2031 | CTN004 | 4454.8318 | 95.1396 | 0 | 0 | 4454.8318 | 10303.1462 | 10398.2858
| 19995060 | 2032 | CTN004 | 4454.8318 | 95.1396 | 0 | 0 | 4454.8318 | 10303.1462 | 10398.2858
| 19995060 | 2033 | CTN004 | 4454.8318 | 95.1396 | 0 | 0 | 4454.8318 | 10303.1462 | 10398.2858
| 19995060 | 2034 | CTN004 | 4454.8318 | 95.1396 | 0 | 0 | 4454.8318 | 10303.1462 | 10398.2858
| 19995958 | 2023 | CTN004 | 1291.6287 | 0 | 0 | 0 | 1291.6287 | 3219.1964 | 3219.1964
| 19995958 | 2024 | CTN004 | 1299.07 | 34.876 | 0 | 0 | 1299.07 | 3219.1964 | 3254.0725
| 19995958 | 2025 | CTN004 | 1299.07 | 34.876 | 0 | 0 | 1299.07 | 3219.1964 | 3254.0725
| 19995958 | 2026 | CTN004 | 1299.07 | 34.876 | 0 | 0 | 1299.07 | 3219.1964 | 3254.0725
| 19995958 | 2027 | CTN004 | 1299.07 | 34.876 | 0 | 0 | 1299.07 | 3219.1964 | 3254.0725
| 19995958 | 2028 | CTN004 | 1299.07 | 34.876 | 0 | 0 | 1299.07 | 3219.1964 | 3254.0725
| 19995958 | 2029 | CTN004 | 1299.07 | 34.876 | 0 | 0 | 1299.07 | 3219.1964 | 3254.0725
| 19995958 | 2030 | CTN004 | 1299.07 | 34.876 | 0 | 0 | 1299.07 | 3219.1964 | 3254.0725
| 19995958 | 2031 | CTN004 | 1299.07 | 34.876 | 0 | 0 | 1299.07 | 3219.1964 | 3254.0725
| 19995958 | 2032 | CTN004 | 1299.07 | 34.876 | 0 | 0 | 1299.07 | 3219.1964 | 3254.0725
| 19995958 | 2033 | CTN004 | 1299.07 | 34.876 | 0 | 0 | 1299.07 | 3219.1964 | 3254.0725
| 19995958 | 2034 | CTN004 | 1299.07 | 34.876 | 0 | 0 | 1299.07 | 3219.1964 | 3254.0725
| 20516961 | 2023 | CTN004 | 2726.2467 | 0 | 0 | 0 | 2726.2467 | 5373.7235 | 5373.7235
| 20516961 | 2024 | CTN004 | 2753.8577 | 53.4079 | 0 | 0 | 2753.8577 | 5373.7235 | 5427.1315
| 20516961 | 2025 | CTN004 | 2753.8577 | 53.4079 | 0 | 0 | 2753.8577 | 5373.7235 | 5427.1315
| 20516961 | 2026 | CTN004 | 2753.8577 | 53.4079 | 0 | 0 | 2753.8577 | 5373.7235 | 5427.1315
| 20516961 | 2027 | CTN004 | 2753.8577 | 53.4079 | 0 | 0 | 2753.8577 | 5373.7235 | 5427.1315
| 20516961 | 2028 | CTN004 | 2753.8577 | 53.4079 | 0 | 0 | 2753.8577 | 5373.7235 | 5427.1315
| 20516961 | 2029 | CTN004 | 2753.8577 | 53.4079 | 0 | 0 | 2753.8577 | 5373.7235 | 5427.1315
| 20516961 | 2030 | CTN004 | 2753.8577 | 53.4079 | 0 | 0 | 2753.8577 | 5373.7235 | 5427.1315
| 20516961 | 2031 | CTN004 | 2753.8577 | 53.4079 | 0 | 0 | 2753.8577 | 5373.7235 | 5427.1315
| 20516961 | 2032 | CTN004 | 2753.8577 | 53.4079 | 0 | 0 | 2753.8577 | 5373.7235 | 5427.1315
| 20516961 | 2033 | CTN004 | 2753.8577 | 53.4079 | 0 | 0 | 2753.8577 | 5373.7235 | 5427.1315
| 20516961 | 2034 | CTN004 | 2753.8577 | 53.4079 | 0 | 0 | 2753.8577 | 5373.7235 | 5427.1315
| 20516979 | 2023 | CTN004 | 0 | 0 | 14.972 | 676.7155 | 14.972 | 12134.0213 | 12810.7368
| 20516979 | 2024 | CTN004 | 0 | 0 | 16.4333 | 742.7607 | 16.4333 | 12134.0213 | 12876.782
| 20516979 | 2025 | CTN004 | 0 | 0 | 16.4333 | 742.7607 | 16.4333 | 12134.0213 | 12876.782
| 20516979 | 2026 | CTN004 | 0 | 0 | 16.4333 | 742.7607 | 16.4333 | 12134.0213 | 12876.782
| 20516979 | 2027 | CTN004 | 0 | 0 | 16.4333 | 742.7607 | 16.4333 | 12134.0213 | 12876.782
| 20516979 | 2028 | CTN004 | 0 | 0 | 16.4333 | 742.7607 | 16.4333 | 12134.0213 | 12876.782
| 20516979 | 2029 | CTN004 | 0 | 0 | 16.4333 | 742.7607 | 16.4333 | 12134.0213 | 12876.782
| 20516979 | 2030 | CTN004 | 0 | 0 | 16.4333 | 742.7607 | 16.4333 | 12134.0213 | 12876.782
| 20516979 | 2031 | CTN004 | 0 | 0 | 16.4333 | 742.7607 | 16.4333 | 12134.0213 | 12876.782
| 20516979 | 2032 | CTN004 | 0 | 0 | 16.4333 | 742.7607 | 16.4333 | 12134.0213 | 12876.782
| 20516979 | 2033 | CTN004 | 0 | 0 | 16.4333 | 742.7607 | 16.4333 | 12134.0213 | 12876.782
| 20516979 | 2034 | CTN004 | 0 | 0 | 16.4333 | 742.7607 | 16.4333 | 12134.0213 | 12876.782
| 20585017 | 2023 | CTN004 | 173.0499 | 0 | 0 | 0 | 173.0499 | 6439.1367 | 6439.1367
| 20585017 | 2024 | CTN004 | 171.1353 | 2.9159 | 0 | 0 | 171.1353 | 6439.1367 | 6442.0526
| 20585017 | 2025 | CTN004 | 171.1353 | 2.9159 | 0 | 0 | 171.1353 | 6439.1367 | 6442.0526
| 20585017 | 2026 | CTN004 | 171.1353 | 2.9159 | 0 | 0 | 171.1353 | 6439.1367 | 6442.0526
| 20585017 | 2027 | CTN004 | 171.1353 | 2.9159 | 0 | 0 | 171.1353 | 6439.1367 | 6442.0526
| 20585017 | 2028 | CTN004 | 171.1353 | 2.9159 | 0 | 0 | 171.1353 | 6439.1367 | 6442.0526
| 20585017 | 2029 | CTN004 | 171.1353 | 2.9159 | 0 | 0 | 171.1353 | 6439.1367 | 6442.0526
| 20585017 | 2030 | CTN004 | 171.1353 | 2.9159 | 0 | 0 | 171.1353 | 6439.1367 | 6442.0526
| 20585017 | 2031 | CTN004 | 171.1353 | 2.9159 | 0 | 0 | 171.1353 | 6439.1367 | 6442.0526
| 20585017 | 2032 | CTN004 | 171.1353 | 2.9159 | 0 | 0 | 171.1353 | 6439.1367 | 6442.0526
| 20585017 | 2033 | CTN004 | 171.1353 | 2.9159 | 0 | 0 | 171.1353 | 6439.1367 | 6442.0526
| 20585017 | 2034 | CTN004 | 171.1353 | 2.9159 | 0 | 0 | 171.1353 | 6439.1367 | 6442.0526
| 19990806 | 2023 | CTN006 | 10679.3417 | 0 | 0 | 0 | 10679.3417 | 14798.0817 | 14798.0817
| 19990806 | 2024 | CTN006 | 10667.7462 | 276.523 | 0 | 0 | 10667.7462 | 14798.0817 | 15074.6047
| 19990806 | 2025 | CTN006 | 15181.9916 | 444.5538 | 0 | 0 | 15181.9916 | 14798.0817 | 15242.6355
| 19990806 | 2026 | CTN006 | 19871.9463 | 389.5985 | 0 | 0 | 19871.9463 | 14798.0817 | 15187.6802
| 19990806 | 2027 | CTN006 | 26260.6267 | 452.4434 | 0 | 0 | 26260.6267 | 14798.0817 | 15250.5251
| 19990806 | 2028 | CTN006 | 32789.995 | 592.527 | 0 | 0 | 32789.995 | 14798.0817 | 15390.6087
| 19990806 | 2029 | CTN006 | 54576.1528 | 879.1123 | 0 | 0 | 54576.1528 | 14798.0817 | 15677.194
| 19990806 | 2030 | CTN006 | 62141.1436 | 1059.5631 | 0 | 0 | 62141.1436 | 14798.0817 | 15857.6448
| 19990806 | 2031 | CTN006 | 63265.6756 | 1301.4332 | 0 | 0 | 63265.6756 | 14798.0817 | 16099.5149
| 19990806 | 2032 | CTN006 | 70969.3763 | 1948.5473 | 0 | 0 | 70969.3763 | 14798.0817 | 16746.629
| 19990806 | 2033 | CTN006 | 71566.3637 | 2946.261 | 0 | 0 | 71566.3637 | 14798.0817 | 17744.3427
| 19990806 | 2034 | CTN006 | 72358.7594 | 3465.8416 | 0 | 0 | 72358.7594 | 14798.0817 | 18263.9233
| 19992125 | 2023 | CTN006 | 8038.5786 | 0 | 0 | 0 | 8038.5786 | 2829.2127 | 2829.2127
| 19992125 | 2024 | CTN006 | 8117.8164 | 180.9128 | 0 | 0 | 8117.8164 | 2829.2127 | 3010.1255
| 19992125 | 2025 | CTN006 | 8525.4335 | 213.2119 | 0 | 0 | 8525.4335 | 2829.2127 | 3042.4246
| 19992125 | 2026 | CTN006 | 9291.5721 | 138.5151 | 0 | 0 | 9291.5721 | 2829.2127 | 2967.7278
| 19992125 | 2027 | CTN006 | 10513.3367 | 133.2655 | 0 | 0 | 10513.3367 | 2829.2127 | 2962.4781
| 19992125 | 2028 | CTN006 | 15298.4623 | 222.7022 | 0 | 0 | 15298.4623 | 2829.2127 | 3051.9149
| 19992125 | 2029 | CTN006 | 19939.2111 | 243.6887 | 0 | 0 | 19939.2111 | 2829.2127 | 3072.9014
| 19992125 | 2030 | CTN006 | 20158.4688 | 271.4248 | 0 | 0 | 20158.4688 | 2829.2127 | 3100.6374
| 19992125 | 2031 | CTN006 | 29152.1675 | 521.3275 | 0 | 0 | 29152.1675 | 2829.2127 | 3350.5401
| 19992125 | 2032 | CTN006 | 30621.0576 | 761.9215 | 0 | 0 | 30621.0576 | 2829.2127 | 3591.1342
| 19992125 | 2033 | CTN006 | 31861.8187 | 1212.2212 | 0 | 0 | 31861.8187 | 2829.2127 | 4041.4339
| 19992125 | 2034 | CTN006 | 33099.0623 | 1495.5664 | 0 | 0 | 33099.0623 | 2829.2127 | 4324.7791
| 19992601 | 2023 | CTN006 | 13799.6674 | 0 | 56.271 | 2543.3721 | 13855.9384 | 10509.5565 | 13052.9286
| 19992601 | 2024 | CTN006 | 20126.3728 | 410.2497 | 48.1313 | 2175.4673 | 20174.504 | 10509.5565 | 13095.2735
| 19992601 | 2025 | CTN006 | 23408.5786 | 465.4076 | 37.345 | 1687.9415 | 23445.9236 | 10509.5565 | 12662.9056
| 19992601 | 2026 | CTN006 | 27307.2194 | 302.5098 | 19.7054 | 890.6595 | 27326.9248 | 10509.5565 | 11702.7257
| 19992601 | 2027 | CTN006 | 40023.4589 | 456.9243 | 6.1478 | 277.8734 | 40029.6067 | 10509.5565 | 11244.3541
| 19992601 | 2028 | CTN006 | 45317.3095 | 601.0678 | 6.1895 | 279.7554 | 45323.499 | 10509.5565 | 11390.3797
| 19992601 | 2029 | CTN006 | 56179.6705 | 633.475 | 3.2565 | 147.1899 | 56182.927 | 10509.5565 | 11290.2214
| 19992601 | 2030 | CTN006 | 57680.9548 | 713.4019 | 2.9732 | 134.3851 | 57683.928 | 10509.5565 | 11357.3434
| 19992601 | 2031 | CTN006 | 64711.4105 | 1089.4557 | 0.37623 | 17.0052 | 64711.7868 | 10509.5565 | 11616.0173
| 19992601 | 2032 | CTN006 | 73308.9833 | 1801.9695 | 0.19649 | 8.881 | 73309.1798 | 10509.5565 | 12320.407
| 19992601 | 2033 | CTN006 | 80240.4183 | 2863.2287 | 0.56621 | 25.592 | 80240.9845 | 10509.5565 | 13398.3772
| 19992601 | 2034 | CTN006 | 91211.1324 | 3520.0192 | 1.7304 | 78.2125 | 91212.8628 | 10509.5565 | 14107.7882
| 19992817 | 2023 | CTN006 | 224.251 | 0 | 2.6588 | 120.1744 | 226.9098 | 7354.207 | 7474.3814
| 19992817 | 2024 | CTN006 | 377.222 | 6.995 | 2.4619 | 111.2759 | 379.684 | 7354.207 | 7472.4779
| 19992817 | 2025 | CTN006 | 562.8457 | 9.6306 | 1.4351 | 64.8643 | 564.2808 | 7354.207 | 7428.7019
| 19992817 | 2026 | CTN006 | 2425.9497 | 25.7299 | 0.16192 | 7.3186 | 2426.1116 | 7354.207 | 7387.2555
| 19992817 | 2027 | CTN006 | 6418.0767 | 74.2152 | 0 | 0 | 6418.0767 | 7354.207 | 7428.4223
| 19992817 | 2028 | CTN006 | 16344.4496 | 214.4124 | 0 | 0 | 16344.4496 | 7354.207 | 7568.6194
| 19992817 | 2029 | CTN006 | 28327.5453 | 347.4321 | 0 | 0 | 28327.5453 | 7354.207 | 7701.6391
| 19992817 | 2030 | CTN006 | 40560.8182 | 602.2809 | 0 | 0 | 40560.8182 | 7354.207 | 7956.488
| 19992817 | 2031 | CTN006 | 42702.932 | 823.815 | 0 | 0 | 42702.932 | 7354.207 | 8178.0221
| 19992817 | 2032 | CTN006 | 44025.0064 | 1160.6978 | 0 | 0 | 44025.0064 | 7354.207 | 8514.9048
| 19992817 | 2033 | CTN006 | 45313.5304 | 1696.3882 | 0 | 0 | 45313.5304 | 7354.207 | 9050.5952
| 19992817 | 2034 | CTN006 | 56085.1244 | 2445.3094 | 0 | 0 | 56085.1244 | 7354.207 | 9799.5164
| 19993099 | 2023 | CTN006 | 0 | 0 | 0 | 0 | 0 | 1476.2475 | 1476.2475
| 19993099 | 2024 | CTN006 | 157.5047 | 3.176 | 0 | 0 | 157.5047 | 1476.2475 | 1479.4234
| 19993099 | 2025 | CTN006 | 395.8526 | 6.4592 | 0 | 0 | 395.8526 | 1476.2475 | 1482.7067
| 19993099 | 2026 | CTN006 | 867.7961 | 6.7967 | 0 | 0 | 867.7961 | 1476.2475 | 1483.0442
| 19993099 | 2027 | CTN006 | 1466.2128 | 15.0426 | 0 | 0 | 1466.2128 | 1476.2475 | 1491.2901
| 19993099 | 2028 | CTN006 | 2319.1542 | 28.3335 | 0 | 0 | 2319.1542 | 1476.2475 | 1504.581
| 19993099 | 2029 | CTN006 | 2687.0405 | 25.4 | 0 | 0 | 2687.0405 | 1476.2475 | 1501.6474
| 19993099 | 2030 | CTN006 | 3077.7838 | 33.7538 | 0 | 0 | 3077.7838 | 1476.2475 | 1510.0013
| 19993099 | 2031 | CTN006 | 5442.221 | 77.8353 | 0 | 0 | 5442.221 | 1476.2475 | 1554.0828
| 19993099 | 2032 | CTN006 | 6089.4833 | 123.3547 | 0 | 0 | 6089.4833 | 1476.2475 | 1599.6022
| 19993099 | 2033 | CTN006 | 6553.3839 | 227.4372 | 0 | 0 | 6553.3839 | 1476.2475 | 1703.6846
| 19993099 | 2034 | CTN006 | 8460.9562 | 339.2609 | 0 | 0 | 8460.9562 | 1476.2475 | 1815.5084
| 19994540 | 2023 | CTN006 | 0 | 0 | 0 | 0 | 0 | 6111.6492 | 6111.6492
| 19994540 | 2024 | CTN006 | 0 | 0 | 0 | 0 | 0 | 6111.6492 | 6111.6492
| 19994540 | 2025 | CTN006 | 0 | 0 | 0 | 0 | 0 | 6111.6492 | 6111.6492
| 19994540 | 2026 | CTN006 | 0 | 0 | 0 | 0 | 0 | 6111.6492 | 6111.6492
| 19994540 | 2027 | CTN006 | 0 | 0 | 0 | 0 | 0 | 6111.6492 | 6111.6492
| 19994540 | 2028 | CTN006 | 0 | 0 | 0 | 0 | 0 | 6111.6492 | 6111.6492
| 19994540 | 2029 | CTN006 | 0 | 0 | 0 | 0 | 0 | 6111.6492 | 6111.6492
| 19994540 | 2030 | CTN006 | 0 | 0 | 0 | 0 | 0 | 6111.6492 | 6111.6492
| 19994540 | 2031 | CTN006 | 0 | 0 | 0 | 0 | 0 | 6111.6492 | 6111.6492
| 19994540 | 2032 | CTN006 | 0 | 0 | 0 | 0 | 0 | 6111.6492 | 6111.6492
| 19994540 | 2033 | CTN006 | 0 | 0 | 0 | 0 | 0 | 6111.6492 | 6111.6492
| 19994540 | 2034 | CTN006 | 0 | 0 | 0 | 0 | 0 | 6111.6492 | 6111.6492
| 20497052 | 2023 | CTN006 | 48.2484 | 0 | 0 | 0 | 48.2484 | 13122.2213 | 13122.2213
| 20497052 | 2024 | CTN006 | 158.2023 | 2.4925 | 0 | 0 | 158.2023 | 13122.2213 | 13124.7138
| 20497052 | 2025 | CTN006 | 410.6942 | 5.753 | 0 | 0 | 410.6942 | 13122.2213 | 13127.9743
| 20497052 | 2026 | CTN006 | 7045.919 | 116.787 | 0 | 0 | 7045.919 | 13122.2213 | 13239.0084
| 20497052 | 2027 | CTN006 | 11100.6366 | 208.6832 | 0 | 0 | 11100.6366 | 13122.2213 | 13330.9046
| 20497052 | 2028 | CTN006 | 20496.4929 | 341.2756 | 0 | 0 | 20496.4929 | 13122.2213 | 13463.497
| 20497052 | 2029 | CTN006 | 21574.9876 | 301.6472 | 0 | 0 | 21574.9876 | 13122.2213 | 13423.8686
| 20497052 | 2030 | CTN006 | 21012.1835 | 322.6426 | 0 | 0 | 21012.1835 | 13122.2213 | 13444.8639
| 20497052 | 2031 | CTN006 | 25900.274 | 516.618 | 0 | 0 | 25900.274 | 13122.2213 | 13638.8393
| 20497052 | 2032 | CTN006 | 26270.2439 | 687.9112 | 0 | 0 | 26270.2439 | 13122.2213 | 13810.1325
| 20497052 | 2033 | CTN006 | 26365.6631 | 1067.0913 | 0 | 0 | 26365.6631 | 13122.2213 | 14189.3126
| 20497052 | 2034 | CTN006 | 26734.206 | 1259.8811 | 0 | 0 | 26734.206 | 13122.2213 | 14382.1024
| 45816354 | 2023 | CTN006 | 619.3896 | 0 | 0 | 0 | 619.3896 | 10482.2708 | 10482.2708
| 45816354 | 2024 | CTN006 | 746.8728 | 13.5644 | 0 | 0 | 746.8728 | 10482.2708 | 10495.8353
| 45816354 | 2025 | CTN006 | 1223.8171 | 21.5949 | 0 | 0 | 1223.8171 | 10482.2708 | 10503.8658
| 45816354 | 2026 | CTN006 | 3704.3688 | 37.5251 | 0 | 0 | 3704.3688 | 10482.2708 | 10519.796
| 45816354 | 2027 | CTN006 | 8551.2961 | 108.051 | 0 | 0 | 8551.2961 | 10482.2708 | 10590.3218
| 45816354 | 2028 | CTN006 | 9010.8058 | 130.2653 | 0 | 0 | 9010.8058 | 10482.2708 | 10612.5361
| 45816354 | 2029 | CTN006 | 14016.7431 | 165.9547 | 0 | 0 | 14016.7431 | 10482.2708 | 10648.2256
| 45816354 | 2030 | CTN006 | 15363.6136 | 194.7718 | 0 | 0 | 15363.6136 | 10482.2708 | 10677.0427
| 45816354 | 2031 | CTN006 | 16400.6658 | 263.4974 | 0 | 0 | 16400.6658 | 10482.2708 | 10745.7683
| 45816354 | 2032 | CTN006 | 17517.293 | 390.3524 | 0 | 0 | 17517.293 | 10482.2708 | 10872.6233
| 45816354 | 2033 | CTN006 | 19113.8865 | 669.0362 | 0 | 0 | 19113.8865 | 10482.2708 | 11151.307
| 45816354 | 2034 | CTN006 | 19996.2102 | 820.9385 | 0 | 0 | 19996.2102 | 10482.2708 | 11303.2093
| 100524912 | 2023 | CTN006 | 1427.3447 | 0 | 129.7524 | 5864.6315 | 1557.0971 | 6356.9897 | 12221.6212
| 100524912 | 2024 | CTN006 | 1883.7349 | 30.529 | 124.1612 | 5611.9171 | 2007.8961 | 6356.9897 | 11999.4358
| 100524912 | 2025 | CTN006 | 2787.0062 | 44.1083 | 93.7663 | 4238.1103 | 2880.7725 | 6356.9897 | 10639.2083
| 100524912 | 2026 | CTN006 | 7627.8617 | 73.111 | 52.4399 | 2370.2104 | 7680.3015 | 6356.9897 | 8800.3112
| 100524912 | 2027 | CTN006 | 11926.7944 | 124.3135 | 13.7647 | 622.1467 | 11940.5591 | 6356.9897 | 7103.4499
| 100524912 | 2028 | CTN006 | 24853.1714 | 310.0316 | 9.8136 | 443.5593 | 24862.985 | 6356.9897 | 7110.5806
| 100524912 | 2029 | CTN006 | 26609.5065 | 268.8614 | 4.888 | 220.9305 | 26614.3945 | 6356.9897 | 6846.7816
| 100524912 | 2030 | CTN006 | 27510.2059 | 310.226 | 4.9617 | 224.2613 | 27515.1676 | 6356.9897 | 6891.4771
| 100524912 | 2031 | CTN006 | 29709.6723 | 450.0746 | 2.3074 | 104.2905 | 29711.9797 | 6356.9897 | 6911.3548
| 100524912 | 2032 | CTN006 | 32508.9458 | 718.1883 | 0.56695 | 25.6253 | 32509.5127 | 6356.9897 | 7100.8033
| 100524912 | 2033 | CTN006 | 33514.3338 | 1210.155 | 1.1694 | 52.855 | 33515.5031 | 6356.9897 | 7619.9997
| 100524912 | 2034 | CTN006 | 34458.0912 | 1493.1599 | 0.38178 | 17.2561 | 34458.473 | 6356.9897 | 7867.4057
| 156526872 | 2023 | CTN006 | 0 | 0 | 34.9023 | 1577.5348 | 34.9023 | 2732.076 | 4309.6108
| 156526872 | 2024 | CTN006 | 0 | 0 | 31.1826 | 1409.4092 | 31.1826 | 2732.076 | 4141.4852
| 156526872 | 2025 | CTN006 | 0 | 0 | 16.5524 | 748.1476 | 16.5524 | 2732.076 | 3480.2235
| 156526872 | 2026 | CTN006 | 0 | 0 | 7.0226 | 317.412 | 7.0226 | 2732.076 | 3049.488
| 156526872 | 2027 | CTN006 | 6.8278 | 0.01198 | 0.020434 | 0.92357 | 6.8482 | 2732.076 | 2733.0115
| 156526872 | 2028 | CTN006 | 390.0127 | 1.8327 | 0.33095 | 14.9585 | 390.3436 | 2732.076 | 2748.8672
| 156526872 | 2029 | CTN006 | 724.7619 | 2.6748 | 0.19441 | 8.7869 | 724.9563 | 2732.076 | 2743.5377
| 156526872 | 2030 | CTN006 | 1150.6219 | 6.0888 | 0.16272 | 7.3548 | 1150.7846 | 2732.076 | 2745.5196
| 156526872 | 2031 | CTN006 | 1570.4599 | 13.1927 | 0 | 0 | 1570.4599 | 2732.076 | 2745.2687
| 156526872 | 2032 | CTN006 | 2232.8282 | 31.5983 | 0.02182 | 0.98622 | 2232.8501 | 2732.076 | 2764.6605
| 156526872 | 2033 | CTN006 | 2748.5516 | 78.3974 | 0.0049705 | 0.22466 | 2748.5566 | 2732.076 | 2810.698
| 156526872 | 2034 | CTN006 | 3351.818 | 110.0546 | 0.0092795 | 0.41942 | 3351.8273 | 2732.076 | 2842.55
| 20324078 | 2023 | ECA007 | 20494.054 | 0 | 0 | 0 | 20494.054 | 6220.751 | 6220.751
| 20324078 | 2024 | ECA007 | 22658.24 | 531.1626 | 0 | 0 | 22658.24 | 6220.751 | 6751.9136
| 20324078 | 2025 | ECA007 | 34808.412 | 1015.9877 | 0 | 0 | 34808.412 | 6220.751 | 7236.7386
| 20324078 | 2026 | ECA007 | 34808.412 | 1015.9877 | 0 | 0 | 34808.412 | 6220.751 | 7236.7386
| 20324078 | 2027 | ECA007 | 34808.412 | 1015.9877 | 0 | 0 | 34808.412 | 6220.751 | 7236.7386
| 20324078 | 2028 | ECA007 | 34808.412 | 1015.9877 | 0 | 0 | 34808.412 | 6220.751 | 7236.7386
| 20324078 | 2029 | ECA007 | 34808.412 | 1015.9877 | 0 | 0 | 34808.412 | 6220.751 | 7236.7386
| 20324078 | 2030 | ECA007 | 34808.412 | 1015.9877 | 0 | 0 | 34808.412 | 6220.751 | 7236.7386
| 20324078 | 2031 | ECA007 | 34808.412 | 1015.9877 | 0 | 0 | 34808.412 | 6220.751 | 7236.7386
| 20324078 | 2032 | ECA007 | 34808.412 | 1015.9877 | 0 | 0 | 34808.412 | 6220.751 | 7236.7386
| 20324078 | 2033 | ECA007 | 34808.412 | 1015.9877 | 0 | 0 | 34808.412 | 6220.751 | 7236.7386
| 20324078 | 2034 | ECA007 | 34808.412 | 1015.9877 | 0 | 0 | 34808.412 | 6220.751 | 7236.7386
| 20364241 | 2023 | ECA007 | 0 | 0 | 0 | 0 | 0 | 7436.0117 | 7436.0117
| 20364241 | 2024 | ECA007 | 0 | 0 | 0 | 0 | 0 | 7436.0117 | 7436.0117
| 20364241 | 2025 | ECA007 | 0 | 0 | 0 | 0 | 0 | 7436.0117 | 7436.0117
| 20364241 | 2026 | ECA007 | 0 | 0 | 0 | 0 | 0 | 7436.0117 | 7436.0117
| 20364241 | 2027 | ECA007 | 0 | 0 | 0 | 0 | 0 | 7436.0117 | 7436.0117
| 20364241 | 2028 | ECA007 | 0 | 0 | 0 | 0 | 0 | 7436.0117 | 7436.0117
| 20364241 | 2029 | ECA007 | 0 | 0 | 0 | 0 | 0 | 7436.0117 | 7436.0117
| 20364241 | 2030 | ECA007 | 0 | 0 | 0 | 0 | 0 | 7436.0117 | 7436.0117
| 20364241 | 2031 | ECA007 | 5966.2257 | 150.9523 | 0 | 0 | 5966.2257 | 7436.0117 | 7586.9641
| 20364241 | 2032 | ECA007 | 6000.6761 | 199.1695 | 0 | 0 | 6000.6761 | 7436.0117 | 7635.1812
| 20364241 | 2033 | ECA007 | 5993.2043 | 286.6717 | 0 | 0 | 5993.2043 | 7436.0117 | 7722.6834
| 20364241 | 2034 | ECA007 | 6011.7002 | 328.5068 | 0 | 0 | 6011.7002 | 7436.0117 | 7764.5186
| 194566231 | 2023 | ECA007 | 0 | 0 | 0 | 0 | 0 | 1779.175 | 1779.175
| 194566231 | 2024 | ECA007 | 0 | 0 | 0 | 0 | 0 | 1779.175 | 1779.175
| 194566231 | 2025 | ECA007 | 0 | 0 | 0 | 0 | 0 | 1779.175 | 1779.175
| 194566231 | 2026 | ECA007 | 3561.6975 | 64.6202 | 0 | 0 | 3561.6975 | 1779.175 | 1843.7952
| 194566231 | 2027 | ECA007 | 3588.1999 | 66.5213 | 0 | 0 | 3588.1999 | 1779.175 | 1845.6963
| 194566231 | 2028 | ECA007 | 3580.9034 | 79.3331 | 0 | 0 | 3580.9034 | 1779.175 | 1858.5081
| 194566231 | 2029 | ECA007 | 3553.2017 | 68.2901 | 0 | 0 | 3553.2017 | 1779.175 | 1847.4651
| 194566231 | 2030 | ECA007 | 3566.403 | 76.5173 | 0 | 0 | 3566.403 | 1779.175 | 1855.6923
| 194566231 | 2031 | ECA007 | 3469.6308 | 91.3648 | 0 | 0 | 3469.6308 | 1779.175 | 1870.5398
| 194566231 | 2032 | ECA007 | 3360.091 | 120.1942 | 0 | 0 | 3360.091 | 1779.175 | 1899.3692
| 194566231 | 2033 | ECA007 | 3461.1806 | 171.8502 | 0 | 0 | 3461.1806 | 1779.175 | 1951.0252
| 194566231 | 2034 | ECA007 | 3460.3813 | 199.4789 | 0 | 0 | 3460.3813 | 1779.175 | 1978.6539
| 20312263 | 2023 | ECA012 | 16.4799 | 0 | 0 | 0 | 16.4799 | 4590.0107 | 4590.0107
| 20312263 | 2024 | ECA012 | 2.2135 | 0.022799 | 0 | 0 | 2.2135 | 4590.0107 | 4590.0335
| 20312263 | 2025 | ECA012 | 2.0474 | 0.027535 | 0 | 0 | 2.0474 | 4590.0107 | 4590.0383
| 20312263 | 2026 | ECA012 | 171.6964 | 0.55189 | 0 | 0 | 171.6964 | 4590.0107 | 4590.5626
| 20312263 | 2027 | ECA012 | 88.0304 | 0.39897 | 0 | 0 | 88.0304 | 4590.0107 | 4590.4097
| 20312263 | 2028 | ECA012 | 372.2065 | 4.161 | 0 | 0 | 372.2065 | 4590.0107 | 4594.1717
| 20312263 | 2029 | ECA012 | 581.4808 | 1.8807 | 0 | 0 | 581.4808 | 4590.0107 | 4591.8915
| 20312263 | 2030 | ECA012 | 619.0169 | 3.1236 | 0 | 0 | 619.0169 | 4590.0107 | 4593.1344
| 20312263 | 2031 | ECA012 | 603.879 | 4.5447 | 0 | 0 | 603.879 | 4590.0107 | 4594.5555
| 20312263 | 2032 | ECA012 | 3778.8869 | 62.034 | 0 | 0 | 3778.8869 | 4590.0107 | 4652.0447
| 20312263 | 2033 | ECA012 | 4551.5574 | 128.0824 | 0 | 0 | 4551.5574 | 4590.0107 | 4718.0931
| 20312263 | 2034 | ECA012 | 6379.239 | 206.3766 | 0 | 0 | 6379.239 | 4590.0107 | 4796.3874
| 20497787 | 2023 | ECA012 | 2460.4657 | 0 | 0 | 0 | 2460.4657 | 2041.2658 | 2041.2658
| 20497787 | 2024 | ECA012 | 3029.1093 | 53.9995 | 0 | 0 | 3029.1093 | 2041.2658 | 2095.2653
| 20497787 | 2025 | ECA012 | 3006.6493 | 45.6627 | 0 | 0 | 3006.6493 | 2041.2658 | 2086.9286
| 20497787 | 2026 | ECA012 | 1900.3233 | 12.0182 | 0 | 0 | 1900.3233 | 2041.2658 | 2053.284
| 20497787 | 2027 | ECA012 | 2104.3898 | 16.0741 | 0.2603 | 12.3699 | 2104.6501 | 2041.2658 | 2069.7099
| 20497787 | 2028 | ECA012 | 2266.4895 | 20.0497 | 0.50756 | 24.1207 | 2266.9971 | 2041.2658 | 2085.4362
| 20497787 | 2029 | ECA012 | 2433.159 | 13.3583 | 0.73174 | 34.7741 | 2433.8907 | 2041.2658 | 2089.3982
| 20497787 | 2030 | ECA012 | 2794.8274 | 19.376 | 0.92045 | 43.7421 | 2795.7478 | 2041.2658 | 2104.384
| 20497787 | 2031 | ECA012 | 3044.7191 | 29.0811 | 1.1169 | 53.078 | 3045.836 | 2041.2658 | 2123.4249
| 20497787 | 2032 | ECA012 | 3100.6678 | 49.3242 | 1.989 | 94.5198 | 3102.6568 | 2041.2658 | 2185.1099
| 20497787 | 2033 | ECA012 | 3079.5414 | 93.3014 | 4.1042 | 195.0401 | 3083.6456 | 2041.2658 | 2329.6073
| 20497787 | 2034 | ECA012 | 3032.3609 | 103.8004 | 16.4554 | 782.0019 | 3048.8163 | 2041.2658 | 2927.0681
| 20318572 | 2023 | EHK031 | 5510.7461 | 0 | 0 | 0 | 5510.7461 | 4761.5621 | 4761.5621
| 20318572 | 2024 | EHK031 | 7438.3022 | 117.2802 | 0 | 0 | 7438.3022 | 4761.5621 | 4878.8423
| 20318572 | 2025 | EHK031 | 9728.2925 | 132.2578 | 0 | 0 | 9728.2925 | 4761.5621 | 4893.8198
| 20318572 | 2026 | EHK031 | 14659.0138 | 65.1782 | 0 | 0 | 14659.0138 | 4761.5621 | 4826.7403
| 20318572 | 2027 | EHK031 | 21674.0964 | 118.3949 | 0 | 0 | 21674.0964 | 4761.5621 | 4879.957
| 20318572 | 2028 | EHK031 | 21674.0964 | 118.3949 | 0 | 0 | 21674.0964 | 4761.5621 | 4879.957
| 20318572 | 2029 | EHK031 | 21674.0964 | 118.3949 | 0 | 0 | 21674.0964 | 4761.5621 | 4879.957
| 20318572 | 2030 | EHK031 | 21674.0964 | 118.3949 | 0 | 0 | 21674.0964 | 4761.5621 | 4879.957
| 20318572 | 2031 | EHK031 | 21674.0964 | 118.3949 | 0 | 0 | 21674.0964 | 4761.5621 | 4879.957
| 20318572 | 2032 | EHK031 | 21674.0964 | 118.3949 | 0 | 0 | 21674.0964 | 4761.5621 | 4879.957
| 20318572 | 2033 | EHK031 | 21674.0964 | 118.3949 | 0 | 0 | 21674.0964 | 4761.5621 | 4879.957
| 20318572 | 2034 | EHK031 | 21674.0964 | 118.3949 | 0 | 0 | 21674.0964 | 4761.5621 | 4879.957
| 143034612 | 2023 | EHK031 | 0 | 0 | 0 | 0 | 0 | 3689.6437 | 3689.6437
| 143034612 | 2024 | EHK031 | 0 | 0 | 0 | 0 | 0 | 3689.6437 | 3689.6437
| 143034612 | 2025 | EHK031 | 0 | 0 | 0 | 0 | 0 | 3689.6437 | 3689.6437
| 143034612 | 2026 | EHK031 | 0 | 0 | 0 | 0 | 0 | 3689.6437 | 3689.6437
| 143034612 | 2027 | EHK031 | 0 | 0 | 0 | 0 | 0 | 3689.6437 | 3689.6437
| 143034612 | 2028 | EHK031 | 0 | 0 | 0 | 0 | 0 | 3689.6437 | 3689.6437
| 143034612 | 2029 | EHK031 | 0 | 0 | 0 | 0 | 0 | 3689.6437 | 3689.6437
| 143034612 | 2030 | EHK031 | 0 | 0 | 0 | 0 | 0 | 3689.6437 | 3689.6437
| 143034612 | 2031 | EHK031 | 0 | 0 | 0 | 0 | 0 | 3689.6437 | 3689.6437
| 143034612 | 2032 | EHK031 | 0 | 0 | 0 | 0 | 0 | 3689.6437 | 3689.6437
| 143034612 | 2033 | EHK031 | 0 | 0 | 0 | 0 | 0 | 3689.6437 | 3689.6437
| 143034612 | 2034 | EHK031 | 0 | 0 | 0 | 0 | 0 | 3689.6437 | 3689.6437
| 20452145 | 2023 | GSB012 | 0 | 0 | 0 | 0 | 0 | 12899.4666 | 12899.4666
| 20452145 | 2024 | GSB012 | 0 | 0 | 0 | 0 | 0 | 12899.4666 | 12899.4666
| 20452145 | 2025 | GSB012 | 0 | 0 | 0 | 0 | 0 | 12899.4666 | 12899.4666
| 20452145 | 2026 | GSB012 | 0 | 0 | 0 | 0 | 0 | 12899.4666 | 12899.4666
| 20452145 | 2027 | GSB012 | 0 | 0 | 0 | 0 | 0 | 12899.4666 | 12899.4666
| 20452145 | 2028 | GSB012 | 0 | 0 | 0 | 0 | 0 | 12899.4666 | 12899.4666
| 20452145 | 2029 | GSB012 | 0 | 0 | 0 | 0 | 0 | 12899.4666 | 12899.4666
| 20452145 | 2030 | GSB012 | 0 | 0 | 0 | 0 | 0 | 12899.4666 | 12899.4666
| 20452145 | 2031 | GSB012 | 0 | 0 | 0 | 0 | 0 | 12899.4666 | 12899.4666
| 20452145 | 2032 | GSB012 | 0 | 0 | 0 | 0 | 0 | 12899.4666 | 12899.4666
| 20452145 | 2033 | GSB012 | 0 | 0 | 0 | 0 | 0 | 12899.4666 | 12899.4666
| 20452145 | 2034 | GSB012 | 0 | 0 | 0 | 0 | 0 | 12899.4666 | 12899.4666
| 20563081 | 2023 | GSB012 | 0 | 0 | 0 | 0 | 0 | 5033.159 | 5033.159
| 20563081 | 2024 | GSB012 | 0 | 0 | 0 | 0 | 0 | 5033.159 | 5033.159
| 20563081 | 2025 | GSB012 | 0 | 0 | 0 | 0 | 0 | 5033.159 | 5033.159
| 20563081 | 2026 | GSB012 | 0 | 0 | 0 | 0 | 0 | 5033.159 | 5033.159
| 20563081 | 2027 | GSB012 | 0 | 0 | 0 | 0 | 0 | 5033.159 | 5033.159
| 20563081 | 2028 | GSB012 | 0 | 0 | 0 | 0 | 0 | 5033.159 | 5033.159
| 20563081 | 2029 | GSB012 | 0 | 0 | 0 | 0 | 0 | 5033.159 | 5033.159
| 20563081 | 2030 | GSB012 | 0 | 0 | 0 | 0 | 0 | 5033.159 | 5033.159
| 20563081 | 2031 | GSB012 | 0 | 0 | 0 | 0 | 0 | 5033.159 | 5033.159
| 20563081 | 2032 | GSB012 | 0 | 0 | 0 | 0 | 0 | 5033.159 | 5033.159
| 20563081 | 2033 | GSB012 | 0 | 0 | 0 | 0 | 0 | 5033.159 | 5033.159
| 20563081 | 2034 | GSB012 | 0 | 0 | 0 | 0 | 0 | 5033.159 | 5033.159
| 177117291 | 2023 | GSB012 | 0 | 0 | 61461.8935 | 1890747.4528 | 61461.8935 | 11654.3507 | 1902401.8035
| 177117291 | 2024 | GSB012 | 0 | 0 | 61461.8935 | 1890747.4528 | 61461.8935 | 11654.3507 | 1902401.8035
| 177117291 | 2025 | GSB012 | 0 | 0 | 61461.8935 | 1890747.4528 | 61461.8935 | 11654.3507 | 1902401.8035
| 177117291 | 2026 | GSB012 | 0 | 0 | 61461.8935 | 1890747.4528 | 61461.8935 | 11654.3507 | 1902401.8035
| 177117291 | 2027 | GSB012 | 0 | 0 | 61461.8935 | 1890747.4528 | 61461.8935 | 11654.3507 | 1902401.8035
| 177117291 | 2028 | GSB012 | 0 | 0 | 61461.8935 | 1890747.4528 | 61461.8935 | 11654.3507 | 1902401.8035
| 177117291 | 2029 | GSB012 | 0 | 0 | 61461.8935 | 1890747.4528 | 61461.8935 | 11654.3507 | 1902401.8035
| 177117291 | 2030 | GSB012 | 0 | 0 | 61461.8935 | 1890747.4528 | 61461.8935 | 11654.3507 | 1902401.8035
| 177117291 | 2031 | GSB012 | 0 | 0 | 61461.8935 | 1890747.4528 | 61461.8935 | 11654.3507 | 1902401.8035
| 177117291 | 2032 | GSB012 | 0 | 0 | 61461.8935 | 1890747.4528 | 61461.8935 | 11654.3507 | 1902401.8035
| 177117291 | 2033 | GSB012 | 0 | 0 | 61461.8935 | 1890747.4528 | 61461.8935 | 11654.3507 | 1902401.8035
| 177117291 | 2034 | GSB012 | 0 | 0 | 61461.8935 | 1890747.4528 | 61461.8935 | 11654.3507 | 1902401.8035
| 181418726 | 2023 | GSB012 | 0 | 0 | 0 | 0 | 0 | 991.2547 | 991.2547
| 181418726 | 2024 | GSB012 | 0 | 0 | 0 | 0 | 0 | 991.2547 | 991.2547
| 181418726 | 2025 | GSB012 | 0 | 0 | 0 | 0 | 0 | 991.2547 | 991.2547
| 181418726 | 2026 | GSB012 | 0 | 0 | 0 | 0 | 0 | 991.2547 | 991.2547
| 181418726 | 2027 | GSB012 | 0 | 0 | 0 | 0 | 0 | 991.2547 | 991.2547
| 181418726 | 2028 | GSB012 | 0 | 0 | 0 | 0 | 0 | 991.2547 | 991.2547
| 181418726 | 2029 | GSB012 | 0 | 0 | 0 | 0 | 0 | 991.2547 | 991.2547
| 181418726 | 2030 | GSB012 | 0 | 0 | 0 | 0 | 0 | 991.2547 | 991.2547
| 181418726 | 2031 | GSB012 | 0 | 0 | 0 | 0 | 0 | 991.2547 | 991.2547
| 181418726 | 2032 | GSB012 | 0 | 0 | 0 | 0 | 0 | 991.2547 | 991.2547
| 181418726 | 2033 | GSB012 | 0 | 0 | 0 | 0 | 0 | 991.2547 | 991.2547
| 181418726 | 2034 | GSB012 | 0 | 0 | 0 | 0 | 0 | 991.2547 | 991.2547
| 19931033 | 2023 | HSM001 | 644.9129 | 0 | 0 | 0 | 644.9129 | 15046.9414 | 15046.9414
| 19931033 | 2024 | HSM001 | 703.0128 | 11.8908 | 0 | 0 | 703.0128 | 15046.9414 | 15058.8322
| 19931033 | 2025 | HSM001 | 696.9236 | 16.7391 | 0 | 0 | 696.9236 | 15046.9414 | 15063.6805
| 19931033 | 2026 | HSM001 | 532.8827 | 8.8229 | 0 | 0 | 532.8827 | 15046.9414 | 15055.7643
| 19931033 | 2027 | HSM001 | 539.7267 | 8.4558 | 0 | 0 | 539.7267 | 15046.9414 | 15055.3972
| 19931033 | 2028 | HSM001 | 539.7267 | 8.4558 | 0 | 0 | 539.7267 | 15046.9414 | 15055.3972
| 19931033 | 2029 | HSM001 | 539.7267 | 8.4558 | 0 | 0 | 539.7267 | 15046.9414 | 15055.3972
| 19931033 | 2030 | HSM001 | 539.7267 | 8.4558 | 0 | 0 | 539.7267 | 15046.9414 | 15055.3972
| 19931033 | 2031 | HSM001 | 539.7267 | 8.4558 | 0 | 0 | 539.7267 | 15046.9414 | 15055.3972
| 19931033 | 2032 | HSM001 | 539.7267 | 8.4558 | 0 | 0 | 539.7267 | 15046.9414 | 15055.3972
| 19931033 | 2033 | HSM001 | 539.7267 | 8.4558 | 0 | 0 | 539.7267 | 15046.9414 | 15055.3972
| 19931033 | 2034 | HSM001 | 539.7267 | 8.4558 | 0 | 0 | 539.7267 | 15046.9414 | 15055.3972
| 19939748 | 2023 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1538.2835 | 1538.2835
| 19939748 | 2024 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1538.2835 | 1538.2835
| 19939748 | 2025 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1538.2835 | 1538.2835
| 19939748 | 2026 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1538.2835 | 1538.2835
| 19939748 | 2027 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1538.2835 | 1538.2835
| 19939748 | 2028 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1538.2835 | 1538.2835
| 19939748 | 2029 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1538.2835 | 1538.2835
| 19939748 | 2030 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1538.2835 | 1538.2835
| 19939748 | 2031 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1538.2835 | 1538.2835
| 19939748 | 2032 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1538.2835 | 1538.2835
| 19939748 | 2033 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1538.2835 | 1538.2835
| 19939748 | 2034 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1538.2835 | 1538.2835
| 19940268 | 2023 | HSM001 | 0 | 0 | 0 | 0 | 0 | 2650.6223 | 2650.6223
| 19940268 | 2024 | HSM001 | 0 | 0 | 0 | 0 | 0 | 2650.6223 | 2650.6223
| 19940268 | 2025 | HSM001 | 0 | 0 | 0 | 0 | 0 | 2650.6223 | 2650.6223
| 19940268 | 2026 | HSM001 | 0 | 0 | 0 | 0 | 0 | 2650.6223 | 2650.6223
| 19940268 | 2027 | HSM001 | 0 | 0 | 0 | 0 | 0 | 2650.6223 | 2650.6223
| 19940268 | 2028 | HSM001 | 0 | 0 | 0 | 0 | 0 | 2650.6223 | 2650.6223
| 19940268 | 2029 | HSM001 | 0 | 0 | 0 | 0 | 0 | 2650.6223 | 2650.6223
| 19940268 | 2030 | HSM001 | 0 | 0 | 0 | 0 | 0 | 2650.6223 | 2650.6223
| 19940268 | 2031 | HSM001 | 0 | 0 | 0 | 0 | 0 | 2650.6223 | 2650.6223
| 19940268 | 2032 | HSM001 | 0 | 0 | 0 | 0 | 0 | 2650.6223 | 2650.6223
| 19940268 | 2033 | HSM001 | 0 | 0 | 0 | 0 | 0 | 2650.6223 | 2650.6223
| 19940268 | 2034 | HSM001 | 0 | 0 | 0 | 0 | 0 | 2650.6223 | 2650.6223
| 19940766 | 2023 | HSM001 | 0 | 0 | 0 | 0 | 0 | 338.2577 | 338.2577
| 19940766 | 2024 | HSM001 | 0 | 0 | 0 | 0 | 0 | 338.2577 | 338.2577
| 19940766 | 2025 | HSM001 | 0 | 0 | 0 | 0 | 0 | 338.2577 | 338.2577
| 19940766 | 2026 | HSM001 | 0 | 0 | 0 | 0 | 0 | 338.2577 | 338.2577
| 19940766 | 2027 | HSM001 | 0 | 0 | 0 | 0 | 0 | 338.2577 | 338.2577
| 19940766 | 2028 | HSM001 | 0 | 0 | 0 | 0 | 0 | 338.2577 | 338.2577
| 19940766 | 2029 | HSM001 | 0 | 0 | 0 | 0 | 0 | 338.2577 | 338.2577
| 19940766 | 2030 | HSM001 | 0 | 0 | 0 | 0 | 0 | 338.2577 | 338.2577
| 19940766 | 2031 | HSM001 | 0 | 0 | 0 | 0 | 0 | 338.2577 | 338.2577
| 19940766 | 2032 | HSM001 | 0 | 0 | 0 | 0 | 0 | 338.2577 | 338.2577
| 19940766 | 2033 | HSM001 | 0 | 0 | 0 | 0 | 0 | 338.2577 | 338.2577
| 19940766 | 2034 | HSM001 | 0 | 0 | 0 | 0 | 0 | 338.2577 | 338.2577
| 19962083 | 2023 | HSM001 | 188.6855 | 0 | 0 | 0 | 188.6855 | 9179.1656 | 9179.1656
| 19962083 | 2024 | HSM001 | 202.4188 | 3.7681 | 0 | 0 | 202.4188 | 9179.1656 | 9182.9337
| 19962083 | 2025 | HSM001 | 170.8194 | 4.501 | 0 | 0 | 170.8194 | 9179.1656 | 9183.6666
| 19962083 | 2026 | HSM001 | 131.0461 | 2.4105 | 0 | 0 | 131.0461 | 9179.1656 | 9181.5761
| 19962083 | 2027 | HSM001 | 140.876 | 2.3946 | 0 | 0 | 140.876 | 9179.1656 | 9181.5602
| 19962083 | 2028 | HSM001 | 140.876 | 2.3946 | 0 | 0 | 140.876 | 9179.1656 | 9181.5602
| 19962083 | 2029 | HSM001 | 140.876 | 2.3946 | 0 | 0 | 140.876 | 9179.1656 | 9181.5602
| 19962083 | 2030 | HSM001 | 140.876 | 2.3946 | 0 | 0 | 140.876 | 9179.1656 | 9181.5602
| 19962083 | 2031 | HSM001 | 140.876 | 2.3946 | 0 | 0 | 140.876 | 9179.1656 | 9181.5602
| 19962083 | 2032 | HSM001 | 140.876 | 2.3946 | 0 | 0 | 140.876 | 9179.1656 | 9181.5602
| 19962083 | 2033 | HSM001 | 140.876 | 2.3946 | 0 | 0 | 140.876 | 9179.1656 | 9181.5602
| 19962083 | 2034 | HSM001 | 140.876 | 2.3946 | 0 | 0 | 140.876 | 9179.1656 | 9181.5602
| 19962134 | 2023 | HSM001 | 154.9067 | 0 | 0 | 0 | 154.9067 | 6062.951 | 6062.951
| 19962134 | 2024 | HSM001 | 174.9065 | 3.8569 | 0 | 0 | 174.9065 | 6062.951 | 6066.8078
| 19962134 | 2025 | HSM001 | 138.605 | 3.9131 | 0 | 0 | 138.605 | 6062.951 | 6066.8641
| 19962134 | 2026 | HSM001 | 137.307 | 2.6348 | 0 | 0 | 137.307 | 6062.951 | 6065.5858
| 19962134 | 2027 | HSM001 | 175.9668 | 3.2358 | 0 | 0 | 175.9668 | 6062.951 | 6066.1868
| 19962134 | 2028 | HSM001 | 175.9668 | 3.2358 | 0 | 0 | 175.9668 | 6062.951 | 6066.1868
| 19962134 | 2029 | HSM001 | 175.9668 | 3.2358 | 0 | 0 | 175.9668 | 6062.951 | 6066.1868
| 19962134 | 2030 | HSM001 | 175.9668 | 3.2358 | 0 | 0 | 175.9668 | 6062.951 | 6066.1868
| 19962134 | 2031 | HSM001 | 175.9668 | 3.2358 | 0 | 0 | 175.9668 | 6062.951 | 6066.1868
| 19962134 | 2032 | HSM001 | 175.9668 | 3.2358 | 0 | 0 | 175.9668 | 6062.951 | 6066.1868
| 19962134 | 2033 | HSM001 | 175.9668 | 3.2358 | 0 | 0 | 175.9668 | 6062.951 | 6066.1868
| 19962134 | 2034 | HSM001 | 175.9668 | 3.2358 | 0 | 0 | 175.9668 | 6062.951 | 6066.1868
| 20025353 | 2023 | HSM001 | 0 | 0 | 731.6416 | 30459.3921 | 731.6416 | 9760.8796 | 40220.2717
| 20025353 | 2024 | HSM001 | 0 | 0 | 813.4622 | 33865.7131 | 813.4622 | 9760.8796 | 43626.5927
| 20025353 | 2025 | HSM001 | 0 | 0 | 694.023 | 28893.2725 | 694.023 | 9760.8796 | 38654.1521
| 20025353 | 2026 | HSM001 | 0 | 0 | 528.914 | 22019.5227 | 528.914 | 9760.8796 | 31780.4023
| 20025353 | 2027 | HSM001 | 4.2795 | 0.0055511 | 522.4109 | 21748.7887 | 526.6904 | 9760.8796 | 31509.6738
| 20025353 | 2028 | HSM001 | 4.2795 | 0.0055511 | 522.4109 | 21748.7887 | 526.6904 | 9760.8796 | 31509.6738
| 20025353 | 2029 | HSM001 | 4.2795 | 0.0055511 | 522.4109 | 21748.7887 | 526.6904 | 9760.8796 | 31509.6738
| 20025353 | 2030 | HSM001 | 4.2795 | 0.0055511 | 522.4109 | 21748.7887 | 526.6904 | 9760.8796 | 31509.6738
| 20025353 | 2031 | HSM001 | 4.2795 | 0.0055511 | 522.4109 | 21748.7887 | 526.6904 | 9760.8796 | 31509.6738
| 20025353 | 2032 | HSM001 | 4.2795 | 0.0055511 | 522.4109 | 21748.7887 | 526.6904 | 9760.8796 | 31509.6738
| 20025353 | 2033 | HSM001 | 4.2795 | 0.0055511 | 522.4109 | 21748.7887 | 526.6904 | 9760.8796 | 31509.6738
| 20025353 | 2034 | HSM001 | 4.2795 | 0.0055511 | 522.4109 | 21748.7887 | 526.6904 | 9760.8796 | 31509.6738
| 94850494 | 2023 | HSM001 | 4.2375 | 0 | 0.0047615 | 0.19823 | 4.2423 | 1753.2574 | 1753.4556
| 94850494 | 2024 | HSM001 | 5.7941 | 0.0080484 | 0.014293 | 0.59503 | 5.8084 | 1753.2574 | 1753.8605
| 94850494 | 2025 | HSM001 | 45.8589 | 1.0312 | 0 | 0 | 45.8589 | 1753.2574 | 1754.2886
| 94850494 | 2026 | HSM001 | 213.2584 | 1.2942 | 0 | 0 | 213.2584 | 1753.2574 | 1754.5516
| 94850494 | 2027 | HSM001 | 372.6568 | 2.7175 | 0 | 0 | 372.6568 | 1753.2574 | 1755.9749
| 94850494 | 2028 | HSM001 | 372.6568 | 2.7175 | 0 | 0 | 372.6568 | 1753.2574 | 1755.9749
| 94850494 | 2029 | HSM001 | 372.6568 | 2.7175 | 0 | 0 | 372.6568 | 1753.2574 | 1755.9749
| 94850494 | 2030 | HSM001 | 372.6568 | 2.7175 | 0 | 0 | 372.6568 | 1753.2574 | 1755.9749
| 94850494 | 2031 | HSM001 | 372.6568 | 2.7175 | 0 | 0 | 372.6568 | 1753.2574 | 1755.9749
| 94850494 | 2032 | HSM001 | 372.6568 | 2.7175 | 0 | 0 | 372.6568 | 1753.2574 | 1755.9749
| 94850494 | 2033 | HSM001 | 372.6568 | 2.7175 | 0 | 0 | 372.6568 | 1753.2574 | 1755.9749
| 94850494 | 2034 | HSM001 | 372.6568 | 2.7175 | 0 | 0 | 372.6568 | 1753.2574 | 1755.9749
| 156672955 | 2023 | HSM001 | 0 | 0 | 94553.865 | 3936426.3435 | 94553.865 | 6175.0727 | 3942601.4162
| 156672955 | 2024 | HSM001 | 0 | 0 | 97114.3834 | 4043024.7591 | 97114.3834 | 6175.0727 | 4049199.8318
| 156672955 | 2025 | HSM001 | 0 | 0 | 93555.2161 | 3894851.0198 | 93555.2161 | 6175.0727 | 3901026.0925
| 156672955 | 2026 | HSM001 | 233.8996 | 1.4616 | 84780.6996 | 3529554.0749 | 85014.5992 | 6175.0727 | 3535730.6091
| 156672955 | 2027 | HSM001 | 1023.829 | 6.4536 | 83410.3735 | 3472505.2413 | 84434.2025 | 6175.0727 | 3478686.7676
| 156672955 | 2028 | HSM001 | 1023.829 | 6.4536 | 83410.3735 | 3472505.2413 | 84434.2025 | 6175.0727 | 3478686.7676
| 156672955 | 2029 | HSM001 | 1023.829 | 6.4536 | 83410.3735 | 3472505.2413 | 84434.2025 | 6175.0727 | 3478686.7676
| 156672955 | 2030 | HSM001 | 1023.829 | 6.4536 | 83410.3735 | 3472505.2413 | 84434.2025 | 6175.0727 | 3478686.7676
| 156672955 | 2031 | HSM001 | 1023.829 | 6.4536 | 83410.3735 | 3472505.2413 | 84434.2025 | 6175.0727 | 3478686.7676
| 156672955 | 2032 | HSM001 | 1023.829 | 6.4536 | 83410.3735 | 3472505.2413 | 84434.2025 | 6175.0727 | 3478686.7676
| 156672955 | 2033 | HSM001 | 1023.829 | 6.4536 | 83410.3735 | 3472505.2413 | 84434.2025 | 6175.0727 | 3478686.7676
| 156672955 | 2034 | HSM001 | 1023.829 | 6.4536 | 83410.3735 | 3472505.2413 | 84434.2025 | 6175.0727 | 3478686.7676
| 157534903 | 2023 | HSM001 | 0 | 0 | 0.43994 | 18.3152 | 0.43994 | 12899.8193 | 12918.1345
| 157534903 | 2024 | HSM001 | 0 | 0 | 0.46844 | 19.5019 | 0.46844 | 12899.8193 | 12919.3212
| 157534903 | 2025 | HSM001 | 0 | 0 | 0.77067 | 32.0842 | 0.77067 | 12899.8193 | 12931.9034
| 157534903 | 2026 | HSM001 | 0 | 0 | 5.4197 | 225.6296 | 5.4197 | 12899.8193 | 13125.4488
| 157534903 | 2027 | HSM001 | 0 | 0 | 40.2731 | 1676.6345 | 40.2731 | 12899.8193 | 14576.4537
| 157534903 | 2028 | HSM001 | 0 | 0 | 40.2731 | 1676.6345 | 40.2731 | 12899.8193 | 14576.4537
| 157534903 | 2029 | HSM001 | 0 | 0 | 40.2731 | 1676.6345 | 40.2731 | 12899.8193 | 14576.4537
| 157534903 | 2030 | HSM001 | 0 | 0 | 40.2731 | 1676.6345 | 40.2731 | 12899.8193 | 14576.4537
| 157534903 | 2031 | HSM001 | 0 | 0 | 40.2731 | 1676.6345 | 40.2731 | 12899.8193 | 14576.4537
| 157534903 | 2032 | HSM001 | 0 | 0 | 40.2731 | 1676.6345 | 40.2731 | 12899.8193 | 14576.4537
| 157534903 | 2033 | HSM001 | 0 | 0 | 40.2731 | 1676.6345 | 40.2731 | 12899.8193 | 14576.4537
| 157534903 | 2034 | HSM001 | 0 | 0 | 40.2731 | 1676.6345 | 40.2731 | 12899.8193 | 14576.4537
| 157577303 | 2023 | HSM001 | 0 | 0 | 38624.8371 | 1608012.8126 | 38624.8371 | 6626.2681 | 1614639.0807
| 157577303 | 2024 | HSM001 | 0 | 0 | 39501.7219 | 1644518.9072 | 39501.7219 | 6626.2681 | 1651145.1753
| 157577303 | 2025 | HSM001 | 0 | 0 | 37226.9465 | 1549816.4236 | 37226.9465 | 6626.2681 | 1556442.6917
| 157577303 | 2026 | HSM001 | 0 | 0 | 33763.2969 | 1405619.236 | 33763.2969 | 6626.2681 | 1412245.5042
| 157577303 | 2027 | HSM001 | 0 | 0 | 33290.9202 | 1385953.451 | 33290.9202 | 6626.2681 | 1392579.7191
| 157577303 | 2028 | HSM001 | 0 | 0 | 33290.9202 | 1385953.451 | 33290.9202 | 6626.2681 | 1392579.7191
| 157577303 | 2029 | HSM001 | 0 | 0 | 33290.9202 | 1385953.451 | 33290.9202 | 6626.2681 | 1392579.7191
| 157577303 | 2030 | HSM001 | 0 | 0 | 33290.9202 | 1385953.451 | 33290.9202 | 6626.2681 | 1392579.7191
| 157577303 | 2031 | HSM001 | 0 | 0 | 33290.9202 | 1385953.451 | 33290.9202 | 6626.2681 | 1392579.7191
| 157577303 | 2032 | HSM001 | 0 | 0 | 33290.9202 | 1385953.451 | 33290.9202 | 6626.2681 | 1392579.7191
| 157577303 | 2033 | HSM001 | 0 | 0 | 33290.9202 | 1385953.451 | 33290.9202 | 6626.2681 | 1392579.7191
| 157577303 | 2034 | HSM001 | 0 | 0 | 33290.9202 | 1385953.451 | 33290.9202 | 6626.2681 | 1392579.7191
| 157577552 | 2023 | HSM001 | 0 | 0 | 38516.0917 | 1603485.5704 | 38516.0917 | 4819.6952 | 1608305.2656
| 157577552 | 2024 | HSM001 | 0 | 0 | 38957.1574 | 1621847.8314 | 38957.1574 | 4819.6952 | 1626667.5266
| 157577552 | 2025 | HSM001 | 0 | 0 | 38014.5631 | 1582606.1433 | 38014.5631 | 4819.6952 | 1587425.8385
| 157577552 | 2026 | HSM001 | 0 | 0 | 35668.6863 | 1484943.5958 | 35668.6863 | 4819.6952 | 1489763.291
| 157577552 | 2027 | HSM001 | 0 | 0 | 35217.1176 | 1466144.08 | 35217.1176 | 4819.6952 | 1470963.7752
| 157577552 | 2028 | HSM001 | 0 | 0 | 35217.1176 | 1466144.08 | 35217.1176 | 4819.6952 | 1470963.7752
| 157577552 | 2029 | HSM001 | 0 | 0 | 35217.1176 | 1466144.08 | 35217.1176 | 4819.6952 | 1470963.7752
| 157577552 | 2030 | HSM001 | 0 | 0 | 35217.1176 | 1466144.08 | 35217.1176 | 4819.6952 | 1470963.7752
| 157577552 | 2031 | HSM001 | 0 | 0 | 35217.1176 | 1466144.08 | 35217.1176 | 4819.6952 | 1470963.7752
| 157577552 | 2032 | HSM001 | 0 | 0 | 35217.1176 | 1466144.08 | 35217.1176 | 4819.6952 | 1470963.7752
| 157577552 | 2033 | HSM001 | 0 | 0 | 35217.1176 | 1466144.08 | 35217.1176 | 4819.6952 | 1470963.7752
| 157577552 | 2034 | HSM001 | 0 | 0 | 35217.1176 | 1466144.08 | 35217.1176 | 4819.6952 | 1470963.7752
| 157599024 | 2023 | HSM001 | 0 | 0 | 19652.1495 | 818149.942 | 19652.1495 | 6855.7691 | 825005.7112
| 157599024 | 2024 | HSM001 | 0 | 0 | 20112.2179 | 837303.3118 | 20112.2179 | 6855.7691 | 844159.081
| 157599024 | 2025 | HSM001 | 0 | 0 | 19219.5624 | 800140.6575 | 19219.5624 | 6855.7691 | 806996.4266
| 157599024 | 2026 | HSM001 | 0 | 0 | 23555.4185 | 980649.1772 | 23555.4185 | 6855.7691 | 987504.9464
| 157599024 | 2027 | HSM001 | 0 | 0 | 54129.4427 | 2253493.9661 | 54129.4427 | 6855.7691 | 2260349.7352
| 157599024 | 2028 | HSM001 | 0 | 0 | 54129.4427 | 2253493.9661 | 54129.4427 | 6855.7691 | 2260349.7352
| 157599024 | 2029 | HSM001 | 0 | 0 | 54129.4427 | 2253493.9661 | 54129.4427 | 6855.7691 | 2260349.7352
| 157599024 | 2030 | HSM001 | 0 | 0 | 54129.4427 | 2253493.9661 | 54129.4427 | 6855.7691 | 2260349.7352
| 157599024 | 2031 | HSM001 | 0 | 0 | 54129.4427 | 2253493.9661 | 54129.4427 | 6855.7691 | 2260349.7352
| 157599024 | 2032 | HSM001 | 0 | 0 | 54129.4427 | 2253493.9661 | 54129.4427 | 6855.7691 | 2260349.7352
| 157599024 | 2033 | HSM001 | 0 | 0 | 54129.4427 | 2253493.9661 | 54129.4427 | 6855.7691 | 2260349.7352
| 157599024 | 2034 | HSM001 | 0 | 0 | 54129.4427 | 2253493.9661 | 54129.4427 | 6855.7691 | 2260349.7352
| 160440481 | 2023 | HSM001 | 0 | 0 | 2523.2152 | 105045.4231 | 2523.2152 | 8574.9956 | 113620.4187
| 160440481 | 2024 | HSM001 | 0 | 0 | 2766.5235 | 115174.7325 | 2766.5235 | 8574.9956 | 123749.7281
| 160440481 | 2025 | HSM001 | 0 | 0 | 2533.8727 | 105489.1119 | 2533.8727 | 8574.9956 | 114064.1074
| 160440481 | 2026 | HSM001 | 0 | 0 | 2130.8044 | 88708.7423 | 2130.8044 | 8574.9956 | 97283.7379
| 160440481 | 2027 | HSM001 | 0 | 0 | 2101.7397 | 87498.7338 | 2101.7397 | 8574.9956 | 96073.7294
| 160440481 | 2028 | HSM001 | 0 | 0 | 2101.7397 | 87498.7338 | 2101.7397 | 8574.9956 | 96073.7294
| 160440481 | 2029 | HSM001 | 0 | 0 | 2101.7397 | 87498.7338 | 2101.7397 | 8574.9956 | 96073.7294
| 160440481 | 2030 | HSM001 | 0 | 0 | 2101.7397 | 87498.7338 | 2101.7397 | 8574.9956 | 96073.7294
| 160440481 | 2031 | HSM001 | 0 | 0 | 2101.7397 | 87498.7338 | 2101.7397 | 8574.9956 | 96073.7294
| 160440481 | 2032 | HSM001 | 0 | 0 | 2101.7397 | 87498.7338 | 2101.7397 | 8574.9956 | 96073.7294
| 160440481 | 2033 | HSM001 | 0 | 0 | 2101.7397 | 87498.7338 | 2101.7397 | 8574.9956 | 96073.7294
| 160440481 | 2034 | HSM001 | 0 | 0 | 2101.7397 | 87498.7338 | 2101.7397 | 8574.9956 | 96073.7294
| 163582150 | 2023 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1706.587 | 1706.587
| 163582150 | 2024 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1706.587 | 1706.587
| 163582150 | 2025 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1706.587 | 1706.587
| 163582150 | 2026 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1706.587 | 1706.587
| 163582150 | 2027 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1706.587 | 1706.587
| 163582150 | 2028 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1706.587 | 1706.587
| 163582150 | 2029 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1706.587 | 1706.587
| 163582150 | 2030 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1706.587 | 1706.587
| 163582150 | 2031 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1706.587 | 1706.587
| 163582150 | 2032 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1706.587 | 1706.587
| 163582150 | 2033 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1706.587 | 1706.587
| 163582150 | 2034 | HSM001 | 0 | 0 | 0 | 0 | 0 | 1706.587 | 1706.587
| 19924679 | 2023 | HSM002 | 1395.911 | 0 | 0 | 0 | 1395.911 | 9343.772 | 9343.772
| 19924679 | 2024 | HSM002 | 803.904 | 9.8383 | 11.2156 | 466.9242 | 815.1196 | 9343.772 | 9820.5344
| 19924679 | 2025 | HSM002 | 2896.2047 | 48.4643 | 0.53296 | 22.1881 | 2896.7377 | 9343.772 | 9414.4244
| 19924679 | 2026 | HSM002 | 3790.0032 | 32.7065 | 91.5232 | 3810.2544 | 3881.5264 | 9343.772 | 13186.7329
| 19924679 | 2027 | HSM002 | 9941.7835 | 92.756 | 107.6939 | 4483.4666 | 10049.4774 | 9343.772 | 13919.9945
| 19924679 | 2028 | HSM002 | 15796.8462 | 161.7991 | 143.8541 | 5988.8739 | 15940.7003 | 9343.772 | 15494.445
| 19924679 | 2029 | HSM002 | 15796.8462 | 161.7991 | 143.8541 | 5988.8739 | 15940.7003 | 9343.772 | 15494.445
| 19924679 | 2030 | HSM002 | 15796.8462 | 161.7991 | 143.8541 | 5988.8739 | 15940.7003 | 9343.772 | 15494.445
| 19924679 | 2031 | HSM002 | 15796.8462 | 161.7991 | 143.8541 | 5988.8739 | 15940.7003 | 9343.772 | 15494.445
| 19924679 | 2032 | HSM002 | 15796.8462 | 161.7991 | 143.8541 | 5988.8739 | 15940.7003 | 9343.772 | 15494.445
| 19924679 | 2033 | HSM002 | 15796.8462 | 161.7991 | 143.8541 | 5988.8739 | 15940.7003 | 9343.772 | 15494.445
| 19924679 | 2034 | HSM002 | 15796.8462 | 161.7991 | 143.8541 | 5988.8739 | 15940.7003 | 9343.772 | 15494.445
| 19924741 | 2023 | HSM002 | 0 | 0 | 0 | 0 | 0 | 2289.5924 | 2289.5924
| 19924741 | 2024 | HSM002 | 0 | 0 | 3.4898 | 145.2857 | 3.4898 | 2289.5924 | 2434.8781
| 19924741 | 2025 | HSM002 | 0 | 0 | 0.90445 | 37.6536 | 0.90445 | 2289.5924 | 2327.246
| 19924741 | 2026 | HSM002 | 0 | 0 | 0.3552 | 14.7877 | 0.3552 | 2289.5924 | 2304.3801
| 19924741 | 2027 | HSM002 | 0 | 0 | 0.38042 | 15.8376 | 0.38042 | 2289.5924 | 2305.4299
| 19924741 | 2028 | HSM002 | 0 | 0 | 0.50587 | 21.0604 | 0.50587 | 2289.5924 | 2310.6527
| 19924741 | 2029 | HSM002 | 0 | 0 | 0.50587 | 21.0604 | 0.50587 | 2289.5924 | 2310.6527
| 19924741 | 2030 | HSM002 | 0 | 0 | 0.50587 | 21.0604 | 0.50587 | 2289.5924 | 2310.6527
| 19924741 | 2031 | HSM002 | 0 | 0 | 0.50587 | 21.0604 | 0.50587 | 2289.5924 | 2310.6527
| 19924741 | 2032 | HSM002 | 0 | 0 | 0.50587 | 21.0604 | 0.50587 | 2289.5924 | 2310.6527
| 19924741 | 2033 | HSM002 | 0 | 0 | 0.50587 | 21.0604 | 0.50587 | 2289.5924 | 2310.6527
| 19924741 | 2034 | HSM002 | 0 | 0 | 0.50587 | 21.0604 | 0.50587 | 2289.5924 | 2310.6527
| 19930894 | 2023 | HSM002 | 0 | 0 | 0 | 0 | 0 | 3813.1499 | 3813.1499
| 19930894 | 2024 | HSM002 | 0 | 0 | 0 | 0 | 0 | 3813.1499 | 3813.1499
| 19930894 | 2025 | HSM002 | 0 | 0 | 0 | 0 | 0 | 3813.1499 | 3813.1499
| 19930894 | 2026 | HSM002 | 0 | 0 | 0 | 0 | 0 | 3813.1499 | 3813.1499
| 19930894 | 2027 | HSM002 | 0 | 0 | 0 | 0 | 0 | 3813.1499 | 3813.1499
| 19930894 | 2028 | HSM002 | 0 | 0 | 0 | 0 | 0 | 3813.1499 | 3813.1499
| 19930894 | 2029 | HSM002 | 0 | 0 | 0 | 0 | 0 | 3813.1499 | 3813.1499
| 19930894 | 2030 | HSM002 | 0 | 0 | 0 | 0 | 0 | 3813.1499 | 3813.1499
| 19930894 | 2031 | HSM002 | 0 | 0 | 0 | 0 | 0 | 3813.1499 | 3813.1499
| 19930894 | 2032 | HSM002 | 0 | 0 | 0 | 0 | 0 | 3813.1499 | 3813.1499
| 19930894 | 2033 | HSM002 | 0 | 0 | 0 | 0 | 0 | 3813.1499 | 3813.1499
| 19930894 | 2034 | HSM002 | 0 | 0 | 0 | 0 | 0 | 3813.1499 | 3813.1499
| 20025741 | 2023 | HSM002 | 0 | 0 | 7331.1465 | 305207.176 | 7331.1465 | 8535.7529 | 313742.9289
| 20025741 | 2024 | HSM002 | 0 | 0 | 10568.2692 | 439973.6924 | 10568.2692 | 8535.7529 | 448509.4453
| 20025741 | 2025 | HSM002 | 0 | 0 | 11089.1534 | 461658.923 | 11089.1534 | 8535.7529 | 470194.6759
| 20025741 | 2026 | HSM002 | 0 | 0 | 18212.2682 | 758205.4148 | 18212.2682 | 8535.7529 | 766741.1677
| 20025741 | 2027 | HSM002 | 0 | 0 | 18231.0763 | 758988.4234 | 18231.0763 | 8535.7529 | 767524.1763
| 20025741 | 2028 | HSM002 | 0 | 0 | 18129.2664 | 754749.9183 | 18129.2664 | 8535.7529 | 763285.6712
| 20025741 | 2029 | HSM002 | 0 | 0 | 18129.2664 | 754749.9183 | 18129.2664 | 8535.7529 | 763285.6712
| 20025741 | 2030 | HSM002 | 0 | 0 | 18129.2664 | 754749.9183 | 18129.2664 | 8535.7529 | 763285.6712
| 20025741 | 2031 | HSM002 | 0 | 0 | 18129.2664 | 754749.9183 | 18129.2664 | 8535.7529 | 763285.6712
| 20025741 | 2032 | HSM002 | 0 | 0 | 18129.2664 | 754749.9183 | 18129.2664 | 8535.7529 | 763285.6712
| 20025741 | 2033 | HSM002 | 0 | 0 | 18129.2664 | 754749.9183 | 18129.2664 | 8535.7529 | 763285.6712
| 20025741 | 2034 | HSM002 | 0 | 0 | 18129.2664 | 754749.9183 | 18129.2664 | 8535.7529 | 763285.6712
| 20026023 | 2023 | HSM002 | 0 | 0 | 3.625 | 150.9151 | 3.625 | 2118.7343 | 2269.6495
| 20026023 | 2024 | HSM002 | 0 | 0 | 32.7373 | 1362.9057 | 32.7373 | 2118.7343 | 3481.64
| 20026023 | 2025 | HSM002 | 0 | 0 | 20.1991 | 840.9204 | 20.1991 | 2118.7343 | 2959.6548
| 20026023 | 2026 | HSM002 | 0 | 0 | 5.9654 | 248.3489 | 5.9654 | 2118.7343 | 2367.0832
| 20026023 | 2027 | HSM002 | 0 | 0 | 4.1562 | 173.0307 | 4.1562 | 2118.7343 | 2291.7651
| 20026023 | 2028 | HSM002 | 0 | 0 | 2.8897 | 120.304 | 2.8897 | 2118.7343 | 2239.0383
| 20026023 | 2029 | HSM002 | 0 | 0 | 2.8897 | 120.304 | 2.8897 | 2118.7343 | 2239.0383
| 20026023 | 2030 | HSM002 | 0 | 0 | 2.8897 | 120.304 | 2.8897 | 2118.7343 | 2239.0383
| 20026023 | 2031 | HSM002 | 0 | 0 | 2.8897 | 120.304 | 2.8897 | 2118.7343 | 2239.0383
| 20026023 | 2032 | HSM002 | 0 | 0 | 2.8897 | 120.304 | 2.8897 | 2118.7343 | 2239.0383
| 20026023 | 2033 | HSM002 | 0 | 0 | 2.8897 | 120.304 | 2.8897 | 2118.7343 | 2239.0383
| 20026023 | 2034 | HSM002 | 0 | 0 | 2.8897 | 120.304 | 2.8897 | 2118.7343 | 2239.0383
| 20031167 | 2023 | HSM002 | 5634.5516 | 0 | 0 | 0 | 5634.5516 | 5346.3132 | 5346.3132
| 20031167 | 2024 | HSM002 | 7652.2065 | 165.348 | 0 | 0 | 7652.2065 | 5346.3132 | 5511.6612
| 20031167 | 2025 | HSM002 | 12053.3346 | 294.3691 | 0 | 0 | 12053.3346 | 5346.3132 | 5640.6823
| 20031167 | 2026 | HSM002 | 21825.5141 | 287.5454 | 0.86175 | 35.8761 | 21826.3759 | 5346.3132 | 5669.7347
| 20031167 | 2027 | HSM002 | 30133.9199 | 325.3819 | 0.98701 | 41.0909 | 30134.9069 | 5346.3132 | 5712.786
| 20031167 | 2028 | HSM002 | 39731.4653 | 468.4459 | 249.083 | 10369.719 | 39980.5483 | 5346.3132 | 16184.4781
| 20031167 | 2029 | HSM002 | 39731.4653 | 468.4459 | 249.083 | 10369.719 | 39980.5483 | 5346.3132 | 16184.4781
| 20031167 | 2030 | HSM002 | 39731.4653 | 468.4459 | 249.083 | 10369.719 | 39980.5483 | 5346.3132 | 16184.4781
| 20031167 | 2031 | HSM002 | 39731.4653 | 468.4459 | 249.083 | 10369.719 | 39980.5483 | 5346.3132 | 16184.4781
| 20031167 | 2032 | HSM002 | 39731.4653 | 468.4459 | 249.083 | 10369.719 | 39980.5483 | 5346.3132 | 16184.4781
| 20031167 | 2033 | HSM002 | 39731.4653 | 468.4459 | 249.083 | 10369.719 | 39980.5483 | 5346.3132 | 16184.4781
| 20031167 | 2034 | HSM002 | 39731.4653 | 468.4459 | 249.083 | 10369.719 | 39980.5483 | 5346.3132 | 16184.4781
| 20031317 | 2023 | HSM002 | 2765.1482 | 0 | 0 | 0 | 2765.1482 | 1289.2429 | 1289.2429
| 20031317 | 2024 | HSM002 | 4855.9652 | 97.7379 | 0 | 0 | 4855.9652 | 1289.2429 | 1386.9808
| 20031317 | 2025 | HSM002 | 5072.5881 | 107.1537 | 0 | 0 | 5072.5881 | 1289.2429 | 1396.3965
| 20031317 | 2026 | HSM002 | 8161.7836 | 115.3874 | 0 | 0 | 8161.7836 | 1289.2429 | 1404.6303
| 20031317 | 2027 | HSM002 | 19074.031 | 262.6675 | 0 | 0 | 19074.031 | 1289.2429 | 1551.9104
| 20031317 | 2028 | HSM002 | 17975.1311 | 257.093 | 0 | 0 | 17975.1311 | 1289.2429 | 1546.3359
| 20031317 | 2029 | HSM002 | 17975.1311 | 257.093 | 0 | 0 | 17975.1311 | 1289.2429 | 1546.3359
| 20031317 | 2030 | HSM002 | 17975.1311 | 257.093 | 0 | 0 | 17975.1311 | 1289.2429 | 1546.3359
| 20031317 | 2031 | HSM002 | 17975.1311 | 257.093 | 0 | 0 | 17975.1311 | 1289.2429 | 1546.3359
| 20031317 | 2032 | HSM002 | 17975.1311 | 257.093 | 0 | 0 | 17975.1311 | 1289.2429 | 1546.3359
| 20031317 | 2033 | HSM002 | 17975.1311 | 257.093 | 0 | 0 | 17975.1311 | 1289.2429 | 1546.3359
| 20031317 | 2034 | HSM002 | 17975.1311 | 257.093 | 0 | 0 | 17975.1311 | 1289.2429 | 1546.3359
| 20031621 | 2023 | HSM002 | 0 | 0 | 0 | 0 | 0 | 4720.0135 | 4720.0135
| 20031621 | 2024 | HSM002 | 5194.5992 | 146.8441 | 0 | 0 | 5194.5992 | 4720.0135 | 4866.8576
| 20031621 | 2025 | HSM002 | 9475.0811 | 270.9574 | 0 | 0 | 9475.0811 | 4720.0135 | 4990.9708
| 20031621 | 2026 | HSM002 | 25354.7501 | 496.704 | 0 | 0 | 25354.7501 | 4720.0135 | 5216.7175
| 20031621 | 2027 | HSM002 | 31430.894 | 574.149 | 0 | 0 | 31430.894 | 4720.0135 | 5294.1625
| 20031621 | 2028 | HSM002 | 40288.123 | 812.4074 | 122.9931 | 5120.3982 | 40411.1162 | 4720.0135 | 10652.819
| 20031621 | 2029 | HSM002 | 40288.123 | 812.4074 | 122.9931 | 5120.3982 | 40411.1162 | 4720.0135 | 10652.819
| 20031621 | 2030 | HSM002 | 40288.123 | 812.4074 | 122.9931 | 5120.3982 | 40411.1162 | 4720.0135 | 10652.819
| 20031621 | 2031 | HSM002 | 40288.123 | 812.4074 | 122.9931 | 5120.3982 | 40411.1162 | 4720.0135 | 10652.819
| 20031621 | 2032 | HSM002 | 40288.123 | 812.4074 | 122.9931 | 5120.3982 | 40411.1162 | 4720.0135 | 10652.819
| 20031621 | 2033 | HSM002 | 40288.123 | 812.4074 | 122.9931 | 5120.3982 | 40411.1162 | 4720.0135 | 10652.819
| 20031621 | 2034 | HSM002 | 40288.123 | 812.4074 | 122.9931 | 5120.3982 | 40411.1162 | 4720.0135 | 10652.819
| 20033571 | 2023 | HSM002 | 211.2263 | 0 | 0 | 0 | 211.2263 | 2502.5992 | 2502.5992
| 20033571 | 2024 | HSM002 | 315.3087 | 5.2321 | 0 | 0 | 315.3087 | 2502.5992 | 2507.8312
| 20033571 | 2025 | HSM002 | 464.2679 | 6.6438 | 0 | 0 | 464.2679 | 2502.5992 | 2509.243
| 20033571 | 2026 | HSM002 | 2127.1683 | 16.2425 | 3.1884 | 132.7388 | 2130.3567 | 2502.5992 | 2651.5805
| 20033571 | 2027 | HSM002 | 4136.1647 | 26.2819 | 4.1546 | 172.9616 | 4140.3193 | 2502.5992 | 2701.8427
| 20033571 | 2028 | HSM002 | 7881.9332 | 59.3967 | 172.0986 | 7164.7357 | 8054.0318 | 2502.5992 | 9726.7316
| 20033571 | 2029 | HSM002 | 7881.9332 | 59.3967 | 172.0986 | 7164.7357 | 8054.0318 | 2502.5992 | 9726.7316
| 20033571 | 2030 | HSM002 | 7881.9332 | 59.3967 | 172.0986 | 7164.7357 | 8054.0318 | 2502.5992 | 9726.7316
| 20033571 | 2031 | HSM002 | 7881.9332 | 59.3967 | 172.0986 | 7164.7357 | 8054.0318 | 2502.5992 | 9726.7316
| 20033571 | 2032 | HSM002 | 7881.9332 | 59.3967 | 172.0986 | 7164.7357 | 8054.0318 | 2502.5992 | 9726.7316
| 20033571 | 2033 | HSM002 | 7881.9332 | 59.3967 | 172.0986 | 7164.7357 | 8054.0318 | 2502.5992 | 9726.7316
| 20033571 | 2034 | HSM002 | 7881.9332 | 59.3967 | 172.0986 | 7164.7357 | 8054.0318 | 2502.5992 | 9726.7316
| 20495668 | 2023 | HSM002 | 97.3794 | 0 | 0 | 0 | 97.3794 | 1650.9313 | 1650.9313
| 20495668 | 2024 | HSM002 | 25375.3783 | 608.2484 | 0 | 0 | 25375.3783 | 1650.9313 | 2259.1797
| 20495668 | 2025 | HSM002 | 25572.0102 | 657.655 | 0 | 0 | 25572.0102 | 1650.9313 | 2308.5863
| 20495668 | 2026 | HSM002 | 30718.5019 | 546.9202 | 0 | 0 | 30718.5019 | 1650.9313 | 2197.8515
| 20495668 | 2027 | HSM002 | 40957.4522 | 662.3353 | 0 | 0 | 40957.4522 | 1650.9313 | 2313.2666
| 20495668 | 2028 | HSM002 | 52571.3309 | 1027.5972 | 0.19918 | 8.292 | 52571.5301 | 1650.9313 | 2686.8205
| 20495668 | 2029 | HSM002 | 52571.3309 | 1027.5972 | 0.19918 | 8.292 | 52571.5301 | 1650.9313 | 2686.8205
| 20495668 | 2030 | HSM002 | 52571.3309 | 1027.5972 | 0.19918 | 8.292 | 52571.5301 | 1650.9313 | 2686.8205
| 20495668 | 2031 | HSM002 | 52571.3309 | 1027.5972 | 0.19918 | 8.292 | 52571.5301 | 1650.9313 | 2686.8205
| 20495668 | 2032 | HSM002 | 52571.3309 | 1027.5972 | 0.19918 | 8.292 | 52571.5301 | 1650.9313 | 2686.8205
| 20495668 | 2033 | HSM002 | 52571.3309 | 1027.5972 | 0.19918 | 8.292 | 52571.5301 | 1650.9313 | 2686.8205
| 20495668 | 2034 | HSM002 | 52571.3309 | 1027.5972 | 0.19918 | 8.292 | 52571.5301 | 1650.9313 | 2686.8205
| 20495907 | 2023 | HSM002 | 11880.9027 | 0 | 0 | 0 | 11880.9027 | 5808.2096 | 5808.2096
| 20495907 | 2024 | HSM002 | 20995.2773 | 474.7139 | 0 | 0 | 20995.2773 | 5808.2096 | 6282.9235
| 20495907 | 2025 | HSM002 | 25365.0695 | 614.3262 | 0 | 0 | 25365.0695 | 5808.2096 | 6422.5358
| 20495907 | 2026 | HSM002 | 28353.711 | 405.1081 | 0 | 0 | 28353.711 | 5808.2096 | 6213.3177
| 20495907 | 2027 | HSM002 | 33970.4978 | 414.9713 | 0 | 0 | 33970.4978 | 5808.2096 | 6223.181
| 20495907 | 2028 | HSM002 | 73594.5417 | 1044.3764 | 514.7253 | 21428.8268 | 74109.267 | 5808.2096 | 28281.4128
| 20495907 | 2029 | HSM002 | 73594.5417 | 1044.3764 | 514.7253 | 21428.8268 | 74109.267 | 5808.2096 | 28281.4128
| 20495907 | 2030 | HSM002 | 73594.5417 | 1044.3764 | 514.7253 | 21428.8268 | 74109.267 | 5808.2096 | 28281.4128
| 20495907 | 2031 | HSM002 | 73594.5417 | 1044.3764 | 514.7253 | 21428.8268 | 74109.267 | 5808.2096 | 28281.4128
| 20495907 | 2032 | HSM002 | 73594.5417 | 1044.3764 | 514.7253 | 21428.8268 | 74109.267 | 5808.2096 | 28281.4128
| 20495907 | 2033 | HSM002 | 73594.5417 | 1044.3764 | 514.7253 | 21428.8268 | 74109.267 | 5808.2096 | 28281.4128
| 20495907 | 2034 | HSM002 | 73594.5417 | 1044.3764 | 514.7253 | 21428.8268 | 74109.267 | 5808.2096 | 28281.4128
| 20495956 | 2023 | HSM002 | 0 | 0 | 0 | 0 | 0 | 2180.917 | 2180.917
| 20495956 | 2024 | HSM002 | 0 | 0 | 0 | 0 | 0 | 2180.917 | 2180.917
| 20495956 | 2025 | HSM002 | 1105.5663 | 16.5779 | 0 | 0 | 1105.5663 | 2180.917 | 2197.4949
| 20495956 | 2026 | HSM002 | 5489.0945 | 46.7738 | 0 | 0 | 5489.0945 | 2180.917 | 2227.6909
| 20495956 | 2027 | HSM002 | 10150.8843 | 80.8694 | 0 | 0 | 10150.8843 | 2180.917 | 2261.7864
| 20495956 | 2028 | HSM002 | 10179.9582 | 101.3319 | 79.7008 | 3318.0702 | 10259.6591 | 2180.917 | 5600.3191
| 20495956 | 2029 | HSM002 | 10179.9582 | 101.3319 | 79.7008 | 3318.0702 | 10259.6591 | 2180.917 | 5600.3191
| 20495956 | 2030 | HSM002 | 10179.9582 | 101.3319 | 79.7008 | 3318.0702 | 10259.6591 | 2180.917 | 5600.3191
| 20495956 | 2031 | HSM002 | 10179.9582 | 101.3319 | 79.7008 | 3318.0702 | 10259.6591 | 2180.917 | 5600.3191
| 20495956 | 2032 | HSM002 | 10179.9582 | 101.3319 | 79.7008 | 3318.0702 | 10259.6591 | 2180.917 | 5600.3191
| 20495956 | 2033 | HSM002 | 10179.9582 | 101.3319 | 79.7008 | 3318.0702 | 10259.6591 | 2180.917 | 5600.3191
| 20495956 | 2034 | HSM002 | 10179.9582 | 101.3319 | 79.7008 | 3318.0702 | 10259.6591 | 2180.917 | 5600.3191
| 94342093 | 2023 | HSM002 | 0 | 0 | 7586.234 | 315826.8711 | 7586.234 | 6358.6437 | 322185.5148
| 94342093 | 2024 | HSM002 | 0 | 0 | 9856.5722 | 410344.6271 | 9856.5722 | 6358.6437 | 416703.2708
| 94342093 | 2025 | HSM002 | 0 | 0 | 10270.0068 | 427556.5613 | 10270.0068 | 6358.6437 | 433915.205
| 94342093 | 2026 | HSM002 | 0 | 0 | 17145.0416 | 713775.0886 | 17145.0416 | 6358.6437 | 720133.7323
| 94342093 | 2027 | HSM002 | 0 | 0 | 16938.7536 | 705186.9931 | 16938.7536 | 6358.6437 | 711545.6368
| 94342093 | 2028 | HSM002 | 0 | 0 | 16979.6013 | 706887.5497 | 16979.6013 | 6358.6437 | 713246.1934
| 94342093 | 2029 | HSM002 | 0 | 0 | 16979.6013 | 706887.5497 | 16979.6013 | 6358.6437 | 713246.1934
| 94342093 | 2030 | HSM002 | 0 | 0 | 16979.6013 | 706887.5497 | 16979.6013 | 6358.6437 | 713246.1934
| 94342093 | 2031 | HSM002 | 0 | 0 | 16979.6013 | 706887.5497 | 16979.6013 | 6358.6437 | 713246.1934
| 94342093 | 2032 | HSM002 | 0 | 0 | 16979.6013 | 706887.5497 | 16979.6013 | 6358.6437 | 713246.1934
| 94342093 | 2033 | HSM002 | 0 | 0 | 16979.6013 | 706887.5497 | 16979.6013 | 6358.6437 | 713246.1934
| 94342093 | 2034 | HSM002 | 0 | 0 | 16979.6013 | 706887.5497 | 16979.6013 | 6358.6437 | 713246.1934
| 157499868 | 2023 | HSM002 | 0 | 0 | 58.5454 | 2437.3372 | 58.5454 | 661.6952 | 3099.0324
| 157499868 | 2024 | HSM002 | 0 | 0 | 166.172 | 6918.0024 | 166.172 | 661.6952 | 7579.6976
| 157499868 | 2025 | HSM002 | 0 | 0 | 183.3784 | 7634.3316 | 183.3784 | 661.6952 | 8296.0268
| 157499868 | 2026 | HSM002 | 0 | 0 | 766.9507 | 31929.3645 | 766.9507 | 661.6952 | 32591.0597
| 157499868 | 2027 | HSM002 | 0 | 0 | 800.2107 | 33314.0332 | 800.2107 | 661.6952 | 33975.7284
| 157499868 | 2028 | HSM002 | 0 | 0 | 868.0352 | 36137.6737 | 868.0352 | 661.6952 | 36799.3688
| 157499868 | 2029 | HSM002 | 0 | 0 | 868.0352 | 36137.6737 | 868.0352 | 661.6952 | 36799.3688
| 157499868 | 2030 | HSM002 | 0 | 0 | 868.0352 | 36137.6737 | 868.0352 | 661.6952 | 36799.3688
| 157499868 | 2031 | HSM002 | 0 | 0 | 868.0352 | 36137.6737 | 868.0352 | 661.6952 | 36799.3688
| 157499868 | 2032 | HSM002 | 0 | 0 | 868.0352 | 36137.6737 | 868.0352 | 661.6952 | 36799.3688
| 157499868 | 2033 | HSM002 | 0 | 0 | 868.0352 | 36137.6737 | 868.0352 | 661.6952 | 36799.3688
| 157499868 | 2034 | HSM002 | 0 | 0 | 868.0352 | 36137.6737 | 868.0352 | 661.6952 | 36799.3688
| 158126550 | 2023 | HSM002 | 0 | 0 | 0 | 0 | 0 | 1122.9341 | 1122.9341
| 158126550 | 2024 | HSM002 | 0 | 0 | 0 | 0 | 0 | 1122.9341 | 1122.9341
| 158126550 | 2025 | HSM002 | 0 | 0 | 0 | 0 | 0 | 1122.9341 | 1122.9341
| 158126550 | 2026 | HSM002 | 0 | 0 | 0 | 0 | 0 | 1122.9341 | 1122.9341
| 158126550 | 2027 | HSM002 | 0 | 0 | 0 | 0 | 0 | 1122.9341 | 1122.9341
| 158126550 | 2028 | HSM002 | 0 | 0 | 0 | 0 | 0 | 1122.9341 | 1122.9341
| 158126550 | 2029 | HSM002 | 0 | 0 | 0 | 0 | 0 | 1122.9341 | 1122.9341
| 158126550 | 2030 | HSM002 | 0 | 0 | 0 | 0 | 0 | 1122.9341 | 1122.9341
| 158126550 | 2031 | HSM002 | 0 | 0 | 0 | 0 | 0 | 1122.9341 | 1122.9341
| 158126550 | 2032 | HSM002 | 0 | 0 | 0 | 0 | 0 | 1122.9341 | 1122.9341
| 158126550 | 2033 | HSM002 | 0 | 0 | 0 | 0 | 0 | 1122.9341 | 1122.9341
| 158126550 | 2034 | HSM002 | 0 | 0 | 0 | 0 | 0 | 1122.9341 | 1122.9341
| 163502879 | 2023 | HSM002 | 22.9619 | 0 | 0 | 0 | 22.9619 | 606.7253 | 606.7253
| 163502879 | 2024 | HSM002 | 15.6123 | 0.71941 | 0 | 0 | 15.6123 | 606.7253 | 607.4447
| 163502879 | 2025 | HSM002 | 26.8084 | 0.77199 | 0 | 0 | 26.8084 | 606.7253 | 607.4973
| 163502879 | 2026 | HSM002 | 124.2289 | 1.3465 | 0 | 0 | 124.2289 | 606.7253 | 608.0718
| 163502879 | 2027 | HSM002 | 129.4507 | 0.99214 | 0 | 0 | 129.4507 | 606.7253 | 607.7174
| 163502879 | 2028 | HSM002 | 199.3378 | 1.675 | 4.1503 | 172.783 | 203.4881 | 606.7253 | 781.1833
| 163502879 | 2029 | HSM002 | 199.3378 | 1.675 | 4.1503 | 172.783 | 203.4881 | 606.7253 | 781.1833
| 163502879 | 2030 | HSM002 | 199.3378 | 1.675 | 4.1503 | 172.783 | 203.4881 | 606.7253 | 781.1833
| 163502879 | 2031 | HSM002 | 199.3378 | 1.675 | 4.1503 | 172.783 | 203.4881 | 606.7253 | 781.1833
| 163502879 | 2032 | HSM002 | 199.3378 | 1.675 | 4.1503 | 172.783 | 203.4881 | 606.7253 | 781.1833
| 163502879 | 2033 | HSM002 | 199.3378 | 1.675 | 4.1503 | 172.783 | 203.4881 | 606.7253 | 781.1833
| 163502879 | 2034 | HSM002 | 199.3378 | 1.675 | 4.1503 | 172.783 | 203.4881 | 606.7253 | 781.1833
| 203671002 | 2023 | HSM002 | 0 | 0 | 0 | 0 | 0 | 5299.0215 | 5299.0215
| 203671002 | 2024 | HSM002 | 0 | 0 | 1.9246 | 80.1227 | 1.9246 | 5299.0215 | 5379.1442
| 203671002 | 2025 | HSM002 | 0 | 0 | 0.63991 | 26.6406 | 0.63991 | 5299.0215 | 5325.6621
| 203671002 | 2026 | HSM002 | 0 | 0 | 21.998 | 915.8115 | 21.998 | 5299.0215 | 6214.833
| 203671002 | 2027 | HSM002 | 0 | 0 | 58.2289 | 2424.1616 | 58.2289 | 5299.0215 | 7723.1831
| 203671002 | 2028 | HSM002 | 0 | 0 | 63.9138 | 2660.8319 | 63.9138 | 5299.0215 | 7959.8534
| 203671002 | 2029 | HSM002 | 0 | 0 | 63.9138 | 2660.8319 | 63.9138 | 5299.0215 | 7959.8534
| 203671002 | 2030 | HSM002 | 0 | 0 | 63.9138 | 2660.8319 | 63.9138 | 5299.0215 | 7959.8534
| 203671002 | 2031 | HSM002 | 0 | 0 | 63.9138 | 2660.8319 | 63.9138 | 5299.0215 | 7959.8534
| 203671002 | 2032 | HSM002 | 0 | 0 | 63.9138 | 2660.8319 | 63.9138 | 5299.0215 | 7959.8534
| 203671002 | 2033 | HSM002 | 0 | 0 | 63.9138 | 2660.8319 | 63.9138 | 5299.0215 | 7959.8534
| 203671002 | 2034 | HSM002 | 0 | 0 | 63.9138 | 2660.8319 | 63.9138 | 5299.0215 | 7959.8534
| 19931696 | 2023 | HSM003 | 0 | 0 | 0 | 0 | 0 | 3636.1009 | 3636.1009
| 19931696 | 2024 | HSM003 | 0 | 0 | 0 | 0 | 0 | 3636.1009 | 3636.1009
| 19931696 | 2025 | HSM003 | 0 | 0 | 0 | 0 | 0 | 3636.1009 | 3636.1009
| 19931696 | 2026 | HSM003 | 0 | 0 | 0 | 0 | 0 | 3636.1009 | 3636.1009
| 19931696 | 2027 | HSM003 | 0 | 0 | 0 | 0 | 0 | 3636.1009 | 3636.1009
| 19931696 | 2028 | HSM003 | 0 | 0 | 0 | 0 | 0 | 3636.1009 | 3636.1009
| 19931696 | 2029 | HSM003 | 0 | 0 | 0 | 0 | 0 | 3636.1009 | 3636.1009
| 19931696 | 2030 | HSM003 | 0 | 0 | 0 | 0 | 0 | 3636.1009 | 3636.1009
| 19931696 | 2031 | HSM003 | 0 | 0 | 0 | 0 | 0 | 3636.1009 | 3636.1009
| 19931696 | 2032 | HSM003 | 0 | 0 | 0 | 0 | 0 | 3636.1009 | 3636.1009
| 19931696 | 2033 | HSM003 | 0 | 0 | 0 | 0 | 0 | 3636.1009 | 3636.1009
| 19931696 | 2034 | HSM003 | 0 | 0 | 0 | 0 | 0 | 3636.1009 | 3636.1009
| 19956238 | 2023 | HSM003 | 0 | 0 | 0 | 0 | 0 | 5351.1497 | 5351.1497
| 19956238 | 2024 | HSM003 | 0 | 0 | 0 | 0 | 0 | 5351.1497 | 5351.1497
| 19956238 | 2025 | HSM003 | 0 | 0 | 0 | 0 | 0 | 5351.1497 | 5351.1497
| 19956238 | 2026 | HSM003 | 0 | 0 | 0 | 0 | 0 | 5351.1497 | 5351.1497
| 19956238 | 2027 | HSM003 | 0 | 0 | 0 | 0 | 0 | 5351.1497 | 5351.1497
| 19956238 | 2028 | HSM003 | 0 | 0 | 0 | 0 | 0 | 5351.1497 | 5351.1497
| 19956238 | 2029 | HSM003 | 0 | 0 | 0 | 0 | 0 | 5351.1497 | 5351.1497
| 19956238 | 2030 | HSM003 | 0 | 0 | 0 | 0 | 0 | 5351.1497 | 5351.1497
| 19956238 | 2031 | HSM003 | 0 | 0 | 0 | 0 | 0 | 5351.1497 | 5351.1497
| 19956238 | 2032 | HSM003 | 0 | 0 | 0 | 0 | 0 | 5351.1497 | 5351.1497
| 19956238 | 2033 | HSM003 | 0 | 0 | 0 | 0 | 0 | 5351.1497 | 5351.1497
| 19956238 | 2034 | HSM003 | 0 | 0 | 0 | 0 | 0 | 5351.1497 | 5351.1497
| 19956512 | 2023 | HSM003 | 3100.0475 | 0 | 0 | 0 | 3100.0475 | 11196.54 | 11196.54
| 19956512 | 2024 | HSM003 | 3167.8053 | 65.1971 | 0 | 0 | 3167.8053 | 11196.54 | 11261.7372
| 19956512 | 2025 | HSM003 | 5359.175 | 107.6465 | 0 | 0 | 5359.175 | 11196.54 | 11304.1866
| 19956512 | 2026 | HSM003 | 10389.5422 | 110.7877 | 0 | 0 | 10389.5422 | 11196.54 | 11307.3277
| 19956512 | 2027 | HSM003 | 19584.4825 | 184.2845 | 0 | 0 | 19584.4825 | 11196.54 | 11380.8246
| 19956512 | 2028 | HSM003 | 19584.4825 | 184.2845 | 0 | 0 | 19584.4825 | 11196.54 | 11380.8246
| 19956512 | 2029 | HSM003 | 19584.4825 | 184.2845 | 0 | 0 | 19584.4825 | 11196.54 | 11380.8246
| 19956512 | 2030 | HSM003 | 19584.4825 | 184.2845 | 0 | 0 | 19584.4825 | 11196.54 | 11380.8246
| 19956512 | 2031 | HSM003 | 19584.4825 | 184.2845 | 0 | 0 | 19584.4825 | 11196.54 | 11380.8246
| 19956512 | 2032 | HSM003 | 19584.4825 | 184.2845 | 0 | 0 | 19584.4825 | 11196.54 | 11380.8246
| 19956512 | 2033 | HSM003 | 19584.4825 | 184.2845 | 0 | 0 | 19584.4825 | 11196.54 | 11380.8246
| 19956512 | 2034 | HSM003 | 19584.4825 | 184.2845 | 0 | 0 | 19584.4825 | 11196.54 | 11380.8246
| 19956541 | 2023 | HSM003 | 0 | 0 | 0 | 0 | 0 | 2799.4762 | 2799.4762
| 19956541 | 2024 | HSM003 | 0 | 0 | 0 | 0 | 0 | 2799.4762 | 2799.4762
| 19956541 | 2025 | HSM003 | 0 | 0 | 0 | 0 | 0 | 2799.4762 | 2799.4762
| 19956541 | 2026 | HSM003 | 0 | 0 | 0 | 0 | 0 | 2799.4762 | 2799.4762
| 19956541 | 2027 | HSM003 | 0 | 0 | 0 | 0 | 0 | 2799.4762 | 2799.4762
| 19956541 | 2028 | HSM003 | 0 | 0 | 0 | 0 | 0 | 2799.4762 | 2799.4762
| 19956541 | 2029 | HSM003 | 0 | 0 | 0 | 0 | 0 | 2799.4762 | 2799.4762
| 19956541 | 2030 | HSM003 | 0 | 0 | 0 | 0 | 0 | 2799.4762 | 2799.4762
| 19956541 | 2031 | HSM003 | 0 | 0 | 0 | 0 | 0 | 2799.4762 | 2799.4762
| 19956541 | 2032 | HSM003 | 0 | 0 | 0 | 0 | 0 | 2799.4762 | 2799.4762
| 19956541 | 2033 | HSM003 | 0 | 0 | 0 | 0 | 0 | 2799.4762 | 2799.4762
| 19956541 | 2034 | HSM003 | 0 | 0 | 0 | 0 | 0 | 2799.4762 | 2799.4762
| 19956812 | 2023 | HSM003 | 5205.7464 | 0 | 0 | 0 | 5205.7464 | 16008.8916 | 16008.8916
| 19956812 | 2024 | HSM003 | 5384.8622 | 105.6965 | 0 | 0 | 5384.8622 | 16008.8916 | 16114.5881
| 19956812 | 2025 | HSM003 | 5539.8237 | 121.7696 | 0 | 0 | 5539.8237 | 16008.8916 | 16130.6611
| 19956812 | 2026 | HSM003 | 6528.9372 | 76.2904 | 0 | 0 | 6528.9372 | 16008.8916 | 16085.182
| 19956812 | 2027 | HSM003 | 6774.4655 | 64.0914 | 0 | 0 | 6774.4655 | 16008.8916 | 16072.983
| 19956812 | 2028 | HSM003 | 6774.4655 | 64.0914 | 0 | 0 | 6774.4655 | 16008.8916 | 16072.983
| 19956812 | 2029 | HSM003 | 6774.4655 | 64.0914 | 0 | 0 | 6774.4655 | 16008.8916 | 16072.983
| 19956812 | 2030 | HSM003 | 6774.4655 | 64.0914 | 0 | 0 | 6774.4655 | 16008.8916 | 16072.983
| 19956812 | 2031 | HSM003 | 6774.4655 | 64.0914 | 0 | 0 | 6774.4655 | 16008.8916 | 16072.983
| 19956812 | 2032 | HSM003 | 6774.4655 | 64.0914 | 0 | 0 | 6774.4655 | 16008.8916 | 16072.983
| 19956812 | 2033 | HSM003 | 6774.4655 | 64.0914 | 0 | 0 | 6774.4655 | 16008.8916 | 16072.983
| 19956812 | 2034 | HSM003 | 6774.4655 | 64.0914 | 0 | 0 | 6774.4655 | 16008.8916 | 16072.983
| 19973422 | 2023 | HSM003 | 0 | 0 | 0 | 0 | 0 | 23144.1216 | 23144.1216
| 19973422 | 2024 | HSM003 | 0 | 0 | 0 | 0 | 0 | 23144.1216 | 23144.1216
| 19973422 | 2025 | HSM003 | 0 | 0 | 0 | 0 | 0 | 23144.1216 | 23144.1216
| 19973422 | 2026 | HSM003 | 0 | 0 | 0 | 0 | 0 | 23144.1216 | 23144.1216
| 19973422 | 2027 | HSM003 | 270.9785 | 3.5245 | 0 | 0 | 270.9785 | 23144.1216 | 23147.6461
| 19973422 | 2028 | HSM003 | 270.9785 | 3.5245 | 0 | 0 | 270.9785 | 23144.1216 | 23147.6461
| 19973422 | 2029 | HSM003 | 270.9785 | 3.5245 | 0 | 0 | 270.9785 | 23144.1216 | 23147.6461
| 19973422 | 2030 | HSM003 | 270.9785 | 3.5245 | 0 | 0 | 270.9785 | 23144.1216 | 23147.6461
| 19973422 | 2031 | HSM003 | 270.9785 | 3.5245 | 0 | 0 | 270.9785 | 23144.1216 | 23147.6461
| 19973422 | 2032 | HSM003 | 270.9785 | 3.5245 | 0 | 0 | 270.9785 | 23144.1216 | 23147.6461
| 19973422 | 2033 | HSM003 | 270.9785 | 3.5245 | 0 | 0 | 270.9785 | 23144.1216 | 23147.6461
| 19973422 | 2034 | HSM003 | 270.9785 | 3.5245 | 0 | 0 | 270.9785 | 23144.1216 | 23147.6461
| 19973722 | 2023 | HSM003 | 3865.0707 | 0 | 0 | 0 | 3865.0707 | 18074.065 | 18074.065
| 19973722 | 2024 | HSM003 | 4119.5081 | 60.4593 | 0 | 0 | 4119.5081 | 18074.065 | 18134.5243
| 19973722 | 2025 | HSM003 | 5650.7528 | 96.387 | 0 | 0 | 5650.7528 | 18074.065 | 18170.452
| 19973722 | 2026 | HSM003 | 10353.0031 | 96.0763 | 0 | 0 | 10353.0031 | 18074.065 | 18170.1413
| 19973722 | 2027 | HSM003 | 15119.8806 | 112.9709 | 0 | 0 | 15119.8806 | 18074.065 | 18187.0359
| 19973722 | 2028 | HSM003 | 15119.8806 | 112.9709 | 0 | 0 | 15119.8806 | 18074.065 | 18187.0359
| 19973722 | 2029 | HSM003 | 15119.8806 | 112.9709 | 0 | 0 | 15119.8806 | 18074.065 | 18187.0359
| 19973722 | 2030 | HSM003 | 15119.8806 | 112.9709 | 0 | 0 | 15119.8806 | 18074.065 | 18187.0359
| 19973722 | 2031 | HSM003 | 15119.8806 | 112.9709 | 0 | 0 | 15119.8806 | 18074.065 | 18187.0359
| 19973722 | 2032 | HSM003 | 15119.8806 | 112.9709 | 0 | 0 | 15119.8806 | 18074.065 | 18187.0359
| 19973722 | 2033 | HSM003 | 15119.8806 | 112.9709 | 0 | 0 | 15119.8806 | 18074.065 | 18187.0359
| 19973722 | 2034 | HSM003 | 15119.8806 | 112.9709 | 0 | 0 | 15119.8806 | 18074.065 | 18187.0359
| 19973762 | 2023 | HSM003 | 1704.7412 | 0 | 0 | 0 | 1704.7412 | 1607.676 | 1607.676
| 19973762 | 2024 | HSM003 | 1723.4656 | 29.7821 | 0 | 0 | 1723.4656 | 1607.676 | 1637.4581
| 19973762 | 2025 | HSM003 | 1810.0703 | 31.96 | 0 | 0 | 1810.0703 | 1607.676 | 1639.6359
| 19973762 | 2026 | HSM003 | 1902.2471 | 17.4917 | 0 | 0 | 1902.2471 | 1607.676 | 1625.1677
| 19973762 | 2027 | HSM003 | 1918.5268 | 14.7128 | 0 | 0 | 1918.5268 | 1607.676 | 1622.3888
| 19973762 | 2028 | HSM003 | 1918.5268 | 14.7128 | 0 | 0 | 1918.5268 | 1607.676 | 1622.3888
| 19973762 | 2029 | HSM003 | 1918.5268 | 14.7128 | 0 | 0 | 1918.5268 | 1607.676 | 1622.3888
| 19973762 | 2030 | HSM003 | 1918.5268 | 14.7128 | 0 | 0 | 1918.5268 | 1607.676 | 1622.3888
| 19973762 | 2031 | HSM003 | 1918.5268 | 14.7128 | 0 | 0 | 1918.5268 | 1607.676 | 1622.3888
| 19973762 | 2032 | HSM003 | 1918.5268 | 14.7128 | 0 | 0 | 1918.5268 | 1607.676 | 1622.3888
| 19973762 | 2033 | HSM003 | 1918.5268 | 14.7128 | 0 | 0 | 1918.5268 | 1607.676 | 1622.3888
| 19973762 | 2034 | HSM003 | 1918.5268 | 14.7128 | 0 | 0 | 1918.5268 | 1607.676 | 1622.3888
| 19974693 | 2023 | HSM003 | 13.5038 | 0 | 0 | 0 | 13.5038 | 13867.7619 | 13867.7619
| 19974693 | 2024 | HSM003 | 15.1305 | 0.30245 | 0 | 0 | 15.1305 | 13867.7619 | 13868.0643
| 19974693 | 2025 | HSM003 | 19.0941 | 0.44706 | 0 | 0 | 19.0941 | 13867.7619 | 13868.2089
| 19974693 | 2026 | HSM003 | 37.5296 | 0.10378 | 0 | 0 | 37.5296 | 13867.7619 | 13867.8656
| 19974693 | 2027 | HSM003 | 97.7809 | 0.43244 | 0 | 0 | 97.7809 | 13867.7619 | 13868.1943
| 19974693 | 2028 | HSM003 | 97.7809 | 0.43244 | 0 | 0 | 97.7809 | 13867.7619 | 13868.1943
| 19974693 | 2029 | HSM003 | 97.7809 | 0.43244 | 0 | 0 | 97.7809 | 13867.7619 | 13868.1943
| 19974693 | 2030 | HSM003 | 97.7809 | 0.43244 | 0 | 0 | 97.7809 | 13867.7619 | 13868.1943
| 19974693 | 2031 | HSM003 | 97.7809 | 0.43244 | 0 | 0 | 97.7809 | 13867.7619 | 13868.1943
| 19974693 | 2032 | HSM003 | 97.7809 | 0.43244 | 0 | 0 | 97.7809 | 13867.7619 | 13868.1943
| 19974693 | 2033 | HSM003 | 97.7809 | 0.43244 | 0 | 0 | 97.7809 | 13867.7619 | 13868.1943
| 19974693 | 2034 | HSM003 | 97.7809 | 0.43244 | 0 | 0 | 97.7809 | 13867.7619 | 13868.1943
| 19979297 | 2023 | HSM003 | 0 | 0 | 310.7896 | 12938.6617 | 310.7896 | 32155.3063 | 45093.968
| 19979297 | 2024 | HSM003 | 0 | 0 | 340.2347 | 14164.5059 | 340.2347 | 32155.3063 | 46319.8122
| 19979297 | 2025 | HSM003 | 0 | 0 | 287.7225 | 11978.34 | 287.7225 | 32155.3063 | 44133.6463
| 19979297 | 2026 | HSM003 | 0 | 0 | 264.8173 | 11024.7612 | 264.8173 | 32155.3063 | 43180.0675
| 19979297 | 2027 | HSM003 | 0 | 0 | 389.0067 | 16194.9602 | 389.0067 | 32155.3063 | 48350.2665
| 19979297 | 2028 | HSM003 | 0 | 0 | 389.0067 | 16194.9602 | 389.0067 | 32155.3063 | 48350.2665
| 19979297 | 2029 | HSM003 | 0 | 0 | 389.0067 | 16194.9602 | 389.0067 | 32155.3063 | 48350.2665
| 19979297 | 2030 | HSM003 | 0 | 0 | 389.0067 | 16194.9602 | 389.0067 | 32155.3063 | 48350.2665
| 19979297 | 2031 | HSM003 | 0 | 0 | 389.0067 | 16194.9602 | 389.0067 | 32155.3063 | 48350.2665
| 19979297 | 2032 | HSM003 | 0 | 0 | 389.0067 | 16194.9602 | 389.0067 | 32155.3063 | 48350.2665
| 19979297 | 2033 | HSM003 | 0 | 0 | 389.0067 | 16194.9602 | 389.0067 | 32155.3063 | 48350.2665
| 19979297 | 2034 | HSM003 | 0 | 0 | 389.0067 | 16194.9602 | 389.0067 | 32155.3063 | 48350.2665
| 19979558 | 2023 | HSM003 | 0 | 0 | 0 | 0 | 0 | 22666.5979 | 22666.5979
| 19979558 | 2024 | HSM003 | 0 | 0 | 0 | 0 | 0 | 22666.5979 | 22666.5979
| 19979558 | 2025 | HSM003 | 0 | 0 | 0 | 0 | 0 | 22666.5979 | 22666.5979
| 19979558 | 2026 | HSM003 | 0 | 0 | 0 | 0 | 0 | 22666.5979 | 22666.5979
| 19979558 | 2027 | HSM003 | 0 | 0 | 0 | 0 | 0 | 22666.5979 | 22666.5979
| 19979558 | 2028 | HSM003 | 0 | 0 | 0 | 0 | 0 | 22666.5979 | 22666.5979
| 19979558 | 2029 | HSM003 | 0 | 0 | 0 | 0 | 0 | 22666.5979 | 22666.5979
| 19979558 | 2030 | HSM003 | 0 | 0 | 0 | 0 | 0 | 22666.5979 | 22666.5979
| 19979558 | 2031 | HSM003 | 0 | 0 | 0 | 0 | 0 | 22666.5979 | 22666.5979
| 19979558 | 2032 | HSM003 | 0 | 0 | 0 | 0 | 0 | 22666.5979 | 22666.5979
| 19979558 | 2033 | HSM003 | 0 | 0 | 0 | 0 | 0 | 22666.5979 | 22666.5979
| 19979558 | 2034 | HSM003 | 0 | 0 | 0 | 0 | 0 | 22666.5979 | 22666.5979
| 19979653 | 2023 | HSM003 | 1824.0579 | 0 | 0 | 0 | 1824.0579 | 31451.9121 | 31451.9121
| 19979653 | 2024 | HSM003 | 2290.2621 | 38.2757 | 0 | 0 | 2290.2621 | 31451.9121 | 31490.1878
| 19979653 | 2025 | HSM003 | 2667.5902 | 40.2595 | 0 | 0 | 2667.5902 | 31451.9121 | 31492.1716
| 19979653 | 2026 | HSM003 | 7888.5577 | 54.6151 | 0 | 0 | 7888.5577 | 31451.9121 | 31506.5272
| 19979653 | 2027 | HSM003 | 9152.3835 | 53.0152 | 0 | 0 | 9152.3835 | 31451.9121 | 31504.9273
| 19979653 | 2028 | HSM003 | 9152.3835 | 53.0152 | 0 | 0 | 9152.3835 | 31451.9121 | 31504.9273
| 19979653 | 2029 | HSM003 | 9152.3835 | 53.0152 | 0 | 0 | 9152.3835 | 31451.9121 | 31504.9273
| 19979653 | 2030 | HSM003 | 9152.3835 | 53.0152 | 0 | 0 | 9152.3835 | 31451.9121 | 31504.9273
| 19979653 | 2031 | HSM003 | 9152.3835 | 53.0152 | 0 | 0 | 9152.3835 | 31451.9121 | 31504.9273
| 19979653 | 2032 | HSM003 | 9152.3835 | 53.0152 | 0 | 0 | 9152.3835 | 31451.9121 | 31504.9273
| 19979653 | 2033 | HSM003 | 9152.3835 | 53.0152 | 0 | 0 | 9152.3835 | 31451.9121 | 31504.9273
| 19979653 | 2034 | HSM003 | 9152.3835 | 53.0152 | 0 | 0 | 9152.3835 | 31451.9121 | 31504.9273
| 20495874 | 2023 | HSM003 | 0 | 0 | 0 | 0 | 0 | 1570.2825 | 1570.2825
| 20495874 | 2024 | HSM003 | 0 | 0 | 0 | 0 | 0 | 1570.2825 | 1570.2825
| 20495874 | 2025 | HSM003 | 0 | 0 | 0 | 0 | 0 | 1570.2825 | 1570.2825
| 20495874 | 2026 | HSM003 | 0 | 0 | 0 | 0 | 0 | 1570.2825 | 1570.2825
| 20495874 | 2027 | HSM003 | 0 | 0 | 0 | 0 | 0 | 1570.2825 | 1570.2825
| 20495874 | 2028 | HSM003 | 0 | 0 | 0 | 0 | 0 | 1570.2825 | 1570.2825
| 20495874 | 2029 | HSM003 | 0 | 0 | 0 | 0 | 0 | 1570.2825 | 1570.2825
| 20495874 | 2030 | HSM003 | 0 | 0 | 0 | 0 | 0 | 1570.2825 | 1570.2825
| 20495874 | 2031 | HSM003 | 0 | 0 | 0 | 0 | 0 | 1570.2825 | 1570.2825
| 20495874 | 2032 | HSM003 | 0 | 0 | 0 | 0 | 0 | 1570.2825 | 1570.2825
| 20495874 | 2033 | HSM003 | 0 | 0 | 0 | 0 | 0 | 1570.2825 | 1570.2825
| 20495874 | 2034 | HSM003 | 0 | 0 | 0 | 0 | 0 | 1570.2825 | 1570.2825
| 20496045 | 2023 | HSM003 | 119.9083 | 0 | 0 | 0 | 119.9083 | 23940.4782 | 23940.4782
| 20496045 | 2024 | HSM003 | 113.8086 | 3.6821 | 0 | 0 | 113.8086 | 23940.4782 | 23944.1603
| 20496045 | 2025 | HSM003 | 119.4141 | 3.6628 | 0 | 0 | 119.4141 | 23940.4782 | 23944.1409
| 20496045 | 2026 | HSM003 | 97.2103 | 1.5991 | 0 | 0 | 97.2103 | 23940.4782 | 23942.0773
| 20496045 | 2027 | HSM003 | 102.6953 | 1.4881 | 0 | 0 | 102.6953 | 23940.4782 | 23941.9663
| 20496045 | 2028 | HSM003 | 102.6953 | 1.4881 | 0 | 0 | 102.6953 | 23940.4782 | 23941.9663
| 20496045 | 2029 | HSM003 | 102.6953 | 1.4881 | 0 | 0 | 102.6953 | 23940.4782 | 23941.9663
| 20496045 | 2030 | HSM003 | 102.6953 | 1.4881 | 0 | 0 | 102.6953 | 23940.4782 | 23941.9663
| 20496045 | 2031 | HSM003 | 102.6953 | 1.4881 | 0 | 0 | 102.6953 | 23940.4782 | 23941.9663
| 20496045 | 2032 | HSM003 | 102.6953 | 1.4881 | 0 | 0 | 102.6953 | 23940.4782 | 23941.9663
| 20496045 | 2033 | HSM003 | 102.6953 | 1.4881 | 0 | 0 | 102.6953 | 23940.4782 | 23941.9663
| 20496045 | 2034 | HSM003 | 102.6953 | 1.4881 | 0 | 0 | 102.6953 | 23940.4782 | 23941.9663
| 20505951 | 2023 | HSM003 | 46.5681 | 0 | 0 | 0 | 46.5681 | 8634.9127 | 8634.9127
| 20505951 | 2024 | HSM003 | 50.0313 | 0.65732 | 0 | 0 | 50.0313 | 8634.9127 | 8635.57
| 20505951 | 2025 | HSM003 | 65.6344 | 0.80579 | 0 | 0 | 65.6344 | 8634.9127 | 8635.7184
| 20505951 | 2026 | HSM003 | 637.4052 | 4.0758 | 0 | 0 | 637.4052 | 8634.9127 | 8638.9885
| 20505951 | 2027 | HSM003 | 4309.6857 | 27.332 | 0 | 0 | 4309.6857 | 8634.9127 | 8662.2447
| 20505951 | 2028 | HSM003 | 4309.6857 | 27.332 | 0 | 0 | 4309.6857 | 8634.9127 | 8662.2447
| 20505951 | 2029 | HSM003 | 4309.6857 | 27.332 | 0 | 0 | 4309.6857 | 8634.9127 | 8662.2447
| 20505951 | 2030 | HSM003 | 4309.6857 | 27.332 | 0 | 0 | 4309.6857 | 8634.9127 | 8662.2447
| 20505951 | 2031 | HSM003 | 4309.6857 | 27.332 | 0 | 0 | 4309.6857 | 8634.9127 | 8662.2447
| 20505951 | 2032 | HSM003 | 4309.6857 | 27.332 | 0 | 0 | 4309.6857 | 8634.9127 | 8662.2447
| 20505951 | 2033 | HSM003 | 4309.6857 | 27.332 | 0 | 0 | 4309.6857 | 8634.9127 | 8662.2447
| 20505951 | 2034 | HSM003 | 4309.6857 | 27.332 | 0 | 0 | 4309.6857 | 8634.9127 | 8662.2447
| 20609946 | 2023 | HSM003 | 0 | 0 | 0 | 0 | 0 | 19758.6426 | 19758.6426
| 20609946 | 2024 | HSM003 | 0 | 0 | 0 | 0 | 0 | 19758.6426 | 19758.6426
| 20609946 | 2025 | HSM003 | 0 | 0 | 0 | 0 | 0 | 19758.6426 | 19758.6426
| 20609946 | 2026 | HSM003 | 0 | 0 | 0 | 0 | 0 | 19758.6426 | 19758.6426
| 20609946 | 2027 | HSM003 | 0 | 0 | 0 | 0 | 0 | 19758.6426 | 19758.6426
| 20609946 | 2028 | HSM003 | 0 | 0 | 0 | 0 | 0 | 19758.6426 | 19758.6426
| 20609946 | 2029 | HSM003 | 0 | 0 | 0 | 0 | 0 | 19758.6426 | 19758.6426
| 20609946 | 2030 | HSM003 | 0 | 0 | 0 | 0 | 0 | 19758.6426 | 19758.6426
| 20609946 | 2031 | HSM003 | 0 | 0 | 0 | 0 | 0 | 19758.6426 | 19758.6426
| 20609946 | 2032 | HSM003 | 0 | 0 | 0 | 0 | 0 | 19758.6426 | 19758.6426
| 20609946 | 2033 | HSM003 | 0 | 0 | 0 | 0 | 0 | 19758.6426 | 19758.6426
| 20609946 | 2034 | HSM003 | 0 | 0 | 0 | 0 | 0 | 19758.6426 | 19758.6426
| 73764748 | 2023 | HSM003 | 3446.1768 | 0 | 0 | 0 | 3446.1768 | 24454.4516 | 24454.4516
| 73764748 | 2024 | HSM003 | 3449.2351 | 45.7807 | 0 | 0 | 3449.2351 | 24454.4516 | 24500.2322
| 73764748 | 2025 | HSM003 | 4107.281 | 65.9364 | 0 | 0 | 4107.281 | 24454.4516 | 24520.388
| 73764748 | 2026 | HSM003 | 5070.8563 | 46.5557 | 0 | 0 | 5070.8563 | 24454.4516 | 24501.0073
| 73764748 | 2027 | HSM003 | 4471.1162 | 31.1038 | 0 | 0 | 4471.1162 | 24454.4516 | 24485.5554
| 73764748 | 2028 | HSM003 | 4471.1162 | 31.1038 | 0 | 0 | 4471.1162 | 24454.4516 | 24485.5554
| 73764748 | 2029 | HSM003 | 4471.1162 | 31.1038 | 0 | 0 | 4471.1162 | 24454.4516 | 24485.5554
| 73764748 | 2030 | HSM003 | 4471.1162 | 31.1038 | 0 | 0 | 4471.1162 | 24454.4516 | 24485.5554
| 73764748 | 2031 | HSM003 | 4471.1162 | 31.1038 | 0 | 0 | 4471.1162 | 24454.4516 | 24485.5554
| 73764748 | 2032 | HSM003 | 4471.1162 | 31.1038 | 0 | 0 | 4471.1162 | 24454.4516 | 24485.5554
| 73764748 | 2033 | HSM003 | 4471.1162 | 31.1038 | 0 | 0 | 4471.1162 | 24454.4516 | 24485.5554
| 73764748 | 2034 | HSM003 | 4471.1162 | 31.1038 | 0 | 0 | 4471.1162 | 24454.4516 | 24485.5554
| 74226142 | 2023 | HSM003 | 533.8875 | 0 | 0 | 0 | 533.8875 | 10459.5811 | 10459.5811
| 74226142 | 2024 | HSM003 | 548.6013 | 9.3814 | 0 | 0 | 548.6013 | 10459.5811 | 10468.9625
| 74226142 | 2025 | HSM003 | 740.0621 | 12.6756 | 0 | 0 | 740.0621 | 10459.5811 | 10472.2567
| 74226142 | 2026 | HSM003 | 814.8795 | 7.1569 | 0 | 0 | 814.8795 | 10459.5811 | 10466.7379
| 74226142 | 2027 | HSM003 | 809.4254 | 7.478 | 0 | 0 | 809.4254 | 10459.5811 | 10467.0591
| 74226142 | 2028 | HSM003 | 809.4254 | 7.478 | 0 | 0 | 809.4254 | 10459.5811 | 10467.0591
| 74226142 | 2029 | HSM003 | 809.4254 | 7.478 | 0 | 0 | 809.4254 | 10459.5811 | 10467.0591
| 74226142 | 2030 | HSM003 | 809.4254 | 7.478 | 0 | 0 | 809.4254 | 10459.5811 | 10467.0591
| 74226142 | 2031 | HSM003 | 809.4254 | 7.478 | 0 | 0 | 809.4254 | 10459.5811 | 10467.0591
| 74226142 | 2032 | HSM003 | 809.4254 | 7.478 | 0 | 0 | 809.4254 | 10459.5811 | 10467.0591
| 74226142 | 2033 | HSM003 | 809.4254 | 7.478 | 0 | 0 | 809.4254 | 10459.5811 | 10467.0591
| 74226142 | 2034 | HSM003 | 809.4254 | 7.478 | 0 | 0 | 809.4254 | 10459.5811 | 10467.0591
| 75520723 | 2023 | HSM003 | 0 | 0 | 0 | 0 | 0 | 29786.6467 | 29786.6467
| 75520723 | 2024 | HSM003 | 0 | 0 | 0.02099 | 0.87384 | 0.02099 | 29786.6467 | 29787.5206
| 75520723 | 2025 | HSM003 | 0 | 0 | 0.0276 | 1.149 | 0.0276 | 29786.6467 | 29787.7957
| 75520723 | 2026 | HSM003 | 0 | 0 | 0 | 0 | 0 | 29786.6467 | 29786.6467
| 75520723 | 2027 | HSM003 | 0 | 0 | 0 | 0 | 0 | 29786.6467 | 29786.6467
| 75520723 | 2028 | HSM003 | 0 | 0 | 0 | 0 | 0 | 29786.6467 | 29786.6467
| 75520723 | 2029 | HSM003 | 0 | 0 | 0 | 0 | 0 | 29786.6467 | 29786.6467
| 75520723 | 2030 | HSM003 | 0 | 0 | 0 | 0 | 0 | 29786.6467 | 29786.6467
| 75520723 | 2031 | HSM003 | 0 | 0 | 0 | 0 | 0 | 29786.6467 | 29786.6467
| 75520723 | 2032 | HSM003 | 0 | 0 | 0 | 0 | 0 | 29786.6467 | 29786.6467
| 75520723 | 2033 | HSM003 | 0 | 0 | 0 | 0 | 0 | 29786.6467 | 29786.6467
| 75520723 | 2034 | HSM003 | 0 | 0 | 0 | 0 | 0 | 29786.6467 | 29786.6467
| 128756100 | 2023 | HSM003 | 0 | 0 | 0 | 0 | 0 | 6746.7004 | 6746.7004
| 128756100 | 2024 | HSM003 | 0 | 0 | 0 | 0 | 0 | 6746.7004 | 6746.7004
| 128756100 | 2025 | HSM003 | 0 | 0 | 0 | 0 | 0 | 6746.7004 | 6746.7004
| 128756100 | 2026 | HSM003 | 0 | 0 | 0 | 0 | 0 | 6746.7004 | 6746.7004
| 128756100 | 2027 | HSM003 | 0 | 0 | 0 | 0 | 0 | 6746.7004 | 6746.7004
| 128756100 | 2028 | HSM003 | 0 | 0 | 0 | 0 | 0 | 6746.7004 | 6746.7004
| 128756100 | 2029 | HSM003 | 0 | 0 | 0 | 0 | 0 | 6746.7004 | 6746.7004
| 128756100 | 2030 | HSM003 | 0 | 0 | 0 | 0 | 0 | 6746.7004 | 6746.7004
| 128756100 | 2031 | HSM003 | 0 | 0 | 0 | 0 | 0 | 6746.7004 | 6746.7004
| 128756100 | 2032 | HSM003 | 0 | 0 | 0 | 0 | 0 | 6746.7004 | 6746.7004
| 128756100 | 2033 | HSM003 | 0 | 0 | 0 | 0 | 0 | 6746.7004 | 6746.7004
| 128756100 | 2034 | HSM003 | 0 | 0 | 0 | 0 | 0 | 6746.7004 | 6746.7004
| 161129189 | 2023 | HSM003 | 0 | 0 | 0 | 0 | 0 | 18190.4649 | 18190.4649
| 161129189 | 2024 | HSM003 | 0 | 0 | 0 | 0 | 0 | 18190.4649 | 18190.4649
| 161129189 | 2025 | HSM003 | 0 | 0 | 0 | 0 | 0 | 18190.4649 | 18190.4649
| 161129189 | 2026 | HSM003 | 3.3876 | 0.0038637 | 0 | 0 | 3.3876 | 18190.4649 | 18190.4687
| 161129189 | 2027 | HSM003 | 0 | 0 | 0 | 0 | 0 | 18190.4649 | 18190.4649
| 161129189 | 2028 | HSM003 | 0 | 0 | 0 | 0 | 0 | 18190.4649 | 18190.4649
| 161129189 | 2029 | HSM003 | 0 | 0 | 0 | 0 | 0 | 18190.4649 | 18190.4649
| 161129189 | 2030 | HSM003 | 0 | 0 | 0 | 0 | 0 | 18190.4649 | 18190.4649
| 161129189 | 2031 | HSM003 | 0 | 0 | 0 | 0 | 0 | 18190.4649 | 18190.4649
| 161129189 | 2032 | HSM003 | 0 | 0 | 0 | 0 | 0 | 18190.4649 | 18190.4649
| 161129189 | 2033 | HSM003 | 0 | 0 | 0 | 0 | 0 | 18190.4649 | 18190.4649
| 161129189 | 2034 | HSM003 | 0 | 0 | 0 | 0 | 0 | 18190.4649 | 18190.4649
| 200921983 | 2023 | HSM003 | 0 | 0 | 0 | 0 | 0 | 31129.7696 | 31129.7696
| 200921983 | 2024 | HSM003 | 0 | 0 | 0 | 0 | 0 | 31129.7696 | 31129.7696
| 200921983 | 2025 | HSM003 | 0 | 0 | 0 | 0 | 0 | 31129.7696 | 31129.7696
| 200921983 | 2026 | HSM003 | 0 | 0 | 0 | 0 | 0 | 31129.7696 | 31129.7696
| 200921983 | 2027 | HSM003 | 0 | 0 | 0 | 0 | 0 | 31129.7696 | 31129.7696
| 200921983 | 2028 | HSM003 | 0 | 0 | 0 | 0 | 0 | 31129.7696 | 31129.7696
| 200921983 | 2029 | HSM003 | 0 | 0 | 0 | 0 | 0 | 31129.7696 | 31129.7696
| 200921983 | 2030 | HSM003 | 0 | 0 | 0 | 0 | 0 | 31129.7696 | 31129.7696
| 200921983 | 2031 | HSM003 | 0 | 0 | 0 | 0 | 0 | 31129.7696 | 31129.7696
| 200921983 | 2032 | HSM003 | 0 | 0 | 0 | 0 | 0 | 31129.7696 | 31129.7696
| 200921983 | 2033 | HSM003 | 0 | 0 | 0 | 0 | 0 | 31129.7696 | 31129.7696
| 200921983 | 2034 | HSM003 | 0 | 0 | 0 | 0 | 0 | 31129.7696 | 31129.7696
| 203313132 | 2023 | HSM003 | 0 | 0 | 524.5479 | 21837.7546 | 524.5479 | 14884.9457 | 36722.7003
| 203313132 | 2024 | HSM003 | 0 | 0 | 594.8646 | 24765.1497 | 594.8646 | 14884.9457 | 39650.0954
| 203313132 | 2025 | HSM003 | 0 | 0 | 493.1716 | 20531.5115 | 493.1716 | 14884.9457 | 35416.4572
| 203313132 | 2026 | HSM003 | 0 | 0 | 467.3121 | 19454.937 | 467.3121 | 14884.9457 | 34339.8827
| 203313132 | 2027 | HSM003 | 0 | 0 | 485.3364 | 20205.318 | 485.3364 | 14884.9457 | 35090.2637
| 203313132 | 2028 | HSM003 | 0 | 0 | 485.3364 | 20205.318 | 485.3364 | 14884.9457 | 35090.2637
| 203313132 | 2029 | HSM003 | 0 | 0 | 485.3364 | 20205.318 | 485.3364 | 14884.9457 | 35090.2637
| 203313132 | 2030 | HSM003 | 0 | 0 | 485.3364 | 20205.318 | 485.3364 | 14884.9457 | 35090.2637
| 203313132 | 2031 | HSM003 | 0 | 0 | 485.3364 | 20205.318 | 485.3364 | 14884.9457 | 35090.2637
| 203313132 | 2032 | HSM003 | 0 | 0 | 485.3364 | 20205.318 | 485.3364 | 14884.9457 | 35090.2637
| 203313132 | 2033 | HSM003 | 0 | 0 | 485.3364 | 20205.318 | 485.3364 | 14884.9457 | 35090.2637
| 203313132 | 2034 | HSM003 | 0 | 0 | 485.3364 | 20205.318 | 485.3364 | 14884.9457 | 35090.2637
| 19903967 | 2023 | HSM004 | 41672.9286 | 0 | 2.632 | 109.5738 | 41675.5606 | 4757.3822 | 4866.9559
| 19903967 | 2024 | HSM004 | 43620.9395 | 991.0696 | 2.8626 | 119.174 | 43623.8021 | 4757.3822 | 5867.6258
| 19903967 | 2025 | HSM004 | 51303.9256 | 1436.6369 | 1.3832 | 57.5845 | 51305.3088 | 4757.3822 | 6251.6036
| 19903967 | 2026 | HSM004 | 76802.1768 | 1481.5923 | 0.35211 | 14.659 | 76802.5289 | 4757.3822 | 6253.6334
| 19903967 | 2027 | HSM004 | 76802.1768 | 1481.5923 | 0.35211 | 14.659 | 76802.5289 | 4757.3822 | 6253.6334
| 19903967 | 2028 | HSM004 | 76802.1768 | 1481.5923 | 0.35211 | 14.659 | 76802.5289 | 4757.3822 | 6253.6334
| 19903967 | 2029 | HSM004 | 76802.1768 | 1481.5923 | 0.35211 | 14.659 | 76802.5289 | 4757.3822 | 6253.6334
| 19903967 | 2030 | HSM004 | 76802.1768 | 1481.5923 | 0.35211 | 14.659 | 76802.5289 | 4757.3822 | 6253.6334
| 19903967 | 2031 | HSM004 | 76802.1768 | 1481.5923 | 0.35211 | 14.659 | 76802.5289 | 4757.3822 | 6253.6334
| 19903967 | 2032 | HSM004 | 76802.1768 | 1481.5923 | 0.35211 | 14.659 | 76802.5289 | 4757.3822 | 6253.6334
| 19903967 | 2033 | HSM004 | 76802.1768 | 1481.5923 | 0.35211 | 14.659 | 76802.5289 | 4757.3822 | 6253.6334
| 19903967 | 2034 | HSM004 | 76802.1768 | 1481.5923 | 0.35211 | 14.659 | 76802.5289 | 4757.3822 | 6253.6334
| 19904337 | 2023 | HSM004 | 0 | 0 | 5.7112 | 237.7666 | 5.7112 | 9044.3647 | 9282.1313
| 19904337 | 2024 | HSM004 | 0 | 0 | 0.49738 | 20.7066 | 0.49738 | 9044.3647 | 9065.0713
| 19904337 | 2025 | HSM004 | 0 | 0 | 0.1123 | 4.6751 | 0.1123 | 9044.3647 | 9049.0397
| 19904337 | 2026 | HSM004 | 5.6867 | 0.0065431 | 0.26249 | 10.928 | 5.9491 | 9044.3647 | 9055.2992
| 19904337 | 2027 | HSM004 | 5.6867 | 0.0065431 | 0.26249 | 10.928 | 5.9491 | 9044.3647 | 9055.2992
| 19904337 | 2028 | HSM004 | 5.6867 | 0.0065431 | 0.26249 | 10.928 | 5.9491 | 9044.3647 | 9055.2992
| 19904337 | 2029 | HSM004 | 5.6867 | 0.0065431 | 0.26249 | 10.928 | 5.9491 | 9044.3647 | 9055.2992
| 19904337 | 2030 | HSM004 | 5.6867 | 0.0065431 | 0.26249 | 10.928 | 5.9491 | 9044.3647 | 9055.2992
| 19904337 | 2031 | HSM004 | 5.6867 | 0.0065431 | 0.26249 | 10.928 | 5.9491 | 9044.3647 | 9055.2992
| 19904337 | 2032 | HSM004 | 5.6867 | 0.0065431 | 0.26249 | 10.928 | 5.9491 | 9044.3647 | 9055.2992
| 19904337 | 2033 | HSM004 | 5.6867 | 0.0065431 | 0.26249 | 10.928 | 5.9491 | 9044.3647 | 9055.2992
| 19904337 | 2034 | HSM004 | 5.6867 | 0.0065431 | 0.26249 | 10.928 | 5.9491 | 9044.3647 | 9055.2992
| 19923657 | 2023 | HSM004 | 0 | 0 | 0 | 0 | 0 | 3120.4721 | 3120.4721
| 19923657 | 2024 | HSM004 | 0 | 0 | 0 | 0 | 0 | 3120.4721 | 3120.4721
| 19923657 | 2025 | HSM004 | 0 | 0 | 0 | 0 | 0 | 3120.4721 | 3120.4721
| 19923657 | 2026 | HSM004 | 0 | 0 | 0 | 0 | 0 | 3120.4721 | 3120.4721
| 19923657 | 2027 | HSM004 | 0 | 0 | 0 | 0 | 0 | 3120.4721 | 3120.4721
| 19923657 | 2028 | HSM004 | 0 | 0 | 0 | 0 | 0 | 3120.4721 | 3120.4721
| 19923657 | 2029 | HSM004 | 0 | 0 | 0 | 0 | 0 | 3120.4721 | 3120.4721
| 19923657 | 2030 | HSM004 | 0 | 0 | 0 | 0 | 0 | 3120.4721 | 3120.4721
| 19923657 | 2031 | HSM004 | 0 | 0 | 0 | 0 | 0 | 3120.4721 | 3120.4721
| 19923657 | 2032 | HSM004 | 0 | 0 | 0 | 0 | 0 | 3120.4721 | 3120.4721
| 19923657 | 2033 | HSM004 | 0 | 0 | 0 | 0 | 0 | 3120.4721 | 3120.4721
| 19923657 | 2034 | HSM004 | 0 | 0 | 0 | 0 | 0 | 3120.4721 | 3120.4721
| 19923796 | 2023 | HSM004 | 0 | 0 | 2240.7172 | 93284.5882 | 2240.7172 | 9679.2222 | 102963.8104
| 19923796 | 2024 | HSM004 | 0 | 0 | 2286.6215 | 95195.6545 | 2286.6215 | 9679.2222 | 104874.8768
| 19923796 | 2025 | HSM004 | 0 | 0 | 1764.9554 | 73477.8745 | 1764.9554 | 9679.2222 | 83157.0967
| 19923796 | 2026 | HSM004 | 0 | 0 | 1643.4328 | 68418.6957 | 1643.4328 | 9679.2222 | 78097.9179
| 19923796 | 2027 | HSM004 | 0 | 0 | 1643.4328 | 68418.6957 | 1643.4328 | 9679.2222 | 78097.9179
| 19923796 | 2028 | HSM004 | 0 | 0 | 1643.4328 | 68418.6957 | 1643.4328 | 9679.2222 | 78097.9179
| 19923796 | 2029 | HSM004 | 0 | 0 | 1643.4328 | 68418.6957 | 1643.4328 | 9679.2222 | 78097.9179
| 19923796 | 2030 | HSM004 | 0 | 0 | 1643.4328 | 68418.6957 | 1643.4328 | 9679.2222 | 78097.9179
| 19923796 | 2031 | HSM004 | 0 | 0 | 1643.4328 | 68418.6957 | 1643.4328 | 9679.2222 | 78097.9179
| 19923796 | 2032 | HSM004 | 0 | 0 | 1643.4328 | 68418.6957 | 1643.4328 | 9679.2222 | 78097.9179
| 19923796 | 2033 | HSM004 | 0 | 0 | 1643.4328 | 68418.6957 | 1643.4328 | 9679.2222 | 78097.9179
| 19923796 | 2034 | HSM004 | 0 | 0 | 1643.4328 | 68418.6957 | 1643.4328 | 9679.2222 | 78097.9179
| 19924342 | 2023 | HSM004 | 0 | 0 | 0.080798 | 3.3638 | 0.080798 | 50484.0024 | 50487.3662
| 19924342 | 2024 | HSM004 | 0 | 0 | 0.051966 | 2.1634 | 0.051966 | 50484.0024 | 50486.1659
| 19924342 | 2025 | HSM004 | 13.0004 | 0.35007 | 0 | 0 | 13.0004 | 50484.0024 | 50484.3525
| 19924342 | 2026 | HSM004 | 582.7117 | 2.6634 | 0 | 0 | 582.7117 | 50484.0024 | 50486.6658
| 19924342 | 2027 | HSM004 | 582.7117 | 2.6634 | 0 | 0 | 582.7117 | 50484.0024 | 50486.6658
| 19924342 | 2028 | HSM004 | 582.7117 | 2.6634 | 0 | 0 | 582.7117 | 50484.0024 | 50486.6658
| 19924342 | 2029 | HSM004 | 582.7117 | 2.6634 | 0 | 0 | 582.7117 | 50484.0024 | 50486.6658
| 19924342 | 2030 | HSM004 | 582.7117 | 2.6634 | 0 | 0 | 582.7117 | 50484.0024 | 50486.6658
| 19924342 | 2031 | HSM004 | 582.7117 | 2.6634 | 0 | 0 | 582.7117 | 50484.0024 | 50486.6658
| 19924342 | 2032 | HSM004 | 582.7117 | 2.6634 | 0 | 0 | 582.7117 | 50484.0024 | 50486.6658
| 19924342 | 2033 | HSM004 | 582.7117 | 2.6634 | 0 | 0 | 582.7117 | 50484.0024 | 50486.6658
| 19924342 | 2034 | HSM004 | 582.7117 | 2.6634 | 0 | 0 | 582.7117 | 50484.0024 | 50486.6658
| 19925177 | 2023 | HSM004 | 0 | 0 | 0 | 0 | 0 | 1426.4678 | 1426.4678
| 19925177 | 2024 | HSM004 | 0 | 0 | 0 | 0 | 0 | 1426.4678 | 1426.4678
| 19925177 | 2025 | HSM004 | 11.1693 | 0.10879 | 0 | 0 | 11.1693 | 1426.4678 | 1426.5766
| 19925177 | 2026 | HSM004 | 261.1173 | 1.0451 | 0 | 0 | 261.1173 | 1426.4678 | 1427.5128
| 19925177 | 2027 | HSM004 | 261.1173 | 1.0451 | 0 | 0 | 261.1173 | 1426.4678 | 1427.5128
| 19925177 | 2028 | HSM004 | 261.1173 | 1.0451 | 0 | 0 | 261.1173 | 1426.4678 | 1427.5128
| 19925177 | 2029 | HSM004 | 261.1173 | 1.0451 | 0 | 0 | 261.1173 | 1426.4678 | 1427.5128
| 19925177 | 2030 | HSM004 | 261.1173 | 1.0451 | 0 | 0 | 261.1173 | 1426.4678 | 1427.5128
| 19925177 | 2031 | HSM004 | 261.1173 | 1.0451 | 0 | 0 | 261.1173 | 1426.4678 | 1427.5128
| 19925177 | 2032 | HSM004 | 261.1173 | 1.0451 | 0 | 0 | 261.1173 | 1426.4678 | 1427.5128
| 19925177 | 2033 | HSM004 | 261.1173 | 1.0451 | 0 | 0 | 261.1173 | 1426.4678 | 1427.5128
| 19925177 | 2034 | HSM004 | 261.1173 | 1.0451 | 0 | 0 | 261.1173 | 1426.4678 | 1427.5128
| 19926947 | 2023 | HSM004 | 0 | 0 | 0 | 0 | 0 | 8306.5537 | 8306.5537
| 19926947 | 2024 | HSM004 | 0 | 0 | 0 | 0 | 0 | 8306.5537 | 8306.5537
| 19926947 | 2025 | HSM004 | 0 | 0 | 0 | 0 | 0 | 8306.5537 | 8306.5537
| 19926947 | 2026 | HSM004 | 0 | 0 | 0 | 0 | 0 | 8306.5537 | 8306.5537
| 19926947 | 2027 | HSM004 | 0 | 0 | 0 | 0 | 0 | 8306.5537 | 8306.5537
| 19926947 | 2028 | HSM004 | 0 | 0 | 0 | 0 | 0 | 8306.5537 | 8306.5537
| 19926947 | 2029 | HSM004 | 0 | 0 | 0 | 0 | 0 | 8306.5537 | 8306.5537
| 19926947 | 2030 | HSM004 | 0 | 0 | 0 | 0 | 0 | 8306.5537 | 8306.5537
| 19926947 | 2031 | HSM004 | 0 | 0 | 0 | 0 | 0 | 8306.5537 | 8306.5537
| 19926947 | 2032 | HSM004 | 0 | 0 | 0 | 0 | 0 | 8306.5537 | 8306.5537
| 19926947 | 2033 | HSM004 | 0 | 0 | 0 | 0 | 0 | 8306.5537 | 8306.5537
| 19926947 | 2034 | HSM004 | 0 | 0 | 0 | 0 | 0 | 8306.5537 | 8306.5537
| 19927300 | 2023 | HSM004 | 0 | 0 | 99.5992 | 4146.473 | 99.5992 | 20948.6644 | 25095.1374
| 19927300 | 2024 | HSM004 | 0 | 0 | 107.0432 | 4456.3786 | 107.0432 | 20948.6644 | 25405.0431
| 19927300 | 2025 | HSM004 | 0 | 0 | 99.4987 | 4142.2895 | 99.4987 | 20948.6644 | 25090.9539
| 19927300 | 2026 | HSM004 | 0 | 0 | 90.3361 | 3760.835 | 90.3361 | 20948.6644 | 24709.4994
| 19927300 | 2027 | HSM004 | 0 | 0 | 90.3361 | 3760.835 | 90.3361 | 20948.6644 | 24709.4994
| 19927300 | 2028 | HSM004 | 0 | 0 | 90.3361 | 3760.835 | 90.3361 | 20948.6644 | 24709.4994
| 19927300 | 2029 | HSM004 | 0 | 0 | 90.3361 | 3760.835 | 90.3361 | 20948.6644 | 24709.4994
| 19927300 | 2030 | HSM004 | 0 | 0 | 90.3361 | 3760.835 | 90.3361 | 20948.6644 | 24709.4994
| 19927300 | 2031 | HSM004 | 0 | 0 | 90.3361 | 3760.835 | 90.3361 | 20948.6644 | 24709.4994
| 19927300 | 2032 | HSM004 | 0 | 0 | 90.3361 | 3760.835 | 90.3361 | 20948.6644 | 24709.4994
| 19927300 | 2033 | HSM004 | 0 | 0 | 90.3361 | 3760.835 | 90.3361 | 20948.6644 | 24709.4994
| 19927300 | 2034 | HSM004 | 0 | 0 | 90.3361 | 3760.835 | 90.3361 | 20948.6644 | 24709.4994
| 19927505 | 2023 | HSM004 | 0 | 0 | 584.2001 | 24321.1696 | 584.2001 | 44107.5027 | 68428.6723
| 19927505 | 2024 | HSM004 | 0 | 0 | 1160.0281 | 48293.7961 | 1160.0281 | 44107.5027 | 92401.2988
| 19927505 | 2025 | HSM004 | 0 | 0 | 998.4953 | 41568.9333 | 998.4953 | 44107.5027 | 85676.436
| 19927505 | 2026 | HSM004 | 0 | 0 | 4266.6636 | 177627.9255 | 4266.6636 | 44107.5027 | 221735.4282
| 19927505 | 2027 | HSM004 | 0 | 0 | 4266.6636 | 177627.9255 | 4266.6636 | 44107.5027 | 221735.4282
| 19927505 | 2028 | HSM004 | 0 | 0 | 4266.6636 | 177627.9255 | 4266.6636 | 44107.5027 | 221735.4282
| 19927505 | 2029 | HSM004 | 0 | 0 | 4266.6636 | 177627.9255 | 4266.6636 | 44107.5027 | 221735.4282
| 19927505 | 2030 | HSM004 | 0 | 0 | 4266.6636 | 177627.9255 | 4266.6636 | 44107.5027 | 221735.4282
| 19927505 | 2031 | HSM004 | 0 | 0 | 4266.6636 | 177627.9255 | 4266.6636 | 44107.5027 | 221735.4282
| 19927505 | 2032 | HSM004 | 0 | 0 | 4266.6636 | 177627.9255 | 4266.6636 | 44107.5027 | 221735.4282
| 19927505 | 2033 | HSM004 | 0 | 0 | 4266.6636 | 177627.9255 | 4266.6636 | 44107.5027 | 221735.4282
| 19927505 | 2034 | HSM004 | 0 | 0 | 4266.6636 | 177627.9255 | 4266.6636 | 44107.5027 | 221735.4282
| 20023138 | 2023 | HSM004 | 2721.1358 | 0 | 0 | 0 | 2721.1358 | 8168.388 | 8168.388
| 20023138 | 2024 | HSM004 | 2938.2068 | 65.3476 | 0 | 0 | 2938.2068 | 8168.388 | 8233.7356
| 20023138 | 2025 | HSM004 | 2967.7098 | 72.5772 | 0 | 0 | 2967.7098 | 8168.388 | 8240.9652
| 20023138 | 2026 | HSM004 | 4279.5769 | 51.3253 | 0 | 0 | 4279.5769 | 8168.388 | 8219.7134
| 20023138 | 2027 | HSM004 | 4279.5769 | 51.3253 | 0 | 0 | 4279.5769 | 8168.388 | 8219.7134
| 20023138 | 2028 | HSM004 | 4279.5769 | 51.3253 | 0 | 0 | 4279.5769 | 8168.388 | 8219.7134
| 20023138 | 2029 | HSM004 | 4279.5769 | 51.3253 | 0 | 0 | 4279.5769 | 8168.388 | 8219.7134
| 20023138 | 2030 | HSM004 | 4279.5769 | 51.3253 | 0 | 0 | 4279.5769 | 8168.388 | 8219.7134
| 20023138 | 2031 | HSM004 | 4279.5769 | 51.3253 | 0 | 0 | 4279.5769 | 8168.388 | 8219.7134
| 20023138 | 2032 | HSM004 | 4279.5769 | 51.3253 | 0 | 0 | 4279.5769 | 8168.388 | 8219.7134
| 20023138 | 2033 | HSM004 | 4279.5769 | 51.3253 | 0 | 0 | 4279.5769 | 8168.388 | 8219.7134
| 20023138 | 2034 | HSM004 | 4279.5769 | 51.3253 | 0 | 0 | 4279.5769 | 8168.388 | 8219.7134
| 20028152 | 2023 | HSM004 | 1762.0962 | 0 | 0 | 0 | 1762.0962 | 526.1975 | 526.1975
| 20028152 | 2024 | HSM004 | 1772.363 | 38.0828 | 0 | 0 | 1772.363 | 526.1975 | 564.2803
| 20028152 | 2025 | HSM004 | 1880.1533 | 48.1371 | 0 | 0 | 1880.1533 | 526.1975 | 574.3346
| 20028152 | 2026 | HSM004 | 1943.8765 | 34.5472 | 0 | 0 | 1943.8765 | 526.1975 | 560.7447
| 20028152 | 2027 | HSM004 | 1943.8765 | 34.5472 | 0 | 0 | 1943.8765 | 526.1975 | 560.7447
| 20028152 | 2028 | HSM004 | 1943.8765 | 34.5472 | 0 | 0 | 1943.8765 | 526.1975 | 560.7447
| 20028152 | 2029 | HSM004 | 1943.8765 | 34.5472 | 0 | 0 | 1943.8765 | 526.1975 | 560.7447
| 20028152 | 2030 | HSM004 | 1943.8765 | 34.5472 | 0 | 0 | 1943.8765 | 526.1975 | 560.7447
| 20028152 | 2031 | HSM004 | 1943.8765 | 34.5472 | 0 | 0 | 1943.8765 | 526.1975 | 560.7447
| 20028152 | 2032 | HSM004 | 1943.8765 | 34.5472 | 0 | 0 | 1943.8765 | 526.1975 | 560.7447
| 20028152 | 2033 | HSM004 | 1943.8765 | 34.5472 | 0 | 0 | 1943.8765 | 526.1975 | 560.7447
| 20028152 | 2034 | HSM004 | 1943.8765 | 34.5472 | 0 | 0 | 1943.8765 | 526.1975 | 560.7447
| 20028291 | 2023 | HSM004 | 1098.2041 | 0 | 0 | 0 | 1098.2041 | 4812.0445 | 4812.0445
| 20028291 | 2024 | HSM004 | 1058.7769 | 17.6958 | 0 | 0 | 1058.7769 | 4812.0445 | 4829.7403
| 20028291 | 2025 | HSM004 | 1098.6107 | 24.3508 | 0 | 0 | 1098.6107 | 4812.0445 | 4836.3953
| 20028291 | 2026 | HSM004 | 4843.2645 | 42.6404 | 0 | 0 | 4843.2645 | 4812.0445 | 4854.6849
| 20028291 | 2027 | HSM004 | 4843.2645 | 42.6404 | 0 | 0 | 4843.2645 | 4812.0445 | 4854.6849
| 20028291 | 2028 | HSM004 | 4843.2645 | 42.6404 | 0 | 0 | 4843.2645 | 4812.0445 | 4854.6849
| 20028291 | 2029 | HSM004 | 4843.2645 | 42.6404 | 0 | 0 | 4843.2645 | 4812.0445 | 4854.6849
| 20028291 | 2030 | HSM004 | 4843.2645 | 42.6404 | 0 | 0 | 4843.2645 | 4812.0445 | 4854.6849
| 20028291 | 2031 | HSM004 | 4843.2645 | 42.6404 | 0 | 0 | 4843.2645 | 4812.0445 | 4854.6849
| 20028291 | 2032 | HSM004 | 4843.2645 | 42.6404 | 0 | 0 | 4843.2645 | 4812.0445 | 4854.6849
| 20028291 | 2033 | HSM004 | 4843.2645 | 42.6404 | 0 | 0 | 4843.2645 | 4812.0445 | 4854.6849
| 20028291 | 2034 | HSM004 | 4843.2645 | 42.6404 | 0 | 0 | 4843.2645 | 4812.0445 | 4854.6849
| 20496116 | 2023 | HSM004 | 5427.9031 | 0 | 0 | 0 | 5427.9031 | 9467.3262 | 9467.3262
| 20496116 | 2024 | HSM004 | 6589.0122 | 114.806 | 0 | 0 | 6589.0122 | 9467.3262 | 9582.1322
| 20496116 | 2025 | HSM004 | 12301.0479 | 229.9392 | 0 | 0 | 12301.0479 | 9467.3262 | 9697.2654
| 20496116 | 2026 | HSM004 | 23883.7457 | 252.8939 | 0 | 0 | 23883.7457 | 9467.3262 | 9720.2201
| 20496116 | 2027 | HSM004 | 23883.7457 | 252.8939 | 0 | 0 | 23883.7457 | 9467.3262 | 9720.2201
| 20496116 | 2028 | HSM004 | 23883.7457 | 252.8939 | 0 | 0 | 23883.7457 | 9467.3262 | 9720.2201
| 20496116 | 2029 | HSM004 | 23883.7457 | 252.8939 | 0 | 0 | 23883.7457 | 9467.3262 | 9720.2201
| 20496116 | 2030 | HSM004 | 23883.7457 | 252.8939 | 0 | 0 | 23883.7457 | 9467.3262 | 9720.2201
| 20496116 | 2031 | HSM004 | 23883.7457 | 252.8939 | 0 | 0 | 23883.7457 | 9467.3262 | 9720.2201
| 20496116 | 2032 | HSM004 | 23883.7457 | 252.8939 | 0 | 0 | 23883.7457 | 9467.3262 | 9720.2201
| 20496116 | 2033 | HSM004 | 23883.7457 | 252.8939 | 0 | 0 | 23883.7457 | 9467.3262 | 9720.2201
| 20496116 | 2034 | HSM004 | 23883.7457 | 252.8939 | 0 | 0 | 23883.7457 | 9467.3262 | 9720.2201
| 20496497 | 2023 | HSM004 | 0 | 0 | 4282.052 | 178268.5721 | 4282.052 | 3168.7475 | 181437.3196
| 20496497 | 2024 | HSM004 | 0 | 0 | 6149.8122 | 256026.3698 | 6149.8122 | 3168.7475 | 259195.1173
| 20496497 | 2025 | HSM004 | 0 | 0 | 5921.1513 | 246506.857 | 5921.1513 | 3168.7475 | 249675.6045
| 20496497 | 2026 | HSM004 | 0 | 0 | 16309.2376 | 678979.2502 | 16309.2376 | 3168.7475 | 682147.9978
| 20496497 | 2027 | HSM004 | 0 | 0 | 16309.2376 | 678979.2502 | 16309.2376 | 3168.7475 | 682147.9978
| 20496497 | 2028 | HSM004 | 0 | 0 | 16309.2376 | 678979.2502 | 16309.2376 | 3168.7475 | 682147.9978
| 20496497 | 2029 | HSM004 | 0 | 0 | 16309.2376 | 678979.2502 | 16309.2376 | 3168.7475 | 682147.9978
| 20496497 | 2030 | HSM004 | 0 | 0 | 16309.2376 | 678979.2502 | 16309.2376 | 3168.7475 | 682147.9978
| 20496497 | 2031 | HSM004 | 0 | 0 | 16309.2376 | 678979.2502 | 16309.2376 | 3168.7475 | 682147.9978
| 20496497 | 2032 | HSM004 | 0 | 0 | 16309.2376 | 678979.2502 | 16309.2376 | 3168.7475 | 682147.9978
| 20496497 | 2033 | HSM004 | 0 | 0 | 16309.2376 | 678979.2502 | 16309.2376 | 3168.7475 | 682147.9978
| 20496497 | 2034 | HSM004 | 0 | 0 | 16309.2376 | 678979.2502 | 16309.2376 | 3168.7475 | 682147.9978
| 20528972 | 2023 | HSM004 | 0 | 0 | 0 | 0 | 0 | 6402.3261 | 6402.3261
| 20528972 | 2024 | HSM004 | 0 | 0 | 0 | 0 | 0 | 6402.3261 | 6402.3261
| 20528972 | 2025 | HSM004 | 0 | 0 | 0 | 0 | 0 | 6402.3261 | 6402.3261
| 20528972 | 2026 | HSM004 | 0 | 0 | 0 | 0 | 0 | 6402.3261 | 6402.3261
| 20528972 | 2027 | HSM004 | 0 | 0 | 0 | 0 | 0 | 6402.3261 | 6402.3261
| 20528972 | 2028 | HSM004 | 0 | 0 | 0 | 0 | 0 | 6402.3261 | 6402.3261
| 20528972 | 2029 | HSM004 | 0 | 0 | 0 | 0 | 0 | 6402.3261 | 6402.3261
| 20528972 | 2030 | HSM004 | 0 | 0 | 0 | 0 | 0 | 6402.3261 | 6402.3261
| 20528972 | 2031 | HSM004 | 0 | 0 | 0 | 0 | 0 | 6402.3261 | 6402.3261
| 20528972 | 2032 | HSM004 | 0 | 0 | 0 | 0 | 0 | 6402.3261 | 6402.3261
| 20528972 | 2033 | HSM004 | 0 | 0 | 0 | 0 | 0 | 6402.3261 | 6402.3261
| 20528972 | 2034 | HSM004 | 0 | 0 | 0 | 0 | 0 | 6402.3261 | 6402.3261
| 44705079 | 2023 | HSM004 | 0 | 0 | 0.095011 | 3.9554 | 0.095011 | 10007.8085 | 10011.7639
| 44705079 | 2024 | HSM004 | 0 | 0 | 0.059688 | 2.4849 | 0.059688 | 10007.8085 | 10010.2934
| 44705079 | 2025 | HSM004 | 0 | 0 | 0 | 0 | 0 | 10007.8085 | 10007.8085
| 44705079 | 2026 | HSM004 | 1945.2978 | 7.93 | 0 | 0 | 1945.2978 | 10007.8085 | 10015.7384
| 44705079 | 2027 | HSM004 | 1945.2978 | 7.93 | 0 | 0 | 1945.2978 | 10007.8085 | 10015.7384
| 44705079 | 2028 | HSM004 | 1945.2978 | 7.93 | 0 | 0 | 1945.2978 | 10007.8085 | 10015.7384
| 44705079 | 2029 | HSM004 | 1945.2978 | 7.93 | 0 | 0 | 1945.2978 | 10007.8085 | 10015.7384
| 44705079 | 2030 | HSM004 | 1945.2978 | 7.93 | 0 | 0 | 1945.2978 | 10007.8085 | 10015.7384
| 44705079 | 2031 | HSM004 | 1945.2978 | 7.93 | 0 | 0 | 1945.2978 | 10007.8085 | 10015.7384
| 44705079 | 2032 | HSM004 | 1945.2978 | 7.93 | 0 | 0 | 1945.2978 | 10007.8085 | 10015.7384
| 44705079 | 2033 | HSM004 | 1945.2978 | 7.93 | 0 | 0 | 1945.2978 | 10007.8085 | 10015.7384
| 44705079 | 2034 | HSM004 | 1945.2978 | 7.93 | 0 | 0 | 1945.2978 | 10007.8085 | 10015.7384
| 46707751 | 2023 | HSM004 | 7.3122 | 0 | 1.3189 | 54.909 | 8.6311 | 5213.4447 | 5268.3537
| 46707751 | 2024 | HSM004 | 1.844 | 0.051639 | 2.0703 | 86.1918 | 3.9143 | 5213.4447 | 5299.6882
| 46707751 | 2025 | HSM004 | 202.2274 | 2.9014 | 1.7065 | 71.0448 | 203.9339 | 5213.4447 | 5287.391
| 46707751 | 2026 | HSM004 | 701.2678 | 4.0651 | 0.51306 | 21.3595 | 701.7809 | 5213.4447 | 5238.8694
| 46707751 | 2027 | HSM004 | 701.2678 | 4.0651 | 0.51306 | 21.3595 | 701.7809 | 5213.4447 | 5238.8694
| 46707751 | 2028 | HSM004 | 701.2678 | 4.0651 | 0.51306 | 21.3595 | 701.7809 | 5213.4447 | 5238.8694
| 46707751 | 2029 | HSM004 | 701.2678 | 4.0651 | 0.51306 | 21.3595 | 701.7809 | 5213.4447 | 5238.8694
| 46707751 | 2030 | HSM004 | 701.2678 | 4.0651 | 0.51306 | 21.3595 | 701.7809 | 5213.4447 | 5238.8694
| 46707751 | 2031 | HSM004 | 701.2678 | 4.0651 | 0.51306 | 21.3595 | 701.7809 | 5213.4447 | 5238.8694
| 46707751 | 2032 | HSM004 | 701.2678 | 4.0651 | 0.51306 | 21.3595 | 701.7809 | 5213.4447 | 5238.8694
| 46707751 | 2033 | HSM004 | 701.2678 | 4.0651 | 0.51306 | 21.3595 | 701.7809 | 5213.4447 | 5238.8694
| 46707751 | 2034 | HSM004 | 701.2678 | 4.0651 | 0.51306 | 21.3595 | 701.7809 | 5213.4447 | 5238.8694
| 76743958 | 2023 | HSM004 | 0 | 0 | 0.062321 | 2.5945 | 0.062321 | 2813.629 | 2816.2235
| 76743958 | 2024 | HSM004 | 2.8549 | 0.016904 | 0 | 0 | 2.8549 | 2813.629 | 2813.6459
| 76743958 | 2025 | HSM004 | 184.5812 | 2.649 | 0 | 0 | 184.5812 | 2813.629 | 2816.2781
| 76743958 | 2026 | HSM004 | 1214.3544 | 4.3567 | 0 | 0 | 1214.3544 | 2813.629 | 2817.9857
| 76743958 | 2027 | HSM004 | 1214.3544 | 4.3567 | 0 | 0 | 1214.3544 | 2813.629 | 2817.9857
| 76743958 | 2028 | HSM004 | 1214.3544 | 4.3567 | 0 | 0 | 1214.3544 | 2813.629 | 2817.9857
| 76743958 | 2029 | HSM004 | 1214.3544 | 4.3567 | 0 | 0 | 1214.3544 | 2813.629 | 2817.9857
| 76743958 | 2030 | HSM004 | 1214.3544 | 4.3567 | 0 | 0 | 1214.3544 | 2813.629 | 2817.9857
| 76743958 | 2031 | HSM004 | 1214.3544 | 4.3567 | 0 | 0 | 1214.3544 | 2813.629 | 2817.9857
| 76743958 | 2032 | HSM004 | 1214.3544 | 4.3567 | 0 | 0 | 1214.3544 | 2813.629 | 2817.9857
| 76743958 | 2033 | HSM004 | 1214.3544 | 4.3567 | 0 | 0 | 1214.3544 | 2813.629 | 2817.9857
| 76743958 | 2034 | HSM004 | 1214.3544 | 4.3567 | 0 | 0 | 1214.3544 | 2813.629 | 2817.9857
| 77226876 | 2023 | HSM004 | 0 | 0 | 0 | 0 | 0 | 18758.3282 | 18758.3282
| 77226876 | 2024 | HSM004 | 0 | 0 | 0 | 0 | 0 | 18758.3282 | 18758.3282
| 77226876 | 2025 | HSM004 | 0 | 0 | 0 | 0 | 0 | 18758.3282 | 18758.3282
| 77226876 | 2026 | HSM004 | 0 | 0 | 0 | 0 | 0 | 18758.3282 | 18758.3282
| 77226876 | 2027 | HSM004 | 0 | 0 | 0 | 0 | 0 | 18758.3282 | 18758.3282
| 77226876 | 2028 | HSM004 | 0 | 0 | 0 | 0 | 0 | 18758.3282 | 18758.3282
| 77226876 | 2029 | HSM004 | 0 | 0 | 0 | 0 | 0 | 18758.3282 | 18758.3282
| 77226876 | 2030 | HSM004 | 0 | 0 | 0 | 0 | 0 | 18758.3282 | 18758.3282
| 77226876 | 2031 | HSM004 | 0 | 0 | 0 | 0 | 0 | 18758.3282 | 18758.3282
| 77226876 | 2032 | HSM004 | 0 | 0 | 0 | 0 | 0 | 18758.3282 | 18758.3282
| 77226876 | 2033 | HSM004 | 0 | 0 | 0 | 0 | 0 | 18758.3282 | 18758.3282
| 77226876 | 2034 | HSM004 | 0 | 0 | 0 | 0 | 0 | 18758.3282 | 18758.3282
| 96221221 | 2023 | HSM004 | 570.7762 | 0 | 0.7225 | 30.0787 | 571.4987 | 23966.2908 | 23996.3695
| 96221221 | 2024 | HSM004 | 512.0724 | 4.4108 | 0.4476 | 18.6345 | 512.52 | 23966.2908 | 23989.3361
| 96221221 | 2025 | HSM004 | 736.9456 | 16.1671 | 0 | 0 | 736.9456 | 23966.2908 | 23982.4579
| 96221221 | 2026 | HSM004 | 1270.203 | 10.8688 | 0 | 0 | 1270.203 | 23966.2908 | 23977.1596
| 96221221 | 2027 | HSM004 | 1270.203 | 10.8688 | 0 | 0 | 1270.203 | 23966.2908 | 23977.1596
| 96221221 | 2028 | HSM004 | 1270.203 | 10.8688 | 0 | 0 | 1270.203 | 23966.2908 | 23977.1596
| 96221221 | 2029 | HSM004 | 1270.203 | 10.8688 | 0 | 0 | 1270.203 | 23966.2908 | 23977.1596
| 96221221 | 2030 | HSM004 | 1270.203 | 10.8688 | 0 | 0 | 1270.203 | 23966.2908 | 23977.1596
| 96221221 | 2031 | HSM004 | 1270.203 | 10.8688 | 0 | 0 | 1270.203 | 23966.2908 | 23977.1596
| 96221221 | 2032 | HSM004 | 1270.203 | 10.8688 | 0 | 0 | 1270.203 | 23966.2908 | 23977.1596
| 96221221 | 2033 | HSM004 | 1270.203 | 10.8688 | 0 | 0 | 1270.203 | 23966.2908 | 23977.1596
| 96221221 | 2034 | HSM004 | 1270.203 | 10.8688 | 0 | 0 | 1270.203 | 23966.2908 | 23977.1596
| 160976862 | 2023 | HSM004 | 1114.2878 | 0 | 0 | 0 | 1114.2878 | 2870.0458 | 2870.0458
| 160976862 | 2024 | HSM004 | 1926.2149 | 37.0447 | 0 | 0 | 1926.2149 | 2870.0458 | 2907.0904
| 160976862 | 2025 | HSM004 | 2228.1093 | 35.3056 | 0 | 0 | 2228.1093 | 2870.0458 | 2905.3514
| 160976862 | 2026 | HSM004 | 5976.6429 | 37.0252 | 0 | 0 | 5976.6429 | 2870.0458 | 2907.071
| 160976862 | 2027 | HSM004 | 5976.6429 | 37.0252 | 0 | 0 | 5976.6429 | 2870.0458 | 2907.071
| 160976862 | 2028 | HSM004 | 5976.6429 | 37.0252 | 0 | 0 | 5976.6429 | 2870.0458 | 2907.071
| 160976862 | 2029 | HSM004 | 5976.6429 | 37.0252 | 0 | 0 | 5976.6429 | 2870.0458 | 2907.071
| 160976862 | 2030 | HSM004 | 5976.6429 | 37.0252 | 0 | 0 | 5976.6429 | 2870.0458 | 2907.071
| 160976862 | 2031 | HSM004 | 5976.6429 | 37.0252 | 0 | 0 | 5976.6429 | 2870.0458 | 2907.071
| 160976862 | 2032 | HSM004 | 5976.6429 | 37.0252 | 0 | 0 | 5976.6429 | 2870.0458 | 2907.071
| 160976862 | 2033 | HSM004 | 5976.6429 | 37.0252 | 0 | 0 | 5976.6429 | 2870.0458 | 2907.071
| 160976862 | 2034 | HSM004 | 5976.6429 | 37.0252 | 0 | 0 | 5976.6429 | 2870.0458 | 2907.071
| 161789292 | 2023 | HSM004 | 4680.1385 | 0 | 0 | 0 | 4680.1385 | 4054.1837 | 4054.1837
| 161789292 | 2024 | HSM004 | 4783.6555 | 102.1902 | 0 | 0 | 4783.6555 | 4054.1837 | 4156.3739
| 161789292 | 2025 | HSM004 | 9136.1983 | 201.1105 | 0 | 0 | 9136.1983 | 4054.1837 | 4255.2942
| 161789292 | 2026 | HSM004 | 10912.5638 | 150.2217 | 0 | 0 | 10912.5638 | 4054.1837 | 4204.4054
| 161789292 | 2027 | HSM004 | 10912.5638 | 150.2217 | 0 | 0 | 10912.5638 | 4054.1837 | 4204.4054
| 161789292 | 2028 | HSM004 | 10912.5638 | 150.2217 | 0 | 0 | 10912.5638 | 4054.1837 | 4204.4054
| 161789292 | 2029 | HSM004 | 10912.5638 | 150.2217 | 0 | 0 | 10912.5638 | 4054.1837 | 4204.4054
| 161789292 | 2030 | HSM004 | 10912.5638 | 150.2217 | 0 | 0 | 10912.5638 | 4054.1837 | 4204.4054
| 161789292 | 2031 | HSM004 | 10912.5638 | 150.2217 | 0 | 0 | 10912.5638 | 4054.1837 | 4204.4054
| 161789292 | 2032 | HSM004 | 10912.5638 | 150.2217 | 0 | 0 | 10912.5638 | 4054.1837 | 4204.4054
| 161789292 | 2033 | HSM004 | 10912.5638 | 150.2217 | 0 | 0 | 10912.5638 | 4054.1837 | 4204.4054
| 161789292 | 2034 | HSM004 | 10912.5638 | 150.2217 | 0 | 0 | 10912.5638 | 4054.1837 | 4204.4054
| 163606350 | 2023 | HSM004 | 0 | 0 | 0 | 0 | 0 | 10033.0151 | 10033.0151
| 163606350 | 2024 | HSM004 | 0 | 0 | 0 | 0 | 0 | 10033.0151 | 10033.0151
| 163606350 | 2025 | HSM004 | 0 | 0 | 0 | 0 | 0 | 10033.0151 | 10033.0151
| 163606350 | 2026 | HSM004 | 0 | 0 | 0 | 0 | 0 | 10033.0151 | 10033.0151
| 163606350 | 2027 | HSM004 | 0 | 0 | 0 | 0 | 0 | 10033.0151 | 10033.0151
| 163606350 | 2028 | HSM004 | 0 | 0 | 0 | 0 | 0 | 10033.0151 | 10033.0151
| 163606350 | 2029 | HSM004 | 0 | 0 | 0 | 0 | 0 | 10033.0151 | 10033.0151
| 163606350 | 2030 | HSM004 | 0 | 0 | 0 | 0 | 0 | 10033.0151 | 10033.0151
| 163606350 | 2031 | HSM004 | 0 | 0 | 0 | 0 | 0 | 10033.0151 | 10033.0151
| 163606350 | 2032 | HSM004 | 0 | 0 | 0 | 0 | 0 | 10033.0151 | 10033.0151
| 163606350 | 2033 | HSM004 | 0 | 0 | 0 | 0 | 0 | 10033.0151 | 10033.0151
| 163606350 | 2034 | HSM004 | 0 | 0 | 0 | 0 | 0 | 10033.0151 | 10033.0151
| 182632597 | 2023 | HSM004 | 1086.9174 | 0 | 63.3507 | 2637.3911 | 1150.2681 | 4938.5968 | 7575.9879
| 182632597 | 2024 | HSM004 | 1491.7902 | 23.4872 | 74.3812 | 3096.6046 | 1566.1714 | 4938.5968 | 8058.6886
| 182632597 | 2025 | HSM004 | 1807.2907 | 28.8009 | 52.2115 | 2173.6457 | 1859.5022 | 4938.5968 | 7141.0434
| 182632597 | 2026 | HSM004 | 5366.0352 | 40.3759 | 29.0088 | 1207.6806 | 5395.044 | 4938.5968 | 6186.6533
| 182632597 | 2027 | HSM004 | 5366.0352 | 40.3759 | 29.0088 | 1207.6806 | 5395.044 | 4938.5968 | 6186.6533
| 182632597 | 2028 | HSM004 | 5366.0352 | 40.3759 | 29.0088 | 1207.6806 | 5395.044 | 4938.5968 | 6186.6533
| 182632597 | 2029 | HSM004 | 5366.0352 | 40.3759 | 29.0088 | 1207.6806 | 5395.044 | 4938.5968 | 6186.6533
| 182632597 | 2030 | HSM004 | 5366.0352 | 40.3759 | 29.0088 | 1207.6806 | 5395.044 | 4938.5968 | 6186.6533
| 182632597 | 2031 | HSM004 | 5366.0352 | 40.3759 | 29.0088 | 1207.6806 | 5395.044 | 4938.5968 | 6186.6533
| 182632597 | 2032 | HSM004 | 5366.0352 | 40.3759 | 29.0088 | 1207.6806 | 5395.044 | 4938.5968 | 6186.6533
| 182632597 | 2033 | HSM004 | 5366.0352 | 40.3759 | 29.0088 | 1207.6806 | 5395.044 | 4938.5968 | 6186.6533
| 182632597 | 2034 | HSM004 | 5366.0352 | 40.3759 | 29.0088 | 1207.6806 | 5395.044 | 4938.5968 | 6186.6533
| 184479483 | 2023 | HSM004 | 945.691 | 0 | 0 | 0 | 945.691 | 4366.044 | 4366.044
| 184479483 | 2024 | HSM004 | 1490.3784 | 26.6042 | 0 | 0 | 1490.3784 | 4366.044 | 4392.6482
| 184479483 | 2025 | HSM004 | 2963.059 | 52.2747 | 0 | 0 | 2963.059 | 4366.044 | 4418.3187
| 184479483 | 2026 | HSM004 | 5051.0096 | 40.516 | 0 | 0 | 5051.0096 | 4366.044 | 4406.56
| 184479483 | 2027 | HSM004 | 5051.0096 | 40.516 | 0 | 0 | 5051.0096 | 4366.044 | 4406.56
| 184479483 | 2028 | HSM004 | 5051.0096 | 40.516 | 0 | 0 | 5051.0096 | 4366.044 | 4406.56
| 184479483 | 2029 | HSM004 | 5051.0096 | 40.516 | 0 | 0 | 5051.0096 | 4366.044 | 4406.56
| 184479483 | 2030 | HSM004 | 5051.0096 | 40.516 | 0 | 0 | 5051.0096 | 4366.044 | 4406.56
| 184479483 | 2031 | HSM004 | 5051.0096 | 40.516 | 0 | 0 | 5051.0096 | 4366.044 | 4406.56
| 184479483 | 2032 | HSM004 | 5051.0096 | 40.516 | 0 | 0 | 5051.0096 | 4366.044 | 4406.56
| 184479483 | 2033 | HSM004 | 5051.0096 | 40.516 | 0 | 0 | 5051.0096 | 4366.044 | 4406.56
| 184479483 | 2034 | HSM004 | 5051.0096 | 40.516 | 0 | 0 | 5051.0096 | 4366.044 | 4406.56
| 195085692 | 2023 | HSM004 | 0 | 0 | 5073.2422 | 211207.0648 | 5073.2422 | 15511.0874 | 226718.1522
| 195085692 | 2024 | HSM004 | 0 | 0 | 5681.099 | 236513.1015 | 5681.099 | 15511.0874 | 252024.1889
| 195085692 | 2025 | HSM004 | 0 | 0 | 5305.8332 | 220890.1947 | 5305.8332 | 15511.0874 | 236401.2821
| 195085692 | 2026 | HSM004 | 0 | 0 | 11282.446 | 469705.9997 | 11282.446 | 15511.0874 | 485217.0871
| 195085692 | 2027 | HSM004 | 0 | 0 | 11282.446 | 469705.9997 | 11282.446 | 15511.0874 | 485217.0871
| 195085692 | 2028 | HSM004 | 0 | 0 | 11282.446 | 469705.9997 | 11282.446 | 15511.0874 | 485217.0871
| 195085692 | 2029 | HSM004 | 0 | 0 | 11282.446 | 469705.9997 | 11282.446 | 15511.0874 | 485217.0871
| 195085692 | 2030 | HSM004 | 0 | 0 | 11282.446 | 469705.9997 | 11282.446 | 15511.0874 | 485217.0871
| 195085692 | 2031 | HSM004 | 0 | 0 | 11282.446 | 469705.9997 | 11282.446 | 15511.0874 | 485217.0871
| 195085692 | 2032 | HSM004 | 0 | 0 | 11282.446 | 469705.9997 | 11282.446 | 15511.0874 | 485217.0871
| 195085692 | 2033 | HSM004 | 0 | 0 | 11282.446 | 469705.9997 | 11282.446 | 15511.0874 | 485217.0871
| 195085692 | 2034 | HSM004 | 0 | 0 | 11282.446 | 469705.9997 | 11282.446 | 15511.0874 | 485217.0871
| 19929810 | 2023 | HSM006 | 0 | 0 | 1411.9849 | 58783.1569 | 1411.9849 | 41121.6197 | 99904.7766
| 19929810 | 2024 | HSM006 | 0 | 0 | 1483.1574 | 61746.1794 | 1483.1574 | 41121.6197 | 102867.799
| 19929810 | 2025 | HSM006 | 0 | 0 | 1410.029 | 58701.728 | 1410.029 | 41121.6197 | 99823.3476
| 19929810 | 2026 | HSM006 | 0 | 0 | 1410.029 | 58701.728 | 1410.029 | 41121.6197 | 99823.3476
| 19929810 | 2027 | HSM006 | 0 | 0 | 1410.029 | 58701.728 | 1410.029 | 41121.6197 | 99823.3476
| 19929810 | 2028 | HSM006 | 0 | 0 | 1410.029 | 58701.728 | 1410.029 | 41121.6197 | 99823.3476
| 19929810 | 2029 | HSM006 | 0 | 0 | 1410.029 | 58701.728 | 1410.029 | 41121.6197 | 99823.3476
| 19929810 | 2030 | HSM006 | 0 | 0 | 1410.029 | 58701.728 | 1410.029 | 41121.6197 | 99823.3476
| 19929810 | 2031 | HSM006 | 0 | 0 | 1410.029 | 58701.728 | 1410.029 | 41121.6197 | 99823.3476
| 19929810 | 2032 | HSM006 | 0 | 0 | 1410.029 | 58701.728 | 1410.029 | 41121.6197 | 99823.3476
| 19929810 | 2033 | HSM006 | 0 | 0 | 1410.029 | 58701.728 | 1410.029 | 41121.6197 | 99823.3476
| 19929810 | 2034 | HSM006 | 0 | 0 | 1410.029 | 58701.728 | 1410.029 | 41121.6197 | 99823.3476
| 19929872 | 2023 | HSM006 | 0 | 0 | 0 | 0 | 0 | 14323.0123 | 14323.0123
| 19929872 | 2024 | HSM006 | 0 | 0 | 0 | 0 | 0 | 14323.0123 | 14323.0123
| 19929872 | 2025 | HSM006 | 1.041 | 0.014254 | 0 | 0 | 1.041 | 14323.0123 | 14323.0266
| 19929872 | 2026 | HSM006 | 1.041 | 0.014254 | 0 | 0 | 1.041 | 14323.0123 | 14323.0266
| 19929872 | 2027 | HSM006 | 1.041 | 0.014254 | 0 | 0 | 1.041 | 14323.0123 | 14323.0266
| 19929872 | 2028 | HSM006 | 1.041 | 0.014254 | 0 | 0 | 1.041 | 14323.0123 | 14323.0266
| 19929872 | 2029 | HSM006 | 1.041 | 0.014254 | 0 | 0 | 1.041 | 14323.0123 | 14323.0266
| 19929872 | 2030 | HSM006 | 1.041 | 0.014254 | 0 | 0 | 1.041 | 14323.0123 | 14323.0266
| 19929872 | 2031 | HSM006 | 1.041 | 0.014254 | 0 | 0 | 1.041 | 14323.0123 | 14323.0266
| 19929872 | 2032 | HSM006 | 1.041 | 0.014254 | 0 | 0 | 1.041 | 14323.0123 | 14323.0266
| 19929872 | 2033 | HSM006 | 1.041 | 0.014254 | 0 | 0 | 1.041 | 14323.0123 | 14323.0266
| 19929872 | 2034 | HSM006 | 1.041 | 0.014254 | 0 | 0 | 1.041 | 14323.0123 | 14323.0266
| 19959571 | 2023 | HSM006 | 0 | 0 | 0 | 0 | 0 | 26111.9757 | 26111.9757
| 19959571 | 2024 | HSM006 | 0 | 0 | 0 | 0 | 0 | 26111.9757 | 26111.9757
| 19959571 | 2025 | HSM006 | 0 | 0 | 0 | 0 | 0 | 26111.9757 | 26111.9757
| 19959571 | 2026 | HSM006 | 0 | 0 | 0 | 0 | 0 | 26111.9757 | 26111.9757
| 19959571 | 2027 | HSM006 | 0 | 0 | 0 | 0 | 0 | 26111.9757 | 26111.9757
| 19959571 | 2028 | HSM006 | 0 | 0 | 0 | 0 | 0 | 26111.9757 | 26111.9757
| 19959571 | 2029 | HSM006 | 0 | 0 | 0 | 0 | 0 | 26111.9757 | 26111.9757
| 19959571 | 2030 | HSM006 | 0 | 0 | 0 | 0 | 0 | 26111.9757 | 26111.9757
| 19959571 | 2031 | HSM006 | 0 | 0 | 0 | 0 | 0 | 26111.9757 | 26111.9757
| 19959571 | 2032 | HSM006 | 0 | 0 | 0 | 0 | 0 | 26111.9757 | 26111.9757
| 19959571 | 2033 | HSM006 | 0 | 0 | 0 | 0 | 0 | 26111.9757 | 26111.9757
| 19959571 | 2034 | HSM006 | 0 | 0 | 0 | 0 | 0 | 26111.9757 | 26111.9757
| 19962390 | 2023 | HSM006 | 0 | 0 | 13687.4264 | 569829.1209 | 13687.4264 | 27081.9056 | 596911.0264
| 19962390 | 2024 | HSM006 | 0 | 0 | 14508.7283 | 604021.2141 | 14508.7283 | 27081.9056 | 631103.1196
| 19962390 | 2025 | HSM006 | 0 | 0 | 13637.2939 | 567742.0254 | 13637.2939 | 27081.9056 | 594823.931
| 19962390 | 2026 | HSM006 | 0 | 0 | 13637.2939 | 567742.0254 | 13637.2939 | 27081.9056 | 594823.931
| 19962390 | 2027 | HSM006 | 0 | 0 | 13637.2939 | 567742.0254 | 13637.2939 | 27081.9056 | 594823.931
| 19962390 | 2028 | HSM006 | 0 | 0 | 13637.2939 | 567742.0254 | 13637.2939 | 27081.9056 | 594823.931
| 19962390 | 2029 | HSM006 | 0 | 0 | 13637.2939 | 567742.0254 | 13637.2939 | 27081.9056 | 594823.931
| 19962390 | 2030 | HSM006 | 0 | 0 | 13637.2939 | 567742.0254 | 13637.2939 | 27081.9056 | 594823.931
| 19962390 | 2031 | HSM006 | 0 | 0 | 13637.2939 | 567742.0254 | 13637.2939 | 27081.9056 | 594823.931
| 19962390 | 2032 | HSM006 | 0 | 0 | 13637.2939 | 567742.0254 | 13637.2939 | 27081.9056 | 594823.931
| 19962390 | 2033 | HSM006 | 0 | 0 | 13637.2939 | 567742.0254 | 13637.2939 | 27081.9056 | 594823.931
| 19962390 | 2034 | HSM006 | 0 | 0 | 13637.2939 | 567742.0254 | 13637.2939 | 27081.9056 | 594823.931
| 42922160 | 2023 | HSM006 | 0 | 0 | 0 | 0 | 0 | 5144.9732 | 5144.9732
| 42922160 | 2024 | HSM006 | 0 | 0 | 0 | 0 | 0 | 5144.9732 | 5144.9732
| 42922160 | 2025 | HSM006 | 0 | 0 | 0 | 0 | 0 | 5144.9732 | 5144.9732
| 42922160 | 2026 | HSM006 | 0 | 0 | 0 | 0 | 0 | 5144.9732 | 5144.9732
| 42922160 | 2027 | HSM006 | 0 | 0 | 0 | 0 | 0 | 5144.9732 | 5144.9732
| 42922160 | 2028 | HSM006 | 0 | 0 | 0 | 0 | 0 | 5144.9732 | 5144.9732
| 42922160 | 2029 | HSM006 | 0 | 0 | 0 | 0 | 0 | 5144.9732 | 5144.9732
| 42922160 | 2030 | HSM006 | 0 | 0 | 0 | 0 | 0 | 5144.9732 | 5144.9732
| 42922160 | 2031 | HSM006 | 0 | 0 | 0 | 0 | 0 | 5144.9732 | 5144.9732
| 42922160 | 2032 | HSM006 | 0 | 0 | 0 | 0 | 0 | 5144.9732 | 5144.9732
| 42922160 | 2033 | HSM006 | 0 | 0 | 0 | 0 | 0 | 5144.9732 | 5144.9732
| 42922160 | 2034 | HSM006 | 0 | 0 | 0 | 0 | 0 | 5144.9732 | 5144.9732
| 48101105 | 2023 | HSM006 | 0 | 0 | 340.0112 | 14155.2024 | 340.0112 | 19408.3374 | 33563.5398
| 48101105 | 2024 | HSM006 | 0 | 0 | 399.6547 | 16638.2551 | 399.6547 | 19408.3374 | 36046.5925
| 48101105 | 2025 | HSM006 | 0 | 0 | 363.6927 | 15141.1007 | 363.6927 | 19408.3374 | 34549.4382
| 48101105 | 2026 | HSM006 | 0 | 0 | 363.6927 | 15141.1007 | 363.6927 | 19408.3374 | 34549.4382
| 48101105 | 2027 | HSM006 | 0 | 0 | 363.6927 | 15141.1007 | 363.6927 | 19408.3374 | 34549.4382
| 48101105 | 2028 | HSM006 | 0 | 0 | 363.6927 | 15141.1007 | 363.6927 | 19408.3374 | 34549.4382
| 48101105 | 2029 | HSM006 | 0 | 0 | 363.6927 | 15141.1007 | 363.6927 | 19408.3374 | 34549.4382
| 48101105 | 2030 | HSM006 | 0 | 0 | 363.6927 | 15141.1007 | 363.6927 | 19408.3374 | 34549.4382
| 48101105 | 2031 | HSM006 | 0 | 0 | 363.6927 | 15141.1007 | 363.6927 | 19408.3374 | 34549.4382
| 48101105 | 2032 | HSM006 | 0 | 0 | 363.6927 | 15141.1007 | 363.6927 | 19408.3374 | 34549.4382
| 48101105 | 2033 | HSM006 | 0 | 0 | 363.6927 | 15141.1007 | 363.6927 | 19408.3374 | 34549.4382
| 48101105 | 2034 | HSM006 | 0 | 0 | 363.6927 | 15141.1007 | 363.6927 | 19408.3374 | 34549.4382
| 153766407 | 2023 | HSM006 | 5344.4884 | 0 | 0 | 0 | 5344.4884 | 21027.4522 | 21027.4522
| 153766407 | 2024 | HSM006 | 14029.3061 | 291.6607 | 0 | 0 | 14029.3061 | 21027.4522 | 21319.113
| 153766407 | 2025 | HSM006 | 17046.5023 | 416.8183 | 0 | 0 | 17046.5023 | 21027.4522 | 21444.2705
| 153766407 | 2026 | HSM006 | 17046.5023 | 416.8183 | 0 | 0 | 17046.5023 | 21027.4522 | 21444.2705
| 153766407 | 2027 | HSM006 | 17046.5023 | 416.8183 | 0 | 0 | 17046.5023 | 21027.4522 | 21444.2705
| 153766407 | 2028 | HSM006 | 17046.5023 | 416.8183 | 0 | 0 | 17046.5023 | 21027.4522 | 21444.2705
| 153766407 | 2029 | HSM006 | 17046.5023 | 416.8183 | 0 | 0 | 17046.5023 | 21027.4522 | 21444.2705
| 153766407 | 2030 | HSM006 | 17046.5023 | 416.8183 | 0 | 0 | 17046.5023 | 21027.4522 | 21444.2705
| 153766407 | 2031 | HSM006 | 17046.5023 | 416.8183 | 0 | 0 | 17046.5023 | 21027.4522 | 21444.2705
| 153766407 | 2032 | HSM006 | 17046.5023 | 416.8183 | 0 | 0 | 17046.5023 | 21027.4522 | 21444.2705
| 153766407 | 2033 | HSM006 | 17046.5023 | 416.8183 | 0 | 0 | 17046.5023 | 21027.4522 | 21444.2705
| 153766407 | 2034 | HSM006 | 17046.5023 | 416.8183 | 0 | 0 | 17046.5023 | 21027.4522 | 21444.2705
| 19969626 | 2023 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5726.261 | 5726.261
| 19969626 | 2024 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5726.261 | 5726.261
| 19969626 | 2025 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5726.261 | 5726.261
| 19969626 | 2026 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5726.261 | 5726.261
| 19969626 | 2027 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5726.261 | 5726.261
| 19969626 | 2028 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5726.261 | 5726.261
| 19969626 | 2029 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5726.261 | 5726.261
| 19969626 | 2030 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5726.261 | 5726.261
| 19969626 | 2031 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5726.261 | 5726.261
| 19969626 | 2032 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5726.261 | 5726.261
| 19969626 | 2033 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5726.261 | 5726.261
| 19969626 | 2034 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5726.261 | 5726.261
| 19970479 | 2023 | HTN032 | 0 | 0 | 0 | 0 | 0 | 455.3065 | 455.3065
| 19970479 | 2024 | HTN032 | 0 | 0 | 0 | 0 | 0 | 455.3065 | 455.3065
| 19970479 | 2025 | HTN032 | 0 | 0 | 0 | 0 | 0 | 455.3065 | 455.3065
| 19970479 | 2026 | HTN032 | 0 | 0 | 0 | 0 | 0 | 455.3065 | 455.3065
| 19970479 | 2027 | HTN032 | 0 | 0 | 0 | 0 | 0 | 455.3065 | 455.3065
| 19970479 | 2028 | HTN032 | 0 | 0 | 0 | 0 | 0 | 455.3065 | 455.3065
| 19970479 | 2029 | HTN032 | 0 | 0 | 0 | 0 | 0 | 455.3065 | 455.3065
| 19970479 | 2030 | HTN032 | 0 | 0 | 0 | 0 | 0 | 455.3065 | 455.3065
| 19970479 | 2031 | HTN032 | 0 | 0 | 0 | 0 | 0 | 455.3065 | 455.3065
| 19970479 | 2032 | HTN032 | 0 | 0 | 0 | 0 | 0 | 455.3065 | 455.3065
| 19970479 | 2033 | HTN032 | 0 | 0 | 0 | 0 | 0 | 455.3065 | 455.3065
| 19970479 | 2034 | HTN032 | 0 | 0 | 0 | 0 | 0 | 455.3065 | 455.3065
| 19971256 | 2023 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7137.3891 | 7137.3891
| 19971256 | 2024 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7137.3891 | 7137.3891
| 19971256 | 2025 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7137.3891 | 7137.3891
| 19971256 | 2026 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7137.3891 | 7137.3891
| 19971256 | 2027 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7137.3891 | 7137.3891
| 19971256 | 2028 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7137.3891 | 7137.3891
| 19971256 | 2029 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7137.3891 | 7137.3891
| 19971256 | 2030 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7137.3891 | 7137.3891
| 19971256 | 2031 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7137.3891 | 7137.3891
| 19971256 | 2032 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7137.3891 | 7137.3891
| 19971256 | 2033 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7137.3891 | 7137.3891
| 19971256 | 2034 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7137.3891 | 7137.3891
| 19971615 | 2023 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7959.0363 | 7959.0363
| 19971615 | 2024 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7959.0363 | 7959.0363
| 19971615 | 2025 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7959.0363 | 7959.0363
| 19971615 | 2026 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7959.0363 | 7959.0363
| 19971615 | 2027 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7959.0363 | 7959.0363
| 19971615 | 2028 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7959.0363 | 7959.0363
| 19971615 | 2029 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7959.0363 | 7959.0363
| 19971615 | 2030 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7959.0363 | 7959.0363
| 19971615 | 2031 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7959.0363 | 7959.0363
| 19971615 | 2032 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7959.0363 | 7959.0363
| 19971615 | 2033 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7959.0363 | 7959.0363
| 19971615 | 2034 | HTN032 | 0 | 0 | 0 | 0 | 0 | 7959.0363 | 7959.0363
| 19971809 | 2023 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8971.4269 | 8971.4269
| 19971809 | 2024 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8971.4269 | 8971.4269
| 19971809 | 2025 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8971.4269 | 8971.4269
| 19971809 | 2026 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8971.4269 | 8971.4269
| 19971809 | 2027 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8971.4269 | 8971.4269
| 19971809 | 2028 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8971.4269 | 8971.4269
| 19971809 | 2029 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8971.4269 | 8971.4269
| 19971809 | 2030 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8971.4269 | 8971.4269
| 19971809 | 2031 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8971.4269 | 8971.4269
| 19971809 | 2032 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8971.4269 | 8971.4269
| 19971809 | 2033 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8971.4269 | 8971.4269
| 19971809 | 2034 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8971.4269 | 8971.4269
| 19977196 | 2023 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5206.3359 | 5206.3359
| 19977196 | 2024 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5206.3359 | 5206.3359
| 19977196 | 2025 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5206.3359 | 5206.3359
| 19977196 | 2026 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5206.3359 | 5206.3359
| 19977196 | 2027 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5206.3359 | 5206.3359
| 19977196 | 2028 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5206.3359 | 5206.3359
| 19977196 | 2029 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5206.3359 | 5206.3359
| 19977196 | 2030 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5206.3359 | 5206.3359
| 19977196 | 2031 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5206.3359 | 5206.3359
| 19977196 | 2032 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5206.3359 | 5206.3359
| 19977196 | 2033 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5206.3359 | 5206.3359
| 19977196 | 2034 | HTN032 | 0 | 0 | 0 | 0 | 0 | 5206.3359 | 5206.3359
| 20012130 | 2023 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8912.324 | 8912.324
| 20012130 | 2024 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8912.324 | 8912.324
| 20012130 | 2025 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8912.324 | 8912.324
| 20012130 | 2026 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8912.324 | 8912.324
| 20012130 | 2027 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8912.324 | 8912.324
| 20012130 | 2028 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8912.324 | 8912.324
| 20012130 | 2029 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8912.324 | 8912.324
| 20012130 | 2030 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8912.324 | 8912.324
| 20012130 | 2031 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8912.324 | 8912.324
| 20012130 | 2032 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8912.324 | 8912.324
| 20012130 | 2033 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8912.324 | 8912.324
| 20012130 | 2034 | HTN032 | 0 | 0 | 0 | 0 | 0 | 8912.324 | 8912.324
| 20026976 | 2023 | HTN032 | 0 | 0 | 0 | 0 | 0 | 217.1435 | 217.1435
| 20026976 | 2024 | HTN032 | 0 | 0 | 0 | 0 | 0 | 217.1435 | 217.1435
| 20026976 | 2025 | HTN032 | 0 | 0 | 0 | 0 | 0 | 217.1435 | 217.1435
| 20026976 | 2026 | HTN032 | 0 | 0 | 0 | 0 | 0 | 217.1435 | 217.1435
| 20026976 | 2027 | HTN032 | 0 | 0 | 0 | 0 | 0 | 217.1435 | 217.1435
| 20026976 | 2028 | HTN032 | 0 | 0 | 0 | 0 | 0 | 217.1435 | 217.1435
| 20026976 | 2029 | HTN032 | 0 | 0 | 0 | 0 | 0 | 217.1435 | 217.1435
| 20026976 | 2030 | HTN032 | 0 | 0 | 0 | 0 | 0 | 217.1435 | 217.1435
| 20026976 | 2031 | HTN032 | 0 | 0 | 0 | 0 | 0 | 217.1435 | 217.1435
| 20026976 | 2032 | HTN032 | 0 | 0 | 0 | 0 | 0 | 217.1435 | 217.1435
| 20026976 | 2033 | HTN032 | 0 | 0 | 0 | 0 | 0 | 217.1435 | 217.1435
| 20026976 | 2034 | HTN032 | 0 | 0 | 0 | 0 | 0 | 217.1435 | 217.1435
| 20154781 | 2023 | HTN032 | 0 | 0 | 0 | 0 | 0 | 9414.3816 | 9414.3816
| 20154781 | 2024 | HTN032 | 0 | 0 | 0 | 0 | 0 | 9414.3816 | 9414.3816
| 20154781 | 2025 | HTN032 | 0 | 0 | 0 | 0 | 0 | 9414.3816 | 9414.3816
| 20154781 | 2026 | HTN032 | 0 | 0 | 0 | 0 | 0 | 9414.3816 | 9414.3816
| 20154781 | 2027 | HTN032 | 0 | 0 | 0 | 0 | 0 | 9414.3816 | 9414.3816
| 20154781 | 2028 | HTN032 | 0 | 0 | 0 | 0 | 0 | 9414.3816 | 9414.3816
| 20154781 | 2029 | HTN032 | 0 | 0 | 0 | 0 | 0 | 9414.3816 | 9414.3816
| 20154781 | 2030 | HTN032 | 0 | 0 | 0 | 0 | 0 | 9414.3816 | 9414.3816
| 20154781 | 2031 | HTN032 | 0 | 0 | 0 | 0 | 0 | 9414.3816 | 9414.3816
| 20154781 | 2032 | HTN032 | 0 | 0 | 0 | 0 | 0 | 9414.3816 | 9414.3816
| 20154781 | 2033 | HTN032 | 0 | 0 | 0 | 0 | 0 | 9414.3816 | 9414.3816
| 20154781 | 2034 | HTN032 | 0 | 0 | 0 | 0 | 0 | 9414.3816 | 9414.3816
| 74630068 | 2023 | HTN032 | 0 | 0 | 0 | 0 | 0 | 1659.7879 | 1659.7879
| 74630068 | 2024 | HTN032 | 0 | 0 | 0 | 0 | 0 | 1659.7879 | 1659.7879
| 74630068 | 2025 | HTN032 | 0 | 0 | 0 | 0 | 0 | 1659.7879 | 1659.7879
| 74630068 | 2026 | HTN032 | 0 | 0 | 0 | 0 | 0 | 1659.7879 | 1659.7879
| 74630068 | 2027 | HTN032 | 0 | 0 | 0 | 0 | 0 | 1659.7879 | 1659.7879
| 74630068 | 2028 | HTN032 | 0 | 0 | 0 | 0 | 0 | 1659.7879 | 1659.7879
| 74630068 | 2029 | HTN032 | 0 | 0 | 0 | 0 | 0 | 1659.7879 | 1659.7879
| 74630068 | 2030 | HTN032 | 0 | 0 | 0 | 0 | 0 | 1659.7879 | 1659.7879
| 74630068 | 2031 | HTN032 | 0 | 0 | 0 | 0 | 0 | 1659.7879 | 1659.7879
| 74630068 | 2032 | HTN032 | 0 | 0 | 0 | 0 | 0 | 1659.7879 | 1659.7879
| 74630068 | 2033 | HTN032 | 0 | 0 | 0 | 0 | 0 | 1659.7879 | 1659.7879
| 74630068 | 2034 | HTN032 | 0 | 0 | 0 | 0 | 0 | 1659.7879 | 1659.7879
| 161720820 | 2023 | HTN032 | 0 | 0 | 0 | 0 | 0 | 2542.9843 | 2542.9843
| 161720820 | 2024 | HTN032 | 0 | 0 | 0 | 0 | 0 | 2542.9843 | 2542.9843
| 161720820 | 2025 | HTN032 | 0 | 0 | 0 | 0 | 0 | 2542.9843 | 2542.9843
| 161720820 | 2026 | HTN032 | 0 | 0 | 0 | 0 | 0 | 2542.9843 | 2542.9843
| 161720820 | 2027 | HTN032 | 0 | 0 | 0 | 0 | 0 | 2542.9843 | 2542.9843
| 161720820 | 2028 | HTN032 | 0 | 0 | 0 | 0 | 0 | 2542.9843 | 2542.9843
| 161720820 | 2029 | HTN032 | 0 | 0 | 0 | 0 | 0 | 2542.9843 | 2542.9843
| 161720820 | 2030 | HTN032 | 0 | 0 | 0 | 0 | 0 | 2542.9843 | 2542.9843
| 161720820 | 2031 | HTN032 | 0 | 0 | 0 | 0 | 0 | 2542.9843 | 2542.9843
| 161720820 | 2032 | HTN032 | 0 | 0 | 0 | 0 | 0 | 2542.9843 | 2542.9843
| 161720820 | 2033 | HTN032 | 0 | 0 | 0 | 0 | 0 | 2542.9843 | 2542.9843
| 161720820 | 2034 | HTN032 | 0 | 0 | 0 | 0 | 0 | 2542.9843 | 2542.9843
| 44600975 | 2023 | HYT011 | 0 | 0 | 0 | 0 | 0 | 913.3591 | 913.3591
| 44600975 | 2024 | HYT011 | 0 | 0 | 0 | 0 | 0 | 913.3591 | 913.3591
| 44600975 | 2025 | HYT011 | 0 | 0 | 0 | 0 | 0 | 913.3591 | 913.3591
| 44600975 | 2026 | HYT011 | 0 | 0 | 0 | 0 | 0 | 913.3591 | 913.3591
| 44600975 | 2027 | HYT011 | 0 | 0 | 0 | 0 | 0 | 913.3591 | 913.3591
| 44600975 | 2028 | HYT011 | 0 | 0 | 0 | 0 | 0 | 913.3591 | 913.3591
| 44600975 | 2029 | HYT011 | 0 | 0 | 0 | 0 | 0 | 913.3591 | 913.3591
| 44600975 | 2030 | HYT011 | 0 | 0 | 0 | 0 | 0 | 913.3591 | 913.3591
| 44600975 | 2031 | HYT011 | 0 | 0 | 0 | 0 | 0 | 913.3591 | 913.3591
| 44600975 | 2032 | HYT011 | 0 | 0 | 0 | 0 | 0 | 913.3591 | 913.3591
| 44600975 | 2033 | HYT011 | 0 | 0 | 0 | 0 | 0 | 913.3591 | 913.3591
| 44600975 | 2034 | HYT011 | 0 | 0 | 0 | 0 | 0 | 913.3591 | 913.3591
| 54405804 | 2023 | HYT011 | 0 | 0 | 0 | 0 | 0 | 448.3793 | 448.3793
| 54405804 | 2024 | HYT011 | 0 | 0 | 0 | 0 | 0 | 448.3793 | 448.3793
| 54405804 | 2025 | HYT011 | 0 | 0 | 0 | 0 | 0 | 448.3793 | 448.3793
| 54405804 | 2026 | HYT011 | 0 | 0 | 0 | 0 | 0 | 448.3793 | 448.3793
| 54405804 | 2027 | HYT011 | 0 | 0 | 0 | 0 | 0 | 448.3793 | 448.3793
| 54405804 | 2028 | HYT011 | 0 | 0 | 0 | 0 | 0 | 448.3793 | 448.3793
| 54405804 | 2029 | HYT011 | 0 | 0 | 0 | 0 | 0 | 448.3793 | 448.3793
| 54405804 | 2030 | HYT011 | 0 | 0 | 0 | 0 | 0 | 448.3793 | 448.3793
| 54405804 | 2031 | HYT011 | 0 | 0 | 0 | 0 | 0 | 448.3793 | 448.3793
| 54405804 | 2032 | HYT011 | 0 | 0 | 0 | 0 | 0 | 448.3793 | 448.3793
| 54405804 | 2033 | HYT011 | 0 | 0 | 0 | 0 | 0 | 448.3793 | 448.3793
| 54405804 | 2034 | HYT011 | 0 | 0 | 0 | 0 | 0 | 448.3793 | 448.3793
| 54406525 | 2023 | HYT011 | 0 | 0 | 0 | 0 | 0 | 277.096 | 277.096
| 54406525 | 2024 | HYT011 | 0 | 0 | 0 | 0 | 0 | 277.096 | 277.096
| 54406525 | 2025 | HYT011 | 0 | 0 | 0 | 0 | 0 | 277.096 | 277.096
| 54406525 | 2026 | HYT011 | 0 | 0 | 0 | 0 | 0 | 277.096 | 277.096
| 54406525 | 2027 | HYT011 | 0 | 0 | 0 | 0 | 0 | 277.096 | 277.096
| 54406525 | 2028 | HYT011 | 0 | 0 | 0 | 0 | 0 | 277.096 | 277.096
| 54406525 | 2029 | HYT011 | 0 | 0 | 0 | 0 | 0 | 277.096 | 277.096
| 54406525 | 2030 | HYT011 | 0 | 0 | 0 | 0 | 0 | 277.096 | 277.096
| 54406525 | 2031 | HYT011 | 0 | 0 | 0 | 0 | 0 | 277.096 | 277.096
| 54406525 | 2032 | HYT011 | 0 | 0 | 0 | 0 | 0 | 277.096 | 277.096
| 54406525 | 2033 | HYT011 | 0 | 0 | 0 | 0 | 0 | 277.096 | 277.096
| 54406525 | 2034 | HYT011 | 0 | 0 | 0 | 0 | 0 | 277.096 | 277.096
| 85341245 | 2023 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1500.8672 | 1500.8672
| 85341245 | 2024 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1500.8672 | 1500.8672
| 85341245 | 2025 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1500.8672 | 1500.8672
| 85341245 | 2026 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1500.8672 | 1500.8672
| 85341245 | 2027 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1500.8672 | 1500.8672
| 85341245 | 2028 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1500.8672 | 1500.8672
| 85341245 | 2029 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1500.8672 | 1500.8672
| 85341245 | 2030 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1500.8672 | 1500.8672
| 85341245 | 2031 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1500.8672 | 1500.8672
| 85341245 | 2032 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1500.8672 | 1500.8672
| 85341245 | 2033 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1500.8672 | 1500.8672
| 85341245 | 2034 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1500.8672 | 1500.8672
| 157998524 | 2023 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1328.895 | 1328.895
| 157998524 | 2024 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1328.895 | 1328.895
| 157998524 | 2025 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1328.895 | 1328.895
| 157998524 | 2026 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1328.895 | 1328.895
| 157998524 | 2027 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1328.895 | 1328.895
| 157998524 | 2028 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1328.895 | 1328.895
| 157998524 | 2029 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1328.895 | 1328.895
| 157998524 | 2030 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1328.895 | 1328.895
| 157998524 | 2031 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1328.895 | 1328.895
| 157998524 | 2032 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1328.895 | 1328.895
| 157998524 | 2033 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1328.895 | 1328.895
| 157998524 | 2034 | HYT011 | 0 | 0 | 0 | 0 | 0 | 1328.895 | 1328.895
| 19937916 | 2023 | KGT003 | 4.092 | 0 | 0 | 0 | 4.092 | 2685.7644 | 2685.7644
| 19937916 | 2024 | KGT003 | 3.5707 | 0.080215 | 0 | 0 | 3.5707 | 2685.7644 | 2685.8447
| 19937916 | 2025 | KGT003 | 517.4015 | 8.125 | 0 | 0 | 517.4015 | 2685.7644 | 2693.8894
| 19937916 | 2026 | KGT003 | 4041.6705 | 27.2703 | 0 | 0 | 4041.6705 | 2685.7644 | 2713.0348
| 19937916 | 2027 | KGT003 | 7214.1269 | 55.6584 | 0 | 0 | 7214.1269 | 2685.7644 | 2741.4228
| 19937916 | 2028 | KGT003 | 7329.7141 | 64.2969 | 0 | 0 | 7329.7141 | 2685.7644 | 2750.0613
| 19937916 | 2029 | KGT003 | 7275.7751 | 41.2446 | 0 | 0 | 7275.7751 | 2685.7644 | 2727.0091
| 19937916 | 2030 | KGT003 | 7275.7751 | 41.2446 | 0 | 0 | 7275.7751 | 2685.7644 | 2727.0091
| 19937916 | 2031 | KGT003 | 7275.7751 | 41.2446 | 0 | 0 | 7275.7751 | 2685.7644 | 2727.0091
| 19937916 | 2032 | KGT003 | 7275.7751 | 41.2446 | 0 | 0 | 7275.7751 | 2685.7644 | 2727.0091
| 19937916 | 2033 | KGT003 | 6799.2189 | 179.8419 | 0 | 0 | 6799.2189 | 2685.7644 | 2865.6064
| 19937916 | 2034 | KGT003 | 6799.2189 | 179.8419 | 0 | 0 | 6799.2189 | 2685.7644 | 2865.6064
| 20014178 | 2023 | KGT003 | 0 | 0 | 0 | 0 | 0 | 374.4357 | 374.4357
| 20014178 | 2024 | KGT003 | 0 | 0 | 0 | 0 | 0 | 374.4357 | 374.4357
| 20014178 | 2025 | KGT003 | 0 | 0 | 0 | 0 | 0 | 374.4357 | 374.4357
| 20014178 | 2026 | KGT003 | 19.5551 | 0.046337 | 0 | 0 | 19.5551 | 374.4357 | 374.4821
| 20014178 | 2027 | KGT003 | 6.5488 | 0.0171 | 0 | 0 | 6.5488 | 374.4357 | 374.4528
| 20014178 | 2028 | KGT003 | 5.5138 | 0.013814 | 0 | 0 | 5.5138 | 374.4357 | 374.4495
| 20014178 | 2029 | KGT003 | 12.632 | 0.024143 | 0 | 0 | 12.632 | 374.4357 | 374.4599
| 20014178 | 2030 | KGT003 | 12.632 | 0.024143 | 0 | 0 | 12.632 | 374.4357 | 374.4599
| 20014178 | 2031 | KGT003 | 12.632 | 0.024143 | 0 | 0 | 12.632 | 374.4357 | 374.4599
| 20014178 | 2032 | KGT003 | 12.632 | 0.024143 | 0 | 0 | 12.632 | 374.4357 | 374.4599
| 20014178 | 2033 | KGT003 | 0 | 0 | 2.7864 | 122.0897 | 2.7864 | 374.4357 | 496.5255
| 20014178 | 2034 | KGT003 | 0 | 0 | 2.7864 | 122.0897 | 2.7864 | 374.4357 | 496.5255
| 20014721 | 2023 | KGT003 | 0 | 0 | 0 | 0 | 0 | 72.6397 | 72.6397
| 20014721 | 2024 | KGT003 | 0 | 0 | 0 | 0 | 0 | 72.6397 | 72.6397
| 20014721 | 2025 | KGT003 | 0 | 0 | 0 | 0 | 0 | 72.6397 | 72.6397
| 20014721 | 2026 | KGT003 | 9.5044 | 0.020849 | 0 | 0 | 9.5044 | 72.6397 | 72.6606
| 20014721 | 2027 | KGT003 | 21.0289 | 0.050739 | 0 | 0 | 21.0289 | 72.6397 | 72.6905
| 20014721 | 2028 | KGT003 | 10.439 | 0.025671 | 0 | 0 | 10.439 | 72.6397 | 72.6654
| 20014721 | 2029 | KGT003 | 7.3296 | 0.013376 | 0 | 0 | 7.3296 | 72.6397 | 72.6531
| 20014721 | 2030 | KGT003 | 7.3296 | 0.013376 | 0 | 0 | 7.3296 | 72.6397 | 72.6531
| 20014721 | 2031 | KGT003 | 7.3296 | 0.013376 | 0 | 0 | 7.3296 | 72.6397 | 72.6531
| 20014721 | 2032 | KGT003 | 7.3296 | 0.013376 | 0 | 0 | 7.3296 | 72.6397 | 72.6531
| 20014721 | 2033 | KGT003 | 0 | 0 | 0 | 0 | 0 | 72.6397 | 72.6397
| 20014721 | 2034 | KGT003 | 0 | 0 | 0 | 0 | 0 | 72.6397 | 72.6397
| 20048858 | 2023 | KGT003 | 2916.7759 | 0 | 0 | 0 | 2916.7759 | 678.1257 | 678.1257
| 20048858 | 2024 | KGT003 | 2926.3744 | 45.0029 | 0 | 0 | 2926.3744 | 678.1257 | 723.1285
| 20048858 | 2025 | KGT003 | 4979.616 | 65.9193 | 0 | 0 | 4979.616 | 678.1257 | 744.0449
| 20048858 | 2026 | KGT003 | 7712.1851 | 38.0167 | 0 | 0 | 7712.1851 | 678.1257 | 716.1424
| 20048858 | 2027 | KGT003 | 7803.6561 | 36.7172 | 0 | 0 | 7803.6561 | 678.1257 | 714.8429
| 20048858 | 2028 | KGT003 | 9496.9154 | 55.3408 | 0 | 0 | 9496.9154 | 678.1257 | 733.4664
| 20048858 | 2029 | KGT003 | 10817.2235 | 36.7745 | 0 | 0 | 10817.2235 | 678.1257 | 714.9001
| 20048858 | 2030 | KGT003 | 10817.2235 | 36.7745 | 0 | 0 | 10817.2235 | 678.1257 | 714.9001
| 20048858 | 2031 | KGT003 | 10817.2235 | 36.7745 | 0 | 0 | 10817.2235 | 678.1257 | 714.9001
| 20048858 | 2032 | KGT003 | 10817.2235 | 36.7745 | 0 | 0 | 10817.2235 | 678.1257 | 714.9001
| 20048858 | 2033 | KGT003 | 11945.3394 | 308.8237 | 0 | 0 | 11945.3394 | 678.1257 | 986.9494
| 20048858 | 2034 | KGT003 | 11945.3394 | 308.8237 | 0 | 0 | 11945.3394 | 678.1257 | 986.9494
| 20050369 | 2023 | KGT003 | 41.8248 | 0 | 0 | 0 | 41.8248 | 43.74 | 43.74
| 20050369 | 2024 | KGT003 | 34.4892 | 0.45589 | 0 | 0 | 34.4892 | 43.74 | 44.1959
| 20050369 | 2025 | KGT003 | 212.8396 | 2.8063 | 0 | 0 | 212.8396 | 43.74 | 46.5463
| 20050369 | 2026 | KGT003 | 446.5795 | 1.0953 | 0 | 0 | 446.5795 | 43.74 | 44.8353
| 20050369 | 2027 | KGT003 | 745.0004 | 3.0282 | 0 | 0 | 745.0004 | 43.74 | 46.7682
| 20050369 | 2028 | KGT003 | 1132.743 | 5.9091 | 0 | 0 | 1132.743 | 43.74 | 49.6491
| 20050369 | 2029 | KGT003 | 1439.0531 | 3.8835 | 0 | 0 | 1439.0531 | 43.74 | 47.6235
| 20050369 | 2030 | KGT003 | 1439.0531 | 3.8835 | 0 | 0 | 1439.0531 | 43.74 | 47.6235
| 20050369 | 2031 | KGT003 | 1439.0531 | 3.8835 | 0 | 0 | 1439.0531 | 43.74 | 47.6235
| 20050369 | 2032 | KGT003 | 1439.0531 | 3.8835 | 0 | 0 | 1439.0531 | 43.74 | 47.6235
| 20050369 | 2033 | KGT003 | 1853.4443 | 44.5406 | 0 | 0 | 1853.4443 | 43.74 | 88.2806
| 20050369 | 2034 | KGT003 | 1853.4443 | 44.5406 | 0 | 0 | 1853.4443 | 43.74 | 88.2806
| 20526231 | 2023 | KGT003 | 43.8223 | 0 | 0 | 0 | 43.8223 | 1262.4853 | 1262.4853
| 20526231 | 2024 | KGT003 | 300.5144 | 3.754 | 0 | 0 | 300.5144 | 1262.4853 | 1266.2394
| 20526231 | 2025 | KGT003 | 986.4947 | 11.9848 | 0 | 0 | 986.4947 | 1262.4853 | 1274.4701
| 20526231 | 2026 | KGT003 | 3027.0672 | 11.8057 | 0 | 0 | 3027.0672 | 1262.4853 | 1274.2911
| 20526231 | 2027 | KGT003 | 3611.0869 | 14.9236 | 0 | 0 | 3611.0869 | 1262.4853 | 1277.4089
| 20526231 | 2028 | KGT003 | 3272.9992 | 14.4562 | 0 | 0 | 3272.9992 | 1262.4853 | 1276.9415
| 20526231 | 2029 | KGT003 | 3445.1838 | 9.3911 | 0 | 0 | 3445.1838 | 1262.4853 | 1271.8765
| 20526231 | 2030 | KGT003 | 3445.1838 | 9.3911 | 0 | 0 | 3445.1838 | 1262.4853 | 1271.8765
| 20526231 | 2031 | KGT003 | 3445.1838 | 9.3911 | 0 | 0 | 3445.1838 | 1262.4853 | 1271.8765
| 20526231 | 2032 | KGT003 | 3445.1838 | 9.3911 | 0 | 0 | 3445.1838 | 1262.4853 | 1271.8765
| 20526231 | 2033 | KGT003 | 10210.3112 | 251.27 | 0 | 0 | 10210.3112 | 1262.4853 | 1513.7553
| 20526231 | 2034 | KGT003 | 10210.3112 | 251.27 | 0 | 0 | 10210.3112 | 1262.4853 | 1513.7553
| 20560831 | 2023 | KGT003 | 2.548 | 0 | 0 | 0 | 2.548 | 2417.5994 | 2417.5994
| 20560831 | 2024 | KGT003 | 2.5129 | 0.031322 | 0 | 0 | 2.5129 | 2417.5994 | 2417.6308
| 20560831 | 2025 | KGT003 | 9.5468 | 0.12931 | 0 | 0 | 9.5468 | 2417.5994 | 2417.7287
| 20560831 | 2026 | KGT003 | 9.8888 | 0.061791 | 0 | 0 | 9.8888 | 2417.5994 | 2417.6612
| 20560831 | 2027 | KGT003 | 82.7761 | 0.18385 | 0 | 0 | 82.7761 | 2417.5994 | 2417.7833
| 20560831 | 2028 | KGT003 | 8.2543 | 0.020811 | 0 | 0 | 8.2543 | 2417.5994 | 2417.6202
| 20560831 | 2029 | KGT003 | 9.2144 | 0.018299 | 0 | 0 | 9.2144 | 2417.5994 | 2417.6177
| 20560831 | 2030 | KGT003 | 9.2144 | 0.018299 | 0 | 0 | 9.2144 | 2417.5994 | 2417.6177
| 20560831 | 2031 | KGT003 | 9.2144 | 0.018299 | 0 | 0 | 9.2144 | 2417.5994 | 2417.6177
| 20560831 | 2032 | KGT003 | 9.2144 | 0.018299 | 0 | 0 | 9.2144 | 2417.5994 | 2417.6177
| 20560831 | 2033 | KGT003 | 0 | 0 | 0 | 0 | 0 | 2417.5994 | 2417.5994
| 20560831 | 2034 | KGT003 | 0 | 0 | 0 | 0 | 0 | 2417.5994 | 2417.5994
| 20683854 | 2023 | KGT003 | 20.475 | 0 | 0 | 0 | 20.475 | 1052.0247 | 1052.0247
| 20683854 | 2024 | KGT003 | 25.7955 | 0.3575 | 0 | 0 | 25.7955 | 1052.0247 | 1052.3822
| 20683854 | 2025 | KGT003 | 43.4345 | 0.71115 | 0 | 0 | 43.4345 | 1052.0247 | 1052.7358
| 20683854 | 2026 | KGT003 | 84.5375 | 0.63782 | 0 | 0 | 84.5375 | 1052.0247 | 1052.6625
| 20683854 | 2027 | KGT003 | 106.2973 | 0.2384 | 0 | 0 | 106.2973 | 1052.0247 | 1052.2631
| 20683854 | 2028 | KGT003 | 17.026 | 0.15774 | 2.6414 | 115.7336 | 19.6674 | 1052.0247 | 1167.916
| 20683854 | 2029 | KGT003 | 23.6844 | 0.078157 | 32.0617 | 1404.802 | 55.7462 | 1052.0247 | 2456.9048
| 20683854 | 2030 | KGT003 | 23.6844 | 0.078157 | 32.0617 | 1404.802 | 55.7462 | 1052.0247 | 2456.9048
| 20683854 | 2031 | KGT003 | 23.6844 | 0.078157 | 32.0617 | 1404.802 | 55.7462 | 1052.0247 | 2456.9048
| 20683854 | 2032 | KGT003 | 23.6844 | 0.078157 | 32.0617 | 1404.802 | 55.7462 | 1052.0247 | 2456.9048
| 20683854 | 2033 | KGT003 | 0 | 0 | 1633.5518 | 71574.9831 | 1633.5518 | 1052.0247 | 72627.0078
| 20683854 | 2034 | KGT003 | 0 | 0 | 1633.5518 | 71574.9831 | 1633.5518 | 1052.0247 | 72627.0078
| 155131373 | 2023 | KGT003 | 0 | 0 | 0.54477 | 23.8692 | 0.54477 | 821.403 | 845.2722
| 155131373 | 2024 | KGT003 | 0 | 0 | 0.41839 | 18.3318 | 0.41839 | 821.403 | 839.7348
| 155131373 | 2025 | KGT003 | 0 | 0 | 1.0497 | 45.9932 | 1.0497 | 821.403 | 867.3962
| 155131373 | 2026 | KGT003 | 0 | 0 | 4.0626 | 178.0032 | 4.0626 | 821.403 | 999.4063
| 155131373 | 2027 | KGT003 | 0 | 0 | 12.8774 | 564.2294 | 12.8774 | 821.403 | 1385.6324
| 155131373 | 2028 | KGT003 | 0 | 0 | 2193.8266 | 96123.7369 | 2193.8266 | 821.403 | 96945.1399
| 155131373 | 2029 | KGT003 | 0 | 0 | 3356.9915 | 147088.458 | 3356.9915 | 821.403 | 147909.8611
| 155131373 | 2030 | KGT003 | 0 | 0 | 3356.9915 | 147088.458 | 3356.9915 | 821.403 | 147909.8611
| 155131373 | 2031 | KGT003 | 0 | 0 | 3356.9915 | 147088.458 | 3356.9915 | 821.403 | 147909.8611
| 155131373 | 2032 | KGT003 | 0 | 0 | 3356.9915 | 147088.458 | 3356.9915 | 821.403 | 147909.8611
| 155131373 | 2033 | KGT003 | 0 | 0 | 13963.8561 | 611834.1541 | 13963.8561 | 821.403 | 612655.5571
| 155131373 | 2034 | KGT003 | 0 | 0 | 13963.8561 | 611834.1541 | 13963.8561 | 821.403 | 612655.5571
| 190649714 | 2023 | KGT003 | 0.024434 | 0 | 0 | 0 | 0.024434 | 374.7535 | 374.7535
| 190649714 | 2024 | KGT003 | 0 | 0 | 0 | 0 | 0 | 374.7535 | 374.7535
| 190649714 | 2025 | KGT003 | 1530.7332 | 43.3889 | 0 | 0 | 1530.7332 | 374.7535 | 418.1424
| 190649714 | 2026 | KGT003 | 1191.3022 | 23.3247 | 0 | 0 | 1191.3022 | 374.7535 | 398.0782
| 190649714 | 2027 | KGT003 | 964.1969 | 14.3225 | 0 | 0 | 964.1969 | 374.7535 | 389.076
| 190649714 | 2028 | KGT003 | 603.4607 | 12.2294 | 0 | 0 | 603.4607 | 374.7535 | 386.9829
| 190649714 | 2029 | KGT003 | 421.2308 | 7.0873 | 0 | 0 | 421.2308 | 374.7535 | 381.8408
| 190649714 | 2030 | KGT003 | 421.2308 | 7.0873 | 0 | 0 | 421.2308 | 374.7535 | 381.8408
| 190649714 | 2031 | KGT003 | 421.2308 | 7.0873 | 0 | 0 | 421.2308 | 374.7535 | 381.8408
| 190649714 | 2032 | KGT003 | 421.2308 | 7.0873 | 0 | 0 | 421.2308 | 374.7535 | 381.8408
| 190649714 | 2033 | KGT003 | 178.8481 | 9.1049 | 0 | 0 | 178.8481 | 374.7535 | 383.8585
| 190649714 | 2034 | KGT003 | 178.8481 | 9.1049 | 0 | 0 | 178.8481 | 374.7535 | 383.8585
| 20038569 | 2023 | KGT004 | 0 | 0 | 0.37024 | 16.2221 | 0.37024 | 10911.8296 | 10928.0516
| 20038569 | 2024 | KGT004 | 0 | 0 | 0.46086 | 20.1929 | 0.46086 | 10911.8296 | 10932.0224
| 20038569 | 2025 | KGT004 | 0 | 0 | 0 | 0 | 0 | 10911.8296 | 10911.8296
| 20038569 | 2026 | KGT004 | 1.5587 | 0.0017934 | 0 | 0 | 1.5587 | 10911.8296 | 10911.8313
| 20038569 | 2027 | KGT004 | 377.3576 | 3.0649 | 0 | 0 | 377.3576 | 10911.8296 | 10914.8945
| 20038569 | 2028 | KGT004 | 1087.1813 | 4.3027 | 0 | 0 | 1087.1813 | 10911.8296 | 10916.1323
| 20038569 | 2029 | KGT004 | 1988.6784 | 7.1478 | 0 | 0 | 1988.6784 | 10911.8296 | 10918.9774
| 20038569 | 2030 | KGT004 | 2410.6631 | 9.3408 | 0 | 0 | 2410.6631 | 10911.8296 | 10921.1704
| 20038569 | 2031 | KGT004 | 2681.8883 | 20.241 | 0 | 0 | 2681.8883 | 10911.8296 | 10932.0705
| 20038569 | 2032 | KGT004 | 2765.012 | 34.1983 | 0 | 0 | 2765.012 | 10911.8296 | 10946.0278
| 20038569 | 2033 | KGT004 | 4178.2256 | 113.5977 | 0 | 0 | 4178.2256 | 10911.8296 | 11025.4273
| 20038569 | 2034 | KGT004 | 4663.5568 | 143.9349 | 0 | 0 | 4663.5568 | 10911.8296 | 11055.7644
| 20045998 | 2023 | KGT004 | 7546.2353 | 0 | 0 | 0 | 7546.2353 | 4649.1584 | 4649.1584
| 20045998 | 2024 | KGT004 | 7724.1459 | 171.7141 | 0 | 0 | 7724.1459 | 4649.1584 | 4820.8725
| 20045998 | 2025 | KGT004 | 7965.5584 | 151.5945 | 0 | 0 | 7965.5584 | 4649.1584 | 4800.7529
| 20045998 | 2026 | KGT004 | 12044.2042 | 139.5572 | 0 | 0 | 12044.2042 | 4649.1584 | 4788.7156
| 20045998 | 2027 | KGT004 | 12526.0989 | 138.1851 | 0 | 0 | 12526.0989 | 4649.1584 | 4787.3435
| 20045998 | 2028 | KGT004 | 17020.0556 | 194.7166 | 0 | 0 | 17020.0556 | 4649.1584 | 4843.8749
| 20045998 | 2029 | KGT004 | 16902.7507 | 150.6831 | 0 | 0 | 16902.7507 | 4649.1584 | 4799.8415
| 20045998 | 2030 | KGT004 | 21760.4294 | 215.4593 | 0 | 0 | 21760.4294 | 4649.1584 | 4864.6177
| 20045998 | 2031 | KGT004 | 22571.1944 | 313.2422 | 0 | 0 | 22571.1944 | 4649.1584 | 4962.4006
| 20045998 | 2032 | KGT004 | 27825.7185 | 592.7024 | 0 | 0 | 27825.7185 | 4649.1584 | 5241.8608
| 20045998 | 2033 | KGT004 | 31815.4273 | 1149.3137 | 0 | 0 | 31815.4273 | 4649.1584 | 5798.4721
| 20045998 | 2034 | KGT004 | 35589.0397 | 1520.2742 | 0 | 0 | 35589.0397 | 4649.1584 | 6169.4326
| 20046375 | 2023 | KGT004 | 140.458 | 0 | 0 | 0 | 140.458 | 2226.2095 | 2226.2095
| 20046375 | 2024 | KGT004 | 507.9052 | 7.161 | 0 | 0 | 507.9052 | 2226.2095 | 2233.3705
| 20046375 | 2025 | KGT004 | 1025.498 | 15.6696 | 0 | 0 | 1025.498 | 2226.2095 | 2241.8791
| 20046375 | 2026 | KGT004 | 1625.8434 | 10.4454 | 0 | 0 | 1625.8434 | 2226.2095 | 2236.6549
| 20046375 | 2027 | KGT004 | 3666.6355 | 26.3462 | 0 | 0 | 3666.6355 | 2226.2095 | 2252.5557
| 20046375 | 2028 | KGT004 | 5060.6888 | 39.3968 | 0 | 0 | 5060.6888 | 2226.2095 | 2265.6063
| 20046375 | 2029 | KGT004 | 15068.0739 | 128.6902 | 0 | 0 | 15068.0739 | 2226.2095 | 2354.8998
| 20046375 | 2030 | KGT004 | 15423.7896 | 154.4474 | 0 | 0 | 15423.7896 | 2226.2095 | 2380.657
| 20046375 | 2031 | KGT004 | 15954.0871 | 259.0602 | 0 | 0 | 15954.0871 | 2226.2095 | 2485.2697
| 20046375 | 2032 | KGT004 | 15879.8028 | 379.1935 | 0 | 0 | 15879.8028 | 2226.2095 | 2605.403
| 20046375 | 2033 | KGT004 | 15778.3241 | 603.3127 | 0 | 0 | 15778.3241 | 2226.2095 | 2829.5222
| 20046375 | 2034 | KGT004 | 15870.3064 | 733.0401 | 0 | 0 | 15870.3064 | 2226.2095 | 2959.2496
| 20046951 | 2023 | KGT004 | 3619.4232 | 0 | 0 | 0 | 3619.4232 | 10376.0043 | 10376.0043
| 20046951 | 2024 | KGT004 | 4028.7089 | 62.8525 | 0 | 0 | 4028.7089 | 10376.0043 | 10438.8568
| 20046951 | 2025 | KGT004 | 6952.6696 | 114.2737 | 0 | 0 | 6952.6696 | 10376.0043 | 10490.278
| 20046951 | 2026 | KGT004 | 7761.87 | 63.1643 | 0 | 0 | 7761.87 | 10376.0043 | 10439.1686
| 20046951 | 2027 | KGT004 | 10969.0776 | 99.387 | 0 | 0 | 10969.0776 | 10376.0043 | 10475.3913
| 20046951 | 2028 | KGT004 | 10600.2535 | 111.5323 | 0 | 0 | 10600.2535 | 10376.0043 | 10487.5365
| 20046951 | 2029 | KGT004 | 21231.0348 | 225.9198 | 0 | 0 | 21231.0348 | 10376.0043 | 10601.9241
| 20046951 | 2030 | KGT004 | 28235.9619 | 365.078 | 0 | 0 | 28235.9619 | 10376.0043 | 10741.0822
| 20046951 | 2031 | KGT004 | 34924.3276 | 584.9936 | 0 | 0 | 34924.3276 | 10376.0043 | 10960.9979
| 20046951 | 2032 | KGT004 | 35213.2551 | 848.8012 | 0 | 0 | 35213.2551 | 10376.0043 | 11224.8055
| 20046951 | 2033 | KGT004 | 35836.4962 | 1339.8162 | 0 | 0 | 35836.4962 | 10376.0043 | 11715.8205
| 20046951 | 2034 | KGT004 | 41104.8576 | 1800.9284 | 0 | 0 | 41104.8576 | 10376.0043 | 12176.9327
| 20608641 | 2023 | KGT004 | 0 | 0 | 0 | 0 | 0 | 744.455 | 744.455
| 20608641 | 2024 | KGT004 | 0 | 0 | 0 | 0 | 0 | 744.455 | 744.455
| 20608641 | 2025 | KGT004 | 0 | 0 | 0 | 0 | 0 | 744.455 | 744.455
| 20608641 | 2026 | KGT004 | 0 | 0 | 0 | 0 | 0 | 744.455 | 744.455
| 20608641 | 2027 | KGT004 | 0 | 0 | 0 | 0 | 0 | 744.455 | 744.455
| 20608641 | 2028 | KGT004 | 0 | 0 | 0 | 0 | 0 | 744.455 | 744.455
| 20608641 | 2029 | KGT004 | 0 | 0 | 0 | 0 | 0 | 744.455 | 744.455
| 20608641 | 2030 | KGT004 | 0 | 0 | 0 | 0 | 0 | 744.455 | 744.455
| 20608641 | 2031 | KGT004 | 782.3701 | 4.2363 | 0 | 0 | 782.3701 | 744.455 | 748.6914
| 20608641 | 2032 | KGT004 | 768.5931 | 7.4958 | 0 | 0 | 768.5931 | 744.455 | 751.9508
| 20608641 | 2033 | KGT004 | 961.8579 | 21.5507 | 0 | 0 | 961.8579 | 744.455 | 766.0058
| 20608641 | 2034 | KGT004 | 1139.6021 | 29.2629 | 0 | 0 | 1139.6021 | 744.455 | 773.7179
| 128871345 | 2023 | KGT004 | 0 | 0 | 0 | 0 | 0 | 4338.2846 | 4338.2846
| 128871345 | 2024 | KGT004 | 0 | 0 | 0 | 0 | 0 | 4338.2846 | 4338.2846
| 128871345 | 2025 | KGT004 | 0 | 0 | 0 | 0 | 0 | 4338.2846 | 4338.2846
| 128871345 | 2026 | KGT004 | 0 | 0 | 0 | 0 | 0 | 4338.2846 | 4338.2846
| 128871345 | 2027 | KGT004 | 0 | 0 | 0 | 0 | 0 | 4338.2846 | 4338.2846
| 128871345 | 2028 | KGT004 | 3294.5916 | 21.3703 | 0 | 0 | 3294.5916 | 4338.2846 | 4359.6549
| 128871345 | 2029 | KGT004 | 5034.0414 | 25.067 | 0 | 0 | 5034.0414 | 4338.2846 | 4363.3516
| 128871345 | 2030 | KGT004 | 5550.4089 | 32.6115 | 0 | 0 | 5550.4089 | 4338.2846 | 4370.8961
| 128871345 | 2031 | KGT004 | 8707.1499 | 94.5177 | 0 | 0 | 8707.1499 | 4338.2846 | 4432.8023
| 128871345 | 2032 | KGT004 | 9050.9184 | 155.2901 | 0 | 0 | 9050.9184 | 4338.2846 | 4493.5747
| 128871345 | 2033 | KGT004 | 9493.7291 | 298.6104 | 0 | 0 | 9493.7291 | 4338.2846 | 4636.895
| 128871345 | 2034 | KGT004 | 9766.6509 | 360.7523 | 0 | 0 | 9766.6509 | 4338.2846 | 4699.0369
| 154971194 | 2023 | KGT004 | 0 | 0 | 0 | 0 | 0 | 669.0828 | 669.0828
| 154971194 | 2024 | KGT004 | 0 | 0 | 0 | 0 | 0 | 669.0828 | 669.0828
| 154971194 | 2025 | KGT004 | 0 | 0 | 0 | 0 | 0 | 669.0828 | 669.0828
| 154971194 | 2026 | KGT004 | 0 | 0 | 0 | 0 | 0 | 669.0828 | 669.0828
| 154971194 | 2027 | KGT004 | 0 | 0 | 0 | 0 | 0 | 669.0828 | 669.0828
| 154971194 | 2028 | KGT004 | 0 | 0 | 0 | 0 | 0 | 669.0828 | 669.0828
| 154971194 | 2029 | KGT004 | 0 | 0 | 0 | 0 | 0 | 669.0828 | 669.0828
| 154971194 | 2030 | KGT004 | 0 | 0 | 0 | 0 | 0 | 669.0828 | 669.0828
| 154971194 | 2031 | KGT004 | 0 | 0 | 0 | 0 | 0 | 669.0828 | 669.0828
| 154971194 | 2032 | KGT004 | 0 | 0 | 0 | 0 | 0 | 669.0828 | 669.0828
| 154971194 | 2033 | KGT004 | 0 | 0 | 0 | 0 | 0 | 669.0828 | 669.0828
| 154971194 | 2034 | KGT004 | 0 | 0 | 0 | 0 | 0 | 669.0828 | 669.0828
| 161224166 | 2023 | KGT004 | 0 | 0 | 0 | 0 | 0 | 7415.1491 | 7415.1491
| 161224166 | 2024 | KGT004 | 0 | 0 | 0 | 0 | 0 | 7415.1491 | 7415.1491
| 161224166 | 2025 | KGT004 | 0 | 0 | 0 | 0 | 0 | 7415.1491 | 7415.1491
| 161224166 | 2026 | KGT004 | 0 | 0 | 0 | 0 | 0 | 7415.1491 | 7415.1491
| 161224166 | 2027 | KGT004 | 935.0592 | 6.5435 | 0 | 0 | 935.0592 | 7415.1491 | 7421.6926
| 161224166 | 2028 | KGT004 | 1345.7116 | 9.5393 | 0 | 0 | 1345.7116 | 7415.1491 | 7424.6885
| 161224166 | 2029 | KGT004 | 4786.5681 | 40.1372 | 0 | 0 | 4786.5681 | 7415.1491 | 7455.2863
| 161224166 | 2030 | KGT004 | 5120.6459 | 54.7332 | 0 | 0 | 5120.6459 | 7415.1491 | 7469.8823
| 161224166 | 2031 | KGT004 | 5256.033 | 78.6089 | 0 | 0 | 5256.033 | 7415.1491 | 7493.7581
| 161224166 | 2032 | KGT004 | 5268.6469 | 124.5549 | 0 | 0 | 5268.6469 | 7415.1491 | 7539.704
| 161224166 | 2033 | KGT004 | 7503.6085 | 301.4584 | 0 | 0 | 7503.6085 | 7415.1491 | 7716.6075
| 161224166 | 2034 | KGT004 | 7712.7147 | 364.9278 | 0 | 0 | 7712.7147 | 7415.1491 | 7780.077
| 162581581 | 2023 | KGT004 | 11.3017 | 0 | 0 | 0 | 11.3017 | 15070.8844 | 15070.8844
| 162581581 | 2024 | KGT004 | 65.5204 | 0.62541 | 0 | 0 | 65.5204 | 15070.8844 | 15071.5098
| 162581581 | 2025 | KGT004 | 624.1624 | 7.8903 | 0 | 0 | 624.1624 | 15070.8844 | 15078.7747
| 162581581 | 2026 | KGT004 | 3931.8274 | 20.3583 | 0 | 0 | 3931.8274 | 15070.8844 | 15091.2428
| 162581581 | 2027 | KGT004 | 6709.186 | 43.6101 | 0 | 0 | 6709.186 | 15070.8844 | 15114.4946
| 162581581 | 2028 | KGT004 | 10692.5104 | 86.2176 | 0 | 0 | 10692.5104 | 15070.8844 | 15157.102
| 162581581 | 2029 | KGT004 | 10901.4281 | 58.8792 | 0 | 0 | 10901.4281 | 15070.8844 | 15129.7636
| 162581581 | 2030 | KGT004 | 17638.6203 | 137.8349 | 0 | 0 | 17638.6203 | 15070.8844 | 15208.7193
| 162581581 | 2031 | KGT004 | 27880.2481 | 378.3095 | 0 | 0 | 27880.2481 | 15070.8844 | 15449.1939
| 162581581 | 2032 | KGT004 | 33647.7565 | 727.9472 | 0 | 0 | 33647.7565 | 15070.8844 | 15798.8316
| 162581581 | 2033 | KGT004 | 36475.8639 | 1337.6565 | 0 | 0 | 36475.8639 | 15070.8844 | 16408.5409
| 162581581 | 2034 | KGT004 | 38827.4293 | 1683.4977 | 0 | 0 | 38827.4293 | 15070.8844 | 16754.3821
| 163034159 | 2023 | KGT004 | 2345.8768 | 0 | 0 | 0 | 2345.8768 | 7516.5471 | 7516.5471
| 163034159 | 2024 | KGT004 | 2484.4959 | 49.3147 | 0 | 0 | 2484.4959 | 7516.5471 | 7565.8618
| 163034159 | 2025 | KGT004 | 5502.9458 | 130.8838 | 0 | 0 | 5502.9458 | 7516.5471 | 7647.4309
| 163034159 | 2026 | KGT004 | 7469.4192 | 90.2016 | 0 | 0 | 7469.4192 | 7516.5471 | 7606.7488
| 163034159 | 2027 | KGT004 | 9444.5116 | 102.9615 | 0 | 0 | 9444.5116 | 7516.5471 | 7619.5086
| 163034159 | 2028 | KGT004 | 12752.8034 | 147.6087 | 0 | 0 | 12752.8034 | 7516.5471 | 7664.1558
| 163034159 | 2029 | KGT004 | 12671.7645 | 108.0565 | 0 | 0 | 12671.7645 | 7516.5471 | 7624.6036
| 163034159 | 2030 | KGT004 | 13757.7658 | 134.2573 | 0 | 0 | 13757.7658 | 7516.5471 | 7650.8044
| 163034159 | 2031 | KGT004 | 16779.561 | 219.0535 | 0 | 0 | 16779.561 | 7516.5471 | 7735.6007
| 163034159 | 2032 | KGT004 | 24395.3063 | 492.4413 | 0 | 0 | 24395.3063 | 7516.5471 | 8008.9884
| 163034159 | 2033 | KGT004 | 28279.7661 | 948.829 | 0 | 0 | 28279.7661 | 7516.5471 | 8465.3762
| 163034159 | 2034 | KGT004 | 28810.652 | 1122.0725 | 0 | 0 | 28810.652 | 7516.5471 | 8638.6196
| 19827189 | 2023 | KRT012 | 0 | 0 | 251.2642 | 11822.7207 | 251.2642 | 2740.5876 | 14563.3082
| 19827189 | 2024 | KRT012 | 0 | 0 | 294.7233 | 13867.599 | 294.7233 | 2740.5876 | 16608.1866
| 19827189 | 2025 | KRT012 | 0 | 0 | 315.5954 | 14849.6945 | 315.5954 | 2740.5876 | 17590.2821
| 19827189 | 2026 | KRT012 | 0 | 0 | 403.7832 | 18999.1896 | 403.7832 | 2740.5876 | 21739.7772
| 19827189 | 2027 | KRT012 | 0 | 0 | 431.4517 | 20301.0726 | 431.4517 | 2740.5876 | 23041.6601
| 19827189 | 2028 | KRT012 | 0 | 0 | 499.0003 | 23479.4338 | 499.0003 | 2740.5876 | 26220.0214
| 19827189 | 2029 | KRT012 | 0 | 0 | 556.5554 | 26187.5677 | 556.5554 | 2740.5876 | 28928.1552
| 19827189 | 2030 | KRT012 | 0 | 0 | 559.2714 | 26315.3634 | 559.2714 | 2740.5876 | 29055.9509
| 19827189 | 2031 | KRT012 | 0 | 0 | 723.4323 | 34039.6174 | 723.4323 | 2740.5876 | 36780.205
| 19827189 | 2032 | KRT012 | 0 | 0 | 849.015 | 39948.6529 | 849.015 | 2740.5876 | 42689.2404
| 19827189 | 2033 | KRT012 | 0 | 0 | 1068.2177 | 50262.7839 | 1068.2177 | 2740.5876 | 53003.3714
| 19827189 | 2034 | KRT012 | 0 | 0 | 1060.691 | 49908.633 | 1060.691 | 2740.5876 | 52649.2206
| 19829689 | 2023 | KRT012 | 0 | 0 | 10.0089 | 470.9502 | 10.0089 | 1734.0699 | 2205.0202
| 19829689 | 2024 | KRT012 | 0 | 0 | 16.3589 | 769.7345 | 16.3589 | 1734.0699 | 2503.8044
| 19829689 | 2025 | KRT012 | 0 | 0 | 23.0237 | 1083.3308 | 23.0237 | 1734.0699 | 2817.4007
| 19829689 | 2026 | KRT012 | 0 | 0 | 24.6751 | 1161.036 | 24.6751 | 1734.0699 | 2895.106
| 19829689 | 2027 | KRT012 | 0 | 0 | 30.7425 | 1446.5245 | 30.7425 | 1734.0699 | 3180.5944
| 19829689 | 2028 | KRT012 | 0 | 0 | 46.4809 | 2187.0635 | 46.4809 | 1734.0699 | 3921.1335
| 19829689 | 2029 | KRT012 | 0 | 0 | 64.498 | 3034.8197 | 64.498 | 1734.0699 | 4768.8897
| 19829689 | 2030 | KRT012 | 0 | 0 | 69.1792 | 3255.0826 | 69.1792 | 1734.0699 | 4989.1525
| 19829689 | 2031 | KRT012 | 0 | 0 | 77.5238 | 3647.7234 | 77.5238 | 1734.0699 | 5381.7934
| 19829689 | 2032 | KRT012 | 0 | 0 | 97.9415 | 4608.4373 | 97.9415 | 1734.0699 | 6342.5073
| 19829689 | 2033 | KRT012 | 0 | 0 | 135.4389 | 6372.8007 | 135.4389 | 1734.0699 | 8106.8707
| 19829689 | 2034 | KRT012 | 0 | 0 | 147.502 | 6940.4017 | 147.502 | 1734.0699 | 8674.4717
| 20490218 | 2023 | KRT012 | 0 | 0 | 0 | 0 | 0 | 5826.5005 | 5826.5005
| 20490218 | 2024 | KRT012 | 293.5988 | 4.7378 | 0 | 0 | 293.5988 | 5826.5005 | 5831.2383
| 20490218 | 2025 | KRT012 | 278.4303 | 4.9582 | 0 | 0 | 278.4303 | 5826.5005 | 5831.4587
| 20490218 | 2026 | KRT012 | 984.5685 | 7.7121 | 0 | 0 | 984.5685 | 5826.5005 | 5834.2126
| 20490218 | 2027 | KRT012 | 1737.5028 | 10.3397 | 0 | 0 | 1737.5028 | 5826.5005 | 5836.8402
| 20490218 | 2028 | KRT012 | 2705.8793 | 15.0922 | 0 | 0 | 2705.8793 | 5826.5005 | 5841.5927
| 20490218 | 2029 | KRT012 | 2776.9329 | 12.6897 | 0 | 0 | 2776.9329 | 5826.5005 | 5839.1902
| 20490218 | 2030 | KRT012 | 3562.0281 | 17.9474 | 0 | 0 | 3562.0281 | 5826.5005 | 5844.4479
| 20490218 | 2031 | KRT012 | 5772.7979 | 51.0638 | 0 | 0 | 5772.7979 | 5826.5005 | 5877.5643
| 20490218 | 2032 | KRT012 | 8910.4708 | 104.2716 | 0 | 0 | 8910.4708 | 5826.5005 | 5930.7721
| 20490218 | 2033 | KRT012 | 10854.0607 | 279.4957 | 9.1997 | 432.8738 | 10863.2605 | 5826.5005 | 6538.8701
| 20490218 | 2034 | KRT012 | 18844.9964 | 602.5466 | 14.2318 | 669.6476 | 18859.2282 | 5826.5005 | 7098.6947
| 20490229 | 2023 | KRT012 | 12.7357 | 0 | 0 | 0 | 12.7357 | 1659.9234 | 1659.9234
| 20490229 | 2024 | KRT012 | 447.4521 | 6.4309 | 0 | 0 | 447.4521 | 1659.9234 | 1666.3543
| 20490229 | 2025 | KRT012 | 382.4533 | 6.0747 | 0 | 0 | 382.4533 | 1659.9234 | 1665.998
| 20490229 | 2026 | KRT012 | 1919.9032 | 13.7004 | 0 | 0 | 1919.9032 | 1659.9234 | 1673.6238
| 20490229 | 2027 | KRT012 | 2137.6417 | 12.2754 | 0 | 0 | 2137.6417 | 1659.9234 | 1672.1988
| 20490229 | 2028 | KRT012 | 2426.8509 | 14.7876 | 0 | 0 | 2426.8509 | 1659.9234 | 1674.7109
| 20490229 | 2029 | KRT012 | 2453.759 | 12.7892 | 0 | 0 | 2453.759 | 1659.9234 | 1672.7126
| 20490229 | 2030 | KRT012 | 2599.7531 | 14.0499 | 0 | 0 | 2599.7531 | 1659.9234 | 1673.9733
| 20490229 | 2031 | KRT012 | 2866.1772 | 25.4424 | 0 | 0 | 2866.1772 | 1659.9234 | 1685.3658
| 20490229 | 2032 | KRT012 | 8921.9949 | 135.7132 | 0 | 0 | 8921.9949 | 1659.9234 | 1795.6366
| 20490229 | 2033 | KRT012 | 9760.1599 | 272.6456 | 0 | 0 | 9760.1599 | 1659.9234 | 1932.5689
| 20490229 | 2034 | KRT012 | 10955.2959 | 384.4547 | 0 | 0 | 10955.2959 | 1659.9234 | 2044.378
| 20490297 | 2023 | KRT012 | 0 | 0 | 0 | 0 | 0 | 1266.0795 | 1266.0795
| 20490297 | 2024 | KRT012 | 0 | 0 | 0 | 0 | 0 | 1266.0795 | 1266.0795
| 20490297 | 2025 | KRT012 | 0 | 0 | 0 | 0 | 0 | 1266.0795 | 1266.0795
| 20490297 | 2026 | KRT012 | 0 | 0 | 0 | 0 | 0 | 1266.0795 | 1266.0795
| 20490297 | 2027 | KRT012 | 0 | 0 | 0 | 0 | 0 | 1266.0795 | 1266.0795
| 20490297 | 2028 | KRT012 | 0 | 0 | 0 | 0 | 0 | 1266.0795 | 1266.0795
| 20490297 | 2029 | KRT012 | 0 | 0 | 0 | 0 | 0 | 1266.0795 | 1266.0795
| 20490297 | 2030 | KRT012 | 0 | 0 | 0 | 0 | 0 | 1266.0795 | 1266.0795
| 20490297 | 2031 | KRT012 | 0 | 0 | 0 | 0 | 0 | 1266.0795 | 1266.0795
| 20490297 | 2032 | KRT012 | 0 | 0 | 0 | 0 | 0 | 1266.0795 | 1266.0795
| 20490297 | 2033 | KRT012 | 0 | 0 | 0 | 0 | 0 | 1266.0795 | 1266.0795
| 20490297 | 2034 | KRT012 | 0 | 0 | 0 | 0 | 0 | 1266.0795 | 1266.0795
| 20583843 | 2023 | KRT012 | 0 | 0 | 0 | 0 | 0 | 6797.7273 | 6797.7273
| 20583843 | 2024 | KRT012 | 0 | 0 | 0 | 0 | 0 | 6797.7273 | 6797.7273
| 20583843 | 2025 | KRT012 | 0 | 0 | 0 | 0 | 0 | 6797.7273 | 6797.7273
| 20583843 | 2026 | KRT012 | 0 | 0 | 0 | 0 | 0 | 6797.7273 | 6797.7273
| 20583843 | 2027 | KRT012 | 0 | 0 | 0 | 0 | 0 | 6797.7273 | 6797.7273
| 20583843 | 2028 | KRT012 | 0 | 0 | 0 | 0 | 0 | 6797.7273 | 6797.7273
| 20583843 | 2029 | KRT012 | 0 | 0 | 0 | 0 | 0 | 6797.7273 | 6797.7273
| 20583843 | 2030 | KRT012 | 0 | 0 | 0 | 0 | 0 | 6797.7273 | 6797.7273
| 20583843 | 2031 | KRT012 | 0 | 0 | 0 | 0 | 0 | 6797.7273 | 6797.7273
| 20583843 | 2032 | KRT012 | 0 | 0 | 0 | 0 | 0 | 6797.7273 | 6797.7273
| 20583843 | 2033 | KRT012 | 0 | 0 | 0 | 0 | 0 | 6797.7273 | 6797.7273
| 20583843 | 2034 | KRT012 | 0 | 0 | 0 | 0 | 0 | 6797.7273 | 6797.7273
| 118960938 | 2023 | KRT012 | 0 | 0 | 821.8301 | 38669.5264 | 821.8301 | 3960.7382 | 42630.2646
| 118960938 | 2024 | KRT012 | 0 | 0 | 945.8132 | 44503.2933 | 945.8132 | 3960.7382 | 48464.0315
| 118960938 | 2025 | KRT012 | 0 | 0 | 1022.2506 | 48099.901 | 1022.2506 | 3960.7382 | 52060.6392
| 118960938 | 2026 | KRT012 | 0 | 0 | 1024.7073 | 48215.4922 | 1024.7073 | 3960.7382 | 52176.2305
| 118960938 | 2027 | KRT012 | 0 | 0 | 1067.1077 | 50210.5571 | 1067.1077 | 3960.7382 | 54171.2953
| 118960938 | 2028 | KRT012 | 0 | 0 | 1155.9661 | 54391.6073 | 1155.9661 | 3960.7382 | 58352.3455
| 118960938 | 2029 | KRT012 | 0 | 0 | 1281.1864 | 60283.5921 | 1281.1864 | 3960.7382 | 64244.3303
| 118960938 | 2030 | KRT012 | 0 | 0 | 1257.4384 | 59166.1759 | 1257.4384 | 3960.7382 | 63126.9141
| 118960938 | 2031 | KRT012 | 0 | 0 | 1307.3377 | 61514.0844 | 1307.3377 | 3960.7382 | 65474.8226
| 118960938 | 2032 | KRT012 | 0 | 0 | 1466.099 | 68984.2725 | 1466.099 | 3960.7382 | 72945.0107
| 118960938 | 2033 | KRT012 | 0 | 0 | 1651.6917 | 77716.9535 | 1651.6917 | 3960.7382 | 81677.6918
| 118960938 | 2034 | KRT012 | 0 | 0 | 1714.9044 | 80691.2974 | 1714.9044 | 3960.7382 | 84652.0357
| 163198819 | 2023 | KRT012 | 0 | 0 | 0.10381 | 4.8844 | 0.10381 | 4480.6525 | 4485.537
| 163198819 | 2024 | KRT012 | 0 | 0 | 0.59477 | 27.9856 | 0.59477 | 4480.6525 | 4508.6381
| 163198819 | 2025 | KRT012 | 0 | 0 | 0.82441 | 38.7911 | 0.82441 | 4480.6525 | 4519.4437
| 163198819 | 2026 | KRT012 | 0 | 0 | 0.95752 | 45.0543 | 0.95752 | 4480.6525 | 4525.7068
| 163198819 | 2027 | KRT012 | 0 | 0 | 1.4488 | 68.1683 | 1.4488 | 4480.6525 | 4548.8208
| 163198819 | 2028 | KRT012 | 0 | 0 | 2.3066 | 108.5309 | 2.3066 | 4480.6525 | 4589.1834
| 163198819 | 2029 | KRT012 | 18.6916 | 0.038433 | 2.717 | 127.8421 | 21.4086 | 4480.6525 | 4608.533
| 163198819 | 2030 | KRT012 | 7.6625 | 0.019872 | 3.6682 | 172.6017 | 11.3308 | 4480.6525 | 4653.2741
| 163198819 | 2031 | KRT012 | 78.8844 | 0.48943 | 3.7211 | 175.0884 | 82.6055 | 4480.6525 | 4656.2304
| 163198819 | 2032 | KRT012 | 305.373 | 2.8327 | 5.7171 | 269.0066 | 311.0901 | 4480.6525 | 4752.4918
| 163198819 | 2033 | KRT012 | 502.0204 | 12.849 | 8.9586 | 421.5276 | 510.979 | 4480.6525 | 4915.0291
| 163198819 | 2034 | KRT012 | 415.4167 | 12.4 | 16.6785 | 784.7743 | 432.0952 | 4480.6525 | 5277.8269
| 171338632 | 2023 | KRT012 | 0 | 0 | 0 | 0 | 0 | 102.0965 | 102.0965
| 171338632 | 2024 | KRT012 | 0 | 0 | 0 | 0 | 0 | 102.0965 | 102.0965
| 171338632 | 2025 | KRT012 | 0 | 0 | 0 | 0 | 0 | 102.0965 | 102.0965
| 171338632 | 2026 | KRT012 | 0 | 0 | 0 | 0 | 0 | 102.0965 | 102.0965
| 171338632 | 2027 | KRT012 | 0 | 0 | 0 | 0 | 0 | 102.0965 | 102.0965
| 171338632 | 2028 | KRT012 | 0 | 0 | 0 | 0 | 0 | 102.0965 | 102.0965
| 171338632 | 2029 | KRT012 | 0 | 0 | 0 | 0 | 0 | 102.0965 | 102.0965
| 171338632 | 2030 | KRT012 | 0 | 0 | 0 | 0 | 0 | 102.0965 | 102.0965
| 171338632 | 2031 | KRT012 | 0 | 0 | 0 | 0 | 0 | 102.0965 | 102.0965
| 171338632 | 2032 | KRT012 | 0 | 0 | 0 | 0 | 0 | 102.0965 | 102.0965
| 171338632 | 2033 | KRT012 | 0 | 0 | 0 | 0 | 0 | 102.0965 | 102.0965
| 171338632 | 2034 | KRT012 | 0 | 0 | 0 | 0 | 0 | 102.0965 | 102.0965
| 19843062 | 2023 | KRT013 | 0 | 0 | 0 | 0 | 0 | 40.6967 | 40.6967
| 19843062 | 2024 | KRT013 | 0 | 0 | 0 | 0 | 0 | 40.6967 | 40.6967
| 19843062 | 2025 | KRT013 | 0 | 0 | 0 | 0 | 0 | 40.6967 | 40.6967
| 19843062 | 2026 | KRT013 | 0 | 0 | 0 | 0 | 0 | 40.6967 | 40.6967
| 19843062 | 2027 | KRT013 | 0 | 0 | 52.3907 | 2465.1368 | 52.3907 | 40.6967 | 2505.8335
| 19843062 | 2028 | KRT013 | 0 | 0 | 47.0701 | 2214.7845 | 47.0701 | 40.6967 | 2255.4812
| 19843062 | 2029 | KRT013 | 0 | 0 | 3399.7153 | 159966.6072 | 3399.7153 | 40.6967 | 160007.3039
| 19843062 | 2030 | KRT013 | 0 | 0 | 1466.9599 | 69024.7823 | 1466.9599 | 40.6967 | 69065.479
| 19843062 | 2031 | KRT013 | 0 | 0 | 1466.9599 | 69024.7823 | 1466.9599 | 40.6967 | 69065.479
| 19843062 | 2032 | KRT013 | 0 | 0 | 1466.9599 | 69024.7823 | 1466.9599 | 40.6967 | 69065.479
| 19843062 | 2033 | KRT013 | 0 | 0 | 1466.9599 | 69024.7823 | 1466.9599 | 40.6967 | 69065.479
| 19843062 | 2034 | KRT013 | 0 | 0 | 1466.9599 | 69024.7823 | 1466.9599 | 40.6967 | 69065.479
| 19843553 | 2023 | KRT013 | 1.0401 | 0 | 0 | 0 | 1.0401 | 1158.8053 | 1158.8053
| 19843553 | 2024 | KRT013 | 1034.5365 | 33.129 | 0 | 0 | 1034.5365 | 1158.8053 | 1191.9344
| 19843553 | 2025 | KRT013 | 907.7293 | 25.1757 | 0 | 0 | 907.7293 | 1158.8053 | 1183.9811
| 19843553 | 2026 | KRT013 | 825.2356 | 12.9825 | 0 | 0 | 825.2356 | 1158.8053 | 1171.7878
| 19843553 | 2027 | KRT013 | 553.4628 | 5.4972 | 1.3838 | 65.1137 | 554.8467 | 1158.8053 | 1229.4162
| 19843553 | 2028 | KRT013 | 505.4749 | 4.319 | 0.14915 | 7.018 | 505.624 | 1158.8053 | 1170.1423
| 19843553 | 2029 | KRT013 | 49.6919 | 0.75384 | 166.3389 | 7826.7329 | 216.0307 | 1158.8053 | 8986.2921
| 19843553 | 2030 | KRT013 | 419.1498 | 4.3121 | 67.6686 | 3184.0049 | 486.8184 | 1158.8053 | 4347.1224
| 19843553 | 2031 | KRT013 | 419.1498 | 4.3121 | 67.6686 | 3184.0049 | 486.8184 | 1158.8053 | 4347.1224
| 19843553 | 2032 | KRT013 | 419.1498 | 4.3121 | 67.6686 | 3184.0049 | 486.8184 | 1158.8053 | 4347.1224
| 19843553 | 2033 | KRT013 | 419.1498 | 4.3121 | 67.6686 | 3184.0049 | 486.8184 | 1158.8053 | 4347.1224
| 19843553 | 2034 | KRT013 | 419.1498 | 4.3121 | 67.6686 | 3184.0049 | 486.8184 | 1158.8053 | 4347.1224
| 19844220 | 2023 | KRT013 | 0 | 0 | 5.708 | 268.5773 | 5.708 | 1329.8618 | 1598.4391
| 19844220 | 2024 | KRT013 | 0 | 0 | 11.4509 | 538.7971 | 11.4509 | 1329.8618 | 1868.6589
| 19844220 | 2025 | KRT013 | 0 | 0 | 13.7304 | 646.0557 | 13.7304 | 1329.8618 | 1975.9175
| 19844220 | 2026 | KRT013 | 0 | 0 | 16.3824 | 770.842 | 16.3824 | 1329.8618 | 2100.7038
| 19844220 | 2027 | KRT013 | 0 | 0 | 363.4229 | 17100.1175 | 363.4229 | 1329.8618 | 18429.9793
| 19844220 | 2028 | KRT013 | 0 | 0 | 296.2639 | 13940.0873 | 296.2639 | 1329.8618 | 15269.9491
| 19844220 | 2029 | KRT013 | 0 | 0 | 2043.5759 | 96156.2598 | 2043.5759 | 1329.8618 | 97486.1216
| 19844220 | 2030 | KRT013 | 0 | 0 | 1284.6649 | 60447.2646 | 1284.6649 | 1329.8618 | 61777.1264
| 19844220 | 2031 | KRT013 | 0 | 0 | 1284.6649 | 60447.2646 | 1284.6649 | 1329.8618 | 61777.1264
| 19844220 | 2032 | KRT013 | 0 | 0 | 1284.6649 | 60447.2646 | 1284.6649 | 1329.8618 | 61777.1264
| 19844220 | 2033 | KRT013 | 0 | 0 | 1284.6649 | 60447.2646 | 1284.6649 | 1329.8618 | 61777.1264
| 19844220 | 2034 | KRT013 | 0 | 0 | 1284.6649 | 60447.2646 | 1284.6649 | 1329.8618 | 61777.1264
| 19845774 | 2023 | KRT013 | 0 | 0 | 7.1445 | 336.1679 | 7.1445 | 2096.5363 | 2432.7041
| 19845774 | 2024 | KRT013 | 0 | 0 | 13.8731 | 652.7679 | 13.8731 | 2096.5363 | 2749.3042
| 19845774 | 2025 | KRT013 | 0 | 0 | 29.0941 | 1368.963 | 29.0941 | 2096.5363 | 3465.4993
| 19845774 | 2026 | KRT013 | 0 | 0 | 34.9174 | 1642.9665 | 34.9174 | 2096.5363 | 3739.5028
| 19845774 | 2027 | KRT013 | 879.997 | 6.4394 | 49.8583 | 2345.9786 | 929.8552 | 2096.5363 | 4448.9543
| 19845774 | 2028 | KRT013 | 1057.8106 | 7.294 | 82.427 | 3878.4327 | 1140.2376 | 2096.5363 | 5982.263
| 19845774 | 2029 | KRT013 | 704.4717 | 3.2799 | 188.2044 | 8855.5709 | 892.6761 | 2096.5363 | 10955.3871
| 19845774 | 2030 | KRT013 | 1050.8375 | 7.1114 | 223.0697 | 10496.0873 | 1273.9073 | 2096.5363 | 12599.735
| 19845774 | 2031 | KRT013 | 1050.8375 | 7.1114 | 223.0697 | 10496.0873 | 1273.9073 | 2096.5363 | 12599.735
| 19845774 | 2032 | KRT013 | 1050.8375 | 7.1114 | 223.0697 | 10496.0873 | 1273.9073 | 2096.5363 | 12599.735
| 19845774 | 2033 | KRT013 | 1050.8375 | 7.1114 | 223.0697 | 10496.0873 | 1273.9073 | 2096.5363 | 12599.735
| 19845774 | 2034 | KRT013 | 1050.8375 | 7.1114 | 223.0697 | 10496.0873 | 1273.9073 | 2096.5363 | 12599.735
| 19849367 | 2023 | KRT013 | 0 | 0 | 0 | 0 | 0 | 330.4027 | 330.4027
| 19849367 | 2024 | KRT013 | 0 | 0 | 0 | 0 | 0 | 330.4027 | 330.4027
| 19849367 | 2025 | KRT013 | 0 | 0 | 0 | 0 | 0 | 330.4027 | 330.4027
| 19849367 | 2026 | KRT013 | 0 | 0 | 0 | 0 | 0 | 330.4027 | 330.4027
| 19849367 | 2027 | KRT013 | 0 | 0 | 0 | 0 | 0 | 330.4027 | 330.4027
| 19849367 | 2028 | KRT013 | 0 | 0 | 0 | 0 | 0 | 330.4027 | 330.4027
| 19849367 | 2029 | KRT013 | 0 | 0 | 2.5269 | 118.8978 | 2.5269 | 330.4027 | 449.3005
| 19849367 | 2030 | KRT013 | 0 | 0 | 3.6606 | 172.2406 | 3.6606 | 330.4027 | 502.6433
| 19849367 | 2031 | KRT013 | 0 | 0 | 3.6606 | 172.2406 | 3.6606 | 330.4027 | 502.6433
| 19849367 | 2032 | KRT013 | 0 | 0 | 3.6606 | 172.2406 | 3.6606 | 330.4027 | 502.6433
| 19849367 | 2033 | KRT013 | 0 | 0 | 3.6606 | 172.2406 | 3.6606 | 330.4027 | 502.6433
| 19849367 | 2034 | KRT013 | 0 | 0 | 3.6606 | 172.2406 | 3.6606 | 330.4027 | 502.6433
| 19849385 | 2023 | KRT013 | 0.73071 | 0 | 54.4797 | 2563.4281 | 55.2104 | 4186.0953 | 6749.5233
| 19849385 | 2024 | KRT013 | 0.36578 | 0.01901 | 75.1334 | 3535.2464 | 75.4992 | 4186.0953 | 7721.3607
| 19849385 | 2025 | KRT013 | 0.90387 | 0.016504 | 104.9503 | 4938.2217 | 105.8542 | 4186.0953 | 9124.3335
| 19849385 | 2026 | KRT013 | 3.4341 | 0.032523 | 93.2002 | 4385.3444 | 96.6344 | 4186.0953 | 8571.4722
| 19849385 | 2027 | KRT013 | 15.4585 | 0.050492 | 767.9979 | 36136.5607 | 783.4564 | 4186.0953 | 40322.7065
| 19849385 | 2028 | KRT013 | 9.6016 | 0.052319 | 885.9435 | 41686.2481 | 895.545 | 4186.0953 | 45872.3957
| 19849385 | 2029 | KRT013 | 0 | 0 | 4982.3838 | 234435.8198 | 4982.3838 | 4186.0953 | 238621.9151
| 19849385 | 2030 | KRT013 | 11.214 | 0.092277 | 3613.6598 | 170033.3271 | 3624.8738 | 4186.0953 | 174219.5146
| 19849385 | 2031 | KRT013 | 11.214 | 0.092277 | 3613.6598 | 170033.3271 | 3624.8738 | 4186.0953 | 174219.5146
| 19849385 | 2032 | KRT013 | 11.214 | 0.092277 | 3613.6598 | 170033.3271 | 3624.8738 | 4186.0953 | 174219.5146
| 19849385 | 2033 | KRT013 | 11.214 | 0.092277 | 3613.6598 | 170033.3271 | 3624.8738 | 4186.0953 | 174219.5146
| 19849385 | 2034 | KRT013 | 11.214 | 0.092277 | 3613.6598 | 170033.3271 | 3624.8738 | 4186.0953 | 174219.5146
| 20490286 | 2023 | KRT013 | 0 | 0 | 0 | 0 | 0 | 1590.8192 | 1590.8192
| 20490286 | 2024 | KRT013 | 0 | 0 | 0 | 0 | 0 | 1590.8192 | 1590.8192
| 20490286 | 2025 | KRT013 | 0 | 0 | 0 | 0 | 0 | 1590.8192 | 1590.8192
| 20490286 | 2026 | KRT013 | 9.8355 | 0.10741 | 0 | 0 | 9.8355 | 1590.8192 | 1590.9266
| 20490286 | 2027 | KRT013 | 29.898 | 0.065776 | 0 | 0 | 29.898 | 1590.8192 | 1590.885
| 20490286 | 2028 | KRT013 | 12.9762 | 0.037329 | 0 | 0 | 12.9762 | 1590.8192 | 1590.8566
| 20490286 | 2029 | KRT013 | 19.3554 | 0.023928 | 0 | 0 | 19.3554 | 1590.8192 | 1590.8432
| 20490286 | 2030 | KRT013 | 35.9687 | 0.030558 | 0.00023458 | 0.011038 | 35.9689 | 1590.8192 | 1590.8608
| 20490286 | 2031 | KRT013 | 35.9687 | 0.030558 | 0.00023458 | 0.011038 | 35.9689 | 1590.8192 | 1590.8608
| 20490286 | 2032 | KRT013 | 35.9687 | 0.030558 | 0.00023458 | 0.011038 | 35.9689 | 1590.8192 | 1590.8608
| 20490286 | 2033 | KRT013 | 35.9687 | 0.030558 | 0.00023458 | 0.011038 | 35.9689 | 1590.8192 | 1590.8608
| 20490286 | 2034 | KRT013 | 35.9687 | 0.030558 | 0.00023458 | 0.011038 | 35.9689 | 1590.8192 | 1590.8608
| 20490968 | 2023 | KRT013 | 0 | 0 | 0 | 0 | 0 | 1257.7487 | 1257.7487
| 20490968 | 2024 | KRT013 | 0 | 0 | 0 | 0 | 0 | 1257.7487 | 1257.7487
| 20490968 | 2025 | KRT013 | 0 | 0 | 0.030275 | 1.4245 | 0.030275 | 1257.7487 | 1259.1732
| 20490968 | 2026 | KRT013 | 0 | 0 | 0.035507 | 1.6707 | 0.035507 | 1257.7487 | 1259.4194
| 20490968 | 2027 | KRT013 | 0 | 0 | 2.6257 | 123.5446 | 2.6257 | 1257.7487 | 1381.2933
| 20490968 | 2028 | KRT013 | 0 | 0 | 3.7144 | 174.7747 | 3.7144 | 1257.7487 | 1432.5234
| 20490968 | 2029 | KRT013 | 0 | 0 | 18.4498 | 868.1188 | 18.4498 | 1257.7487 | 2125.8674
| 20490968 | 2030 | KRT013 | 0 | 0 | 25.2406 | 1187.6469 | 25.2406 | 1257.7487 | 2445.3955
| 20490968 | 2031 | KRT013 | 0 | 0 | 25.2406 | 1187.6469 | 25.2406 | 1257.7487 | 2445.3955
| 20490968 | 2032 | KRT013 | 0 | 0 | 25.2406 | 1187.6469 | 25.2406 | 1257.7487 | 2445.3955
| 20490968 | 2033 | KRT013 | 0 | 0 | 25.2406 | 1187.6469 | 25.2406 | 1257.7487 | 2445.3955
| 20490968 | 2034 | KRT013 | 0 | 0 | 25.2406 | 1187.6469 | 25.2406 | 1257.7487 | 2445.3955
| 20496348 | 2023 | KRT013 | 5.8981 | 0 | 0 | 0 | 5.8981 | 546.0138 | 546.0138
| 20496348 | 2024 | KRT013 | 2491.5864 | 55.7053 | 0 | 0 | 2491.5864 | 546.0138 | 601.7191
| 20496348 | 2025 | KRT013 | 3788.0184 | 89.5959 | 0 | 0 | 3788.0184 | 546.0138 | 635.6097
| 20496348 | 2026 | KRT013 | 3891.7527 | 51.0388 | 0 | 0 | 3891.7527 | 546.0138 | 597.0526
| 20496348 | 2027 | KRT013 | 9436.0064 | 104.6186 | 0 | 0 | 9436.0064 | 546.0138 | 650.6324
| 20496348 | 2028 | KRT013 | 15107.9336 | 208.8514 | 0 | 0 | 15107.9336 | 546.0138 | 754.8652
| 20496348 | 2029 | KRT013 | 15677.8346 | 180.6948 | 0 | 0 | 15677.8346 | 546.0138 | 726.7086
| 20496348 | 2030 | KRT013 | 19108.7421 | 235.1842 | 0 | 0 | 19108.7421 | 546.0138 | 781.198
| 20496348 | 2031 | KRT013 | 19108.7421 | 235.1842 | 0 | 0 | 19108.7421 | 546.0138 | 781.198
| 20496348 | 2032 | KRT013 | 19108.7421 | 235.1842 | 0 | 0 | 19108.7421 | 546.0138 | 781.198
| 20496348 | 2033 | KRT013 | 19108.7421 | 235.1842 | 0 | 0 | 19108.7421 | 546.0138 | 781.198
| 20496348 | 2034 | KRT013 | 19108.7421 | 235.1842 | 0 | 0 | 19108.7421 | 546.0138 | 781.198
| 20526308 | 2023 | KRT013 | 0 | 0 | 0 | 0 | 0 | 769.914 | 769.914
| 20526308 | 2024 | KRT013 | 0 | 0 | 0 | 0 | 0 | 769.914 | 769.914
| 20526308 | 2025 | KRT013 | 0 | 0 | 0 | 0 | 0 | 769.914 | 769.914
| 20526308 | 2026 | KRT013 | 0 | 0 | 0 | 0 | 0 | 769.914 | 769.914
| 20526308 | 2027 | KRT013 | 0 | 0 | 0 | 0 | 0 | 769.914 | 769.914
| 20526308 | 2028 | KRT013 | 0 | 0 | 1.7215 | 81.0014 | 1.7215 | 769.914 | 850.9154
| 20526308 | 2029 | KRT013 | 0 | 0 | 2.7619 | 129.954 | 2.7619 | 769.914 | 899.8679
| 20526308 | 2030 | KRT013 | 0 | 0 | 2.9534 | 138.9681 | 2.9534 | 769.914 | 908.8821
| 20526308 | 2031 | KRT013 | 0 | 0 | 2.9534 | 138.9681 | 2.9534 | 769.914 | 908.8821
| 20526308 | 2032 | KRT013 | 0 | 0 | 2.9534 | 138.9681 | 2.9534 | 769.914 | 908.8821
| 20526308 | 2033 | KRT013 | 0 | 0 | 2.9534 | 138.9681 | 2.9534 | 769.914 | 908.8821
| 20526308 | 2034 | KRT013 | 0 | 0 | 2.9534 | 138.9681 | 2.9534 | 769.914 | 908.8821
| 20624610 | 2023 | KRT013 | 0 | 0 | 0 | 0 | 0 | 482.4818 | 482.4818
| 20624610 | 2024 | KRT013 | 1.1943 | 0.013366 | 0 | 0 | 1.1943 | 482.4818 | 482.4951
| 20624610 | 2025 | KRT013 | 1.1796 | 0.0092388 | 0 | 0 | 1.1796 | 482.4818 | 482.491
| 20624610 | 2026 | KRT013 | 38.6618 | 0.14587 | 0 | 0 | 38.6618 | 482.4818 | 482.6276
| 20624610 | 2027 | KRT013 | 150.4894 | 0.4232 | 0 | 0 | 150.4894 | 482.4818 | 482.9049
| 20624610 | 2028 | KRT013 | 185.7898 | 0.59711 | 0 | 0 | 185.7898 | 482.4818 | 483.0789
| 20624610 | 2029 | KRT013 | 48.981 | 0.31702 | 0 | 0 | 48.981 | 482.4818 | 482.7988
| 20624610 | 2030 | KRT013 | 463.1847 | 2.2044 | 0 | 0 | 463.1847 | 482.4818 | 484.6861
| 20624610 | 2031 | KRT013 | 463.1847 | 2.2044 | 0 | 0 | 463.1847 | 482.4818 | 484.6861
| 20624610 | 2032 | KRT013 | 463.1847 | 2.2044 | 0 | 0 | 463.1847 | 482.4818 | 484.6861
| 20624610 | 2033 | KRT013 | 463.1847 | 2.2044 | 0 | 0 | 463.1847 | 482.4818 | 484.6861
| 20624610 | 2034 | KRT013 | 463.1847 | 2.2044 | 0 | 0 | 463.1847 | 482.4818 | 484.6861
| 72859584 | 2023 | KRT013 | 153.4648 | 0 | 0 | 0 | 153.4648 | 403.7784 | 403.7784
| 72859584 | 2024 | KRT013 | 786.7725 | 25.3164 | 0 | 0 | 786.7725 | 403.7784 | 429.0949
| 72859584 | 2025 | KRT013 | 1101.202 | 27.5956 | 0 | 0 | 1101.202 | 403.7784 | 431.3741
| 72859584 | 2026 | KRT013 | 839.0848 | 12.3683 | 0 | 0 | 839.0848 | 403.7784 | 416.1468
| 72859584 | 2027 | KRT013 | 718.9882 | 5.2184 | 0 | 0 | 718.9882 | 403.7784 | 408.9968
| 72859584 | 2028 | KRT013 | 576.7445 | 4.6778 | 0 | 0 | 576.7445 | 403.7784 | 408.4563
| 72859584 | 2029 | KRT013 | 79.3348 | 1.3208 | 0 | 0 | 79.3348 | 403.7784 | 405.0993
| 72859584 | 2030 | KRT013 | 709.3443 | 7.1044 | 0 | 0 | 709.3443 | 403.7784 | 410.8828
| 72859584 | 2031 | KRT013 | 709.3443 | 7.1044 | 0 | 0 | 709.3443 | 403.7784 | 410.8828
| 72859584 | 2032 | KRT013 | 709.3443 | 7.1044 | 0 | 0 | 709.3443 | 403.7784 | 410.8828
| 72859584 | 2033 | KRT013 | 709.3443 | 7.1044 | 0 | 0 | 709.3443 | 403.7784 | 410.8828
| 72859584 | 2034 | KRT013 | 709.3443 | 7.1044 | 0 | 0 | 709.3443 | 403.7784 | 410.8828
| 161724387 | 2023 | KRT013 | 0 | 0 | 0 | 0 | 0 | 478.5696 | 478.5696
| 161724387 | 2024 | KRT013 | 0 | 0 | 0 | 0 | 0 | 478.5696 | 478.5696
| 161724387 | 2025 | KRT013 | 0 | 0 | 0 | 0 | 0 | 478.5696 | 478.5696
| 161724387 | 2026 | KRT013 | 0 | 0 | 0 | 0 | 0 | 478.5696 | 478.5696
| 161724387 | 2027 | KRT013 | 0 | 0 | 0 | 0 | 0 | 478.5696 | 478.5696
| 161724387 | 2028 | KRT013 | 0 | 0 | 0 | 0 | 0 | 478.5696 | 478.5696
| 161724387 | 2029 | KRT013 | 0 | 0 | 0 | 0 | 0 | 478.5696 | 478.5696
| 161724387 | 2030 | KRT013 | 0 | 0 | 0 | 0 | 0 | 478.5696 | 478.5696
| 161724387 | 2031 | KRT013 | 0 | 0 | 0 | 0 | 0 | 478.5696 | 478.5696
| 161724387 | 2032 | KRT013 | 0 | 0 | 0 | 0 | 0 | 478.5696 | 478.5696
| 161724387 | 2033 | KRT013 | 0 | 0 | 0 | 0 | 0 | 478.5696 | 478.5696
| 161724387 | 2034 | KRT013 | 0 | 0 | 0 | 0 | 0 | 478.5696 | 478.5696
| 20494773 | 2023 | KRT031 | 0 | 0 | 0 | 0 | 0 | 1222.9219 | 1222.9219
| 20494773 | 2024 | KRT031 | 0 | 0 | 0 | 0 | 0 | 1222.9219 | 1222.9219
| 20494773 | 2025 | KRT031 | 0 | 0 | 0 | 0 | 0 | 1222.9219 | 1222.9219
| 20494773 | 2026 | KRT031 | 0 | 0 | 0 | 0 | 0 | 1222.9219 | 1222.9219
| 20494773 | 2027 | KRT031 | 0 | 0 | 0 | 0 | 0 | 1222.9219 | 1222.9219
| 20494773 | 2028 | KRT031 | 0 | 0 | 0 | 0 | 0 | 1222.9219 | 1222.9219
| 20494773 | 2029 | KRT031 | 0 | 0 | 0 | 0 | 0 | 1222.9219 | 1222.9219
| 20494773 | 2030 | KRT031 | 0 | 0 | 0 | 0 | 0 | 1222.9219 | 1222.9219
| 20494773 | 2031 | KRT031 | 0 | 0 | 0 | 0 | 0 | 1222.9219 | 1222.9219
| 20494773 | 2032 | KRT031 | 0 | 0 | 0 | 0 | 0 | 1222.9219 | 1222.9219
| 20494773 | 2033 | KRT031 | 0 | 0 | 0 | 0 | 0 | 1222.9219 | 1222.9219
| 20494773 | 2034 | KRT031 | 0 | 0 | 0 | 0 | 0 | 1222.9219 | 1222.9219
| 20198559 | 2023 | KYM001 | 0 | 0 | 2001.3347 | 95664.4985 | 2001.3347 | 1165.9399 | 96830.4384
| 20198559 | 2024 | KYM001 | 0 | 0 | 2001.4587 | 95670.4234 | 2001.4587 | 1165.9399 | 96836.3632
| 20198559 | 2025 | KYM001 | 0 | 0 | 2001.3347 | 95664.4985 | 2001.3347 | 1165.9399 | 96830.4384
| 20198559 | 2026 | KYM001 | 0 | 0 | 2001.5921 | 95676.8022 | 2001.5921 | 1165.9399 | 96842.7421
| 20198559 | 2027 | KYM001 | 0 | 0 | 2780.7888 | 132922.677 | 2780.7888 | 1165.9399 | 134088.6169
| 20198559 | 2028 | KYM001 | 0 | 0 | 3164.7803 | 151277.6039 | 3164.7803 | 1165.9399 | 152443.5437
| 20198559 | 2029 | KYM001 | 0 | 0 | 3354.2423 | 160333.9539 | 3354.2423 | 1165.9399 | 161499.8938
| 20198559 | 2030 | KYM001 | 0 | 0 | 3367.7948 | 160981.7685 | 3367.7948 | 1165.9399 | 162147.7084
| 20198559 | 2031 | KYM001 | 0 | 0 | 3409.6619 | 162983.0323 | 3409.6619 | 1165.9399 | 164148.9721
| 20198559 | 2032 | KYM001 | 0 | 0 | 3608.2263 | 172474.4802 | 3608.2263 | 1165.9399 | 173640.4201
| 20198559 | 2033 | KYM001 | 0 | 0 | 3648.6023 | 174404.4651 | 3648.6023 | 1165.9399 | 175570.405
| 20198559 | 2034 | KYM001 | 0 | 0 | 3755.4631 | 179512.4509 | 3755.4631 | 1165.9399 | 180678.3908
| 20133777 | 2023 | KYM003 | 0 | 0 | 0 | 0 | 0 | 980.286 | 980.286
| 20133777 | 2024 | KYM003 | 0 | 0 | 0 | 0 | 0 | 980.286 | 980.286
| 20133777 | 2025 | KYM003 | 0 | 0 | 0 | 0 | 0 | 980.286 | 980.286
| 20133777 | 2026 | KYM003 | 0 | 0 | 0 | 0 | 0 | 980.286 | 980.286
| 20133777 | 2027 | KYM003 | 0 | 0 | 0 | 0 | 0 | 980.286 | 980.286
| 20133777 | 2028 | KYM003 | 0 | 0 | 0 | 0 | 0 | 980.286 | 980.286
| 20133777 | 2029 | KYM003 | 0 | 0 | 0 | 0 | 0 | 980.286 | 980.286
| 20133777 | 2030 | KYM003 | 0 | 0 | 0 | 0 | 0 | 980.286 | 980.286
| 20133777 | 2031 | KYM003 | 0 | 0 | 0 | 0 | 0 | 980.286 | 980.286
| 20133777 | 2032 | KYM003 | 0 | 0 | 0 | 0 | 0 | 980.286 | 980.286
| 20133777 | 2033 | KYM003 | 0 | 0 | 0 | 0 | 0 | 980.286 | 980.286
| 20133777 | 2034 | KYM003 | 0 | 0 | 0 | 0 | 0 | 980.286 | 980.286
| 44712203 | 2023 | KYM003 | 0 | 0 | 0 | 0 | 0 | 2489.0843 | 2489.0843
| 44712203 | 2024 | KYM003 | 0 | 0 | 0 | 0 | 0 | 2489.0843 | 2489.0843
| 44712203 | 2025 | KYM003 | 0 | 0 | 0 | 0 | 0 | 2489.0843 | 2489.0843
| 44712203 | 2026 | KYM003 | 0 | 0 | 0 | 0 | 0 | 2489.0843 | 2489.0843
| 44712203 | 2027 | KYM003 | 4.2747 | 0.0082282 | 0 | 0 | 4.2747 | 2489.0843 | 2489.0926
| 44712203 | 2028 | KYM003 | 1.1485 | 0.0029412 | 0 | 0 | 1.1485 | 2489.0843 | 2489.0873
| 44712203 | 2029 | KYM003 | 6.3381 | 0.020507 | 0 | 0 | 6.3381 | 2489.0843 | 2489.1048
| 44712203 | 2030 | KYM003 | 4.0493 | 0.024583 | 0 | 0 | 4.0493 | 2489.0843 | 2489.1089
| 44712203 | 2031 | KYM003 | 20.9679 | 0.15884 | 0 | 0 | 20.9679 | 2489.0843 | 2489.2432
| 44712203 | 2032 | KYM003 | 4.6257 | 0.038789 | 0 | 0 | 4.6257 | 2489.0843 | 2489.1231
| 44712203 | 2033 | KYM003 | 17.3908 | 0.47611 | 0 | 0 | 17.3908 | 2489.0843 | 2489.5604
| 44712203 | 2034 | KYM003 | 112.7802 | 2.5511 | 2.1952 | 104.9336 | 114.9754 | 2489.0843 | 2596.569
| 163787989 | 2023 | MBN014 | 0 | 0 | 0 | 0 | 0 | 2313.6418 | 2313.6418
| 163787989 | 2024 | MBN014 | 0 | 0 | 0 | 0 | 0 | 2313.6418 | 2313.6418
| 163787989 | 2025 | MBN014 | 0 | 0 | 0 | 0 | 0 | 2313.6418 | 2313.6418
| 163787989 | 2026 | MBN014 | 0 | 0 | 0 | 0 | 0 | 2313.6418 | 2313.6418
| 163787989 | 2027 | MBN014 | 0 | 0 | 0 | 0 | 0 | 2313.6418 | 2313.6418
| 163787989 | 2028 | MBN014 | 0 | 0 | 0 | 0 | 0 | 2313.6418 | 2313.6418
| 163787989 | 2029 | MBN014 | 0 | 0 | 0 | 0 | 0 | 2313.6418 | 2313.6418
| 163787989 | 2030 | MBN014 | 0 | 0 | 0 | 0 | 0 | 2313.6418 | 2313.6418
| 163787989 | 2031 | MBN014 | 0 | 0 | 0 | 0 | 0 | 2313.6418 | 2313.6418
| 163787989 | 2032 | MBN014 | 0 | 0 | 0 | 0 | 0 | 2313.6418 | 2313.6418
| 163787989 | 2033 | MBN014 | 0 | 0 | 0 | 0 | 0 | 2313.6418 | 2313.6418
| 163787989 | 2034 | MBN014 | 0 | 0 | 0 | 0 | 0 | 2313.6418 | 2313.6418
| 20133605 | 2023 | MNA014 | 0 | 0 | 0 | 0 | 0 | 2028.3206 | 2028.3206
| 20133605 | 2024 | MNA014 | 0 | 0 | 0 | 0 | 0 | 2028.3206 | 2028.3206
| 20133605 | 2025 | MNA014 | 0 | 0 | 0 | 0 | 0 | 2028.3206 | 2028.3206
| 20133605 | 2026 | MNA014 | 0 | 0 | 0 | 0 | 0 | 2028.3206 | 2028.3206
| 20133605 | 2027 | MNA014 | 0 | 0 | 0 | 0 | 0 | 2028.3206 | 2028.3206
| 20133605 | 2028 | MNA014 | 0 | 0 | 0 | 0 | 0 | 2028.3206 | 2028.3206
| 20133605 | 2029 | MNA014 | 0 | 0 | 0 | 0 | 0 | 2028.3206 | 2028.3206
| 20133605 | 2030 | MNA014 | 0 | 0 | 0 | 0 | 0 | 2028.3206 | 2028.3206
| 20133605 | 2031 | MNA014 | 0 | 0 | 0 | 0 | 0 | 2028.3206 | 2028.3206
| 20133605 | 2032 | MNA014 | 0 | 0 | 0 | 0 | 0 | 2028.3206 | 2028.3206
| 20133605 | 2033 | MNA014 | 0 | 0 | 0 | 0 | 0 | 2028.3206 | 2028.3206
| 20133605 | 2034 | MNA014 | 0 | 0 | 0 | 0 | 0 | 2028.3206 | 2028.3206
| 20136175 | 2023 | MNA014 | 0 | 0 | 0 | 0 | 0 | 1846.9444 | 1846.9444
| 20136175 | 2024 | MNA014 | 0 | 0 | 0 | 0 | 0 | 1846.9444 | 1846.9444
| 20136175 | 2025 | MNA014 | 0 | 0 | 0 | 0 | 0 | 1846.9444 | 1846.9444
| 20136175 | 2026 | MNA014 | 0 | 0 | 0 | 0 | 0 | 1846.9444 | 1846.9444
| 20136175 | 2027 | MNA014 | 0 | 0 | 0 | 0 | 0 | 1846.9444 | 1846.9444
| 20136175 | 2028 | MNA014 | 0 | 0 | 0 | 0 | 0 | 1846.9444 | 1846.9444
| 20136175 | 2029 | MNA014 | 0 | 0 | 0 | 0 | 0 | 1846.9444 | 1846.9444
| 20136175 | 2030 | MNA014 | 0 | 0 | 0 | 0 | 0 | 1846.9444 | 1846.9444
| 20136175 | 2031 | MNA014 | 0 | 0 | 0 | 0 | 0 | 1846.9444 | 1846.9444
| 20136175 | 2032 | MNA014 | 0 | 0 | 0 | 0 | 0 | 1846.9444 | 1846.9444
| 20136175 | 2033 | MNA014 | 0 | 0 | 0 | 0 | 0 | 1846.9444 | 1846.9444
| 20136175 | 2034 | MNA014 | 0 | 0 | 0 | 0 | 0 | 1846.9444 | 1846.9444
| 20514636 | 2023 | MNA014 | 0 | 0 | 0 | 0 | 0 | 4359.167 | 4359.167
| 20514636 | 2024 | MNA014 | 0 | 0 | 0 | 0 | 0 | 4359.167 | 4359.167
| 20514636 | 2025 | MNA014 | 0 | 0 | 0 | 0 | 0 | 4359.167 | 4359.167
| 20514636 | 2026 | MNA014 | 0 | 0 | 0 | 0 | 0 | 4359.167 | 4359.167
| 20514636 | 2027 | MNA014 | 0 | 0 | 0 | 0 | 0 | 4359.167 | 4359.167
| 20514636 | 2028 | MNA014 | 0 | 0 | 0 | 0 | 0 | 4359.167 | 4359.167
| 20514636 | 2029 | MNA014 | 0 | 0 | 0 | 0 | 0 | 4359.167 | 4359.167
| 20514636 | 2030 | MNA014 | 0 | 0 | 0 | 0 | 0 | 4359.167 | 4359.167
| 20514636 | 2031 | MNA014 | 0 | 0 | 0 | 0 | 0 | 4359.167 | 4359.167
| 20514636 | 2032 | MNA014 | 0 | 0 | 0 | 0 | 0 | 4359.167 | 4359.167
| 20514636 | 2033 | MNA014 | 0 | 0 | 0 | 0 | 0 | 4359.167 | 4359.167
| 20514636 | 2034 | MNA014 | 0 | 0 | 0 | 0 | 0 | 4359.167 | 4359.167
| 20651907 | 2023 | MNA014 | 0 | 0 | 1.4504 | 70.4536 | 1.4504 | 2157.505 | 2227.9587
| 20651907 | 2024 | MNA014 | 0 | 0 | 1.7531 | 85.158 | 1.7531 | 2157.505 | 2242.663
| 20651907 | 2025 | MNA014 | 0 | 0 | 1.7531 | 85.158 | 1.7531 | 2157.505 | 2242.663
| 20651907 | 2026 | MNA014 | 0 | 0 | 1.7531 | 85.158 | 1.7531 | 2157.505 | 2242.663
| 20651907 | 2027 | MNA014 | 0 | 0 | 1.7531 | 85.158 | 1.7531 | 2157.505 | 2242.663
| 20651907 | 2028 | MNA014 | 0 | 0 | 1.7531 | 85.158 | 1.7531 | 2157.505 | 2242.663
| 20651907 | 2029 | MNA014 | 0 | 0 | 1.7531 | 85.158 | 1.7531 | 2157.505 | 2242.663
| 20651907 | 2030 | MNA014 | 0 | 0 | 1.7531 | 85.158 | 1.7531 | 2157.505 | 2242.663
| 20651907 | 2031 | MNA014 | 0 | 0 | 1.7531 | 85.158 | 1.7531 | 2157.505 | 2242.663
| 20651907 | 2032 | MNA014 | 0 | 0 | 1.7531 | 85.158 | 1.7531 | 2157.505 | 2242.663
| 20651907 | 2033 | MNA014 | 0 | 0 | 1.7531 | 85.158 | 1.7531 | 2157.505 | 2242.663
| 20651907 | 2034 | MNA014 | 0 | 0 | 1.7531 | 85.158 | 1.7531 | 2157.505 | 2242.663
| 54420337 | 2023 | MNA014 | 0 | 0 | 0 | 0 | 0 | 726.0381 | 726.0381
| 54420337 | 2024 | MNA014 | 0 | 0 | 0 | 0 | 0 | 726.0381 | 726.0381
| 54420337 | 2025 | MNA014 | 0 | 0 | 0 | 0 | 0 | 726.0381 | 726.0381
| 54420337 | 2026 | MNA014 | 0 | 0 | 0 | 0 | 0 | 726.0381 | 726.0381
| 54420337 | 2027 | MNA014 | 0 | 0 | 0 | 0 | 0 | 726.0381 | 726.0381
| 54420337 | 2028 | MNA014 | 0 | 0 | 0 | 0 | 0 | 726.0381 | 726.0381
| 54420337 | 2029 | MNA014 | 0 | 0 | 0 | 0 | 0 | 726.0381 | 726.0381
| 54420337 | 2030 | MNA014 | 0 | 0 | 0 | 0 | 0 | 726.0381 | 726.0381
| 54420337 | 2031 | MNA014 | 0 | 0 | 0 | 0 | 0 | 726.0381 | 726.0381
| 54420337 | 2032 | MNA014 | 0 | 0 | 0 | 0 | 0 | 726.0381 | 726.0381
| 54420337 | 2033 | MNA014 | 0 | 0 | 0 | 0 | 0 | 726.0381 | 726.0381
| 54420337 | 2034 | MNA014 | 0 | 0 | 0 | 0 | 0 | 726.0381 | 726.0381
| 163873654 | 2023 | MNA014 | 0 | 0 | 9058.8544 | 440041.9912 | 9058.8544 | 4256.0249 | 444298.0162
| 163873654 | 2024 | MNA014 | 0 | 0 | 9318.5736 | 452658.086 | 9318.5736 | 4256.0249 | 456914.111
| 163873654 | 2025 | MNA014 | 0 | 0 | 9318.5736 | 452658.086 | 9318.5736 | 4256.0249 | 456914.111
| 163873654 | 2026 | MNA014 | 0 | 0 | 9318.5736 | 452658.086 | 9318.5736 | 4256.0249 | 456914.111
| 163873654 | 2027 | MNA014 | 0 | 0 | 9318.5736 | 452658.086 | 9318.5736 | 4256.0249 | 456914.111
| 163873654 | 2028 | MNA014 | 0 | 0 | 9318.5736 | 452658.086 | 9318.5736 | 4256.0249 | 456914.111
| 163873654 | 2029 | MNA014 | 0 | 0 | 9318.5736 | 452658.086 | 9318.5736 | 4256.0249 | 456914.111
| 163873654 | 2030 | MNA014 | 0 | 0 | 9318.5736 | 452658.086 | 9318.5736 | 4256.0249 | 456914.111
| 163873654 | 2031 | MNA014 | 0 | 0 | 9318.5736 | 452658.086 | 9318.5736 | 4256.0249 | 456914.111
| 163873654 | 2032 | MNA014 | 0 | 0 | 9318.5736 | 452658.086 | 9318.5736 | 4256.0249 | 456914.111
| 163873654 | 2033 | MNA014 | 0 | 0 | 9318.5736 | 452658.086 | 9318.5736 | 4256.0249 | 456914.111
| 163873654 | 2034 | MNA014 | 0 | 0 | 9318.5736 | 452658.086 | 9318.5736 | 4256.0249 | 456914.111
| 198038345 | 2023 | MNA014 | 0 | 0 | 0 | 0 | 0 | 572.688 | 572.688
| 198038345 | 2024 | MNA014 | 0 | 0 | 0 | 0 | 0 | 572.688 | 572.688
| 198038345 | 2025 | MNA014 | 0 | 0 | 0 | 0 | 0 | 572.688 | 572.688
| 198038345 | 2026 | MNA014 | 0 | 0 | 0 | 0 | 0 | 572.688 | 572.688
| 198038345 | 2027 | MNA014 | 0 | 0 | 0 | 0 | 0 | 572.688 | 572.688
| 198038345 | 2028 | MNA014 | 0 | 0 | 0 | 0 | 0 | 572.688 | 572.688
| 198038345 | 2029 | MNA014 | 0 | 0 | 0 | 0 | 0 | 572.688 | 572.688
| 198038345 | 2030 | MNA014 | 0 | 0 | 0 | 0 | 0 | 572.688 | 572.688
| 198038345 | 2031 | MNA014 | 0 | 0 | 0 | 0 | 0 | 572.688 | 572.688
| 198038345 | 2032 | MNA014 | 0 | 0 | 0 | 0 | 0 | 572.688 | 572.688
| 198038345 | 2033 | MNA014 | 0 | 0 | 0 | 0 | 0 | 572.688 | 572.688
| 198038345 | 2034 | MNA014 | 0 | 0 | 0 | 0 | 0 | 572.688 | 572.688
| 20221178 | 2023 | MRO007 | 3135.6592 | 0 | 0 | 0 | 3135.6592 | 7519.106 | 7519.106
| 20221178 | 2024 | MRO007 | 7571.9995 | 116.2894 | 0 | 0 | 7571.9995 | 7519.106 | 7635.3954
| 20221178 | 2025 | MRO007 | 10765.5251 | 172.1187 | 0 | 0 | 10765.5251 | 7519.106 | 7691.2247
| 20221178 | 2026 | MRO007 | 10765.5251 | 172.1187 | 0 | 0 | 10765.5251 | 7519.106 | 7691.2247
| 20221178 | 2027 | MRO007 | 10765.5251 | 172.1187 | 0 | 0 | 10765.5251 | 7519.106 | 7691.2247
| 20221178 | 2028 | MRO007 | 10765.5251 | 172.1187 | 0 | 0 | 10765.5251 | 7519.106 | 7691.2247
| 20221178 | 2029 | MRO007 | 10765.5251 | 172.1187 | 0 | 0 | 10765.5251 | 7519.106 | 7691.2247
| 20221178 | 2030 | MRO007 | 10765.5251 | 172.1187 | 0 | 0 | 10765.5251 | 7519.106 | 7691.2247
| 20221178 | 2031 | MRO007 | 10765.5251 | 172.1187 | 0 | 0 | 10765.5251 | 7519.106 | 7691.2247
| 20221178 | 2032 | MRO007 | 10765.5251 | 172.1187 | 0 | 0 | 10765.5251 | 7519.106 | 7691.2247
| 20221178 | 2033 | MRO007 | 10765.5251 | 172.1187 | 0 | 0 | 10765.5251 | 7519.106 | 7691.2247
| 20221178 | 2034 | MRO007 | 10765.5251 | 172.1187 | 0 | 0 | 10765.5251 | 7519.106 | 7691.2247
| 20243680 | 2023 | MRO007 | 54.7497 | 0 | 0 | 0 | 54.7497 | 11379.0953 | 11379.0953
| 20243680 | 2024 | MRO007 | 166.6013 | 2.3211 | 0 | 0 | 166.6013 | 11379.0953 | 11381.4164
| 20243680 | 2025 | MRO007 | 690.5702 | 11.0735 | 0 | 0 | 690.5702 | 11379.0953 | 11390.1688
| 20243680 | 2026 | MRO007 | 690.5702 | 11.0735 | 0 | 0 | 690.5702 | 11379.0953 | 11390.1688
| 20243680 | 2027 | MRO007 | 690.5702 | 11.0735 | 0 | 0 | 690.5702 | 11379.0953 | 11390.1688
| 20243680 | 2028 | MRO007 | 690.5702 | 11.0735 | 0 | 0 | 690.5702 | 11379.0953 | 11390.1688
| 20243680 | 2029 | MRO007 | 690.5702 | 11.0735 | 0 | 0 | 690.5702 | 11379.0953 | 11390.1688
| 20243680 | 2030 | MRO007 | 690.5702 | 11.0735 | 0 | 0 | 690.5702 | 11379.0953 | 11390.1688
| 20243680 | 2031 | MRO007 | 690.5702 | 11.0735 | 0 | 0 | 690.5702 | 11379.0953 | 11390.1688
| 20243680 | 2032 | MRO007 | 690.5702 | 11.0735 | 0 | 0 | 690.5702 | 11379.0953 | 11390.1688
| 20243680 | 2033 | MRO007 | 690.5702 | 11.0735 | 0 | 0 | 690.5702 | 11379.0953 | 11390.1688
| 20243680 | 2034 | MRO007 | 690.5702 | 11.0735 | 0 | 0 | 690.5702 | 11379.0953 | 11390.1688
| 20419244 | 2023 | MRO007 | 5918.1615 | 0 | 0 | 0 | 5918.1615 | 3815.9262 | 3815.9262
| 20419244 | 2024 | MRO007 | 7903.6693 | 155.4595 | 0 | 0 | 7903.6693 | 3815.9262 | 3971.3858
| 20419244 | 2025 | MRO007 | 8019.1066 | 155.1287 | 0 | 0 | 8019.1066 | 3815.9262 | 3971.055
| 20419244 | 2026 | MRO007 | 8019.1066 | 155.1287 | 0 | 0 | 8019.1066 | 3815.9262 | 3971.055
| 20419244 | 2027 | MRO007 | 8019.1066 | 155.1287 | 0 | 0 | 8019.1066 | 3815.9262 | 3971.055
| 20419244 | 2028 | MRO007 | 8019.1066 | 155.1287 | 0 | 0 | 8019.1066 | 3815.9262 | 3971.055
| 20419244 | 2029 | MRO007 | 8019.1066 | 155.1287 | 0 | 0 | 8019.1066 | 3815.9262 | 3971.055
| 20419244 | 2030 | MRO007 | 8019.1066 | 155.1287 | 0 | 0 | 8019.1066 | 3815.9262 | 3971.055
| 20419244 | 2031 | MRO007 | 8019.1066 | 155.1287 | 0 | 0 | 8019.1066 | 3815.9262 | 3971.055
| 20419244 | 2032 | MRO007 | 8019.1066 | 155.1287 | 0 | 0 | 8019.1066 | 3815.9262 | 3971.055
| 20419244 | 2033 | MRO007 | 8019.1066 | 155.1287 | 0 | 0 | 8019.1066 | 3815.9262 | 3971.055
| 20419244 | 2034 | MRO007 | 8019.1066 | 155.1287 | 0 | 0 | 8019.1066 | 3815.9262 | 3971.055
| 20419295 | 2023 | MRO007 | 12038.879 | 0 | 0 | 0 | 12038.879 | 2072.8152 | 2072.8152
| 20419295 | 2024 | MRO007 | 15393.4267 | 262.7269 | 0 | 0 | 15393.4267 | 2072.8152 | 2335.5421
| 20419295 | 2025 | MRO007 | 23243.8295 | 416.4075 | 0 | 0 | 23243.8295 | 2072.8152 | 2489.2227
| 20419295 | 2026 | MRO007 | 23243.8295 | 416.4075 | 0 | 0 | 23243.8295 | 2072.8152 | 2489.2227
| 20419295 | 2027 | MRO007 | 23243.8295 | 416.4075 | 0 | 0 | 23243.8295 | 2072.8152 | 2489.2227
| 20419295 | 2028 | MRO007 | 23243.8295 | 416.4075 | 0 | 0 | 23243.8295 | 2072.8152 | 2489.2227
| 20419295 | 2029 | MRO007 | 23243.8295 | 416.4075 | 0 | 0 | 23243.8295 | 2072.8152 | 2489.2227
| 20419295 | 2030 | MRO007 | 23243.8295 | 416.4075 | 0 | 0 | 23243.8295 | 2072.8152 | 2489.2227
| 20419295 | 2031 | MRO007 | 23243.8295 | 416.4075 | 0 | 0 | 23243.8295 | 2072.8152 | 2489.2227
| 20419295 | 2032 | MRO007 | 23243.8295 | 416.4075 | 0 | 0 | 23243.8295 | 2072.8152 | 2489.2227
| 20419295 | 2033 | MRO007 | 23243.8295 | 416.4075 | 0 | 0 | 23243.8295 | 2072.8152 | 2489.2227
| 20419295 | 2034 | MRO007 | 23243.8295 | 416.4075 | 0 | 0 | 23243.8295 | 2072.8152 | 2489.2227
| 20563092 | 2023 | MRO007 | 0 | 0 | 0 | 0 | 0 | 2171.366 | 2171.366
| 20563092 | 2024 | MRO007 | 0 | 0 | 0 | 0 | 0 | 2171.366 | 2171.366
| 20563092 | 2025 | MRO007 | 0 | 0 | 0 | 0 | 0 | 2171.366 | 2171.366
| 20563092 | 2026 | MRO007 | 0 | 0 | 0 | 0 | 0 | 2171.366 | 2171.366
| 20563092 | 2027 | MRO007 | 0 | 0 | 0 | 0 | 0 | 2171.366 | 2171.366
| 20563092 | 2028 | MRO007 | 0 | 0 | 0 | 0 | 0 | 2171.366 | 2171.366
| 20563092 | 2029 | MRO007 | 0 | 0 | 0 | 0 | 0 | 2171.366 | 2171.366
| 20563092 | 2030 | MRO007 | 0 | 0 | 0 | 0 | 0 | 2171.366 | 2171.366
| 20563092 | 2031 | MRO007 | 0 | 0 | 0 | 0 | 0 | 2171.366 | 2171.366
| 20563092 | 2032 | MRO007 | 0 | 0 | 0 | 0 | 0 | 2171.366 | 2171.366
| 20563092 | 2033 | MRO007 | 0 | 0 | 0 | 0 | 0 | 2171.366 | 2171.366
| 20563092 | 2034 | MRO007 | 0 | 0 | 0 | 0 | 0 | 2171.366 | 2171.366
| 47502161 | 2023 | MRO007 | 8895.0241 | 0 | 0 | 0 | 8895.0241 | 4022.9721 | 4022.9721
| 47502161 | 2024 | MRO007 | 14327.1804 | 345.2213 | 0 | 0 | 14327.1804 | 4022.9721 | 4368.1934
| 47502161 | 2025 | MRO007 | 16731.3056 | 395.4732 | 0 | 0 | 16731.3056 | 4022.9721 | 4418.4453
| 47502161 | 2026 | MRO007 | 16731.3056 | 395.4732 | 0 | 0 | 16731.3056 | 4022.9721 | 4418.4453
| 47502161 | 2027 | MRO007 | 16731.3056 | 395.4732 | 0 | 0 | 16731.3056 | 4022.9721 | 4418.4453
| 47502161 | 2028 | MRO007 | 16731.3056 | 395.4732 | 0 | 0 | 16731.3056 | 4022.9721 | 4418.4453
| 47502161 | 2029 | MRO007 | 16731.3056 | 395.4732 | 0 | 0 | 16731.3056 | 4022.9721 | 4418.4453
| 47502161 | 2030 | MRO007 | 16731.3056 | 395.4732 | 0 | 0 | 16731.3056 | 4022.9721 | 4418.4453
| 47502161 | 2031 | MRO007 | 16731.3056 | 395.4732 | 0 | 0 | 16731.3056 | 4022.9721 | 4418.4453
| 47502161 | 2032 | MRO007 | 16731.3056 | 395.4732 | 0 | 0 | 16731.3056 | 4022.9721 | 4418.4453
| 47502161 | 2033 | MRO007 | 16731.3056 | 395.4732 | 0 | 0 | 16731.3056 | 4022.9721 | 4418.4453
| 47502161 | 2034 | MRO007 | 16731.3056 | 395.4732 | 0 | 0 | 16731.3056 | 4022.9721 | 4418.4453
| 139674843 | 2023 | MRO007 | 2595.1857 | 0 | 0 | 0 | 2595.1857 | 2444.8621 | 2444.8621
| 139674843 | 2024 | MRO007 | 2296.875 | 58.245 | 0 | 0 | 2296.875 | 2444.8621 | 2503.1071
| 139674843 | 2025 | MRO007 | 2704.7773 | 80.6279 | 0 | 0 | 2704.7773 | 2444.8621 | 2525.49
| 139674843 | 2026 | MRO007 | 2704.7773 | 80.6279 | 0 | 0 | 2704.7773 | 2444.8621 | 2525.49
| 139674843 | 2027 | MRO007 | 2704.7773 | 80.6279 | 0 | 0 | 2704.7773 | 2444.8621 | 2525.49
| 139674843 | 2028 | MRO007 | 2704.7773 | 80.6279 | 0 | 0 | 2704.7773 | 2444.8621 | 2525.49
| 139674843 | 2029 | MRO007 | 2704.7773 | 80.6279 | 0 | 0 | 2704.7773 | 2444.8621 | 2525.49
| 139674843 | 2030 | MRO007 | 2704.7773 | 80.6279 | 0 | 0 | 2704.7773 | 2444.8621 | 2525.49
| 139674843 | 2031 | MRO007 | 2704.7773 | 80.6279 | 0 | 0 | 2704.7773 | 2444.8621 | 2525.49
| 139674843 | 2032 | MRO007 | 2704.7773 | 80.6279 | 0 | 0 | 2704.7773 | 2444.8621 | 2525.49
| 139674843 | 2033 | MRO007 | 2704.7773 | 80.6279 | 0 | 0 | 2704.7773 | 2444.8621 | 2525.49
| 139674843 | 2034 | MRO007 | 2704.7773 | 80.6279 | 0 | 0 | 2704.7773 | 2444.8621 | 2525.49
| 162074576 | 2023 | MRO007 | 3393.5467 | 0 | 0 | 0 | 3393.5467 | 4322.1956 | 4322.1956
| 162074576 | 2024 | MRO007 | 5280.3694 | 95.1894 | 0 | 0 | 5280.3694 | 4322.1956 | 4417.385
| 162074576 | 2025 | MRO007 | 6550.1539 | 106.8615 | 0 | 0 | 6550.1539 | 4322.1956 | 4429.0572
| 162074576 | 2026 | MRO007 | 6550.1539 | 106.8615 | 0 | 0 | 6550.1539 | 4322.1956 | 4429.0572
| 162074576 | 2027 | MRO007 | 6550.1539 | 106.8615 | 0 | 0 | 6550.1539 | 4322.1956 | 4429.0572
| 162074576 | 2028 | MRO007 | 6550.1539 | 106.8615 | 0 | 0 | 6550.1539 | 4322.1956 | 4429.0572
| 162074576 | 2029 | MRO007 | 6550.1539 | 106.8615 | 0 | 0 | 6550.1539 | 4322.1956 | 4429.0572
| 162074576 | 2030 | MRO007 | 6550.1539 | 106.8615 | 0 | 0 | 6550.1539 | 4322.1956 | 4429.0572
| 162074576 | 2031 | MRO007 | 6550.1539 | 106.8615 | 0 | 0 | 6550.1539 | 4322.1956 | 4429.0572
| 162074576 | 2032 | MRO007 | 6550.1539 | 106.8615 | 0 | 0 | 6550.1539 | 4322.1956 | 4429.0572
| 162074576 | 2033 | MRO007 | 6550.1539 | 106.8615 | 0 | 0 | 6550.1539 | 4322.1956 | 4429.0572
| 162074576 | 2034 | MRO007 | 6550.1539 | 106.8615 | 0 | 0 | 6550.1539 | 4322.1956 | 4429.0572
| 20163297 | 2023 | MRO008 | 0 | 0 | 0 | 0 | 0 | 1663.4225 | 1663.4225
| 20163297 | 2024 | MRO008 | 0 | 0 | 0 | 0 | 0 | 1663.4225 | 1663.4225
| 20163297 | 2025 | MRO008 | 0 | 0 | 0 | 0 | 0 | 1663.4225 | 1663.4225
| 20163297 | 2026 | MRO008 | 0 | 0 | 0 | 0 | 0 | 1663.4225 | 1663.4225
| 20163297 | 2027 | MRO008 | 0 | 0 | 0 | 0 | 0 | 1663.4225 | 1663.4225
| 20163297 | 2028 | MRO008 | 0 | 0 | 0 | 0 | 0 | 1663.4225 | 1663.4225
| 20163297 | 2029 | MRO008 | 0 | 0 | 0 | 0 | 0 | 1663.4225 | 1663.4225
| 20163297 | 2030 | MRO008 | 0 | 0 | 0 | 0 | 0 | 1663.4225 | 1663.4225
| 20163297 | 2031 | MRO008 | 0 | 0 | 0 | 0 | 0 | 1663.4225 | 1663.4225
| 20163297 | 2032 | MRO008 | 0 | 0 | 0 | 0 | 0 | 1663.4225 | 1663.4225
| 20163297 | 2033 | MRO008 | 0 | 0 | 0 | 0 | 0 | 1663.4225 | 1663.4225
| 20163297 | 2034 | MRO008 | 0 | 0 | 0 | 0 | 0 | 1663.4225 | 1663.4225
| 20163513 | 2023 | MRO008 | 9825.1618 | 0 | 124.5196 | 5103.5228 | 9949.6815 | 5194.0836 | 10297.6064
| 20163513 | 2024 | MRO008 | 10814.6414 | 234.8686 | 136.6934 | 5602.473 | 10951.3348 | 5194.0836 | 11031.4253
| 20163513 | 2025 | MRO008 | 10814.6414 | 234.8686 | 136.6934 | 5602.473 | 10951.3348 | 5194.0836 | 11031.4253
| 20163513 | 2026 | MRO008 | 10814.6414 | 234.8686 | 136.6934 | 5602.473 | 10951.3348 | 5194.0836 | 11031.4253
| 20163513 | 2027 | MRO008 | 10814.6414 | 234.8686 | 136.6934 | 5602.473 | 10951.3348 | 5194.0836 | 11031.4253
| 20163513 | 2028 | MRO008 | 10814.6414 | 234.8686 | 136.6934 | 5602.473 | 10951.3348 | 5194.0836 | 11031.4253
| 20163513 | 2029 | MRO008 | 10814.6414 | 234.8686 | 136.6934 | 5602.473 | 10951.3348 | 5194.0836 | 11031.4253
| 20163513 | 2030 | MRO008 | 10814.6414 | 234.8686 | 136.6934 | 5602.473 | 10951.3348 | 5194.0836 | 11031.4253
| 20163513 | 2031 | MRO008 | 10814.6414 | 234.8686 | 136.6934 | 5602.473 | 10951.3348 | 5194.0836 | 11031.4253
| 20163513 | 2032 | MRO008 | 10814.6414 | 234.8686 | 136.6934 | 5602.473 | 10951.3348 | 5194.0836 | 11031.4253
| 20163513 | 2033 | MRO008 | 10814.6414 | 234.8686 | 136.6934 | 5602.473 | 10951.3348 | 5194.0836 | 11031.4253
| 20163513 | 2034 | MRO008 | 10814.6414 | 234.8686 | 136.6934 | 5602.473 | 10951.3348 | 5194.0836 | 11031.4253
| 20280442 | 2023 | MRO008 | 0 | 0 | 0 | 0 | 0 | 3641.9443 | 3641.9443
| 20280442 | 2024 | MRO008 | 25.977 | 0.46055 | 0 | 0 | 25.977 | 3641.9443 | 3642.4048
| 20280442 | 2025 | MRO008 | 25.977 | 0.46055 | 0 | 0 | 25.977 | 3641.9443 | 3642.4048
| 20280442 | 2026 | MRO008 | 25.977 | 0.46055 | 0 | 0 | 25.977 | 3641.9443 | 3642.4048
| 20280442 | 2027 | MRO008 | 25.977 | 0.46055 | 0 | 0 | 25.977 | 3641.9443 | 3642.4048
| 20280442 | 2028 | MRO008 | 25.977 | 0.46055 | 0 | 0 | 25.977 | 3641.9443 | 3642.4048
| 20280442 | 2029 | MRO008 | 25.977 | 0.46055 | 0 | 0 | 25.977 | 3641.9443 | 3642.4048
| 20280442 | 2030 | MRO008 | 25.977 | 0.46055 | 0 | 0 | 25.977 | 3641.9443 | 3642.4048
| 20280442 | 2031 | MRO008 | 25.977 | 0.46055 | 0 | 0 | 25.977 | 3641.9443 | 3642.4048
| 20280442 | 2032 | MRO008 | 25.977 | 0.46055 | 0 | 0 | 25.977 | 3641.9443 | 3642.4048
| 20280442 | 2033 | MRO008 | 25.977 | 0.46055 | 0 | 0 | 25.977 | 3641.9443 | 3642.4048
| 20280442 | 2034 | MRO008 | 25.977 | 0.46055 | 0 | 0 | 25.977 | 3641.9443 | 3642.4048
| 20531985 | 2023 | MRO008 | 0 | 0 | 0 | 0 | 0 | 1676.4069 | 1676.4069
| 20531985 | 2024 | MRO008 | 1057.5969 | 19.7186 | 0 | 0 | 1057.5969 | 1676.4069 | 1696.1255
| 20531985 | 2025 | MRO008 | 1057.5969 | 19.7186 | 0 | 0 | 1057.5969 | 1676.4069 | 1696.1255
| 20531985 | 2026 | MRO008 | 1057.5969 | 19.7186 | 0 | 0 | 1057.5969 | 1676.4069 | 1696.1255
| 20531985 | 2027 | MRO008 | 1057.5969 | 19.7186 | 0 | 0 | 1057.5969 | 1676.4069 | 1696.1255
| 20531985 | 2028 | MRO008 | 1057.5969 | 19.7186 | 0 | 0 | 1057.5969 | 1676.4069 | 1696.1255
| 20531985 | 2029 | MRO008 | 1057.5969 | 19.7186 | 0 | 0 | 1057.5969 | 1676.4069 | 1696.1255
| 20531985 | 2030 | MRO008 | 1057.5969 | 19.7186 | 0 | 0 | 1057.5969 | 1676.4069 | 1696.1255
| 20531985 | 2031 | MRO008 | 1057.5969 | 19.7186 | 0 | 0 | 1057.5969 | 1676.4069 | 1696.1255
| 20531985 | 2032 | MRO008 | 1057.5969 | 19.7186 | 0 | 0 | 1057.5969 | 1676.4069 | 1696.1255
| 20531985 | 2033 | MRO008 | 1057.5969 | 19.7186 | 0 | 0 | 1057.5969 | 1676.4069 | 1696.1255
| 20531985 | 2034 | MRO008 | 1057.5969 | 19.7186 | 0 | 0 | 1057.5969 | 1676.4069 | 1696.1255
| 20546216 | 2023 | MRO008 | 1537.308 | 0 | 0 | 0 | 1537.308 | 1199.6889 | 1199.6889
| 20546216 | 2024 | MRO008 | 1648.6736 | 29.859 | 0 | 0 | 1648.6736 | 1199.6889 | 1229.5479
| 20546216 | 2025 | MRO008 | 1648.6736 | 29.859 | 0 | 0 | 1648.6736 | 1199.6889 | 1229.5479
| 20546216 | 2026 | MRO008 | 1648.6736 | 29.859 | 0 | 0 | 1648.6736 | 1199.6889 | 1229.5479
| 20546216 | 2027 | MRO008 | 1648.6736 | 29.859 | 0 | 0 | 1648.6736 | 1199.6889 | 1229.5479
| 20546216 | 2028 | MRO008 | 1648.6736 | 29.859 | 0 | 0 | 1648.6736 | 1199.6889 | 1229.5479
| 20546216 | 2029 | MRO008 | 1648.6736 | 29.859 | 0 | 0 | 1648.6736 | 1199.6889 | 1229.5479
| 20546216 | 2030 | MRO008 | 1648.6736 | 29.859 | 0 | 0 | 1648.6736 | 1199.6889 | 1229.5479
| 20546216 | 2031 | MRO008 | 1648.6736 | 29.859 | 0 | 0 | 1648.6736 | 1199.6889 | 1229.5479
| 20546216 | 2032 | MRO008 | 1648.6736 | 29.859 | 0 | 0 | 1648.6736 | 1199.6889 | 1229.5479
| 20546216 | 2033 | MRO008 | 1648.6736 | 29.859 | 0 | 0 | 1648.6736 | 1199.6889 | 1229.5479
| 20546216 | 2034 | MRO008 | 1648.6736 | 29.859 | 0 | 0 | 1648.6736 | 1199.6889 | 1229.5479
| 19922723 | 2023 | NHL015 | 317.7941 | 0 | 0 | 0 | 317.7941 | 13959.1093 | 13959.1093
| 19922723 | 2024 | NHL015 | 966.3597 | 12.2529 | 0 | 0 | 966.3597 | 13959.1093 | 13971.3621
| 19922723 | 2025 | NHL015 | 1145.0957 | 11.5277 | 0 | 0 | 1145.0957 | 13959.1093 | 13970.637
| 19922723 | 2026 | NHL015 | 2495.1049 | 8.7337 | 0 | 0 | 2495.1049 | 13959.1093 | 13967.843
| 19922723 | 2027 | NHL015 | 2495.1049 | 8.7337 | 0 | 0 | 2495.1049 | 13959.1093 | 13967.843
| 19922723 | 2028 | NHL015 | 2495.1049 | 8.7337 | 0 | 0 | 2495.1049 | 13959.1093 | 13967.843
| 19922723 | 2029 | NHL015 | 2495.1049 | 8.7337 | 0 | 0 | 2495.1049 | 13959.1093 | 13967.843
| 19922723 | 2030 | NHL015 | 2495.1049 | 8.7337 | 0 | 0 | 2495.1049 | 13959.1093 | 13967.843
| 19922723 | 2031 | NHL015 | 2495.1049 | 8.7337 | 0 | 0 | 2495.1049 | 13959.1093 | 13967.843
| 19922723 | 2032 | NHL015 | 2495.1049 | 8.7337 | 0 | 0 | 2495.1049 | 13959.1093 | 13967.843
| 19922723 | 2033 | NHL015 | 2495.1049 | 8.7337 | 0 | 0 | 2495.1049 | 13959.1093 | 13967.843
| 19922723 | 2034 | NHL015 | 2495.1049 | 8.7337 | 0 | 0 | 2495.1049 | 13959.1093 | 13967.843
| 19933363 | 2023 | NHL015 | 0 | 0 | 0 | 0 | 0 | 22139.459 | 22139.459
| 19933363 | 2024 | NHL015 | 0 | 0 | 0 | 0 | 0 | 22139.459 | 22139.459
| 19933363 | 2025 | NHL015 | 0 | 0 | 0 | 0 | 0 | 22139.459 | 22139.459
| 19933363 | 2026 | NHL015 | 0 | 0 | 0 | 0 | 0 | 22139.459 | 22139.459
| 19933363 | 2027 | NHL015 | 0 | 0 | 0 | 0 | 0 | 22139.459 | 22139.459
| 19933363 | 2028 | NHL015 | 0 | 0 | 0 | 0 | 0 | 22139.459 | 22139.459
| 19933363 | 2029 | NHL015 | 0 | 0 | 0 | 0 | 0 | 22139.459 | 22139.459
| 19933363 | 2030 | NHL015 | 0 | 0 | 0 | 0 | 0 | 22139.459 | 22139.459
| 19933363 | 2031 | NHL015 | 0 | 0 | 0 | 0 | 0 | 22139.459 | 22139.459
| 19933363 | 2032 | NHL015 | 0 | 0 | 0 | 0 | 0 | 22139.459 | 22139.459
| 19933363 | 2033 | NHL015 | 0 | 0 | 0 | 0 | 0 | 22139.459 | 22139.459
| 19933363 | 2034 | NHL015 | 0 | 0 | 0 | 0 | 0 | 22139.459 | 22139.459
| 19933414 | 2023 | NHL015 | 0 | 0 | 0 | 0 | 0 | 9820.8177 | 9820.8177
| 19933414 | 2024 | NHL015 | 109.3904 | 2.2942 | 0 | 0 | 109.3904 | 9820.8177 | 9823.1119
| 19933414 | 2025 | NHL015 | 174.0057 | 2.1781 | 0 | 0 | 174.0057 | 9820.8177 | 9822.9958
| 19933414 | 2026 | NHL015 | 968.3367 | 3.1735 | 0 | 0 | 968.3367 | 9820.8177 | 9823.9912
| 19933414 | 2027 | NHL015 | 968.3367 | 3.1735 | 0 | 0 | 968.3367 | 9820.8177 | 9823.9912
| 19933414 | 2028 | NHL015 | 968.3367 | 3.1735 | 0 | 0 | 968.3367 | 9820.8177 | 9823.9912
| 19933414 | 2029 | NHL015 | 968.3367 | 3.1735 | 0 | 0 | 968.3367 | 9820.8177 | 9823.9912
| 19933414 | 2030 | NHL015 | 968.3367 | 3.1735 | 0 | 0 | 968.3367 | 9820.8177 | 9823.9912
| 19933414 | 2031 | NHL015 | 968.3367 | 3.1735 | 0 | 0 | 968.3367 | 9820.8177 | 9823.9912
| 19933414 | 2032 | NHL015 | 968.3367 | 3.1735 | 0 | 0 | 968.3367 | 9820.8177 | 9823.9912
| 19933414 | 2033 | NHL015 | 968.3367 | 3.1735 | 0 | 0 | 968.3367 | 9820.8177 | 9823.9912
| 19933414 | 2034 | NHL015 | 968.3367 | 3.1735 | 0 | 0 | 968.3367 | 9820.8177 | 9823.9912
| 19933685 | 2023 | NHL015 | 2591.909 | 0 | 0 | 0 | 2591.909 | 17804.3438 | 17804.3438
| 19933685 | 2024 | NHL015 | 3346.6759 | 50.9012 | 0 | 0 | 3346.6759 | 17804.3438 | 17855.245
| 19933685 | 2025 | NHL015 | 2619.2481 | 41.9366 | 0 | 0 | 2619.2481 | 17804.3438 | 17846.2804
| 19933685 | 2026 | NHL015 | 2776.304 | 18.9545 | 0 | 0 | 2776.304 | 17804.3438 | 17823.2983
| 19933685 | 2027 | NHL015 | 2776.304 | 18.9545 | 0 | 0 | 2776.304 | 17804.3438 | 17823.2983
| 19933685 | 2028 | NHL015 | 2776.304 | 18.9545 | 0 | 0 | 2776.304 | 17804.3438 | 17823.2983
| 19933685 | 2029 | NHL015 | 2776.304 | 18.9545 | 0 | 0 | 2776.304 | 17804.3438 | 17823.2983
| 19933685 | 2030 | NHL015 | 2776.304 | 18.9545 | 0 | 0 | 2776.304 | 17804.3438 | 17823.2983
| 19933685 | 2031 | NHL015 | 2776.304 | 18.9545 | 0 | 0 | 2776.304 | 17804.3438 | 17823.2983
| 19933685 | 2032 | NHL015 | 2776.304 | 18.9545 | 0 | 0 | 2776.304 | 17804.3438 | 17823.2983
| 19933685 | 2033 | NHL015 | 2776.304 | 18.9545 | 0 | 0 | 2776.304 | 17804.3438 | 17823.2983
| 19933685 | 2034 | NHL015 | 2776.304 | 18.9545 | 0 | 0 | 2776.304 | 17804.3438 | 17823.2983
| 19936793 | 2023 | NHL015 | 93.8523 | 0 | 0 | 0 | 93.8523 | 6069.1998 | 6069.1998
| 19936793 | 2024 | NHL015 | 70.0202 | 1.0847 | 0 | 0 | 70.0202 | 6069.1998 | 6070.2844
| 19936793 | 2025 | NHL015 | 279.9568 | 2.7207 | 0 | 0 | 279.9568 | 6069.1998 | 6071.9204
| 19936793 | 2026 | NHL015 | 2158.0282 | 7.375 | 0 | 0 | 2158.0282 | 6069.1998 | 6076.5748
| 19936793 | 2027 | NHL015 | 2158.0282 | 7.375 | 0 | 0 | 2158.0282 | 6069.1998 | 6076.5748
| 19936793 | 2028 | NHL015 | 2158.0282 | 7.375 | 0 | 0 | 2158.0282 | 6069.1998 | 6076.5748
| 19936793 | 2029 | NHL015 | 2158.0282 | 7.375 | 0 | 0 | 2158.0282 | 6069.1998 | 6076.5748
| 19936793 | 2030 | NHL015 | 2158.0282 | 7.375 | 0 | 0 | 2158.0282 | 6069.1998 | 6076.5748
| 19936793 | 2031 | NHL015 | 2158.0282 | 7.375 | 0 | 0 | 2158.0282 | 6069.1998 | 6076.5748
| 19936793 | 2032 | NHL015 | 2158.0282 | 7.375 | 0 | 0 | 2158.0282 | 6069.1998 | 6076.5748
| 19936793 | 2033 | NHL015 | 2158.0282 | 7.375 | 0 | 0 | 2158.0282 | 6069.1998 | 6076.5748
| 19936793 | 2034 | NHL015 | 2158.0282 | 7.375 | 0 | 0 | 2158.0282 | 6069.1998 | 6076.5748
| 19951861 | 2023 | NHL015 | 0 | 0 | 0.26994 | 12.0085 | 0.26994 | 14042.9912 | 14054.9997
| 19951861 | 2024 | NHL015 | 0 | 0 | 0.32971 | 14.6675 | 0.32971 | 14042.9912 | 14057.6587
| 19951861 | 2025 | NHL015 | 0 | 0 | 0.046214 | 2.0559 | 0.046214 | 14042.9912 | 14045.0471
| 19951861 | 2026 | NHL015 | 0 | 0 | 0.0040039 | 0.17811 | 0.0040039 | 14042.9912 | 14043.1693
| 19951861 | 2027 | NHL015 | 0 | 0 | 0.0040039 | 0.17811 | 0.0040039 | 14042.9912 | 14043.1693
| 19951861 | 2028 | NHL015 | 0 | 0 | 0.0040039 | 0.17811 | 0.0040039 | 14042.9912 | 14043.1693
| 19951861 | 2029 | NHL015 | 0 | 0 | 0.0040039 | 0.17811 | 0.0040039 | 14042.9912 | 14043.1693
| 19951861 | 2030 | NHL015 | 0 | 0 | 0.0040039 | 0.17811 | 0.0040039 | 14042.9912 | 14043.1693
| 19951861 | 2031 | NHL015 | 0 | 0 | 0.0040039 | 0.17811 | 0.0040039 | 14042.9912 | 14043.1693
| 19951861 | 2032 | NHL015 | 0 | 0 | 0.0040039 | 0.17811 | 0.0040039 | 14042.9912 | 14043.1693
| 19951861 | 2033 | NHL015 | 0 | 0 | 0.0040039 | 0.17811 | 0.0040039 | 14042.9912 | 14043.1693
| 19951861 | 2034 | NHL015 | 0 | 0 | 0.0040039 | 0.17811 | 0.0040039 | 14042.9912 | 14043.1693
| 19952077 | 2023 | NHL015 | 0 | 0 | 4.9406 | 219.7883 | 4.9406 | 2912.2659 | 3132.0541
| 19952077 | 2024 | NHL015 | 0 | 0 | 7.5001 | 333.6458 | 7.5001 | 2912.2659 | 3245.9117
| 19952077 | 2025 | NHL015 | 0 | 0 | 3.9429 | 175.4045 | 3.9429 | 2912.2659 | 3087.6704
| 19952077 | 2026 | NHL015 | 0 | 0 | 1175.5611 | 52295.7841 | 1175.5611 | 2912.2659 | 55208.0499
| 19952077 | 2027 | NHL015 | 0 | 0 | 1175.5611 | 52295.7841 | 1175.5611 | 2912.2659 | 55208.0499
| 19952077 | 2028 | NHL015 | 0 | 0 | 1175.5611 | 52295.7841 | 1175.5611 | 2912.2659 | 55208.0499
| 19952077 | 2029 | NHL015 | 0 | 0 | 1175.5611 | 52295.7841 | 1175.5611 | 2912.2659 | 55208.0499
| 19952077 | 2030 | NHL015 | 0 | 0 | 1175.5611 | 52295.7841 | 1175.5611 | 2912.2659 | 55208.0499
| 19952077 | 2031 | NHL015 | 0 | 0 | 1175.5611 | 52295.7841 | 1175.5611 | 2912.2659 | 55208.0499
| 19952077 | 2032 | NHL015 | 0 | 0 | 1175.5611 | 52295.7841 | 1175.5611 | 2912.2659 | 55208.0499
| 19952077 | 2033 | NHL015 | 0 | 0 | 1175.5611 | 52295.7841 | 1175.5611 | 2912.2659 | 55208.0499
| 19952077 | 2034 | NHL015 | 0 | 0 | 1175.5611 | 52295.7841 | 1175.5611 | 2912.2659 | 55208.0499
| 19955740 | 2023 | NHL015 | 0 | 0 | 0 | 0 | 0 | 5509.1731 | 5509.1731
| 19955740 | 2024 | NHL015 | 0 | 0 | 0 | 0 | 0 | 5509.1731 | 5509.1731
| 19955740 | 2025 | NHL015 | 0 | 0 | 0 | 0 | 0 | 5509.1731 | 5509.1731
| 19955740 | 2026 | NHL015 | 0 | 0 | 0 | 0 | 0 | 5509.1731 | 5509.1731
| 19955740 | 2027 | NHL015 | 0 | 0 | 0 | 0 | 0 | 5509.1731 | 5509.1731
| 19955740 | 2028 | NHL015 | 0 | 0 | 0 | 0 | 0 | 5509.1731 | 5509.1731
| 19955740 | 2029 | NHL015 | 0 | 0 | 0 | 0 | 0 | 5509.1731 | 5509.1731
| 19955740 | 2030 | NHL015 | 0 | 0 | 0 | 0 | 0 | 5509.1731 | 5509.1731
| 19955740 | 2031 | NHL015 | 0 | 0 | 0 | 0 | 0 | 5509.1731 | 5509.1731
| 19955740 | 2032 | NHL015 | 0 | 0 | 0 | 0 | 0 | 5509.1731 | 5509.1731
| 19955740 | 2033 | NHL015 | 0 | 0 | 0 | 0 | 0 | 5509.1731 | 5509.1731
| 19955740 | 2034 | NHL015 | 0 | 0 | 0 | 0 | 0 | 5509.1731 | 5509.1731
| 19957666 | 2023 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2366.88 | 2366.88
| 19957666 | 2024 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2366.88 | 2366.88
| 19957666 | 2025 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2366.88 | 2366.88
| 19957666 | 2026 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2366.88 | 2366.88
| 19957666 | 2027 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2366.88 | 2366.88
| 19957666 | 2028 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2366.88 | 2366.88
| 19957666 | 2029 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2366.88 | 2366.88
| 19957666 | 2030 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2366.88 | 2366.88
| 19957666 | 2031 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2366.88 | 2366.88
| 19957666 | 2032 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2366.88 | 2366.88
| 19957666 | 2033 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2366.88 | 2366.88
| 19957666 | 2034 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2366.88 | 2366.88
| 19957706 | 2023 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16209.7487 | 16209.7487
| 19957706 | 2024 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16209.7487 | 16209.7487
| 19957706 | 2025 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16209.7487 | 16209.7487
| 19957706 | 2026 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16209.7487 | 16209.7487
| 19957706 | 2027 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16209.7487 | 16209.7487
| 19957706 | 2028 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16209.7487 | 16209.7487
| 19957706 | 2029 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16209.7487 | 16209.7487
| 19957706 | 2030 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16209.7487 | 16209.7487
| 19957706 | 2031 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16209.7487 | 16209.7487
| 19957706 | 2032 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16209.7487 | 16209.7487
| 19957706 | 2033 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16209.7487 | 16209.7487
| 19957706 | 2034 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16209.7487 | 16209.7487
| 19959047 | 2023 | NHL015 | 0 | 0 | 693.5597 | 30853.5651 | 693.5597 | 2128.8877 | 32982.4528
| 19959047 | 2024 | NHL015 | 0 | 0 | 760.1127 | 33814.2284 | 760.1127 | 2128.8877 | 35943.1161
| 19959047 | 2025 | NHL015 | 0 | 0 | 10139.1738 | 451049.3462 | 10139.1738 | 2128.8877 | 453178.2339
| 19959047 | 2026 | NHL015 | 0 | 0 | 9545.3648 | 424633.273 | 9545.3648 | 2128.8877 | 426762.1607
| 19959047 | 2027 | NHL015 | 0 | 0 | 9545.3648 | 424633.273 | 9545.3648 | 2128.8877 | 426762.1607
| 19959047 | 2028 | NHL015 | 0 | 0 | 9545.3648 | 424633.273 | 9545.3648 | 2128.8877 | 426762.1607
| 19959047 | 2029 | NHL015 | 0 | 0 | 9545.3648 | 424633.273 | 9545.3648 | 2128.8877 | 426762.1607
| 19959047 | 2030 | NHL015 | 0 | 0 | 9545.3648 | 424633.273 | 9545.3648 | 2128.8877 | 426762.1607
| 19959047 | 2031 | NHL015 | 0 | 0 | 9545.3648 | 424633.273 | 9545.3648 | 2128.8877 | 426762.1607
| 19959047 | 2032 | NHL015 | 0 | 0 | 9545.3648 | 424633.273 | 9545.3648 | 2128.8877 | 426762.1607
| 19959047 | 2033 | NHL015 | 0 | 0 | 9545.3648 | 424633.273 | 9545.3648 | 2128.8877 | 426762.1607
| 19959047 | 2034 | NHL015 | 0 | 0 | 9545.3648 | 424633.273 | 9545.3648 | 2128.8877 | 426762.1607
| 19964900 | 2023 | NHL015 | 948.2903 | 0 | 0 | 0 | 948.2903 | 9533.6341 | 9533.6341
| 19964900 | 2024 | NHL015 | 992.9009 | 14.2713 | 0 | 0 | 992.9009 | 9533.6341 | 9547.9054
| 19964900 | 2025 | NHL015 | 4066.6955 | 57.0732 | 0 | 0 | 4066.6955 | 9533.6341 | 9590.7073
| 19964900 | 2026 | NHL015 | 6840.5895 | 51.3574 | 0 | 0 | 6840.5895 | 9533.6341 | 9584.9915
| 19964900 | 2027 | NHL015 | 6840.5895 | 51.3574 | 0 | 0 | 6840.5895 | 9533.6341 | 9584.9915
| 19964900 | 2028 | NHL015 | 6840.5895 | 51.3574 | 0 | 0 | 6840.5895 | 9533.6341 | 9584.9915
| 19964900 | 2029 | NHL015 | 6840.5895 | 51.3574 | 0 | 0 | 6840.5895 | 9533.6341 | 9584.9915
| 19964900 | 2030 | NHL015 | 6840.5895 | 51.3574 | 0 | 0 | 6840.5895 | 9533.6341 | 9584.9915
| 19964900 | 2031 | NHL015 | 6840.5895 | 51.3574 | 0 | 0 | 6840.5895 | 9533.6341 | 9584.9915
| 19964900 | 2032 | NHL015 | 6840.5895 | 51.3574 | 0 | 0 | 6840.5895 | 9533.6341 | 9584.9915
| 19964900 | 2033 | NHL015 | 6840.5895 | 51.3574 | 0 | 0 | 6840.5895 | 9533.6341 | 9584.9915
| 19964900 | 2034 | NHL015 | 6840.5895 | 51.3574 | 0 | 0 | 6840.5895 | 9533.6341 | 9584.9915
| 19968509 | 2023 | NHL015 | 4612.3371 | 0 | 0 | 0 | 4612.3371 | 15161.2497 | 15161.2497
| 19968509 | 2024 | NHL015 | 4318.4029 | 98.8336 | 0 | 0 | 4318.4029 | 15161.2497 | 15260.0832
| 19968509 | 2025 | NHL015 | 6310.6957 | 139.4174 | 0 | 0 | 6310.6957 | 15161.2497 | 15300.6671
| 19968509 | 2026 | NHL015 | 6881.9718 | 84.7108 | 0 | 0 | 6881.9718 | 15161.2497 | 15245.9605
| 19968509 | 2027 | NHL015 | 6881.9718 | 84.7108 | 0 | 0 | 6881.9718 | 15161.2497 | 15245.9605
| 19968509 | 2028 | NHL015 | 6881.9718 | 84.7108 | 0 | 0 | 6881.9718 | 15161.2497 | 15245.9605
| 19968509 | 2029 | NHL015 | 6881.9718 | 84.7108 | 0 | 0 | 6881.9718 | 15161.2497 | 15245.9605
| 19968509 | 2030 | NHL015 | 6881.9718 | 84.7108 | 0 | 0 | 6881.9718 | 15161.2497 | 15245.9605
| 19968509 | 2031 | NHL015 | 6881.9718 | 84.7108 | 0 | 0 | 6881.9718 | 15161.2497 | 15245.9605
| 19968509 | 2032 | NHL015 | 6881.9718 | 84.7108 | 0 | 0 | 6881.9718 | 15161.2497 | 15245.9605
| 19968509 | 2033 | NHL015 | 6881.9718 | 84.7108 | 0 | 0 | 6881.9718 | 15161.2497 | 15245.9605
| 19968509 | 2034 | NHL015 | 6881.9718 | 84.7108 | 0 | 0 | 6881.9718 | 15161.2497 | 15245.9605
| 19968736 | 2023 | NHL015 | 0 | 0 | 0 | 0 | 0 | 11186.9686 | 11186.9686
| 19968736 | 2024 | NHL015 | 0 | 0 | 0 | 0 | 0 | 11186.9686 | 11186.9686
| 19968736 | 2025 | NHL015 | 2360.1279 | 41.64 | 0 | 0 | 2360.1279 | 11186.9686 | 11228.6086
| 19968736 | 2026 | NHL015 | 6877.3159 | 60.8756 | 0 | 0 | 6877.3159 | 11186.9686 | 11247.8443
| 19968736 | 2027 | NHL015 | 6877.3159 | 60.8756 | 0 | 0 | 6877.3159 | 11186.9686 | 11247.8443
| 19968736 | 2028 | NHL015 | 6877.3159 | 60.8756 | 0 | 0 | 6877.3159 | 11186.9686 | 11247.8443
| 19968736 | 2029 | NHL015 | 6877.3159 | 60.8756 | 0 | 0 | 6877.3159 | 11186.9686 | 11247.8443
| 19968736 | 2030 | NHL015 | 6877.3159 | 60.8756 | 0 | 0 | 6877.3159 | 11186.9686 | 11247.8443
| 19968736 | 2031 | NHL015 | 6877.3159 | 60.8756 | 0 | 0 | 6877.3159 | 11186.9686 | 11247.8443
| 19968736 | 2032 | NHL015 | 6877.3159 | 60.8756 | 0 | 0 | 6877.3159 | 11186.9686 | 11247.8443
| 19968736 | 2033 | NHL015 | 6877.3159 | 60.8756 | 0 | 0 | 6877.3159 | 11186.9686 | 11247.8443
| 19968736 | 2034 | NHL015 | 6877.3159 | 60.8756 | 0 | 0 | 6877.3159 | 11186.9686 | 11247.8443
| 19969040 | 2023 | NHL015 | 0 | 0 | 0 | 0 | 0 | 5031.9919 | 5031.9919
| 19969040 | 2024 | NHL015 | 0 | 0 | 0 | 0 | 0 | 5031.9919 | 5031.9919
| 19969040 | 2025 | NHL015 | 0 | 0 | 0 | 0 | 0 | 5031.9919 | 5031.9919
| 19969040 | 2026 | NHL015 | 13.6009 | 0.028211 | 0 | 0 | 13.6009 | 5031.9919 | 5032.0201
| 19969040 | 2027 | NHL015 | 13.6009 | 0.028211 | 0 | 0 | 13.6009 | 5031.9919 | 5032.0201
| 19969040 | 2028 | NHL015 | 13.6009 | 0.028211 | 0 | 0 | 13.6009 | 5031.9919 | 5032.0201
| 19969040 | 2029 | NHL015 | 13.6009 | 0.028211 | 0 | 0 | 13.6009 | 5031.9919 | 5032.0201
| 19969040 | 2030 | NHL015 | 13.6009 | 0.028211 | 0 | 0 | 13.6009 | 5031.9919 | 5032.0201
| 19969040 | 2031 | NHL015 | 13.6009 | 0.028211 | 0 | 0 | 13.6009 | 5031.9919 | 5032.0201
| 19969040 | 2032 | NHL015 | 13.6009 | 0.028211 | 0 | 0 | 13.6009 | 5031.9919 | 5032.0201
| 19969040 | 2033 | NHL015 | 13.6009 | 0.028211 | 0 | 0 | 13.6009 | 5031.9919 | 5032.0201
| 19969040 | 2034 | NHL015 | 13.6009 | 0.028211 | 0 | 0 | 13.6009 | 5031.9919 | 5032.0201
| 19980785 | 2023 | NHL015 | 27.2341 | 0 | 0 | 0 | 27.2341 | 23774.4104 | 23774.4104
| 19980785 | 2024 | NHL015 | 34.3914 | 1.6754 | 0 | 0 | 34.3914 | 23774.4104 | 23776.0859
| 19980785 | 2025 | NHL015 | 17.9718 | 0.60824 | 0 | 0 | 17.9718 | 23774.4104 | 23775.0187
| 19980785 | 2026 | NHL015 | 14.386 | 0.49621 | 0 | 0 | 14.386 | 23774.4104 | 23774.9067
| 19980785 | 2027 | NHL015 | 14.386 | 0.49621 | 0 | 0 | 14.386 | 23774.4104 | 23774.9067
| 19980785 | 2028 | NHL015 | 14.386 | 0.49621 | 0 | 0 | 14.386 | 23774.4104 | 23774.9067
| 19980785 | 2029 | NHL015 | 14.386 | 0.49621 | 0 | 0 | 14.386 | 23774.4104 | 23774.9067
| 19980785 | 2030 | NHL015 | 14.386 | 0.49621 | 0 | 0 | 14.386 | 23774.4104 | 23774.9067
| 19980785 | 2031 | NHL015 | 14.386 | 0.49621 | 0 | 0 | 14.386 | 23774.4104 | 23774.9067
| 19980785 | 2032 | NHL015 | 14.386 | 0.49621 | 0 | 0 | 14.386 | 23774.4104 | 23774.9067
| 19980785 | 2033 | NHL015 | 14.386 | 0.49621 | 0 | 0 | 14.386 | 23774.4104 | 23774.9067
| 19980785 | 2034 | NHL015 | 14.386 | 0.49621 | 0 | 0 | 14.386 | 23774.4104 | 23774.9067
| 20649789 | 2023 | NHL015 | 0 | 0 | 0 | 0 | 0 | 11389.7528 | 11389.7528
| 20649789 | 2024 | NHL015 | 0 | 0 | 0 | 0 | 0 | 11389.7528 | 11389.7528
| 20649789 | 2025 | NHL015 | 0 | 0 | 0 | 0 | 0 | 11389.7528 | 11389.7528
| 20649789 | 2026 | NHL015 | 0 | 0 | 0 | 0 | 0 | 11389.7528 | 11389.7528
| 20649789 | 2027 | NHL015 | 0 | 0 | 0 | 0 | 0 | 11389.7528 | 11389.7528
| 20649789 | 2028 | NHL015 | 0 | 0 | 0 | 0 | 0 | 11389.7528 | 11389.7528
| 20649789 | 2029 | NHL015 | 0 | 0 | 0 | 0 | 0 | 11389.7528 | 11389.7528
| 20649789 | 2030 | NHL015 | 0 | 0 | 0 | 0 | 0 | 11389.7528 | 11389.7528
| 20649789 | 2031 | NHL015 | 0 | 0 | 0 | 0 | 0 | 11389.7528 | 11389.7528
| 20649789 | 2032 | NHL015 | 0 | 0 | 0 | 0 | 0 | 11389.7528 | 11389.7528
| 20649789 | 2033 | NHL015 | 0 | 0 | 0 | 0 | 0 | 11389.7528 | 11389.7528
| 20649789 | 2034 | NHL015 | 0 | 0 | 0 | 0 | 0 | 11389.7528 | 11389.7528
| 40400939 | 2023 | NHL015 | 4929.1216 | 0 | 0 | 0 | 4929.1216 | 20744.0719 | 20744.0719
| 40400939 | 2024 | NHL015 | 7349.5442 | 208.2038 | 0 | 0 | 7349.5442 | 20744.0719 | 20952.2757
| 40400939 | 2025 | NHL015 | 7556.7865 | 254.8692 | 0 | 0 | 7556.7865 | 20744.0719 | 20998.9411
| 40400939 | 2026 | NHL015 | 10695.089 | 258.4643 | 0 | 0 | 10695.089 | 20744.0719 | 21002.5362
| 40400939 | 2027 | NHL015 | 10695.089 | 258.4643 | 0 | 0 | 10695.089 | 20744.0719 | 21002.5362
| 40400939 | 2028 | NHL015 | 10695.089 | 258.4643 | 0 | 0 | 10695.089 | 20744.0719 | 21002.5362
| 40400939 | 2029 | NHL015 | 10695.089 | 258.4643 | 0 | 0 | 10695.089 | 20744.0719 | 21002.5362
| 40400939 | 2030 | NHL015 | 10695.089 | 258.4643 | 0 | 0 | 10695.089 | 20744.0719 | 21002.5362
| 40400939 | 2031 | NHL015 | 10695.089 | 258.4643 | 0 | 0 | 10695.089 | 20744.0719 | 21002.5362
| 40400939 | 2032 | NHL015 | 10695.089 | 258.4643 | 0 | 0 | 10695.089 | 20744.0719 | 21002.5362
| 40400939 | 2033 | NHL015 | 10695.089 | 258.4643 | 0 | 0 | 10695.089 | 20744.0719 | 21002.5362
| 40400939 | 2034 | NHL015 | 10695.089 | 258.4643 | 0 | 0 | 10695.089 | 20744.0719 | 21002.5362
| 41527585 | 2023 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2284.7188 | 2284.7188
| 41527585 | 2024 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2284.7188 | 2284.7188
| 41527585 | 2025 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2284.7188 | 2284.7188
| 41527585 | 2026 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2284.7188 | 2284.7188
| 41527585 | 2027 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2284.7188 | 2284.7188
| 41527585 | 2028 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2284.7188 | 2284.7188
| 41527585 | 2029 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2284.7188 | 2284.7188
| 41527585 | 2030 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2284.7188 | 2284.7188
| 41527585 | 2031 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2284.7188 | 2284.7188
| 41527585 | 2032 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2284.7188 | 2284.7188
| 41527585 | 2033 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2284.7188 | 2284.7188
| 41527585 | 2034 | NHL015 | 0 | 0 | 0 | 0 | 0 | 2284.7188 | 2284.7188
| 52509148 | 2023 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16940.3467 | 16940.3467
| 52509148 | 2024 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16940.3467 | 16940.3467
| 52509148 | 2025 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16940.3467 | 16940.3467
| 52509148 | 2026 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16940.3467 | 16940.3467
| 52509148 | 2027 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16940.3467 | 16940.3467
| 52509148 | 2028 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16940.3467 | 16940.3467
| 52509148 | 2029 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16940.3467 | 16940.3467
| 52509148 | 2030 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16940.3467 | 16940.3467
| 52509148 | 2031 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16940.3467 | 16940.3467
| 52509148 | 2032 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16940.3467 | 16940.3467
| 52509148 | 2033 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16940.3467 | 16940.3467
| 52509148 | 2034 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16940.3467 | 16940.3467
| 72848118 | 2023 | NHL015 | 0 | 0 | 0 | 0 | 0 | 6868.6582 | 6868.6582
| 72848118 | 2024 | NHL015 | 0 | 0 | 0 | 0 | 0 | 6868.6582 | 6868.6582
| 72848118 | 2025 | NHL015 | 0 | 0 | 0 | 0 | 0 | 6868.6582 | 6868.6582
| 72848118 | 2026 | NHL015 | 0 | 0 | 0 | 0 | 0 | 6868.6582 | 6868.6582
| 72848118 | 2027 | NHL015 | 0 | 0 | 0 | 0 | 0 | 6868.6582 | 6868.6582
| 72848118 | 2028 | NHL015 | 0 | 0 | 0 | 0 | 0 | 6868.6582 | 6868.6582
| 72848118 | 2029 | NHL015 | 0 | 0 | 0 | 0 | 0 | 6868.6582 | 6868.6582
| 72848118 | 2030 | NHL015 | 0 | 0 | 0 | 0 | 0 | 6868.6582 | 6868.6582
| 72848118 | 2031 | NHL015 | 0 | 0 | 0 | 0 | 0 | 6868.6582 | 6868.6582
| 72848118 | 2032 | NHL015 | 0 | 0 | 0 | 0 | 0 | 6868.6582 | 6868.6582
| 72848118 | 2033 | NHL015 | 0 | 0 | 0 | 0 | 0 | 6868.6582 | 6868.6582
| 72848118 | 2034 | NHL015 | 0 | 0 | 0 | 0 | 0 | 6868.6582 | 6868.6582
| 154154915 | 2023 | NHL015 | 2565.2848 | 0 | 170.7384 | 7595.4376 | 2736.0232 | 9611.5941 | 17207.0317
| 154154915 | 2024 | NHL015 | 2549.9967 | 67.1589 | 201.9792 | 8985.207 | 2751.9759 | 9611.5941 | 18663.96
| 154154915 | 2025 | NHL015 | 2445.5627 | 75.2347 | 164.6214 | 7323.3142 | 2610.1841 | 9611.5941 | 17010.143
| 154154915 | 2026 | NHL015 | 2394.6871 | 50.6428 | 134.9046 | 6001.3402 | 2529.5917 | 9611.5941 | 15663.5771
| 154154915 | 2027 | NHL015 | 2394.6871 | 50.6428 | 134.9046 | 6001.3402 | 2529.5917 | 9611.5941 | 15663.5771
| 154154915 | 2028 | NHL015 | 2394.6871 | 50.6428 | 134.9046 | 6001.3402 | 2529.5917 | 9611.5941 | 15663.5771
| 154154915 | 2029 | NHL015 | 2394.6871 | 50.6428 | 134.9046 | 6001.3402 | 2529.5917 | 9611.5941 | 15663.5771
| 154154915 | 2030 | NHL015 | 2394.6871 | 50.6428 | 134.9046 | 6001.3402 | 2529.5917 | 9611.5941 | 15663.5771
| 154154915 | 2031 | NHL015 | 2394.6871 | 50.6428 | 134.9046 | 6001.3402 | 2529.5917 | 9611.5941 | 15663.5771
| 154154915 | 2032 | NHL015 | 2394.6871 | 50.6428 | 134.9046 | 6001.3402 | 2529.5917 | 9611.5941 | 15663.5771
| 154154915 | 2033 | NHL015 | 2394.6871 | 50.6428 | 134.9046 | 6001.3402 | 2529.5917 | 9611.5941 | 15663.5771
| 154154915 | 2034 | NHL015 | 2394.6871 | 50.6428 | 134.9046 | 6001.3402 | 2529.5917 | 9611.5941 | 15663.5771
| 158071754 | 2023 | NHL015 | 886.7777 | 0 | 0 | 0 | 886.7777 | 23116.124 | 23116.124
| 158071754 | 2024 | NHL015 | 1528.2761 | 48.1988 | 0 | 0 | 1528.2761 | 23116.124 | 23164.3227
| 158071754 | 2025 | NHL015 | 1491.1221 | 51.711 | 0 | 0 | 1491.1221 | 23116.124 | 23167.835
| 158071754 | 2026 | NHL015 | 2422.2299 | 55.3285 | 0 | 0 | 2422.2299 | 23116.124 | 23171.4525
| 158071754 | 2027 | NHL015 | 2422.2299 | 55.3285 | 0 | 0 | 2422.2299 | 23116.124 | 23171.4525
| 158071754 | 2028 | NHL015 | 2422.2299 | 55.3285 | 0 | 0 | 2422.2299 | 23116.124 | 23171.4525
| 158071754 | 2029 | NHL015 | 2422.2299 | 55.3285 | 0 | 0 | 2422.2299 | 23116.124 | 23171.4525
| 158071754 | 2030 | NHL015 | 2422.2299 | 55.3285 | 0 | 0 | 2422.2299 | 23116.124 | 23171.4525
| 158071754 | 2031 | NHL015 | 2422.2299 | 55.3285 | 0 | 0 | 2422.2299 | 23116.124 | 23171.4525
| 158071754 | 2032 | NHL015 | 2422.2299 | 55.3285 | 0 | 0 | 2422.2299 | 23116.124 | 23171.4525
| 158071754 | 2033 | NHL015 | 2422.2299 | 55.3285 | 0 | 0 | 2422.2299 | 23116.124 | 23171.4525
| 158071754 | 2034 | NHL015 | 2422.2299 | 55.3285 | 0 | 0 | 2422.2299 | 23116.124 | 23171.4525
| 182422326 | 2023 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16532.8708 | 16532.8708
| 182422326 | 2024 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16532.8708 | 16532.8708
| 182422326 | 2025 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16532.8708 | 16532.8708
| 182422326 | 2026 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16532.8708 | 16532.8708
| 182422326 | 2027 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16532.8708 | 16532.8708
| 182422326 | 2028 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16532.8708 | 16532.8708
| 182422326 | 2029 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16532.8708 | 16532.8708
| 182422326 | 2030 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16532.8708 | 16532.8708
| 182422326 | 2031 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16532.8708 | 16532.8708
| 182422326 | 2032 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16532.8708 | 16532.8708
| 182422326 | 2033 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16532.8708 | 16532.8708
| 182422326 | 2034 | NHL015 | 0 | 0 | 0 | 0 | 0 | 16532.8708 | 16532.8708
| 200847925 | 2023 | NHL015 | 0 | 0 | 0 | 0 | 0 | 25576.6146 | 25576.6146
| 200847925 | 2024 | NHL015 | 0 | 0 | 0 | 0 | 0 | 25576.6146 | 25576.6146
| 200847925 | 2025 | NHL015 | 0 | 0 | 0 | 0 | 0 | 25576.6146 | 25576.6146
| 200847925 | 2026 | NHL015 | 8.8513 | 0.020447 | 0 | 0 | 8.8513 | 25576.6146 | 25576.635
| 200847925 | 2027 | NHL015 | 8.8513 | 0.020447 | 0 | 0 | 8.8513 | 25576.6146 | 25576.635
| 200847925 | 2028 | NHL015 | 8.8513 | 0.020447 | 0 | 0 | 8.8513 | 25576.6146 | 25576.635
| 200847925 | 2029 | NHL015 | 8.8513 | 0.020447 | 0 | 0 | 8.8513 | 25576.6146 | 25576.635
| 200847925 | 2030 | NHL015 | 8.8513 | 0.020447 | 0 | 0 | 8.8513 | 25576.6146 | 25576.635
| 200847925 | 2031 | NHL015 | 8.8513 | 0.020447 | 0 | 0 | 8.8513 | 25576.6146 | 25576.635
| 200847925 | 2032 | NHL015 | 8.8513 | 0.020447 | 0 | 0 | 8.8513 | 25576.6146 | 25576.635
| 200847925 | 2033 | NHL015 | 8.8513 | 0.020447 | 0 | 0 | 8.8513 | 25576.6146 | 25576.635
| 200847925 | 2034 | NHL015 | 8.8513 | 0.020447 | 0 | 0 | 8.8513 | 25576.6146 | 25576.635
| 19950898 | 2023 | NHL016 | 0 | 0 | 0.0073537 | 0.32713 | 0.0073537 | 5547.5568 | 5547.8839
| 19950898 | 2024 | NHL016 | 0 | 0 | 0.0087429 | 0.38894 | 0.0087429 | 5547.5568 | 5547.9457
| 19950898 | 2025 | NHL016 | 0 | 0 | 0.0087429 | 0.38894 | 0.0087429 | 5547.5568 | 5547.9457
| 19950898 | 2026 | NHL016 | 0 | 0 | 0.0087429 | 0.38894 | 0.0087429 | 5547.5568 | 5547.9457
| 19950898 | 2027 | NHL016 | 0 | 0 | 0.0087429 | 0.38894 | 0.0087429 | 5547.5568 | 5547.9457
| 19950898 | 2028 | NHL016 | 0 | 0 | 0.0087429 | 0.38894 | 0.0087429 | 5547.5568 | 5547.9457
| 19950898 | 2029 | NHL016 | 0 | 0 | 0.0087429 | 0.38894 | 0.0087429 | 5547.5568 | 5547.9457
| 19950898 | 2030 | NHL016 | 0 | 0 | 0.0087429 | 0.38894 | 0.0087429 | 5547.5568 | 5547.9457
| 19950898 | 2031 | NHL016 | 0 | 0 | 0.0087429 | 0.38894 | 0.0087429 | 5547.5568 | 5547.9457
| 19950898 | 2032 | NHL016 | 0 | 0 | 0.0087429 | 0.38894 | 0.0087429 | 5547.5568 | 5547.9457
| 19950898 | 2033 | NHL016 | 0 | 0 | 0.0087429 | 0.38894 | 0.0087429 | 5547.5568 | 5547.9457
| 19950898 | 2034 | NHL016 | 0 | 0 | 0.0087429 | 0.38894 | 0.0087429 | 5547.5568 | 5547.9457
| 19951396 | 2023 | NHL016 | 0 | 0 | 0 | 0 | 0 | 8394.7434 | 8394.7434
| 19951396 | 2024 | NHL016 | 0 | 0 | 0 | 0 | 0 | 8394.7434 | 8394.7434
| 19951396 | 2025 | NHL016 | 0 | 0 | 0 | 0 | 0 | 8394.7434 | 8394.7434
| 19951396 | 2026 | NHL016 | 0 | 0 | 0 | 0 | 0 | 8394.7434 | 8394.7434
| 19951396 | 2027 | NHL016 | 0 | 0 | 0 | 0 | 0 | 8394.7434 | 8394.7434
| 19951396 | 2028 | NHL016 | 0 | 0 | 0 | 0 | 0 | 8394.7434 | 8394.7434
| 19951396 | 2029 | NHL016 | 0 | 0 | 0 | 0 | 0 | 8394.7434 | 8394.7434
| 19951396 | 2030 | NHL016 | 0 | 0 | 0 | 0 | 0 | 8394.7434 | 8394.7434
| 19951396 | 2031 | NHL016 | 0 | 0 | 0 | 0 | 0 | 8394.7434 | 8394.7434
| 19951396 | 2032 | NHL016 | 0 | 0 | 0 | 0 | 0 | 8394.7434 | 8394.7434
| 19951396 | 2033 | NHL016 | 0 | 0 | 0 | 0 | 0 | 8394.7434 | 8394.7434
| 19951396 | 2034 | NHL016 | 0 | 0 | 0 | 0 | 0 | 8394.7434 | 8394.7434
| 19952436 | 2023 | NHL016 | 0 | 0 | 0 | 0 | 0 | 5225.7644 | 5225.7644
| 19952436 | 2024 | NHL016 | 0 | 0 | 0 | 0 | 0 | 5225.7644 | 5225.7644
| 19952436 | 2025 | NHL016 | 0 | 0 | 0 | 0 | 0 | 5225.7644 | 5225.7644
| 19952436 | 2026 | NHL016 | 0 | 0 | 0 | 0 | 0 | 5225.7644 | 5225.7644
| 19952436 | 2027 | NHL016 | 0 | 0 | 0 | 0 | 0 | 5225.7644 | 5225.7644
| 19952436 | 2028 | NHL016 | 0 | 0 | 0 | 0 | 0 | 5225.7644 | 5225.7644
| 19952436 | 2029 | NHL016 | 0 | 0 | 0 | 0 | 0 | 5225.7644 | 5225.7644
| 19952436 | 2030 | NHL016 | 0 | 0 | 0 | 0 | 0 | 5225.7644 | 5225.7644
| 19952436 | 2031 | NHL016 | 0 | 0 | 0 | 0 | 0 | 5225.7644 | 5225.7644
| 19952436 | 2032 | NHL016 | 0 | 0 | 0 | 0 | 0 | 5225.7644 | 5225.7644
| 19952436 | 2033 | NHL016 | 0 | 0 | 0 | 0 | 0 | 5225.7644 | 5225.7644
| 19952436 | 2034 | NHL016 | 0 | 0 | 0 | 0 | 0 | 5225.7644 | 5225.7644
| 19965083 | 2023 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2941.904 | 2941.904
| 19965083 | 2024 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2941.904 | 2941.904
| 19965083 | 2025 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2941.904 | 2941.904
| 19965083 | 2026 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2941.904 | 2941.904
| 19965083 | 2027 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2941.904 | 2941.904
| 19965083 | 2028 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2941.904 | 2941.904
| 19965083 | 2029 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2941.904 | 2941.904
| 19965083 | 2030 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2941.904 | 2941.904
| 19965083 | 2031 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2941.904 | 2941.904
| 19965083 | 2032 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2941.904 | 2941.904
| 19965083 | 2033 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2941.904 | 2941.904
| 19965083 | 2034 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2941.904 | 2941.904
| 19968436 | 2023 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2032.4376 | 2032.4376
| 19968436 | 2024 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2032.4376 | 2032.4376
| 19968436 | 2025 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2032.4376 | 2032.4376
| 19968436 | 2026 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2032.4376 | 2032.4376
| 19968436 | 2027 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2032.4376 | 2032.4376
| 19968436 | 2028 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2032.4376 | 2032.4376
| 19968436 | 2029 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2032.4376 | 2032.4376
| 19968436 | 2030 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2032.4376 | 2032.4376
| 19968436 | 2031 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2032.4376 | 2032.4376
| 19968436 | 2032 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2032.4376 | 2032.4376
| 19968436 | 2033 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2032.4376 | 2032.4376
| 19968436 | 2034 | NHL016 | 0 | 0 | 0 | 0 | 0 | 2032.4376 | 2032.4376
| 20541660 | 2023 | NHL016 | 0 | 0 | 12105.0662 | 538503.6598 | 12105.0662 | 10543.011 | 549046.6709
| 20541660 | 2024 | NHL016 | 0 | 0 | 15159.7459 | 674393.5555 | 15159.7459 | 10543.011 | 684936.5665
| 20541660 | 2025 | NHL016 | 0 | 0 | 15159.7459 | 674393.5555 | 15159.7459 | 10543.011 | 684936.5665
| 20541660 | 2026 | NHL016 | 0 | 0 | 15159.7459 | 674393.5555 | 15159.7459 | 10543.011 | 684936.5665
| 20541660 | 2027 | NHL016 | 0 | 0 | 15159.7459 | 674393.5555 | 15159.7459 | 10543.011 | 684936.5665
| 20541660 | 2028 | NHL016 | 0 | 0 | 15159.7459 | 674393.5555 | 15159.7459 | 10543.011 | 684936.5665
| 20541660 | 2029 | NHL016 | 0 | 0 | 15159.7459 | 674393.5555 | 15159.7459 | 10543.011 | 684936.5665
| 20541660 | 2030 | NHL016 | 0 | 0 | 15159.7459 | 674393.5555 | 15159.7459 | 10543.011 | 684936.5665
| 20541660 | 2031 | NHL016 | 0 | 0 | 15159.7459 | 674393.5555 | 15159.7459 | 10543.011 | 684936.5665
| 20541660 | 2032 | NHL016 | 0 | 0 | 15159.7459 | 674393.5555 | 15159.7459 | 10543.011 | 684936.5665
| 20541660 | 2033 | NHL016 | 0 | 0 | 15159.7459 | 674393.5555 | 15159.7459 | 10543.011 | 684936.5665
| 20541660 | 2034 | NHL016 | 0 | 0 | 15159.7459 | 674393.5555 | 15159.7459 | 10543.011 | 684936.5665
| 157328687 | 2023 | NHL016 | 0 | 0 | 266.6841 | 11863.6565 | 266.6841 | 5558.5518 | 17422.2083
| 157328687 | 2024 | NHL016 | 0 | 0 | 222.0175 | 9876.6274 | 222.0175 | 5558.5518 | 15435.1792
| 157328687 | 2025 | NHL016 | 0 | 0 | 222.0175 | 9876.6274 | 222.0175 | 5558.5518 | 15435.1792
| 157328687 | 2026 | NHL016 | 0 | 0 | 222.0175 | 9876.6274 | 222.0175 | 5558.5518 | 15435.1792
| 157328687 | 2027 | NHL016 | 0 | 0 | 222.0175 | 9876.6274 | 222.0175 | 5558.5518 | 15435.1792
| 157328687 | 2028 | NHL016 | 0 | 0 | 222.0175 | 9876.6274 | 222.0175 | 5558.5518 | 15435.1792
| 157328687 | 2029 | NHL016 | 0 | 0 | 222.0175 | 9876.6274 | 222.0175 | 5558.5518 | 15435.1792
| 157328687 | 2030 | NHL016 | 0 | 0 | 222.0175 | 9876.6274 | 222.0175 | 5558.5518 | 15435.1792
| 157328687 | 2031 | NHL016 | 0 | 0 | 222.0175 | 9876.6274 | 222.0175 | 5558.5518 | 15435.1792
| 157328687 | 2032 | NHL016 | 0 | 0 | 222.0175 | 9876.6274 | 222.0175 | 5558.5518 | 15435.1792
| 157328687 | 2033 | NHL016 | 0 | 0 | 222.0175 | 9876.6274 | 222.0175 | 5558.5518 | 15435.1792
| 157328687 | 2034 | NHL016 | 0 | 0 | 222.0175 | 9876.6274 | 222.0175 | 5558.5518 | 15435.1792
| 163161294 | 2023 | NHL016 | 0 | 0 | 21.7139 | 965.9616 | 21.7139 | 4782.951 | 5748.9125
| 163161294 | 2024 | NHL016 | 0 | 0 | 21.3293 | 948.8499 | 21.3293 | 4782.951 | 5731.8009
| 163161294 | 2025 | NHL016 | 0 | 0 | 21.3293 | 948.8499 | 21.3293 | 4782.951 | 5731.8009
| 163161294 | 2026 | NHL016 | 0 | 0 | 21.3293 | 948.8499 | 21.3293 | 4782.951 | 5731.8009
| 163161294 | 2027 | NHL016 | 0 | 0 | 21.3293 | 948.8499 | 21.3293 | 4782.951 | 5731.8009
| 163161294 | 2028 | NHL016 | 0 | 0 | 21.3293 | 948.8499 | 21.3293 | 4782.951 | 5731.8009
| 163161294 | 2029 | NHL016 | 0 | 0 | 21.3293 | 948.8499 | 21.3293 | 4782.951 | 5731.8009
| 163161294 | 2030 | NHL016 | 0 | 0 | 21.3293 | 948.8499 | 21.3293 | 4782.951 | 5731.8009
| 163161294 | 2031 | NHL016 | 0 | 0 | 21.3293 | 948.8499 | 21.3293 | 4782.951 | 5731.8009
| 163161294 | 2032 | NHL016 | 0 | 0 | 21.3293 | 948.8499 | 21.3293 | 4782.951 | 5731.8009
| 163161294 | 2033 | NHL016 | 0 | 0 | 21.3293 | 948.8499 | 21.3293 | 4782.951 | 5731.8009
| 163161294 | 2034 | NHL016 | 0 | 0 | 21.3293 | 948.8499 | 21.3293 | 4782.951 | 5731.8009
| 19945139 | 2023 | NHL031 | 0 | 0 | 3479.5824 | 154792.0386 | 3479.5824 | 13469.9165 | 168261.9551
| 19945139 | 2024 | NHL031 | 0 | 0 | 3479.5824 | 154792.0386 | 3479.5824 | 13469.9165 | 168261.9551
| 19945139 | 2025 | NHL031 | 0 | 0 | 3479.5824 | 154792.0386 | 3479.5824 | 13469.9165 | 168261.9551
| 19945139 | 2026 | NHL031 | 0 | 0 | 3479.5824 | 154792.0386 | 3479.5824 | 13469.9165 | 168261.9551
| 19945139 | 2027 | NHL031 | 0 | 0 | 3479.5824 | 154792.0386 | 3479.5824 | 13469.9165 | 168261.9551
| 19945139 | 2028 | NHL031 | 0 | 0 | 3479.5824 | 154792.0386 | 3479.5824 | 13469.9165 | 168261.9551
| 19945139 | 2029 | NHL031 | 0 | 0 | 3479.5824 | 154792.0386 | 3479.5824 | 13469.9165 | 168261.9551
| 19945139 | 2030 | NHL031 | 0 | 0 | 3479.5824 | 154792.0386 | 3479.5824 | 13469.9165 | 168261.9551
| 19945139 | 2031 | NHL031 | 0 | 0 | 3479.5824 | 154792.0386 | 3479.5824 | 13469.9165 | 168261.9551
| 19945139 | 2032 | NHL031 | 0 | 0 | 3479.5824 | 154792.0386 | 3479.5824 | 13469.9165 | 168261.9551
| 19945139 | 2033 | NHL031 | 0 | 0 | 3479.5824 | 154792.0386 | 3479.5824 | 13469.9165 | 168261.9551
| 19945139 | 2034 | NHL031 | 0 | 0 | 3479.5824 | 154792.0386 | 3479.5824 | 13469.9165 | 168261.9551
| 19945509 | 2023 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7854.0618 | 7854.0618
| 19945509 | 2024 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7854.0618 | 7854.0618
| 19945509 | 2025 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7854.0618 | 7854.0618
| 19945509 | 2026 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7854.0618 | 7854.0618
| 19945509 | 2027 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7854.0618 | 7854.0618
| 19945509 | 2028 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7854.0618 | 7854.0618
| 19945509 | 2029 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7854.0618 | 7854.0618
| 19945509 | 2030 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7854.0618 | 7854.0618
| 19945509 | 2031 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7854.0618 | 7854.0618
| 19945509 | 2032 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7854.0618 | 7854.0618
| 19945509 | 2033 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7854.0618 | 7854.0618
| 19945509 | 2034 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7854.0618 | 7854.0618
| 19947904 | 2023 | NHL031 | 0 | 0 | 0 | 0 | 0 | 1240.4824 | 1240.4824
| 19947904 | 2024 | NHL031 | 0 | 0 | 0 | 0 | 0 | 1240.4824 | 1240.4824
| 19947904 | 2025 | NHL031 | 0 | 0 | 0 | 0 | 0 | 1240.4824 | 1240.4824
| 19947904 | 2026 | NHL031 | 0 | 0 | 0 | 0 | 0 | 1240.4824 | 1240.4824
| 19947904 | 2027 | NHL031 | 0 | 0 | 0 | 0 | 0 | 1240.4824 | 1240.4824
| 19947904 | 2028 | NHL031 | 0 | 0 | 0 | 0 | 0 | 1240.4824 | 1240.4824
| 19947904 | 2029 | NHL031 | 0 | 0 | 0 | 0 | 0 | 1240.4824 | 1240.4824
| 19947904 | 2030 | NHL031 | 0 | 0 | 0 | 0 | 0 | 1240.4824 | 1240.4824
| 19947904 | 2031 | NHL031 | 0 | 0 | 0 | 0 | 0 | 1240.4824 | 1240.4824
| 19947904 | 2032 | NHL031 | 0 | 0 | 0 | 0 | 0 | 1240.4824 | 1240.4824
| 19947904 | 2033 | NHL031 | 0 | 0 | 0 | 0 | 0 | 1240.4824 | 1240.4824
| 19947904 | 2034 | NHL031 | 0 | 0 | 0 | 0 | 0 | 1240.4824 | 1240.4824
| 19948545 | 2023 | NHL031 | 0 | 0 | 0.24812 | 11.038 | 0.24812 | 4448.9703 | 4460.0083
| 19948545 | 2024 | NHL031 | 0 | 0 | 0.24812 | 11.038 | 0.24812 | 4448.9703 | 4460.0083
| 19948545 | 2025 | NHL031 | 0 | 0 | 0.24812 | 11.038 | 0.24812 | 4448.9703 | 4460.0083
| 19948545 | 2026 | NHL031 | 0 | 0 | 0.24812 | 11.038 | 0.24812 | 4448.9703 | 4460.0083
| 19948545 | 2027 | NHL031 | 0 | 0 | 0.24812 | 11.038 | 0.24812 | 4448.9703 | 4460.0083
| 19948545 | 2028 | NHL031 | 0 | 0 | 0.24812 | 11.038 | 0.24812 | 4448.9703 | 4460.0083
| 19948545 | 2029 | NHL031 | 0 | 0 | 0.24812 | 11.038 | 0.24812 | 4448.9703 | 4460.0083
| 19948545 | 2030 | NHL031 | 0 | 0 | 0.24812 | 11.038 | 0.24812 | 4448.9703 | 4460.0083
| 19948545 | 2031 | NHL031 | 0 | 0 | 0.24812 | 11.038 | 0.24812 | 4448.9703 | 4460.0083
| 19948545 | 2032 | NHL031 | 0 | 0 | 0.24812 | 11.038 | 0.24812 | 4448.9703 | 4460.0083
| 19948545 | 2033 | NHL031 | 0 | 0 | 0.24812 | 11.038 | 0.24812 | 4448.9703 | 4460.0083
| 19948545 | 2034 | NHL031 | 0 | 0 | 0.24812 | 11.038 | 0.24812 | 4448.9703 | 4460.0083
| 19950704 | 2023 | NHL031 | 0 | 0 | 0 | 0 | 0 | 8639.4701 | 8639.4701
| 19950704 | 2024 | NHL031 | 0 | 0 | 0 | 0 | 0 | 8639.4701 | 8639.4701
| 19950704 | 2025 | NHL031 | 0 | 0 | 0 | 0 | 0 | 8639.4701 | 8639.4701
| 19950704 | 2026 | NHL031 | 0 | 0 | 0 | 0 | 0 | 8639.4701 | 8639.4701
| 19950704 | 2027 | NHL031 | 0 | 0 | 0 | 0 | 0 | 8639.4701 | 8639.4701
| 19950704 | 2028 | NHL031 | 0 | 0 | 0 | 0 | 0 | 8639.4701 | 8639.4701
| 19950704 | 2029 | NHL031 | 0 | 0 | 0 | 0 | 0 | 8639.4701 | 8639.4701
| 19950704 | 2030 | NHL031 | 0 | 0 | 0 | 0 | 0 | 8639.4701 | 8639.4701
| 19950704 | 2031 | NHL031 | 0 | 0 | 0 | 0 | 0 | 8639.4701 | 8639.4701
| 19950704 | 2032 | NHL031 | 0 | 0 | 0 | 0 | 0 | 8639.4701 | 8639.4701
| 19950704 | 2033 | NHL031 | 0 | 0 | 0 | 0 | 0 | 8639.4701 | 8639.4701
| 19950704 | 2034 | NHL031 | 0 | 0 | 0 | 0 | 0 | 8639.4701 | 8639.4701
| 19953282 | 2023 | NHL031 | 0 | 0 | 0 | 0 | 0 | 4636.3316 | 4636.3316
| 19953282 | 2024 | NHL031 | 0 | 0 | 0 | 0 | 0 | 4636.3316 | 4636.3316
| 19953282 | 2025 | NHL031 | 0 | 0 | 0 | 0 | 0 | 4636.3316 | 4636.3316
| 19953282 | 2026 | NHL031 | 0 | 0 | 0 | 0 | 0 | 4636.3316 | 4636.3316
| 19953282 | 2027 | NHL031 | 0 | 0 | 0 | 0 | 0 | 4636.3316 | 4636.3316
| 19953282 | 2028 | NHL031 | 0 | 0 | 0 | 0 | 0 | 4636.3316 | 4636.3316
| 19953282 | 2029 | NHL031 | 0 | 0 | 0 | 0 | 0 | 4636.3316 | 4636.3316
| 19953282 | 2030 | NHL031 | 0 | 0 | 0 | 0 | 0 | 4636.3316 | 4636.3316
| 19953282 | 2031 | NHL031 | 0 | 0 | 0 | 0 | 0 | 4636.3316 | 4636.3316
| 19953282 | 2032 | NHL031 | 0 | 0 | 0 | 0 | 0 | 4636.3316 | 4636.3316
| 19953282 | 2033 | NHL031 | 0 | 0 | 0 | 0 | 0 | 4636.3316 | 4636.3316
| 19953282 | 2034 | NHL031 | 0 | 0 | 0 | 0 | 0 | 4636.3316 | 4636.3316
| 19953868 | 2023 | NHL031 | 0 | 0 | 0 | 0 | 0 | 13956.7387 | 13956.7387
| 19953868 | 2024 | NHL031 | 0 | 0 | 0 | 0 | 0 | 13956.7387 | 13956.7387
| 19953868 | 2025 | NHL031 | 0 | 0 | 0 | 0 | 0 | 13956.7387 | 13956.7387
| 19953868 | 2026 | NHL031 | 0 | 0 | 0 | 0 | 0 | 13956.7387 | 13956.7387
| 19953868 | 2027 | NHL031 | 0 | 0 | 0 | 0 | 0 | 13956.7387 | 13956.7387
| 19953868 | 2028 | NHL031 | 0 | 0 | 0 | 0 | 0 | 13956.7387 | 13956.7387
| 19953868 | 2029 | NHL031 | 0 | 0 | 0 | 0 | 0 | 13956.7387 | 13956.7387
| 19953868 | 2030 | NHL031 | 0 | 0 | 0 | 0 | 0 | 13956.7387 | 13956.7387
| 19953868 | 2031 | NHL031 | 0 | 0 | 0 | 0 | 0 | 13956.7387 | 13956.7387
| 19953868 | 2032 | NHL031 | 0 | 0 | 0 | 0 | 0 | 13956.7387 | 13956.7387
| 19953868 | 2033 | NHL031 | 0 | 0 | 0 | 0 | 0 | 13956.7387 | 13956.7387
| 19953868 | 2034 | NHL031 | 0 | 0 | 0 | 0 | 0 | 13956.7387 | 13956.7387
| 19954227 | 2023 | NHL031 | 0 | 0 | 0 | 0 | 0 | 6035.3638 | 6035.3638
| 19954227 | 2024 | NHL031 | 0 | 0 | 0 | 0 | 0 | 6035.3638 | 6035.3638
| 19954227 | 2025 | NHL031 | 0 | 0 | 0 | 0 | 0 | 6035.3638 | 6035.3638
| 19954227 | 2026 | NHL031 | 0 | 0 | 0 | 0 | 0 | 6035.3638 | 6035.3638
| 19954227 | 2027 | NHL031 | 0 | 0 | 0 | 0 | 0 | 6035.3638 | 6035.3638
| 19954227 | 2028 | NHL031 | 0 | 0 | 0 | 0 | 0 | 6035.3638 | 6035.3638
| 19954227 | 2029 | NHL031 | 0 | 0 | 0 | 0 | 0 | 6035.3638 | 6035.3638
| 19954227 | 2030 | NHL031 | 0 | 0 | 0 | 0 | 0 | 6035.3638 | 6035.3638
| 19954227 | 2031 | NHL031 | 0 | 0 | 0 | 0 | 0 | 6035.3638 | 6035.3638
| 19954227 | 2032 | NHL031 | 0 | 0 | 0 | 0 | 0 | 6035.3638 | 6035.3638
| 19954227 | 2033 | NHL031 | 0 | 0 | 0 | 0 | 0 | 6035.3638 | 6035.3638
| 19954227 | 2034 | NHL031 | 0 | 0 | 0 | 0 | 0 | 6035.3638 | 6035.3638
| 19954278 | 2023 | NHL031 | 0 | 0 | 303.5944 | 13505.641 | 303.5944 | 5281.9727 | 18787.6137
| 19954278 | 2024 | NHL031 | 0 | 0 | 303.5944 | 13505.641 | 303.5944 | 5281.9727 | 18787.6137
| 19954278 | 2025 | NHL031 | 0 | 0 | 303.5944 | 13505.641 | 303.5944 | 5281.9727 | 18787.6137
| 19954278 | 2026 | NHL031 | 0 | 0 | 303.5944 | 13505.641 | 303.5944 | 5281.9727 | 18787.6137
| 19954278 | 2027 | NHL031 | 0 | 0 | 303.5944 | 13505.641 | 303.5944 | 5281.9727 | 18787.6137
| 19954278 | 2028 | NHL031 | 0 | 0 | 303.5944 | 13505.641 | 303.5944 | 5281.9727 | 18787.6137
| 19954278 | 2029 | NHL031 | 0 | 0 | 303.5944 | 13505.641 | 303.5944 | 5281.9727 | 18787.6137
| 19954278 | 2030 | NHL031 | 0 | 0 | 303.5944 | 13505.641 | 303.5944 | 5281.9727 | 18787.6137
| 19954278 | 2031 | NHL031 | 0 | 0 | 303.5944 | 13505.641 | 303.5944 | 5281.9727 | 18787.6137
| 19954278 | 2032 | NHL031 | 0 | 0 | 303.5944 | 13505.641 | 303.5944 | 5281.9727 | 18787.6137
| 19954278 | 2033 | NHL031 | 0 | 0 | 303.5944 | 13505.641 | 303.5944 | 5281.9727 | 18787.6137
| 19954278 | 2034 | NHL031 | 0 | 0 | 303.5944 | 13505.641 | 303.5944 | 5281.9727 | 18787.6137
| 19954417 | 2023 | NHL031 | 0 | 0 | 3042.7573 | 135359.521 | 3042.7573 | 10612.029 | 145971.55
| 19954417 | 2024 | NHL031 | 0 | 0 | 3042.7573 | 135359.521 | 3042.7573 | 10612.029 | 145971.55
| 19954417 | 2025 | NHL031 | 0 | 0 | 3042.7573 | 135359.521 | 3042.7573 | 10612.029 | 145971.55
| 19954417 | 2026 | NHL031 | 0 | 0 | 3042.7573 | 135359.521 | 3042.7573 | 10612.029 | 145971.55
| 19954417 | 2027 | NHL031 | 0 | 0 | 3042.7573 | 135359.521 | 3042.7573 | 10612.029 | 145971.55
| 19954417 | 2028 | NHL031 | 0 | 0 | 3042.7573 | 135359.521 | 3042.7573 | 10612.029 | 145971.55
| 19954417 | 2029 | NHL031 | 0 | 0 | 3042.7573 | 135359.521 | 3042.7573 | 10612.029 | 145971.55
| 19954417 | 2030 | NHL031 | 0 | 0 | 3042.7573 | 135359.521 | 3042.7573 | 10612.029 | 145971.55
| 19954417 | 2031 | NHL031 | 0 | 0 | 3042.7573 | 135359.521 | 3042.7573 | 10612.029 | 145971.55
| 19954417 | 2032 | NHL031 | 0 | 0 | 3042.7573 | 135359.521 | 3042.7573 | 10612.029 | 145971.55
| 19954417 | 2033 | NHL031 | 0 | 0 | 3042.7573 | 135359.521 | 3042.7573 | 10612.029 | 145971.55
| 19954417 | 2034 | NHL031 | 0 | 0 | 3042.7573 | 135359.521 | 3042.7573 | 10612.029 | 145971.55
| 19955967 | 2023 | NHL031 | 0 | 0 | 0 | 0 | 0 | 2487.5045 | 2487.5045
| 19955967 | 2024 | NHL031 | 0 | 0 | 0 | 0 | 0 | 2487.5045 | 2487.5045
| 19955967 | 2025 | NHL031 | 0 | 0 | 0 | 0 | 0 | 2487.5045 | 2487.5045
| 19955967 | 2026 | NHL031 | 0 | 0 | 0 | 0 | 0 | 2487.5045 | 2487.5045
| 19955967 | 2027 | NHL031 | 0 | 0 | 0 | 0 | 0 | 2487.5045 | 2487.5045
| 19955967 | 2028 | NHL031 | 0 | 0 | 0 | 0 | 0 | 2487.5045 | 2487.5045
| 19955967 | 2029 | NHL031 | 0 | 0 | 0 | 0 | 0 | 2487.5045 | 2487.5045
| 19955967 | 2030 | NHL031 | 0 | 0 | 0 | 0 | 0 | 2487.5045 | 2487.5045
| 19955967 | 2031 | NHL031 | 0 | 0 | 0 | 0 | 0 | 2487.5045 | 2487.5045
| 19955967 | 2032 | NHL031 | 0 | 0 | 0 | 0 | 0 | 2487.5045 | 2487.5045
| 19955967 | 2033 | NHL031 | 0 | 0 | 0 | 0 | 0 | 2487.5045 | 2487.5045
| 19955967 | 2034 | NHL031 | 0 | 0 | 0 | 0 | 0 | 2487.5045 | 2487.5045
| 20495774 | 2023 | NHL031 | 0 | 0 | 0 | 0 | 0 | 10222.9367 | 10222.9367
| 20495774 | 2024 | NHL031 | 0 | 0 | 0 | 0 | 0 | 10222.9367 | 10222.9367
| 20495774 | 2025 | NHL031 | 0 | 0 | 0 | 0 | 0 | 10222.9367 | 10222.9367
| 20495774 | 2026 | NHL031 | 0 | 0 | 0 | 0 | 0 | 10222.9367 | 10222.9367
| 20495774 | 2027 | NHL031 | 0 | 0 | 0 | 0 | 0 | 10222.9367 | 10222.9367
| 20495774 | 2028 | NHL031 | 0 | 0 | 0 | 0 | 0 | 10222.9367 | 10222.9367
| 20495774 | 2029 | NHL031 | 0 | 0 | 0 | 0 | 0 | 10222.9367 | 10222.9367
| 20495774 | 2030 | NHL031 | 0 | 0 | 0 | 0 | 0 | 10222.9367 | 10222.9367
| 20495774 | 2031 | NHL031 | 0 | 0 | 0 | 0 | 0 | 10222.9367 | 10222.9367
| 20495774 | 2032 | NHL031 | 0 | 0 | 0 | 0 | 0 | 10222.9367 | 10222.9367
| 20495774 | 2033 | NHL031 | 0 | 0 | 0 | 0 | 0 | 10222.9367 | 10222.9367
| 20495774 | 2034 | NHL031 | 0 | 0 | 0 | 0 | 0 | 10222.9367 | 10222.9367
| 20495814 | 2023 | NHL031 | 0 | 0 | 0 | 0 | 0 | 14745.1793 | 14745.1793
| 20495814 | 2024 | NHL031 | 0 | 0 | 0 | 0 | 0 | 14745.1793 | 14745.1793
| 20495814 | 2025 | NHL031 | 0 | 0 | 0 | 0 | 0 | 14745.1793 | 14745.1793
| 20495814 | 2026 | NHL031 | 0 | 0 | 0 | 0 | 0 | 14745.1793 | 14745.1793
| 20495814 | 2027 | NHL031 | 0 | 0 | 0 | 0 | 0 | 14745.1793 | 14745.1793
| 20495814 | 2028 | NHL031 | 0 | 0 | 0 | 0 | 0 | 14745.1793 | 14745.1793
| 20495814 | 2029 | NHL031 | 0 | 0 | 0 | 0 | 0 | 14745.1793 | 14745.1793
| 20495814 | 2030 | NHL031 | 0 | 0 | 0 | 0 | 0 | 14745.1793 | 14745.1793
| 20495814 | 2031 | NHL031 | 0 | 0 | 0 | 0 | 0 | 14745.1793 | 14745.1793
| 20495814 | 2032 | NHL031 | 0 | 0 | 0 | 0 | 0 | 14745.1793 | 14745.1793
| 20495814 | 2033 | NHL031 | 0 | 0 | 0 | 0 | 0 | 14745.1793 | 14745.1793
| 20495814 | 2034 | NHL031 | 0 | 0 | 0 | 0 | 0 | 14745.1793 | 14745.1793
| 20663112 | 2023 | NHL031 | 37.7356 | 0 | 0 | 0 | 37.7356 | 6542.6091 | 6542.6091
| 20663112 | 2024 | NHL031 | 37.7356 | 0 | 0 | 0 | 37.7356 | 6542.6091 | 6542.6091
| 20663112 | 2025 | NHL031 | 37.7356 | 0 | 0 | 0 | 37.7356 | 6542.6091 | 6542.6091
| 20663112 | 2026 | NHL031 | 37.7356 | 0 | 0 | 0 | 37.7356 | 6542.6091 | 6542.6091
| 20663112 | 2027 | NHL031 | 37.7356 | 0 | 0 | 0 | 37.7356 | 6542.6091 | 6542.6091
| 20663112 | 2028 | NHL031 | 37.7356 | 0 | 0 | 0 | 37.7356 | 6542.6091 | 6542.6091
| 20663112 | 2029 | NHL031 | 37.7356 | 0 | 0 | 0 | 37.7356 | 6542.6091 | 6542.6091
| 20663112 | 2030 | NHL031 | 37.7356 | 0 | 0 | 0 | 37.7356 | 6542.6091 | 6542.6091
| 20663112 | 2031 | NHL031 | 37.7356 | 0 | 0 | 0 | 37.7356 | 6542.6091 | 6542.6091
| 20663112 | 2032 | NHL031 | 37.7356 | 0 | 0 | 0 | 37.7356 | 6542.6091 | 6542.6091
| 20663112 | 2033 | NHL031 | 37.7356 | 0 | 0 | 0 | 37.7356 | 6542.6091 | 6542.6091
| 20663112 | 2034 | NHL031 | 37.7356 | 0 | 0 | 0 | 37.7356 | 6542.6091 | 6542.6091
| 40374941 | 2023 | NHL031 | 0 | 0 | 0 | 0 | 0 | 3694.2916 | 3694.2916
| 40374941 | 2024 | NHL031 | 0 | 0 | 0 | 0 | 0 | 3694.2916 | 3694.2916
| 40374941 | 2025 | NHL031 | 0 | 0 | 0 | 0 | 0 | 3694.2916 | 3694.2916
| 40374941 | 2026 | NHL031 | 0 | 0 | 0 | 0 | 0 | 3694.2916 | 3694.2916
| 40374941 | 2027 | NHL031 | 0 | 0 | 0 | 0 | 0 | 3694.2916 | 3694.2916
| 40374941 | 2028 | NHL031 | 0 | 0 | 0 | 0 | 0 | 3694.2916 | 3694.2916
| 40374941 | 2029 | NHL031 | 0 | 0 | 0 | 0 | 0 | 3694.2916 | 3694.2916
| 40374941 | 2030 | NHL031 | 0 | 0 | 0 | 0 | 0 | 3694.2916 | 3694.2916
| 40374941 | 2031 | NHL031 | 0 | 0 | 0 | 0 | 0 | 3694.2916 | 3694.2916
| 40374941 | 2032 | NHL031 | 0 | 0 | 0 | 0 | 0 | 3694.2916 | 3694.2916
| 40374941 | 2033 | NHL031 | 0 | 0 | 0 | 0 | 0 | 3694.2916 | 3694.2916
| 40374941 | 2034 | NHL031 | 0 | 0 | 0 | 0 | 0 | 3694.2916 | 3694.2916
| 44211635 | 2023 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11114.3256 | 11114.3256
| 44211635 | 2024 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11114.3256 | 11114.3256
| 44211635 | 2025 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11114.3256 | 11114.3256
| 44211635 | 2026 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11114.3256 | 11114.3256
| 44211635 | 2027 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11114.3256 | 11114.3256
| 44211635 | 2028 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11114.3256 | 11114.3256
| 44211635 | 2029 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11114.3256 | 11114.3256
| 44211635 | 2030 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11114.3256 | 11114.3256
| 44211635 | 2031 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11114.3256 | 11114.3256
| 44211635 | 2032 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11114.3256 | 11114.3256
| 44211635 | 2033 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11114.3256 | 11114.3256
| 44211635 | 2034 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11114.3256 | 11114.3256
| 158072599 | 2023 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11164.3012 | 11164.3012
| 158072599 | 2024 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11164.3012 | 11164.3012
| 158072599 | 2025 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11164.3012 | 11164.3012
| 158072599 | 2026 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11164.3012 | 11164.3012
| 158072599 | 2027 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11164.3012 | 11164.3012
| 158072599 | 2028 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11164.3012 | 11164.3012
| 158072599 | 2029 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11164.3012 | 11164.3012
| 158072599 | 2030 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11164.3012 | 11164.3012
| 158072599 | 2031 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11164.3012 | 11164.3012
| 158072599 | 2032 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11164.3012 | 11164.3012
| 158072599 | 2033 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11164.3012 | 11164.3012
| 158072599 | 2034 | NHL031 | 0 | 0 | 0 | 0 | 0 | 11164.3012 | 11164.3012
| 158072999 | 2023 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7657.3938 | 7657.3938
| 158072999 | 2024 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7657.3938 | 7657.3938
| 158072999 | 2025 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7657.3938 | 7657.3938
| 158072999 | 2026 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7657.3938 | 7657.3938
| 158072999 | 2027 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7657.3938 | 7657.3938
| 158072999 | 2028 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7657.3938 | 7657.3938
| 158072999 | 2029 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7657.3938 | 7657.3938
| 158072999 | 2030 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7657.3938 | 7657.3938
| 158072999 | 2031 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7657.3938 | 7657.3938
| 158072999 | 2032 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7657.3938 | 7657.3938
| 158072999 | 2033 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7657.3938 | 7657.3938
| 158072999 | 2034 | NHL031 | 0 | 0 | 0 | 0 | 0 | 7657.3938 | 7657.3938
| 158085563 | 2023 | NHL031 | 80.0054 | 0 | 0 | 0 | 80.0054 | 11884.3866 | 11884.3866
| 158085563 | 2024 | NHL031 | 80.0054 | 0 | 0 | 0 | 80.0054 | 11884.3866 | 11884.3866
| 158085563 | 2025 | NHL031 | 80.0054 | 0 | 0 | 0 | 80.0054 | 11884.3866 | 11884.3866
| 158085563 | 2026 | NHL031 | 80.0054 | 0 | 0 | 0 | 80.0054 | 11884.3866 | 11884.3866
| 158085563 | 2027 | NHL031 | 80.0054 | 0 | 0 | 0 | 80.0054 | 11884.3866 | 11884.3866
| 158085563 | 2028 | NHL031 | 80.0054 | 0 | 0 | 0 | 80.0054 | 11884.3866 | 11884.3866
| 158085563 | 2029 | NHL031 | 80.0054 | 0 | 0 | 0 | 80.0054 | 11884.3866 | 11884.3866
| 158085563 | 2030 | NHL031 | 80.0054 | 0 | 0 | 0 | 80.0054 | 11884.3866 | 11884.3866
| 158085563 | 2031 | NHL031 | 80.0054 | 0 | 0 | 0 | 80.0054 | 11884.3866 | 11884.3866
| 158085563 | 2032 | NHL031 | 80.0054 | 0 | 0 | 0 | 80.0054 | 11884.3866 | 11884.3866
| 158085563 | 2033 | NHL031 | 80.0054 | 0 | 0 | 0 | 80.0054 | 11884.3866 | 11884.3866
| 158085563 | 2034 | NHL031 | 80.0054 | 0 | 0 | 0 | 80.0054 | 11884.3866 | 11884.3866
| 158104025 | 2023 | NHL031 | 0 | 0 | 0.97051 | 43.174 | 0.97051 | 12573.0211 | 12616.195
| 158104025 | 2024 | NHL031 | 0 | 0 | 0.97051 | 43.174 | 0.97051 | 12573.0211 | 12616.195
| 158104025 | 2025 | NHL031 | 0 | 0 | 0.97051 | 43.174 | 0.97051 | 12573.0211 | 12616.195
| 158104025 | 2026 | NHL031 | 0 | 0 | 0.97051 | 43.174 | 0.97051 | 12573.0211 | 12616.195
| 158104025 | 2027 | NHL031 | 0 | 0 | 0.97051 | 43.174 | 0.97051 | 12573.0211 | 12616.195
| 158104025 | 2028 | NHL031 | 0 | 0 | 0.97051 | 43.174 | 0.97051 | 12573.0211 | 12616.195
| 158104025 | 2029 | NHL031 | 0 | 0 | 0.97051 | 43.174 | 0.97051 | 12573.0211 | 12616.195
| 158104025 | 2030 | NHL031 | 0 | 0 | 0.97051 | 43.174 | 0.97051 | 12573.0211 | 12616.195
| 158104025 | 2031 | NHL031 | 0 | 0 | 0.97051 | 43.174 | 0.97051 | 12573.0211 | 12616.195
| 158104025 | 2032 | NHL031 | 0 | 0 | 0.97051 | 43.174 | 0.97051 | 12573.0211 | 12616.195
| 158104025 | 2033 | NHL031 | 0 | 0 | 0.97051 | 43.174 | 0.97051 | 12573.0211 | 12616.195
| 158104025 | 2034 | NHL031 | 0 | 0 | 0.97051 | 43.174 | 0.97051 | 12573.0211 | 12616.195
| 177772115 | 2023 | NHL031 | 0 | 0 | 1.1364 | 50.5549 | 1.1364 | 25228.2851 | 25278.84
| 177772115 | 2024 | NHL031 | 0 | 0 | 1.1364 | 50.5549 | 1.1364 | 25228.2851 | 25278.84
| 177772115 | 2025 | NHL031 | 0 | 0 | 1.1364 | 50.5549 | 1.1364 | 25228.2851 | 25278.84
| 177772115 | 2026 | NHL031 | 0 | 0 | 1.1364 | 50.5549 | 1.1364 | 25228.2851 | 25278.84
| 177772115 | 2027 | NHL031 | 0 | 0 | 1.1364 | 50.5549 | 1.1364 | 25228.2851 | 25278.84
| 177772115 | 2028 | NHL031 | 0 | 0 | 1.1364 | 50.5549 | 1.1364 | 25228.2851 | 25278.84
| 177772115 | 2029 | NHL031 | 0 | 0 | 1.1364 | 50.5549 | 1.1364 | 25228.2851 | 25278.84
| 177772115 | 2030 | NHL031 | 0 | 0 | 1.1364 | 50.5549 | 1.1364 | 25228.2851 | 25278.84
| 177772115 | 2031 | NHL031 | 0 | 0 | 1.1364 | 50.5549 | 1.1364 | 25228.2851 | 25278.84
| 177772115 | 2032 | NHL031 | 0 | 0 | 1.1364 | 50.5549 | 1.1364 | 25228.2851 | 25278.84
| 177772115 | 2033 | NHL031 | 0 | 0 | 1.1364 | 50.5549 | 1.1364 | 25228.2851 | 25278.84
| 177772115 | 2034 | NHL031 | 0 | 0 | 1.1364 | 50.5549 | 1.1364 | 25228.2851 | 25278.84
| 20628480 | 2023 | NKA001 | 0 | 0 | 0 | 0 | 0 | 2509.1412 | 2509.1412
| 20628480 | 2024 | NKA001 | 0 | 0 | 0 | 0 | 0 | 2509.1412 | 2509.1412
| 20628480 | 2025 | NKA001 | 0 | 0 | 0 | 0 | 0 | 2509.1412 | 2509.1412
| 20628480 | 2026 | NKA001 | 0 | 0 | 0 | 0 | 0 | 2509.1412 | 2509.1412
| 20628480 | 2027 | NKA001 | 0 | 0 | 0 | 0 | 0 | 2509.1412 | 2509.1412
| 20628480 | 2028 | NKA001 | 0 | 0 | 4.2903 | 224.8161 | 4.2903 | 2509.1412 | 2733.9573
| 20628480 | 2029 | NKA001 | 0 | 0 | 4.728 | 247.7517 | 4.728 | 2509.1412 | 2756.8929
| 20628480 | 2030 | NKA001 | 0 | 0 | 23.6902 | 1241.3921 | 23.6902 | 2509.1412 | 3750.5333
| 20628480 | 2031 | NKA001 | 0 | 0 | 23.6902 | 1241.3921 | 23.6902 | 2509.1412 | 3750.5333
| 20628480 | 2032 | NKA001 | 0 | 0 | 23.6902 | 1241.3921 | 23.6902 | 2509.1412 | 3750.5333
| 20628480 | 2033 | NKA001 | 0 | 0 | 23.6902 | 1241.3921 | 23.6902 | 2509.1412 | 3750.5333
| 20628480 | 2034 | NKA001 | 0 | 0 | 23.6902 | 1241.3921 | 23.6902 | 2509.1412 | 3750.5333
| 112129651 | 2023 | NKA001 | 2585.2174 | 0 | 0 | 0 | 2585.2174 | 3803.9803 | 3803.9803
| 112129651 | 2024 | NKA001 | 9045.2349 | 177.9006 | 0 | 0 | 9045.2349 | 3803.9803 | 3981.8808
| 112129651 | 2025 | NKA001 | 11692.4829 | 247.2498 | 0 | 0 | 11692.4829 | 3803.9803 | 4051.2301
| 112129651 | 2026 | NKA001 | 16299.6507 | 197.1075 | 0 | 0 | 16299.6507 | 3803.9803 | 4001.0877
| 112129651 | 2027 | NKA001 | 20166.2634 | 205.5794 | 0 | 0 | 20166.2634 | 3803.9803 | 4009.5596
| 112129651 | 2028 | NKA001 | 21597.5508 | 229.1111 | 0 | 0 | 21597.5508 | 3803.9803 | 4033.0914
| 112129651 | 2029 | NKA001 | 25210.2412 | 199.3093 | 0 | 0 | 25210.2412 | 3803.9803 | 4003.2896
| 112129651 | 2030 | NKA001 | 23828.7206 | 205.7098 | 0 | 0 | 23828.7206 | 3803.9803 | 4009.6901
| 112129651 | 2031 | NKA001 | 23828.7206 | 205.7098 | 0 | 0 | 23828.7206 | 3803.9803 | 4009.6901
| 112129651 | 2032 | NKA001 | 23828.7206 | 205.7098 | 0 | 0 | 23828.7206 | 3803.9803 | 4009.6901
| 112129651 | 2033 | NKA001 | 23828.7206 | 205.7098 | 0 | 0 | 23828.7206 | 3803.9803 | 4009.6901
| 112129651 | 2034 | NKA001 | 23828.7206 | 205.7098 | 0 | 0 | 23828.7206 | 3803.9803 | 4009.6901
| 138135552 | 2023 | NKA001 | 2686.0199 | 0 | 0 | 0 | 2686.0199 | 5118.5511 | 5118.5511
| 138135552 | 2024 | NKA001 | 2666.548 | 58.361 | 0 | 0 | 2666.548 | 5118.5511 | 5176.912
| 138135552 | 2025 | NKA001 | 5107.7652 | 125.4555 | 0 | 0 | 5107.7652 | 5118.5511 | 5244.0066
| 138135552 | 2026 | NKA001 | 5180.6539 | 76.2083 | 0 | 0 | 5180.6539 | 5118.5511 | 5194.7593
| 138135552 | 2027 | NKA001 | 5098.0369 | 65.4625 | 0 | 0 | 5098.0369 | 5118.5511 | 5184.0136
| 138135552 | 2028 | NKA001 | 4195.6863 | 61.0174 | 0 | 0 | 4195.6863 | 5118.5511 | 5179.5684
| 138135552 | 2029 | NKA001 | 4498.4112 | 45.0755 | 0 | 0 | 4498.4112 | 5118.5511 | 5163.6265
| 138135552 | 2030 | NKA001 | 6546.6182 | 74.2597 | 0.0011242 | 0.058911 | 6546.6194 | 5118.5511 | 5192.8696
| 138135552 | 2031 | NKA001 | 6546.6182 | 74.2597 | 0.0011242 | 0.058911 | 6546.6194 | 5118.5511 | 5192.8696
| 138135552 | 2032 | NKA001 | 6546.6182 | 74.2597 | 0.0011242 | 0.058911 | 6546.6194 | 5118.5511 | 5192.8696
| 138135552 | 2033 | NKA001 | 6546.6182 | 74.2597 | 0.0011242 | 0.058911 | 6546.6194 | 5118.5511 | 5192.8696
| 138135552 | 2034 | NKA001 | 6546.6182 | 74.2597 | 0.0011242 | 0.058911 | 6546.6194 | 5118.5511 | 5192.8696
| 20497765 | 2023 | NKA003 | 0 | 0 | 0 | 0 | 0 | 3498.5697 | 3498.5697
| 20497765 | 2024 | NKA003 | 0 | 0 | 0 | 0 | 0 | 3498.5697 | 3498.5697
| 20497765 | 2025 | NKA003 | 0 | 0 | 0 | 0 | 0 | 3498.5697 | 3498.5697
| 20497765 | 2026 | NKA003 | 0 | 0 | 0 | 0 | 0 | 3498.5697 | 3498.5697
| 20497765 | 2027 | NKA003 | 0 | 0 | 0 | 0 | 0 | 3498.5697 | 3498.5697
| 20497765 | 2028 | NKA003 | 0 | 0 | 0 | 0 | 0 | 3498.5697 | 3498.5697
| 20497765 | 2029 | NKA003 | 0 | 0 | 0 | 0 | 0 | 3498.5697 | 3498.5697
| 20497765 | 2030 | NKA003 | 7.1193 | 6.2455e-12 | 0 | 0 | 7.1193 | 3498.5697 | 3498.5697
| 20497765 | 2031 | NKA003 | 7.1193 | 6.2455e-12 | 0 | 0 | 7.1193 | 3498.5697 | 3498.5697
| 20497765 | 2032 | NKA003 | 7.1193 | 6.2455e-12 | 0 | 0 | 7.1193 | 3498.5697 | 3498.5697
| 20497765 | 2033 | NKA003 | 7.1193 | 6.2455e-12 | 0 | 0 | 7.1193 | 3498.5697 | 3498.5697
| 20497765 | 2034 | NKA003 | 7.1193 | 6.2455e-12 | 0 | 0 | 7.1193 | 3498.5697 | 3498.5697
| 20544027 | 2023 | NKA004 | 0 | 0 | 0 | 0 | 0 | 3115.0847 | 3115.0847
| 20544027 | 2024 | NKA004 | 0 | 0 | 0 | 0 | 0 | 3115.0847 | 3115.0847
| 20544027 | 2025 | NKA004 | 0 | 0 | 0 | 0 | 0 | 3115.0847 | 3115.0847
| 20544027 | 2026 | NKA004 | 0 | 0 | 0 | 0 | 0 | 3115.0847 | 3115.0847
| 20544027 | 2027 | NKA004 | 0 | 0 | 0 | 0 | 0 | 3115.0847 | 3115.0847
| 20544027 | 2028 | NKA004 | 0 | 0 | 0 | 0 | 0 | 3115.0847 | 3115.0847
| 20544027 | 2029 | NKA004 | 0 | 0 | 0 | 0 | 0 | 3115.0847 | 3115.0847
| 20544027 | 2030 | NKA004 | 0 | 0 | 0 | 0 | 0 | 3115.0847 | 3115.0847
| 20544027 | 2031 | NKA004 | 0 | 0 | 0 | 0 | 0 | 3115.0847 | 3115.0847
| 20544027 | 2032 | NKA004 | 0 | 0 | 0 | 0 | 0 | 3115.0847 | 3115.0847
| 20544027 | 2033 | NKA004 | 0 | 0 | 0 | 0 | 0 | 3115.0847 | 3115.0847
| 20544027 | 2034 | NKA004 | 0 | 0 | 0 | 0 | 0 | 3115.0847 | 3115.0847
| 19931835 | 2023 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9237.213 | 9237.213
| 19931835 | 2024 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9237.213 | 9237.213
| 19931835 | 2025 | OYN001 | 1746.4383 | 29.3575 | 0 | 0 | 1746.4383 | 9237.213 | 9266.5705
| 19931835 | 2026 | OYN001 | 2433.4605 | 30.1573 | 0 | 0 | 2433.4605 | 9237.213 | 9267.3703
| 19931835 | 2027 | OYN001 | 2730.3054 | 37.2846 | 0 | 0 | 2730.3054 | 9237.213 | 9274.4975
| 19931835 | 2028 | OYN001 | 6047.5649 | 120.3547 | 0 | 0 | 6047.5649 | 9237.213 | 9357.5677
| 19931835 | 2029 | OYN001 | 6218.185 | 117.274 | 0 | 0 | 6218.185 | 9237.213 | 9354.4869
| 19931835 | 2030 | OYN001 | 6697.5579 | 137.4496 | 0 | 0 | 6697.5579 | 9237.213 | 9374.6626
| 19931835 | 2031 | OYN001 | 6687.88 | 163.0061 | 70.7937 | 3031.4782 | 6758.6737 | 9237.213 | 12431.6973
| 19931835 | 2032 | OYN001 | 6687.88 | 163.0061 | 70.7937 | 3031.4782 | 6758.6737 | 9237.213 | 12431.6973
| 19931835 | 2033 | OYN001 | 6687.88 | 163.0061 | 70.7937 | 3031.4782 | 6758.6737 | 9237.213 | 12431.6973
| 19931835 | 2034 | OYN001 | 6687.88 | 163.0061 | 70.7937 | 3031.4782 | 6758.6737 | 9237.213 | 12431.6973
| 19936888 | 2023 | OYN001 | 0 | 0 | 39.764 | 1702.7474 | 39.764 | 10906.9953 | 12609.7428
| 19936888 | 2024 | OYN001 | 0 | 0 | 35.6018 | 1524.5139 | 35.6018 | 10906.9953 | 12431.5092
| 19936888 | 2025 | OYN001 | 0 | 0 | 28.0888 | 1202.7965 | 28.0888 | 10906.9953 | 12109.7919
| 19936888 | 2026 | OYN001 | 0 | 0 | 21.5163 | 921.3572 | 21.5163 | 10906.9953 | 11828.3525
| 19936888 | 2027 | OYN001 | 67.2043 | 0.17609 | 19.5366 | 836.5803 | 86.7408 | 10906.9953 | 11743.7517
| 19936888 | 2028 | OYN001 | 1732.103 | 12.1693 | 14.5742 | 624.0862 | 1746.6772 | 10906.9953 | 11543.2508
| 19936888 | 2029 | OYN001 | 1998.6585 | 10.1387 | 14.1382 | 605.4178 | 2012.7968 | 10906.9953 | 11522.5518
| 19936888 | 2030 | OYN001 | 2549.6767 | 21.3413 | 15.6631 | 670.7159 | 2565.3399 | 10906.9953 | 11599.0526
| 19936888 | 2031 | OYN001 | 6496.7723 | 92.1622 | 90.1504 | 3860.3582 | 6586.9227 | 10906.9953 | 14859.5158
| 19936888 | 2032 | OYN001 | 6496.7723 | 92.1622 | 90.1504 | 3860.3582 | 6586.9227 | 10906.9953 | 14859.5158
| 19936888 | 2033 | OYN001 | 6496.7723 | 92.1622 | 90.1504 | 3860.3582 | 6586.9227 | 10906.9953 | 14859.5158
| 19936888 | 2034 | OYN001 | 6496.7723 | 92.1622 | 90.1504 | 3860.3582 | 6586.9227 | 10906.9953 | 14859.5158
| 19936906 | 2023 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9444.0325 | 9444.0325
| 19936906 | 2024 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9444.0325 | 9444.0325
| 19936906 | 2025 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9444.0325 | 9444.0325
| 19936906 | 2026 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9444.0325 | 9444.0325
| 19936906 | 2027 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9444.0325 | 9444.0325
| 19936906 | 2028 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9444.0325 | 9444.0325
| 19936906 | 2029 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9444.0325 | 9444.0325
| 19936906 | 2030 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9444.0325 | 9444.0325
| 19936906 | 2031 | OYN001 | 0 | 0 | 67.0605 | 2871.6158 | 67.0605 | 9444.0325 | 12315.6482
| 19936906 | 2032 | OYN001 | 0 | 0 | 67.0605 | 2871.6158 | 67.0605 | 9444.0325 | 12315.6482
| 19936906 | 2033 | OYN001 | 0 | 0 | 67.0605 | 2871.6158 | 67.0605 | 9444.0325 | 12315.6482
| 19936906 | 2034 | OYN001 | 0 | 0 | 67.0605 | 2871.6158 | 67.0605 | 9444.0325 | 12315.6482
| 19937056 | 2023 | OYN001 | 0 | 0 | 51.8121 | 2218.6591 | 51.8121 | 14624.2797 | 16842.9388
| 19937056 | 2024 | OYN001 | 0 | 0 | 56.2603 | 2409.1375 | 56.2603 | 14624.2797 | 17033.4172
| 19937056 | 2025 | OYN001 | 0 | 0 | 47.2048 | 2021.3705 | 47.2048 | 14624.2797 | 16645.6502
| 19937056 | 2026 | OYN001 | 0 | 0 | 47.0452 | 2014.5371 | 47.0452 | 14624.2797 | 16638.8168
| 19937056 | 2027 | OYN001 | 0 | 0 | 44.5443 | 1907.4456 | 44.5443 | 14624.2797 | 16531.7253
| 19937056 | 2028 | OYN001 | 0 | 0 | 44.9299 | 1923.9571 | 44.9299 | 14624.2797 | 16548.2368
| 19937056 | 2029 | OYN001 | 0 | 0 | 44.5505 | 1907.7106 | 44.5505 | 14624.2797 | 16531.9903
| 19937056 | 2030 | OYN001 | 0 | 0 | 45.0453 | 1928.8959 | 45.0453 | 14624.2797 | 16553.1756
| 19937056 | 2031 | OYN001 | 0 | 0 | 172.3159 | 7378.79 | 172.3159 | 14624.2797 | 22003.0697
| 19937056 | 2032 | OYN001 | 0 | 0 | 172.3159 | 7378.79 | 172.3159 | 14624.2797 | 22003.0697
| 19937056 | 2033 | OYN001 | 0 | 0 | 172.3159 | 7378.79 | 172.3159 | 14624.2797 | 22003.0697
| 19937056 | 2034 | OYN001 | 0 | 0 | 172.3159 | 7378.79 | 172.3159 | 14624.2797 | 22003.0697
| 19937096 | 2023 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9867.717 | 9867.717
| 19937096 | 2024 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9867.717 | 9867.717
| 19937096 | 2025 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9867.717 | 9867.717
| 19937096 | 2026 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9867.717 | 9867.717
| 19937096 | 2027 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9867.717 | 9867.717
| 19937096 | 2028 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9867.717 | 9867.717
| 19937096 | 2029 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9867.717 | 9867.717
| 19937096 | 2030 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9867.717 | 9867.717
| 19937096 | 2031 | OYN001 | 0 | 0 | 41.937 | 1795.7983 | 41.937 | 9867.717 | 11663.5153
| 19937096 | 2032 | OYN001 | 0 | 0 | 41.937 | 1795.7983 | 41.937 | 9867.717 | 11663.5153
| 19937096 | 2033 | OYN001 | 0 | 0 | 41.937 | 1795.7983 | 41.937 | 9867.717 | 11663.5153
| 19937096 | 2034 | OYN001 | 0 | 0 | 41.937 | 1795.7983 | 41.937 | 9867.717 | 11663.5153
| 19941264 | 2023 | OYN001 | 0 | 0 | 0.48792 | 20.8935 | 0.48792 | 6582.579 | 6603.4726
| 19941264 | 2024 | OYN001 | 0 | 0 | 0.12659 | 5.4209 | 0.12659 | 6582.579 | 6587.9999
| 19941264 | 2025 | OYN001 | 0 | 0 | 0 | 0 | 0 | 6582.579 | 6582.579
| 19941264 | 2026 | OYN001 | 0 | 0 | 0 | 0 | 0 | 6582.579 | 6582.579
| 19941264 | 2027 | OYN001 | 0 | 0 | 0 | 0 | 0 | 6582.579 | 6582.579
| 19941264 | 2028 | OYN001 | 0 | 0 | 0.066297 | 2.8389 | 0.066297 | 6582.579 | 6585.4179
| 19941264 | 2029 | OYN001 | 0 | 0 | 0 | 0 | 0 | 6582.579 | 6582.579
| 19941264 | 2030 | OYN001 | 0 | 0 | 0 | 0 | 0 | 6582.579 | 6582.579
| 19941264 | 2031 | OYN001 | 0 | 0 | 39.6266 | 1696.8611 | 39.6266 | 6582.579 | 8279.4401
| 19941264 | 2032 | OYN001 | 0 | 0 | 39.6266 | 1696.8611 | 39.6266 | 6582.579 | 8279.4401
| 19941264 | 2033 | OYN001 | 0 | 0 | 39.6266 | 1696.8611 | 39.6266 | 6582.579 | 8279.4401
| 19941264 | 2034 | OYN001 | 0 | 0 | 39.6266 | 1696.8611 | 39.6266 | 6582.579 | 8279.4401
| 19941447 | 2023 | OYN001 | 0 | 0 | 0 | 0 | 0 | 833.6173 | 833.6173
| 19941447 | 2024 | OYN001 | 0 | 0 | 0 | 0 | 0 | 833.6173 | 833.6173
| 19941447 | 2025 | OYN001 | 0 | 0 | 0 | 0 | 0 | 833.6173 | 833.6173
| 19941447 | 2026 | OYN001 | 0 | 0 | 0 | 0 | 0 | 833.6173 | 833.6173
| 19941447 | 2027 | OYN001 | 0 | 0 | 0 | 0 | 0 | 833.6173 | 833.6173
| 19941447 | 2028 | OYN001 | 0 | 0 | 0 | 0 | 0 | 833.6173 | 833.6173
| 19941447 | 2029 | OYN001 | 0 | 0 | 0 | 0 | 0 | 833.6173 | 833.6173
| 19941447 | 2030 | OYN001 | 0 | 0 | 0 | 0 | 0 | 833.6173 | 833.6173
| 19941447 | 2031 | OYN001 | 0 | 0 | 0.97854 | 41.9022 | 0.97854 | 833.6173 | 875.5195
| 19941447 | 2032 | OYN001 | 0 | 0 | 0.97854 | 41.9022 | 0.97854 | 833.6173 | 875.5195
| 19941447 | 2033 | OYN001 | 0 | 0 | 0.97854 | 41.9022 | 0.97854 | 833.6173 | 875.5195
| 19941447 | 2034 | OYN001 | 0 | 0 | 0.97854 | 41.9022 | 0.97854 | 833.6173 | 875.5195
| 19942323 | 2023 | OYN001 | 0 | 0 | 0.025448 | 1.0897 | 0.025448 | 3962.2974 | 3963.3871
| 19942323 | 2024 | OYN001 | 0 | 0 | 0.018834 | 0.80651 | 0.018834 | 3962.2974 | 3963.1039
| 19942323 | 2025 | OYN001 | 0 | 0 | 0 | 0 | 0 | 3962.2974 | 3962.2974
| 19942323 | 2026 | OYN001 | 0 | 0 | 0 | 0 | 0 | 3962.2974 | 3962.2974
| 19942323 | 2027 | OYN001 | 0 | 0 | 0.0046485 | 0.19905 | 0.0046485 | 3962.2974 | 3962.4964
| 19942323 | 2028 | OYN001 | 0 | 0 | 0.015625 | 0.66907 | 0.015625 | 3962.2974 | 3962.9665
| 19942323 | 2029 | OYN001 | 0 | 0 | 0 | 0 | 0 | 3962.2974 | 3962.2974
| 19942323 | 2030 | OYN001 | 0 | 0 | 0 | 0 | 0 | 3962.2974 | 3962.2974
| 19942323 | 2031 | OYN001 | 0 | 0 | 40.795 | 1746.8935 | 40.795 | 3962.2974 | 5709.1909
| 19942323 | 2032 | OYN001 | 0 | 0 | 40.795 | 1746.8935 | 40.795 | 3962.2974 | 5709.1909
| 19942323 | 2033 | OYN001 | 0 | 0 | 40.795 | 1746.8935 | 40.795 | 3962.2974 | 5709.1909
| 19942323 | 2034 | OYN001 | 0 | 0 | 40.795 | 1746.8935 | 40.795 | 3962.2974 | 5709.1909
| 19942363 | 2023 | OYN001 | 0 | 0 | 0 | 0 | 0 | 1294.5858 | 1294.5858
| 19942363 | 2024 | OYN001 | 0 | 0 | 0 | 0 | 0 | 1294.5858 | 1294.5858
| 19942363 | 2025 | OYN001 | 0 | 0 | 0 | 0 | 0 | 1294.5858 | 1294.5858
| 19942363 | 2026 | OYN001 | 0 | 0 | 0 | 0 | 0 | 1294.5858 | 1294.5858
| 19942363 | 2027 | OYN001 | 0 | 0 | 0 | 0 | 0 | 1294.5858 | 1294.5858
| 19942363 | 2028 | OYN001 | 0 | 0 | 0 | 0 | 0 | 1294.5858 | 1294.5858
| 19942363 | 2029 | OYN001 | 0 | 0 | 0 | 0 | 0 | 1294.5858 | 1294.5858
| 19942363 | 2030 | OYN001 | 0 | 0 | 0 | 0 | 0 | 1294.5858 | 1294.5858
| 19942363 | 2031 | OYN001 | 0 | 0 | 8.0561 | 344.9742 | 8.0561 | 1294.5858 | 1639.56
| 19942363 | 2032 | OYN001 | 0 | 0 | 8.0561 | 344.9742 | 8.0561 | 1294.5858 | 1639.56
| 19942363 | 2033 | OYN001 | 0 | 0 | 8.0561 | 344.9742 | 8.0561 | 1294.5858 | 1639.56
| 19942363 | 2034 | OYN001 | 0 | 0 | 8.0561 | 344.9742 | 8.0561 | 1294.5858 | 1639.56
| 19942623 | 2023 | OYN001 | 0 | 0 | 0 | 0 | 0 | 4293.4443 | 4293.4443
| 19942623 | 2024 | OYN001 | 0 | 0 | 0 | 0 | 0 | 4293.4443 | 4293.4443
| 19942623 | 2025 | OYN001 | 0 | 0 | 0 | 0 | 0 | 4293.4443 | 4293.4443
| 19942623 | 2026 | OYN001 | 0 | 0 | 0 | 0 | 0 | 4293.4443 | 4293.4443
| 19942623 | 2027 | OYN001 | 0 | 0 | 0 | 0 | 0 | 4293.4443 | 4293.4443
| 19942623 | 2028 | OYN001 | 0 | 0 | 0 | 0 | 0 | 4293.4443 | 4293.4443
| 19942623 | 2029 | OYN001 | 0 | 0 | 0 | 0 | 0 | 4293.4443 | 4293.4443
| 19942623 | 2030 | OYN001 | 1764.8323 | 18.3906 | 0 | 0 | 1764.8323 | 4293.4443 | 4311.8349
| 19942623 | 2031 | OYN001 | 1909.3338 | 26.5099 | 15.0456 | 644.27 | 1924.3794 | 4293.4443 | 4964.2241
| 19942623 | 2032 | OYN001 | 1909.3338 | 26.5099 | 15.0456 | 644.27 | 1924.3794 | 4293.4443 | 4964.2241
| 19942623 | 2033 | OYN001 | 1909.3338 | 26.5099 | 15.0456 | 644.27 | 1924.3794 | 4293.4443 | 4964.2241
| 19942623 | 2034 | OYN001 | 1909.3338 | 26.5099 | 15.0456 | 644.27 | 1924.3794 | 4293.4443 | 4964.2241
| 19942927 | 2023 | OYN001 | 0 | 0 | 1.5536 | 66.5292 | 1.5536 | 6984.6038 | 7051.133
| 19942927 | 2024 | OYN001 | 0 | 0 | 1.4035 | 60.1008 | 1.4035 | 6984.6038 | 7044.7046
| 19942927 | 2025 | OYN001 | 0 | 0 | 0.12456 | 5.3339 | 0.12456 | 6984.6038 | 6989.9377
| 19942927 | 2026 | OYN001 | 0 | 0 | 0 | 0 | 0 | 6984.6038 | 6984.6038
| 19942927 | 2027 | OYN001 | 0.38661 | 0.00050149 | 0.20215 | 8.6561 | 0.58876 | 6984.6038 | 6993.2604
| 19942927 | 2028 | OYN001 | 15.6682 | 0.063395 | 0.45185 | 19.3489 | 16.12 | 6984.6038 | 7004.0161
| 19942927 | 2029 | OYN001 | 33.4453 | 0.080014 | 0 | 0 | 33.4453 | 6984.6038 | 6984.6838
| 19942927 | 2030 | OYN001 | 56.3277 | 0.23096 | 0 | 0 | 56.3277 | 6984.6038 | 6984.8347
| 19942927 | 2031 | OYN001 | 1257.3786 | 13.7368 | 136.8277 | 5859.1398 | 1394.2064 | 6984.6038 | 12857.4804
| 19942927 | 2032 | OYN001 | 1257.3786 | 13.7368 | 136.8277 | 5859.1398 | 1394.2064 | 6984.6038 | 12857.4804
| 19942927 | 2033 | OYN001 | 1257.3786 | 13.7368 | 136.8277 | 5859.1398 | 1394.2064 | 6984.6038 | 12857.4804
| 19942927 | 2034 | OYN001 | 1257.3786 | 13.7368 | 136.8277 | 5859.1398 | 1394.2064 | 6984.6038 | 12857.4804
| 20062674 | 2023 | OYN001 | 0 | 0 | 0 | 0 | 0 | 19360.7175 | 19360.7175
| 20062674 | 2024 | OYN001 | 0 | 0 | 0 | 0 | 0 | 19360.7175 | 19360.7175
| 20062674 | 2025 | OYN001 | 0 | 0 | 0 | 0 | 0 | 19360.7175 | 19360.7175
| 20062674 | 2026 | OYN001 | 0 | 0 | 0 | 0 | 0 | 19360.7175 | 19360.7175
| 20062674 | 2027 | OYN001 | 0 | 0 | 0 | 0 | 0 | 19360.7175 | 19360.7175
| 20062674 | 2028 | OYN001 | 0 | 0 | 0 | 0 | 0 | 19360.7175 | 19360.7175
| 20062674 | 2029 | OYN001 | 0 | 0 | 0 | 0 | 0 | 19360.7175 | 19360.7175
| 20062674 | 2030 | OYN001 | 0 | 0 | 0 | 0 | 0 | 19360.7175 | 19360.7175
| 20062674 | 2031 | OYN001 | 0 | 0 | 27.5554 | 1179.9596 | 27.5554 | 19360.7175 | 20540.6772
| 20062674 | 2032 | OYN001 | 0 | 0 | 27.5554 | 1179.9596 | 27.5554 | 19360.7175 | 20540.6772
| 20062674 | 2033 | OYN001 | 0 | 0 | 27.5554 | 1179.9596 | 27.5554 | 19360.7175 | 20540.6772
| 20062674 | 2034 | OYN001 | 0 | 0 | 27.5554 | 1179.9596 | 27.5554 | 19360.7175 | 20540.6772
| 20062890 | 2023 | OYN001 | 46.5545 | 0 | 0 | 0 | 46.5545 | 20077.3606 | 20077.3606
| 20062890 | 2024 | OYN001 | 38.7551 | 1.384 | 0 | 0 | 38.7551 | 20077.3606 | 20078.7446
| 20062890 | 2025 | OYN001 | 127.2261 | 3.5681 | 0 | 0 | 127.2261 | 20077.3606 | 20080.9288
| 20062890 | 2026 | OYN001 | 99.8963 | 1.7601 | 0 | 0 | 99.8963 | 20077.3606 | 20079.1207
| 20062890 | 2027 | OYN001 | 84.5837 | 1.2894 | 0 | 0 | 84.5837 | 20077.3606 | 20078.65
| 20062890 | 2028 | OYN001 | 87.1724 | 1.7593 | 0 | 0 | 87.1724 | 20077.3606 | 20079.12
| 20062890 | 2029 | OYN001 | 67.1026 | 1.4076 | 0 | 0 | 67.1026 | 20077.3606 | 20078.7682
| 20062890 | 2030 | OYN001 | 60.8704 | 1.4552 | 0 | 0 | 60.8704 | 20077.3606 | 20078.8158
| 20062890 | 2031 | OYN001 | 27.9345 | 0.84672 | 136.9942 | 5866.2686 | 164.9287 | 20077.3606 | 25944.476
| 20062890 | 2032 | OYN001 | 27.9345 | 0.84672 | 136.9942 | 5866.2686 | 164.9287 | 20077.3606 | 25944.476
| 20062890 | 2033 | OYN001 | 27.9345 | 0.84672 | 136.9942 | 5866.2686 | 164.9287 | 20077.3606 | 25944.476
| 20062890 | 2034 | OYN001 | 27.9345 | 0.84672 | 136.9942 | 5866.2686 | 164.9287 | 20077.3606 | 25944.476
| 20064881 | 2023 | OYN001 | 0 | 0 | 0 | 0 | 0 | 11480.602 | 11480.602
| 20064881 | 2024 | OYN001 | 0 | 0 | 0 | 0 | 0 | 11480.602 | 11480.602
| 20064881 | 2025 | OYN001 | 0 | 0 | 0 | 0 | 0 | 11480.602 | 11480.602
| 20064881 | 2026 | OYN001 | 17.5457 | 0.21397 | 0 | 0 | 17.5457 | 11480.602 | 11480.8159
| 20064881 | 2027 | OYN001 | 23.9924 | 0.045758 | 0 | 0 | 23.9924 | 11480.602 | 11480.6477
| 20064881 | 2028 | OYN001 | 0 | 0 | 0 | 0 | 0 | 11480.602 | 11480.602
| 20064881 | 2029 | OYN001 | 1.6629 | 0.00098819 | 0 | 0 | 1.6629 | 11480.602 | 11480.6029
| 20064881 | 2030 | OYN001 | 0 | 0 | 0 | 0 | 0 | 11480.602 | 11480.602
| 20064881 | 2031 | OYN001 | 0 | 0 | 0 | 0 | 0 | 11480.602 | 11480.602
| 20064881 | 2032 | OYN001 | 0 | 0 | 0 | 0 | 0 | 11480.602 | 11480.602
| 20064881 | 2033 | OYN001 | 0 | 0 | 0 | 0 | 0 | 11480.602 | 11480.602
| 20064881 | 2034 | OYN001 | 0 | 0 | 0 | 0 | 0 | 11480.602 | 11480.602
| 20065390 | 2023 | OYN001 | 0 | 0 | 0 | 0 | 0 | 3039.9393 | 3039.9393
| 20065390 | 2024 | OYN001 | 0 | 0 | 0 | 0 | 0 | 3039.9393 | 3039.9393
| 20065390 | 2025 | OYN001 | 0 | 0 | 0 | 0 | 0 | 3039.9393 | 3039.9393
| 20065390 | 2026 | OYN001 | 0 | 0 | 0 | 0 | 0 | 3039.9393 | 3039.9393
| 20065390 | 2027 | OYN001 | 0 | 0 | 0 | 0 | 0 | 3039.9393 | 3039.9393
| 20065390 | 2028 | OYN001 | 0 | 0 | 0 | 0 | 0 | 3039.9393 | 3039.9393
| 20065390 | 2029 | OYN001 | 0 | 0 | 0 | 0 | 0 | 3039.9393 | 3039.9393
| 20065390 | 2030 | OYN001 | 0 | 0 | 0.082762 | 3.544 | 0.082762 | 3039.9393 | 3043.4832
| 20065390 | 2031 | OYN001 | 0 | 0 | 0.03284 | 1.4063 | 0.03284 | 3039.9393 | 3041.3455
| 20065390 | 2032 | OYN001 | 0 | 0 | 0.03284 | 1.4063 | 0.03284 | 3039.9393 | 3041.3455
| 20065390 | 2033 | OYN001 | 0 | 0 | 0.03284 | 1.4063 | 0.03284 | 3039.9393 | 3041.3455
| 20065390 | 2034 | OYN001 | 0 | 0 | 0.03284 | 1.4063 | 0.03284 | 3039.9393 | 3041.3455
| 20065430 | 2023 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9582.5309 | 9582.5309
| 20065430 | 2024 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9582.5309 | 9582.5309
| 20065430 | 2025 | OYN001 | 0 | 0 | 0 | 0 | 0 | 9582.5309 | 9582.5309
| 20065430 | 2026 | OYN001 | 4.4323 | 0.047808 | 0 | 0 | 4.4323 | 9582.5309 | 9582.5787
| 20065430 | 2027 | OYN001 | 327.3775 | 2.7485 | 0 | 0 | 327.3775 | 9582.5309 | 9585.2794
| 20065430 | 2028 | OYN001 | 77.4202 | 0.90956 | 0 | 0 | 77.4202 | 9582.5309 | 9583.4404
| 20065430 | 2029 | OYN001 | 537.7963 | 3.8236 | 0 | 0 | 537.7963 | 9582.5309 | 9586.3544
| 20065430 | 2030 | OYN001 | 502.0093 | 2.1928 | 0 | 0 | 502.0093 | 9582.5309 | 9584.7236
| 20065430 | 2031 | OYN001 | 764.9367 | 5.606 | 0 | 0 | 764.9367 | 9582.5309 | 9588.1369
| 20065430 | 2032 | OYN001 | 764.9367 | 5.606 | 0 | 0 | 764.9367 | 9582.5309 | 9588.1369
| 20065430 | 2033 | OYN001 | 764.9367 | 5.606 | 0 | 0 | 764.9367 | 9582.5309 | 9588.1369
| 20065430 | 2034 | OYN001 | 764.9367 | 5.606 | 0 | 0 | 764.9367 | 9582.5309 | 9588.1369
| 20545743 | 2023 | OYN001 | 0 | 0 | 0 | 0 | 0 | 19359.8182 | 19359.8182
| 20545743 | 2024 | OYN001 | 0 | 0 | 0 | 0 | 0 | 19359.8182 | 19359.8182
| 20545743 | 2025 | OYN001 | 0 | 0 | 0 | 0 | 0 | 19359.8182 | 19359.8182
| 20545743 | 2026 | OYN001 | 0 | 0 | 0 | 0 | 0 | 19359.8182 | 19359.8182
| 20545743 | 2027 | OYN001 | 0 | 0 | 0 | 0 | 0 | 19359.8182 | 19359.8182
| 20545743 | 2028 | OYN001 | 0 | 0 | 0 | 0 | 0 | 19359.8182 | 19359.8182
| 20545743 | 2029 | OYN001 | 36.338 | 0.33739 | 0 | 0 | 36.338 | 19359.8182 | 19360.1556
| 20545743 | 2030 | OYN001 | 19.1884 | 0.19569 | 0 | 0 | 19.1884 | 19359.8182 | 19360.0139
| 20545743 | 2031 | OYN001 | 1.2406 | 7.8663e-05 | 0 | 0 | 1.2406 | 19359.8182 | 19359.8183
| 20545743 | 2032 | OYN001 | 1.2406 | 7.8663e-05 | 0 | 0 | 1.2406 | 19359.8182 | 19359.8183
| 20545743 | 2033 | OYN001 | 1.2406 | 7.8663e-05 | 0 | 0 | 1.2406 | 19359.8182 | 19359.8183
| 20545743 | 2034 | OYN001 | 1.2406 | 7.8663e-05 | 0 | 0 | 1.2406 | 19359.8182 | 19359.8183
| 20638508 | 2023 | OYN001 | 0 | 0 | 0 | 0 | 0 | 26040.7274 | 26040.7274
| 20638508 | 2024 | OYN001 | 0 | 0 | 0 | 0 | 0 | 26040.7274 | 26040.7274
| 20638508 | 2025 | OYN001 | 0 | 0 | 0 | 0 | 0 | 26040.7274 | 26040.7274
| 20638508 | 2026 | OYN001 | 0 | 0 | 0 | 0 | 0 | 26040.7274 | 26040.7274
| 20638508 | 2027 | OYN001 | 274.2596 | 2.0096 | 0 | 0 | 274.2596 | 26040.7274 | 26042.737
| 20638508 | 2028 | OYN001 | 267.7218 | 4.874 | 0 | 0 | 267.7218 | 26040.7274 | 26045.6014
| 20638508 | 2029 | OYN001 | 166.5197 | 2.5217 | 0 | 0 | 166.5197 | 26040.7274 | 26043.2491
| 20638508 | 2030 | OYN001 | 165.3564 | 2.7228 | 0 | 0 | 165.3564 | 26040.7274 | 26043.4502
| 20638508 | 2031 | OYN001 | 130.577 | 2.7543 | 120.4877 | 5159.4397 | 251.0648 | 26040.7274 | 31202.9214
| 20638508 | 2032 | OYN001 | 130.577 | 2.7543 | 120.4877 | 5159.4397 | 251.0648 | 26040.7274 | 31202.9214
| 20638508 | 2033 | OYN001 | 130.577 | 2.7543 | 120.4877 | 5159.4397 | 251.0648 | 26040.7274 | 31202.9214
| 20638508 | 2034 | OYN001 | 130.577 | 2.7543 | 120.4877 | 5159.4397 | 251.0648 | 26040.7274 | 31202.9214
| 76722023 | 2023 | OYN001 | 0 | 0 | 0 | 0 | 0 | 8472.5049 | 8472.5049
| 76722023 | 2024 | OYN001 | 0 | 0 | 0 | 0 | 0 | 8472.5049 | 8472.5049
| 76722023 | 2025 | OYN001 | 0 | 0 | 0 | 0 | 0 | 8472.5049 | 8472.5049
| 76722023 | 2026 | OYN001 | 0 | 0 | 0 | 0 | 0 | 8472.5049 | 8472.5049
| 76722023 | 2027 | OYN001 | 0 | 0 | 0 | 0 | 0 | 8472.5049 | 8472.5049
| 76722023 | 2028 | OYN001 | 0 | 0 | 0 | 0 | 0 | 8472.5049 | 8472.5049
| 76722023 | 2029 | OYN001 | 0 | 0 | 0 | 0 | 0 | 8472.5049 | 8472.5049
| 76722023 | 2030 | OYN001 | 0 | 0 | 0 | 0 | 0 | 8472.5049 | 8472.5049
| 76722023 | 2031 | OYN001 | 0 | 0 | 79.7269 | 3414.0081 | 79.7269 | 8472.5049 | 11886.513
| 76722023 | 2032 | OYN001 | 0 | 0 | 79.7269 | 3414.0081 | 79.7269 | 8472.5049 | 11886.513
| 76722023 | 2033 | OYN001 | 0 | 0 | 79.7269 | 3414.0081 | 79.7269 | 8472.5049 | 11886.513
| 76722023 | 2034 | OYN001 | 0 | 0 | 79.7269 | 3414.0081 | 79.7269 | 8472.5049 | 11886.513
| 199358270 | 2023 | OYN001 | 0 | 0 | 0 | 0 | 0 | 7733.8916 | 7733.8916
| 199358270 | 2024 | OYN001 | 0 | 0 | 0 | 0 | 0 | 7733.8916 | 7733.8916
| 199358270 | 2025 | OYN001 | 0 | 0 | 0 | 0 | 0 | 7733.8916 | 7733.8916
| 199358270 | 2026 | OYN001 | 0 | 0 | 0 | 0 | 0 | 7733.8916 | 7733.8916
| 199358270 | 2027 | OYN001 | 0 | 0 | 0.26376 | 11.2947 | 0.26376 | 7733.8916 | 7745.1863
| 199358270 | 2028 | OYN001 | 0 | 0 | 9.9484 | 426.0023 | 9.9484 | 7733.8916 | 8159.8939
| 199358270 | 2029 | OYN001 | 0 | 0 | 31.9183 | 1366.7811 | 31.9183 | 7733.8916 | 9100.6727
| 199358270 | 2030 | OYN001 | 0 | 0 | 95.2387 | 4078.2457 | 95.2387 | 7733.8916 | 11812.1373
| 199358270 | 2031 | OYN001 | 0 | 0 | 390.1293 | 16705.8394 | 390.1293 | 7733.8916 | 24439.731
| 199358270 | 2032 | OYN001 | 0 | 0 | 390.1293 | 16705.8394 | 390.1293 | 7733.8916 | 24439.731
| 199358270 | 2033 | OYN001 | 0 | 0 | 390.1293 | 16705.8394 | 390.1293 | 7733.8916 | 24439.731
| 199358270 | 2034 | OYN001 | 0 | 0 | 390.1293 | 16705.8394 | 390.1293 | 7733.8916 | 24439.731
| 20064499 | 2023 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7195.2085 | 7195.2085
| 20064499 | 2024 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7195.2085 | 7195.2085
| 20064499 | 2025 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7195.2085 | 7195.2085
| 20064499 | 2026 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7195.2085 | 7195.2085
| 20064499 | 2027 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7195.2085 | 7195.2085
| 20064499 | 2028 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7195.2085 | 7195.2085
| 20064499 | 2029 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7195.2085 | 7195.2085
| 20064499 | 2030 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7195.2085 | 7195.2085
| 20064499 | 2031 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7195.2085 | 7195.2085
| 20064499 | 2032 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7195.2085 | 7195.2085
| 20064499 | 2033 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7195.2085 | 7195.2085
| 20064499 | 2034 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7195.2085 | 7195.2085
| 20064921 | 2023 | OYN003 | 0 | 0 | 0 | 0 | 0 | 1947.6069 | 1947.6069
| 20064921 | 2024 | OYN003 | 0 | 0 | 0 | 0 | 0 | 1947.6069 | 1947.6069
| 20064921 | 2025 | OYN003 | 0 | 0 | 0 | 0 | 0 | 1947.6069 | 1947.6069
| 20064921 | 2026 | OYN003 | 0 | 0 | 0 | 0 | 0 | 1947.6069 | 1947.6069
| 20064921 | 2027 | OYN003 | 0 | 0 | 0 | 0 | 0 | 1947.6069 | 1947.6069
| 20064921 | 2028 | OYN003 | 0 | 0 | 0 | 0 | 0 | 1947.6069 | 1947.6069
| 20064921 | 2029 | OYN003 | 0 | 0 | 0 | 0 | 0 | 1947.6069 | 1947.6069
| 20064921 | 2030 | OYN003 | 0 | 0 | 0 | 0 | 0 | 1947.6069 | 1947.6069
| 20064921 | 2031 | OYN003 | 0 | 0 | 0 | 0 | 0 | 1947.6069 | 1947.6069
| 20064921 | 2032 | OYN003 | 0 | 0 | 0 | 0 | 0 | 1947.6069 | 1947.6069
| 20064921 | 2033 | OYN003 | 0 | 0 | 0 | 0 | 0 | 1947.6069 | 1947.6069
| 20064921 | 2034 | OYN003 | 0 | 0 | 0 | 0 | 0 | 1947.6069 | 1947.6069
| 20075900 | 2023 | OYN003 | 0 | 0 | 0 | 0 | 0 | 14506.7585 | 14506.7585
| 20075900 | 2024 | OYN003 | 0 | 0 | 0 | 0 | 0 | 14506.7585 | 14506.7585
| 20075900 | 2025 | OYN003 | 0 | 0 | 0 | 0 | 0 | 14506.7585 | 14506.7585
| 20075900 | 2026 | OYN003 | 0 | 0 | 0 | 0 | 0 | 14506.7585 | 14506.7585
| 20075900 | 2027 | OYN003 | 0 | 0 | 0 | 0 | 0 | 14506.7585 | 14506.7585
| 20075900 | 2028 | OYN003 | 0 | 0 | 0 | 0 | 0 | 14506.7585 | 14506.7585
| 20075900 | 2029 | OYN003 | 0 | 0 | 0 | 0 | 0 | 14506.7585 | 14506.7585
| 20075900 | 2030 | OYN003 | 0 | 0 | 0 | 0 | 0 | 14506.7585 | 14506.7585
| 20075900 | 2031 | OYN003 | 0 | 0 | 0 | 0 | 0 | 14506.7585 | 14506.7585
| 20075900 | 2032 | OYN003 | 0 | 0 | 0 | 0 | 0 | 14506.7585 | 14506.7585
| 20075900 | 2033 | OYN003 | 0 | 0 | 0 | 0 | 0 | 14506.7585 | 14506.7585
| 20075900 | 2034 | OYN003 | 0 | 0 | 0 | 0 | 0 | 14506.7585 | 14506.7585
| 20076061 | 2023 | OYN003 | 0 | 0 | 7215.1279 | 308961.0629 | 7215.1279 | 24767.3419 | 333728.4048
| 20076061 | 2024 | OYN003 | 0 | 0 | 7164.7123 | 306802.2022 | 7164.7123 | 24767.3419 | 331569.544
| 20076061 | 2025 | OYN003 | 0 | 0 | 7064.7421 | 302521.35 | 7064.7421 | 24767.3419 | 327288.6919
| 20076061 | 2026 | OYN003 | 0 | 0 | 6387.9318 | 273539.4642 | 6387.9318 | 24767.3419 | 298306.8061
| 20076061 | 2027 | OYN003 | 0 | 0 | 6254.1426 | 267810.4385 | 6254.1426 | 24767.3419 | 292577.7804
| 20076061 | 2028 | OYN003 | 0 | 0 | 6489.1113 | 277872.1011 | 6489.1113 | 24767.3419 | 302639.443
| 20076061 | 2029 | OYN003 | 0 | 0 | 6385.5731 | 273438.4621 | 6385.5731 | 24767.3419 | 298205.804
| 20076061 | 2030 | OYN003 | 0 | 0 | 5937.7145 | 254260.577 | 5937.7145 | 24767.3419 | 279027.9189
| 20076061 | 2031 | OYN003 | 0 | 0 | 5798.7597 | 248310.3554 | 5798.7597 | 24767.3419 | 273077.6972
| 20076061 | 2032 | OYN003 | 0 | 0 | 5642.1267 | 241603.1282 | 5642.1267 | 24767.3419 | 266370.4701
| 20076061 | 2033 | OYN003 | 0 | 0 | 5548.9194 | 237611.8719 | 5548.9194 | 24767.3419 | 262379.2138
| 20076061 | 2034 | OYN003 | 0 | 0 | 5341.3656 | 228724.1521 | 5341.3656 | 24767.3419 | 253491.494
| 20076178 | 2023 | OYN003 | 0 | 0 | 0 | 0 | 0 | 17313.1201 | 17313.1201
| 20076178 | 2024 | OYN003 | 0 | 0 | 0 | 0 | 0 | 17313.1201 | 17313.1201
| 20076178 | 2025 | OYN003 | 0 | 0 | 0 | 0 | 0 | 17313.1201 | 17313.1201
| 20076178 | 2026 | OYN003 | 0 | 0 | 0 | 0 | 0 | 17313.1201 | 17313.1201
| 20076178 | 2027 | OYN003 | 0 | 0 | 0 | 0 | 0 | 17313.1201 | 17313.1201
| 20076178 | 2028 | OYN003 | 0 | 0 | 0 | 0 | 0 | 17313.1201 | 17313.1201
| 20076178 | 2029 | OYN003 | 23.6921 | 0.040533 | 0 | 0 | 23.6921 | 17313.1201 | 17313.1606
| 20076178 | 2030 | OYN003 | 796.5969 | 2.2796 | 0 | 0 | 796.5969 | 17313.1201 | 17315.3997
| 20076178 | 2031 | OYN003 | 2493.7653 | 18.5952 | 0 | 0 | 2493.7653 | 17313.1201 | 17331.7153
| 20076178 | 2032 | OYN003 | 2698.4042 | 35.3893 | 0 | 0 | 2698.4042 | 17313.1201 | 17348.5094
| 20076178 | 2033 | OYN003 | 3123.7353 | 80.8132 | 0 | 0 | 3123.7353 | 17313.1201 | 17393.9333
| 20076178 | 2034 | OYN003 | 3559.138 | 112.173 | 0 | 0 | 3559.138 | 17313.1201 | 17425.2931
| 20625464 | 2023 | OYN003 | 3.7375 | 0 | 0 | 0 | 3.7375 | 21531.0458 | 21531.0458
| 20625464 | 2024 | OYN003 | 375.3035 | 4.7962 | 0 | 0 | 375.3035 | 21531.0458 | 21535.842
| 20625464 | 2025 | OYN003 | 388.2212 | 4.662 | 0 | 0 | 388.2212 | 21531.0458 | 21535.7078
| 20625464 | 2026 | OYN003 | 1667.3933 | 9.5457 | 0 | 0 | 1667.3933 | 21531.0458 | 21540.5915
| 20625464 | 2027 | OYN003 | 1873.9616 | 11.0658 | 0 | 0 | 1873.9616 | 21531.0458 | 21542.1116
| 20625464 | 2028 | OYN003 | 3955.2313 | 27.6296 | 0 | 0 | 3955.2313 | 21531.0458 | 21558.6754
| 20625464 | 2029 | OYN003 | 4196.3585 | 20.5571 | 0 | 0 | 4196.3585 | 21531.0458 | 21551.6029
| 20625464 | 2030 | OYN003 | 5070.3 | 33.7267 | 0 | 0 | 5070.3 | 21531.0458 | 21564.7725
| 20625464 | 2031 | OYN003 | 5685.2336 | 61.9202 | 0 | 0 | 5685.2336 | 21531.0458 | 21592.966
| 20625464 | 2032 | OYN003 | 6128.967 | 120.062 | 0 | 0 | 6128.967 | 21531.0458 | 21651.1078
| 20625464 | 2033 | OYN003 | 6185.5182 | 204.1265 | 0 | 0 | 6185.5182 | 21531.0458 | 21735.1723
| 20625464 | 2034 | OYN003 | 6284.1399 | 250.8028 | 0 | 0 | 6284.1399 | 21531.0458 | 21781.8486
| 41093522 | 2023 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7592.7325 | 7592.7325
| 41093522 | 2024 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7592.7325 | 7592.7325
| 41093522 | 2025 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7592.7325 | 7592.7325
| 41093522 | 2026 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7592.7325 | 7592.7325
| 41093522 | 2027 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7592.7325 | 7592.7325
| 41093522 | 2028 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7592.7325 | 7592.7325
| 41093522 | 2029 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7592.7325 | 7592.7325
| 41093522 | 2030 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7592.7325 | 7592.7325
| 41093522 | 2031 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7592.7325 | 7592.7325
| 41093522 | 2032 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7592.7325 | 7592.7325
| 41093522 | 2033 | OYN003 | 0 | 0 | 0 | 0 | 0 | 7592.7325 | 7592.7325
| 41093522 | 2034 | OYN003 | 2.491 | 0.0538 | 0 | 0 | 2.491 | 7592.7325 | 7592.7863
| 155682571 | 2023 | OYN003 | 0 | 0 | 47.3856 | 2029.1117 | 47.3856 | 24340.3828 | 26369.4945
| 155682571 | 2024 | OYN003 | 0 | 0 | 43.4906 | 1862.3244 | 43.4906 | 24340.3828 | 26202.7072
| 155682571 | 2025 | OYN003 | 0 | 0 | 38.2025 | 1635.8798 | 38.2025 | 24340.3828 | 25976.2626
| 155682571 | 2026 | OYN003 | 0 | 0 | 17.6575 | 756.1165 | 17.6575 | 24340.3828 | 25096.4993
| 155682571 | 2027 | OYN003 | 0 | 0 | 13.856 | 593.3322 | 13.856 | 24340.3828 | 24933.715
| 155682571 | 2028 | OYN003 | 0 | 0 | 22.0708 | 945.1013 | 22.0708 | 24340.3828 | 25285.4841
| 155682571 | 2029 | OYN003 | 0 | 0 | 21.4446 | 918.2846 | 21.4446 | 24340.3828 | 25258.6674
| 155682571 | 2030 | OYN003 | 0 | 0 | 12.2457 | 524.3775 | 12.2457 | 24340.3828 | 24864.7603
| 155682571 | 2031 | OYN003 | 0 | 0 | 10.7219 | 459.1254 | 10.7219 | 24340.3828 | 24799.5082
| 155682571 | 2032 | OYN003 | 0 | 0 | 10.587 | 453.3474 | 10.587 | 24340.3828 | 24793.7302
| 155682571 | 2033 | OYN003 | 0 | 0 | 8.7911 | 376.4457 | 8.7911 | 24340.3828 | 24716.8285
| 155682571 | 2034 | OYN003 | 0 | 0 | 8.3974 | 359.5894 | 8.3974 | 24340.3828 | 24699.9722
| 162750718 | 2023 | OYN003 | 0 | 0 | 0 | 0 | 0 | 3407.296 | 3407.296
| 162750718 | 2024 | OYN003 | 0 | 0 | 0 | 0 | 0 | 3407.296 | 3407.296
| 162750718 | 2025 | OYN003 | 0 | 0 | 0 | 0 | 0 | 3407.296 | 3407.296
| 162750718 | 2026 | OYN003 | 0 | 0 | 0 | 0 | 0 | 3407.296 | 3407.296
| 162750718 | 2027 | OYN003 | 0 | 0 | 0 | 0 | 0 | 3407.296 | 3407.296
| 162750718 | 2028 | OYN003 | 0 | 0 | 0 | 0 | 0 | 3407.296 | 3407.296
| 162750718 | 2029 | OYN003 | 0 | 0 | 0 | 0 | 0 | 3407.296 | 3407.296
| 162750718 | 2030 | OYN003 | 0 | 0 | 0 | 0 | 0 | 3407.296 | 3407.296
| 162750718 | 2031 | OYN003 | 0 | 0 | 0 | 0 | 0 | 3407.296 | 3407.296
| 162750718 | 2032 | OYN003 | 0 | 0 | 0 | 0 | 0 | 3407.296 | 3407.296
| 162750718 | 2033 | OYN003 | 0 | 0 | 0 | 0 | 0 | 3407.296 | 3407.296
| 162750718 | 2034 | OYN003 | 0 | 0 | 0 | 0 | 0 | 3407.296 | 3407.296
| 19892268 | 2023 | PLD001 | 0 | 0 | 0 | 0 | 0 | 1065.7012 | 1065.7012
| 19892268 | 2024 | PLD001 | 0 | 0 | 0 | 0 | 0 | 1065.7012 | 1065.7012
| 19892268 | 2025 | PLD001 | 0 | 0 | 0 | 0 | 0 | 1065.7012 | 1065.7012
| 19892268 | 2026 | PLD001 | 0 | 0 | 0 | 0 | 0 | 1065.7012 | 1065.7012
| 19892268 | 2027 | PLD001 | 0 | 0 | 0 | 0 | 0 | 1065.7012 | 1065.7012
| 19892268 | 2028 | PLD001 | 8.1983 | 0.015803 | 0 | 0 | 8.1983 | 1065.7012 | 1065.717
| 19892268 | 2029 | PLD001 | 320.7242 | 0.49661 | 0 | 0 | 320.7242 | 1065.7012 | 1066.1979
| 19892268 | 2030 | PLD001 | 648.6908 | 0.74238 | 0 | 0 | 648.6908 | 1065.7012 | 1066.4436
| 19892268 | 2031 | PLD001 | 3226.8748 | 17.3625 | 0 | 0 | 3226.8748 | 1065.7012 | 1083.0637
| 19892268 | 2032 | PLD001 | 5675.0121 | 63.5978 | 0 | 0 | 5675.0121 | 1065.7012 | 1129.2991
| 19892268 | 2033 | PLD001 | 6641.9323 | 168.4239 | 0 | 0 | 6641.9323 | 1065.7012 | 1234.1252
| 19892268 | 2034 | PLD001 | 6641.9323 | 168.4239 | 0 | 0 | 6641.9323 | 1065.7012 | 1234.1252
| 19896675 | 2023 | PLD001 | 0 | 0 | 0 | 0 | 0 | 459.7424 | 459.7424
| 19896675 | 2024 | PLD001 | 0 | 0 | 0 | 0 | 0 | 459.7424 | 459.7424
| 19896675 | 2025 | PLD001 | 0 | 0 | 0 | 0 | 0 | 459.7424 | 459.7424
| 19896675 | 2026 | PLD001 | 0 | 0 | 0 | 0 | 0 | 459.7424 | 459.7424
| 19896675 | 2027 | PLD001 | 0 | 0 | 0 | 0 | 0 | 459.7424 | 459.7424
| 19896675 | 2028 | PLD001 | 152.2791 | 3.0501 | 0 | 0 | 152.2791 | 459.7424 | 462.7925
| 19896675 | 2029 | PLD001 | 154.5416 | 2.4237 | 0 | 0 | 154.5416 | 459.7424 | 462.166
| 19896675 | 2030 | PLD001 | 111.4813 | 2.164 | 0 | 0 | 111.4813 | 459.7424 | 461.9064
| 19896675 | 2031 | PLD001 | 1379.0972 | 32.962 | 0 | 0 | 1379.0972 | 459.7424 | 492.7043
| 19896675 | 2032 | PLD001 | 1232.3175 | 45.9645 | 0 | 0 | 1232.3175 | 459.7424 | 505.7069
| 19896675 | 2033 | PLD001 | 894.0264 | 50.9794 | 0 | 0 | 894.0264 | 459.7424 | 510.7217
| 19896675 | 2034 | PLD001 | 894.0264 | 50.9794 | 0 | 0 | 894.0264 | 459.7424 | 510.7217
| 19896869 | 2023 | PLD001 | 0 | 0 | 0 | 0 | 0 | 1648.7959 | 1648.7959
| 19896869 | 2024 | PLD001 | 0 | 0 | 0 | 0 | 0 | 1648.7959 | 1648.7959
| 19896869 | 2025 | PLD001 | 0 | 0 | 0 | 0 | 0 | 1648.7959 | 1648.7959
| 19896869 | 2026 | PLD001 | 0 | 0 | 0 | 0 | 0 | 1648.7959 | 1648.7959
| 19896869 | 2027 | PLD001 | 0 | 0 | 0 | 0 | 0 | 1648.7959 | 1648.7959
| 19896869 | 2028 | PLD001 | 0 | 0 | 0.11753 | 4.9572 | 0.11753 | 1648.7959 | 1653.7531
| 19896869 | 2029 | PLD001 | 0 | 0 | 14.9562 | 630.8163 | 14.9562 | 1648.7959 | 2279.6121
| 19896869 | 2030 | PLD001 | 0 | 0 | 2149.0377 | 90640.9378 | 2149.0377 | 1648.7959 | 92289.7336
| 19896869 | 2031 | PLD001 | 0 | 0 | 778.0675 | 32816.904 | 778.0675 | 1648.7959 | 34465.6999
| 19896869 | 2032 | PLD001 | 0 | 0 | 3030.0899 | 127801.4732 | 3030.0899 | 1648.7959 | 129450.269
| 19896869 | 2033 | PLD001 | 0 | 0 | 5482.1223 | 231221.955 | 5482.1223 | 1648.7959 | 232870.7508
| 19896869 | 2034 | PLD001 | 0 | 0 | 5482.1223 | 231221.955 | 5482.1223 | 1648.7959 | 232870.7508
| 19897943 | 2023 | PLD001 | 819.6837 | 0 | 0 | 0 | 819.6837 | 1201.8443 | 1201.8443
| 19897943 | 2024 | PLD001 | 829.3197 | 19.3209 | 0 | 0 | 829.3197 | 1201.8443 | 1221.1652
| 19897943 | 2025 | PLD001 | 848.5578 | 21.3782 | 0 | 0 | 848.5578 | 1201.8443 | 1223.2225
| 19897943 | 2026 | PLD001 | 2787.9716 | 34.6545 | 0 | 0 | 2787.9716 | 1201.8443 | 1236.4988
| 19897943 | 2027 | PLD001 | 8168.4946 | 140.1476 | 0 | 0 | 8168.4946 | 1201.8443 | 1341.9919
| 19897943 | 2028 | PLD001 | 11967.5799 | 224.8698 | 0 | 0 | 11967.5799 | 1201.8443 | 1426.7142
| 19897943 | 2029 | PLD001 | 11855.5654 | 178.9677 | 0 | 0 | 11855.5654 | 1201.8443 | 1380.8121
| 19897943 | 2030 | PLD001 | 10448.8737 | 151.4726 | 0.63 | 26.5717 | 10449.5037 | 1201.8443 | 1379.8886
| 19897943 | 2031 | PLD001 | 23105.1916 | 408.4892 | 0 | 0 | 23105.1916 | 1201.8443 | 1610.3336
| 19897943 | 2032 | PLD001 | 20996.6309 | 547.1654 | 27.0476 | 1140.7995 | 21023.6785 | 1201.8443 | 2889.8092
| 19897943 | 2033 | PLD001 | 19301.3142 | 774.1844 | 401.4908 | 16933.8573 | 19702.8049 | 1201.8443 | 18909.8861
| 19897943 | 2034 | PLD001 | 19301.3142 | 774.1844 | 401.4908 | 16933.8573 | 19702.8049 | 1201.8443 | 18909.8861
| 19898910 | 2023 | PLD001 | 0 | 0 | 0 | 0 | 0 | 232.227 | 232.227
| 19898910 | 2024 | PLD001 | 0 | 0 | 0 | 0 | 0 | 232.227 | 232.227
| 19898910 | 2025 | PLD001 | 0 | 0 | 0 | 0 | 0 | 232.227 | 232.227
| 19898910 | 2026 | PLD001 | 0 | 0 | 0 | 0 | 0 | 232.227 | 232.227
| 19898910 | 2027 | PLD001 | 0 | 0 | 0 | 0 | 0 | 232.227 | 232.227
| 19898910 | 2028 | PLD001 | 0 | 0 | 0 | 0 | 0 | 232.227 | 232.227
| 19898910 | 2029 | PLD001 | 0 | 0 | 0.015178 | 0.64019 | 0.015178 | 232.227 | 232.8672
| 19898910 | 2030 | PLD001 | 0 | 0 | 219.2674 | 9248.139 | 219.2674 | 232.227 | 9480.366
| 19898910 | 2031 | PLD001 | 0 | 0 | 15.3949 | 649.3176 | 15.3949 | 232.227 | 881.5446
| 19898910 | 2032 | PLD001 | 0 | 0 | 296.2299 | 12494.2216 | 296.2299 | 232.227 | 12726.4486
| 19898910 | 2033 | PLD001 | 0 | 0 | 1135.9775 | 47912.6387 | 1135.9775 | 232.227 | 48144.8657
| 19898910 | 2034 | PLD001 | 0 | 0 | 1135.9775 | 47912.6387 | 1135.9775 | 232.227 | 48144.8657
| 19899321 | 2023 | PLD001 | 0 | 0 | 0 | 0 | 0 | 485.6785 | 485.6785
| 19899321 | 2024 | PLD001 | 0 | 0 | 0 | 0 | 0 | 485.6785 | 485.6785
| 19899321 | 2025 | PLD001 | 0 | 0 | 0 | 0 | 0 | 485.6785 | 485.6785
| 19899321 | 2026 | PLD001 | 0 | 0 | 0 | 0 | 0 | 485.6785 | 485.6785
| 19899321 | 2027 | PLD001 | 0 | 0 | 0 | 0 | 0 | 485.6785 | 485.6785
| 19899321 | 2028 | PLD001 | 0 | 0 | 0 | 0 | 0 | 485.6785 | 485.6785
| 19899321 | 2029 | PLD001 | 0 | 0 | 3.5432 | 149.444 | 3.5432 | 485.6785 | 635.1225
| 19899321 | 2030 | PLD001 | 0 | 0 | 232.8136 | 9819.4863 | 232.8136 | 485.6785 | 10305.1648
| 19899321 | 2031 | PLD001 | 0 | 0 | 32.7449 | 1381.095 | 32.7449 | 485.6785 | 1866.7736
| 19899321 | 2032 | PLD001 | 0 | 0 | 248.7155 | 10490.1884 | 248.7155 | 485.6785 | 10975.867
| 19899321 | 2033 | PLD001 | 2.2589 | 0.087968 | 491.983 | 20750.5919 | 494.2419 | 485.6785 | 21236.3584
| 19899321 | 2034 | PLD001 | 2.2589 | 0.087968 | 491.983 | 20750.5919 | 494.2419 | 485.6785 | 21236.3584
| 19899526 | 2023 | PLD001 | 0 | 0 | 9309.42 | 392647.6281 | 9309.42 | 1340.8831 | 393988.5112
| 19899526 | 2024 | PLD001 | 0 | 0 | 13574.501 | 572537.882 | 13574.501 | 1340.8831 | 573878.7651
| 19899526 | 2025 | PLD001 | 0 | 0 | 13202.8807 | 556863.8847 | 13202.8807 | 1340.8831 | 558204.7678
| 19899526 | 2026 | PLD001 | 0 | 0 | 12424.7364 | 524043.7369 | 12424.7364 | 1340.8831 | 525384.62
| 19899526 | 2027 | PLD001 | 0 | 0 | 12150.9128 | 512494.5572 | 12150.9128 | 1340.8831 | 513835.4403
| 19899526 | 2028 | PLD001 | 0 | 0 | 12717.3201 | 536384.1716 | 12717.3201 | 1340.8831 | 537725.0547
| 19899526 | 2029 | PLD001 | 0 | 0 | 15782.2063 | 665653.2692 | 15782.2063 | 1340.8831 | 666994.1523
| 19899526 | 2030 | PLD001 | 0 | 0 | 15432.9475 | 650922.4213 | 15432.9475 | 1340.8831 | 652263.3044
| 19899526 | 2031 | PLD001 | 0 | 0 | 15697.1463 | 662065.6522 | 15697.1463 | 1340.8831 | 663406.5354
| 19899526 | 2032 | PLD001 | 0 | 0 | 17145.8754 | 723169.3575 | 17145.8754 | 1340.8831 | 724510.2406
| 19899526 | 2033 | PLD001 | 0 | 0 | 16609.663 | 700553.282 | 16609.663 | 1340.8831 | 701894.1651
| 19899526 | 2034 | PLD001 | 0 | 0 | 16609.663 | 700553.282 | 16609.663 | 1340.8831 | 701894.1651
| 19900248 | 2023 | PLD001 | 3151.4672 | 0 | 0 | 0 | 3151.4672 | 1571.9567 | 1571.9567
| 19900248 | 2024 | PLD001 | 5594.2 | 144.0806 | 0 | 0 | 5594.2 | 1571.9567 | 1716.0372
| 19900248 | 2025 | PLD001 | 10580.7599 | 317.3877 | 0 | 0 | 10580.7599 | 1571.9567 | 1889.3444
| 19900248 | 2026 | PLD001 | 11026.4607 | 234.5932 | 0 | 0 | 11026.4607 | 1571.9567 | 1806.5499
| 19900248 | 2027 | PLD001 | 17908.3447 | 377.8333 | 0 | 0 | 17908.3447 | 1571.9567 | 1949.79
| 19900248 | 2028 | PLD001 | 26176.6805 | 595.0958 | 0 | 0 | 26176.6805 | 1571.9567 | 2167.0525
| 19900248 | 2029 | PLD001 | 31008.2949 | 619.6044 | 0 | 0 | 31008.2949 | 1571.9567 | 2191.5611
| 19900248 | 2030 | PLD001 | 38781.1667 | 790.1632 | 0 | 0 | 38781.1667 | 1571.9567 | 2362.1198
| 19900248 | 2031 | PLD001 | 44410.7993 | 1062.8001 | 0 | 0 | 44410.7993 | 1571.9567 | 2634.7568
| 19900248 | 2032 | PLD001 | 50184.0793 | 1540.3628 | 0 | 0 | 50184.0793 | 1571.9567 | 3112.3195
| 19900248 | 2033 | PLD001 | 55515.1238 | 2492.3735 | 0 | 0 | 55515.1238 | 1571.9567 | 4064.3302
| 19900248 | 2034 | PLD001 | 55515.1238 | 2492.3735 | 0 | 0 | 55515.1238 | 1571.9567 | 4064.3302
| 19900288 | 2023 | PLD001 | 0 | 0 | 0 | 0 | 0 | 466.5049 | 466.5049
| 19900288 | 2024 | PLD001 | 0 | 0 | 0 | 0 | 0 | 466.5049 | 466.5049
| 19900288 | 2025 | PLD001 | 0 | 0 | 0 | 0 | 0 | 466.5049 | 466.5049
| 19900288 | 2026 | PLD001 | 0 | 0 | 0 | 0 | 0 | 466.5049 | 466.5049
| 19900288 | 2027 | PLD001 | 0 | 0 | 0 | 0 | 0 | 466.5049 | 466.5049
| 19900288 | 2028 | PLD001 | 0 | 0 | 0 | 0 | 0 | 466.5049 | 466.5049
| 19900288 | 2029 | PLD001 | 0 | 0 | 0 | 0 | 0 | 466.5049 | 466.5049
| 19900288 | 2030 | PLD001 | 0 | 0 | 0 | 0 | 0 | 466.5049 | 466.5049
| 19900288 | 2031 | PLD001 | 0 | 0 | 0 | 0 | 0 | 466.5049 | 466.5049
| 19900288 | 2032 | PLD001 | 48.3734 | 0.14384 | 0 | 0 | 48.3734 | 466.5049 | 466.6487
| 19900288 | 2033 | PLD001 | 90.2401 | 1.5737 | 0 | 0 | 90.2401 | 466.5049 | 468.0786
| 19900288 | 2034 | PLD001 | 90.2401 | 1.5737 | 0 | 0 | 90.2401 | 466.5049 | 468.0786
| 20491162 | 2023 | PLD001 | 0 | 0 | 0 | 0 | 0 | 914.3005 | 914.3005
| 20491162 | 2024 | PLD001 | 0 | 0 | 0 | 0 | 0 | 914.3005 | 914.3005
| 20491162 | 2025 | PLD001 | 0 | 0 | 0 | 0 | 0 | 914.3005 | 914.3005
| 20491162 | 2026 | PLD001 | 0 | 0 | 0 | 0 | 0 | 914.3005 | 914.3005
| 20491162 | 2027 | PLD001 | 0 | 0 | 0 | 0 | 0 | 914.3005 | 914.3005
| 20491162 | 2028 | PLD001 | 0 | 0 | 0 | 0 | 0 | 914.3005 | 914.3005
| 20491162 | 2029 | PLD001 | 0 | 0 | 4.152 | 175.1215 | 4.152 | 914.3005 | 1089.422
| 20491162 | 2030 | PLD001 | 0 | 0 | 591.5032 | 24948.1 | 591.5032 | 914.3005 | 25862.4005
| 20491162 | 2031 | PLD001 | 0 | 0 | 61.7911 | 2606.1892 | 61.7911 | 914.3005 | 3520.4896
| 20491162 | 2032 | PLD001 | 0 | 0 | 468.6645 | 19767.0735 | 468.6645 | 914.3005 | 20681.374
| 20491162 | 2033 | PLD001 | 0 | 0 | 904.5044 | 38149.6921 | 904.5044 | 914.3005 | 39063.9926
| 20491162 | 2034 | PLD001 | 0 | 0 | 904.5044 | 38149.6921 | 904.5044 | 914.3005 | 39063.9926
| 20597302 | 2023 | PLD001 | 0 | 0 | 0 | 0 | 0 | 350.8972 | 350.8972
| 20597302 | 2024 | PLD001 | 0 | 0 | 0 | 0 | 0 | 350.8972 | 350.8972
| 20597302 | 2025 | PLD001 | 0 | 0 | 0 | 0 | 0 | 350.8972 | 350.8972
| 20597302 | 2026 | PLD001 | 0 | 0 | 0 | 0 | 0 | 350.8972 | 350.8972
| 20597302 | 2027 | PLD001 | 0 | 0 | 0 | 0 | 0 | 350.8972 | 350.8972
| 20597302 | 2028 | PLD001 | 0 | 0 | 0.83028 | 35.019 | 0.83028 | 350.8972 | 385.9162
| 20597302 | 2029 | PLD001 | 0 | 0 | 24.6157 | 1038.2293 | 24.6157 | 350.8972 | 1389.1266
| 20597302 | 2030 | PLD001 | 0 | 0 | 3269.1015 | 137882.3766 | 3269.1015 | 350.8972 | 138233.2738
| 20597302 | 2031 | PLD001 | 0 | 0 | 992.7151 | 41870.1927 | 992.7151 | 350.8972 | 42221.0899
| 20597302 | 2032 | PLD001 | 0 | 0 | 3252.4568 | 137180.3459 | 3252.4568 | 350.8972 | 137531.2431
| 20597302 | 2033 | PLD001 | 0 | 0 | 4316.3334 | 182051.9495 | 4316.3334 | 350.8972 | 182402.8467
| 20597302 | 2034 | PLD001 | 0 | 0 | 4316.3334 | 182051.9495 | 4316.3334 | 350.8972 | 182402.8467
| 20623470 | 2023 | PLD001 | 0 | 0 | 10943.772 | 461580.4299 | 10943.772 | 2874.997 | 464455.4269
| 20623470 | 2024 | PLD001 | 0 | 0 | 11397.6156 | 480722.4001 | 11397.6156 | 2874.997 | 483597.3971
| 20623470 | 2025 | PLD001 | 0 | 0 | 10907.5064 | 460050.8405 | 10907.5064 | 2874.997 | 462925.8375
| 20623470 | 2026 | PLD001 | 0 | 0 | 10097.8383 | 425901.1044 | 10097.8383 | 2874.997 | 428776.1014
| 20623470 | 2027 | PLD001 | 0 | 0 | 9746.7456 | 411092.905 | 9746.7456 | 2874.997 | 413967.902
| 20623470 | 2028 | PLD001 | 0 | 0 | 9774.8531 | 412278.4091 | 9774.8531 | 2874.997 | 415153.4061
| 20623470 | 2029 | PLD001 | 0 | 0 | 9811.6686 | 413831.1943 | 9811.6686 | 2874.997 | 416706.1913
| 20623470 | 2030 | PLD001 | 0 | 0 | 9258.7057 | 390508.626 | 9258.7057 | 2874.997 | 393383.6229
| 20623470 | 2031 | PLD001 | 0 | 0 | 9315.2101 | 392891.8362 | 9315.2101 | 2874.997 | 395766.8332
| 20623470 | 2032 | PLD001 | 0 | 0 | 9931.2688 | 418875.6255 | 9931.2688 | 2874.997 | 421750.6225
| 20623470 | 2033 | PLD001 | 2.3927 | 0.017453 | 9817.5798 | 414080.5118 | 9819.9725 | 2874.997 | 416955.5262
| 20623470 | 2034 | PLD001 | 2.3927 | 0.017453 | 9817.5798 | 414080.5118 | 9819.9725 | 2874.997 | 416955.5262
| 20662562 | 2023 | PLD001 | 0 | 0 | 0 | 0 | 0 | 439.992 | 439.992
| 20662562 | 2024 | PLD001 | 0 | 0 | 0 | 0 | 0 | 439.992 | 439.992
| 20662562 | 2025 | PLD001 | 0 | 0 | 0 | 0 | 0 | 439.992 | 439.992
| 20662562 | 2026 | PLD001 | 0 | 0 | 0 | 0 | 0 | 439.992 | 439.992
| 20662562 | 2027 | PLD001 | 0 | 0 | 0 | 0 | 0 | 439.992 | 439.992
| 20662562 | 2028 | PLD001 | 0 | 0 | 0 | 0 | 0 | 439.992 | 439.992
| 20662562 | 2029 | PLD001 | 9.7124 | 0.013072 | 0 | 0 | 9.7124 | 439.992 | 440.0051
| 20662562 | 2030 | PLD001 | 127.8575 | 0.029654 | 0 | 0 | 127.8575 | 439.992 | 440.0217
| 20662562 | 2031 | PLD001 | 437.4402 | 0.9737 | 0 | 0 | 437.4402 | 439.992 | 440.9657
| 20662562 | 2032 | PLD001 | 1779.101 | 15.8561 | 0 | 0 | 1779.101 | 439.992 | 455.8482
| 20662562 | 2033 | PLD001 | 2382.67 | 55.107 | 0 | 0 | 2382.67 | 439.992 | 495.0991
| 20662562 | 2034 | PLD001 | 2382.67 | 55.107 | 0 | 0 | 2382.67 | 439.992 | 495.0991
| 95142700 | 2023 | PLD001 | 0 | 0 | 0 | 0 | 0 | 1042.2902 | 1042.2902
| 95142700 | 2024 | PLD001 | 0 | 0 | 0 | 0 | 0 | 1042.2902 | 1042.2902
| 95142700 | 2025 | PLD001 | 0 | 0 | 0 | 0 | 0 | 1042.2902 | 1042.2902
| 95142700 | 2026 | PLD001 | 0 | 0 | 0 | 0 | 0 | 1042.2902 | 1042.2902
| 95142700 | 2027 | PLD001 | 0 | 0 | 0 | 0 | 0 | 1042.2902 | 1042.2902
| 95142700 | 2028 | PLD001 | 38.8874 | 0.094216 | 0 | 0 | 38.8874 | 1042.2902 | 1042.3844
| 95142700 | 2029 | PLD001 | 193.0433 | 0.64223 | 0 | 0 | 193.0433 | 1042.2902 | 1042.9324
| 95142700 | 2030 | PLD001 | 296.2222 | 0.61435 | 0 | 0 | 296.2222 | 1042.2902 | 1042.9045
| 95142700 | 2031 | PLD001 | 535.9898 | 3.4796 | 0 | 0 | 535.9898 | 1042.2902 | 1045.7697
| 95142700 | 2032 | PLD001 | 2807.5221 | 35.1139 | 0 | 0 | 2807.5221 | 1042.2902 | 1077.4041
| 95142700 | 2033 | PLD001 | 3162.7085 | 86.1577 | 0 | 0 | 3162.7085 | 1042.2902 | 1128.4479
| 95142700 | 2034 | PLD001 | 3162.7085 | 86.1577 | 0 | 0 | 3162.7085 | 1042.2902 | 1128.4479
| 163099244 | 2023 | PLD001 | 0 | 0 | 403.4177 | 17015.1313 | 403.4177 | 601.4308 | 17616.5621
| 163099244 | 2024 | PLD001 | 0 | 0 | 467.1055 | 19701.3212 | 467.1055 | 601.4308 | 20302.752
| 163099244 | 2025 | PLD001 | 0 | 0 | 411.2744 | 17346.5054 | 411.2744 | 601.4308 | 17947.9362
| 163099244 | 2026 | PLD001 | 0 | 0 | 318.2057 | 13421.106 | 318.2057 | 601.4308 | 14022.5368
| 163099244 | 2027 | PLD001 | 0 | 0 | 274.9948 | 11598.58 | 274.9948 | 601.4308 | 12200.0108
| 163099244 | 2028 | PLD001 | 0 | 0 | 268.7342 | 11334.5223 | 268.7342 | 601.4308 | 11935.9531
| 163099244 | 2029 | PLD001 | 0 | 0 | 254.2197 | 10722.3404 | 254.2197 | 601.4308 | 11323.7712
| 163099244 | 2030 | PLD001 | 0 | 0 | 216.5373 | 9132.9932 | 216.5373 | 601.4308 | 9734.424
| 163099244 | 2031 | PLD001 | 0 | 0 | 254.3071 | 10726.025 | 254.3071 | 601.4308 | 11327.4558
| 163099244 | 2032 | PLD001 | 0 | 0 | 281.4545 | 11871.0325 | 281.4545 | 601.4308 | 12472.4633
| 163099244 | 2033 | PLD001 | 0 | 0 | 316.4851 | 13348.5363 | 316.4851 | 601.4308 | 13949.9671
| 163099244 | 2034 | PLD001 | 0 | 0 | 316.4851 | 13348.5363 | 316.4851 | 601.4308 | 13949.9671
| 171177017 | 2023 | PLD001 | 0 | 0 | 0 | 0 | 0 | 348.8644 | 348.8644
| 171177017 | 2024 | PLD001 | 0 | 0 | 0 | 0 | 0 | 348.8644 | 348.8644
| 171177017 | 2025 | PLD001 | 0 | 0 | 0 | 0 | 0 | 348.8644 | 348.8644
| 171177017 | 2026 | PLD001 | 0 | 0 | 0 | 0 | 0 | 348.8644 | 348.8644
| 171177017 | 2027 | PLD001 | 0 | 0 | 0 | 0 | 0 | 348.8644 | 348.8644
| 171177017 | 2028 | PLD001 | 0 | 0 | 1.3061 | 55.0862 | 1.3061 | 348.8644 | 403.9507
| 171177017 | 2029 | PLD001 | 0 | 0 | 29.9364 | 1262.6425 | 29.9364 | 348.8644 | 1611.5069
| 171177017 | 2030 | PLD001 | 0 | 0 | 2159.069 | 91064.0314 | 2159.069 | 348.8644 | 91412.8958
| 171177017 | 2031 | PLD001 | 0 | 0 | 622.1205 | 26239.4603 | 622.1205 | 348.8644 | 26588.3248
| 171177017 | 2032 | PLD001 | 0 | 0 | 2564.6197 | 108169.1258 | 2564.6197 | 348.8644 | 108517.9902
| 171177017 | 2033 | PLD001 | 0 | 0 | 6288.6999 | 265241.346 | 6288.6999 | 348.8644 | 265590.2105
| 171177017 | 2034 | PLD001 | 0 | 0 | 6288.6999 | 265241.346 | 6288.6999 | 348.8644 | 265590.2105
| 199367719 | 2023 | PLD001 | 0 | 0 | 0 | 0 | 0 | 135.8495 | 135.8495
| 199367719 | 2024 | PLD001 | 0 | 0 | 0 | 0 | 0 | 135.8495 | 135.8495
| 199367719 | 2025 | PLD001 | 0 | 0 | 0 | 0 | 0 | 135.8495 | 135.8495
| 199367719 | 2026 | PLD001 | 0 | 0 | 0 | 0 | 0 | 135.8495 | 135.8495
| 199367719 | 2027 | PLD001 | 0 | 0 | 0 | 0 | 0 | 135.8495 | 135.8495
| 199367719 | 2028 | PLD001 | 0 | 0 | 0 | 0 | 0 | 135.8495 | 135.8495
| 199367719 | 2029 | PLD001 | 0 | 0 | 0 | 0 | 0 | 135.8495 | 135.8495
| 199367719 | 2030 | PLD001 | 0 | 0 | 0 | 0 | 0 | 135.8495 | 135.8495
| 199367719 | 2031 | PLD001 | 0 | 0 | 0 | 0 | 0 | 135.8495 | 135.8495
| 199367719 | 2032 | PLD001 | 0 | 0 | 0 | 0 | 0 | 135.8495 | 135.8495
| 199367719 | 2033 | PLD001 | 0 | 0 | 0 | 0 | 0 | 135.8495 | 135.8495
| 199367719 | 2034 | PLD001 | 0 | 0 | 0 | 0 | 0 | 135.8495 | 135.8495
| 19895285 | 2023 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1570.7953 | 1570.7953
| 19895285 | 2024 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1570.7953 | 1570.7953
| 19895285 | 2025 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1570.7953 | 1570.7953
| 19895285 | 2026 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1570.7953 | 1570.7953
| 19895285 | 2027 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1570.7953 | 1570.7953
| 19895285 | 2028 | PLD003 | 3613.1978 | 48.8964 | 0 | 0 | 3613.1978 | 1570.7953 | 1619.6917
| 19895285 | 2029 | PLD003 | 6857.2252 | 72.8407 | 0 | 0 | 6857.2252 | 1570.7953 | 1643.636
| 19895285 | 2030 | PLD003 | 6839.6009 | 78.1319 | 0 | 0 | 6839.6009 | 1570.7953 | 1648.9272
| 19895285 | 2031 | PLD003 | 6802.5726 | 101.3901 | 0 | 0 | 6802.5726 | 1570.7953 | 1672.1854
| 19895285 | 2032 | PLD003 | 6629.4201 | 146.1969 | 0 | 0 | 6629.4201 | 1570.7953 | 1716.9922
| 19895285 | 2033 | PLD003 | 6205.1841 | 208.479 | 0 | 0 | 6205.1841 | 1570.7953 | 1779.2743
| 19895285 | 2034 | PLD003 | 5819.8587 | 237.0397 | 0 | 0 | 5819.8587 | 1570.7953 | 1807.835
| 19895589 | 2023 | PLD003 | 0 | 0 | 0 | 0 | 0 | 4941.8013 | 4941.8013
| 19895589 | 2024 | PLD003 | 0 | 0 | 0 | 0 | 0 | 4941.8013 | 4941.8013
| 19895589 | 2025 | PLD003 | 0 | 0 | 0 | 0 | 0 | 4941.8013 | 4941.8013
| 19895589 | 2026 | PLD003 | 0 | 0 | 0 | 0 | 0 | 4941.8013 | 4941.8013
| 19895589 | 2027 | PLD003 | 0 | 0 | 0 | 0 | 0 | 4941.8013 | 4941.8013
| 19895589 | 2028 | PLD003 | 0 | 0 | 0 | 0 | 0 | 4941.8013 | 4941.8013
| 19895589 | 2029 | PLD003 | 0 | 0 | 0 | 0 | 0 | 4941.8013 | 4941.8013
| 19895589 | 2030 | PLD003 | 0 | 0 | 0 | 0 | 0 | 4941.8013 | 4941.8013
| 19895589 | 2031 | PLD003 | 0 | 0 | 0 | 0 | 0 | 4941.8013 | 4941.8013
| 19895589 | 2032 | PLD003 | 0 | 0 | 0 | 0 | 0 | 4941.8013 | 4941.8013
| 19895589 | 2033 | PLD003 | 0 | 0 | 0 | 0 | 0 | 4941.8013 | 4941.8013
| 19895589 | 2034 | PLD003 | 0 | 0 | 0.14822 | 6.2514 | 0.14822 | 4941.8013 | 4948.0526
| 19896286 | 2023 | PLD003 | 0 | 0 | 1.1205 | 47.2604 | 1.1205 | 1699.8724 | 1747.1328
| 19896286 | 2024 | PLD003 | 0 | 0 | 1.5516 | 65.442 | 1.5516 | 1699.8724 | 1765.3144
| 19896286 | 2025 | PLD003 | 0 | 0 | 1.5671 | 66.097 | 1.5671 | 1699.8724 | 1765.9693
| 19896286 | 2026 | PLD003 | 0 | 0 | 1.3409 | 56.5546 | 1.3409 | 1699.8724 | 1756.4269
| 19896286 | 2027 | PLD003 | 0 | 0 | 1.3783 | 58.1328 | 1.3783 | 1699.8724 | 1758.0051
| 19896286 | 2028 | PLD003 | 0 | 0 | 2.2433 | 94.6172 | 2.2433 | 1699.8724 | 1794.4896
| 19896286 | 2029 | PLD003 | 0 | 0 | 2.5876 | 109.1396 | 2.5876 | 1699.8724 | 1809.012
| 19896286 | 2030 | PLD003 | 0 | 0 | 2.1901 | 92.3713 | 2.1901 | 1699.8724 | 1792.2437
| 19896286 | 2031 | PLD003 | 0 | 0 | 2.1517 | 90.7548 | 2.1517 | 1699.8724 | 1790.6272
| 19896286 | 2032 | PLD003 | 0 | 0 | 2.5499 | 107.5483 | 2.5499 | 1699.8724 | 1807.4206
| 19896286 | 2033 | PLD003 | 0 | 0 | 3.5806 | 151.0215 | 3.5806 | 1699.8724 | 1850.8939
| 19896286 | 2034 | PLD003 | 0 | 0 | 2.1844 | 92.1343 | 2.1844 | 1699.8724 | 1792.0066
| 19896382 | 2023 | PLD003 | 0 | 0 | 0 | 0 | 0 | 466.021 | 466.021
| 19896382 | 2024 | PLD003 | 0 | 0 | 0 | 0 | 0 | 466.021 | 466.021
| 19896382 | 2025 | PLD003 | 0 | 0 | 0 | 0 | 0 | 466.021 | 466.021
| 19896382 | 2026 | PLD003 | 0 | 0 | 0 | 0 | 0 | 466.021 | 466.021
| 19896382 | 2027 | PLD003 | 0 | 0 | 0 | 0 | 0 | 466.021 | 466.021
| 19896382 | 2028 | PLD003 | 0 | 0 | 0 | 0 | 0 | 466.021 | 466.021
| 19896382 | 2029 | PLD003 | 0 | 0 | 0 | 0 | 0 | 466.021 | 466.021
| 19896382 | 2030 | PLD003 | 0 | 0 | 0 | 0 | 0 | 466.021 | 466.021
| 19896382 | 2031 | PLD003 | 0 | 0 | 0 | 0 | 0 | 466.021 | 466.021
| 19896382 | 2032 | PLD003 | 0 | 0 | 0 | 0 | 0 | 466.021 | 466.021
| 19896382 | 2033 | PLD003 | 0 | 0 | 0 | 0 | 0 | 466.021 | 466.021
| 19896382 | 2034 | PLD003 | 0 | 0 | 0 | 0 | 0 | 466.021 | 466.021
| 19903440 | 2023 | PLD003 | 0 | 0 | 306.2272 | 12915.8845 | 306.2272 | 8791.7799 | 21707.6643
| 19903440 | 2024 | PLD003 | 0 | 0 | 352.3843 | 14862.6712 | 352.3843 | 8791.7799 | 23654.4511
| 19903440 | 2025 | PLD003 | 0 | 0 | 343.5155 | 14488.6091 | 343.5155 | 8791.7799 | 23280.3889
| 19903440 | 2026 | PLD003 | 0 | 0 | 316.2846 | 13340.0793 | 316.2846 | 8791.7799 | 22131.8592
| 19903440 | 2027 | PLD003 | 0 | 0 | 313.771 | 13234.0618 | 313.771 | 8791.7799 | 22025.8416
| 19903440 | 2028 | PLD003 | 0 | 0 | 359.1222 | 15146.8582 | 359.1222 | 8791.7799 | 23938.6381
| 19903440 | 2029 | PLD003 | 0 | 0 | 383.4063 | 16171.1024 | 383.4063 | 8791.7799 | 24962.8823
| 19903440 | 2030 | PLD003 | 0 | 0 | 354.2975 | 14943.3664 | 354.2975 | 8791.7799 | 23735.1462
| 19903440 | 2031 | PLD003 | 0 | 0 | 382.086 | 16115.4155 | 382.086 | 8791.7799 | 24907.1953
| 19903440 | 2032 | PLD003 | 0 | 0 | 410.1472 | 17298.9632 | 410.1472 | 8791.7799 | 26090.743
| 19903440 | 2033 | PLD003 | 0 | 0 | 6639.0116 | 280016.6018 | 6639.0116 | 8791.7799 | 288808.3817
| 19903440 | 2034 | PLD003 | 0 | 0 | 6578.0526 | 277445.5039 | 6578.0526 | 8791.7799 | 286237.2837
| 19903623 | 2023 | PLD003 | 0 | 0 | 0 | 0 | 0 | 15303.5725 | 15303.5725
| 19903623 | 2024 | PLD003 | 0 | 0 | 0 | 0 | 0 | 15303.5725 | 15303.5725
| 19903623 | 2025 | PLD003 | 0 | 0 | 0 | 0 | 0 | 15303.5725 | 15303.5725
| 19903623 | 2026 | PLD003 | 0 | 0 | 0 | 0 | 0 | 15303.5725 | 15303.5725
| 19903623 | 2027 | PLD003 | 0 | 0 | 0 | 0 | 0 | 15303.5725 | 15303.5725
| 19903623 | 2028 | PLD003 | 0 | 0 | 0 | 0 | 0 | 15303.5725 | 15303.5725
| 19903623 | 2029 | PLD003 | 0 | 0 | 0 | 0 | 0 | 15303.5725 | 15303.5725
| 19903623 | 2030 | PLD003 | 0 | 0 | 0 | 0 | 0 | 15303.5725 | 15303.5725
| 19903623 | 2031 | PLD003 | 0 | 0 | 0 | 0 | 0 | 15303.5725 | 15303.5725
| 19903623 | 2032 | PLD003 | 0 | 0 | 0 | 0 | 0 | 15303.5725 | 15303.5725
| 19903623 | 2033 | PLD003 | 0 | 0 | 0 | 0 | 0 | 15303.5725 | 15303.5725
| 19903623 | 2034 | PLD003 | 0 | 0 | 0 | 0 | 0 | 15303.5725 | 15303.5725
| 19908858 | 2023 | PLD003 | 0 | 0 | 1.1114 | 46.8779 | 1.1114 | 3361.9044 | 3408.7823
| 19908858 | 2024 | PLD003 | 0 | 0 | 1.0098 | 42.5929 | 1.0098 | 3361.9044 | 3404.4973
| 19908858 | 2025 | PLD003 | 0 | 0 | 1.1175 | 47.1344 | 1.1175 | 3361.9044 | 3409.0388
| 19908858 | 2026 | PLD003 | 0 | 0 | 1.2809 | 54.0258 | 1.2809 | 3361.9044 | 3415.9302
| 19908858 | 2027 | PLD003 | 0 | 0 | 1.2957 | 54.65 | 1.2957 | 3361.9044 | 3416.5544
| 19908858 | 2028 | PLD003 | 0 | 0 | 0.8998 | 37.9512 | 0.8998 | 3361.9044 | 3399.8556
| 19908858 | 2029 | PLD003 | 0 | 0 | 0.97553 | 41.1454 | 0.97553 | 3361.9044 | 3403.0498
| 19908858 | 2030 | PLD003 | 0 | 0 | 11.9725 | 504.9688 | 11.9725 | 3361.9044 | 3866.8732
| 19908858 | 2031 | PLD003 | 0 | 0 | 37.2113 | 1569.4798 | 37.2113 | 3361.9044 | 4931.3842
| 19908858 | 2032 | PLD003 | 0 | 0 | 59.2807 | 2500.3102 | 59.2807 | 3361.9044 | 5862.2146
| 19908858 | 2033 | PLD003 | 0 | 0 | 366.7776 | 15469.746 | 366.7776 | 3361.9044 | 18831.6504
| 19908858 | 2034 | PLD003 | 0 | 0 | 823.1911 | 34720.1046 | 823.1911 | 3361.9044 | 38082.009
| 19908997 | 2023 | PLD003 | 0 | 0 | 216.5133 | 9131.9796 | 216.5133 | 485.9368 | 9617.9165
| 19908997 | 2024 | PLD003 | 0 | 0 | 212.1091 | 8946.2226 | 212.1091 | 485.9368 | 9432.1594
| 19908997 | 2025 | PLD003 | 0 | 0 | 225.9358 | 9529.3977 | 225.9358 | 485.9368 | 10015.3345
| 19908997 | 2026 | PLD003 | 0 | 0 | 285.3988 | 12037.3928 | 285.3988 | 485.9368 | 12523.3296
| 19908997 | 2027 | PLD003 | 0 | 0 | 1510.9453 | 63727.8239 | 1510.9453 | 485.9368 | 64213.7608
| 19908997 | 2028 | PLD003 | 0 | 0 | 1526.5771 | 64387.1341 | 1526.5771 | 485.9368 | 64873.071
| 19908997 | 2029 | PLD003 | 0 | 0 | 1520.9816 | 64151.1301 | 1520.9816 | 485.9368 | 64637.0669
| 19908997 | 2030 | PLD003 | 0 | 0 | 1565.6686 | 66035.9137 | 1565.6686 | 485.9368 | 66521.8506
| 19908997 | 2031 | PLD003 | 0 | 0 | 1506.4769 | 63539.3595 | 1506.4769 | 485.9368 | 64025.2963
| 19908997 | 2032 | PLD003 | 0 | 0 | 1546.2825 | 65218.2561 | 1546.2825 | 485.9368 | 65704.1929
| 19908997 | 2033 | PLD003 | 0 | 0 | 1907.0778 | 80435.6826 | 1907.0778 | 485.9368 | 80921.6195
| 19908997 | 2034 | PLD003 | 0 | 0 | 3067.1152 | 129363.1093 | 3067.1152 | 485.9368 | 129849.0461
| 19909236 | 2023 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1483.4572 | 1483.4572
| 19909236 | 2024 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1483.4572 | 1483.4572
| 19909236 | 2025 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1483.4572 | 1483.4572
| 19909236 | 2026 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1483.4572 | 1483.4572
| 19909236 | 2027 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1483.4572 | 1483.4572
| 19909236 | 2028 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1483.4572 | 1483.4572
| 19909236 | 2029 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1483.4572 | 1483.4572
| 19909236 | 2030 | PLD003 | 0 | 0 | 0.93167 | 39.2953 | 0.93167 | 1483.4572 | 1522.7525
| 19909236 | 2031 | PLD003 | 0 | 0 | 4.2274 | 178.2992 | 4.2274 | 1483.4572 | 1661.7564
| 19909236 | 2032 | PLD003 | 0 | 0 | 7.5088 | 316.7006 | 7.5088 | 1483.4572 | 1800.1578
| 19909236 | 2033 | PLD003 | 0 | 0 | 60.1106 | 2535.3134 | 60.1106 | 1483.4572 | 4018.7706
| 19909236 | 2034 | PLD003 | 0 | 0 | 149.8755 | 6321.3663 | 149.8755 | 1483.4572 | 7804.8236
| 19909287 | 2023 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1182.3891 | 1182.3891
| 19909287 | 2024 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1182.3891 | 1182.3891
| 19909287 | 2025 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1182.3891 | 1182.3891
| 19909287 | 2026 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1182.3891 | 1182.3891
| 19909287 | 2027 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1182.3891 | 1182.3891
| 19909287 | 2028 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1182.3891 | 1182.3891
| 19909287 | 2029 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1182.3891 | 1182.3891
| 19909287 | 2030 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1182.3891 | 1182.3891
| 19909287 | 2031 | PLD003 | 0 | 0 | 0.014187 | 0.59838 | 0.014187 | 1182.3891 | 1182.9875
| 19909287 | 2032 | PLD003 | 0 | 0 | 0.089435 | 3.7721 | 0.089435 | 1182.3891 | 1186.1612
| 19909287 | 2033 | PLD003 | 0 | 0 | 0.43725 | 18.4421 | 0.43725 | 1182.3891 | 1200.8312
| 19909287 | 2034 | PLD003 | 0 | 0 | 2.5949 | 109.4469 | 2.5949 | 1182.3891 | 1291.836
| 19910067 | 2023 | PLD003 | 0 | 0 | 0 | 0 | 0 | 789.8385 | 789.8385
| 19910067 | 2024 | PLD003 | 0 | 0 | 0 | 0 | 0 | 789.8385 | 789.8385
| 19910067 | 2025 | PLD003 | 0 | 0 | 0 | 0 | 0 | 789.8385 | 789.8385
| 19910067 | 2026 | PLD003 | 0 | 0 | 0 | 0 | 0 | 789.8385 | 789.8385
| 19910067 | 2027 | PLD003 | 0 | 0 | 0 | 0 | 0 | 789.8385 | 789.8385
| 19910067 | 2028 | PLD003 | 0 | 0 | 0 | 0 | 0 | 789.8385 | 789.8385
| 19910067 | 2029 | PLD003 | 0 | 0 | 0 | 0 | 0 | 789.8385 | 789.8385
| 19910067 | 2030 | PLD003 | 0 | 0 | 0 | 0 | 0 | 789.8385 | 789.8385
| 19910067 | 2031 | PLD003 | 0 | 0 | 0.15138 | 6.3847 | 0.15138 | 789.8385 | 796.2232
| 19910067 | 2032 | PLD003 | 0 | 0 | 1.4825 | 62.527 | 1.4825 | 789.8385 | 852.3655
| 19910067 | 2033 | PLD003 | 0 | 0 | 3.2693 | 137.8893 | 3.2693 | 789.8385 | 927.7279
| 19910067 | 2034 | PLD003 | 0 | 0 | 8.8771 | 374.4124 | 8.8771 | 789.8385 | 1164.251
| 20564668 | 2023 | PLD003 | 0 | 0 | 0 | 0 | 0 | 280.9587 | 280.9587
| 20564668 | 2024 | PLD003 | 0 | 0 | 0 | 0 | 0 | 280.9587 | 280.9587
| 20564668 | 2025 | PLD003 | 0 | 0 | 0 | 0 | 0 | 280.9587 | 280.9587
| 20564668 | 2026 | PLD003 | 0 | 0 | 0 | 0 | 0 | 280.9587 | 280.9587
| 20564668 | 2027 | PLD003 | 0 | 0 | 0 | 0 | 0 | 280.9587 | 280.9587
| 20564668 | 2028 | PLD003 | 0 | 0 | 0 | 0 | 0 | 280.9587 | 280.9587
| 20564668 | 2029 | PLD003 | 0 | 0 | 0 | 0 | 0 | 280.9587 | 280.9587
| 20564668 | 2030 | PLD003 | 0 | 0 | 0 | 0 | 0 | 280.9587 | 280.9587
| 20564668 | 2031 | PLD003 | 0 | 0 | 0 | 0 | 0 | 280.9587 | 280.9587
| 20564668 | 2032 | PLD003 | 0 | 0 | 0 | 0 | 0 | 280.9587 | 280.9587
| 20564668 | 2033 | PLD003 | 0 | 0 | 0 | 0 | 0 | 280.9587 | 280.9587
| 20564668 | 2034 | PLD003 | 0 | 0 | 0 | 0 | 0 | 280.9587 | 280.9587
| 20567465 | 2023 | PLD003 | 0 | 0 | 0.11336 | 4.7813 | 0.11336 | 1200.8214 | 1205.6027
| 20567465 | 2024 | PLD003 | 0 | 0 | 0.13722 | 5.7876 | 0.13722 | 1200.8214 | 1206.609
| 20567465 | 2025 | PLD003 | 0 | 0 | 0.35625 | 15.0256 | 0.35625 | 1200.8214 | 1215.847
| 20567465 | 2026 | PLD003 | 0 | 0 | 4.5428 | 191.6049 | 4.5428 | 1200.8214 | 1392.4263
| 20567465 | 2027 | PLD003 | 0 | 0 | 8.4624 | 356.9214 | 8.4624 | 1200.8214 | 1557.7428
| 20567465 | 2028 | PLD003 | 0 | 0 | 11.3936 | 480.5521 | 11.3936 | 1200.8214 | 1681.3735
| 20567465 | 2029 | PLD003 | 0 | 0 | 11.7225 | 494.4265 | 11.7225 | 1200.8214 | 1695.2479
| 20567465 | 2030 | PLD003 | 0 | 0 | 31.5362 | 1330.1183 | 31.5362 | 1200.8214 | 2530.9397
| 20567465 | 2031 | PLD003 | 0 | 0 | 72.0574 | 3039.1988 | 72.0574 | 1200.8214 | 4240.0202
| 20567465 | 2032 | PLD003 | 0 | 0 | 94.8003 | 3998.4334 | 94.8003 | 1200.8214 | 5199.2548
| 20567465 | 2033 | PLD003 | 0 | 0 | 411.2533 | 17345.6186 | 411.2533 | 1200.8214 | 18546.44
| 20567465 | 2034 | PLD003 | 0 | 0 | 954.5401 | 40260.0702 | 954.5401 | 1200.8214 | 41460.8916
| 86833640 | 2023 | PLD003 | 0 | 0 | 0 | 0 | 0 | 2089.181 | 2089.181
| 86833640 | 2024 | PLD003 | 0 | 0 | 0 | 0 | 0 | 2089.181 | 2089.181
| 86833640 | 2025 | PLD003 | 0 | 0 | 0 | 0 | 0 | 2089.181 | 2089.181
| 86833640 | 2026 | PLD003 | 0 | 0 | 0 | 0 | 0 | 2089.181 | 2089.181
| 86833640 | 2027 | PLD003 | 0 | 0 | 0 | 0 | 0 | 2089.181 | 2089.181
| 86833640 | 2028 | PLD003 | 0 | 0 | 0 | 0 | 0 | 2089.181 | 2089.181
| 86833640 | 2029 | PLD003 | 0 | 0 | 0 | 0 | 0 | 2089.181 | 2089.181
| 86833640 | 2030 | PLD003 | 0 | 0 | 0 | 0 | 0 | 2089.181 | 2089.181
| 86833640 | 2031 | PLD003 | 0 | 0 | 0 | 0 | 0 | 2089.181 | 2089.181
| 86833640 | 2032 | PLD003 | 0 | 0 | 0 | 0 | 0 | 2089.181 | 2089.181
| 86833640 | 2033 | PLD003 | 0 | 0 | 0 | 0 | 0 | 2089.181 | 2089.181
| 86833640 | 2034 | PLD003 | 0 | 0 | 0 | 0 | 0 | 2089.181 | 2089.181
| 110224787 | 2023 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1773.4265 | 1773.4265
| 110224787 | 2024 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1773.4265 | 1773.4265
| 110224787 | 2025 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1773.4265 | 1773.4265
| 110224787 | 2026 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1773.4265 | 1773.4265
| 110224787 | 2027 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1773.4265 | 1773.4265
| 110224787 | 2028 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1773.4265 | 1773.4265
| 110224787 | 2029 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1773.4265 | 1773.4265
| 110224787 | 2030 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1773.4265 | 1773.4265
| 110224787 | 2031 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1773.4265 | 1773.4265
| 110224787 | 2032 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1773.4265 | 1773.4265
| 110224787 | 2033 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1773.4265 | 1773.4265
| 110224787 | 2034 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1773.4265 | 1773.4265
| 160451578 | 2023 | PLD003 | 0 | 0 | 357.8679 | 15093.958 | 357.8679 | 7458.9145 | 22552.8724
| 160451578 | 2024 | PLD003 | 0 | 0 | 411.19 | 17342.9462 | 411.19 | 7458.9145 | 24801.8607
| 160451578 | 2025 | PLD003 | 0 | 0 | 409.7574 | 17282.525 | 409.7574 | 7458.9145 | 24741.4395
| 160451578 | 2026 | PLD003 | 0 | 0 | 382.9711 | 16152.7454 | 382.9711 | 7458.9145 | 23611.6599
| 160451578 | 2027 | PLD003 | 0 | 0 | 440.7421 | 18589.3807 | 440.7421 | 7458.9145 | 26048.2952
| 160451578 | 2028 | PLD003 | 0 | 0 | 490.7942 | 20700.4512 | 490.7942 | 7458.9145 | 28159.3657
| 160451578 | 2029 | PLD003 | 0 | 0 | 524.4525 | 22120.0721 | 524.4525 | 7458.9145 | 29578.9866
| 160451578 | 2030 | PLD003 | 0 | 0 | 514.9236 | 21718.1661 | 514.9236 | 7458.9145 | 29177.0806
| 160451578 | 2031 | PLD003 | 0 | 0 | 526.4619 | 22204.8216 | 526.4619 | 7458.9145 | 29663.7361
| 160451578 | 2032 | PLD003 | 0 | 0 | 524.2493 | 22111.5016 | 524.2493 | 7458.9145 | 29570.4161
| 160451578 | 2033 | PLD003 | 0 | 0 | 579.9923 | 24462.5993 | 579.9923 | 7458.9145 | 31921.5138
| 160451578 | 2034 | PLD003 | 0 | 0 | 595.4584 | 25114.9181 | 595.4584 | 7458.9145 | 32573.8326
| 160705636 | 2023 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1632.3888 | 1632.3888
| 160705636 | 2024 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1632.3888 | 1632.3888
| 160705636 | 2025 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1632.3888 | 1632.3888
| 160705636 | 2026 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1632.3888 | 1632.3888
| 160705636 | 2027 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1632.3888 | 1632.3888
| 160705636 | 2028 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1632.3888 | 1632.3888
| 160705636 | 2029 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1632.3888 | 1632.3888
| 160705636 | 2030 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1632.3888 | 1632.3888
| 160705636 | 2031 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1632.3888 | 1632.3888
| 160705636 | 2032 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1632.3888 | 1632.3888
| 160705636 | 2033 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1632.3888 | 1632.3888
| 160705636 | 2034 | PLD003 | 0 | 0 | 0 | 0 | 0 | 1632.3888 | 1632.3888
| 161722801 | 2023 | PLD003 | 0 | 0 | 0 | 0 | 0 | 5318.2778 | 5318.2778
| 161722801 | 2024 | PLD003 | 0 | 0 | 0 | 0 | 0 | 5318.2778 | 5318.2778
| 161722801 | 2025 | PLD003 | 0 | 0 | 0 | 0 | 0 | 5318.2778 | 5318.2778
| 161722801 | 2026 | PLD003 | 0 | 0 | 0 | 0 | 0 | 5318.2778 | 5318.2778
| 161722801 | 2027 | PLD003 | 0 | 0 | 0 | 0 | 0 | 5318.2778 | 5318.2778
| 161722801 | 2028 | PLD003 | 0 | 0 | 0 | 0 | 0 | 5318.2778 | 5318.2778
| 161722801 | 2029 | PLD003 | 0 | 0 | 0 | 0 | 0 | 5318.2778 | 5318.2778
| 161722801 | 2030 | PLD003 | 0 | 0 | 0 | 0 | 0 | 5318.2778 | 5318.2778
| 161722801 | 2031 | PLD003 | 0 | 0 | 0 | 0 | 0 | 5318.2778 | 5318.2778
| 161722801 | 2032 | PLD003 | 0 | 0 | 0 | 0 | 0 | 5318.2778 | 5318.2778
| 161722801 | 2033 | PLD003 | 0 | 0 | 0 | 0 | 0 | 5318.2778 | 5318.2778
| 161722801 | 2034 | PLD003 | 0 | 0 | 0 | 0 | 0 | 5318.2778 | 5318.2778
| 163610121 | 2023 | PLD003 | 0 | 0 | 0 | 0 | 0 | 3227.9922 | 3227.9922
| 163610121 | 2024 | PLD003 | 0 | 0 | 0 | 0 | 0 | 3227.9922 | 3227.9922
| 163610121 | 2025 | PLD003 | 0 | 0 | 0 | 0 | 0 | 3227.9922 | 3227.9922
| 163610121 | 2026 | PLD003 | 0 | 0 | 0 | 0 | 0 | 3227.9922 | 3227.9922
| 163610121 | 2027 | PLD003 | 0 | 0 | 0 | 0 | 0 | 3227.9922 | 3227.9922
| 163610121 | 2028 | PLD003 | 0 | 0 | 0 | 0 | 0 | 3227.9922 | 3227.9922
| 163610121 | 2029 | PLD003 | 0 | 0 | 0 | 0 | 0 | 3227.9922 | 3227.9922
| 163610121 | 2030 | PLD003 | 0 | 0 | 0 | 0 | 0 | 3227.9922 | 3227.9922
| 163610121 | 2031 | PLD003 | 0 | 0 | 0 | 0 | 0 | 3227.9922 | 3227.9922
| 163610121 | 2032 | PLD003 | 0 | 0 | 0 | 0 | 0 | 3227.9922 | 3227.9922
| 163610121 | 2033 | PLD003 | 0 | 0 | 0 | 0 | 0 | 3227.9922 | 3227.9922
| 163610121 | 2034 | PLD003 | 0 | 0 | 0 | 0 | 0 | 3227.9922 | 3227.9922
| 19908051 | 2023 | PLD006 | 0 | 0 | 0 | 0 | 0 | 3306.2161 | 3306.2161
| 19908051 | 2024 | PLD006 | 0 | 0 | 0 | 0 | 0 | 3306.2161 | 3306.2161
| 19908051 | 2025 | PLD006 | 0 | 0 | 0 | 0 | 0 | 3306.2161 | 3306.2161
| 19908051 | 2026 | PLD006 | 0 | 0 | 0 | 0 | 0 | 3306.2161 | 3306.2161
| 19908051 | 2027 | PLD006 | 0 | 0 | 0 | 0 | 0 | 3306.2161 | 3306.2161
| 19908051 | 2028 | PLD006 | 0 | 0 | 0 | 0 | 0 | 3306.2161 | 3306.2161
| 19908051 | 2029 | PLD006 | 0 | 0 | 0 | 0 | 0 | 3306.2161 | 3306.2161
| 19908051 | 2030 | PLD006 | 0 | 0 | 0 | 0 | 0 | 3306.2161 | 3306.2161
| 19908051 | 2031 | PLD006 | 0 | 0 | 0 | 0 | 0 | 3306.2161 | 3306.2161
| 19908051 | 2032 | PLD006 | 0 | 0 | 0 | 0 | 0 | 3306.2161 | 3306.2161
| 19908051 | 2033 | PLD006 | 0 | 0 | 0 | 0 | 0 | 3306.2161 | 3306.2161
| 19908051 | 2034 | PLD006 | 0 | 0 | 0 | 0 | 0 | 3306.2161 | 3306.2161
| 19912672 | 2023 | PLD006 | 0 | 0 | 0 | 0 | 0 | 4308.0296 | 4308.0296
| 19912672 | 2024 | PLD006 | 0 | 0 | 0 | 0 | 0 | 4308.0296 | 4308.0296
| 19912672 | 2025 | PLD006 | 0 | 0 | 0 | 0 | 0 | 4308.0296 | 4308.0296
| 19912672 | 2026 | PLD006 | 0 | 0 | 0 | 0 | 0 | 4308.0296 | 4308.0296
| 19912672 | 2027 | PLD006 | 0 | 0 | 0 | 0 | 0 | 4308.0296 | 4308.0296
| 19912672 | 2028 | PLD006 | 0 | 0 | 0 | 0 | 0 | 4308.0296 | 4308.0296
| 19912672 | 2029 | PLD006 | 29.1748 | 0.053209 | 0 | 0 | 29.1748 | 4308.0296 | 4308.0828
| 19912672 | 2030 | PLD006 | 425.1361 | 1.0798 | 0 | 0 | 425.1361 | 4308.0296 | 4309.1095
| 19912672 | 2031 | PLD006 | 879.5453 | 5.4175 | 0 | 0 | 879.5453 | 4308.0296 | 4313.4472
| 19912672 | 2032 | PLD006 | 2156.1321 | 23.4877 | 0 | 0 | 2156.1321 | 4308.0296 | 4331.5173
| 19912672 | 2033 | PLD006 | 3612.9419 | 96.2552 | 0 | 0 | 3612.9419 | 4308.0296 | 4404.2848
| 19912672 | 2034 | PLD006 | 6098.2523 | 200.201 | 0 | 0 | 6098.2523 | 4308.0296 | 4508.2306
| 19912690 | 2023 | PLD006 | 0 | 0 | 0 | 0 | 0 | 848.9852 | 848.9852
| 19912690 | 2024 | PLD006 | 0 | 0 | 0 | 0 | 0 | 848.9852 | 848.9852
| 19912690 | 2025 | PLD006 | 0 | 0 | 0 | 0 | 0 | 848.9852 | 848.9852
| 19912690 | 2026 | PLD006 | 0 | 0 | 0 | 0 | 0 | 848.9852 | 848.9852
| 19912690 | 2027 | PLD006 | 0 | 0 | 0 | 0 | 0 | 848.9852 | 848.9852
| 19912690 | 2028 | PLD006 | 0 | 0 | 0 | 0 | 0 | 848.9852 | 848.9852
| 19912690 | 2029 | PLD006 | 0 | 0 | 0 | 0 | 0 | 848.9852 | 848.9852
| 19912690 | 2030 | PLD006 | 0 | 0 | 0 | 0 | 0 | 848.9852 | 848.9852
| 19912690 | 2031 | PLD006 | 0 | 0 | 0 | 0 | 0 | 848.9852 | 848.9852
| 19912690 | 2032 | PLD006 | 0 | 0 | 0 | 0 | 0 | 848.9852 | 848.9852
| 19912690 | 2033 | PLD006 | 0 | 0 | 0 | 0 | 0 | 848.9852 | 848.9852
| 19912690 | 2034 | PLD006 | 0 | 0 | 0 | 0 | 0 | 848.9852 | 848.9852
| 20530090 | 2023 | PLD006 | 0 | 0 | 0 | 0 | 0 | 2629.4675 | 2629.4675
| 20530090 | 2024 | PLD006 | 0 | 0 | 0 | 0 | 0 | 2629.4675 | 2629.4675
| 20530090 | 2025 | PLD006 | 0 | 0 | 0 | 0 | 0 | 2629.4675 | 2629.4675
| 20530090 | 2026 | PLD006 | 0 | 0 | 0 | 0 | 0 | 2629.4675 | 2629.4675
| 20530090 | 2027 | PLD006 | 0 | 0 | 0 | 0 | 0 | 2629.4675 | 2629.4675
| 20530090 | 2028 | PLD006 | 0 | 0 | 0 | 0 | 0 | 2629.4675 | 2629.4675
| 20530090 | 2029 | PLD006 | 0 | 0 | 0 | 0 | 0 | 2629.4675 | 2629.4675
| 20530090 | 2030 | PLD006 | 0 | 0 | 0 | 0 | 0 | 2629.4675 | 2629.4675
| 20530090 | 2031 | PLD006 | 0 | 0 | 0 | 0 | 0 | 2629.4675 | 2629.4675
| 20530090 | 2032 | PLD006 | 0 | 0 | 0 | 0 | 0 | 2629.4675 | 2629.4675
| 20530090 | 2033 | PLD006 | 0 | 0 | 0 | 0 | 0 | 2629.4675 | 2629.4675
| 20530090 | 2034 | PLD006 | 0.31883 | 0.005923 | 0 | 0 | 0.31883 | 2629.4675 | 2629.4734
| 20543778 | 2023 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1141.1492 | 1141.1492
| 20543778 | 2024 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1141.1492 | 1141.1492
| 20543778 | 2025 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1141.1492 | 1141.1492
| 20543778 | 2026 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1141.1492 | 1141.1492
| 20543778 | 2027 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1141.1492 | 1141.1492
| 20543778 | 2028 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1141.1492 | 1141.1492
| 20543778 | 2029 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1141.1492 | 1141.1492
| 20543778 | 2030 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1141.1492 | 1141.1492
| 20543778 | 2031 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1141.1492 | 1141.1492
| 20543778 | 2032 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1141.1492 | 1141.1492
| 20543778 | 2033 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1141.1492 | 1141.1492
| 20543778 | 2034 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1141.1492 | 1141.1492
| 161891847 | 2023 | PLD006 | 0 | 0 | 0 | 0 | 0 | 330.2605 | 330.2605
| 161891847 | 2024 | PLD006 | 0 | 0 | 0 | 0 | 0 | 330.2605 | 330.2605
| 161891847 | 2025 | PLD006 | 0 | 0 | 0 | 0 | 0 | 330.2605 | 330.2605
| 161891847 | 2026 | PLD006 | 0 | 0 | 0 | 0 | 0 | 330.2605 | 330.2605
| 161891847 | 2027 | PLD006 | 0 | 0 | 0 | 0 | 0 | 330.2605 | 330.2605
| 161891847 | 2028 | PLD006 | 0 | 0 | 0 | 0 | 0 | 330.2605 | 330.2605
| 161891847 | 2029 | PLD006 | 0 | 0 | 0 | 0 | 0 | 330.2605 | 330.2605
| 161891847 | 2030 | PLD006 | 0 | 0 | 0 | 0 | 0 | 330.2605 | 330.2605
| 161891847 | 2031 | PLD006 | 0 | 0 | 0 | 0 | 0 | 330.2605 | 330.2605
| 161891847 | 2032 | PLD006 | 0 | 0 | 0 | 0 | 0 | 330.2605 | 330.2605
| 161891847 | 2033 | PLD006 | 0 | 0 | 0 | 0 | 0 | 330.2605 | 330.2605
| 161891847 | 2034 | PLD006 | 0 | 0 | 0 | 0 | 0 | 330.2605 | 330.2605
| 176990801 | 2023 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1224.9033 | 1224.9033
| 176990801 | 2024 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1224.9033 | 1224.9033
| 176990801 | 2025 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1224.9033 | 1224.9033
| 176990801 | 2026 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1224.9033 | 1224.9033
| 176990801 | 2027 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1224.9033 | 1224.9033
| 176990801 | 2028 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1224.9033 | 1224.9033
| 176990801 | 2029 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1224.9033 | 1224.9033
| 176990801 | 2030 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1224.9033 | 1224.9033
| 176990801 | 2031 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1224.9033 | 1224.9033
| 176990801 | 2032 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1224.9033 | 1224.9033
| 176990801 | 2033 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1224.9033 | 1224.9033
| 176990801 | 2034 | PLD006 | 0 | 0 | 0 | 0 | 0 | 1224.9033 | 1224.9033
| 20418533 | 2023 | RCT022 | 0 | 0 | 0 | 0 | 0 | 16995.4485 | 16995.4485
| 20418533 | 2024 | RCT022 | 3325.6462 | 72.9914 | 0 | 0 | 3325.6462 | 16995.4485 | 17068.4399
| 20418533 | 2025 | RCT022 | 3377.6736 | 113.6699 | 0 | 0 | 3377.6736 | 16995.4485 | 17109.1184
| 20418533 | 2026 | RCT022 | 6972.6529 | 179.9623 | 0 | 0 | 6972.6529 | 16995.4485 | 17175.4108
| 20418533 | 2027 | RCT022 | 13504.9489 | 305.6526 | 0 | 0 | 13504.9489 | 16995.4485 | 17301.1011
| 20418533 | 2028 | RCT022 | 17740.8093 | 425.017 | 0 | 0 | 17740.8093 | 16995.4485 | 17420.4655
| 20418533 | 2029 | RCT022 | 27047.6359 | 634.4939 | 0 | 0 | 27047.6359 | 16995.4485 | 17629.9423
| 20418533 | 2030 | RCT022 | 27047.6359 | 634.4939 | 0 | 0 | 27047.6359 | 16995.4485 | 17629.9423
| 20418533 | 2031 | RCT022 | 27047.6359 | 634.4939 | 0 | 0 | 27047.6359 | 16995.4485 | 17629.9423
| 20418533 | 2032 | RCT022 | 27047.6359 | 634.4939 | 0 | 0 | 27047.6359 | 16995.4485 | 17629.9423
| 20418533 | 2033 | RCT022 | 27047.6359 | 634.4939 | 0 | 0 | 27047.6359 | 16995.4485 | 17629.9423
| 20418533 | 2034 | RCT022 | 27047.6359 | 634.4939 | 0 | 0 | 27047.6359 | 16995.4485 | 17629.9423
| 20428138 | 2023 | RCT022 | 886.5906 | 0 | 0 | 0 | 886.5906 | 586.4759 | 586.4759
| 20428138 | 2024 | RCT022 | 895.6545 | 19.703 | 0 | 0 | 895.6545 | 586.4759 | 606.1789
| 20428138 | 2025 | RCT022 | 926.0816 | 28.9492 | 0 | 0 | 926.0816 | 586.4759 | 615.425
| 20428138 | 2026 | RCT022 | 1262.128 | 25.591 | 0 | 0 | 1262.128 | 586.4759 | 612.0669
| 20428138 | 2027 | RCT022 | 1100.0265 | 21.1561 | 0 | 0 | 1100.0265 | 586.4759 | 607.6319
| 20428138 | 2028 | RCT022 | 1191.061 | 24.8108 | 0 | 0 | 1191.061 | 586.4759 | 611.2867
| 20428138 | 2029 | RCT022 | 2065.4466 | 29.4151 | 0 | 0 | 2065.4466 | 586.4759 | 615.891
| 20428138 | 2030 | RCT022 | 2065.4466 | 29.4151 | 0 | 0 | 2065.4466 | 586.4759 | 615.891
| 20428138 | 2031 | RCT022 | 2065.4466 | 29.4151 | 0 | 0 | 2065.4466 | 586.4759 | 615.891
| 20428138 | 2032 | RCT022 | 2065.4466 | 29.4151 | 0 | 0 | 2065.4466 | 586.4759 | 615.891
| 20428138 | 2033 | RCT022 | 2065.4466 | 29.4151 | 0 | 0 | 2065.4466 | 586.4759 | 615.891
| 20428138 | 2034 | RCT022 | 2065.4466 | 29.4151 | 0 | 0 | 2065.4466 | 586.4759 | 615.891
| 20497106 | 2023 | RCT022 | 0 | 0 | 0 | 0 | 0 | 5826.1546 | 5826.1546
| 20497106 | 2024 | RCT022 | 0 | 0 | 0 | 0 | 0 | 5826.1546 | 5826.1546
| 20497106 | 2025 | RCT022 | 0 | 0 | 0 | 0 | 0 | 5826.1546 | 5826.1546
| 20497106 | 2026 | RCT022 | 0 | 0 | 0 | 0 | 0 | 5826.1546 | 5826.1546
| 20497106 | 2027 | RCT022 | 0 | 0 | 59.4553 | 2605.0692 | 59.4553 | 5826.1546 | 8431.2239
| 20497106 | 2028 | RCT022 | 0 | 0 | 16.5024 | 723.0604 | 16.5024 | 5826.1546 | 6549.215
| 20497106 | 2029 | RCT022 | 0 | 0 | 4.2575 | 186.5445 | 4.2575 | 5826.1546 | 6012.6992
| 20497106 | 2030 | RCT022 | 0 | 0 | 4.2575 | 186.5445 | 4.2575 | 5826.1546 | 6012.6992
| 20497106 | 2031 | RCT022 | 0 | 0 | 4.2575 | 186.5445 | 4.2575 | 5826.1546 | 6012.6992
| 20497106 | 2032 | RCT022 | 0 | 0 | 4.2575 | 186.5445 | 4.2575 | 5826.1546 | 6012.6992
| 20497106 | 2033 | RCT022 | 0 | 0 | 4.2575 | 186.5445 | 4.2575 | 5826.1546 | 6012.6992
| 20497106 | 2034 | RCT022 | 0 | 0 | 4.2575 | 186.5445 | 4.2575 | 5826.1546 | 6012.6992
| 20539743 | 2023 | RCT022 | 0 | 0 | 0 | 0 | 0 | 1171.8113 | 1171.8113
| 20539743 | 2024 | RCT022 | 0 | 0 | 0 | 0 | 0 | 1171.8113 | 1171.8113
| 20539743 | 2025 | RCT022 | 0 | 0 | 0 | 0 | 0 | 1171.8113 | 1171.8113
| 20539743 | 2026 | RCT022 | 0 | 0 | 0 | 0 | 0 | 1171.8113 | 1171.8113
| 20539743 | 2027 | RCT022 | 0 | 0 | 0 | 0 | 0 | 1171.8113 | 1171.8113
| 20539743 | 2028 | RCT022 | 0 | 0 | 0 | 0 | 0 | 1171.8113 | 1171.8113
| 20539743 | 2029 | RCT022 | 0 | 0 | 0 | 0 | 0 | 1171.8113 | 1171.8113
| 20539743 | 2030 | RCT022 | 0 | 0 | 0 | 0 | 0 | 1171.8113 | 1171.8113
| 20539743 | 2031 | RCT022 | 0 | 0 | 0 | 0 | 0 | 1171.8113 | 1171.8113
| 20539743 | 2032 | RCT022 | 0 | 0 | 0 | 0 | 0 | 1171.8113 | 1171.8113
| 20539743 | 2033 | RCT022 | 0 | 0 | 0 | 0 | 0 | 1171.8113 | 1171.8113
| 20539743 | 2034 | RCT022 | 0 | 0 | 0 | 0 | 0 | 1171.8113 | 1171.8113
| 20011694 | 2023 | SHL001 | 0 | 0 | 0 | 0 | 0 | 2738.9191 | 2738.9191
| 20011694 | 2024 | SHL001 | 0 | 0 | 0 | 0 | 0 | 2738.9191 | 2738.9191
| 20011694 | 2025 | SHL001 | 0 | 0 | 0 | 0 | 0 | 2738.9191 | 2738.9191
| 20011694 | 2026 | SHL001 | 0 | 0 | 0 | 0 | 0 | 2738.9191 | 2738.9191
| 20011694 | 2027 | SHL001 | 0 | 0 | 0 | 0 | 0 | 2738.9191 | 2738.9191
| 20011694 | 2028 | SHL001 | 0 | 0 | 0 | 0 | 0 | 2738.9191 | 2738.9191
| 20011694 | 2029 | SHL001 | 0 | 0 | 0 | 0 | 0 | 2738.9191 | 2738.9191
| 20011694 | 2030 | SHL001 | 0 | 0 | 0 | 0 | 0 | 2738.9191 | 2738.9191
| 20011694 | 2031 | SHL001 | 0 | 0 | 0 | 0 | 0 | 2738.9191 | 2738.9191
| 20011694 | 2032 | SHL001 | 0 | 0 | 0 | 0 | 0 | 2738.9191 | 2738.9191
| 20011694 | 2033 | SHL001 | 0 | 0 | 0 | 0 | 0 | 2738.9191 | 2738.9191
| 20011694 | 2034 | SHL001 | 0 | 0 | 0 | 0 | 0 | 2738.9191 | 2738.9191
| 20015446 | 2023 | SHL001 | 0 | 0 | 0 | 0 | 0 | 5306.7663 | 5306.7663
| 20015446 | 2024 | SHL001 | 0 | 0 | 0 | 0 | 0 | 5306.7663 | 5306.7663
| 20015446 | 2025 | SHL001 | 0 | 0 | 0 | 0 | 0 | 5306.7663 | 5306.7663
| 20015446 | 2026 | SHL001 | 0 | 0 | 0 | 0 | 0 | 5306.7663 | 5306.7663
| 20015446 | 2027 | SHL001 | 0 | 0 | 0 | 0 | 0 | 5306.7663 | 5306.7663
| 20015446 | 2028 | SHL001 | 0 | 0 | 0 | 0 | 0 | 5306.7663 | 5306.7663
| 20015446 | 2029 | SHL001 | 0 | 0 | 0 | 0 | 0 | 5306.7663 | 5306.7663
| 20015446 | 2030 | SHL001 | 0 | 0 | 0 | 0 | 0 | 5306.7663 | 5306.7663
| 20015446 | 2031 | SHL001 | 0 | 0 | 0 | 0 | 0 | 5306.7663 | 5306.7663
| 20015446 | 2032 | SHL001 | 0 | 0 | 0 | 0 | 0 | 5306.7663 | 5306.7663
| 20015446 | 2033 | SHL001 | 0 | 0 | 0 | 0 | 0 | 5306.7663 | 5306.7663
| 20015446 | 2034 | SHL001 | 0 | 0 | 0 | 0 | 0 | 5306.7663 | 5306.7663
| 20016842 | 2023 | SHL001 | 0 | 0 | 0 | 0 | 0 | 11198.0417 | 11198.0417
| 20016842 | 2024 | SHL001 | 0 | 0 | 0 | 0 | 0 | 11198.0417 | 11198.0417
| 20016842 | 2025 | SHL001 | 0 | 0 | 0 | 0 | 0 | 11198.0417 | 11198.0417
| 20016842 | 2026 | SHL001 | 0 | 0 | 0 | 0 | 0 | 11198.0417 | 11198.0417
| 20016842 | 2027 | SHL001 | 0 | 0 | 0 | 0 | 0 | 11198.0417 | 11198.0417
| 20016842 | 2028 | SHL001 | 0 | 0 | 0 | 0 | 0 | 11198.0417 | 11198.0417
| 20016842 | 2029 | SHL001 | 0 | 0 | 0 | 0 | 0 | 11198.0417 | 11198.0417
| 20016842 | 2030 | SHL001 | 0 | 0 | 0 | 0 | 0 | 11198.0417 | 11198.0417
| 20016842 | 2031 | SHL001 | 0 | 0 | 0 | 0 | 0 | 11198.0417 | 11198.0417
| 20016842 | 2032 | SHL001 | 0 | 0 | 0 | 0 | 0 | 11198.0417 | 11198.0417
| 20016842 | 2033 | SHL001 | 0 | 0 | 0 | 0 | 0 | 11198.0417 | 11198.0417
| 20016842 | 2034 | SHL001 | 0 | 0 | 0 | 0 | 0 | 11198.0417 | 11198.0417
| 20017124 | 2023 | SHL001 | 323.6109 | 0 | 0 | 0 | 323.6109 | 17104.2552 | 17104.2552
| 20017124 | 2024 | SHL001 | 297.8492 | 4.2785 | 0 | 0 | 297.8492 | 17104.2552 | 17108.5337
| 20017124 | 2025 | SHL001 | 324.5449 | 4.5408 | 0 | 0 | 324.5449 | 17104.2552 | 17108.796
| 20017124 | 2026 | SHL001 | 482.3005 | 2.5351 | 0 | 0 | 482.3005 | 17104.2552 | 17106.7902
| 20017124 | 2027 | SHL001 | 482.3005 | 2.5351 | 0 | 0 | 482.3005 | 17104.2552 | 17106.7902
| 20017124 | 2028 | SHL001 | 482.3005 | 2.5351 | 0 | 0 | 482.3005 | 17104.2552 | 17106.7902
| 20017124 | 2029 | SHL001 | 482.3005 | 2.5351 | 0 | 0 | 482.3005 | 17104.2552 | 17106.7902
| 20017124 | 2030 | SHL001 | 482.3005 | 2.5351 | 0 | 0 | 482.3005 | 17104.2552 | 17106.7902
| 20017124 | 2031 | SHL001 | 482.3005 | 2.5351 | 0 | 0 | 482.3005 | 17104.2552 | 17106.7902
| 20017124 | 2032 | SHL001 | 482.3005 | 2.5351 | 0 | 0 | 482.3005 | 17104.2552 | 17106.7902
| 20017124 | 2033 | SHL001 | 482.3005 | 2.5351 | 0 | 0 | 482.3005 | 17104.2552 | 17106.7902
| 20017124 | 2034 | SHL001 | 482.3005 | 2.5351 | 0 | 0 | 482.3005 | 17104.2552 | 17106.7902
| 20019070 | 2023 | SHL001 | 0 | 0 | 0 | 0 | 0 | 4047.4871 | 4047.4871
| 20019070 | 2024 | SHL001 | 0 | 0 | 0 | 0 | 0 | 4047.4871 | 4047.4871
| 20019070 | 2025 | SHL001 | 0 | 0 | 0 | 0 | 0 | 4047.4871 | 4047.4871
| 20019070 | 2026 | SHL001 | 0 | 0 | 0 | 0 | 0 | 4047.4871 | 4047.4871
| 20019070 | 2027 | SHL001 | 0 | 0 | 0 | 0 | 0 | 4047.4871 | 4047.4871
| 20019070 | 2028 | SHL001 | 0 | 0 | 0 | 0 | 0 | 4047.4871 | 4047.4871
| 20019070 | 2029 | SHL001 | 0 | 0 | 0 | 0 | 0 | 4047.4871 | 4047.4871
| 20019070 | 2030 | SHL001 | 0 | 0 | 0 | 0 | 0 | 4047.4871 | 4047.4871
| 20019070 | 2031 | SHL001 | 0 | 0 | 0 | 0 | 0 | 4047.4871 | 4047.4871
| 20019070 | 2032 | SHL001 | 0 | 0 | 0 | 0 | 0 | 4047.4871 | 4047.4871
| 20019070 | 2033 | SHL001 | 0 | 0 | 0 | 0 | 0 | 4047.4871 | 4047.4871
| 20019070 | 2034 | SHL001 | 0 | 0 | 0 | 0 | 0 | 4047.4871 | 4047.4871
| 20041373 | 2023 | SHL001 | 0 | 0 | 0 | 0 | 0 | 19672.2817 | 19672.2817
| 20041373 | 2024 | SHL001 | 0 | 0 | 0 | 0 | 0 | 19672.2817 | 19672.2817
| 20041373 | 2025 | SHL001 | 0 | 0 | 0 | 0 | 0 | 19672.2817 | 19672.2817
| 20041373 | 2026 | SHL001 | 0 | 0 | 0 | 0 | 0 | 19672.2817 | 19672.2817
| 20041373 | 2027 | SHL001 | 0 | 0 | 0 | 0 | 0 | 19672.2817 | 19672.2817
| 20041373 | 2028 | SHL001 | 0 | 0 | 0 | 0 | 0 | 19672.2817 | 19672.2817
| 20041373 | 2029 | SHL001 | 0 | 0 | 0 | 0 | 0 | 19672.2817 | 19672.2817
| 20041373 | 2030 | SHL001 | 0 | 0 | 0 | 0 | 0 | 19672.2817 | 19672.2817
| 20041373 | 2031 | SHL001 | 0 | 0 | 0 | 0 | 0 | 19672.2817 | 19672.2817
| 20041373 | 2032 | SHL001 | 0 | 0 | 0 | 0 | 0 | 19672.2817 | 19672.2817
| 20041373 | 2033 | SHL001 | 0 | 0 | 0 | 0 | 0 | 19672.2817 | 19672.2817
| 20041373 | 2034 | SHL001 | 0 | 0 | 0 | 0 | 0 | 19672.2817 | 19672.2817
| 20496023 | 2023 | SHL001 | 0 | 0 | 75.3494 | 3379.8521 | 75.3494 | 25234.4429 | 28614.2951
| 20496023 | 2024 | SHL001 | 0 | 0 | 82.1585 | 3685.2817 | 82.1585 | 25234.4429 | 28919.7246
| 20496023 | 2025 | SHL001 | 0 | 0 | 68.6923 | 3081.2431 | 68.6923 | 25234.4429 | 28315.686
| 20496023 | 2026 | SHL001 | 0 | 0 | 47.3723 | 2124.9202 | 47.3723 | 25234.4429 | 27359.3631
| 20496023 | 2027 | SHL001 | 0 | 0 | 47.3723 | 2124.9202 | 47.3723 | 25234.4429 | 27359.3631
| 20496023 | 2028 | SHL001 | 0 | 0 | 47.3723 | 2124.9202 | 47.3723 | 25234.4429 | 27359.3631
| 20496023 | 2029 | SHL001 | 0 | 0 | 47.3723 | 2124.9202 | 47.3723 | 25234.4429 | 27359.3631
| 20496023 | 2030 | SHL001 | 0 | 0 | 47.3723 | 2124.9202 | 47.3723 | 25234.4429 | 27359.3631
| 20496023 | 2031 | SHL001 | 0 | 0 | 47.3723 | 2124.9202 | 47.3723 | 25234.4429 | 27359.3631
| 20496023 | 2032 | SHL001 | 0 | 0 | 47.3723 | 2124.9202 | 47.3723 | 25234.4429 | 27359.3631
| 20496023 | 2033 | SHL001 | 0 | 0 | 47.3723 | 2124.9202 | 47.3723 | 25234.4429 | 27359.3631
| 20496023 | 2034 | SHL001 | 0 | 0 | 47.3723 | 2124.9202 | 47.3723 | 25234.4429 | 27359.3631
| 20496034 | 2023 | SHL001 | 0 | 0 | 0 | 0 | 0 | 13122.5334 | 13122.5334
| 20496034 | 2024 | SHL001 | 0 | 0 | 0 | 0 | 0 | 13122.5334 | 13122.5334
| 20496034 | 2025 | SHL001 | 0 | 0 | 0 | 0 | 0 | 13122.5334 | 13122.5334
| 20496034 | 2026 | SHL001 | 0 | 0 | 0 | 0 | 0 | 13122.5334 | 13122.5334
| 20496034 | 2027 | SHL001 | 0 | 0 | 0 | 0 | 0 | 13122.5334 | 13122.5334
| 20496034 | 2028 | SHL001 | 0 | 0 | 0 | 0 | 0 | 13122.5334 | 13122.5334
| 20496034 | 2029 | SHL001 | 0 | 0 | 0 | 0 | 0 | 13122.5334 | 13122.5334
| 20496034 | 2030 | SHL001 | 0 | 0 | 0 | 0 | 0 | 13122.5334 | 13122.5334
| 20496034 | 2031 | SHL001 | 0 | 0 | 0 | 0 | 0 | 13122.5334 | 13122.5334
| 20496034 | 2032 | SHL001 | 0 | 0 | 0 | 0 | 0 | 13122.5334 | 13122.5334
| 20496034 | 2033 | SHL001 | 0 | 0 | 0 | 0 | 0 | 13122.5334 | 13122.5334
| 20496034 | 2034 | SHL001 | 0 | 0 | 0 | 0 | 0 | 13122.5334 | 13122.5334
| 107933921 | 2023 | SHL001 | 0 | 0 | 0 | 0 | 0 | 10716.2155 | 10716.2155
| 107933921 | 2024 | SHL001 | 0 | 0 | 0 | 0 | 0 | 10716.2155 | 10716.2155
| 107933921 | 2025 | SHL001 | 0 | 0 | 0 | 0 | 0 | 10716.2155 | 10716.2155
| 107933921 | 2026 | SHL001 | 0 | 0 | 0 | 0 | 0 | 10716.2155 | 10716.2155
| 107933921 | 2027 | SHL001 | 0 | 0 | 0 | 0 | 0 | 10716.2155 | 10716.2155
| 107933921 | 2028 | SHL001 | 0 | 0 | 0 | 0 | 0 | 10716.2155 | 10716.2155
| 107933921 | 2029 | SHL001 | 0 | 0 | 0 | 0 | 0 | 10716.2155 | 10716.2155
| 107933921 | 2030 | SHL001 | 0 | 0 | 0 | 0 | 0 | 10716.2155 | 10716.2155
| 107933921 | 2031 | SHL001 | 0 | 0 | 0 | 0 | 0 | 10716.2155 | 10716.2155
| 107933921 | 2032 | SHL001 | 0 | 0 | 0 | 0 | 0 | 10716.2155 | 10716.2155
| 107933921 | 2033 | SHL001 | 0 | 0 | 0 | 0 | 0 | 10716.2155 | 10716.2155
| 107933921 | 2034 | SHL001 | 0 | 0 | 0 | 0 | 0 | 10716.2155 | 10716.2155
| 109628139 | 2023 | SHL001 | 0 | 0 | 0 | 0 | 0 | 9478.1608 | 9478.1608
| 109628139 | 2024 | SHL001 | 0 | 0 | 0 | 0 | 0 | 9478.1608 | 9478.1608
| 109628139 | 2025 | SHL001 | 0 | 0 | 0 | 0 | 0 | 9478.1608 | 9478.1608
| 109628139 | 2026 | SHL001 | 0 | 0 | 0 | 0 | 0 | 9478.1608 | 9478.1608
| 109628139 | 2027 | SHL001 | 0 | 0 | 0 | 0 | 0 | 9478.1608 | 9478.1608
| 109628139 | 2028 | SHL001 | 0 | 0 | 0 | 0 | 0 | 9478.1608 | 9478.1608
| 109628139 | 2029 | SHL001 | 0 | 0 | 0 | 0 | 0 | 9478.1608 | 9478.1608
| 109628139 | 2030 | SHL001 | 0 | 0 | 0 | 0 | 0 | 9478.1608 | 9478.1608
| 109628139 | 2031 | SHL001 | 0 | 0 | 0 | 0 | 0 | 9478.1608 | 9478.1608
| 109628139 | 2032 | SHL001 | 0 | 0 | 0 | 0 | 0 | 9478.1608 | 9478.1608
| 109628139 | 2033 | SHL001 | 0 | 0 | 0 | 0 | 0 | 9478.1608 | 9478.1608
| 109628139 | 2034 | SHL001 | 0 | 0 | 0 | 0 | 0 | 9478.1608 | 9478.1608
| 163212783 | 2023 | SHL001 | 492.4507 | 0 | 0 | 0 | 492.4507 | 5240.4225 | 5240.4225
| 163212783 | 2024 | SHL001 | 458.0939 | 6.7448 | 0 | 0 | 458.0939 | 5240.4225 | 5247.1673
| 163212783 | 2025 | SHL001 | 498.3508 | 6.8267 | 0 | 0 | 498.3508 | 5240.4225 | 5247.2492
| 163212783 | 2026 | SHL001 | 681.4656 | 3.9604 | 0 | 0 | 681.4656 | 5240.4225 | 5244.3829
| 163212783 | 2027 | SHL001 | 681.4656 | 3.9604 | 0 | 0 | 681.4656 | 5240.4225 | 5244.3829
| 163212783 | 2028 | SHL001 | 681.4656 | 3.9604 | 0 | 0 | 681.4656 | 5240.4225 | 5244.3829
| 163212783 | 2029 | SHL001 | 681.4656 | 3.9604 | 0 | 0 | 681.4656 | 5240.4225 | 5244.3829
| 163212783 | 2030 | SHL001 | 681.4656 | 3.9604 | 0 | 0 | 681.4656 | 5240.4225 | 5244.3829
| 163212783 | 2031 | SHL001 | 681.4656 | 3.9604 | 0 | 0 | 681.4656 | 5240.4225 | 5244.3829
| 163212783 | 2032 | SHL001 | 681.4656 | 3.9604 | 0 | 0 | 681.4656 | 5240.4225 | 5244.3829
| 163212783 | 2033 | SHL001 | 681.4656 | 3.9604 | 0 | 0 | 681.4656 | 5240.4225 | 5244.3829
| 163212783 | 2034 | SHL001 | 681.4656 | 3.9604 | 0 | 0 | 681.4656 | 5240.4225 | 5244.3829
| 20602534 | 2023 | SHN011 | 0 | 0 | 0 | 0 | 0 | 2432.9631 | 2432.9631
| 20602534 | 2024 | SHN011 | 442.6088 | 5.1505 | 0 | 0 | 442.6088 | 2432.9631 | 2438.1136
| 20602534 | 2025 | SHN011 | 442.6088 | 5.1505 | 0 | 0 | 442.6088 | 2432.9631 | 2438.1136
| 20602534 | 2026 | SHN011 | 442.6088 | 5.1505 | 0 | 0 | 442.6088 | 2432.9631 | 2438.1136
| 20602534 | 2027 | SHN011 | 442.6088 | 5.1505 | 0 | 0 | 442.6088 | 2432.9631 | 2438.1136
| 20602534 | 2028 | SHN011 | 442.6088 | 5.1505 | 0 | 0 | 442.6088 | 2432.9631 | 2438.1136
| 20602534 | 2029 | SHN011 | 442.6088 | 5.1505 | 0 | 0 | 442.6088 | 2432.9631 | 2438.1136
| 20602534 | 2030 | SHN011 | 442.6088 | 5.1505 | 0 | 0 | 442.6088 | 2432.9631 | 2438.1136
| 20602534 | 2031 | SHN011 | 442.6088 | 5.1505 | 0 | 0 | 442.6088 | 2432.9631 | 2438.1136
| 20602534 | 2032 | SHN011 | 442.6088 | 5.1505 | 0 | 0 | 442.6088 | 2432.9631 | 2438.1136
| 20602534 | 2033 | SHN011 | 442.6088 | 5.1505 | 0 | 0 | 442.6088 | 2432.9631 | 2438.1136
| 20602534 | 2034 | SHN011 | 442.6088 | 5.1505 | 0 | 0 | 442.6088 | 2432.9631 | 2438.1136
| 109031579 | 2023 | SHN011 | 7035.6007 | 0 | 0.68067 | 32.0782 | 7036.2814 | 5043.5543 | 5075.6324
| 109031579 | 2024 | SHN011 | 18805.3184 | 360.8994 | 0.32108 | 15.1315 | 18805.6395 | 5043.5543 | 5419.5852
| 109031579 | 2025 | SHN011 | 18805.3184 | 360.8994 | 0.32108 | 15.1315 | 18805.6395 | 5043.5543 | 5419.5852
| 109031579 | 2026 | SHN011 | 18805.3184 | 360.8994 | 0.32108 | 15.1315 | 18805.6395 | 5043.5543 | 5419.5852
| 109031579 | 2027 | SHN011 | 18805.3184 | 360.8994 | 0.32108 | 15.1315 | 18805.6395 | 5043.5543 | 5419.5852
| 109031579 | 2028 | SHN011 | 18805.3184 | 360.8994 | 0.32108 | 15.1315 | 18805.6395 | 5043.5543 | 5419.5852
| 109031579 | 2029 | SHN011 | 18805.3184 | 360.8994 | 0.32108 | 15.1315 | 18805.6395 | 5043.5543 | 5419.5852
| 109031579 | 2030 | SHN011 | 18805.3184 | 360.8994 | 0.32108 | 15.1315 | 18805.6395 | 5043.5543 | 5419.5852
| 109031579 | 2031 | SHN011 | 18805.3184 | 360.8994 | 0.32108 | 15.1315 | 18805.6395 | 5043.5543 | 5419.5852
| 109031579 | 2032 | SHN011 | 18805.3184 | 360.8994 | 0.32108 | 15.1315 | 18805.6395 | 5043.5543 | 5419.5852
| 109031579 | 2033 | SHN011 | 18805.3184 | 360.8994 | 0.32108 | 15.1315 | 18805.6395 | 5043.5543 | 5419.5852
| 109031579 | 2034 | SHN011 | 18805.3184 | 360.8994 | 0.32108 | 15.1315 | 18805.6395 | 5043.5543 | 5419.5852
| 20120064 | 2023 | SHN024 | 0 | 0 | 0 | 0 | 0 | 2897.9274 | 2897.9274
| 20120064 | 2024 | SHN024 | 0 | 0 | 0 | 0 | 0 | 2897.9274 | 2897.9274
| 20120064 | 2025 | SHN024 | 0 | 0 | 0 | 0 | 0 | 2897.9274 | 2897.9274
| 20120064 | 2026 | SHN024 | 0 | 0 | 0 | 0 | 0 | 2897.9274 | 2897.9274
| 20120064 | 2027 | SHN024 | 0 | 0 | 0 | 0 | 0 | 2897.9274 | 2897.9274
| 20120064 | 2028 | SHN024 | 0 | 0 | 0 | 0 | 0 | 2897.9274 | 2897.9274
| 20120064 | 2029 | SHN024 | 0 | 0 | 0 | 0 | 0 | 2897.9274 | 2897.9274
| 20120064 | 2030 | SHN024 | 2.3876 | 2.3876e-12 | 0 | 0 | 2.3876 | 2897.9274 | 2897.9274
| 20120064 | 2031 | SHN024 | 60.2985 | 0.47587 | 0 | 0 | 60.2985 | 2897.9274 | 2898.4033
| 20120064 | 2032 | SHN024 | 148.8285 | 3.1532 | 0 | 0 | 148.8285 | 2897.9274 | 2901.0806
| 20120064 | 2033 | SHN024 | 169.1395 | 4.9641 | 0 | 0 | 169.1395 | 2897.9274 | 2902.8915
| 20120064 | 2034 | SHN024 | 203.5063 | 4.293 | 0 | 0 | 203.5063 | 2897.9274 | 2902.2205
| 20497839 | 2023 | SHN024 | 0 | 0 | 0 | 0 | 0 | 200.4331 | 200.4331
| 20497839 | 2024 | SHN024 | 0 | 0 | 0 | 0 | 0 | 200.4331 | 200.4331
| 20497839 | 2025 | SHN024 | 4.1661 | 0.019088 | 0 | 0 | 4.1661 | 200.4331 | 200.4522
| 20497839 | 2026 | SHN024 | 6.2523 | 0.0070007 | 0 | 0 | 6.2523 | 200.4331 | 200.4401
| 20497839 | 2027 | SHN024 | 62.1703 | 0.12255 | 0 | 0 | 62.1703 | 200.4331 | 200.5556
| 20497839 | 2028 | SHN024 | 167.002 | 0.60885 | 0 | 0 | 167.002 | 200.4331 | 201.0419
| 20497839 | 2029 | SHN024 | 671.8659 | 1.2673 | 0 | 0 | 671.8659 | 200.4331 | 201.7004
| 20497839 | 2030 | SHN024 | 2538.6446 | 6.6977 | 0 | 0 | 2538.6446 | 200.4331 | 207.1308
| 20497839 | 2031 | SHN024 | 2650.2144 | 11.8819 | 0 | 0 | 2650.2144 | 200.4331 | 212.315
| 20497839 | 2032 | SHN024 | 7015.3978 | 72.7564 | 0 | 0 | 7015.3978 | 200.4331 | 273.1895
| 20497839 | 2033 | SHN024 | 6678.0226 | 151.7497 | 0 | 0 | 6678.0226 | 200.4331 | 352.1828
| 20497839 | 2034 | SHN024 | 8899.7293 | 233.8996 | 0 | 0 | 8899.7293 | 200.4331 | 434.3327
| 20497858 | 2023 | SHN024 | 0 | 0 | 0 | 0 | 0 | 995.9984 | 995.9984
| 20497858 | 2024 | SHN024 | 0 | 0 | 0 | 0 | 0 | 995.9984 | 995.9984
| 20497858 | 2025 | SHN024 | 0 | 0 | 0 | 0 | 0 | 995.9984 | 995.9984
| 20497858 | 2026 | SHN024 | 0 | 0 | 0 | 0 | 0 | 995.9984 | 995.9984
| 20497858 | 2027 | SHN024 | 9.7602 | 0.066682 | 0 | 0 | 9.7602 | 995.9984 | 996.065
| 20497858 | 2028 | SHN024 | 543.1046 | 3.4786 | 0 | 0 | 543.1046 | 995.9984 | 999.4769
| 20497858 | 2029 | SHN024 | 511.3401 | 1.2552 | 0 | 0 | 511.3401 | 995.9984 | 997.2536
| 20497858 | 2030 | SHN024 | 587.0662 | 1.3464 | 0 | 0 | 587.0662 | 995.9984 | 997.3448
| 20497858 | 2031 | SHN024 | 763.7613 | 3.6884 | 0 | 0 | 763.7613 | 995.9984 | 999.6868
| 20497858 | 2032 | SHN024 | 872.7349 | 8.503 | 0 | 0 | 872.7349 | 995.9984 | 1004.5014
| 20497858 | 2033 | SHN024 | 842.451 | 18.6592 | 0 | 0 | 842.451 | 995.9984 | 1014.6576
| 20497858 | 2034 | SHN024 | 1060.556 | 27.509 | 0 | 0 | 1060.556 | 995.9984 | 1023.5073
| 196924497 | 2023 | SHP011 | 0 | 0 | 4.7228 | 237.0462 | 4.7228 | 1561.3259 | 1798.3721
| 196924497 | 2024 | SHP011 | 0 | 0 | 5.4254 | 272.308 | 5.4254 | 1561.3259 | 1833.6339
| 196924497 | 2025 | SHP011 | 0 | 0 | 5.5935 | 280.7449 | 5.5935 | 1561.3259 | 1842.0708
| 196924497 | 2026 | SHP011 | 0 | 0 | 4.9701 | 249.4561 | 4.9701 | 1561.3259 | 1810.7819
| 196924497 | 2027 | SHP011 | 0 | 0 | 3.7216 | 186.7921 | 3.7216 | 1561.3259 | 1748.118
| 196924497 | 2028 | SHP011 | 0 | 0 | 4.8931 | 245.5943 | 4.8931 | 1561.3259 | 1806.9202
| 196924497 | 2029 | SHP011 | 0 | 0 | 4.8931 | 245.5943 | 4.8931 | 1561.3259 | 1806.9202
| 196924497 | 2030 | SHP011 | 0 | 0 | 4.8931 | 245.5943 | 4.8931 | 1561.3259 | 1806.9202
| 196924497 | 2031 | SHP011 | 0 | 0 | 4.8931 | 245.5943 | 4.8931 | 1561.3259 | 1806.9202
| 196924497 | 2032 | SHP011 | 0 | 0 | 4.8931 | 245.5943 | 4.8931 | 1561.3259 | 1806.9202
| 196924497 | 2033 | SHP011 | 0 | 0 | 4.8931 | 245.5943 | 4.8931 | 1561.3259 | 1806.9202
| 196924497 | 2034 | SHP011 | 0 | 0 | 4.8931 | 245.5943 | 4.8931 | 1561.3259 | 1806.9202
| 20321424 | 2023 | SHP012 | 0 | 0 | 33827.8171 | 1697873.4407 | 33827.8171 | 5901.9499 | 1703775.3906
| 20321424 | 2024 | SHP012 | 0 | 0 | 33013.8386 | 1657018.5254 | 33013.8386 | 5901.9499 | 1662920.4753
| 20321424 | 2025 | SHP012 | 0 | 0 | 32457.0848 | 1629074.1454 | 32457.0848 | 5901.9499 | 1634976.0953
| 20321424 | 2026 | SHP012 | 0 | 0 | 30908.5794 | 1551352.1247 | 30908.5794 | 5901.9499 | 1557254.0746
| 20321424 | 2027 | SHP012 | 0 | 0 | 30852.2663 | 1548525.6801 | 30852.2663 | 5901.9499 | 1554427.63
| 20321424 | 2028 | SHP012 | 0 | 0 | 66518.6571 | 3338680.138 | 66518.6571 | 5901.9499 | 3344582.0879
| 20321424 | 2029 | SHP012 | 0 | 0 | 66518.6571 | 3338680.138 | 66518.6571 | 5901.9499 | 3344582.0879
| 20321424 | 2030 | SHP012 | 0 | 0 | 66518.6571 | 3338680.138 | 66518.6571 | 5901.9499 | 3344582.0879
| 20321424 | 2031 | SHP012 | 0 | 0 | 92803.2479 | 4657946.7187 | 92803.2479 | 5901.9499 | 4663848.6686
| 20321424 | 2032 | SHP012 | 0 | 0 | 92803.2479 | 4657946.7187 | 92803.2479 | 5901.9499 | 4663848.6686
| 20321424 | 2033 | SHP012 | 0 | 0 | 92803.2479 | 4657946.7187 | 92803.2479 | 5901.9499 | 4663848.6686
| 20321424 | 2034 | SHP012 | 0 | 0 | 92803.2479 | 4657946.7187 | 92803.2479 | 5901.9499 | 4663848.6686
| 20336332 | 2023 | SHP012 | 0 | 0 | 0 | 0 | 0 | 3965.7209 | 3965.7209
| 20336332 | 2024 | SHP012 | 0 | 0 | 0 | 0 | 0 | 3965.7209 | 3965.7209
| 20336332 | 2025 | SHP012 | 0 | 0 | 0.087988 | 4.4162 | 0.087988 | 3965.7209 | 3970.1371
| 20336332 | 2026 | SHP012 | 0 | 0 | 0.28132 | 14.1197 | 0.28132 | 3965.7209 | 3979.8406
| 20336332 | 2027 | SHP012 | 0 | 0 | 2.0999 | 105.3979 | 2.0999 | 3965.7209 | 4071.1187
| 20336332 | 2028 | SHP012 | 0 | 0 | 7775.0197 | 390240.949 | 7775.0197 | 3965.7209 | 394206.6699
| 20336332 | 2029 | SHP012 | 0 | 0 | 7775.0197 | 390240.949 | 7775.0197 | 3965.7209 | 394206.6699
| 20336332 | 2030 | SHP012 | 0 | 0 | 7775.0197 | 390240.949 | 7775.0197 | 3965.7209 | 394206.6699
| 20336332 | 2031 | SHP012 | 0 | 0 | 22740.1901 | 1141367.3134 | 22740.1901 | 3965.7209 | 1145333.0342
| 20336332 | 2032 | SHP012 | 0 | 0 | 22740.1901 | 1141367.3134 | 22740.1901 | 3965.7209 | 1145333.0342
| 20336332 | 2033 | SHP012 | 0 | 0 | 22740.1901 | 1141367.3134 | 22740.1901 | 3965.7209 | 1145333.0342
| 20336332 | 2034 | SHP012 | 0 | 0 | 22740.1901 | 1141367.3134 | 22740.1901 | 3965.7209 | 1145333.0342
| 20336438 | 2023 | SHP012 | 1.0583 | 0 | 0 | 0 | 1.0583 | 3814.5879 | 3814.5879
| 20336438 | 2024 | SHP012 | 4.0459 | 0.35087 | 0 | 0 | 4.0459 | 3814.5879 | 3814.9388
| 20336438 | 2025 | SHP012 | 2.1497 | 0.17925 | 0 | 0 | 2.1497 | 3814.5879 | 3814.7672
| 20336438 | 2026 | SHP012 | 8.4964 | 0.54857 | 0 | 0 | 8.4964 | 3814.5879 | 3815.1365
| 20336438 | 2027 | SHP012 | 3.2184 | 0.36662 | 0 | 0 | 3.2184 | 3814.5879 | 3814.9546
| 20336438 | 2028 | SHP012 | 6.4843 | 0.466 | 0 | 0 | 6.4843 | 3814.5879 | 3815.0539
| 20336438 | 2029 | SHP012 | 6.4843 | 0.466 | 0 | 0 | 6.4843 | 3814.5879 | 3815.0539
| 20336438 | 2030 | SHP012 | 6.4843 | 0.466 | 0 | 0 | 6.4843 | 3814.5879 | 3815.0539
| 20336438 | 2031 | SHP012 | 11.8932 | 0.35225 | 0.15868 | 7.9643 | 12.0519 | 3814.5879 | 3822.9045
| 20336438 | 2032 | SHP012 | 11.8932 | 0.35225 | 0.15868 | 7.9643 | 12.0519 | 3814.5879 | 3822.9045
| 20336438 | 2033 | SHP012 | 11.8932 | 0.35225 | 0.15868 | 7.9643 | 12.0519 | 3814.5879 | 3822.9045
| 20336438 | 2034 | SHP012 | 11.8932 | 0.35225 | 0.15868 | 7.9643 | 12.0519 | 3814.5879 | 3822.9045
| 182057941 | 2023 | SHP012 | 1622.081 | 0 | 0 | 0 | 1622.081 | 4949.8772 | 4949.8772
| 182057941 | 2024 | SHP012 | 1898.8067 | 48.6399 | 0 | 0 | 1898.8067 | 4949.8772 | 4998.5171
| 182057941 | 2025 | SHP012 | 2571.35 | 65.9999 | 0 | 0 | 2571.35 | 4949.8772 | 5015.8771
| 182057941 | 2026 | SHP012 | 2477.0468 | 35.6274 | 0 | 0 | 2477.0468 | 4949.8772 | 4985.5047
| 182057941 | 2027 | SHP012 | 2319.4791 | 27.7475 | 0 | 0 | 2319.4791 | 4949.8772 | 4977.6247
| 182057941 | 2028 | SHP012 | 9536.0592 | 160.5636 | 15.2595 | 765.8984 | 9551.3187 | 4949.8772 | 5876.3392
| 182057941 | 2029 | SHP012 | 9536.0592 | 160.5636 | 15.2595 | 765.8984 | 9551.3187 | 4949.8772 | 5876.3392
| 182057941 | 2030 | SHP012 | 9536.0592 | 160.5636 | 15.2595 | 765.8984 | 9551.3187 | 4949.8772 | 5876.3392
| 182057941 | 2031 | SHP012 | 8407.9301 | 118.5586 | 504.1319 | 25303.2034 | 8912.062 | 4949.8772 | 30371.6392
| 182057941 | 2032 | SHP012 | 8407.9301 | 118.5586 | 504.1319 | 25303.2034 | 8912.062 | 4949.8772 | 30371.6392
| 182057941 | 2033 | SHP012 | 8407.9301 | 118.5586 | 504.1319 | 25303.2034 | 8912.062 | 4949.8772 | 30371.6392
| 182057941 | 2034 | SHP012 | 8407.9301 | 118.5586 | 504.1319 | 25303.2034 | 8912.062 | 4949.8772 | 30371.6392
| 20357159 | 2023 | SHP014 | 0 | 0 | 42440.3029 | 2130148.1809 | 42440.3029 | 1815.9669 | 2131964.1478
| 20357159 | 2024 | SHP014 | 0 | 0 | 43283.6028 | 2172474.7779 | 43283.6028 | 1815.9669 | 2174290.7449
| 20357159 | 2025 | SHP014 | 0 | 0 | 43236.5429 | 2170112.7655 | 43236.5429 | 1815.9669 | 2171928.7325
| 20357159 | 2026 | SHP014 | 0 | 0 | 42479.4366 | 2132112.3623 | 42479.4366 | 1815.9669 | 2133928.3293
| 20357159 | 2027 | SHP014 | 0 | 0 | 42772.4715 | 2146820.2631 | 42772.4715 | 1815.9669 | 2148636.23
| 20357159 | 2028 | SHP014 | 0 | 0 | 42067.1924 | 2111421.1511 | 42067.1924 | 1815.9669 | 2113237.118
| 20357159 | 2029 | SHP014 | 0 | 0 | 42222.617 | 2119222.17 | 42222.617 | 1815.9669 | 2121038.1369
| 20357159 | 2030 | SHP014 | 0 | 0 | 42222.617 | 2119222.17 | 42222.617 | 1815.9669 | 2121038.1369
| 20357159 | 2031 | SHP014 | 0 | 0 | 42222.617 | 2119222.17 | 42222.617 | 1815.9669 | 2121038.1369
| 20357159 | 2032 | SHP014 | 0 | 0 | 42222.617 | 2119222.17 | 42222.617 | 1815.9669 | 2121038.1369
| 20357159 | 2033 | SHP014 | 0 | 0 | 42222.617 | 2119222.17 | 42222.617 | 1815.9669 | 2121038.1369
| 20357159 | 2034 | SHP014 | 0 | 0 | 42222.617 | 2119222.17 | 42222.617 | 1815.9669 | 2121038.1369
| 20532014 | 2023 | SHP014 | 29.0461 | 0 | 0 | 0 | 29.0461 | 3621.8893 | 3621.8893
| 20532014 | 2024 | SHP014 | 59.0709 | 0.51293 | 0 | 0 | 59.0709 | 3621.8893 | 3622.4022
| 20532014 | 2025 | SHP014 | 4038.5039 | 61.7778 | 0 | 0 | 4038.5039 | 3621.8893 | 3683.6671
| 20532014 | 2026 | SHP014 | 5462.4596 | 33.8662 | 0 | 0 | 5462.4596 | 3621.8893 | 3655.7555
| 20532014 | 2027 | SHP014 | 9231.7024 | 63.3892 | 0 | 0 | 9231.7024 | 3621.8893 | 3685.2785
| 20532014 | 2028 | SHP014 | 14119.341 | 116.1239 | 0 | 0 | 14119.341 | 3621.8893 | 3738.0132
| 20532014 | 2029 | SHP014 | 18311.4954 | 103.1381 | 0 | 0 | 18311.4954 | 3621.8893 | 3725.0275
| 20532014 | 2030 | SHP014 | 18311.4954 | 103.1381 | 0 | 0 | 18311.4954 | 3621.8893 | 3725.0275
| 20532014 | 2031 | SHP014 | 18311.4954 | 103.1381 | 0 | 0 | 18311.4954 | 3621.8893 | 3725.0275
| 20532014 | 2032 | SHP014 | 18311.4954 | 103.1381 | 0 | 0 | 18311.4954 | 3621.8893 | 3725.0275
| 20532014 | 2033 | SHP014 | 18311.4954 | 103.1381 | 0 | 0 | 18311.4954 | 3621.8893 | 3725.0275
| 20532014 | 2034 | SHP014 | 18311.4954 | 103.1381 | 0 | 0 | 18311.4954 | 3621.8893 | 3725.0275
| 20098479 | 2023 | STL005 | 0 | 0 | 20.0726 | 949.7686 | 20.0726 | 6803.1336 | 7752.9022
| 20098479 | 2024 | STL005 | 0 | 0 | 30.801 | 1457.4034 | 30.801 | 6803.1336 | 8260.537
| 20098479 | 2025 | STL005 | 0 | 0 | 28.3154 | 1339.7935 | 28.3154 | 6803.1336 | 8142.9271
| 20098479 | 2026 | STL005 | 0 | 0 | 36.5526 | 1729.5497 | 36.5526 | 6803.1336 | 8532.6833
| 20098479 | 2027 | STL005 | 0 | 0 | 30.7845 | 1456.624 | 30.7845 | 6803.1336 | 8259.7577
| 20098479 | 2028 | STL005 | 0 | 0 | 23.7127 | 1122.0085 | 23.7127 | 6803.1336 | 7925.1421
| 20098479 | 2029 | STL005 | 0 | 0 | 15.97 | 755.6478 | 15.97 | 6803.1336 | 7558.7814
| 20098479 | 2030 | STL005 | 0 | 0 | 12.2798 | 581.04 | 12.2798 | 6803.1336 | 7384.1736
| 20098479 | 2031 | STL005 | 0 | 0 | 12.2798 | 581.04 | 12.2798 | 6803.1336 | 7384.1736
| 20098479 | 2032 | STL005 | 0 | 0 | 12.2798 | 581.04 | 12.2798 | 6803.1336 | 7384.1736
| 20098479 | 2033 | STL005 | 0 | 0 | 12.2798 | 581.04 | 12.2798 | 6803.1336 | 7384.1736
| 20098479 | 2034 | STL005 | 0 | 0 | 12.2798 | 581.04 | 12.2798 | 6803.1336 | 7384.1736
| 20101686 | 2023 | STL005 | 0 | 0 | 0 | 0 | 0 | 8027.3349 | 8027.3349
| 20101686 | 2024 | STL005 | 0 | 0 | 0 | 0 | 0 | 8027.3349 | 8027.3349
| 20101686 | 2025 | STL005 | 0 | 0 | 0 | 0 | 0 | 8027.3349 | 8027.3349
| 20101686 | 2026 | STL005 | 0 | 0 | 0 | 0 | 0 | 8027.3349 | 8027.3349
| 20101686 | 2027 | STL005 | 0 | 0 | 0 | 0 | 0 | 8027.3349 | 8027.3349
| 20101686 | 2028 | STL005 | 0 | 0 | 0 | 0 | 0 | 8027.3349 | 8027.3349
| 20101686 | 2029 | STL005 | 0 | 0 | 14.5776 | 689.7647 | 14.5776 | 8027.3349 | 8717.0995
| 20101686 | 2030 | STL005 | 0 | 0 | 467.4796 | 22119.6033 | 467.4796 | 8027.3349 | 30146.9381
| 20101686 | 2031 | STL005 | 0 | 0 | 467.4796 | 22119.6033 | 467.4796 | 8027.3349 | 30146.9381
| 20101686 | 2032 | STL005 | 0 | 0 | 467.4796 | 22119.6033 | 467.4796 | 8027.3349 | 30146.9381
| 20101686 | 2033 | STL005 | 0 | 0 | 467.4796 | 22119.6033 | 467.4796 | 8027.3349 | 30146.9381
| 20101686 | 2034 | STL005 | 0 | 0 | 467.4796 | 22119.6033 | 467.4796 | 8027.3349 | 30146.9381
| 20102111 | 2023 | STL005 | 8800.8586 | 0 | 0 | 0 | 8800.8586 | 572.2971 | 572.2971
| 20102111 | 2024 | STL005 | 12491.9944 | 277.3668 | 0 | 0 | 12491.9944 | 572.2971 | 849.6639
| 20102111 | 2025 | STL005 | 12470.859 | 253.9235 | 0 | 0 | 12470.859 | 572.2971 | 826.2205
| 20102111 | 2026 | STL005 | 17285.0964 | 188.2795 | 0 | 0 | 17285.0964 | 572.2971 | 760.5766
| 20102111 | 2027 | STL005 | 18054.6933 | 175.6027 | 0 | 0 | 18054.6933 | 572.2971 | 747.8998
| 20102111 | 2028 | STL005 | 18847.1785 | 206.3985 | 0 | 0 | 18847.1785 | 572.2971 | 778.6955
| 20102111 | 2029 | STL005 | 18808.5628 | 157.6511 | 0.025268 | 1.1956 | 18808.5881 | 572.2971 | 731.1437
| 20102111 | 2030 | STL005 | 26140.8596 | 250.2012 | 2.6588 | 125.805 | 26143.5184 | 572.2971 | 948.3033
| 20102111 | 2031 | STL005 | 26140.8596 | 250.2012 | 2.6588 | 125.805 | 26143.5184 | 572.2971 | 948.3033
| 20102111 | 2032 | STL005 | 26140.8596 | 250.2012 | 2.6588 | 125.805 | 26143.5184 | 572.2971 | 948.3033
| 20102111 | 2033 | STL005 | 26140.8596 | 250.2012 | 2.6588 | 125.805 | 26143.5184 | 572.2971 | 948.3033
| 20102111 | 2034 | STL005 | 26140.8596 | 250.2012 | 2.6588 | 125.805 | 26143.5184 | 572.2971 | 948.3033
| 20102250 | 2023 | STL005 | 461.3282 | 0 | 0 | 0 | 461.3282 | 879.3687 | 879.3687
| 20102250 | 2024 | STL005 | 2104.1651 | 39.2365 | 0 | 0 | 2104.1651 | 879.3687 | 918.6051
| 20102250 | 2025 | STL005 | 2025.4042 | 35.7286 | 0 | 0 | 2025.4042 | 879.3687 | 915.0973
| 20102250 | 2026 | STL005 | 2336.9209 | 20.8518 | 0 | 0 | 2336.9209 | 879.3687 | 900.2204
| 20102250 | 2027 | STL005 | 2669.4291 | 22.5236 | 0 | 0 | 2669.4291 | 879.3687 | 901.8923
| 20102250 | 2028 | STL005 | 2967.2016 | 27.744 | 0 | 0 | 2967.2016 | 879.3687 | 907.1126
| 20102250 | 2029 | STL005 | 3278.245 | 23.8239 | 0 | 0 | 3278.245 | 879.3687 | 903.1926
| 20102250 | 2030 | STL005 | 3296.4968 | 26.9913 | 0 | 0 | 3296.4968 | 879.3687 | 906.36
| 20102250 | 2031 | STL005 | 3296.4968 | 26.9913 | 0 | 0 | 3296.4968 | 879.3687 | 906.36
| 20102250 | 2032 | STL005 | 3296.4968 | 26.9913 | 0 | 0 | 3296.4968 | 879.3687 | 906.36
| 20102250 | 2033 | STL005 | 3296.4968 | 26.9913 | 0 | 0 | 3296.4968 | 879.3687 | 906.36
| 20102250 | 2034 | STL005 | 3296.4968 | 26.9913 | 0 | 0 | 3296.4968 | 879.3687 | 906.36
| 20548557 | 2023 | STL005 | 1865.8388 | 0 | 0 | 0 | 1865.8388 | 1489.759 | 1489.759
| 20548557 | 2024 | STL005 | 2328.9069 | 40.2245 | 0 | 0 | 2328.9069 | 1489.759 | 1529.9836
| 20548557 | 2025 | STL005 | 2239.6907 | 38.5464 | 0 | 0 | 2239.6907 | 1489.759 | 1528.3054
| 20548557 | 2026 | STL005 | 3299.2114 | 23.6056 | 0 | 0 | 3299.2114 | 1489.759 | 1513.3646
| 20548557 | 2027 | STL005 | 4819.1285 | 31.4535 | 0 | 0 | 4819.1285 | 1489.759 | 1521.2126
| 20548557 | 2028 | STL005 | 5471.7233 | 38.3941 | 0 | 0 | 5471.7233 | 1489.759 | 1528.1531
| 20548557 | 2029 | STL005 | 12931.3385 | 133.9647 | 0 | 0 | 12931.3385 | 1489.759 | 1623.7237
| 20548557 | 2030 | STL005 | 12325.3658 | 133.0353 | 1.1354 | 53.7222 | 12326.5012 | 1489.759 | 1676.5166
| 20548557 | 2031 | STL005 | 12325.3658 | 133.0353 | 1.1354 | 53.7222 | 12326.5012 | 1489.759 | 1676.5166
| 20548557 | 2032 | STL005 | 12325.3658 | 133.0353 | 1.1354 | 53.7222 | 12326.5012 | 1489.759 | 1676.5166
| 20548557 | 2033 | STL005 | 12325.3658 | 133.0353 | 1.1354 | 53.7222 | 12326.5012 | 1489.759 | 1676.5166
| 20548557 | 2034 | STL005 | 12325.3658 | 133.0353 | 1.1354 | 53.7222 | 12326.5012 | 1489.759 | 1676.5166
| 186998791 | 2023 | STL005 | 1774.2902 | 0 | 0 | 0 | 1774.2902 | 1275.8483 | 1275.8483
| 186998791 | 2024 | STL005 | 3364.3161 | 66.989 | 0 | 0 | 3364.3161 | 1275.8483 | 1342.8373
| 186998791 | 2025 | STL005 | 3343.7659 | 66.1216 | 0 | 0 | 3343.7659 | 1275.8483 | 1341.9699
| 186998791 | 2026 | STL005 | 3926.8775 | 41.7856 | 0 | 0 | 3926.8775 | 1275.8483 | 1317.6339
| 186998791 | 2027 | STL005 | 12462.5614 | 116.5725 | 0 | 0 | 12462.5614 | 1275.8483 | 1392.4208
| 186998791 | 2028 | STL005 | 16071.6218 | 157.8401 | 0 | 0 | 16071.6218 | 1275.8483 | 1433.6884
| 186998791 | 2029 | STL005 | 16804.4439 | 125.4047 | 0 | 0 | 16804.4439 | 1275.8483 | 1401.253
| 186998791 | 2030 | STL005 | 16983.1772 | 135.3049 | 0.41047 | 19.4222 | 16983.5877 | 1275.8483 | 1430.5754
| 186998791 | 2031 | STL005 | 16983.1772 | 135.3049 | 0.41047 | 19.4222 | 16983.5877 | 1275.8483 | 1430.5754
| 186998791 | 2032 | STL005 | 16983.1772 | 135.3049 | 0.41047 | 19.4222 | 16983.5877 | 1275.8483 | 1430.5754
| 186998791 | 2033 | STL005 | 16983.1772 | 135.3049 | 0.41047 | 19.4222 | 16983.5877 | 1275.8483 | 1430.5754
| 186998791 | 2034 | STL005 | 16983.1772 | 135.3049 | 0.41047 | 19.4222 | 16983.5877 | 1275.8483 | 1430.5754
| 198192939 | 2023 | STL005 | 0 | 0 | 0 | 0 | 0 | 6517.7662 | 6517.7662
| 198192939 | 2024 | STL005 | 0 | 0 | 0 | 0 | 0 | 6517.7662 | 6517.7662
| 198192939 | 2025 | STL005 | 0 | 0 | 0 | 0 | 0 | 6517.7662 | 6517.7662
| 198192939 | 2026 | STL005 | 0 | 0 | 0 | 0 | 0 | 6517.7662 | 6517.7662
| 198192939 | 2027 | STL005 | 0 | 0 | 0 | 0 | 0 | 6517.7662 | 6517.7662
| 198192939 | 2028 | STL005 | 82.8734 | 0.19082 | 0 | 0 | 82.8734 | 6517.7662 | 6517.957
| 198192939 | 2029 | STL005 | 386.2532 | 0.82203 | 0 | 0 | 386.2532 | 6517.7662 | 6518.5882
| 198192939 | 2030 | STL005 | 1372.8321 | 5.162 | 0 | 0 | 1372.8321 | 6517.7662 | 6522.9281
| 198192939 | 2031 | STL005 | 1372.8321 | 5.162 | 0 | 0 | 1372.8321 | 6517.7662 | 6522.9281
| 198192939 | 2032 | STL005 | 1372.8321 | 5.162 | 0 | 0 | 1372.8321 | 6517.7662 | 6522.9281
| 198192939 | 2033 | STL005 | 1372.8321 | 5.162 | 0 | 0 | 1372.8321 | 6517.7662 | 6522.9281
| 198192939 | 2034 | STL005 | 1372.8321 | 5.162 | 0 | 0 | 1372.8321 | 6517.7662 | 6522.9281
| 19938359 | 2023 | STL006 | 0 | 0 | 0 | 0 | 0 | 96.3378 | 96.3378
| 19938359 | 2024 | STL006 | 0 | 0 | 0 | 0 | 0 | 96.3378 | 96.3378
| 19938359 | 2025 | STL006 | 0 | 0 | 0 | 0 | 0 | 96.3378 | 96.3378
| 19938359 | 2026 | STL006 | 0 | 0 | 0 | 0 | 0 | 96.3378 | 96.3378
| 19938359 | 2027 | STL006 | 0 | 0 | 0 | 0 | 0 | 96.3378 | 96.3378
| 19938359 | 2028 | STL006 | 0 | 0 | 0 | 0 | 0 | 96.3378 | 96.3378
| 19938359 | 2029 | STL006 | 0 | 0 | 0 | 0 | 0 | 96.3378 | 96.3378
| 19938359 | 2030 | STL006 | 0 | 0 | 0 | 0 | 0 | 96.3378 | 96.3378
| 19938359 | 2031 | STL006 | 0 | 0 | 0 | 0 | 0 | 96.3378 | 96.3378
| 19938359 | 2032 | STL006 | 0 | 0 | 0 | 0 | 0 | 96.3378 | 96.3378
| 19938359 | 2033 | STL006 | 0 | 0 | 0 | 0 | 0 | 96.3378 | 96.3378
| 19938359 | 2034 | STL006 | 0 | 0 | 0 | 0 | 0 | 96.3378 | 96.3378
| 19941169 | 2023 | STL006 | 0 | 0 | 13.8562 | 655.6321 | 13.8562 | 4916.7068 | 5572.3389
| 19941169 | 2024 | STL006 | 0 | 0 | 16.5466 | 782.9302 | 16.5466 | 4916.7068 | 5699.637
| 19941169 | 2025 | STL006 | 0 | 0 | 35.7789 | 1692.9404 | 35.7789 | 4916.7068 | 6609.6472
| 19941169 | 2026 | STL006 | 0 | 0 | 58.6137 | 2773.4083 | 58.6137 | 4916.7068 | 7690.1151
| 19941169 | 2027 | STL006 | 0 | 0 | 58.6137 | 2773.4083 | 58.6137 | 4916.7068 | 7690.1151
| 19941169 | 2028 | STL006 | 0 | 0 | 58.6137 | 2773.4083 | 58.6137 | 4916.7068 | 7690.1151
| 19941169 | 2029 | STL006 | 0 | 0 | 58.6137 | 2773.4083 | 58.6137 | 4916.7068 | 7690.1151
| 19941169 | 2030 | STL006 | 0 | 0 | 58.6137 | 2773.4083 | 58.6137 | 4916.7068 | 7690.1151
| 19941169 | 2031 | STL006 | 0 | 0 | 58.6137 | 2773.4083 | 58.6137 | 4916.7068 | 7690.1151
| 19941169 | 2032 | STL006 | 0 | 0 | 58.6137 | 2773.4083 | 58.6137 | 4916.7068 | 7690.1151
| 19941169 | 2033 | STL006 | 0 | 0 | 58.6137 | 2773.4083 | 58.6137 | 4916.7068 | 7690.1151
| 19941169 | 2034 | STL006 | 0 | 0 | 58.6137 | 2773.4083 | 58.6137 | 4916.7068 | 7690.1151
| 19943260 | 2023 | STL006 | 5.1913 | 0 | 0 | 0 | 5.1913 | 4362.5606 | 4362.5606
| 19943260 | 2024 | STL006 | 2.417 | 0.038213 | 0 | 0 | 2.417 | 4362.5606 | 4362.5988
| 19943260 | 2025 | STL006 | 52.882 | 0.94355 | 0 | 0 | 52.882 | 4362.5606 | 4363.5042
| 19943260 | 2026 | STL006 | 154.5205 | 0.64822 | 0 | 0 | 154.5205 | 4362.5606 | 4363.2089
| 19943260 | 2027 | STL006 | 154.5205 | 0.64822 | 0 | 0 | 154.5205 | 4362.5606 | 4363.2089
| 19943260 | 2028 | STL006 | 154.5205 | 0.64822 | 0 | 0 | 154.5205 | 4362.5606 | 4363.2089
| 19943260 | 2029 | STL006 | 154.5205 | 0.64822 | 0 | 0 | 154.5205 | 4362.5606 | 4363.2089
| 19943260 | 2030 | STL006 | 154.5205 | 0.64822 | 0 | 0 | 154.5205 | 4362.5606 | 4363.2089
| 19943260 | 2031 | STL006 | 154.5205 | 0.64822 | 0 | 0 | 154.5205 | 4362.5606 | 4363.2089
| 19943260 | 2032 | STL006 | 154.5205 | 0.64822 | 0 | 0 | 154.5205 | 4362.5606 | 4363.2089
| 19943260 | 2033 | STL006 | 154.5205 | 0.64822 | 0 | 0 | 154.5205 | 4362.5606 | 4363.2089
| 19943260 | 2034 | STL006 | 154.5205 | 0.64822 | 0 | 0 | 154.5205 | 4362.5606 | 4363.2089
| 19943978 | 2023 | STL006 | 0 | 0 | 6018.3963 | 284770.8217 | 6018.3963 | 8645.8489 | 293416.6706
| 19943978 | 2024 | STL006 | 0 | 0 | 6423.3215 | 303930.5573 | 6423.3215 | 8645.8489 | 312576.4061
| 19943978 | 2025 | STL006 | 0 | 0 | 6145.6211 | 290790.6828 | 6145.6211 | 8645.8489 | 299436.5317
| 19943978 | 2026 | STL006 | 0 | 0 | 5689.0073 | 269185.2123 | 5689.0073 | 8645.8489 | 277831.0611
| 19943978 | 2027 | STL006 | 0 | 0 | 5689.0073 | 269185.2123 | 5689.0073 | 8645.8489 | 277831.0611
| 19943978 | 2028 | STL006 | 0 | 0 | 5689.0073 | 269185.2123 | 5689.0073 | 8645.8489 | 277831.0611
| 19943978 | 2029 | STL006 | 0 | 0 | 5689.0073 | 269185.2123 | 5689.0073 | 8645.8489 | 277831.0611
| 19943978 | 2030 | STL006 | 0 | 0 | 5689.0073 | 269185.2123 | 5689.0073 | 8645.8489 | 277831.0611
| 19943978 | 2031 | STL006 | 0 | 0 | 5689.0073 | 269185.2123 | 5689.0073 | 8645.8489 | 277831.0611
| 19943978 | 2032 | STL006 | 0 | 0 | 5689.0073 | 269185.2123 | 5689.0073 | 8645.8489 | 277831.0611
| 19943978 | 2033 | STL006 | 0 | 0 | 5689.0073 | 269185.2123 | 5689.0073 | 8645.8489 | 277831.0611
| 19943978 | 2034 | STL006 | 0 | 0 | 5689.0073 | 269185.2123 | 5689.0073 | 8645.8489 | 277831.0611
| 19944117 | 2023 | STL006 | 0 | 0 | 5810.7752 | 274946.8729 | 5810.7752 | 7797.5123 | 282744.3852
| 19944117 | 2024 | STL006 | 0 | 0 | 6336.8744 | 299840.1631 | 6336.8744 | 7797.5123 | 307637.6753
| 19944117 | 2025 | STL006 | 0 | 0 | 6103.967 | 288819.7498 | 6103.967 | 7797.5123 | 296617.2621
| 19944117 | 2026 | STL006 | 0 | 0 | 6027.7359 | 285212.7405 | 6027.7359 | 7797.5123 | 293010.2528
| 19944117 | 2027 | STL006 | 0 | 0 | 6027.7359 | 285212.7405 | 6027.7359 | 7797.5123 | 293010.2528
| 19944117 | 2028 | STL006 | 0 | 0 | 6027.7359 | 285212.7405 | 6027.7359 | 7797.5123 | 293010.2528
| 19944117 | 2029 | STL006 | 0 | 0 | 6027.7359 | 285212.7405 | 6027.7359 | 7797.5123 | 293010.2528
| 19944117 | 2030 | STL006 | 0 | 0 | 6027.7359 | 285212.7405 | 6027.7359 | 7797.5123 | 293010.2528
| 19944117 | 2031 | STL006 | 0 | 0 | 6027.7359 | 285212.7405 | 6027.7359 | 7797.5123 | 293010.2528
| 19944117 | 2032 | STL006 | 0 | 0 | 6027.7359 | 285212.7405 | 6027.7359 | 7797.5123 | 293010.2528
| 19944117 | 2033 | STL006 | 0 | 0 | 6027.7359 | 285212.7405 | 6027.7359 | 7797.5123 | 293010.2528
| 19944117 | 2034 | STL006 | 0 | 0 | 6027.7359 | 285212.7405 | 6027.7359 | 7797.5123 | 293010.2528
| 19946974 | 2023 | STL006 | 40.9719 | 0 | 20.1112 | 951.5941 | 61.0831 | 11917.1034 | 12868.6975
| 19946974 | 2024 | STL006 | 61.6301 | 1.5006 | 26.26 | 1242.5366 | 87.8901 | 11917.1034 | 13161.1406
| 19946974 | 2025 | STL006 | 652.4031 | 9.3648 | 22.8094 | 1079.265 | 675.2124 | 11917.1034 | 13005.7332
| 19946974 | 2026 | STL006 | 10010.6955 | 53.6268 | 15.4857 | 732.7348 | 10026.1813 | 11917.1034 | 12703.465
| 19946974 | 2027 | STL006 | 10010.6955 | 53.6268 | 15.4857 | 732.7348 | 10026.1813 | 11917.1034 | 12703.465
| 19946974 | 2028 | STL006 | 10010.6955 | 53.6268 | 15.4857 | 732.7348 | 10026.1813 | 11917.1034 | 12703.465
| 19946974 | 2029 | STL006 | 10010.6955 | 53.6268 | 15.4857 | 732.7348 | 10026.1813 | 11917.1034 | 12703.465
| 19946974 | 2030 | STL006 | 10010.6955 | 53.6268 | 15.4857 | 732.7348 | 10026.1813 | 11917.1034 | 12703.465
| 19946974 | 2031 | STL006 | 10010.6955 | 53.6268 | 15.4857 | 732.7348 | 10026.1813 | 11917.1034 | 12703.465
| 19946974 | 2032 | STL006 | 10010.6955 | 53.6268 | 15.4857 | 732.7348 | 10026.1813 | 11917.1034 | 12703.465
| 19946974 | 2033 | STL006 | 10010.6955 | 53.6268 | 15.4857 | 732.7348 | 10026.1813 | 11917.1034 | 12703.465
| 19946974 | 2034 | STL006 | 10010.6955 | 53.6268 | 15.4857 | 732.7348 | 10026.1813 | 11917.1034 | 12703.465
| 19947080 | 2023 | STL006 | 141.566 | 0 | 0 | 0 | 141.566 | 4768.5754 | 4768.5754
| 19947080 | 2024 | STL006 | 114.3068 | 1.7166 | 0 | 0 | 114.3068 | 4768.5754 | 4770.292
| 19947080 | 2025 | STL006 | 178.9548 | 4.3646 | 0 | 0 | 178.9548 | 4768.5754 | 4772.94
| 19947080 | 2026 | STL006 | 111.0207 | 2.1082 | 0 | 0 | 111.0207 | 4768.5754 | 4770.6836
| 19947080 | 2027 | STL006 | 111.0207 | 2.1082 | 0 | 0 | 111.0207 | 4768.5754 | 4770.6836
| 19947080 | 2028 | STL006 | 111.0207 | 2.1082 | 0 | 0 | 111.0207 | 4768.5754 | 4770.6836
| 19947080 | 2029 | STL006 | 111.0207 | 2.1082 | 0 | 0 | 111.0207 | 4768.5754 | 4770.6836
| 19947080 | 2030 | STL006 | 111.0207 | 2.1082 | 0 | 0 | 111.0207 | 4768.5754 | 4770.6836
| 19947080 | 2031 | STL006 | 111.0207 | 2.1082 | 0 | 0 | 111.0207 | 4768.5754 | 4770.6836
| 19947080 | 2032 | STL006 | 111.0207 | 2.1082 | 0 | 0 | 111.0207 | 4768.5754 | 4770.6836
| 19947080 | 2033 | STL006 | 111.0207 | 2.1082 | 0 | 0 | 111.0207 | 4768.5754 | 4770.6836
| 19947080 | 2034 | STL006 | 111.0207 | 2.1082 | 0 | 0 | 111.0207 | 4768.5754 | 4770.6836
| 19947175 | 2023 | STL006 | 0 | 0 | 0 | 0 | 0 | 3477.6373 | 3477.6373
| 19947175 | 2024 | STL006 | 0 | 0 | 0 | 0 | 0 | 3477.6373 | 3477.6373
| 19947175 | 2025 | STL006 | 0 | 0 | 0 | 0 | 0 | 3477.6373 | 3477.6373
| 19947175 | 2026 | STL006 | 0 | 0 | 0 | 0 | 0 | 3477.6373 | 3477.6373
| 19947175 | 2027 | STL006 | 0 | 0 | 0 | 0 | 0 | 3477.6373 | 3477.6373
| 19947175 | 2028 | STL006 | 0 | 0 | 0 | 0 | 0 | 3477.6373 | 3477.6373
| 19947175 | 2029 | STL006 | 0 | 0 | 0 | 0 | 0 | 3477.6373 | 3477.6373
| 19947175 | 2030 | STL006 | 0 | 0 | 0 | 0 | 0 | 3477.6373 | 3477.6373
| 19947175 | 2031 | STL006 | 0 | 0 | 0 | 0 | 0 | 3477.6373 | 3477.6373
| 19947175 | 2032 | STL006 | 0 | 0 | 0 | 0 | 0 | 3477.6373 | 3477.6373
| 19947175 | 2033 | STL006 | 0 | 0 | 0 | 0 | 0 | 3477.6373 | 3477.6373
| 19947175 | 2034 | STL006 | 0 | 0 | 0 | 0 | 0 | 3477.6373 | 3477.6373
| 19963350 | 2023 | STL006 | 0 | 0 | 0 | 0 | 0 | 12673.6012 | 12673.6012
| 19963350 | 2024 | STL006 | 0 | 0 | 0 | 0 | 0 | 12673.6012 | 12673.6012
| 19963350 | 2025 | STL006 | 115.2694 | 2.7121 | 0 | 0 | 115.2694 | 12673.6012 | 12676.3133
| 19963350 | 2026 | STL006 | 530.8206 | 7.5931 | 0 | 0 | 530.8206 | 12673.6012 | 12681.1943
| 19963350 | 2027 | STL006 | 530.8206 | 7.5931 | 0 | 0 | 530.8206 | 12673.6012 | 12681.1943
| 19963350 | 2028 | STL006 | 530.8206 | 7.5931 | 0 | 0 | 530.8206 | 12673.6012 | 12681.1943
| 19963350 | 2029 | STL006 | 530.8206 | 7.5931 | 0 | 0 | 530.8206 | 12673.6012 | 12681.1943
| 19963350 | 2030 | STL006 | 530.8206 | 7.5931 | 0 | 0 | 530.8206 | 12673.6012 | 12681.1943
| 19963350 | 2031 | STL006 | 530.8206 | 7.5931 | 0 | 0 | 530.8206 | 12673.6012 | 12681.1943
| 19963350 | 2032 | STL006 | 530.8206 | 7.5931 | 0 | 0 | 530.8206 | 12673.6012 | 12681.1943
| 19963350 | 2033 | STL006 | 530.8206 | 7.5931 | 0 | 0 | 530.8206 | 12673.6012 | 12681.1943
| 19963350 | 2034 | STL006 | 530.8206 | 7.5931 | 0 | 0 | 530.8206 | 12673.6012 | 12681.1943
| 19963742 | 2023 | STL006 | 0 | 0 | 0 | 0 | 0 | 5360.4344 | 5360.4344
| 19963742 | 2024 | STL006 | 0 | 0 | 0 | 0 | 0 | 5360.4344 | 5360.4344
| 19963742 | 2025 | STL006 | 5508.2143 | 218.9768 | 0 | 0 | 5508.2143 | 5360.4344 | 5579.4112
| 19963742 | 2026 | STL006 | 8447.6284 | 227.936 | 0 | 0 | 8447.6284 | 5360.4344 | 5588.3704
| 19963742 | 2027 | STL006 | 8447.6284 | 227.936 | 0 | 0 | 8447.6284 | 5360.4344 | 5588.3704
| 19963742 | 2028 | STL006 | 8447.6284 | 227.936 | 0 | 0 | 8447.6284 | 5360.4344 | 5588.3704
| 19963742 | 2029 | STL006 | 8447.6284 | 227.936 | 0 | 0 | 8447.6284 | 5360.4344 | 5588.3704
| 19963742 | 2030 | STL006 | 8447.6284 | 227.936 | 0 | 0 | 8447.6284 | 5360.4344 | 5588.3704
| 19963742 | 2031 | STL006 | 8447.6284 | 227.936 | 0 | 0 | 8447.6284 | 5360.4344 | 5588.3704
| 19963742 | 2032 | STL006 | 8447.6284 | 227.936 | 0 | 0 | 8447.6284 | 5360.4344 | 5588.3704
| 19963742 | 2033 | STL006 | 8447.6284 | 227.936 | 0 | 0 | 8447.6284 | 5360.4344 | 5588.3704
| 19963742 | 2034 | STL006 | 8447.6284 | 227.936 | 0 | 0 | 8447.6284 | 5360.4344 | 5588.3704
| 19963837 | 2023 | STL006 | 13.1946 | 0 | 0 | 0 | 13.1946 | 14349.9449 | 14349.9449
| 19963837 | 2024 | STL006 | 21.312 | 0.36737 | 0 | 0 | 21.312 | 14349.9449 | 14350.3123
| 19963837 | 2025 | STL006 | 4099.1264 | 142.4695 | 0 | 0 | 4099.1264 | 14349.9449 | 14492.4144
| 19963837 | 2026 | STL006 | 4501.1077 | 107.7247 | 0 | 0 | 4501.1077 | 14349.9449 | 14457.6696
| 19963837 | 2027 | STL006 | 4501.1077 | 107.7247 | 0 | 0 | 4501.1077 | 14349.9449 | 14457.6696
| 19963837 | 2028 | STL006 | 4501.1077 | 107.7247 | 0 | 0 | 4501.1077 | 14349.9449 | 14457.6696
| 19963837 | 2029 | STL006 | 4501.1077 | 107.7247 | 0 | 0 | 4501.1077 | 14349.9449 | 14457.6696
| 19963837 | 2030 | STL006 | 4501.1077 | 107.7247 | 0 | 0 | 4501.1077 | 14349.9449 | 14457.6696
| 19963837 | 2031 | STL006 | 4501.1077 | 107.7247 | 0 | 0 | 4501.1077 | 14349.9449 | 14457.6696
| 19963837 | 2032 | STL006 | 4501.1077 | 107.7247 | 0 | 0 | 4501.1077 | 14349.9449 | 14457.6696
| 19963837 | 2033 | STL006 | 4501.1077 | 107.7247 | 0 | 0 | 4501.1077 | 14349.9449 | 14457.6696
| 19963837 | 2034 | STL006 | 4501.1077 | 107.7247 | 0 | 0 | 4501.1077 | 14349.9449 | 14457.6696
| 20096386 | 2023 | STL006 | 0 | 0 | 7.0819 | 335.0926 | 7.0819 | 12667.9358 | 13003.0284
| 20096386 | 2024 | STL006 | 0 | 0 | 9.6849 | 458.26 | 9.6849 | 12667.9358 | 13126.1958
| 20096386 | 2025 | STL006 | 0 | 0 | 8.6164 | 407.6993 | 8.6164 | 12667.9358 | 13075.6351
| 20096386 | 2026 | STL006 | 0 | 0 | 166.3398 | 7870.6531 | 166.3398 | 12667.9358 | 20538.589
| 20096386 | 2027 | STL006 | 0 | 0 | 166.3398 | 7870.6531 | 166.3398 | 12667.9358 | 20538.589
| 20096386 | 2028 | STL006 | 0 | 0 | 166.3398 | 7870.6531 | 166.3398 | 12667.9358 | 20538.589
| 20096386 | 2029 | STL006 | 0 | 0 | 166.3398 | 7870.6531 | 166.3398 | 12667.9358 | 20538.589
| 20096386 | 2030 | STL006 | 0 | 0 | 166.3398 | 7870.6531 | 166.3398 | 12667.9358 | 20538.589
| 20096386 | 2031 | STL006 | 0 | 0 | 166.3398 | 7870.6531 | 166.3398 | 12667.9358 | 20538.589
| 20096386 | 2032 | STL006 | 0 | 0 | 166.3398 | 7870.6531 | 166.3398 | 12667.9358 | 20538.589
| 20096386 | 2033 | STL006 | 0 | 0 | 166.3398 | 7870.6531 | 166.3398 | 12667.9358 | 20538.589
| 20096386 | 2034 | STL006 | 0 | 0 | 166.3398 | 7870.6531 | 166.3398 | 12667.9358 | 20538.589
| 20496486 | 2023 | STL006 | 67.1564 | 0 | 0 | 0 | 67.1564 | 12203.8053 | 12203.8053
| 20496486 | 2024 | STL006 | 854.8644 | 11.9971 | 0 | 0 | 854.8644 | 12203.8053 | 12215.8025
| 20496486 | 2025 | STL006 | 742.2792 | 15.2378 | 0 | 0 | 742.2792 | 12203.8053 | 12219.0431
| 20496486 | 2026 | STL006 | 963.1332 | 10.8373 | 0 | 0 | 963.1332 | 12203.8053 | 12214.6426
| 20496486 | 2027 | STL006 | 963.1332 | 10.8373 | 0 | 0 | 963.1332 | 12203.8053 | 12214.6426
| 20496486 | 2028 | STL006 | 963.1332 | 10.8373 | 0 | 0 | 963.1332 | 12203.8053 | 12214.6426
| 20496486 | 2029 | STL006 | 963.1332 | 10.8373 | 0 | 0 | 963.1332 | 12203.8053 | 12214.6426
| 20496486 | 2030 | STL006 | 963.1332 | 10.8373 | 0 | 0 | 963.1332 | 12203.8053 | 12214.6426
| 20496486 | 2031 | STL006 | 963.1332 | 10.8373 | 0 | 0 | 963.1332 | 12203.8053 | 12214.6426
| 20496486 | 2032 | STL006 | 963.1332 | 10.8373 | 0 | 0 | 963.1332 | 12203.8053 | 12214.6426
| 20496486 | 2033 | STL006 | 963.1332 | 10.8373 | 0 | 0 | 963.1332 | 12203.8053 | 12214.6426
| 20496486 | 2034 | STL006 | 963.1332 | 10.8373 | 0 | 0 | 963.1332 | 12203.8053 | 12214.6426
| 20497594 | 2023 | STL006 | 0 | 0 | 0 | 0 | 0 | 10488.5675 | 10488.5675
| 20497594 | 2024 | STL006 | 0 | 0 | 0 | 0 | 0 | 10488.5675 | 10488.5675
| 20497594 | 2025 | STL006 | 0 | 0 | 0 | 0 | 0 | 10488.5675 | 10488.5675
| 20497594 | 2026 | STL006 | 0 | 0 | 0 | 0 | 0 | 10488.5675 | 10488.5675
| 20497594 | 2027 | STL006 | 0 | 0 | 0 | 0 | 0 | 10488.5675 | 10488.5675
| 20497594 | 2028 | STL006 | 0 | 0 | 0 | 0 | 0 | 10488.5675 | 10488.5675
| 20497594 | 2029 | STL006 | 0 | 0 | 0 | 0 | 0 | 10488.5675 | 10488.5675
| 20497594 | 2030 | STL006 | 0 | 0 | 0 | 0 | 0 | 10488.5675 | 10488.5675
| 20497594 | 2031 | STL006 | 0 | 0 | 0 | 0 | 0 | 10488.5675 | 10488.5675
| 20497594 | 2032 | STL006 | 0 | 0 | 0 | 0 | 0 | 10488.5675 | 10488.5675
| 20497594 | 2033 | STL006 | 0 | 0 | 0 | 0 | 0 | 10488.5675 | 10488.5675
| 20497594 | 2034 | STL006 | 0 | 0 | 0 | 0 | 0 | 10488.5675 | 10488.5675
| 20560252 | 2023 | STL006 | 0 | 0 | 0 | 0 | 0 | 2883.9504 | 2883.9504
| 20560252 | 2024 | STL006 | 0 | 0 | 0 | 0 | 0 | 2883.9504 | 2883.9504
| 20560252 | 2025 | STL006 | 321.405 | 8.2685 | 0 | 0 | 321.405 | 2883.9504 | 2892.2189
| 20560252 | 2026 | STL006 | 249.4981 | 4.0769 | 0 | 0 | 249.4981 | 2883.9504 | 2888.0273
| 20560252 | 2027 | STL006 | 249.4981 | 4.0769 | 0 | 0 | 249.4981 | 2883.9504 | 2888.0273
| 20560252 | 2028 | STL006 | 249.4981 | 4.0769 | 0 | 0 | 249.4981 | 2883.9504 | 2888.0273
| 20560252 | 2029 | STL006 | 249.4981 | 4.0769 | 0 | 0 | 249.4981 | 2883.9504 | 2888.0273
| 20560252 | 2030 | STL006 | 249.4981 | 4.0769 | 0 | 0 | 249.4981 | 2883.9504 | 2888.0273
| 20560252 | 2031 | STL006 | 249.4981 | 4.0769 | 0 | 0 | 249.4981 | 2883.9504 | 2888.0273
| 20560252 | 2032 | STL006 | 249.4981 | 4.0769 | 0 | 0 | 249.4981 | 2883.9504 | 2888.0273
| 20560252 | 2033 | STL006 | 249.4981 | 4.0769 | 0 | 0 | 249.4981 | 2883.9504 | 2888.0273
| 20560252 | 2034 | STL006 | 249.4981 | 4.0769 | 0 | 0 | 249.4981 | 2883.9504 | 2888.0273
| 82629098 | 2023 | STL006 | 0 | 0 | 0 | 0 | 0 | 1331.2319 | 1331.2319
| 82629098 | 2024 | STL006 | 0 | 0 | 0 | 0 | 0 | 1331.2319 | 1331.2319
| 82629098 | 2025 | STL006 | 0 | 0 | 0 | 0 | 0 | 1331.2319 | 1331.2319
| 82629098 | 2026 | STL006 | 0 | 0 | 0 | 0 | 0 | 1331.2319 | 1331.2319
| 82629098 | 2027 | STL006 | 0 | 0 | 0 | 0 | 0 | 1331.2319 | 1331.2319
| 82629098 | 2028 | STL006 | 0 | 0 | 0 | 0 | 0 | 1331.2319 | 1331.2319
| 82629098 | 2029 | STL006 | 0 | 0 | 0 | 0 | 0 | 1331.2319 | 1331.2319
| 82629098 | 2030 | STL006 | 0 | 0 | 0 | 0 | 0 | 1331.2319 | 1331.2319
| 82629098 | 2031 | STL006 | 0 | 0 | 0 | 0 | 0 | 1331.2319 | 1331.2319
| 82629098 | 2032 | STL006 | 0 | 0 | 0 | 0 | 0 | 1331.2319 | 1331.2319
| 82629098 | 2033 | STL006 | 0 | 0 | 0 | 0 | 0 | 1331.2319 | 1331.2319
| 82629098 | 2034 | STL006 | 0 | 0 | 0 | 0 | 0 | 1331.2319 | 1331.2319
| 83364686 | 2023 | STL006 | 0 | 0 | 0 | 0 | 0 | 8104.2938 | 8104.2938
| 83364686 | 2024 | STL006 | 0 | 0 | 0 | 0 | 0 | 8104.2938 | 8104.2938
| 83364686 | 2025 | STL006 | 0 | 0 | 0 | 0 | 0 | 8104.2938 | 8104.2938
| 83364686 | 2026 | STL006 | 0 | 0 | 0 | 0 | 0 | 8104.2938 | 8104.2938
| 83364686 | 2027 | STL006 | 0 | 0 | 0 | 0 | 0 | 8104.2938 | 8104.2938
| 83364686 | 2028 | STL006 | 0 | 0 | 0 | 0 | 0 | 8104.2938 | 8104.2938
| 83364686 | 2029 | STL006 | 0 | 0 | 0 | 0 | 0 | 8104.2938 | 8104.2938
| 83364686 | 2030 | STL006 | 0 | 0 | 0 | 0 | 0 | 8104.2938 | 8104.2938
| 83364686 | 2031 | STL006 | 0 | 0 | 0 | 0 | 0 | 8104.2938 | 8104.2938
| 83364686 | 2032 | STL006 | 0 | 0 | 0 | 0 | 0 | 8104.2938 | 8104.2938
| 83364686 | 2033 | STL006 | 0 | 0 | 0 | 0 | 0 | 8104.2938 | 8104.2938
| 83364686 | 2034 | STL006 | 0 | 0 | 0 | 0 | 0 | 8104.2938 | 8104.2938
| 128437144 | 2023 | STL006 | 0 | 0 | 5472.3996 | 258936.0446 | 5472.3996 | 8182.4039 | 267118.4486
| 128437144 | 2024 | STL006 | 0 | 0 | 5568.5282 | 263484.5362 | 5568.5282 | 8182.4039 | 271666.9402
| 128437144 | 2025 | STL006 | 0 | 0 | 5612.2125 | 265551.5359 | 5612.2125 | 8182.4039 | 273733.9399
| 128437144 | 2026 | STL006 | 0 | 0 | 5537.275 | 262005.736 | 5537.275 | 8182.4039 | 270188.14
| 128437144 | 2027 | STL006 | 0 | 0 | 5537.275 | 262005.736 | 5537.275 | 8182.4039 | 270188.14
| 128437144 | 2028 | STL006 | 0 | 0 | 5537.275 | 262005.736 | 5537.275 | 8182.4039 | 270188.14
| 128437144 | 2029 | STL006 | 0 | 0 | 5537.275 | 262005.736 | 5537.275 | 8182.4039 | 270188.14
| 128437144 | 2030 | STL006 | 0 | 0 | 5537.275 | 262005.736 | 5537.275 | 8182.4039 | 270188.14
| 128437144 | 2031 | STL006 | 0 | 0 | 5537.275 | 262005.736 | 5537.275 | 8182.4039 | 270188.14
| 128437144 | 2032 | STL006 | 0 | 0 | 5537.275 | 262005.736 | 5537.275 | 8182.4039 | 270188.14
| 128437144 | 2033 | STL006 | 0 | 0 | 5537.275 | 262005.736 | 5537.275 | 8182.4039 | 270188.14
| 128437144 | 2034 | STL006 | 0 | 0 | 5537.275 | 262005.736 | 5537.275 | 8182.4039 | 270188.14
| 155132762 | 2023 | STL006 | 0 | 0 | 1869.7638 | 88471.1036 | 1869.7638 | 3934.3393 | 92405.443
| 155132762 | 2024 | STL006 | 0 | 0 | 1930.9497 | 91366.2204 | 1930.9497 | 3934.3393 | 95300.5597
| 155132762 | 2025 | STL006 | 0 | 0 | 1887.3951 | 89305.3601 | 1887.3951 | 3934.3393 | 93239.6994
| 155132762 | 2026 | STL006 | 0 | 0 | 1696.779 | 80286.0289 | 1696.779 | 3934.3393 | 84220.3682
| 155132762 | 2027 | STL006 | 0 | 0 | 1696.779 | 80286.0289 | 1696.779 | 3934.3393 | 84220.3682
| 155132762 | 2028 | STL006 | 0 | 0 | 1696.779 | 80286.0289 | 1696.779 | 3934.3393 | 84220.3682
| 155132762 | 2029 | STL006 | 0 | 0 | 1696.779 | 80286.0289 | 1696.779 | 3934.3393 | 84220.3682
| 155132762 | 2030 | STL006 | 0 | 0 | 1696.779 | 80286.0289 | 1696.779 | 3934.3393 | 84220.3682
| 155132762 | 2031 | STL006 | 0 | 0 | 1696.779 | 80286.0289 | 1696.779 | 3934.3393 | 84220.3682
| 155132762 | 2032 | STL006 | 0 | 0 | 1696.779 | 80286.0289 | 1696.779 | 3934.3393 | 84220.3682
| 155132762 | 2033 | STL006 | 0 | 0 | 1696.779 | 80286.0289 | 1696.779 | 3934.3393 | 84220.3682
| 155132762 | 2034 | STL006 | 0 | 0 | 1696.779 | 80286.0289 | 1696.779 | 3934.3393 | 84220.3682
| 155249882 | 2023 | STL006 | 0 | 0 | 0 | 0 | 0 | 4515.9278 | 4515.9278
| 155249882 | 2024 | STL006 | 0 | 0 | 0.041732 | 1.9746 | 0.041732 | 4515.9278 | 4517.9025
| 155249882 | 2025 | STL006 | 0 | 0 | 0 | 0 | 0 | 4515.9278 | 4515.9278
| 155249882 | 2026 | STL006 | 0 | 0 | 0 | 0 | 0 | 4515.9278 | 4515.9278
| 155249882 | 2027 | STL006 | 0 | 0 | 0 | 0 | 0 | 4515.9278 | 4515.9278
| 155249882 | 2028 | STL006 | 0 | 0 | 0 | 0 | 0 | 4515.9278 | 4515.9278
| 155249882 | 2029 | STL006 | 0 | 0 | 0 | 0 | 0 | 4515.9278 | 4515.9278
| 155249882 | 2030 | STL006 | 0 | 0 | 0 | 0 | 0 | 4515.9278 | 4515.9278
| 155249882 | 2031 | STL006 | 0 | 0 | 0 | 0 | 0 | 4515.9278 | 4515.9278
| 155249882 | 2032 | STL006 | 0 | 0 | 0 | 0 | 0 | 4515.9278 | 4515.9278
| 155249882 | 2033 | STL006 | 0 | 0 | 0 | 0 | 0 | 4515.9278 | 4515.9278
| 155249882 | 2034 | STL006 | 0 | 0 | 0 | 0 | 0 | 4515.9278 | 4515.9278
| 155250536 | 2023 | STL006 | 0 | 0 | 0 | 0 | 0 | 3209.7234 | 3209.7234
| 155250536 | 2024 | STL006 | 0 | 0 | 0 | 0 | 0 | 3209.7234 | 3209.7234
| 155250536 | 2025 | STL006 | 0 | 0 | 0 | 0 | 0 | 3209.7234 | 3209.7234
| 155250536 | 2026 | STL006 | 0 | 0 | 0 | 0 | 0 | 3209.7234 | 3209.7234
| 155250536 | 2027 | STL006 | 0 | 0 | 0 | 0 | 0 | 3209.7234 | 3209.7234
| 155250536 | 2028 | STL006 | 0 | 0 | 0 | 0 | 0 | 3209.7234 | 3209.7234
| 155250536 | 2029 | STL006 | 0 | 0 | 0 | 0 | 0 | 3209.7234 | 3209.7234
| 155250536 | 2030 | STL006 | 0 | 0 | 0 | 0 | 0 | 3209.7234 | 3209.7234
| 155250536 | 2031 | STL006 | 0 | 0 | 0 | 0 | 0 | 3209.7234 | 3209.7234
| 155250536 | 2032 | STL006 | 0 | 0 | 0 | 0 | 0 | 3209.7234 | 3209.7234
| 155250536 | 2033 | STL006 | 0 | 0 | 0 | 0 | 0 | 3209.7234 | 3209.7234
| 155250536 | 2034 | STL006 | 0 | 0 | 0 | 0 | 0 | 3209.7234 | 3209.7234
| 155325091 | 2023 | STL006 | 0 | 0 | 0 | 0 | 0 | 2123.2394 | 2123.2394
| 155325091 | 2024 | STL006 | 0 | 0 | 0 | 0 | 0 | 2123.2394 | 2123.2394
| 155325091 | 2025 | STL006 | 0 | 0 | 0 | 0 | 0 | 2123.2394 | 2123.2394
| 155325091 | 2026 | STL006 | 0 | 0 | 0 | 0 | 0 | 2123.2394 | 2123.2394
| 155325091 | 2027 | STL006 | 0 | 0 | 0 | 0 | 0 | 2123.2394 | 2123.2394
| 155325091 | 2028 | STL006 | 0 | 0 | 0 | 0 | 0 | 2123.2394 | 2123.2394
| 155325091 | 2029 | STL006 | 0 | 0 | 0 | 0 | 0 | 2123.2394 | 2123.2394
| 155325091 | 2030 | STL006 | 0 | 0 | 0 | 0 | 0 | 2123.2394 | 2123.2394
| 155325091 | 2031 | STL006 | 0 | 0 | 0 | 0 | 0 | 2123.2394 | 2123.2394
| 155325091 | 2032 | STL006 | 0 | 0 | 0 | 0 | 0 | 2123.2394 | 2123.2394
| 155325091 | 2033 | STL006 | 0 | 0 | 0 | 0 | 0 | 2123.2394 | 2123.2394
| 155325091 | 2034 | STL006 | 0 | 0 | 0 | 0 | 0 | 2123.2394 | 2123.2394
| 181401765 | 2023 | STL006 | 0 | 0 | 0 | 0 | 0 | 15485.4903 | 15485.4903
| 181401765 | 2024 | STL006 | 5.2699 | 0.15772 | 0 | 0 | 5.2699 | 15485.4903 | 15485.648
| 181401765 | 2025 | STL006 | 136.2317 | 2.259 | 0 | 0 | 136.2317 | 15485.4903 | 15487.7493
| 181401765 | 2026 | STL006 | 402.9927 | 2.8783 | 0 | 0 | 402.9927 | 15485.4903 | 15488.3686
| 181401765 | 2027 | STL006 | 402.9927 | 2.8783 | 0 | 0 | 402.9927 | 15485.4903 | 15488.3686
| 181401765 | 2028 | STL006 | 402.9927 | 2.8783 | 0 | 0 | 402.9927 | 15485.4903 | 15488.3686
| 181401765 | 2029 | STL006 | 402.9927 | 2.8783 | 0 | 0 | 402.9927 | 15485.4903 | 15488.3686
| 181401765 | 2030 | STL006 | 402.9927 | 2.8783 | 0 | 0 | 402.9927 | 15485.4903 | 15488.3686
| 181401765 | 2031 | STL006 | 402.9927 | 2.8783 | 0 | 0 | 402.9927 | 15485.4903 | 15488.3686
| 181401765 | 2032 | STL006 | 402.9927 | 2.8783 | 0 | 0 | 402.9927 | 15485.4903 | 15488.3686
| 181401765 | 2033 | STL006 | 402.9927 | 2.8783 | 0 | 0 | 402.9927 | 15485.4903 | 15488.3686
| 181401765 | 2034 | STL006 | 402.9927 | 2.8783 | 0 | 0 | 402.9927 | 15485.4903 | 15488.3686
| 198543687 | 2023 | STL006 | 19883.8407 | 0 | 0 | 0 | 19883.8407 | 5342.9686 | 5342.9686
| 198543687 | 2024 | STL006 | 21553.1298 | 358.7731 | 0 | 0 | 21553.1298 | 5342.9686 | 5701.7417
| 198543687 | 2025 | STL006 | 24882.2346 | 395.3185 | 0 | 0 | 24882.2346 | 5342.9686 | 5738.2871
| 198543687 | 2026 | STL006 | 27732.1229 | 202.6242 | 0 | 0 | 27732.1229 | 5342.9686 | 5545.5927
| 198543687 | 2027 | STL006 | 27732.1229 | 202.6242 | 0 | 0 | 27732.1229 | 5342.9686 | 5545.5927
| 198543687 | 2028 | STL006 | 27732.1229 | 202.6242 | 0 | 0 | 27732.1229 | 5342.9686 | 5545.5927
| 198543687 | 2029 | STL006 | 27732.1229 | 202.6242 | 0 | 0 | 27732.1229 | 5342.9686 | 5545.5927
| 198543687 | 2030 | STL006 | 27732.1229 | 202.6242 | 0 | 0 | 27732.1229 | 5342.9686 | 5545.5927
| 198543687 | 2031 | STL006 | 27732.1229 | 202.6242 | 0 | 0 | 27732.1229 | 5342.9686 | 5545.5927
| 198543687 | 2032 | STL006 | 27732.1229 | 202.6242 | 0 | 0 | 27732.1229 | 5342.9686 | 5545.5927
| 198543687 | 2033 | STL006 | 27732.1229 | 202.6242 | 0 | 0 | 27732.1229 | 5342.9686 | 5545.5927
| 198543687 | 2034 | STL006 | 27732.1229 | 202.6242 | 0 | 0 | 27732.1229 | 5342.9686 | 5545.5927
| 20088998 | 2023 | STL007 | 67.1519 | 0 | 0 | 0 | 67.1519 | 4365.9966 | 4365.9966
| 20088998 | 2024 | STL007 | 69.1502 | 1.0987 | 0 | 0 | 69.1502 | 4365.9966 | 4367.0953
| 20088998 | 2025 | STL007 | 191.9399 | 2.7857 | 0 | 0 | 191.9399 | 4365.9966 | 4368.7823
| 20088998 | 2026 | STL007 | 274.0661 | 1.376 | 0 | 0 | 274.0661 | 4365.9966 | 4367.3725
| 20088998 | 2027 | STL007 | 244.4582 | 0.85131 | 0 | 0 | 244.4582 | 4365.9966 | 4366.8479
| 20088998 | 2028 | STL007 | 148.3519 | 0.63885 | 14.2898 | 676.1483 | 162.6417 | 4365.9966 | 5042.7837
| 20088998 | 2029 | STL007 | 148.3519 | 0.63885 | 14.2898 | 676.1483 | 162.6417 | 4365.9966 | 5042.7837
| 20088998 | 2030 | STL007 | 148.3519 | 0.63885 | 14.2898 | 676.1483 | 162.6417 | 4365.9966 | 5042.7837
| 20088998 | 2031 | STL007 | 148.3519 | 0.63885 | 14.2898 | 676.1483 | 162.6417 | 4365.9966 | 5042.7837
| 20088998 | 2032 | STL007 | 148.3519 | 0.63885 | 14.2898 | 676.1483 | 162.6417 | 4365.9966 | 5042.7837
| 20088998 | 2033 | STL007 | 148.3519 | 0.63885 | 14.2898 | 676.1483 | 162.6417 | 4365.9966 | 5042.7837
| 20088998 | 2034 | STL007 | 148.3519 | 0.63885 | 14.2898 | 676.1483 | 162.6417 | 4365.9966 | 5042.7837
| 20089423 | 2023 | STL007 | 0 | 0 | 7841.1578 | 371017.9331 | 7841.1578 | 11889.1106 | 382907.0437
| 20089423 | 2024 | STL007 | 0 | 0 | 8083.0343 | 382462.7358 | 8083.0343 | 11889.1106 | 394351.8464
| 20089423 | 2025 | STL007 | 0 | 0 | 7358.7856 | 348193.657 | 7358.7856 | 11889.1106 | 360082.7676
| 20089423 | 2026 | STL007 | 0 | 0 | 6698.5527 | 316953.5974 | 6698.5527 | 11889.1106 | 328842.7079
| 20089423 | 2027 | STL007 | 0 | 0 | 6198.6465 | 293299.6723 | 6198.6465 | 11889.1106 | 305188.7829
| 20089423 | 2028 | STL007 | 0 | 0 | 5258.5209 | 248816.0042 | 5258.5209 | 11889.1106 | 260705.1148
| 20089423 | 2029 | STL007 | 0 | 0 | 5258.5209 | 248816.0042 | 5258.5209 | 11889.1106 | 260705.1148
| 20089423 | 2030 | STL007 | 0 | 0 | 5258.5209 | 248816.0042 | 5258.5209 | 11889.1106 | 260705.1148
| 20089423 | 2031 | STL007 | 0 | 0 | 5258.5209 | 248816.0042 | 5258.5209 | 11889.1106 | 260705.1148
| 20089423 | 2032 | STL007 | 0 | 0 | 5258.5209 | 248816.0042 | 5258.5209 | 11889.1106 | 260705.1148
| 20089423 | 2033 | STL007 | 0 | 0 | 5258.5209 | 248816.0042 | 5258.5209 | 11889.1106 | 260705.1148
| 20089423 | 2034 | STL007 | 0 | 0 | 5258.5209 | 248816.0042 | 5258.5209 | 11889.1106 | 260705.1148
| 20627970 | 2023 | STL007 | 0 | 0 | 64072.2426 | 3031688.8916 | 64072.2426 | 9514.454 | 3041203.3456
| 20627970 | 2024 | STL007 | 0 | 0 | 65365.5274 | 3092882.8984 | 65365.5274 | 9514.454 | 3102397.3524
| 20627970 | 2025 | STL007 | 0 | 0 | 61759.9617 | 2922279.325 | 61759.9617 | 9514.454 | 2931793.779
| 20627970 | 2026 | STL007 | 0 | 0 | 56971.1171 | 2695686.8682 | 56971.1171 | 9514.454 | 2705201.3222
| 20627970 | 2027 | STL007 | 0 | 0 | 54604.603 | 2583711.1619 | 54604.603 | 9514.454 | 2593225.6159
| 20627970 | 2028 | STL007 | 0 | 0 | 52755.7213 | 2496228.1268 | 52755.7213 | 9514.454 | 2505742.5808
| 20627970 | 2029 | STL007 | 0 | 0 | 52755.7213 | 2496228.1268 | 52755.7213 | 9514.454 | 2505742.5808
| 20627970 | 2030 | STL007 | 0 | 0 | 52755.7213 | 2496228.1268 | 52755.7213 | 9514.454 | 2505742.5808
| 20627970 | 2031 | STL007 | 0 | 0 | 52755.7213 | 2496228.1268 | 52755.7213 | 9514.454 | 2505742.5808
| 20627970 | 2032 | STL007 | 0 | 0 | 52755.7213 | 2496228.1268 | 52755.7213 | 9514.454 | 2505742.5808
| 20627970 | 2033 | STL007 | 0 | 0 | 52755.7213 | 2496228.1268 | 52755.7213 | 9514.454 | 2505742.5808
| 20627970 | 2034 | STL007 | 0 | 0 | 52755.7213 | 2496228.1268 | 52755.7213 | 9514.454 | 2505742.5808
| 42160628 | 2023 | STL007 | 2313.4488 | 0 | 7.4624 | 353.0943 | 2320.9111 | 7503.5511 | 7856.6454
| 42160628 | 2024 | STL007 | 5337.9898 | 91.404 | 9.3219 | 441.083 | 5347.3117 | 7503.5511 | 8036.0382
| 42160628 | 2025 | STL007 | 13506.768 | 226.2607 | 7.4488 | 352.4509 | 13514.2167 | 7503.5511 | 8082.2627
| 42160628 | 2026 | STL007 | 24689.9067 | 189.2219 | 5.0997 | 241.3026 | 24695.0064 | 7503.5511 | 7934.0756
| 42160628 | 2027 | STL007 | 53169.0729 | 440.8648 | 4.7397 | 224.2692 | 53173.8127 | 7503.5511 | 8168.6851
| 42160628 | 2028 | STL007 | 60533.8676 | 527.4896 | 659.4749 | 31204.1963 | 61193.3425 | 7503.5511 | 39235.2371
| 42160628 | 2029 | STL007 | 60533.8676 | 527.4896 | 659.4749 | 31204.1963 | 61193.3425 | 7503.5511 | 39235.2371
| 42160628 | 2030 | STL007 | 60533.8676 | 527.4896 | 659.4749 | 31204.1963 | 61193.3425 | 7503.5511 | 39235.2371
| 42160628 | 2031 | STL007 | 60533.8676 | 527.4896 | 659.4749 | 31204.1963 | 61193.3425 | 7503.5511 | 39235.2371
| 42160628 | 2032 | STL007 | 60533.8676 | 527.4896 | 659.4749 | 31204.1963 | 61193.3425 | 7503.5511 | 39235.2371
| 42160628 | 2033 | STL007 | 60533.8676 | 527.4896 | 659.4749 | 31204.1963 | 61193.3425 | 7503.5511 | 39235.2371
| 42160628 | 2034 | STL007 | 60533.8676 | 527.4896 | 659.4749 | 31204.1963 | 61193.3425 | 7503.5511 | 39235.2371
| 64227317 | 2023 | STL007 | 0 | 0 | 0 | 0 | 0 | 1730.7958 | 1730.7958
| 64227317 | 2024 | STL007 | 0 | 0 | 0 | 0 | 0 | 1730.7958 | 1730.7958
| 64227317 | 2025 | STL007 | 0 | 0 | 0 | 0 | 0 | 1730.7958 | 1730.7958
| 64227317 | 2026 | STL007 | 0 | 0 | 0 | 0 | 0 | 1730.7958 | 1730.7958
| 64227317 | 2027 | STL007 | 0 | 0 | 0 | 0 | 0 | 1730.7958 | 1730.7958
| 64227317 | 2028 | STL007 | 0 | 0 | 0 | 0 | 0 | 1730.7958 | 1730.7958
| 64227317 | 2029 | STL007 | 0 | 0 | 0 | 0 | 0 | 1730.7958 | 1730.7958
| 64227317 | 2030 | STL007 | 0 | 0 | 0 | 0 | 0 | 1730.7958 | 1730.7958
| 64227317 | 2031 | STL007 | 0 | 0 | 0 | 0 | 0 | 1730.7958 | 1730.7958
| 64227317 | 2032 | STL007 | 0 | 0 | 0 | 0 | 0 | 1730.7958 | 1730.7958
| 64227317 | 2033 | STL007 | 0 | 0 | 0 | 0 | 0 | 1730.7958 | 1730.7958
| 64227317 | 2034 | STL007 | 0 | 0 | 0 | 0 | 0 | 1730.7958 | 1730.7958
| 154864885 | 2023 | STL007 | 0 | 0 | 710.5054 | 33618.7894 | 710.5054 | 8383.1761 | 42001.9655
| 154864885 | 2024 | STL007 | 0 | 0 | 750.4209 | 35507.462 | 750.4209 | 8383.1761 | 43890.6381
| 154864885 | 2025 | STL007 | 0 | 0 | 703.6047 | 33292.2744 | 703.6047 | 8383.1761 | 41675.4505
| 154864885 | 2026 | STL007 | 0 | 0 | 609.067 | 28819.0586 | 609.067 | 8383.1761 | 37202.2347
| 154864885 | 2027 | STL007 | 0 | 0 | 550.7534 | 26059.8473 | 550.7534 | 8383.1761 | 34443.0234
| 154864885 | 2028 | STL007 | 0 | 0 | 476.9798 | 22569.1256 | 476.9798 | 8383.1761 | 30952.3017
| 154864885 | 2029 | STL007 | 0 | 0 | 476.9798 | 22569.1256 | 476.9798 | 8383.1761 | 30952.3017
| 154864885 | 2030 | STL007 | 0 | 0 | 476.9798 | 22569.1256 | 476.9798 | 8383.1761 | 30952.3017
| 154864885 | 2031 | STL007 | 0 | 0 | 476.9798 | 22569.1256 | 476.9798 | 8383.1761 | 30952.3017
| 154864885 | 2032 | STL007 | 0 | 0 | 476.9798 | 22569.1256 | 476.9798 | 8383.1761 | 30952.3017
| 154864885 | 2033 | STL007 | 0 | 0 | 476.9798 | 22569.1256 | 476.9798 | 8383.1761 | 30952.3017
| 154864885 | 2034 | STL007 | 0 | 0 | 476.9798 | 22569.1256 | 476.9798 | 8383.1761 | 30952.3017
| 155267201 | 2023 | STL007 | 0 | 0 | 0 | 0 | 0 | 645.1529 | 645.1529
| 155267201 | 2024 | STL007 | 0 | 0 | 0 | 0 | 0 | 645.1529 | 645.1529
| 155267201 | 2025 | STL007 | 0 | 0 | 0 | 0 | 0 | 645.1529 | 645.1529
| 155267201 | 2026 | STL007 | 0 | 0 | 0 | 0 | 0 | 645.1529 | 645.1529
| 155267201 | 2027 | STL007 | 0 | 0 | 0 | 0 | 0 | 645.1529 | 645.1529
| 155267201 | 2028 | STL007 | 0 | 0 | 0 | 0 | 0 | 645.1529 | 645.1529
| 155267201 | 2029 | STL007 | 0 | 0 | 0 | 0 | 0 | 645.1529 | 645.1529
| 155267201 | 2030 | STL007 | 0 | 0 | 0 | 0 | 0 | 645.1529 | 645.1529
| 155267201 | 2031 | STL007 | 0 | 0 | 0 | 0 | 0 | 645.1529 | 645.1529
| 155267201 | 2032 | STL007 | 0 | 0 | 0 | 0 | 0 | 645.1529 | 645.1529
| 155267201 | 2033 | STL007 | 0 | 0 | 0 | 0 | 0 | 645.1529 | 645.1529
| 155267201 | 2034 | STL007 | 0 | 0 | 0 | 0 | 0 | 645.1529 | 645.1529
| 188648707 | 2023 | STL007 | 0 | 0 | 0.089463 | 4.2331 | 0.089463 | 2162.616 | 2166.8491
| 188648707 | 2024 | STL007 | 0 | 0 | 0.1126 | 5.3279 | 0.1126 | 2162.616 | 2167.9439
| 188648707 | 2025 | STL007 | 0 | 0 | 0.094192 | 4.4569 | 0.094192 | 2162.616 | 2167.0729
| 188648707 | 2026 | STL007 | 0 | 0 | 0.044425 | 2.102 | 0.044425 | 2162.616 | 2164.7181
| 188648707 | 2027 | STL007 | 0 | 0 | 0.023741 | 1.1234 | 0.023741 | 2162.616 | 2163.7394
| 188648707 | 2028 | STL007 | 0 | 0 | 0.014869 | 0.70355 | 0.014869 | 2162.616 | 2163.3196
| 188648707 | 2029 | STL007 | 0 | 0 | 0.014869 | 0.70355 | 0.014869 | 2162.616 | 2163.3196
| 188648707 | 2030 | STL007 | 0 | 0 | 0.014869 | 0.70355 | 0.014869 | 2162.616 | 2163.3196
| 188648707 | 2031 | STL007 | 0 | 0 | 0.014869 | 0.70355 | 0.014869 | 2162.616 | 2163.3196
| 188648707 | 2032 | STL007 | 0 | 0 | 0.014869 | 0.70355 | 0.014869 | 2162.616 | 2163.3196
| 188648707 | 2033 | STL007 | 0 | 0 | 0.014869 | 0.70355 | 0.014869 | 2162.616 | 2163.3196
| 188648707 | 2034 | STL007 | 0 | 0 | 0.014869 | 0.70355 | 0.014869 | 2162.616 | 2163.3196
| 20598544 | 2023 | STN021 | 0 | 0 | 1633.8167 | 82286.8713 | 1633.8167 | 2502.5241 | 84789.3954
| 20598544 | 2024 | STN021 | 0 | 0 | 1856.6292 | 93508.7791 | 1856.6292 | 2502.5241 | 96011.3032
| 20598544 | 2025 | STN021 | 0 | 0 | 2157.6982 | 108672.0641 | 2157.6982 | 2502.5241 | 111174.5882
| 20598544 | 2026 | STN021 | 0 | 0 | 2197.3322 | 110668.2221 | 2197.3322 | 2502.5241 | 113170.7462
| 20598544 | 2027 | STN021 | 0 | 0 | 2413.4496 | 121552.9329 | 2413.4496 | 2502.5241 | 124055.457
| 20598544 | 2028 | STN021 | 0 | 0 | 2815.2546 | 141789.7668 | 2815.2546 | 2502.5241 | 144292.2909
| 20598544 | 2029 | STN021 | 0 | 0 | 3037.4577 | 152980.9844 | 3037.4577 | 2502.5241 | 155483.5085
| 20598544 | 2030 | STN021 | 0 | 0 | 3337.9872 | 168117.0944 | 3337.9872 | 2502.5241 | 170619.6185
| 20598544 | 2031 | STN021 | 0 | 0 | 3946.5585 | 198767.6742 | 3946.5585 | 2502.5241 | 201270.1983
| 20598544 | 2032 | STN021 | 0 | 0 | 4642.7629 | 233831.8786 | 4642.7629 | 2502.5241 | 236334.4027
| 20598544 | 2033 | STN021 | 0 | 0 | 6198.7596 | 312199.3579 | 6198.7596 | 2502.5241 | 314701.882
| 20598544 | 2034 | STN021 | 0 | 0 | 7083.7581 | 356772.1399 | 7083.7581 | 2502.5241 | 359274.664
| 20662060 | 2023 | STN021 | 0 | 0 | 3401.1057 | 171296.046 | 3401.1057 | 3004.6494 | 174300.6954
| 20662060 | 2024 | STN021 | 0 | 0 | 3719.9838 | 187356.2801 | 3719.9838 | 3004.6494 | 190360.9296
| 20662060 | 2025 | STN021 | 0 | 0 | 3916.0377 | 197230.4993 | 3916.0377 | 3004.6494 | 200235.1488
| 20662060 | 2026 | STN021 | 0 | 0 | 3944.9438 | 198686.3484 | 3944.9438 | 3004.6494 | 201690.9978
| 20662060 | 2027 | STN021 | 0 | 0 | 4149.8771 | 209007.7749 | 4149.8771 | 3004.6494 | 212012.4244
| 20662060 | 2028 | STN021 | 0 | 0 | 4591.6734 | 231258.7613 | 4591.6734 | 3004.6494 | 234263.4107
| 20662060 | 2029 | STN021 | 0 | 0 | 4963.6458 | 249993.0811 | 4963.6458 | 3004.6494 | 252997.7306
| 20662060 | 2030 | STN021 | 0 | 0 | 9985.6652 | 502926.1425 | 9985.6652 | 3004.6494 | 505930.7919
| 20662060 | 2031 | STN021 | 0 | 0 | 13909.2711 | 700537.8108 | 13909.2711 | 3004.6494 | 703542.4603
| 20662060 | 2032 | STN021 | 0 | 0 | 14364.2637 | 723453.4251 | 14364.2637 | 3004.6494 | 726458.0745
| 20662060 | 2033 | STN021 | 0 | 0 | 15220.6253 | 766583.9169 | 15220.6253 | 3004.6494 | 769588.5664
| 20662060 | 2034 | STN021 | 0 | 0 | 15847.9681 | 798179.917 | 15847.9681 | 3004.6494 | 801184.5665
| 20178774 | 2023 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2638.3447 | 2638.3447
| 20178774 | 2024 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2638.3447 | 2638.3447
| 20178774 | 2025 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2638.3447 | 2638.3447
| 20178774 | 2026 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2638.3447 | 2638.3447
| 20178774 | 2027 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2638.3447 | 2638.3447
| 20178774 | 2028 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2638.3447 | 2638.3447
| 20178774 | 2029 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2638.3447 | 2638.3447
| 20178774 | 2030 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2638.3447 | 2638.3447
| 20178774 | 2031 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2638.3447 | 2638.3447
| 20178774 | 2032 | TRG013 | 0 | 0 | 20.1587 | 925.509 | 20.1587 | 2638.3447 | 3563.8537
| 20178774 | 2033 | TRG013 | 0 | 0 | 20.1587 | 925.509 | 20.1587 | 2638.3447 | 3563.8537
| 20178774 | 2034 | TRG013 | 0 | 0 | 20.1587 | 925.509 | 20.1587 | 2638.3447 | 3563.8537
| 20188288 | 2023 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1345.6502 | 1345.6502
| 20188288 | 2024 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1345.6502 | 1345.6502
| 20188288 | 2025 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1345.6502 | 1345.6502
| 20188288 | 2026 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1345.6502 | 1345.6502
| 20188288 | 2027 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1345.6502 | 1345.6502
| 20188288 | 2028 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1345.6502 | 1345.6502
| 20188288 | 2029 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1345.6502 | 1345.6502
| 20188288 | 2030 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1345.6502 | 1345.6502
| 20188288 | 2031 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1345.6502 | 1345.6502
| 20188288 | 2032 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1345.6502 | 1345.6502
| 20188288 | 2033 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1345.6502 | 1345.6502
| 20188288 | 2034 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1345.6502 | 1345.6502
| 20191227 | 2023 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1127.8647 | 1127.8647
| 20191227 | 2024 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1127.8647 | 1127.8647
| 20191227 | 2025 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1127.8647 | 1127.8647
| 20191227 | 2026 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1127.8647 | 1127.8647
| 20191227 | 2027 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1127.8647 | 1127.8647
| 20191227 | 2028 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1127.8647 | 1127.8647
| 20191227 | 2029 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1127.8647 | 1127.8647
| 20191227 | 2030 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1127.8647 | 1127.8647
| 20191227 | 2031 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1127.8647 | 1127.8647
| 20191227 | 2032 | TRG013 | 0 | 0 | 10.7628 | 494.1332 | 10.7628 | 1127.8647 | 1621.9979
| 20191227 | 2033 | TRG013 | 0 | 0 | 10.7628 | 494.1332 | 10.7628 | 1127.8647 | 1621.9979
| 20191227 | 2034 | TRG013 | 0 | 0 | 10.7628 | 494.1332 | 10.7628 | 1127.8647 | 1621.9979
| 20191256 | 2023 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2208.3118 | 2208.3118
| 20191256 | 2024 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2208.3118 | 2208.3118
| 20191256 | 2025 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2208.3118 | 2208.3118
| 20191256 | 2026 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2208.3118 | 2208.3118
| 20191256 | 2027 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2208.3118 | 2208.3118
| 20191256 | 2028 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2208.3118 | 2208.3118
| 20191256 | 2029 | TRG013 | 0 | 0 | 0 | 0 | 0 | 2208.3118 | 2208.3118
| 20191256 | 2030 | TRG013 | 2.3968 | 1.9654e-12 | 0 | 0 | 2.3968 | 2208.3118 | 2208.3118
| 20191256 | 2031 | TRG013 | 6.8112 | 0.00056722 | 0 | 0 | 6.8112 | 2208.3118 | 2208.3124
| 20191256 | 2032 | TRG013 | 28.7339 | 0.059662 | 28.8744 | 1325.6536 | 57.6083 | 2208.3118 | 3534.0251
| 20191256 | 2033 | TRG013 | 28.7339 | 0.059662 | 28.8744 | 1325.6536 | 57.6083 | 2208.3118 | 3534.0251
| 20191256 | 2034 | TRG013 | 28.7339 | 0.059662 | 28.8744 | 1325.6536 | 57.6083 | 2208.3118 | 3534.0251
| 20191806 | 2023 | TRG013 | 0 | 0 | 0 | 0 | 0 | 3063.8716 | 3063.8716
| 20191806 | 2024 | TRG013 | 0 | 0 | 0 | 0 | 0 | 3063.8716 | 3063.8716
| 20191806 | 2025 | TRG013 | 0 | 0 | 0 | 0 | 0 | 3063.8716 | 3063.8716
| 20191806 | 2026 | TRG013 | 0 | 0 | 0 | 0 | 0 | 3063.8716 | 3063.8716
| 20191806 | 2027 | TRG013 | 0 | 0 | 0 | 0 | 0 | 3063.8716 | 3063.8716
| 20191806 | 2028 | TRG013 | 0 | 0 | 0 | 0 | 0 | 3063.8716 | 3063.8716
| 20191806 | 2029 | TRG013 | 0 | 0 | 0 | 0 | 0 | 3063.8716 | 3063.8716
| 20191806 | 2030 | TRG013 | 0 | 0 | 0 | 0 | 0 | 3063.8716 | 3063.8716
| 20191806 | 2031 | TRG013 | 0 | 0 | 1151.3131 | 52857.9728 | 1151.3131 | 3063.8716 | 55921.8444
| 20191806 | 2032 | TRG013 | 0 | 0 | 1729.5175 | 79403.9382 | 1729.5175 | 3063.8716 | 82467.8098
| 20191806 | 2033 | TRG013 | 0 | 0 | 1729.5175 | 79403.9382 | 1729.5175 | 3063.8716 | 82467.8098
| 20191806 | 2034 | TRG013 | 0 | 0 | 1729.5175 | 79403.9382 | 1729.5175 | 3063.8716 | 82467.8098
| 20193390 | 2023 | TRG013 | 0 | 0 | 0 | 0 | 0 | 59.0808 | 59.0808
| 20193390 | 2024 | TRG013 | 0 | 0 | 0 | 0 | 0 | 59.0808 | 59.0808
| 20193390 | 2025 | TRG013 | 0 | 0 | 0 | 0 | 0 | 59.0808 | 59.0808
| 20193390 | 2026 | TRG013 | 0 | 0 | 0 | 0 | 0 | 59.0808 | 59.0808
| 20193390 | 2027 | TRG013 | 0 | 0 | 0 | 0 | 0 | 59.0808 | 59.0808
| 20193390 | 2028 | TRG013 | 0 | 0 | 0 | 0 | 0 | 59.0808 | 59.0808
| 20193390 | 2029 | TRG013 | 0 | 0 | 0 | 0 | 0 | 59.0808 | 59.0808
| 20193390 | 2030 | TRG013 | 0 | 0 | 0 | 0 | 0 | 59.0808 | 59.0808
| 20193390 | 2031 | TRG013 | 0 | 0 | 0 | 0 | 0 | 59.0808 | 59.0808
| 20193390 | 2032 | TRG013 | 0 | 0 | 0.10784 | 4.951 | 0.10784 | 59.0808 | 64.0318
| 20193390 | 2033 | TRG013 | 0 | 0 | 0.10784 | 4.951 | 0.10784 | 59.0808 | 64.0318
| 20193390 | 2034 | TRG013 | 0 | 0 | 0.10784 | 4.951 | 0.10784 | 59.0808 | 64.0318
| 20193552 | 2023 | TRG013 | 0 | 0 | 0 | 0 | 0 | 591.5931 | 591.5931
| 20193552 | 2024 | TRG013 | 0 | 0 | 0 | 0 | 0 | 591.5931 | 591.5931
| 20193552 | 2025 | TRG013 | 0 | 0 | 0 | 0 | 0 | 591.5931 | 591.5931
| 20193552 | 2026 | TRG013 | 0 | 0 | 0 | 0 | 0 | 591.5931 | 591.5931
| 20193552 | 2027 | TRG013 | 0 | 0 | 0 | 0 | 0 | 591.5931 | 591.5931
| 20193552 | 2028 | TRG013 | 0 | 0 | 0 | 0 | 0 | 591.5931 | 591.5931
| 20193552 | 2029 | TRG013 | 0 | 0 | 0 | 0 | 0 | 591.5931 | 591.5931
| 20193552 | 2030 | TRG013 | 0 | 0 | 0 | 0 | 0 | 591.5931 | 591.5931
| 20193552 | 2031 | TRG013 | 0 | 0 | 0 | 0 | 0 | 591.5931 | 591.5931
| 20193552 | 2032 | TRG013 | 0 | 0 | 1.1732 | 53.8646 | 1.1732 | 591.5931 | 645.4577
| 20193552 | 2033 | TRG013 | 0 | 0 | 1.1732 | 53.8646 | 1.1732 | 591.5931 | 645.4577
| 20193552 | 2034 | TRG013 | 0 | 0 | 1.1732 | 53.8646 | 1.1732 | 591.5931 | 645.4577
| 20419357 | 2023 | TRG013 | 0 | 0 | 0.0054008 | 0.24795 | 0.0054008 | 383.8389 | 384.0868
| 20419357 | 2024 | TRG013 | 0 | 0 | 0 | 0 | 0 | 383.8389 | 383.8389
| 20419357 | 2025 | TRG013 | 0 | 0 | 0.020839 | 0.95673 | 0.020839 | 383.8389 | 384.7956
| 20419357 | 2026 | TRG013 | 0 | 0 | 0.072026 | 3.3068 | 0.072026 | 383.8389 | 387.1457
| 20419357 | 2027 | TRG013 | 0 | 0 | 0.098499 | 4.5222 | 0.098499 | 383.8389 | 388.3611
| 20419357 | 2028 | TRG013 | 0 | 0 | 0.01696 | 0.77866 | 0.01696 | 383.8389 | 384.6176
| 20419357 | 2029 | TRG013 | 0 | 0 | 0 | 0 | 0 | 383.8389 | 383.8389
| 20419357 | 2030 | TRG013 | 0 | 0 | 0.024632 | 1.1309 | 0.024632 | 383.8389 | 384.9698
| 20419357 | 2031 | TRG013 | 0 | 0 | 609.9383 | 28002.8965 | 609.9383 | 383.8389 | 28386.7354
| 20419357 | 2032 | TRG013 | 0 | 0 | 821.9157 | 37734.998 | 821.9157 | 383.8389 | 38118.8369
| 20419357 | 2033 | TRG013 | 0 | 0 | 821.9157 | 37734.998 | 821.9157 | 383.8389 | 38118.8369
| 20419357 | 2034 | TRG013 | 0 | 0 | 821.9157 | 37734.998 | 821.9157 | 383.8389 | 38118.8369
| 20444130 | 2023 | TRG013 | 0 | 0 | 0 | 0 | 0 | 182.7842 | 182.7842
| 20444130 | 2024 | TRG013 | 0 | 0 | 0 | 0 | 0 | 182.7842 | 182.7842
| 20444130 | 2025 | TRG013 | 0 | 0 | 0 | 0 | 0 | 182.7842 | 182.7842
| 20444130 | 2026 | TRG013 | 0 | 0 | 0 | 0 | 0 | 182.7842 | 182.7842
| 20444130 | 2027 | TRG013 | 0 | 0 | 0 | 0 | 0 | 182.7842 | 182.7842
| 20444130 | 2028 | TRG013 | 0 | 0 | 0 | 0 | 0 | 182.7842 | 182.7842
| 20444130 | 2029 | TRG013 | 0 | 0 | 0 | 0 | 0 | 182.7842 | 182.7842
| 20444130 | 2030 | TRG013 | 0 | 0 | 0 | 0 | 0 | 182.7842 | 182.7842
| 20444130 | 2031 | TRG013 | 0 | 0 | 0 | 0 | 0 | 182.7842 | 182.7842
| 20444130 | 2032 | TRG013 | 0 | 0 | 15.828 | 726.679 | 15.828 | 182.7842 | 909.4632
| 20444130 | 2033 | TRG013 | 0 | 0 | 15.828 | 726.679 | 15.828 | 182.7842 | 909.4632
| 20444130 | 2034 | TRG013 | 0 | 0 | 15.828 | 726.679 | 15.828 | 182.7842 | 909.4632
| 20490131 | 2023 | TRG013 | 0 | 0 | 8.3708 | 384.3139 | 8.3708 | 1209.6423 | 1593.9562
| 20490131 | 2024 | TRG013 | 0 | 0 | 11.7915 | 541.3595 | 11.7915 | 1209.6423 | 1751.0017
| 20490131 | 2025 | TRG013 | 0 | 0 | 14.4731 | 664.4751 | 14.4731 | 1209.6423 | 1874.1173
| 20490131 | 2026 | TRG013 | 0 | 0 | 13.6215 | 625.3772 | 13.6215 | 1209.6423 | 1835.0195
| 20490131 | 2027 | TRG013 | 0 | 0 | 18.0829 | 830.2059 | 18.0829 | 1209.6423 | 2039.8482
| 20490131 | 2028 | TRG013 | 0 | 0 | 25.6969 | 1179.7696 | 25.6969 | 1209.6423 | 2389.4119
| 20490131 | 2029 | TRG013 | 0 | 0 | 31.0911 | 1427.423 | 31.0911 | 1209.6423 | 2637.0653
| 20490131 | 2030 | TRG013 | 0 | 0 | 30.4041 | 1395.8829 | 30.4041 | 1209.6423 | 2605.5251
| 20490131 | 2031 | TRG013 | 0 | 0 | 2358.8259 | 108296.1356 | 2358.8259 | 1209.6423 | 109505.7778
| 20490131 | 2032 | TRG013 | 0 | 0 | 2358.8259 | 108296.1356 | 2358.8259 | 1209.6423 | 109505.7778
| 20490131 | 2033 | TRG013 | 0 | 0 | 2358.8259 | 108296.1356 | 2358.8259 | 1209.6423 | 109505.7778
| 20490131 | 2034 | TRG013 | 0 | 0 | 2358.8259 | 108296.1356 | 2358.8259 | 1209.6423 | 109505.7778
| 20697075 | 2023 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1726.4942 | 1726.4942
| 20697075 | 2024 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1726.4942 | 1726.4942
| 20697075 | 2025 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1726.4942 | 1726.4942
| 20697075 | 2026 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1726.4942 | 1726.4942
| 20697075 | 2027 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1726.4942 | 1726.4942
| 20697075 | 2028 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1726.4942 | 1726.4942
| 20697075 | 2029 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1726.4942 | 1726.4942
| 20697075 | 2030 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1726.4942 | 1726.4942
| 20697075 | 2031 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1726.4942 | 1726.4942
| 20697075 | 2032 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1726.4942 | 1726.4942
| 20697075 | 2033 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1726.4942 | 1726.4942
| 20697075 | 2034 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1726.4942 | 1726.4942
| 160957458 | 2023 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1227.3886 | 1227.3886
| 160957458 | 2024 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1227.3886 | 1227.3886
| 160957458 | 2025 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1227.3886 | 1227.3886
| 160957458 | 2026 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1227.3886 | 1227.3886
| 160957458 | 2027 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1227.3886 | 1227.3886
| 160957458 | 2028 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1227.3886 | 1227.3886
| 160957458 | 2029 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1227.3886 | 1227.3886
| 160957458 | 2030 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1227.3886 | 1227.3886
| 160957458 | 2031 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1227.3886 | 1227.3886
| 160957458 | 2032 | TRG013 | 0 | 0 | 6.7011 | 307.6523 | 6.7011 | 1227.3886 | 1535.0409
| 160957458 | 2033 | TRG013 | 0 | 0 | 6.7011 | 307.6523 | 6.7011 | 1227.3886 | 1535.0409
| 160957458 | 2034 | TRG013 | 0 | 0 | 6.7011 | 307.6523 | 6.7011 | 1227.3886 | 1535.0409
| 162783566 | 2023 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1142.21 | 1142.21
| 162783566 | 2024 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1142.21 | 1142.21
| 162783566 | 2025 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1142.21 | 1142.21
| 162783566 | 2026 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1142.21 | 1142.21
| 162783566 | 2027 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1142.21 | 1142.21
| 162783566 | 2028 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1142.21 | 1142.21
| 162783566 | 2029 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1142.21 | 1142.21
| 162783566 | 2030 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1142.21 | 1142.21
| 162783566 | 2031 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1142.21 | 1142.21
| 162783566 | 2032 | TRG013 | 0 | 0 | 4.3626 | 200.2893 | 4.3626 | 1142.21 | 1342.4993
| 162783566 | 2033 | TRG013 | 0 | 0 | 4.3626 | 200.2893 | 4.3626 | 1142.21 | 1342.4993
| 162783566 | 2034 | TRG013 | 0 | 0 | 4.3626 | 200.2893 | 4.3626 | 1142.21 | 1342.4993
| 171121713 | 2023 | TRG013 | 0 | 0 | 0 | 0 | 0 | 717.2633 | 717.2633
| 171121713 | 2024 | TRG013 | 0 | 0 | 0 | 0 | 0 | 717.2633 | 717.2633
| 171121713 | 2025 | TRG013 | 0 | 0 | 0 | 0 | 0 | 717.2633 | 717.2633
| 171121713 | 2026 | TRG013 | 0 | 0 | 0 | 0 | 0 | 717.2633 | 717.2633
| 171121713 | 2027 | TRG013 | 0 | 0 | 0 | 0 | 0 | 717.2633 | 717.2633
| 171121713 | 2028 | TRG013 | 0 | 0 | 0 | 0 | 0 | 717.2633 | 717.2633
| 171121713 | 2029 | TRG013 | 0 | 0 | 0 | 0 | 0 | 717.2633 | 717.2633
| 171121713 | 2030 | TRG013 | 0 | 0 | 0 | 0 | 0 | 717.2633 | 717.2633
| 171121713 | 2031 | TRG013 | 0 | 0 | 0 | 0 | 0 | 717.2633 | 717.2633
| 171121713 | 2032 | TRG013 | 0 | 0 | 12.5259 | 575.0789 | 12.5259 | 717.2633 | 1292.3423
| 171121713 | 2033 | TRG013 | 0 | 0 | 12.5259 | 575.0789 | 12.5259 | 717.2633 | 1292.3423
| 171121713 | 2034 | TRG013 | 0 | 0 | 12.5259 | 575.0789 | 12.5259 | 717.2633 | 1292.3423
| 171744023 | 2023 | TRG013 | 375.0101 | 0 | 0 | 0 | 375.0101 | 1117.0354 | 1117.0354
| 171744023 | 2024 | TRG013 | 379.3056 | 5.1998 | 0 | 0 | 379.3056 | 1117.0354 | 1122.2352
| 171744023 | 2025 | TRG013 | 383.7906 | 6.8292 | 0 | 0 | 383.7906 | 1117.0354 | 1123.8646
| 171744023 | 2026 | TRG013 | 391.3976 | 4.1117 | 0 | 0 | 391.3976 | 1117.0354 | 1121.1471
| 171744023 | 2027 | TRG013 | 4005.1192 | 27.453 | 0 | 0 | 4005.1192 | 1117.0354 | 1144.4884
| 171744023 | 2028 | TRG013 | 4261.7226 | 37.6312 | 0 | 0 | 4261.7226 | 1117.0354 | 1154.6666
| 171744023 | 2029 | TRG013 | 4460.2285 | 30.2511 | 0 | 0 | 4460.2285 | 1117.0354 | 1147.2865
| 171744023 | 2030 | TRG013 | 4267.2288 | 31.2945 | 0 | 0 | 4267.2288 | 1117.0354 | 1148.33
| 171744023 | 2031 | TRG013 | 3112.9478 | 34.8554 | 0 | 0 | 3112.9478 | 1117.0354 | 1151.8909
| 171744023 | 2032 | TRG013 | 3155.6869 | 62.7923 | 90.4338 | 4151.9108 | 3246.1208 | 1117.0354 | 5331.7386
| 171744023 | 2033 | TRG013 | 3155.6869 | 62.7923 | 90.4338 | 4151.9108 | 3246.1208 | 1117.0354 | 5331.7386
| 171744023 | 2034 | TRG013 | 3155.6869 | 62.7923 | 90.4338 | 4151.9108 | 3246.1208 | 1117.0354 | 5331.7386
| 175478803 | 2023 | TRG013 | 0 | 0 | 0 | 0 | 0 | 548.3972 | 548.3972
| 175478803 | 2024 | TRG013 | 0 | 0 | 0 | 0 | 0 | 548.3972 | 548.3972
| 175478803 | 2025 | TRG013 | 0 | 0 | 0 | 0 | 0 | 548.3972 | 548.3972
| 175478803 | 2026 | TRG013 | 0 | 0 | 0 | 0 | 0 | 548.3972 | 548.3972
| 175478803 | 2027 | TRG013 | 0 | 0 | 0 | 0 | 0 | 548.3972 | 548.3972
| 175478803 | 2028 | TRG013 | 0 | 0 | 0 | 0 | 0 | 548.3972 | 548.3972
| 175478803 | 2029 | TRG013 | 0 | 0 | 0 | 0 | 0 | 548.3972 | 548.3972
| 175478803 | 2030 | TRG013 | 0 | 0 | 0 | 0 | 0 | 548.3972 | 548.3972
| 175478803 | 2031 | TRG013 | 0 | 0 | 0 | 0 | 0 | 548.3972 | 548.3972
| 175478803 | 2032 | TRG013 | 0 | 0 | 10.0192 | 459.9924 | 10.0192 | 548.3972 | 1008.3896
| 175478803 | 2033 | TRG013 | 0 | 0 | 10.0192 | 459.9924 | 10.0192 | 548.3972 | 1008.3896
| 175478803 | 2034 | TRG013 | 0 | 0 | 10.0192 | 459.9924 | 10.0192 | 548.3972 | 1008.3896
| 186007897 | 2023 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1162.6304 | 1162.6304
| 186007897 | 2024 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1162.6304 | 1162.6304
| 186007897 | 2025 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1162.6304 | 1162.6304
| 186007897 | 2026 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1162.6304 | 1162.6304
| 186007897 | 2027 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1162.6304 | 1162.6304
| 186007897 | 2028 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1162.6304 | 1162.6304
| 186007897 | 2029 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1162.6304 | 1162.6304
| 186007897 | 2030 | TRG013 | 0 | 0 | 0 | 0 | 0 | 1162.6304 | 1162.6304
| 186007897 | 2031 | TRG013 | 0 | 0 | 416.8989 | 19140.2592 | 416.8989 | 1162.6304 | 20302.8896
| 186007897 | 2032 | TRG013 | 0 | 0 | 416.8989 | 19140.2592 | 416.8989 | 1162.6304 | 20302.8896
| 186007897 | 2033 | TRG013 | 0 | 0 | 416.8989 | 19140.2592 | 416.8989 | 1162.6304 | 20302.8896
| 186007897 | 2034 | TRG013 | 0 | 0 | 416.8989 | 19140.2592 | 416.8989 | 1162.6304 | 20302.8896
| 19819814 | 2023 | TRG014 | 3.6697 | 0 | 0 | 0 | 3.6697 | 5730.8334 | 5730.8334
| 19819814 | 2024 | TRG014 | 16.1019 | 0.11194 | 0 | 0 | 16.1019 | 5730.8334 | 5730.9454
| 19819814 | 2025 | TRG014 | 118.043 | 1.1384 | 0 | 0 | 118.043 | 5730.8334 | 5731.9718
| 19819814 | 2026 | TRG014 | 809.4579 | 1.5906 | 0 | 0 | 809.4579 | 5730.8334 | 5732.424
| 19819814 | 2027 | TRG014 | 1505.8523 | 2.971 | 0 | 0 | 1505.8523 | 5730.8334 | 5733.8044
| 19819814 | 2028 | TRG014 | 3051.1837 | 9.919 | 0 | 0 | 3051.1837 | 5730.8334 | 5740.7524
| 19819814 | 2029 | TRG014 | 4885.9564 | 13.2824 | 0 | 0 | 4885.9564 | 5730.8334 | 5744.1158
| 19819814 | 2030 | TRG014 | 5457.68 | 15.9157 | 0 | 0 | 5457.68 | 5730.8334 | 5746.7491
| 19819814 | 2031 | TRG014 | 5457.68 | 15.9157 | 0 | 0 | 5457.68 | 5730.8334 | 5746.7491
| 19819814 | 2032 | TRG014 | 5457.68 | 15.9157 | 0 | 0 | 5457.68 | 5730.8334 | 5746.7491
| 19819814 | 2033 | TRG014 | 5457.68 | 15.9157 | 0 | 0 | 5457.68 | 5730.8334 | 5746.7491
| 19819814 | 2034 | TRG014 | 5457.68 | 15.9157 | 0 | 0 | 5457.68 | 5730.8334 | 5746.7491
| 20489497 | 2023 | TRG014 | 0 | 0 | 0 | 0 | 0 | 2633.5247 | 2633.5247
| 20489497 | 2024 | TRG014 | 0 | 0 | 0 | 0 | 0 | 2633.5247 | 2633.5247
| 20489497 | 2025 | TRG014 | 0 | 0 | 0 | 0 | 0 | 2633.5247 | 2633.5247
| 20489497 | 2026 | TRG014 | 0 | 0 | 0 | 0 | 0 | 2633.5247 | 2633.5247
| 20489497 | 2027 | TRG014 | 0 | 0 | 0 | 0 | 0 | 2633.5247 | 2633.5247
| 20489497 | 2028 | TRG014 | 0 | 0 | 0 | 0 | 0 | 2633.5247 | 2633.5247
| 20489497 | 2029 | TRG014 | 0 | 0 | 0 | 0 | 0 | 2633.5247 | 2633.5247
| 20489497 | 2030 | TRG014 | 0 | 0 | 0 | 0 | 0 | 2633.5247 | 2633.5247
| 20489497 | 2031 | TRG014 | 0 | 0 | 0 | 0 | 0 | 2633.5247 | 2633.5247
| 20489497 | 2032 | TRG014 | 0 | 0 | 0 | 0 | 0 | 2633.5247 | 2633.5247
| 20489497 | 2033 | TRG014 | 0 | 0 | 0 | 0 | 0 | 2633.5247 | 2633.5247
| 20489497 | 2034 | TRG014 | 0 | 0 | 0 | 0 | 0 | 2633.5247 | 2633.5247
| 20490150 | 2023 | TRG014 | 0 | 0 | 0 | 0 | 0 | 3499.7584 | 3499.7584
| 20490150 | 2024 | TRG014 | 0 | 0 | 0 | 0 | 0 | 3499.7584 | 3499.7584
| 20490150 | 2025 | TRG014 | 0 | 0 | 0 | 0 | 0 | 3499.7584 | 3499.7584
| 20490150 | 2026 | TRG014 | 0 | 0 | 0 | 0 | 0 | 3499.7584 | 3499.7584
| 20490150 | 2027 | TRG014 | 0 | 0 | 0 | 0 | 0 | 3499.7584 | 3499.7584
| 20490150 | 2028 | TRG014 | 0 | 0 | 0 | 0 | 0 | 3499.7584 | 3499.7584
| 20490150 | 2029 | TRG014 | 0 | 0 | 0 | 0 | 0 | 3499.7584 | 3499.7584
| 20490150 | 2030 | TRG014 | 0 | 0 | 0 | 0 | 0 | 3499.7584 | 3499.7584
| 20490150 | 2031 | TRG014 | 0 | 0 | 0 | 0 | 0 | 3499.7584 | 3499.7584
| 20490150 | 2032 | TRG014 | 0 | 0 | 0 | 0 | 0 | 3499.7584 | 3499.7584
| 20490150 | 2033 | TRG014 | 0 | 0 | 0 | 0 | 0 | 3499.7584 | 3499.7584
| 20490150 | 2034 | TRG014 | 0 | 0 | 0 | 0 | 0 | 3499.7584 | 3499.7584
| 163879163 | 2023 | TRG014 | 0 | 0 | 0 | 0 | 0 | 5989.3274 | 5989.3274
| 163879163 | 2024 | TRG014 | 0.50898 | 0.002336 | 0 | 0 | 0.50898 | 5989.3274 | 5989.3298
| 163879163 | 2025 | TRG014 | 0 | 0 | 0 | 0 | 0 | 5989.3274 | 5989.3274
| 163879163 | 2026 | TRG014 | 7.3166 | 0.01037 | 0 | 0 | 7.3166 | 5989.3274 | 5989.3378
| 163879163 | 2027 | TRG014 | 68.7099 | 0.11844 | 0 | 0 | 68.7099 | 5989.3274 | 5989.4459
| 163879163 | 2028 | TRG014 | 2707.4848 | 8.4865 | 0 | 0 | 2707.4848 | 5989.3274 | 5997.8139
| 163879163 | 2029 | TRG014 | 4121.2064 | 11.1515 | 0 | 0 | 4121.2064 | 5989.3274 | 6000.4789
| 163879163 | 2030 | TRG014 | 5748.3761 | 19.336 | 0 | 0 | 5748.3761 | 5989.3274 | 6008.6634
| 163879163 | 2031 | TRG014 | 5748.3761 | 19.336 | 0 | 0 | 5748.3761 | 5989.3274 | 6008.6634
| 163879163 | 2032 | TRG014 | 5748.3761 | 19.336 | 0 | 0 | 5748.3761 | 5989.3274 | 6008.6634
| 163879163 | 2033 | TRG014 | 5748.3761 | 19.336 | 0 | 0 | 5748.3761 | 5989.3274 | 6008.6634
| 163879163 | 2034 | TRG014 | 5748.3761 | 19.336 | 0 | 0 | 5748.3761 | 5989.3274 | 6008.6634
| 20189098 | 2023 | TRG024 | 0 | 0 | 380.2126 | 17455.9535 | 380.2126 | 3477.0831 | 20933.0366
| 20189098 | 2024 | TRG024 | 0 | 0 | 464.1271 | 21308.5572 | 464.1271 | 3477.0831 | 24785.6403
| 20189098 | 2025 | TRG024 | 0 | 0 | 534.4364 | 24536.5296 | 534.4364 | 3477.0831 | 28013.6127
| 20189098 | 2026 | TRG024 | 0 | 0 | 581.231 | 26684.9146 | 581.231 | 3477.0831 | 30161.9978
| 20189098 | 2027 | TRG024 | 0 | 0 | 699.5989 | 32119.3084 | 699.5989 | 3477.0831 | 35596.3915
| 20189098 | 2028 | TRG024 | 0 | 0 | 967.3233 | 44410.8147 | 967.3233 | 3477.0831 | 47887.8978
| 20189098 | 2029 | TRG024 | 0 | 0 | 1169.158 | 53677.2528 | 1169.158 | 3477.0831 | 57154.336
| 20189098 | 2030 | TRG024 | 0 | 0 | 1208.4466 | 55481.0343 | 1208.4466 | 3477.0831 | 58958.1175
| 20189098 | 2031 | TRG024 | 0 | 0 | 1270.1851 | 58315.5109 | 1270.1851 | 3477.0831 | 61792.594
| 20189098 | 2032 | TRG024 | 0 | 0 | 1503.9967 | 69050.0414 | 1503.9967 | 3477.0831 | 72527.1246
| 20189098 | 2033 | TRG024 | 0 | 0 | 1941.0082 | 89113.6915 | 1941.0082 | 3477.0831 | 92590.7747
| 20189098 | 2034 | TRG024 | 0 | 0 | 1976.1964 | 90729.2214 | 1976.1964 | 3477.0831 | 94206.3046
| 20191033 | 2023 | TRG024 | 1231.9501 | 0 | 0 | 0 | 1231.9501 | 1421.4878 | 1421.4878
| 20191033 | 2024 | TRG024 | 1273.2192 | 34.7478 | 0 | 0 | 1273.2192 | 1421.4878 | 1456.2357
| 20191033 | 2025 | TRG024 | 1264.631 | 41.9994 | 0 | 0 | 1264.631 | 1421.4878 | 1463.4873
| 20191033 | 2026 | TRG024 | 1246.2078 | 31.611 | 0 | 0 | 1246.2078 | 1421.4878 | 1453.0989
| 20191033 | 2027 | TRG024 | 1212.9266 | 26.2702 | 0 | 0 | 1212.9266 | 1421.4878 | 1447.758
| 20191033 | 2028 | TRG024 | 1221.3545 | 29.6571 | 0 | 0 | 1221.3545 | 1421.4878 | 1451.145
| 20191033 | 2029 | TRG024 | 1234.9679 | 24.2626 | 0 | 0 | 1234.9679 | 1421.4878 | 1445.7504
| 20191033 | 2030 | TRG024 | 2399.1757 | 47.4269 | 0 | 0 | 2399.1757 | 1421.4878 | 1468.9148
| 20191033 | 2031 | TRG024 | 2440.7049 | 54.9734 | 0 | 0 | 2440.7049 | 1421.4878 | 1476.4612
| 20191033 | 2032 | TRG024 | 2394.2675 | 76.1679 | 0 | 0 | 2394.2675 | 1421.4878 | 1497.6557
| 20191033 | 2033 | TRG024 | 3453.0333 | 144.8611 | 0 | 0 | 3453.0333 | 1421.4878 | 1566.3489
| 20191033 | 2034 | TRG024 | 3509.5496 | 182.6729 | 0 | 0 | 3509.5496 | 1421.4878 | 1604.1607
| 20193057 | 2023 | TRG024 | 0 | 0 | 0 | 0 | 0 | 733.3489 | 733.3489
| 20193057 | 2024 | TRG024 | 0 | 0 | 0 | 0 | 0 | 733.3489 | 733.3489
| 20193057 | 2025 | TRG024 | 0 | 0 | 0 | 0 | 0 | 733.3489 | 733.3489
| 20193057 | 2026 | TRG024 | 0 | 0 | 0 | 0 | 0 | 733.3489 | 733.3489
| 20193057 | 2027 | TRG024 | 0 | 0 | 0 | 0 | 0 | 733.3489 | 733.3489
| 20193057 | 2028 | TRG024 | 314.8122 | 4.8148 | 0 | 0 | 314.8122 | 733.3489 | 738.1637
| 20193057 | 2029 | TRG024 | 294.4752 | 3.8817 | 0 | 0 | 294.4752 | 733.3489 | 737.2306
| 20193057 | 2030 | TRG024 | 309.5856 | 4.5969 | 0 | 0 | 309.5856 | 733.3489 | 737.9458
| 20193057 | 2031 | TRG024 | 298.2177 | 5.816 | 0 | 0 | 298.2177 | 733.3489 | 739.1649
| 20193057 | 2032 | TRG024 | 676.7317 | 22.5208 | 0 | 0 | 676.7317 | 733.3489 | 755.8697
| 20193057 | 2033 | TRG024 | 763.0647 | 28.566 | 0 | 0 | 763.0647 | 733.3489 | 761.9149
| 20193057 | 2034 | TRG024 | 763.6176 | 36.9464 | 0 | 0 | 763.6176 | 733.3489 | 770.2952
| 20196676 | 2023 | TRG024 | 197.8001 | 0 | 0 | 0 | 197.8001 | 1060.6377 | 1060.6377
| 20196676 | 2024 | TRG024 | 195.7335 | 3.7809 | 0 | 0 | 195.7335 | 1060.6377 | 1064.4186
| 20196676 | 2025 | TRG024 | 186.7921 | 4.0455 | 0 | 0 | 186.7921 | 1060.6377 | 1064.6832
| 20196676 | 2026 | TRG024 | 183.157 | 2.6221 | 0 | 0 | 183.157 | 1060.6377 | 1063.2598
| 20196676 | 2027 | TRG024 | 185.7163 | 1.9927 | 0 | 0 | 185.7163 | 1060.6377 | 1062.6304
| 20196676 | 2028 | TRG024 | 173.5854 | 1.8625 | 0 | 0 | 173.5854 | 1060.6377 | 1062.5002
| 20196676 | 2029 | TRG024 | 181.8736 | 1.7428 | 0 | 0 | 181.8736 | 1060.6377 | 1062.3805
| 20196676 | 2030 | TRG024 | 2303.7986 | 43.926 | 0 | 0 | 2303.7986 | 1060.6377 | 1104.5637
| 20196676 | 2031 | TRG024 | 2306.062 | 49.1556 | 0 | 0 | 2306.062 | 1060.6377 | 1109.7933
| 20196676 | 2032 | TRG024 | 2256.6768 | 68.5279 | 0 | 0 | 2256.6768 | 1060.6377 | 1129.1656
| 20196676 | 2033 | TRG024 | 2195.3864 | 86.8374 | 0 | 0 | 2195.3864 | 1060.6377 | 1147.4751
| 20196676 | 2034 | TRG024 | 2178.3849 | 108.9661 | 0 | 0 | 2178.3849 | 1060.6377 | 1169.6038
| 20526773 | 2023 | TRG024 | 0 | 0 | 0 | 0 | 0 | 173.2127 | 173.2127
| 20526773 | 2024 | TRG024 | 0 | 0 | 0 | 0 | 0 | 173.2127 | 173.2127
| 20526773 | 2025 | TRG024 | 0 | 0 | 0 | 0 | 0 | 173.2127 | 173.2127
| 20526773 | 2026 | TRG024 | 0 | 0 | 0 | 0 | 0 | 173.2127 | 173.2127
| 20526773 | 2027 | TRG024 | 0 | 0 | 0 | 0 | 0 | 173.2127 | 173.2127
| 20526773 | 2028 | TRG024 | 0 | 0 | 0 | 0 | 0 | 173.2127 | 173.2127
| 20526773 | 2029 | TRG024 | 0 | 0 | 0 | 0 | 0 | 173.2127 | 173.2127
| 20526773 | 2030 | TRG024 | 0 | 0 | 0 | 0 | 0 | 173.2127 | 173.2127
| 20526773 | 2031 | TRG024 | 0 | 0 | 0 | 0 | 0 | 173.2127 | 173.2127
| 20526773 | 2032 | TRG024 | 336.7637 | 10.6028 | 0 | 0 | 336.7637 | 173.2127 | 183.8154
| 20526773 | 2033 | TRG024 | 401.8469 | 14.5858 | 0 | 0 | 401.8469 | 173.2127 | 187.7985
| 20526773 | 2034 | TRG024 | 398.9894 | 18.6294 | 0 | 0 | 398.9894 | 173.2127 | 191.8421
| 52804885 | 2023 | TRG024 | 212.4304 | 0 | 0 | 0 | 212.4304 | 447.2052 | 447.2052
| 52804885 | 2024 | TRG024 | 228.8412 | 2.7572 | 0 | 0 | 228.8412 | 447.2052 | 449.9624
| 52804885 | 2025 | TRG024 | 222.0393 | 4.1294 | 0 | 0 | 222.0393 | 447.2052 | 451.3346
| 52804885 | 2026 | TRG024 | 220.5659 | 2.8056 | 0 | 0 | 220.5659 | 447.2052 | 450.0108
| 52804885 | 2027 | TRG024 | 219.3905 | 1.578 | 0 | 0 | 219.3905 | 447.2052 | 448.7832
| 52804885 | 2028 | TRG024 | 212.5724 | 2.4814 | 0 | 0 | 212.5724 | 447.2052 | 449.6866
| 52804885 | 2029 | TRG024 | 203.3333 | 1.5208 | 0 | 0 | 203.3333 | 447.2052 | 448.726
| 52804885 | 2030 | TRG024 | 196.2727 | 1.743 | 0 | 0 | 196.2727 | 447.2052 | 448.9482
| 52804885 | 2031 | TRG024 | 196.0372 | 2.359 | 0 | 0 | 196.0372 | 447.2052 | 449.5642
| 52804885 | 2032 | TRG024 | 194.7633 | 4.4184 | 0 | 0 | 194.7633 | 447.2052 | 451.6236
| 52804885 | 2033 | TRG024 | 192.1315 | 5.3494 | 0 | 0 | 192.1315 | 447.2052 | 452.5546
| 52804885 | 2034 | TRG024 | 188.0874 | 6.9535 | 0 | 0 | 188.0874 | 447.2052 | 454.1587
| 117365596 | 2023 | TRG024 | 0 | 0 | 1.7544 | 80.5476 | 1.7544 | 2015.4159 | 2095.9635
| 117365596 | 2024 | TRG024 | 0 | 0 | 2.3716 | 108.882 | 2.3716 | 2015.4159 | 2124.2978
| 117365596 | 2025 | TRG024 | 0 | 0 | 3.6046 | 165.4912 | 3.6046 | 2015.4159 | 2180.907
| 117365596 | 2026 | TRG024 | 0 | 0 | 4.5148 | 207.2812 | 4.5148 | 2015.4159 | 2222.697
| 117365596 | 2027 | TRG024 | 0 | 0 | 7.4631 | 342.6398 | 7.4631 | 2015.4159 | 2358.0557
| 117365596 | 2028 | TRG024 | 0 | 0 | 10.0753 | 462.5674 | 10.0753 | 2015.4159 | 2477.9833
| 117365596 | 2029 | TRG024 | 0 | 0 | 13.8296 | 634.9324 | 13.8296 | 2015.4159 | 2650.3483
| 117365596 | 2030 | TRG024 | 0 | 0 | 15.7997 | 725.3823 | 15.7997 | 2015.4159 | 2740.7982
| 117365596 | 2031 | TRG024 | 0 | 0 | 17.7926 | 816.8758 | 17.7926 | 2015.4159 | 2832.2916
| 117365596 | 2032 | TRG024 | 0 | 0 | 25.0452 | 1149.8501 | 25.0452 | 2015.4159 | 3165.266
| 117365596 | 2033 | TRG024 | 0 | 0 | 38.0484 | 1746.8423 | 38.0484 | 2015.4159 | 3762.2582
| 117365596 | 2034 | TRG024 | 0 | 0 | 38.3886 | 1762.4606 | 38.3886 | 2015.4159 | 3777.8764
| 158040795 | 2023 | TRG024 | 2596.5653 | 0 | 0 | 0 | 2596.5653 | 5605.1194 | 5605.1194
| 158040795 | 2024 | TRG024 | 4229.2082 | 97.9484 | 0 | 0 | 4229.2082 | 5605.1194 | 5703.0678
| 158040795 | 2025 | TRG024 | 4173.5723 | 89.9331 | 0 | 0 | 4173.5723 | 5605.1194 | 5695.0525
| 158040795 | 2026 | TRG024 | 4281.0374 | 49.984 | 0 | 0 | 4281.0374 | 5605.1194 | 5655.1034
| 158040795 | 2027 | TRG024 | 4494.8961 | 48.7443 | 0 | 0 | 4494.8961 | 5605.1194 | 5653.8638
| 158040795 | 2028 | TRG024 | 6025.3888 | 72.7316 | 0 | 0 | 6025.3888 | 5605.1194 | 5677.851
| 158040795 | 2029 | TRG024 | 6155.5908 | 57.6362 | 0 | 0 | 6155.5908 | 5605.1194 | 5662.7556
| 158040795 | 2030 | TRG024 | 9937.1573 | 106.9767 | 0 | 0 | 9937.1573 | 5605.1194 | 5712.0961
| 158040795 | 2031 | TRG024 | 12499.5169 | 175.9185 | 0 | 0 | 12499.5169 | 5605.1194 | 5781.0379
| 158040795 | 2032 | TRG024 | 12396.2719 | 259.8122 | 0 | 0 | 12396.2719 | 5605.1194 | 5864.9316
| 158040795 | 2033 | TRG024 | 14138.1581 | 479.1781 | 0 | 0 | 14138.1581 | 5605.1194 | 6084.2975
| 158040795 | 2034 | TRG024 | 15853.7425 | 650.3756 | 0 | 0 | 15853.7425 | 5605.1194 | 6255.495
| 162940936 | 2023 | TRG024 | 0 | 0 | 7.8536 | 360.5685 | 7.8536 | 1457.0439 | 1817.6125
| 162940936 | 2024 | TRG024 | 0 | 0 | 7.6114 | 349.4471 | 7.6114 | 1457.0439 | 1806.4911
| 162940936 | 2025 | TRG024 | 0 | 0 | 8.1745 | 375.2977 | 8.1745 | 1457.0439 | 1832.3417
| 162940936 | 2026 | TRG024 | 0 | 0 | 8.1213 | 372.8563 | 8.1213 | 1457.0439 | 1829.9002
| 162940936 | 2027 | TRG024 | 0 | 0 | 12.6257 | 579.6603 | 12.6257 | 1457.0439 | 2036.7042
| 162940936 | 2028 | TRG024 | 0 | 0 | 17.4849 | 802.7481 | 17.4849 | 1457.0439 | 2259.792
| 162940936 | 2029 | TRG024 | 0 | 0 | 28.0332 | 1287.0341 | 28.0332 | 1457.0439 | 2744.078
| 162940936 | 2030 | TRG024 | 0 | 0 | 28.8694 | 1325.4227 | 28.8694 | 1457.0439 | 2782.4666
| 162940936 | 2031 | TRG024 | 0 | 0 | 30.9514 | 1421.0126 | 30.9514 | 1457.0439 | 2878.0565
| 162940936 | 2032 | TRG024 | 0 | 0 | 56.3938 | 2589.0995 | 56.3938 | 1457.0439 | 4046.1435
| 162940936 | 2033 | TRG024 | 0 | 0 | 67.5899 | 3103.1221 | 67.5899 | 1457.0439 | 4560.1661
| 162940936 | 2034 | TRG024 | 0 | 0 | 71.074 | 3263.0811 | 71.074 | 1457.0439 | 4720.1251
| 19821046 | 2023 | WBL002 | 0 | 0 | 0 | 0 | 0 | 144.7616 | 144.7616
| 19821046 | 2024 | WBL002 | 0 | 0 | 0 | 0 | 0 | 144.7616 | 144.7616
| 19821046 | 2025 | WBL002 | 0 | 0 | 0 | 0 | 0 | 144.7616 | 144.7616
| 19821046 | 2026 | WBL002 | 0 | 0 | 0 | 0 | 0 | 144.7616 | 144.7616
| 19821046 | 2027 | WBL002 | 0 | 0 | 0 | 0 | 0 | 144.7616 | 144.7616
| 19821046 | 2028 | WBL002 | 0 | 0 | 0 | 0 | 0 | 144.7616 | 144.7616
| 19821046 | 2029 | WBL002 | 0 | 0 | 0 | 0 | 0 | 144.7616 | 144.7616
| 19821046 | 2030 | WBL002 | 0 | 0 | 0 | 0 | 0 | 144.7616 | 144.7616
| 19821046 | 2031 | WBL002 | 0 | 0 | 0 | 0 | 0 | 144.7616 | 144.7616
| 19821046 | 2032 | WBL002 | 0 | 0 | 0 | 0 | 0 | 144.7616 | 144.7616
| 19821046 | 2033 | WBL002 | 0 | 0 | 0 | 0 | 0 | 144.7616 | 144.7616
| 19821046 | 2034 | WBL002 | 0 | 0 | 0 | 0 | 0 | 144.7616 | 144.7616
| 20273841 | 2023 | WIN011 | 0 | 0 | 3497.4791 | 127256.0326 | 3497.4791 | 8897.92 | 136153.9526
| 20273841 | 2024 | WIN011 | 0 | 0 | 6503.9408 | 236646.36 | 6503.9408 | 8897.92 | 245544.28
| 20273841 | 2025 | WIN011 | 0 | 0 | 7313.0763 | 266086.8137 | 7313.0763 | 8897.92 | 274984.7337
| 20273841 | 2026 | WIN011 | 0 | 0 | 7938.2323 | 288833.1597 | 7938.2323 | 8897.92 | 297731.0797
| 20273841 | 2027 | WIN011 | 0 | 0 | 8292.7445 | 301732.111 | 8292.7445 | 8897.92 | 310630.0311
| 20273841 | 2028 | WIN011 | 93.9993 | 0.24627 | 8490.7085 | 308935.0471 | 8584.7079 | 8897.92 | 317833.2134
| 20273841 | 2029 | WIN011 | 467.1322 | 1.1929 | 10310.4566 | 375146.7131 | 10777.5888 | 8897.92 | 384045.826
| 20273841 | 2030 | WIN011 | 467.1322 | 1.1929 | 10310.4566 | 375146.7131 | 10777.5888 | 8897.92 | 384045.826
| 20273841 | 2031 | WIN011 | 467.1322 | 1.1929 | 10310.4566 | 375146.7131 | 10777.5888 | 8897.92 | 384045.826
| 20273841 | 2032 | WIN011 | 467.1322 | 1.1929 | 10310.4566 | 375146.7131 | 10777.5888 | 8897.92 | 384045.826
| 20273841 | 2033 | WIN011 | 467.1322 | 1.1929 | 10310.4566 | 375146.7131 | 10777.5888 | 8897.92 | 384045.826
| 20273841 | 2034 | WIN011 | 467.1322 | 1.1929 | 10310.4566 | 375146.7131 | 10777.5888 | 8897.92 | 384045.826
| 20365858 | 2023 | WIN011 | 0 | 0 | 0 | 0 | 0 | 6806.6658 | 6806.6658
| 20365858 | 2024 | WIN011 | 0 | 0 | 0 | 0 | 0 | 6806.6658 | 6806.6658
| 20365858 | 2025 | WIN011 | 0 | 0 | 0 | 0 | 0 | 6806.6658 | 6806.6658
| 20365858 | 2026 | WIN011 | 0 | 0 | 0 | 0 | 0 | 6806.6658 | 6806.6658
| 20365858 | 2027 | WIN011 | 0 | 0 | 0 | 0 | 0 | 6806.6658 | 6806.6658
| 20365858 | 2028 | WIN011 | 0 | 0 | 0 | 0 | 0 | 6806.6658 | 6806.6658
| 20365858 | 2029 | WIN011 | 0 | 0 | 0 | 0 | 0 | 6806.6658 | 6806.6658
| 20365858 | 2030 | WIN011 | 0 | 0 | 0 | 0 | 0 | 6806.6658 | 6806.6658
| 20365858 | 2031 | WIN011 | 0 | 0 | 0 | 0 | 0 | 6806.6658 | 6806.6658
| 20365858 | 2032 | WIN011 | 0 | 0 | 0 | 0 | 0 | 6806.6658 | 6806.6658
| 20365858 | 2033 | WIN011 | 0 | 0 | 0 | 0 | 0 | 6806.6658 | 6806.6658
| 20365858 | 2034 | WIN011 | 0 | 0 | 0 | 0 | 0 | 6806.6658 | 6806.6658
| 124930850 | 2023 | WIN011 | 0 | 0 | 0 | 0 | 0 | 9445.2195 | 9445.2195
| 124930850 | 2024 | WIN011 | 0 | 0 | 0.00079087 | 0.028776 | 0.00079087 | 9445.2195 | 9445.2483
| 124930850 | 2025 | WIN011 | 0 | 0 | 2.2427 | 81.6024 | 2.2427 | 9445.2195 | 9526.8218
| 124930850 | 2026 | WIN011 | 0 | 0 | 2.4975 | 90.8731 | 2.4975 | 9445.2195 | 9536.0926
| 124930850 | 2027 | WIN011 | 611.9805 | 2.561 | 14.5003 | 527.5947 | 626.4808 | 9445.2195 | 9975.3751
| 124930850 | 2028 | WIN011 | 1209.2581 | 6.5041 | 18.1355 | 659.8626 | 1227.3936 | 9445.2195 | 10111.5862
| 124930850 | 2029 | WIN011 | 2492.4022 | 14.9362 | 79.4833 | 2892.0053 | 2571.8855 | 9445.2195 | 12352.161
| 124930850 | 2030 | WIN011 | 2492.4022 | 14.9362 | 79.4833 | 2892.0053 | 2571.8855 | 9445.2195 | 12352.161
| 124930850 | 2031 | WIN011 | 2492.4022 | 14.9362 | 79.4833 | 2892.0053 | 2571.8855 | 9445.2195 | 12352.161
| 124930850 | 2032 | WIN011 | 2492.4022 | 14.9362 | 79.4833 | 2892.0053 | 2571.8855 | 9445.2195 | 12352.161
| 124930850 | 2033 | WIN011 | 2492.4022 | 14.9362 | 79.4833 | 2892.0053 | 2571.8855 | 9445.2195 | 12352.161
| 124930850 | 2034 | WIN011 | 2492.4022 | 14.9362 | 79.4833 | 2892.0053 | 2571.8855 | 9445.2195 | 12352.161
| 177828198 | 2023 | WIN011 | 0 | 0 | 0 | 0 | 0 | 15136.8547 | 15136.8547
| 177828198 | 2024 | WIN011 | 3.5211 | 0.025331 | 1.3067 | 47.5452 | 4.8278 | 15136.8547 | 15184.4252
| 177828198 | 2025 | WIN011 | 114.4476 | 1.5286 | 1.6628 | 60.4994 | 116.1103 | 15136.8547 | 15198.8827
| 177828198 | 2026 | WIN011 | 2179.3648 | 16.6437 | 2.0836 | 75.8108 | 2181.4483 | 15136.8547 | 15229.3091
| 177828198 | 2027 | WIN011 | 5283.5817 | 36.4246 | 2.5874 | 94.1432 | 5286.1691 | 15136.8547 | 15267.4225
| 177828198 | 2028 | WIN011 | 8966.2291 | 65.853 | 8.1832 | 297.7459 | 8974.4122 | 15136.8547 | 15500.4536
| 177828198 | 2029 | WIN011 | 12926.2866 | 81.1808 | 12.9715 | 471.9695 | 12939.2581 | 15136.8547 | 15690.005
| 177828198 | 2030 | WIN011 | 12926.2866 | 81.1808 | 12.9715 | 471.9695 | 12939.2581 | 15136.8547 | 15690.005
| 177828198 | 2031 | WIN011 | 12926.2866 | 81.1808 | 12.9715 | 471.9695 | 12939.2581 | 15136.8547 | 15690.005
| 177828198 | 2032 | WIN011 | 12926.2866 | 81.1808 | 12.9715 | 471.9695 | 12939.2581 | 15136.8547 | 15690.005
| 177828198 | 2033 | WIN011 | 12926.2866 | 81.1808 | 12.9715 | 471.9695 | 12939.2581 | 15136.8547 | 15690.005
| 177828198 | 2034 | WIN011 | 12926.2866 | 81.1808 | 12.9715 | 471.9695 | 12939.2581 | 15136.8547 | 15690.005
| 192850737 | 2023 | WIN011 | 0 | 0 | 71.709 | 2609.1366 | 71.709 | 5404.7598 | 8013.8963
| 192850737 | 2024 | WIN011 | 0 | 0 | 162.4631 | 5911.2313 | 162.4631 | 5404.7598 | 11315.9911
| 192850737 | 2025 | WIN011 | 0 | 0 | 191.4038 | 6964.2395 | 191.4038 | 5404.7598 | 12368.9993
| 192850737 | 2026 | WIN011 | 0 | 0 | 206.731 | 7521.923 | 206.731 | 5404.7598 | 12926.6828
| 192850737 | 2027 | WIN011 | 0 | 0 | 224.9856 | 8186.1165 | 224.9856 | 5404.7598 | 13590.8763
| 192850737 | 2028 | WIN011 | 0 | 0 | 261.4786 | 9513.9185 | 261.4786 | 5404.7598 | 14918.6782
| 192850737 | 2029 | WIN011 | 0 | 0 | 291.9094 | 10621.1436 | 291.9094 | 5404.7598 | 16025.9033
| 192850737 | 2030 | WIN011 | 0 | 0 | 291.9094 | 10621.1436 | 291.9094 | 5404.7598 | 16025.9033
| 192850737 | 2031 | WIN011 | 0 | 0 | 291.9094 | 10621.1436 | 291.9094 | 5404.7598 | 16025.9033
| 192850737 | 2032 | WIN011 | 0 | 0 | 291.9094 | 10621.1436 | 291.9094 | 5404.7598 | 16025.9033
| 192850737 | 2033 | WIN011 | 0 | 0 | 291.9094 | 10621.1436 | 291.9094 | 5404.7598 | 16025.9033
| 192850737 | 2034 | WIN011 | 0 | 0 | 291.9094 | 10621.1436 | 291.9094 | 5404.7598 | 16025.9033
| 199934675 | 2023 | WIN011 | 0 | 0 | 0.026816 | 0.97572 | 0.026816 | 4603.8618 | 4604.8375
| 199934675 | 2024 | WIN011 | 0 | 0 | 1.6864 | 61.3583 | 1.6864 | 4603.8618 | 4665.2201
| 199934675 | 2025 | WIN011 | 0 | 0 | 3.9715 | 144.5019 | 3.9715 | 4603.8618 | 4748.3637
| 199934675 | 2026 | WIN011 | 0 | 0 | 6.1916 | 225.2807 | 6.1916 | 4603.8618 | 4829.1425
| 199934675 | 2027 | WIN011 | 0 | 0 | 8.5668 | 311.7028 | 8.5668 | 4603.8618 | 4915.5646
| 199934675 | 2028 | WIN011 | 0 | 0 | 15.75 | 573.0637 | 15.75 | 4603.8618 | 5176.9255
| 199934675 | 2029 | WIN011 | 0 | 0 | 26.3706 | 959.4947 | 26.3706 | 4603.8618 | 5563.3566
| 199934675 | 2030 | WIN011 | 0 | 0 | 26.3706 | 959.4947 | 26.3706 | 4603.8618 | 5563.3566
| 199934675 | 2031 | WIN011 | 0 | 0 | 26.3706 | 959.4947 | 26.3706 | 4603.8618 | 5563.3566
| 199934675 | 2032 | WIN011 | 0 | 0 | 26.3706 | 959.4947 | 26.3706 | 4603.8618 | 5563.3566
| 199934675 | 2033 | WIN011 | 0 | 0 | 26.3706 | 959.4947 | 26.3706 | 4603.8618 | 5563.3566
| 199934675 | 2034 | WIN011 | 0 | 0 | 26.3706 | 959.4947 | 26.3706 | 4603.8618 | 5563.3566
| 20477004 | 2023 | WIN022 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 20477004 | 2024 | WIN022 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 20477004 | 2025 | WIN022 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 20477004 | 2026 | WIN022 | 174.7987 | 1.4022 | 0 | 0 | 174.7987 | 0 | 1.4022
| 20477004 | 2027 | WIN022 | 655.2935 | 4.2193 | 0 | 0 | 655.2935 | 0 | 4.2193
| 20477004 | 2028 | WIN022 | 779.705 | 6.0204 | 0 | 0 | 779.705 | 0 | 6.0204
| 20477004 | 2029 | WIN022 | 896.7975 | 5.6743 | 0 | 0 | 896.7975 | 0 | 5.6743
| 20477004 | 2030 | WIN022 | 1101.7486 | 7.9464 | 0 | 0 | 1101.7486 | 0 | 7.9464
| 20477004 | 2031 | WIN022 | 1207.7348 | 13.0576 | 0 | 0 | 1207.7348 | 0 | 13.0576
| 20477004 | 2032 | WIN022 | 1376.2397 | 20.0828 | 0 | 0 | 1376.2397 | 0 | 20.0828
| 20477004 | 2033 | WIN022 | 1605.5746 | 45.6714 | 0 | 0 | 1605.5746 | 0 | 45.6714
| 20477004 | 2034 | WIN022 | 1688.0291 | 59.001 | 0 | 0 | 1688.0291 | 0 | 59.001
| 122831306 | 2023 | WIN022 | 3550.0791 | 0 | 0 | 0 | 3550.0791 | 36.7345 | 36.7345
| 122831306 | 2024 | WIN022 | 4069.5903 | 75.8189 | 0 | 0 | 4069.5903 | 36.7345 | 112.5534
| 122831306 | 2025 | WIN022 | 4079.6192 | 72.2323 | 0 | 0 | 4079.6192 | 36.7345 | 108.9668
| 122831306 | 2026 | WIN022 | 4977.7526 | 48.007 | 0 | 0 | 4977.7526 | 36.7345 | 84.7415
| 122831306 | 2027 | WIN022 | 8701.6968 | 66.2261 | 0 | 0 | 8701.6968 | 36.7345 | 102.9606
| 122831306 | 2028 | WIN022 | 10090.992 | 82.7371 | 0 | 0 | 10090.992 | 36.7345 | 119.4716
| 122831306 | 2029 | WIN022 | 10828.5343 | 73.3953 | 0 | 0 | 10828.5343 | 36.7345 | 110.1298
| 122831306 | 2030 | WIN022 | 12024.6414 | 88.4224 | 0 | 0 | 12024.6414 | 36.7345 | 125.1569
| 122831306 | 2031 | WIN022 | 15321.749 | 172.0955 | 0 | 0 | 15321.749 | 36.7345 | 208.83
| 122831306 | 2032 | WIN022 | 19054.276 | 310.4524 | 0 | 0 | 19054.276 | 36.7345 | 347.1869
| 122831306 | 2033 | WIN022 | 21008.4534 | 620.9271 | 0 | 0 | 21008.4534 | 36.7345 | 657.6616
| 122831306 | 2034 | WIN022 | 21807.2259 | 777.1458 | 0 | 0 | 21807.2259 | 36.7345 | 813.8803
| 131057147 | 2023 | WIN022 | 0 | 0 | 0 | 0 | 0 | 25.2054 | 25.2054
| 131057147 | 2024 | WIN022 | 0 | 0 | 0 | 0 | 0 | 25.2054 | 25.2054
| 131057147 | 2025 | WIN022 | 0 | 0 | 0 | 0 | 0 | 25.2054 | 25.2054
| 131057147 | 2026 | WIN022 | 0 | 0 | 0 | 0 | 0 | 25.2054 | 25.2054
| 131057147 | 2027 | WIN022 | 0 | 0 | 0 | 0 | 0 | 25.2054 | 25.2054
| 131057147 | 2028 | WIN022 | 0 | 0 | 0 | 0 | 0 | 25.2054 | 25.2054
| 131057147 | 2029 | WIN022 | 0 | 0 | 0 | 0 | 0 | 25.2054 | 25.2054
| 131057147 | 2030 | WIN022 | 0 | 0 | 0 | 0 | 0 | 25.2054 | 25.2054
| 131057147 | 2031 | WIN022 | 0 | 0 | 0 | 0 | 0 | 25.2054 | 25.2054
| 131057147 | 2032 | WIN022 | 0 | 0 | 0 | 0 | 0 | 25.2054 | 25.2054
| 131057147 | 2033 | WIN022 | 0 | 0 | 0 | 0 | 0 | 25.2054 | 25.2054
| 131057147 | 2034 | WIN022 | 0 | 0 | 0 | 0 | 0 | 25.2054 | 25.2054
| 183129040 | 2023 | WIN022 | 0 | 0 | 0 | 0 | 0 | 2233.7617 | 2233.7617
| 183129040 | 2024 | WIN022 | 0 | 0 | 0 | 0 | 0 | 2233.7617 | 2233.7617
| 183129040 | 2025 | WIN022 | 0 | 0 | 0 | 0 | 0 | 2233.7617 | 2233.7617
| 183129040 | 2026 | WIN022 | 0 | 0 | 0 | 0 | 0 | 2233.7617 | 2233.7617
| 183129040 | 2027 | WIN022 | 0 | 0 | 0 | 0 | 0 | 2233.7617 | 2233.7617
| 183129040 | 2028 | WIN022 | 0 | 0 | 0 | 0 | 0 | 2233.7617 | 2233.7617
| 183129040 | 2029 | WIN022 | 0 | 0 | 0 | 0 | 0 | 2233.7617 | 2233.7617
| 183129040 | 2030 | WIN022 | 0 | 0 | 0 | 0 | 0 | 2233.7617 | 2233.7617
| 183129040 | 2031 | WIN022 | 0 | 0 | 0 | 0 | 0 | 2233.7617 | 2233.7617
| 183129040 | 2032 | WIN022 | 0 | 0 | 0 | 0 | 0 | 2233.7617 | 2233.7617
| 183129040 | 2033 | WIN022 | 0 | 0 | 0 | 0 | 0 | 2233.7617 | 2233.7617
| 183129040 | 2034 | WIN022 | 0 | 0 | 0 | 0 | 0 | 2233.7617 | 2233.7617
| 185848916 | 2023 | WIN022 | 0 | 0 | 754.5865 | 27455.6834 | 754.5865 | 2885.2995 | 30340.9829
| 185848916 | 2024 | WIN022 | 0 | 0 | 780.5507 | 28400.3932 | 780.5507 | 2885.2995 | 31285.6928
| 185848916 | 2025 | WIN022 | 0 | 0 | 862.2771 | 31374.0135 | 862.2771 | 2885.2995 | 34259.313
| 185848916 | 2026 | WIN022 | 0 | 0 | 937.8219 | 34122.7191 | 937.8219 | 2885.2995 | 37008.0187
| 185848916 | 2027 | WIN022 | 0 | 0 | 991.0673 | 36060.0557 | 991.0673 | 2885.2995 | 38945.3552
| 185848916 | 2028 | WIN022 | 0 | 0 | 1082.9746 | 39404.1113 | 1082.9746 | 2885.2995 | 42289.4108
| 185848916 | 2029 | WIN022 | 0 | 0 | 1144.9983 | 41660.8474 | 1144.9983 | 2885.2995 | 44546.1469
| 185848916 | 2030 | WIN022 | 0 | 0 | 1239.0089 | 45081.4287 | 1239.0089 | 2885.2995 | 47966.7282
| 185848916 | 2031 | WIN022 | 0 | 0 | 1315.2503 | 47855.4791 | 1315.2503 | 2885.2995 | 50740.7787
| 185848916 | 2032 | WIN022 | 0 | 0 | 1486.9612 | 54103.1903 | 1486.9612 | 2885.2995 | 56988.4898
| 185848916 | 2033 | WIN022 | 0 | 0 | 1723.6051 | 62713.4969 | 1723.6051 | 2885.2995 | 65598.7964
| 185848916 | 2034 | WIN022 | 0 | 0 | 1894.4098 | 68928.2366 | 1894.4098 | 2885.2995 | 71813.5362
| 20284653 | 2023 | WIN023 | 422.0152 | 0 | 12.2722 | 446.5235 | 434.2874 | 10177.36 | 10623.8835
| 20284653 | 2024 | WIN023 | 739.1963 | 12.1833 | 15.2934 | 556.4504 | 754.4897 | 10177.36 | 10745.9937
| 20284653 | 2025 | WIN023 | 1671.7609 | 26.2198 | 22.7778 | 828.7702 | 1694.5387 | 10177.36 | 11032.35
| 20284653 | 2026 | WIN023 | 4828.329 | 36.935 | 28.63 | 1041.7029 | 4856.959 | 10177.36 | 11255.9979
| 20284653 | 2027 | WIN023 | 9767.6745 | 70.8379 | 42.0143 | 1528.6932 | 9809.6887 | 10177.36 | 11776.8912
| 20284653 | 2028 | WIN023 | 30854.3267 | 296.0856 | 49.1581 | 1788.6209 | 30903.4848 | 10177.36 | 12262.0666
| 20284653 | 2029 | WIN023 | 33483.5345 | 247.1247 | 153.9335 | 5600.8816 | 33637.468 | 10177.36 | 16025.3663
| 20284653 | 2030 | WIN023 | 48876.617 | 427.246 | 277.8002 | 10107.7796 | 49154.4172 | 10177.36 | 20712.3855
| 20284653 | 2031 | WIN023 | 53694.0459 | 632.7114 | 396.1951 | 14415.5869 | 54090.241 | 10177.36 | 25225.6583
| 20284653 | 2032 | WIN023 | 54315.3759 | 945.5206 | 505.8105 | 18403.9514 | 54821.1864 | 10177.36 | 29526.832
| 20284653 | 2033 | WIN023 | 64923.055 | 2038.0619 | 574.8419 | 20915.6645 | 65497.8969 | 10177.36 | 33131.0863
| 20284653 | 2034 | WIN023 | 81612.983 | 3133.5318 | 649.7812 | 23642.3367 | 82262.7642 | 10177.36 | 36953.2285
| 20284737 | 2023 | WIN023 | 0 | 0 | 4.8933 | 178.044 | 4.8933 | 5882.7608 | 6060.8048
| 20284737 | 2024 | WIN023 | 0 | 0 | 9.1624 | 333.3728 | 9.1624 | 5882.7608 | 6216.1336
| 20284737 | 2025 | WIN023 | 0 | 0 | 17.7122 | 644.4601 | 17.7122 | 5882.7608 | 6527.2209
| 20284737 | 2026 | WIN023 | 0 | 0 | 25.7627 | 937.3792 | 25.7627 | 5882.7608 | 6820.14
| 20284737 | 2027 | WIN023 | 0 | 0 | 36.3129 | 1321.2465 | 36.3129 | 5882.7608 | 7204.0073
| 20284737 | 2028 | WIN023 | 0 | 0 | 58.0391 | 2111.7565 | 58.0391 | 5882.7608 | 7994.5173
| 20284737 | 2029 | WIN023 | 404.9753 | 2.3343 | 84.8139 | 3085.959 | 489.7892 | 5882.7608 | 8971.0541
| 20284737 | 2030 | WIN023 | 546.6142 | 2.7903 | 132.8703 | 4834.4963 | 679.4845 | 5882.7608 | 10720.0474
| 20284737 | 2031 | WIN023 | 1293.3207 | 10.4308 | 146.4611 | 5328.9964 | 1439.7818 | 5882.7608 | 11222.188
| 20284737 | 2032 | WIN023 | 1450.865 | 17.1257 | 282.2593 | 10270.0245 | 1733.1243 | 5882.7608 | 16169.911
| 20284737 | 2033 | WIN023 | 2638.7592 | 64.75 | 479.589 | 17449.8801 | 3118.3482 | 5882.7608 | 23397.3909
| 20284737 | 2034 | WIN023 | 3231.4843 | 103.1616 | 641.8424 | 23353.4807 | 3873.3267 | 5882.7608 | 29339.4031
| 20326226 | 2023 | WIN023 | 0 | 0 | 0 | 0 | 0 | 94.5848 | 94.5848
| 20326226 | 2024 | WIN023 | 0 | 0 | 0 | 0 | 0 | 94.5848 | 94.5848
| 20326226 | 2025 | WIN023 | 0 | 0 | 0 | 0 | 0 | 94.5848 | 94.5848
| 20326226 | 2026 | WIN023 | 0 | 0 | 0 | 0 | 0 | 94.5848 | 94.5848
| 20326226 | 2027 | WIN023 | 0 | 0 | 0 | 0 | 0 | 94.5848 | 94.5848
| 20326226 | 2028 | WIN023 | 0 | 0 | 0 | 0 | 0 | 94.5848 | 94.5848
| 20326226 | 2029 | WIN023 | 0 | 0 | 0 | 0 | 0 | 94.5848 | 94.5848
| 20326226 | 2030 | WIN023 | 0 | 0 | 0 | 0 | 0 | 94.5848 | 94.5848
| 20326226 | 2031 | WIN023 | 0 | 0 | 0 | 0 | 0 | 94.5848 | 94.5848
| 20326226 | 2032 | WIN023 | 0 | 0 | 0 | 0 | 0 | 94.5848 | 94.5848
| 20326226 | 2033 | WIN023 | 0 | 0 | 0 | 0 | 0 | 94.5848 | 94.5848
| 20326226 | 2034 | WIN023 | 23.7893 | 1.0971 | 0 | 0 | 23.7893 | 94.5848 | 95.6819
| 154876579 | 2023 | WIN023 | 0 | 0 | 4.641 | 168.8628 | 4.641 | 2454.8227 | 2623.6855
| 154876579 | 2024 | WIN023 | 0 | 0 | 7.8998 | 287.4337 | 7.8998 | 2454.8227 | 2742.2564
| 154876579 | 2025 | WIN023 | 0 | 0 | 14.1694 | 515.554 | 14.1694 | 2454.8227 | 2970.3766
| 154876579 | 2026 | WIN023 | 726.8952 | 4.8018 | 21.2442 | 772.9725 | 748.1394 | 2454.8227 | 3232.5969
| 154876579 | 2027 | WIN023 | 1045.273 | 6.8386 | 36.3898 | 1324.045 | 1081.6628 | 2454.8227 | 3785.7063
| 154876579 | 2028 | WIN023 | 2818.9076 | 20.4542 | 57.613 | 2096.2523 | 2876.5206 | 2454.8227 | 4571.5292
| 154876579 | 2029 | WIN023 | 4590.6641 | 29.2881 | 76.2051 | 2772.727 | 4666.8692 | 2454.8227 | 5256.8378
| 154876579 | 2030 | WIN023 | 3809.419 | 23.0926 | 119.2602 | 4339.2912 | 3928.6792 | 2454.8227 | 6817.2065
| 154876579 | 2031 | WIN023 | 4963.9795 | 44.1181 | 148.3404 | 5397.376 | 5112.3199 | 2454.8227 | 7896.3168
| 154876579 | 2032 | WIN023 | 8200.8678 | 109.8806 | 213.6145 | 7772.3783 | 8414.4823 | 2454.8227 | 10337.0815
| 154876579 | 2033 | WIN023 | 9934.0181 | 270.3294 | 365.7074 | 13306.2919 | 10299.7256 | 2454.8227 | 16031.444
| 154876579 | 2034 | WIN023 | 13407.3199 | 457.7039 | 431.8297 | 15712.1538 | 13839.1495 | 2454.8227 | 18624.6803
| 20692956 | 2023 | WMN014 | 0 | 0 | 0 | 0 | 0 | 453.4919 | 453.4919
| 20692956 | 2024 | WMN014 | 0 | 0 | 0 | 0 | 0 | 453.4919 | 453.4919
| 20692956 | 2025 | WMN014 | 0 | 0 | 0 | 0 | 0 | 453.4919 | 453.4919
| 20692956 | 2026 | WMN014 | 0 | 0 | 0 | 0 | 0 | 453.4919 | 453.4919
| 20692956 | 2027 | WMN014 | 0 | 0 | 0 | 0 | 0 | 453.4919 | 453.4919
| 20692956 | 2028 | WMN014 | 0 | 0 | 0 | 0 | 0 | 453.4919 | 453.4919
| 20692956 | 2029 | WMN014 | 0 | 0 | 0 | 0 | 0 | 453.4919 | 453.4919
| 20692956 | 2030 | WMN014 | 0 | 0 | 0 | 0 | 0 | 453.4919 | 453.4919
| 20692956 | 2031 | WMN014 | 0 | 0 | 0 | 0 | 0 | 453.4919 | 453.4919
| 20692956 | 2032 | WMN014 | 0 | 0 | 0 | 0 | 0 | 453.4919 | 453.4919
| 20692956 | 2033 | WMN014 | 0 | 0 | 0 | 0 | 0 | 453.4919 | 453.4919
| 20692956 | 2034 | WMN014 | 0 | 0 | 0 | 0 | 0 | 453.4919 | 453.4919
| 20451231 | 2023 | WND011 | 149.6468 | 0 | 0 | 0 | 149.6468 | 6235.3268 | 6235.3268
| 20451231 | 2024 | WND011 | 1255.8884 | 19.9556 | 0 | 0 | 1255.8884 | 6235.3268 | 6255.2824
| 20451231 | 2025 | WND011 | 3643.4788 | 50.7914 | 0 | 0 | 3643.4788 | 6235.3268 | 6286.1182
| 20451231 | 2026 | WND011 | 5386.4135 | 31.0935 | 0 | 0 | 5386.4135 | 6235.3268 | 6266.4204
| 20451231 | 2027 | WND011 | 11389.0702 | 64.7406 | 0 | 0 | 11389.0702 | 6235.3268 | 6300.0674
| 20451231 | 2028 | WND011 | 22482.0871 | 145.8488 | 0 | 0 | 22482.0871 | 6235.3268 | 6381.1757
| 20451231 | 2029 | WND011 | 28229.6672 | 153.5347 | 0 | 0 | 28229.6672 | 6235.3268 | 6388.8616
| 20451231 | 2030 | WND011 | 28903.4555 | 163.5913 | 0 | 0 | 28903.4555 | 6235.3268 | 6398.9182
| 20451231 | 2031 | WND011 | 28416.0036 | 274.0728 | 0 | 0 | 28416.0036 | 6235.3268 | 6509.3996
| 20451231 | 2032 | WND011 | 29252.9979 | 396.0959 | 0 | 0 | 29252.9979 | 6235.3268 | 6631.4227
| 20451231 | 2033 | WND011 | 27996.998 | 794.5089 | 0 | 0 | 27996.998 | 6235.3268 | 7029.8357
| 20451231 | 2034 | WND011 | 31473.7916 | 1079.2563 | 0 | 0 | 31473.7916 | 6235.3268 | 7314.5831
| 83121218 | 2023 | WND011 | 0 | 0 | 0 | 0 | 0 | 88.0204 | 88.0204
| 83121218 | 2024 | WND011 | 0 | 0 | 0 | 0 | 0 | 88.0204 | 88.0204
| 83121218 | 2025 | WND011 | 0 | 0 | 0 | 0 | 0 | 88.0204 | 88.0204
| 83121218 | 2026 | WND011 | 0 | 0 | 0 | 0 | 0 | 88.0204 | 88.0204
| 83121218 | 2027 | WND011 | 0 | 0 | 0 | 0 | 0 | 88.0204 | 88.0204
| 83121218 | 2028 | WND011 | 0 | 0 | 0 | 0 | 0 | 88.0204 | 88.0204
| 83121218 | 2029 | WND011 | 3.1832 | 0.0070252 | 0 | 0 | 3.1832 | 88.0204 | 88.0275
| 83121218 | 2030 | WND011 | 221.4589 | 0.85386 | 0 | 0 | 221.4589 | 88.0204 | 88.8743
| 83121218 | 2031 | WND011 | 536.3011 | 5.8978 | 0 | 0 | 536.3011 | 88.0204 | 93.9182
| 83121218 | 2032 | WND011 | 734.6704 | 9.7896 | 0 | 0 | 734.6704 | 88.0204 | 97.81
| 83121218 | 2033 | WND011 | 1972.7941 | 51.716 | 0 | 0 | 1972.7941 | 88.0204 | 139.7364
| 83121218 | 2034 | WND011 | 2203.8043 | 63.3082 | 0 | 0 | 2203.8043 | 88.0204 | 151.3286
| 20381097 | 2023 | WND013 | 0 | 0 | 1513.4536 | 51607.1886 | 1513.4536 | 4447.4018 | 56054.5904
| 20381097 | 2024 | WND013 | 0 | 0 | 2471.6316 | 84280.0606 | 2471.6316 | 4447.4018 | 88727.4625
| 20381097 | 2025 | WND013 | 0 | 0 | 2471.6316 | 84280.0606 | 2471.6316 | 4447.4018 | 88727.4625
| 20381097 | 2026 | WND013 | 0 | 0 | 2471.6316 | 84280.0606 | 2471.6316 | 4447.4018 | 88727.4625
| 20381097 | 2027 | WND013 | 0 | 0 | 2471.6316 | 84280.0606 | 2471.6316 | 4447.4018 | 88727.4625
| 20381097 | 2028 | WND013 | 0 | 0 | 2471.6316 | 84280.0606 | 2471.6316 | 4447.4018 | 88727.4625
| 20381097 | 2029 | WND013 | 0 | 0 | 2471.6316 | 84280.0606 | 2471.6316 | 4447.4018 | 88727.4625
| 20381097 | 2030 | WND013 | 0 | 0 | 2471.6316 | 84280.0606 | 2471.6316 | 4447.4018 | 88727.4625
| 20381097 | 2031 | WND013 | 0 | 0 | 2471.6316 | 84280.0606 | 2471.6316 | 4447.4018 | 88727.4625
| 20381097 | 2032 | WND013 | 0 | 0 | 2471.6316 | 84280.0606 | 2471.6316 | 4447.4018 | 88727.4625
| 20381097 | 2033 | WND013 | 0 | 0 | 2471.6316 | 84280.0606 | 2471.6316 | 4447.4018 | 88727.4625
| 20381097 | 2034 | WND013 | 0 | 0 | 2471.6316 | 84280.0606 | 2471.6316 | 4447.4018 | 88727.4625
| 20385551 | 2023 | WND013 | 0 | 0 | 0 | 0 | 0 | 751.5991 | 751.5991
| 20385551 | 2024 | WND013 | 0 | 0 | 0 | 0 | 0 | 751.5991 | 751.5991
| 20385551 | 2025 | WND013 | 0 | 0 | 0 | 0 | 0 | 751.5991 | 751.5991
| 20385551 | 2026 | WND013 | 0 | 0 | 0 | 0 | 0 | 751.5991 | 751.5991
| 20385551 | 2027 | WND013 | 0 | 0 | 0 | 0 | 0 | 751.5991 | 751.5991
| 20385551 | 2028 | WND013 | 0 | 0 | 0 | 0 | 0 | 751.5991 | 751.5991
| 20385551 | 2029 | WND013 | 0 | 0 | 0 | 0 | 0 | 751.5991 | 751.5991
| 20385551 | 2030 | WND013 | 0 | 0 | 0 | 0 | 0 | 751.5991 | 751.5991
| 20385551 | 2031 | WND013 | 0 | 0 | 0 | 0 | 0 | 751.5991 | 751.5991
| 20385551 | 2032 | WND013 | 0 | 0 | 0 | 0 | 0 | 751.5991 | 751.5991
| 20385551 | 2033 | WND013 | 0 | 0 | 0 | 0 | 0 | 751.5991 | 751.5991
| 20385551 | 2034 | WND013 | 0 | 0 | 0 | 0 | 0 | 751.5991 | 751.5991
| 20521531 | 2023 | WND013 | 0 | 0 | 13569.6016 | 462709.2655 | 13569.6016 | 5409.096 | 468118.3616
| 20521531 | 2024 | WND013 | 3.6555 | 0.048008 | 15866.5676 | 541033.4118 | 15870.223 | 5409.096 | 546442.5559
| 20521531 | 2025 | WND013 | 3.6555 | 0.048008 | 15866.5676 | 541033.4118 | 15870.223 | 5409.096 | 546442.5559
| 20521531 | 2026 | WND013 | 3.6555 | 0.048008 | 15866.5676 | 541033.4118 | 15870.223 | 5409.096 | 546442.5559
| 20521531 | 2027 | WND013 | 3.6555 | 0.048008 | 15866.5676 | 541033.4118 | 15870.223 | 5409.096 | 546442.5559
| 20521531 | 2028 | WND013 | 3.6555 | 0.048008 | 15866.5676 | 541033.4118 | 15870.223 | 5409.096 | 546442.5559
| 20521531 | 2029 | WND013 | 3.6555 | 0.048008 | 15866.5676 | 541033.4118 | 15870.223 | 5409.096 | 546442.5559
| 20521531 | 2030 | WND013 | 3.6555 | 0.048008 | 15866.5676 | 541033.4118 | 15870.223 | 5409.096 | 546442.5559
| 20521531 | 2031 | WND013 | 3.6555 | 0.048008 | 15866.5676 | 541033.4118 | 15870.223 | 5409.096 | 546442.5559
| 20521531 | 2032 | WND013 | 3.6555 | 0.048008 | 15866.5676 | 541033.4118 | 15870.223 | 5409.096 | 546442.5559
| 20521531 | 2033 | WND013 | 3.6555 | 0.048008 | 15866.5676 | 541033.4118 | 15870.223 | 5409.096 | 546442.5559
| 20521531 | 2034 | WND013 | 3.6555 | 0.048008 | 15866.5676 | 541033.4118 | 15870.223 | 5409.096 | 546442.5559
| 20545427 | 2023 | WND013 | 15095.9376 | 0 | 0 | 0 | 15095.9376 | 2458.5624 | 2458.5624
| 20545427 | 2024 | WND013 | 15865.4666 | 353.3023 | 0 | 0 | 15865.4666 | 2458.5624 | 2811.8647
| 20545427 | 2025 | WND013 | 15865.4666 | 353.3023 | 0 | 0 | 15865.4666 | 2458.5624 | 2811.8647
| 20545427 | 2026 | WND013 | 15865.4666 | 353.3023 | 0 | 0 | 15865.4666 | 2458.5624 | 2811.8647
| 20545427 | 2027 | WND013 | 15865.4666 | 353.3023 | 0 | 0 | 15865.4666 | 2458.5624 | 2811.8647
| 20545427 | 2028 | WND013 | 15865.4666 | 353.3023 | 0 | 0 | 15865.4666 | 2458.5624 | 2811.8647
| 20545427 | 2029 | WND013 | 15865.4666 | 353.3023 | 0 | 0 | 15865.4666 | 2458.5624 | 2811.8647
| 20545427 | 2030 | WND013 | 15865.4666 | 353.3023 | 0 | 0 | 15865.4666 | 2458.5624 | 2811.8647
| 20545427 | 2031 | WND013 | 15865.4666 | 353.3023 | 0 | 0 | 15865.4666 | 2458.5624 | 2811.8647
| 20545427 | 2032 | WND013 | 15865.4666 | 353.3023 | 0 | 0 | 15865.4666 | 2458.5624 | 2811.8647
| 20545427 | 2033 | WND013 | 15865.4666 | 353.3023 | 0 | 0 | 15865.4666 | 2458.5624 | 2811.8647
| 20545427 | 2034 | WND013 | 15865.4666 | 353.3023 | 0 | 0 | 15865.4666 | 2458.5624 | 2811.8647
| 20546543 | 2023 | WND013 | 0 | 0 | 0 | 0 | 0 | 1245.195 | 1245.195
| 20546543 | 2024 | WND013 | 929.1044 | 16.9185 | 0 | 0 | 929.1044 | 1245.195 | 1262.1136
| 20546543 | 2025 | WND013 | 929.1044 | 16.9185 | 0 | 0 | 929.1044 | 1245.195 | 1262.1136
| 20546543 | 2026 | WND013 | 929.1044 | 16.9185 | 0 | 0 | 929.1044 | 1245.195 | 1262.1136
| 20546543 | 2027 | WND013 | 929.1044 | 16.9185 | 0 | 0 | 929.1044 | 1245.195 | 1262.1136
| 20546543 | 2028 | WND013 | 929.1044 | 16.9185 | 0 | 0 | 929.1044 | 1245.195 | 1262.1136
| 20546543 | 2029 | WND013 | 929.1044 | 16.9185 | 0 | 0 | 929.1044 | 1245.195 | 1262.1136
| 20546543 | 2030 | WND013 | 929.1044 | 16.9185 | 0 | 0 | 929.1044 | 1245.195 | 1262.1136
| 20546543 | 2031 | WND013 | 929.1044 | 16.9185 | 0 | 0 | 929.1044 | 1245.195 | 1262.1136
| 20546543 | 2032 | WND013 | 929.1044 | 16.9185 | 0 | 0 | 929.1044 | 1245.195 | 1262.1136
| 20546543 | 2033 | WND013 | 929.1044 | 16.9185 | 0 | 0 | 929.1044 | 1245.195 | 1262.1136
| 20546543 | 2034 | WND013 | 929.1044 | 16.9185 | 0 | 0 | 929.1044 | 1245.195 | 1262.1136
| 20559409 | 2023 | WND013 | 0 | 0 | 0 | 0 | 0 | 4957.9177 | 4957.9177
| 20559409 | 2024 | WND013 | 0 | 0 | 0 | 0 | 0 | 4957.9177 | 4957.9177
| 20559409 | 2025 | WND013 | 0 | 0 | 0 | 0 | 0 | 4957.9177 | 4957.9177
| 20559409 | 2026 | WND013 | 0 | 0 | 0 | 0 | 0 | 4957.9177 | 4957.9177
| 20559409 | 2027 | WND013 | 0 | 0 | 0 | 0 | 0 | 4957.9177 | 4957.9177
| 20559409 | 2028 | WND013 | 0 | 0 | 0 | 0 | 0 | 4957.9177 | 4957.9177
| 20559409 | 2029 | WND013 | 0 | 0 | 0 | 0 | 0 | 4957.9177 | 4957.9177
| 20559409 | 2030 | WND013 | 0 | 0 | 0 | 0 | 0 | 4957.9177 | 4957.9177
| 20559409 | 2031 | WND013 | 0 | 0 | 0 | 0 | 0 | 4957.9177 | 4957.9177
| 20559409 | 2032 | WND013 | 0 | 0 | 0 | 0 | 0 | 4957.9177 | 4957.9177
| 20559409 | 2033 | WND013 | 0 | 0 | 0 | 0 | 0 | 4957.9177 | 4957.9177
| 20559409 | 2034 | WND013 | 0 | 0 | 0 | 0 | 0 | 4957.9177 | 4957.9177
| 20592222 | 2023 | WND013 | 0 | 0 | 4541.1601 | 154848.8242 | 4541.1601 | 4935.5131 | 159784.3374
| 20592222 | 2024 | WND013 | 0 | 0 | 5444.6375 | 185656.4619 | 5444.6375 | 4935.5131 | 190591.975
| 20592222 | 2025 | WND013 | 0 | 0 | 5444.6375 | 185656.4619 | 5444.6375 | 4935.5131 | 190591.975
| 20592222 | 2026 | WND013 | 0 | 0 | 5444.6375 | 185656.4619 | 5444.6375 | 4935.5131 | 190591.975
| 20592222 | 2027 | WND013 | 0 | 0 | 5444.6375 | 185656.4619 | 5444.6375 | 4935.5131 | 190591.975
| 20592222 | 2028 | WND013 | 0 | 0 | 5444.6375 | 185656.4619 | 5444.6375 | 4935.5131 | 190591.975
| 20592222 | 2029 | WND013 | 0 | 0 | 5444.6375 | 185656.4619 | 5444.6375 | 4935.5131 | 190591.975
| 20592222 | 2030 | WND013 | 0 | 0 | 5444.6375 | 185656.4619 | 5444.6375 | 4935.5131 | 190591.975
| 20592222 | 2031 | WND013 | 0 | 0 | 5444.6375 | 185656.4619 | 5444.6375 | 4935.5131 | 190591.975
| 20592222 | 2032 | WND013 | 0 | 0 | 5444.6375 | 185656.4619 | 5444.6375 | 4935.5131 | 190591.975
| 20592222 | 2033 | WND013 | 0 | 0 | 5444.6375 | 185656.4619 | 5444.6375 | 4935.5131 | 190591.975
| 20592222 | 2034 | WND013 | 0 | 0 | 5444.6375 | 185656.4619 | 5444.6375 | 4935.5131 | 190591.975
| 20592233 | 2023 | WND013 | 0 | 0 | 1040.8562 | 35492.1127 | 1040.8562 | 640.5219 | 36132.6346
| 20592233 | 2024 | WND013 | 0 | 0 | 1203.0243 | 41021.8729 | 1203.0243 | 640.5219 | 41662.3947
| 20592233 | 2025 | WND013 | 0 | 0 | 1203.0243 | 41021.8729 | 1203.0243 | 640.5219 | 41662.3947
| 20592233 | 2026 | WND013 | 0 | 0 | 1203.0243 | 41021.8729 | 1203.0243 | 640.5219 | 41662.3947
| 20592233 | 2027 | WND013 | 0 | 0 | 1203.0243 | 41021.8729 | 1203.0243 | 640.5219 | 41662.3947
| 20592233 | 2028 | WND013 | 0 | 0 | 1203.0243 | 41021.8729 | 1203.0243 | 640.5219 | 41662.3947
| 20592233 | 2029 | WND013 | 0 | 0 | 1203.0243 | 41021.8729 | 1203.0243 | 640.5219 | 41662.3947
| 20592233 | 2030 | WND013 | 0 | 0 | 1203.0243 | 41021.8729 | 1203.0243 | 640.5219 | 41662.3947
| 20592233 | 2031 | WND013 | 0 | 0 | 1203.0243 | 41021.8729 | 1203.0243 | 640.5219 | 41662.3947
| 20592233 | 2032 | WND013 | 0 | 0 | 1203.0243 | 41021.8729 | 1203.0243 | 640.5219 | 41662.3947
| 20592233 | 2033 | WND013 | 0 | 0 | 1203.0243 | 41021.8729 | 1203.0243 | 640.5219 | 41662.3947
| 20592233 | 2034 | WND013 | 0 | 0 | 1203.0243 | 41021.8729 | 1203.0243 | 640.5219 | 41662.3947
| 20592563 | 2023 | WND013 | 9509.2868 | 0 | 48.8491 | 1665.702 | 9558.1359 | 7115.4838 | 8781.1858
| 20592563 | 2024 | WND013 | 11646.8383 | 233.6177 | 96.825 | 3301.6315 | 11743.6633 | 7115.4838 | 10650.7331
| 20592563 | 2025 | WND013 | 11646.8383 | 233.6177 | 96.825 | 3301.6315 | 11743.6633 | 7115.4838 | 10650.7331
| 20592563 | 2026 | WND013 | 11646.8383 | 233.6177 | 96.825 | 3301.6315 | 11743.6633 | 7115.4838 | 10650.7331
| 20592563 | 2027 | WND013 | 11646.8383 | 233.6177 | 96.825 | 3301.6315 | 11743.6633 | 7115.4838 | 10650.7331
| 20592563 | 2028 | WND013 | 11646.8383 | 233.6177 | 96.825 | 3301.6315 | 11743.6633 | 7115.4838 | 10650.7331
| 20592563 | 2029 | WND013 | 11646.8383 | 233.6177 | 96.825 | 3301.6315 | 11743.6633 | 7115.4838 | 10650.7331
| 20592563 | 2030 | WND013 | 11646.8383 | 233.6177 | 96.825 | 3301.6315 | 11743.6633 | 7115.4838 | 10650.7331
| 20592563 | 2031 | WND013 | 11646.8383 | 233.6177 | 96.825 | 3301.6315 | 11743.6633 | 7115.4838 | 10650.7331
| 20592563 | 2032 | WND013 | 11646.8383 | 233.6177 | 96.825 | 3301.6315 | 11743.6633 | 7115.4838 | 10650.7331
| 20592563 | 2033 | WND013 | 11646.8383 | 233.6177 | 96.825 | 3301.6315 | 11743.6633 | 7115.4838 | 10650.7331
| 20592563 | 2034 | WND013 | 11646.8383 | 233.6177 | 96.825 | 3301.6315 | 11743.6633 | 7115.4838 | 10650.7331
| 20594990 | 2023 | WND013 | 0 | 0 | 0 | 0 | 0 | 262.0711 | 262.0711
| 20594990 | 2024 | WND013 | 0 | 0 | 0 | 0 | 0 | 262.0711 | 262.0711
| 20594990 | 2025 | WND013 | 0 | 0 | 0 | 0 | 0 | 262.0711 | 262.0711
| 20594990 | 2026 | WND013 | 0 | 0 | 0 | 0 | 0 | 262.0711 | 262.0711
| 20594990 | 2027 | WND013 | 0 | 0 | 0 | 0 | 0 | 262.0711 | 262.0711
| 20594990 | 2028 | WND013 | 0 | 0 | 0 | 0 | 0 | 262.0711 | 262.0711
| 20594990 | 2029 | WND013 | 0 | 0 | 0 | 0 | 0 | 262.0711 | 262.0711
| 20594990 | 2030 | WND013 | 0 | 0 | 0 | 0 | 0 | 262.0711 | 262.0711
| 20594990 | 2031 | WND013 | 0 | 0 | 0 | 0 | 0 | 262.0711 | 262.0711
| 20594990 | 2032 | WND013 | 0 | 0 | 0 | 0 | 0 | 262.0711 | 262.0711
| 20594990 | 2033 | WND013 | 0 | 0 | 0 | 0 | 0 | 262.0711 | 262.0711
| 20594990 | 2034 | WND013 | 0 | 0 | 0 | 0 | 0 | 262.0711 | 262.0711
| 20623140 | 2023 | WND013 | 0 | 0 | 27450.2231 | 936023.99 | 27450.2231 | 3176.1658 | 939200.1558
| 20623140 | 2024 | WND013 | 0 | 0 | 39760.9394 | 1355806.5802 | 39760.9394 | 3176.1658 | 1358982.746
| 20623140 | 2025 | WND013 | 0 | 0 | 39760.9394 | 1355806.5802 | 39760.9394 | 3176.1658 | 1358982.746
| 20623140 | 2026 | WND013 | 0 | 0 | 39760.9394 | 1355806.5802 | 39760.9394 | 3176.1658 | 1358982.746
| 20623140 | 2027 | WND013 | 0 | 0 | 39760.9394 | 1355806.5802 | 39760.9394 | 3176.1658 | 1358982.746
| 20623140 | 2028 | WND013 | 0 | 0 | 39760.9394 | 1355806.5802 | 39760.9394 | 3176.1658 | 1358982.746
| 20623140 | 2029 | WND013 | 0 | 0 | 39760.9394 | 1355806.5802 | 39760.9394 | 3176.1658 | 1358982.746
| 20623140 | 2030 | WND013 | 0 | 0 | 39760.9394 | 1355806.5802 | 39760.9394 | 3176.1658 | 1358982.746
| 20623140 | 2031 | WND013 | 0 | 0 | 39760.9394 | 1355806.5802 | 39760.9394 | 3176.1658 | 1358982.746
| 20623140 | 2032 | WND013 | 0 | 0 | 39760.9394 | 1355806.5802 | 39760.9394 | 3176.1658 | 1358982.746
| 20623140 | 2033 | WND013 | 0 | 0 | 39760.9394 | 1355806.5802 | 39760.9394 | 3176.1658 | 1358982.746
| 20623140 | 2034 | WND013 | 0 | 0 | 39760.9394 | 1355806.5802 | 39760.9394 | 3176.1658 | 1358982.746
| 20653160 | 2023 | WND013 | 418.2078 | 0 | 0 | 0 | 418.2078 | 1654.5136 | 1654.5136
| 20653160 | 2024 | WND013 | 676.428 | 11.516 | 0 | 0 | 676.428 | 1654.5136 | 1666.0296
| 20653160 | 2025 | WND013 | 676.428 | 11.516 | 0 | 0 | 676.428 | 1654.5136 | 1666.0296
| 20653160 | 2026 | WND013 | 676.428 | 11.516 | 0 | 0 | 676.428 | 1654.5136 | 1666.0296
| 20653160 | 2027 | WND013 | 676.428 | 11.516 | 0 | 0 | 676.428 | 1654.5136 | 1666.0296
| 20653160 | 2028 | WND013 | 676.428 | 11.516 | 0 | 0 | 676.428 | 1654.5136 | 1666.0296
| 20653160 | 2029 | WND013 | 676.428 | 11.516 | 0 | 0 | 676.428 | 1654.5136 | 1666.0296
| 20653160 | 2030 | WND013 | 676.428 | 11.516 | 0 | 0 | 676.428 | 1654.5136 | 1666.0296
| 20653160 | 2031 | WND013 | 676.428 | 11.516 | 0 | 0 | 676.428 | 1654.5136 | 1666.0296
| 20653160 | 2032 | WND013 | 676.428 | 11.516 | 0 | 0 | 676.428 | 1654.5136 | 1666.0296
| 20653160 | 2033 | WND013 | 676.428 | 11.516 | 0 | 0 | 676.428 | 1654.5136 | 1666.0296
| 20653160 | 2034 | WND013 | 676.428 | 11.516 | 0 | 0 | 676.428 | 1654.5136 | 1666.0296
| 55505387 | 2023 | WND013 | 4539.6544 | 0 | 0 | 0 | 4539.6544 | 5456.941 | 5456.941
| 55505387 | 2024 | WND013 | 6386.5598 | 133.1379 | 0.14176 | 4.8339 | 6386.7016 | 5456.941 | 5594.9128
| 55505387 | 2025 | WND013 | 6386.5598 | 133.1379 | 0.14176 | 4.8339 | 6386.7016 | 5456.941 | 5594.9128
| 55505387 | 2026 | WND013 | 6386.5598 | 133.1379 | 0.14176 | 4.8339 | 6386.7016 | 5456.941 | 5594.9128
| 55505387 | 2027 | WND013 | 6386.5598 | 133.1379 | 0.14176 | 4.8339 | 6386.7016 | 5456.941 | 5594.9128
| 55505387 | 2028 | WND013 | 6386.5598 | 133.1379 | 0.14176 | 4.8339 | 6386.7016 | 5456.941 | 5594.9128
| 55505387 | 2029 | WND013 | 6386.5598 | 133.1379 | 0.14176 | 4.8339 | 6386.7016 | 5456.941 | 5594.9128
| 55505387 | 2030 | WND013 | 6386.5598 | 133.1379 | 0.14176 | 4.8339 | 6386.7016 | 5456.941 | 5594.9128
| 55505387 | 2031 | WND013 | 6386.5598 | 133.1379 | 0.14176 | 4.8339 | 6386.7016 | 5456.941 | 5594.9128
| 55505387 | 2032 | WND013 | 6386.5598 | 133.1379 | 0.14176 | 4.8339 | 6386.7016 | 5456.941 | 5594.9128
| 55505387 | 2033 | WND013 | 6386.5598 | 133.1379 | 0.14176 | 4.8339 | 6386.7016 | 5456.941 | 5594.9128
| 55505387 | 2034 | WND013 | 6386.5598 | 133.1379 | 0.14176 | 4.8339 | 6386.7016 | 5456.941 | 5594.9128
| 82431532 | 2023 | WND013 | 154.6275 | 0 | 0 | 0 | 154.6275 | 3129.8216 | 3129.8216
| 82431532 | 2024 | WND013 | 316.7996 | 4.5613 | 0 | 0 | 316.7996 | 3129.8216 | 3134.3828
| 82431532 | 2025 | WND013 | 316.7996 | 4.5613 | 0 | 0 | 316.7996 | 3129.8216 | 3134.3828
| 82431532 | 2026 | WND013 | 316.7996 | 4.5613 | 0 | 0 | 316.7996 | 3129.8216 | 3134.3828
| 82431532 | 2027 | WND013 | 316.7996 | 4.5613 | 0 | 0 | 316.7996 | 3129.8216 | 3134.3828
| 82431532 | 2028 | WND013 | 316.7996 | 4.5613 | 0 | 0 | 316.7996 | 3129.8216 | 3134.3828
| 82431532 | 2029 | WND013 | 316.7996 | 4.5613 | 0 | 0 | 316.7996 | 3129.8216 | 3134.3828
| 82431532 | 2030 | WND013 | 316.7996 | 4.5613 | 0 | 0 | 316.7996 | 3129.8216 | 3134.3828
| 82431532 | 2031 | WND013 | 316.7996 | 4.5613 | 0 | 0 | 316.7996 | 3129.8216 | 3134.3828
| 82431532 | 2032 | WND013 | 316.7996 | 4.5613 | 0 | 0 | 316.7996 | 3129.8216 | 3134.3828
| 82431532 | 2033 | WND013 | 316.7996 | 4.5613 | 0 | 0 | 316.7996 | 3129.8216 | 3134.3828
| 82431532 | 2034 | WND013 | 316.7996 | 4.5613 | 0 | 0 | 316.7996 | 3129.8216 | 3134.3828
| 160755450 | 2023 | WND013 | 0 | 0 | 3737.22 | 127435.3044 | 3737.22 | 3175.1061 | 130610.4105
| 160755450 | 2024 | WND013 | 0 | 0 | 4054.9043 | 138268.0083 | 4054.9043 | 3175.1061 | 141443.1143
| 160755450 | 2025 | WND013 | 0 | 0 | 4054.9043 | 138268.0083 | 4054.9043 | 3175.1061 | 141443.1143
| 160755450 | 2026 | WND013 | 0 | 0 | 4054.9043 | 138268.0083 | 4054.9043 | 3175.1061 | 141443.1143
| 160755450 | 2027 | WND013 | 0 | 0 | 4054.9043 | 138268.0083 | 4054.9043 | 3175.1061 | 141443.1143
| 160755450 | 2028 | WND013 | 0 | 0 | 4054.9043 | 138268.0083 | 4054.9043 | 3175.1061 | 141443.1143
| 160755450 | 2029 | WND013 | 0 | 0 | 4054.9043 | 138268.0083 | 4054.9043 | 3175.1061 | 141443.1143
| 160755450 | 2030 | WND013 | 0 | 0 | 4054.9043 | 138268.0083 | 4054.9043 | 3175.1061 | 141443.1143
| 160755450 | 2031 | WND013 | 0 | 0 | 4054.9043 | 138268.0083 | 4054.9043 | 3175.1061 | 141443.1143
| 160755450 | 2032 | WND013 | 0 | 0 | 4054.9043 | 138268.0083 | 4054.9043 | 3175.1061 | 141443.1143
| 160755450 | 2033 | WND013 | 0 | 0 | 4054.9043 | 138268.0083 | 4054.9043 | 3175.1061 | 141443.1143
| 160755450 | 2034 | WND013 | 0 | 0 | 4054.9043 | 138268.0083 | 4054.9043 | 3175.1061 | 141443.1143
| 171177820 | 2023 | WND013 | 0 | 0 | 0 | 0 | 0 | 1924.7669 | 1924.7669
| 171177820 | 2024 | WND013 | 0 | 0 | 0 | 0 | 0 | 1924.7669 | 1924.7669
| 171177820 | 2025 | WND013 | 0 | 0 | 0 | 0 | 0 | 1924.7669 | 1924.7669
| 171177820 | 2026 | WND013 | 0 | 0 | 0 | 0 | 0 | 1924.7669 | 1924.7669
| 171177820 | 2027 | WND013 | 0 | 0 | 0 | 0 | 0 | 1924.7669 | 1924.7669
| 171177820 | 2028 | WND013 | 0 | 0 | 0 | 0 | 0 | 1924.7669 | 1924.7669
| 171177820 | 2029 | WND013 | 0 | 0 | 0 | 0 | 0 | 1924.7669 | 1924.7669
| 171177820 | 2030 | WND013 | 0 | 0 | 0 | 0 | 0 | 1924.7669 | 1924.7669
| 171177820 | 2031 | WND013 | 0 | 0 | 0 | 0 | 0 | 1924.7669 | 1924.7669
| 171177820 | 2032 | WND013 | 0 | 0 | 0 | 0 | 0 | 1924.7669 | 1924.7669
| 171177820 | 2033 | WND013 | 0 | 0 | 0 | 0 | 0 | 1924.7669 | 1924.7669
| 171177820 | 2034 | WND013 | 0 | 0 | 0 | 0 | 0 | 1924.7669 | 1924.7669
| 197821077 | 2023 | WND013 | 0 | 0 | 336.0992 | 11460.6329 | 336.0992 | 3358.9345 | 14819.5674
| 197821077 | 2024 | WND013 | 0 | 0 | 481.0963 | 16404.8832 | 481.0963 | 3358.9345 | 19763.8177
| 197821077 | 2025 | WND013 | 0 | 0 | 481.0963 | 16404.8832 | 481.0963 | 3358.9345 | 19763.8177
| 197821077 | 2026 | WND013 | 0 | 0 | 481.0963 | 16404.8832 | 481.0963 | 3358.9345 | 19763.8177
| 197821077 | 2027 | WND013 | 0 | 0 | 481.0963 | 16404.8832 | 481.0963 | 3358.9345 | 19763.8177
| 197821077 | 2028 | WND013 | 0 | 0 | 481.0963 | 16404.8832 | 481.0963 | 3358.9345 | 19763.8177
| 197821077 | 2029 | WND013 | 0 | 0 | 481.0963 | 16404.8832 | 481.0963 | 3358.9345 | 19763.8177
| 197821077 | 2030 | WND013 | 0 | 0 | 481.0963 | 16404.8832 | 481.0963 | 3358.9345 | 19763.8177
| 197821077 | 2031 | WND013 | 0 | 0 | 481.0963 | 16404.8832 | 481.0963 | 3358.9345 | 19763.8177
| 197821077 | 2032 | WND013 | 0 | 0 | 481.0963 | 16404.8832 | 481.0963 | 3358.9345 | 19763.8177
| 197821077 | 2033 | WND013 | 0 | 0 | 481.0963 | 16404.8832 | 481.0963 | 3358.9345 | 19763.8177
| 197821077 | 2034 | WND013 | 0 | 0 | 481.0963 | 16404.8832 | 481.0963 | 3358.9345 | 19763.8177
| 20361880 | 2023 | WND023 | 10314.812 | 0 | 17.4784 | 595.9957 | 10332.2904 | 7154.7631 | 7750.7588
| 20361880 | 2024 | WND023 | 12000.3348 | 247.388 | 28.309 | 965.3068 | 12028.6437 | 7154.7631 | 8367.4579
| 20361880 | 2025 | WND023 | 19651.5468 | 385.3159 | 50.636 | 1726.6351 | 19702.1828 | 7154.7631 | 9266.7141
| 20361880 | 2026 | WND023 | 30248.5507 | 315.5926 | 79.7475 | 2719.3067 | 30328.2982 | 7154.7631 | 10189.6624
| 20361880 | 2027 | WND023 | 53620.8997 | 581.0988 | 229.5383 | 7827.0163 | 53850.438 | 7154.7631 | 15562.8782
| 20361880 | 2028 | WND023 | 63083.4845 | 771.2642 | 449.9781 | 15343.785 | 63533.4626 | 7154.7631 | 23269.8123
| 20361880 | 2029 | WND023 | 82039.974 | 843.1826 | 751.4792 | 25624.656 | 82791.4532 | 7154.7631 | 33622.6017
| 20361880 | 2030 | WND023 | 95576.2193 | 1104.9147 | 1447.1025 | 49344.6856 | 97023.3218 | 7154.7631 | 57604.3635
| 20361880 | 2031 | WND023 | 101362.7495 | 1571.9698 | 1925.3428 | 65652.1821 | 103288.0923 | 7154.7631 | 74378.915
| 20361880 | 2032 | WND023 | 137361.9268 | 2992.2748 | 4145.234 | 141348.159 | 141507.1609 | 7154.7631 | 151495.1969
| 20361880 | 2033 | WND023 | 141157.9818 | 4917.5552 | 7611.0867 | 259530.1225 | 148769.0685 | 7154.7631 | 271602.4407
| 20361880 | 2034 | WND023 | 141598.2884 | 5619.3379 | 10112.8941 | 344839.1462 | 151711.1825 | 7154.7631 | 357613.2472
| 20375645 | 2023 | WND023 | 0 | 0 | 8318.2581 | 283643.9287 | 8318.2581 | 6696.7528 | 290340.6815
| 20375645 | 2024 | WND023 | 0 | 0 | 9162.9698 | 312447.7177 | 9162.9698 | 6696.7528 | 319144.4704
| 20375645 | 2025 | WND023 | 0 | 0 | 11996.172 | 409056.9589 | 11996.172 | 6696.7528 | 415753.7117
| 20375645 | 2026 | WND023 | 0 | 0 | 13708.9754 | 467461.7689 | 13708.9754 | 6696.7528 | 474158.5217
| 20375645 | 2027 | WND023 | 0 | 0 | 15625.3886 | 532809.4606 | 15625.3886 | 6696.7528 | 539506.2134
| 20375645 | 2028 | WND023 | 0 | 0 | 19423.0216 | 662304.785 | 19423.0216 | 6696.7528 | 669001.5378
| 20375645 | 2029 | WND023 | 0 | 0 | 22698.163 | 773983.6932 | 22698.163 | 6696.7528 | 780680.446
| 20375645 | 2030 | WND023 | 0 | 0 | 23682.2916 | 807541.4518 | 23682.2916 | 6696.7528 | 814238.2045
| 20375645 | 2031 | WND023 | 6.7013 | 0.044862 | 29885.7745 | 1019073.7522 | 29892.4758 | 6696.7528 | 1025770.5498
| 20375645 | 2032 | WND023 | 97.114 | 1.0486 | 33831.316 | 1153612.6036 | 33928.43 | 6696.7528 | 1160310.405
| 20375645 | 2033 | WND023 | 82.2703 | 2.091 | 39115.5272 | 1333798.6963 | 39197.7975 | 6696.7528 | 1340497.5401
| 20375645 | 2034 | WND023 | 218.9028 | 5.0896 | 41298.9 | 1408249.4316 | 41517.8027 | 6696.7528 | 1414951.274
| 43606479 | 2023 | WND023 | 2218.018 | 0 | 0 | 0 | 2218.018 | 4035.5181 | 4035.5181
| 43606479 | 2024 | WND023 | 2726.3059 | 49.9173 | 0 | 0 | 2726.3059 | 4035.5181 | 4085.4353
| 43606479 | 2025 | WND023 | 8446.3455 | 164.5669 | 0 | 0 | 8446.3455 | 4035.5181 | 4200.085
| 43606479 | 2026 | WND023 | 13695.547 | 144.4047 | 0 | 0 | 13695.547 | 4035.5181 | 4179.9227
| 43606479 | 2027 | WND023 | 14473.8406 | 133.8273 | 0 | 0 | 14473.8406 | 4035.5181 | 4169.3454
| 43606479 | 2028 | WND023 | 14541.5505 | 140.0996 | 0 | 0 | 14541.5505 | 4035.5181 | 4175.6177
| 43606479 | 2029 | WND023 | 20871.5348 | 163.8756 | 0 | 0 | 20871.5348 | 4035.5181 | 4199.3936
| 43606479 | 2030 | WND023 | 23703.8239 | 203.4575 | 0 | 0 | 23703.8239 | 4035.5181 | 4238.9756
| 43606479 | 2031 | WND023 | 24266.8294 | 285.9428 | 0 | 0 | 24266.8294 | 4035.5181 | 4321.4608
| 43606479 | 2032 | WND023 | 26008.1852 | 410.5734 | 0 | 0 | 26008.1852 | 4035.5181 | 4446.0915
| 43606479 | 2033 | WND023 | 26516.211 | 773.9653 | 0 | 0 | 26516.211 | 4035.5181 | 4809.4834
| 43606479 | 2034 | WND023 | 29744.966 | 1020.5258 | 0 | 0 | 29744.966 | 4035.5181 | 5056.0438
| 83526343 | 2023 | WND024 | 516.856 | 0 | 0 | 0 | 516.856 | 91.7068 | 91.7068
| 83526343 | 2024 | WND024 | 1860.6468 | 38.8928 | 0 | 0 | 1860.6468 | 91.7068 | 130.5996
| 83526343 | 2025 | WND024 | 1870.6358 | 34.6397 | 0 | 0 | 1870.6358 | 91.7068 | 126.3465
| 83526343 | 2026 | WND024 | 3580.7936 | 36.8411 | 0 | 0 | 3580.7936 | 91.7068 | 128.5479
| 83526343 | 2027 | WND024 | 3648.8937 | 37.2589 | 0 | 0 | 3648.8937 | 91.7068 | 128.9657
| 83526343 | 2028 | WND024 | 5588.5494 | 65.7518 | 0 | 0 | 5588.5494 | 91.7068 | 157.4586
| 83526343 | 2029 | WND024 | 6022.758 | 53.4679 | 0 | 0 | 6022.758 | 91.7068 | 145.1747
| 83526343 | 2030 | WND024 | 6471.7918 | 60.031 | 0 | 0 | 6471.7918 | 91.7068 | 151.7378
| 83526343 | 2031 | WND024 | 10884.3233 | 170.4195 | 0 | 0 | 10884.3233 | 91.7068 | 262.1263
| 83526343 | 2032 | WND024 | 13559.6945 | 279.5483 | 0 | 0 | 13559.6945 | 91.7068 | 371.2551
| 83526343 | 2033 | WND024 | 14069.0763 | 489.1266 | 0 | 0 | 14069.0763 | 91.7068 | 580.8334
| 83526343 | 2034 | WND024 | 14310.244 | 583.9396 | 0 | 0 | 14310.244 | 91.7068 | 675.6464
| 132232100 | 2023 | WND024 | 0 | 0 | 0 | 0 | 0 | 195.4253 | 195.4253
| 132232100 | 2024 | WND024 | 0 | 0 | 0 | 0 | 0 | 195.4253 | 195.4253
| 132232100 | 2025 | WND024 | 0 | 0 | 0 | 0 | 0 | 195.4253 | 195.4253
| 132232100 | 2026 | WND024 | 0 | 0 | 0 | 0 | 0 | 195.4253 | 195.4253
| 132232100 | 2027 | WND024 | 0 | 0 | 0 | 0 | 0 | 195.4253 | 195.4253
| 132232100 | 2028 | WND024 | 0 | 0 | 0 | 0 | 0 | 195.4253 | 195.4253
| 132232100 | 2029 | WND024 | 1.3976 | 0.0030846 | 0 | 0 | 1.3976 | 195.4253 | 195.4284
| 132232100 | 2030 | WND024 | 2.6176 | 0.0085249 | 0 | 0 | 2.6176 | 195.4253 | 195.4338
| 132232100 | 2031 | WND024 | 39.6744 | 0.27102 | 0 | 0 | 39.6744 | 195.4253 | 195.6963
| 132232100 | 2032 | WND024 | 240.0672 | 2.3537 | 0 | 0 | 240.0672 | 195.4253 | 197.779
| 132232100 | 2033 | WND024 | 578.1319 | 14.8567 | 0 | 0 | 578.1319 | 195.4253 | 210.282
| 132232100 | 2034 | WND024 | 878.0417 | 23.4219 | 0.0285 | 0.97182 | 878.0702 | 195.4253 | 219.819
| 156707631 | 2023 | WND024 | 11162.0193 | 0 | 0 | 0 | 11162.0193 | 1124.6912 | 1124.6912
| 156707631 | 2024 | WND024 | 13116.7145 | 279.6616 | 0 | 0 | 13116.7145 | 1124.6912 | 1404.3528
| 156707631 | 2025 | WND024 | 12963.0979 | 262.9843 | 0 | 0 | 12963.0979 | 1124.6912 | 1387.6755
| 156707631 | 2026 | WND024 | 14634.5792 | 163.3214 | 0 | 0 | 14634.5792 | 1124.6912 | 1288.0126
| 156707631 | 2027 | WND024 | 16845.2011 | 158.4752 | 0 | 0 | 16845.2011 | 1124.6912 | 1283.1664
| 156707631 | 2028 | WND024 | 18038.0399 | 176.0379 | 0 | 0 | 18038.0399 | 1124.6912 | 1300.7292
| 156707631 | 2029 | WND024 | 19082.9617 | 140.7876 | 0 | 0 | 19082.9617 | 1124.6912 | 1265.4788
| 156707631 | 2030 | WND024 | 22633.2163 | 185.7278 | 0 | 0 | 22633.2163 | 1124.6912 | 1310.419
| 156707631 | 2031 | WND024 | 31116.9449 | 362.6248 | 0.72596 | 24.7544 | 31117.6709 | 1124.6912 | 1512.0705
| 156707631 | 2032 | WND024 | 31401.7794 | 521.5465 | 2.195 | 74.8487 | 31403.9745 | 1124.6912 | 1721.0865
| 156707631 | 2033 | WND024 | 33024.3605 | 1010.7586 | 6.3579 | 216.7989 | 33030.7185 | 1124.6912 | 2352.2487
| 156707631 | 2034 | WND024 | 34177.0598 | 1250.2626 | 17.2838 | 589.3581 | 34194.3436 | 1124.6912 | 2964.3119
| 158402233 | 2023 | WND024 | 0 | 0 | 0 | 0 | 0 | 1496.4463 | 1496.4463
| 158402233 | 2024 | WND024 | 0 | 0 | 0 | 0 | 0 | 1496.4463 | 1496.4463
| 158402233 | 2025 | WND024 | 0 | 0 | 0 | 0 | 0 | 1496.4463 | 1496.4463
| 158402233 | 2026 | WND024 | 0 | 0 | 0 | 0 | 0 | 1496.4463 | 1496.4463
| 158402233 | 2027 | WND024 | 75.9337 | 0.33479 | 0 | 0 | 75.9337 | 1496.4463 | 1496.7811
| 158402233 | 2028 | WND024 | 322.8933 | 1.3776 | 0 | 0 | 322.8933 | 1496.4463 | 1497.8239
| 158402233 | 2029 | WND024 | 510.879 | 1.6405 | 0 | 0 | 510.879 | 1496.4463 | 1498.0868
| 158402233 | 2030 | WND024 | 680.5113 | 2.6665 | 0 | 0 | 680.5113 | 1496.4463 | 1499.1128
| 158402233 | 2031 | WND024 | 983.7532 | 7.9066 | 0 | 0 | 983.7532 | 1496.4463 | 1504.3529
| 158402233 | 2032 | WND024 | 1191.009 | 14.2978 | 0 | 0 | 1191.009 | 1496.4463 | 1510.7441
| 158402233 | 2033 | WND024 | 1321.2086 | 37.2707 | 0 | 0 | 1321.2086 | 1496.4463 | 1533.717
| 158402233 | 2034 | WND024 | 1477.845 | 47.3786 | 0 | 0 | 1477.845 | 1496.4463 | 1543.825

## Options_risk
Powercor
Regional and rural supply upgrades
WORKINGS - OPTIONS
| Option | Year | total_risk_kwh | total_risk_cost | total_risk_cost_discounted | total_augmentation_cost | total_augmentation_cost_2026
| Option3 | 2023 | 742136.4513 | 31443018.2849 | 31443018.2849 | 52342147.3841 | 58032674.4206
| Option3 | 2024 | 790383.9754 | 33346528.4905 | 32218868.1068 | 52342147.3841 | 58032674.4206
| Option3 | 2025 | 849164.8241 | 35949127.4071 | 33558895.1033 | 56131624.6715 | 62234135.626
| Option3 | 2026 | 860068.9418 | 36316572.8958 | 32755468.0182 | 56131624.6715 | 62234135.626
| Option3 | 2027 | 985823.9608 | 41864756 | 36482716.2307 | 56131624.6715 | 62234135.626
| Option3 | 2028 | 1037370.6815 | 44355217.3784 | 37345902.8428 | 56344195.2488 | 62469816.4248
| Option3 | 2029 | 1050236.4518 | 44868611.6369 | 36500644.4758 | 56344195.2488 | 62469816.4248
| Option3 | 2030 | 1055759.6399 | 45127707.6408 | 35469970.282 | 56344195.2488 | 62469816.4248
| Option3 | 2031 | 1106462.9458 | 47583597.8995 | 36135534.1312 | 56344195.2488 | 62469816.4248
| Option3 | 2032 | 1115847.7981 | 47954270.0541 | 35185533.1874 | 56344195.2488 | 62469816.4248
| Option3 | 2033 | 1126615.2352 | 48386181.3234 | 34301874.2638 | 56344195.2488 | 62469816.4248
| Option3 | 2034 | 1130554.4425 | 48541911.8253 | 33248574.441 | 56344195.2488 | 62469816.4248
| Option3 | 2035 | 1130554.4425 | 48541911.8253 | 33248574.441 | 56344195.2488 | 62469816.4248
| Option3 | 2036 | 1130554.4425 | 48541911.8253 | 33248574.441 | 56344195.2488 | 62469816.4248
| Option3 | 2037 | 1130554.4425 | 48541911.8253 | 33248574.441 | 56344195.2488 | 62469816.4248
| Option3 | 2038 | 1130554.4425 | 48541911.8253 | 33248574.441 | 56344195.2488 | 62469816.4248
| Option3 | 2039 | 1130554.4425 | 48541911.8253 | 33248574.441 | 56344195.2488 | 62469816.4248
| Option3 | 2040 | 1130554.4425 | 48541911.8253 | 33248574.441 | 56344195.2488 | 62469816.4248
| Option2 | 2023 | 677601.4532 | 28685990.6394 | 28685990.6394 | 36289048.5357 | 40234316.7782
| Option2 | 2024 | 719799.8554 | 30331849.5423 | 29306134.8235 | 36289048.5357 | 40234316.7782
| Option2 | 2025 | 778236.9288 | 32914231.5712 | 30725787.366 | 39332356.4776 | 43608486.6926
| Option2 | 2026 | 787701.8614 | 33224882.618 | 29966940.524 | 39332356.4776 | 43608486.6926
| Option2 | 2027 | 912409.1757 | 38722469.9999 | 33744395.5187 | 39332356.4776 | 43608486.6926
| Option2 | 2028 | 963174.1144 | 41174534.8835 | 34667853.5297 | 39544927.0549 | 43844167.4914
| Option2 | 2029 | 972246.944 | 41508722.1954 | 33767372.2503 | 39544927.0549 | 43844167.4914
| Option2 | 2030 | 977259.6729 | 41753174.7107 | 32817617.9025 | 39544927.0549 | 43844167.4914
| Option2 | 2031 | 1028849.4888 | 44241237.697 | 33597307.1684 | 39544927.0549 | 43844167.4914
| Option2 | 2032 | 1035397.0731 | 44485424.5337 | 32640333.7914 | 39544927.0549 | 43844167.4914
| Option2 | 2033 | 1040844.0574 | 44679966.1186 | 31674468.5774 | 39544927.0549 | 43844167.4914
| Option2 | 2034 | 1043791.4054 | 44786015.8526 | 30675989.5933 | 39544927.0549 | 43844167.4914
| Option2 | 2035 | 1043791.4054 | 44786015.8526 | 30675989.5933 | 39544927.0549 | 43844167.4914
| Option2 | 2036 | 1043791.4054 | 44786015.8526 | 30675989.5933 | 39544927.0549 | 43844167.4914
| Option2 | 2037 | 1043791.4054 | 44786015.8526 | 30675989.5933 | 39544927.0549 | 43844167.4914
| Option2 | 2038 | 1043791.4054 | 44786015.8526 | 30675989.5933 | 39544927.0549 | 43844167.4914
| Option2 | 2039 | 1043791.4054 | 44786015.8526 | 30675989.5933 | 39544927.0549 | 43844167.4914
| Option2 | 2040 | 1043791.4054 | 44786015.8526 | 30675989.5933 | 39544927.0549 | 43844167.4914
| Option4 | 2023 | 821819.3623 | 33825945.3882 | 33825945.3882 | 99288080.9418 | 110082470.1146
| Option4 | 2024 | 879464.3145 | 35883961.0089 | 34670493.7284 | 99288080.9418 | 110082470.1146
| Option4 | 2025 | 952935.9849 | 38478441.1589 | 35920036.5553 | 107222191.216 | 118879159.9979
| Option4 | 2026 | 989042.3877 | 38955540.5474 | 35135665.6421 | 107222191.216 | 118879159.9979
| Option4 | 2027 | 1142484.0247 | 44647448.1205 | 38907671.6512 | 107222191.216 | 118879159.9979
| Option4 | 2028 | 1203781.5678 | 47145913.5861 | 39695594.1665 | 107434761.7934 | 119114840.7967
| Option4 | 2029 | 1240434.8071 | 47882684.6032 | 38952594.7759 | 107434761.7934 | 119114840.7967
| Option4 | 2030 | 1264112.5034 | 48323301.8923 | 37981678.4777 | 107434761.7934 | 119114840.7967
| Option4 | 2031 | 1320366.5553 | 50777735.3986 | 38561199.0602 | 107434761.7934 | 119114840.7967
| Option4 | 2032 | 1373590.2705 | 51464648.0368 | 37761206.2375 | 107434761.7934 | 119114840.7967
| Option4 | 2033 | 1403587.8181 | 52524003.512 | 37235254.261 | 107434761.7934 | 119114840.7967
| Option4 | 2034 | 1411616.8536 | 52813377.7904 | 36174296.7451 | 107434761.7934 | 119114840.7967
| Option4 | 2035 | 1411616.8536 | 52813377.7904 | 36174296.7451 | 107434761.7934 | 119114840.7967
| Option4 | 2036 | 1411616.8536 | 52813377.7904 | 36174296.7451 | 107434761.7934 | 119114840.7967
| Option4 | 2037 | 1411616.8536 | 52813377.7904 | 36174296.7451 | 107434761.7934 | 119114840.7967
| Option4 | 2038 | 1411616.8536 | 52813377.7904 | 36174296.7451 | 107434761.7934 | 119114840.7967
| Option4 | 2039 | 1411616.8536 | 52813377.7904 | 36174296.7451 | 107434761.7934 | 119114840.7967
| Option4 | 2040 | 1411616.8536 | 52813377.7904 | 36174296.7451 | 107434761.7934 | 119114840.7967

## Workings_risks
Powercor
Regional and rural supply upgrades
WORKINGS - RISKS
[5 empty] | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
[5 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | Option 1 (base case) | Total risk | 2034 | 43929947.0411 | 49988716.7362 | 52690343.3273 | 53585767.7148 | 54058138.6687 | 56646621.3435 | 57424173.2902 | 59134679.1394 | 59492948.7658 | 59492948.7658 | 59492948.7658 | 59492948.7658 | 59492948.7658 | 59492948.7658 | 59492948.7658
Reduction in risk
| Option2 | Option 2 | Reduction in risk from limited SWER upgrades | 2040 | 33224882.618 | 38722469.9999 | 41174534.8835 | 41508722.1954 | 41753174.7107 | 44241237.697 | 44485424.5337 | 44679966.1186 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526 | 44786015.8526
| Option3 | Option 3 | Reduction in risk from economic SWER upgrades | 2040 | 36316572.8958 | 41864756 | 44355217.3784 | 44868611.6369 | 45127707.6408 | 47583597.8995 | 47954270.0541 | 48386181.3234 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253 | 48541911.8253
| Option4 | Option 4 | Reduction in risk from accelerated SWER upgrades | 2040 | 38955540.5474 | 44647448.1205 | 47145913.5861 | 47882684.6032 | 48323301.8923 | 50777735.3986 | 51464648.0368 | 52524003.512 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904 | 52813377.7904
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option2 | Option 2 | Residual risk |  | 10705064.4231 | 11266246.7363 | 11515808.4439 | 12077045.5195 | 12304963.958 | 12405383.6465 | 12938748.7564 | 14454713.0208 | 14706932.9132 | 14706932.9132 | 14706932.9132 | 14706932.9132 | 14706932.9132 | 14706932.9132 | 14706932.9132
| Option3 | Option 3 | Residual risk |  | 7613374.1453 | 8123960.7362 | 8335125.949 | 8717156.0779 | 8930431.0279 | 9063023.444 | 9469903.2361 | 10748497.816 | 10951036.9405 | 10951036.9405 | 10951036.9405 | 10951036.9405 | 10951036.9405 | 10951036.9405 | 10951036.9405
| Option4 | Option 4 | Residual risk |  | 4974406.4937 | 5341268.6157 | 5544429.7412 | 5703083.1117 | 5734836.7765 | 5868885.9449 | 5959525.2533 | 6610675.6274 | 6679570.9754 | 6679570.9754 | 6679570.9754 | 6679570.9754 | 6679570.9754 | 6679570.9754 | 6679570.9754

## Misc_calcs
Powercor
Regional and rural supply upgrades
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 1 | TRUE
| Option 3 | 1 | TRUE
| Option 4 | 1 | TRUE
| Option 5 | Not used | FALSE
| First year | 1
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
Powercor
Regional and rural supply upgrades
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | FALSE |  |  | FALSE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
Powercor
| Reliability in worst-served areas | per MWh | 151432.8174
| Network resilience | per MWh | 24590
| Enabling solar exports | per MWh | 88.3577
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.35181
| Customer value of time - business | per minute customer time | 0.35181
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020