## Cover
Powercor
Regulatory proposal 2026-31
SHN transformer
| Model number: | 4.03
2025-01-31
15

## Summary
Powercor
SHN transformer replacement
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Replace transformer #2 completed in 2030-2031 |  | -3.814 | 4.5676 | 0.75356
| Option 3 | Refurbish transformer #2 completed in 2029-2030 |  | -0.49333 | 0.31603 | -0.1773
| Option 4 | 0
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | Replace transformer #2 completed in 2030-2031 |  | 0.75356
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 0 | 0 | 0 | 5.0249 | 2.5124 |  | 7.5373
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
| Capex and risk ($M, 2026) |  | Value of expected unserved energy ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 0.75356 | -0.1773 |  |  |  | Option 2
| Capex 10% higher |  | 0 | 0.37215 | -0.22663 |  |  |  | Option 2
| Capex 10% lower |  | 0 | 1.135 | -0.12796 |  |  |  | Option 2
| Total benefits 10% higher |  | 0 | 1.2103 | -0.14569 |  |  |  | Option 2
| Total benefits 10% lower |  | 0 | 0.2968 | -0.2089 |  |  |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  | 0 | -0.084608 | -0.25823 |  |  |  | Option 1 (base case)
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
Powercor
SHN transformer replacement
Project
|  | Business: |  | Powercor
|  | Descripton: |  | SHN transformer replacement
|  | Date of cost inputs: |  | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Replace transformer #2 completed in 2030-2031
|  | Option 3 |  | Refurbish transformer #2 completed in 2029-2030
Option 4
Option 5
|  | Compliance project |  | No
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | SHN |  | Shepparton North | 47127.1698 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 151432.8174 | 2023-12-31 | per MWh
|  | Network resilience |  |  |  | 24590 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 88.3577 | 2023-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
Powercor
SHN transformer replacement
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 47127.1698 | 2023-12-31 |  | 261320.5924 | 275273.7171 | 290699.4756 | 305387.7555 | 318262.5666 | 331870.3465 | 349435.5104 | 367531.6743 | 381910.2637 | 394526.7084 | 407313.9549 | 420271.1857 | 433397.6064 | 446692.4445 | 460154.9488 | 473784.3885 | 487580.0524 | 501541.248 | 515667.3013 | 529957.5555 | 544411.371 | 559028.1242 | 573807.2076 | 588748.0286 | 603850.0095
| Safety risk | (after DF) |  | 2023-12-31 |  | 303.6386 | 315.4632 | 327.4732 | 339.6673 | 352.0445 | 364.6034 | 377.3431 | 390.2624 | 403.3602 | 416.6356 | 430.0875 | 443.7149 | 457.5168 | 471.4924 | 485.6406 | 499.9606 | 514.4516 | 529.1126 | 543.9429 | 558.9415 | 574.1077 | 589.4407 | 589.4407 | 589.4407 | 589.4407
| Unplanned replacement risk |  |  | 2023-12-31 |  | 13904.2221 | 14445.6943 | 14995.6557 | 15554.0505 | 16120.8245 | 16695.9249 | 17279.3003 | 17870.9008 | 18470.6777 | 19078.5833 | 19694.5715 | 20318.597 | 20950.6157 | 21590.5845 | 22238.4613 | 22894.2049 | 23557.7751 | 24229.1325 | 24908.2386 | 25595.0557 | 26289.5469 | 26991.676 | 26991.676 | 26991.676 | 26991.676
| Unplanned fault risk |  |  | 2023-12-31 |  | 1122.3175 | 1166.0239 | 1210.4155 | 1255.4879 | 1301.2366 | 1347.6574 | 1394.7462 | 1442.4988 | 1490.9115 | 1539.9803 | 1589.7014 | 1640.0714 | 1691.0865 | 1742.7433 | 1795.0385 | 1847.9686 | 1901.5305 | 1955.721 | 2010.5369 | 2065.9752 | 2122.033 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073
| Enviromental risk | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 276650.7706 | 291200.8984 | 307233.02 | 322536.9612 | 336036.6722 | 350278.5322 | 368486.8999 | 387235.3363 | 402275.213 | 415561.9076 | 429028.3153 | 442673.569 | 456496.8254 | 470497.2647 | 484674.0892 | 499026.5227 | 513553.8096 | 528255.2141 | 543130.0196 | 558177.5279 | 573397.0586 | 588787.9482 | 603567.0315 | 618507.8525 | 633609.8334
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
Powercor
SHN transformer replacement
OPTION 2 | Replace transformer #2 completed in 2030-2031
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Replace 1 transformer |  | 50 | 2023-12-31 | 0 | 0 | 0 | 4515047.3 | 2257523.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 4515047.3 | 2257523.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 47127.1698 | 2023-12-31 | 261320.5924 | 275273.7171 | 290699.4756 | 305387.7555 | 318262.5666 | 12104.0395 | 22580.7784 | 32962.8955 | 43024.0746 | 52863.6902 | 62719.4986 | 72630.995 | 82624.3523 | 92717.8391 | 102924.6923 | 113254.7731 | 123715.5845 | 134312.9282 | 145051.3461 | 155934.4264 | 166965.0229 | 178145.414 | 189477.4226 | 200962.5058 | 212601.8244
| Safety risk | (after DF) |  | 2023-12-31 | 303.6386 | 315.4632 | 327.4732 | 339.6673 | 352.0445 | 182.5457 | 189.4644 | 196.7109 | 204.2562 | 212.0823 | 220.1761 | 228.5274 | 237.1281 | 245.9713 | 255.0512 | 264.3625 | 273.9008 | 283.6619 | 293.6422 | 303.8383 | 314.2471 | 324.8657 | 324.8657 | 324.8657 | 324.8657
| Unplanned replacement risk |  |  | 2023-12-31 | 13904.2221 | 14445.6943 | 14995.6557 | 15554.0505 | 16120.8245 | 8359.1375 | 8675.9578 | 9007.7862 | 9353.3027 | 9711.6754 | 10082.3055 | 10464.73 | 10858.5737 | 11263.5224 | 11679.3069 | 12105.6918 | 12542.4688 | 12989.451 | 13446.4692 | 13913.3688 | 14390.0079 | 14876.255 | 14876.255 | 14876.255 | 14876.255
| Unplanned fault risk |  |  | 2023-12-31 | 1122.3175 | 1166.0239 | 1210.4155 | 1255.4879 | 1301.2366 | 674.7307 | 700.3038 | 727.0882 | 754.9775 | 783.9046 | 813.821 | 844.6894 | 876.4796 | 909.1662 | 942.7273 | 977.1442 | 1012.3998 | 1048.4792 | 1085.3687 | 1123.0558 | 1161.529 | 1200.7778 | 1200.7778 | 1200.7778 | 1200.7778
| Enviromental risk | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 276650.7706 | 291200.8984 | 307233.02 | 322536.9612 | 336036.6722 | 21320.4535 | 32146.5044 | 42894.4808 | 53336.611 | 63571.3524 | 73835.8011 | 84168.9418 | 94596.5337 | 105136.499 | 115801.7777 | 126601.9716 | 137544.3539 | 148634.5204 | 159876.8262 | 171274.6893 | 182830.8068 | 194547.3125 | 205879.3212 | 217364.4043 | 229003.723
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - residential | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - business | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 328958.0787 | 336340.3956 | 344340.8555 | 348938.602 | 351990.5552 | 355192.5142 | 358504.6271 | 361900.2917 | 365360.7657 | 368872.3116 | 372424.5511 | 376009.4556 | 379620.6937 | 383253.1935 | 386902.8386 | 390566.2517 | 394240.6356 | 397687.7104 | 401143.4482 | 404606.1104
Capital expenditure
| Replace 1 transformer |  |  | 2023-12-31 | 0 | 0 | 0 | -4515047.3 | -2257523.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Replace 1 transformer |  |  | 2023-12-31 | 0 | 0 | 0 | -4515047.3 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95 | -6772570.95
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Replace 1 transformer |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -192493.2153 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -192493.2153 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -192493.2153 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 328958.0787 | 336340.3956 | 344340.8555 | 348938.602 | 351990.5552 | 355192.5142 | 358504.6271 | 361900.2917 | 365360.7657 | 368872.3116 | 372424.5511 | 376009.4556 | 379620.6937 | 383253.1935 | 386902.8386 | 390566.2517 | 394240.6356 | 397687.7104 | 401143.4482 | 404606.1104
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -192493.2153 | 40218.2558 | 47600.5727 | 55601.0326 | 60198.7791 | 63250.7323 | 66452.6913 | 69764.8042 | 73160.4688 | 76620.9428 | 80132.4887 | 83684.7282 | 87269.6327 | 90880.8708 | 94513.3706 | 98163.0157 | 101826.4288 | 105500.8127 | 108947.8875 | 112403.6253 | 115866.2875
| First capex year |  |  | 4
| First year |  |  | 4
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | 0 | 0 | 0 | -192493.2153 | 40218.2558 | 47600.5727 | 55601.0326 | 60198.7791 | 63250.7323 | 66452.6913 | 69764.8042 | 73160.4688 | 76620.9428 | 80132.4887 | 83684.7282 | 87269.6327 | 90880.8708 | 94513.3706 | 98163.0157 | 101826.4288 | 105500.8127 | 108947.8875 | 112403.6253 | 115866.2875
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | -192493.2153 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229 | -288739.8229
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 328958.0787 | 336340.3956 | 344340.8555 | 348938.602 | 351990.5552 | 355192.5142 | 358504.6271 | 361900.2917 | 365360.7657 | 368872.3116 | 372424.5511 | 376009.4556 | 379620.6937 | 383253.1935 | 386902.8386 | 390566.2517 | 394240.6356 | 397687.7104 | 401143.4482 | 404606.1104
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | 0 | 0 | 0 | -211742.5368 | 11344.2736 | 18726.5904 | 26727.0503 | 31324.7968 | 34376.75 | 37578.7091 | 40890.822 | 44286.4866 | 47746.9605 | 51258.5064 | 54810.7459 | 58395.6505 | 62006.8885 | 65639.3883 | 69289.0334 | 72952.4465 | 76626.8304 | 80073.9052 | 83529.643 | 86992.3052
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | 0 | 0 | 0 | -173243.8937 | 69092.2381 | 76474.555 | 84475.0149 | 89072.7614 | 92124.7146 | 95326.6736 | 98638.7865 | 102034.4511 | 105494.9251 | 109006.4709 | 112558.7105 | 116143.615 | 119754.8531 | 123387.3529 | 127036.998 | 130700.4111 | 134374.795 | 137821.8698 | 141277.6076 | 144740.2698
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | 0 | 0 | 0 | -192493.2153 | 73114.0637 | 81234.6122 | 90035.1182 | 95092.6393 | 98449.7878 | 101971.9428 | 105615.267 | 109350.498 | 113157.0194 | 117019.7198 | 120927.1833 | 124870.5783 | 128842.9402 | 132838.6899 | 136853.2996 | 140883.054 | 144924.8763 | 148716.6585 | 152517.9701 | 156326.8986
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | 0 | 0 | 0 | -192493.2153 | 7322.448 | 13966.5331 | 21166.9471 | 25304.9189 | 28051.6768 | 30933.4399 | 33914.3415 | 36970.4397 | 40084.8663 | 43245.2575 | 46442.2731 | 49668.6872 | 52918.8014 | 56188.0512 | 59472.7319 | 62769.8036 | 66076.7492 | 69179.1164 | 72289.2805 | 75405.6765
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | 0 | 0 | 0 | -211742.5368 | -21551.5343 | -14907.4492 | -7707.0352 | -3569.0634 | -822.3055 | 2059.4576 | 5040.3592 | 8096.4574 | 11210.884 | 14371.2752 | 17568.2908 | 20794.7049 | 24044.8192 | 27314.0689 | 30598.7496 | 33895.8213 | 37202.7669 | 40305.1341 | 43415.2982 | 46531.6942
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 0 | 0 | -192493.2153 | 40218.2558 | 47600.5727 | 55601.0326 | 60198.7791 | 63250.7323 | 66452.6913 | 69764.8042 | 73160.4688 | 76620.9428 | 80132.4887 | 83684.7282 | 87269.6327 | 90880.8708 | 94513.3706 | 98163.0157 | 101826.4288 | 105500.8127 | 108947.8875 | 112403.6253 | 115866.2875
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 0 | 0 | -192493.2153 | 40218.2558 | 47600.5727 | 55601.0326 | 60198.7791 | 63250.7323 | 66452.6913 | 69764.8042 | 73160.4688 | 76620.9428 | 80132.4887 | 83684.7282 | 87269.6327 | 90880.8708 | 94513.3706 | 98163.0157 | 101826.4288 | 105500.8127 | 108947.8875 | 112403.6253 | 115866.2875
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 0 | 0 | -192493.2153 | 40218.2558 | 47600.5727 | 55601.0326 | 60198.7791 | 63250.7323 | 66452.6913 | 69764.8042 | 73160.4688 | 76620.9428 | 80132.4887 | 83684.7282 | 87269.6327 | 90880.8708 | 94513.3706 | 98163.0157 | 101826.4288 | 105500.8127 | 108947.8875 | 112403.6253 | 115866.2875

## Option3
Powercor
SHN transformer replacement
OPTION 3 | Refurbish transformer #2 completed in 2029-2030
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Refurbish 1 transformer |  | 10 | 2023-12-31 | 0 | 0 | 0 | 500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 47127.1698 | 2023-12-31 | 261320.5924 | 275273.7171 | 290699.4756 | 305387.7555 | 301881.3627 | 314786.9228 | 331445.958 | 348608.4301 | 362244.5237 | 374209.0269 | 386335.3581 | 398622.7363 | 411070.4022 | 423677.6174 | 436443.6635 | 449367.8415 | 462449.471 | 475687.8894 | 489082.4512 | 502632.5277 | 516337.5061 | 530196.7889 | 544209.7938 | 558375.9526 | 572694.7112
| Safety risk | (after DF) |  | 2023-12-31 | 303.6386 | 315.4632 | 327.4732 | 339.6673 | 348.524 | 360.9574 | 373.5697 | 386.3598 | 399.3266 | 412.4692 | 425.7866 | 439.2777 | 452.9416 | 466.7774 | 480.7842 | 494.961 | 509.3071 | 523.8215 | 538.5034 | 553.3521 | 568.3666 | 583.5463 | 583.5463 | 583.5463 | 583.5463
| Unplanned replacement risk |  |  | 2023-12-31 | 13904.2221 | 14445.6943 | 14995.6557 | 15554.0505 | 15314.7832 | 15861.1286 | 16415.3353 | 16977.3558 | 17547.1438 | 18124.6542 | 18709.843 | 19302.6672 | 19903.0849 | 20511.0553 | 21126.5382 | 21749.4946 | 22379.8863 | 23017.6759 | 23662.8267 | 24315.3029 | 24975.0695 | 25642.0922 | 25642.0922 | 25642.0922 | 25642.0922
| Unplanned fault risk |  |  | 2023-12-31 | 1122.3175 | 1166.0239 | 1210.4155 | 1255.4879 | 1301.2366 | 1347.6574 | 1394.7462 | 1442.4988 | 1490.9115 | 1539.9803 | 1589.7014 | 1640.0714 | 1691.0865 | 1742.7433 | 1795.0385 | 1847.9686 | 1901.5305 | 1955.721 | 2010.5369 | 2065.9752 | 2122.033 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073
| Enviromental risk | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 276650.7706 | 291200.8984 | 307233.02 | 322536.9612 | 318845.9065 | 332356.6662 | 349629.6091 | 367414.6445 | 381681.9056 | 394286.1306 | 407060.6891 | 420004.7526 | 433117.5153 | 446398.1934 | 459846.0244 | 473460.2658 | 487240.1949 | 501185.1077 | 515294.3182 | 529567.1579 | 544002.9752 | 558601.1347 | 572614.1395 | 586780.2983 | 601099.0569
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 17190.7656 | 17921.866 | 18857.2908 | 19820.6919 | 20593.3074 | 21275.777 | 21967.6262 | 22668.8164 | 23379.3102 | 24099.0713 | 24828.0648 | 25566.2569 | 26313.6146 | 27070.1064 | 27835.7014 | 28610.37 | 29394.0833 | 30186.8135 | 30952.892 | 31727.5542 | 32510.7764
Capital expenditure
| Refurbish 1 transformer |  |  | 2023-12-31 | 0 | 0 | 0 | -500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Refurbish 1 transformer |  |  | 2023-12-31 | 0 | 0 | 0 | -500000 | -500000 | -500000 | -500000 | -500000 | -500000 | -500000 | -500000 | -500000 | -500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Refurbish 1 transformer |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 17190.7656 | 17921.866 | 18857.2908 | 19820.6919 | 20593.3074 | 21275.777 | 21967.6262 | 22668.8164 | 23379.3102 | 24099.0713 | 24828.0648 | 25566.2569 | 26313.6146 | 27070.1064 | 27835.7014 | 28610.37 | 29394.0833 | 30186.8135 | 30952.892 | 31727.5542 | 32510.7764
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -42929.9183 | -42198.8179 | -41263.3931 | -40299.992 | -39527.3765 | -38844.9069 | -38153.0577 | -37451.8675 | -36741.3738 | -36021.6126 | 24828.0648 | 25566.2569 | 26313.6146 | 27070.1064 | 27835.7014 | 28610.37 | 29394.0833 | 30186.8135 | 30952.892 | 31727.5542 | 32510.7764
| First capex year |  |  | 4
| First year |  |  | 4
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | 0 | 0 | 0 | -42929.9183 | -42198.8179 | -41263.3931 | -40299.992 | -39527.3765 | -38844.9069 | -38153.0577 | -37451.8675 | -36741.3738 | -36021.6126 | 24828.0648 | 25566.2569 | 26313.6146 | 27070.1064 | 27835.7014 | 28610.37 | 29394.0833 | 30186.8135 | 30952.892 | 31727.5542 | 32510.7764
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 17190.7656 | 17921.866 | 18857.2908 | 19820.6919 | 20593.3074 | 21275.777 | 21967.6262 | 22668.8164 | 23379.3102 | 24099.0713 | 24828.0648 | 25566.2569 | 26313.6146 | 27070.1064 | 27835.7014 | 28610.37 | 29394.0833 | 30186.8135 | 30952.892 | 31727.5542 | 32510.7764
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | 0 | 0 | 0 | -48941.9867 | -48210.8863 | -47275.4615 | -46312.0604 | -45539.4449 | -44856.9753 | -44165.1261 | -43463.9359 | -42753.4422 | -42033.681 | 24828.0648 | 25566.2569 | 26313.6146 | 27070.1064 | 27835.7014 | 28610.37 | 29394.0833 | 30186.8135 | 30952.892 | 31727.5542 | 32510.7764
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | 0 | 0 | 0 | -36917.8499 | -36186.7495 | -35251.3247 | -34287.9237 | -33515.3081 | -32832.8385 | -32140.9893 | -31439.7991 | -30729.3054 | -30009.5442 | 24828.0648 | 25566.2569 | 26313.6146 | 27070.1064 | 27835.7014 | 28610.37 | 29394.0833 | 30186.8135 | 30952.892 | 31727.5542 | 32510.7764
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | 0 | 0 | 0 | -41210.8417 | -40406.6313 | -39377.664 | -38317.9229 | -37468.0457 | -36717.3292 | -35956.2951 | -35184.9859 | -34403.4428 | -33611.7055 | 27310.8713 | 28122.8826 | 28944.9761 | 29777.117 | 30619.2716 | 31471.407 | 32333.4916 | 33205.4949 | 34048.1812 | 34900.3096 | 35761.8541
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | 0 | 0 | 0 | -44648.9949 | -43991.0045 | -43149.1222 | -42282.0612 | -41586.7072 | -40972.4846 | -40349.8203 | -39718.7492 | -39079.3048 | -38431.5198 | 22345.2584 | 23009.6312 | 23682.2532 | 24363.0957 | 25052.1313 | 25749.333 | 26454.675 | 27168.1322 | 27857.6028 | 28554.7988 | 29259.6988
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | 0 | 0 | 0 | -50661.0632 | -50003.0729 | -49161.1906 | -48294.1296 | -47598.7756 | -46984.553 | -46361.8887 | -45730.8176 | -45091.3732 | -44443.5881 | 22345.2584 | 23009.6312 | 23682.2532 | 24363.0957 | 25052.1313 | 25749.333 | 26454.675 | 27168.1322 | 27857.6028 | 28554.7988 | 29259.6988
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 0 | -42929.9183 | -42198.8179 | -41263.3931 | -40299.992 | -39527.3765 | -38844.9069 | -38153.0577 | -37451.8675 | -36741.3738 | -36021.6126 | 24828.0648 | 25566.2569 | 26313.6146 | 27070.1064 | 27835.7014 | 28610.37 | 29394.0833 | 30186.8135 | 30952.892 | 31727.5542 | 32510.7764
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 0 | -42929.9183 | -42198.8179 | -41263.3931 | -40299.992 | -39527.3765 | -38844.9069 | -38153.0577 | -37451.8675 | -36741.3738 | -36021.6126 | 24828.0648 | 25566.2569 | 26313.6146 | 27070.1064 | 27835.7014 | 28610.37 | 29394.0833 | 30186.8135 | 30952.892 | 31727.5542 | 32510.7764
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 0 | -42929.9183 | -42198.8179 | -41263.3931 | -40299.992 | -39527.3765 | -38844.9069 | -38153.0577 | -37451.8675 | -36741.3738 | -36021.6126 | 24828.0648 | 25566.2569 | 26313.6146 | 27070.1064 | 27835.7014 | 28610.37 | 29394.0833 | 30186.8135 | 30952.892 | 31727.5542 | 32510.7764

## Option4
Powercor
SHN transformer replacement
OPTION 4 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 47127.1698 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option5
Powercor
SHN transformer replacement
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 47127.1698 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
Powercor
SHN transformer replacement
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 7612846.3313 | 2026-06-30 |  | 290826.9921 | 306355.601 | 323523.1227 | 339869.8952 | 354198.4353 | 369342.7056 | 388891.1986 | 409030.6483 | 425032.7622 | 439073.7631 | 453304.8514 | 467725.1175 | 482333.6771 | 497129.6706 | 512112.2619 | 527280.6377 | 542634.0064 | 558171.5976 | 573892.6609 | 589796.4656 | 605882.2996 | 622149.4692 | 638597.298 | 655225.1266 | 672032.3121
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 7412579.677 | 2026-06-30 |  | 307888.1412 | 324081.1625 | 341923.5133 | 358955.4631 | 373979.4621 | 389829.4083 | 410093.731 | 430959.103 | 447697.1719 | 462484.1023 | 477471.0378 | 492657.0132 | 508041.0901 | 523622.356 | 539399.9233 | 555372.928 | 571540.5293 | 587901.9083 | 604456.2675 | 621202.8298 | 638140.8379 | 655269.5536 | 671717.3823 | 688345.211 | 705152.3965
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 2806633.7321 | 2026-06-30 |  | 290826.9921 | 306355.601 | 323523.1227 | 339869.8952 | 354198.4353 | 13470.7386 | 25130.4338 | 36684.8233 | 47882.0367 | 58832.6693 | 69801.3231 | 80831.9529 | 91953.6865 | 103186.8556 | 114546.1917 | 126042.6692 | 137684.6386 | 149478.5564 | 161429.4774 | 173541.3952 | 185817.4854 | 198260.2842 | 210871.8198 | 223653.7141 | 236607.2591
Option 2 | Capital expenditure | Option 2Capital expenditure | -6606937.3341 | 2026-06-30 |  | 0 | 0 | 0 | -5024853.2393 | -2512426.6197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 2844986.444 | 2026-06-30 |  | 307888.1412 | 324081.1625 | 341923.5133 | 358955.4631 | 373979.4621 | 23727.8023 | 35776.2513 | 47737.8102 | 59358.9889 | 70749.362 | 82172.7968 | 93672.6798 | 105277.6787 | 117007.7393 | 128877.2628 | 140896.9352 | 153074.8509 | 165417.2374 | 177928.9417 | 190613.7678 | 203474.7171 | 216514.1645 | 229125.7001 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -3814037.7179 | 2026-06-30 |  | 0 | 0 | 0 | 0 | -214228.1336 | -321342.2004 | -321342.2004 | -321342.2004 | -321342.2004 | -321342.2004 | -321342.2004 | -321342.2004 | -321342.2004 | -321342.2004 | -321342.2004 | -321342.2004 | -321342.2004 | -321342.2004 | -321342.2004 | -321342.2004 | -321342.2004 | -321342.2004 | -321342.2004 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 4567593.2331 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 366101.606 | 374317.4797 | 383221.2928 | 388338.183 | 391734.7403 | 395298.241 | 398984.3334 | 402763.4114 | 406614.6167 | 410522.6604 | 414475.9928 | 418465.6784 | 422484.6709 | 426527.3258 | 430589.062 | 434666.1208 | 438755.3891 | 442591.6822 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | -214228.1336 | 44759.4055 | 52975.2793 | 61879.0924 | 66995.9826 | 70392.5399 | 73956.0406 | 77642.1329 | 81421.211 | 85272.4163 | 89180.46 | 93133.7923 | 97123.4779 | 101142.4705 | 105185.1254 | 109246.8616 | 113323.9204 | 117413.1887 | 121249.4818 | 0 | 0
Option 2 | NPV | Option 2NPV | 753555.5152 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -3814037.7179 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 4567593.2331 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 7281107.1793 | 2026-06-30 |  | 290826.9921 | 306355.601 | 323523.1227 | 339869.8952 | 335967.5862 | 350330.3473 | 368870.3982 | 387970.7305 | 403146.5115 | 416461.9584 | 429957.5058 | 443632.2844 | 457485.4492 | 471516.1784 | 485723.6725 | 500107.1537 | 514665.8646 | 529399.0678 | 544306.0451 | 559386.0966 | 574638.5404 | 590062.7115 | 605657.9618 | 621423.6591 | 637359.1867
Option 3 | Capital expenditure | Option 3Capital expenditure | -493332.6482 | 2026-06-30 |  | 0 | 0 | 0 | -556456.3232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 7096545.273 | 2026-06-30 |  | 307888.1412 | 324081.1625 | 341923.5133 | 358955.4631 | 354847.6416 | 369883.9369 | 389107.2135 | 408900.4043 | 424778.6197 | 438806.021 | 453022.9888 | 467428.6007 | 482021.9601 | 496802.1948 | 511768.4559 | 526919.9174 | 542255.7748 | 557775.2446 | 573477.5634 | 589361.9872 | 605427.7908 | 621674.2671 | 637269.5174 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -493332.6482 | 2026-06-30 |  | 0 | 0 | 0 | 0 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 316034.404 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 19131.8205 | 19945.4713 | 20986.5174 | 22058.6987 | 22918.5523 | 23678.0813 | 24448.049 | 25228.4125 | 26019.1299 | 26820.1612 | 27631.4673 | 28453.0106 | 29284.7545 | 30126.6637 | 30978.7041 | 31840.8426 | 32713.0471 | 33595.2865 | 34447.8649 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | -47777.249 | -46963.5981 | -45922.552 | -44850.3708 | -43990.5172 | -43230.9882 | -42461.0204 | -41680.657 | -40889.9395 | -40088.9082 | 27631.4673 | 28453.0106 | 29284.7545 | 30126.6637 | 30978.7041 | 31840.8426 | 32713.0471 | 33595.2865 | 34447.8649 | 0 | 0
Option 3 | NPV | Option 3NPV | -177298.2442 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -493332.6482 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 316034.404 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 0 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | 0 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 0 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0.32134 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 0.30789 | 0.32408 | 0.34192 | 0.35896 | 0.37398 | 0.38983 | 0.41009 | 0.43096 | 0.4477 | 0.46248 | 0.47747 | 0.49266 | 0.50804 | 0.52362 | 0.5394 | 0.55537 | 0.57154 | 0.5879 | 0.60446 | 0.6212 | 0.63814 | 0.65527 | 0.67172 | 0.68835 | 0.70515
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 0 |  |  | Energy at risk energy at risk (weighted) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Energy at risk value | 0.60385 |  |  | Option 1 (base case) risk cost | 0.26132 | 0.27527 | 0.2907 | 0.30539 | 0.31826 | 0.33187 | 0.34944 | 0.36753 | 0.38191 | 0.39453 | 0.40731 | 0.42027 | 0.4334 | 0.44669 | 0.46015 | 0.47378 | 0.48758 | 0.50154 | 0.51567 | 0.52996 | 0.54441 | 0.55903 | 0.57381 | 0.58875 | 0.60385

## Sensitivity_calcs
Powercor
SHN transformer replacement
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
[7 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 105185.1254 | 109246.8616 | 113323.9204 | 117413.1887 | 121249.4818 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 753555.5152 |  | 0 | 0 | 0 | 0 | 0 | -214228.1336 | 44759.4055 | 52975.2793 | 61879.0924 | 66995.9826 | 70392.5399 | 73956.0406 | 77642.1329 | 81421.211 | 85272.4163 | 89180.46 | 93133.7923 | 97123.4779 | 101142.4705 | 105185.1254 | 109246.8616 | 113323.9204 | 117413.1887 | 121249.4818 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 372151.7434 |  | 0 | 0 | 0 | 0 | 0 | -235650.947 | 12625.1855 | 20841.0593 | 29744.8723 | 34861.7625 | 38258.3198 | 41821.8205 | 45507.9129 | 49286.991 | 53138.1962 | 57046.24 | 60999.5723 | 64989.2579 | 69008.2504 | 73050.9053 | 77112.6416 | 81189.7003 | 85278.9686 | 89115.2617 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 1134959.287 |  | 0 | 0 | 0 | 0 | 0 | -192805.3203 | 76893.6256 | 85109.4993 | 94013.3124 | 99130.2026 | 102526.7599 | 106090.2606 | 109776.353 | 113555.431 | 117406.6363 | 121314.6801 | 125268.0124 | 129257.698 | 133276.6905 | 137319.3454 | 141381.0816 | 145458.1404 | 149547.4087 | 153383.7018 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 1210314.8385 |  | 0 | 0 | 0 | 0 | 0 | -214228.1336 | 81369.5661 | 90407.0273 | 100201.2217 | 105829.8009 | 109566.0139 | 113485.8647 | 117540.5663 | 121697.5521 | 125933.8779 | 130232.7261 | 134581.3916 | 138970.0458 | 143390.9375 | 147837.8579 | 152305.7678 | 156790.5324 | 161288.7276 | 165508.65 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 296796.1919 |  | 0 | 0 | 0 | 0 | 0 | -214228.1336 | 8149.2449 | 15543.5313 | 23556.9631 | 28162.1643 | 31219.0658 | 34426.2165 | 37743.6996 | 41144.8699 | 44610.9546 | 48128.194 | 51686.1931 | 55276.9101 | 58894.0034 | 62532.3928 | 66187.9554 | 69857.3083 | 73537.6498 | 76990.3135 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | -84607.5799 |  | 0 | 0 | 0 | 0 | 0 | -235650.947 | -23984.9751 | -16590.6887 | -8577.257 | -3972.0558 | -915.1542 | 2291.9964 | 5609.4795 | 9010.6498 | 12476.7346 | 15993.9739 | 19551.973 | 23142.6901 | 26759.7833 | 30398.1727 | 34053.7354 | 37723.0882 | 41403.4297 | 44856.0935 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 753555.5152 |  | 0 | 0 | 0 | 0 | 0 | -214228.1336 | 44759.4055 | 52975.2793 | 61879.0924 | 66995.9826 | 70392.5399 | 73956.0406 | 77642.1329 | 81421.211 | 85272.4163 | 89180.46 | 93133.7923 | 97123.4779 | 101142.4705 | 105185.1254 | 109246.8616 | 113323.9204 | 117413.1887 | 121249.4818 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 753555.5152 |  | 0 | 0 | 0 | 0 | 0 | -214228.1336 | 44759.4055 | 52975.2793 | 61879.0924 | 66995.9826 | 70392.5399 | 73956.0406 | 77642.1329 | 81421.211 | 85272.4163 | 89180.46 | 93133.7923 | 97123.4779 | 101142.4705 | 105185.1254 | 109246.8616 | 113323.9204 | 117413.1887 | 121249.4818 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 753555.5152 |  | 0 | 0 | 0 | 0 | 0 | -214228.1336 | 44759.4055 | 52975.2793 | 61879.0924 | 66995.9826 | 70392.5399 | 73956.0406 | 77642.1329 | 81421.211 | 85272.4163 | 89180.46 | 93133.7923 | 97123.4779 | 101142.4705 | 105185.1254 | 109246.8616 | 113323.9204 | 117413.1887 | 121249.4818 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 0 | -47777.249 | -46963.5981 | -45922.552 | -44850.3708 | -43990.5172 | -43230.9882 | -42461.0204 | -41680.657 | -40889.9395 | -40088.9082 | 27631.4673 | 28453.0106 | 29284.7545 | 30126.6637 | 30978.7041 | 31840.8426 | 32713.0471 | 33595.2865 | 34447.8649 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | -177298.2442 |  | 0 | 0 | 0 | 0 | 0 | -47777.249 | -46963.5981 | -45922.552 | -44850.3708 | -43990.5172 | -43230.9882 | -42461.0204 | -41680.657 | -40889.9395 | -40088.9082 | 27631.4673 | 28453.0106 | 29284.7545 | 30126.6637 | 30978.7041 | 31840.8426 | 32713.0471 | 33595.2865 | 34447.8649 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | -226631.509 |  | 0 | 0 | 0 | 0 | 0 | -54468.1559 | -53654.5051 | -52613.459 | -51541.2777 | -50681.4241 | -49921.8951 | -49151.9274 | -48371.564 | -47580.8465 | -46779.8152 | 27631.4673 | 28453.0106 | 29284.7545 | 30126.6637 | 30978.7041 | 31840.8426 | 32713.0471 | 33595.2865 | 34447.8649 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | -127964.9794 |  | 0 | 0 | 0 | 0 | 0 | -41086.342 | -40272.6912 | -39231.6451 | -38159.4639 | -37299.6102 | -36540.0812 | -35770.1135 | -34989.7501 | -34199.0326 | -33398.0013 | 27631.4673 | 28453.0106 | 29284.7545 | 30126.6637 | 30978.7041 | 31840.8426 | 32713.0471 | 33595.2865 | 34447.8649 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | -145694.8038 |  | 0 | 0 | 0 | 0 | 0 | -45864.0669 | -44969.051 | -43823.9003 | -42644.5009 | -41698.6619 | -40863.1801 | -40016.2155 | -39157.8158 | -38288.0265 | -37406.8921 | 30394.6141 | 31298.3117 | 32213.2299 | 33139.3301 | 34076.5745 | 35024.9268 | 35984.3518 | 36954.8152 | 37892.6514 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | -208901.6846 |  | 0 | 0 | 0 | 0 | 0 | -49690.431 | -48958.1453 | -48021.2038 | -47056.2407 | -46282.3724 | -45598.7963 | -44905.8253 | -44203.4983 | -43491.8525 | -42770.9244 | 24868.3206 | 25607.7095 | 26356.279 | 27113.9974 | 27880.8337 | 28656.7583 | 29441.7423 | 30235.7579 | 31003.0785 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | -258234.9494 |  | 0 | 0 | 0 | 0 | 0 | -56381.338 | -55649.0522 | -54712.1107 | -53747.1476 | -52973.2794 | -52289.7033 | -51596.7323 | -50894.4052 | -50182.7595 | -49461.8313 | 24868.3206 | 25607.7095 | 26356.279 | 27113.9974 | 27880.8337 | 28656.7583 | 29441.7423 | 30235.7579 | 31003.0785 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -177298.2442 |  | 0 | 0 | 0 | 0 | 0 | -47777.249 | -46963.5981 | -45922.552 | -44850.3708 | -43990.5172 | -43230.9882 | -42461.0204 | -41680.657 | -40889.9395 | -40088.9082 | 27631.4673 | 28453.0106 | 29284.7545 | 30126.6637 | 30978.7041 | 31840.8426 | 32713.0471 | 33595.2865 | 34447.8649 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -177298.2442 |  | 0 | 0 | 0 | 0 | 0 | -47777.249 | -46963.5981 | -45922.552 | -44850.3708 | -43990.5172 | -43230.9882 | -42461.0204 | -41680.657 | -40889.9395 | -40088.9082 | 27631.4673 | 28453.0106 | 29284.7545 | 30126.6637 | 30978.7041 | 31840.8426 | 32713.0471 | 33595.2865 | 34447.8649 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -177298.2442 |  | 0 | 0 | 0 | 0 | 0 | -47777.249 | -46963.5981 | -45922.552 | -44850.3708 | -43990.5172 | -43230.9882 | -42461.0204 | -41680.657 | -40889.9395 | -40088.9082 | 27631.4673 | 28453.0106 | 29284.7545 | 30126.6637 | 30978.7041 | 31840.8426 | 32713.0471 | 33595.2865 | 34447.8649 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 1 | 1 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 0.75356 | -0.1773 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens1 | Capex 10% higher | 0 | 0.37215 | -0.22663 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens2 | Capex 10% lower | 0 | 1.135 | -0.12796 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens3 | Total benefits 10% higher | 0 | 1.2103 | -0.14569 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens4 | Total benefits 10% lower | 0 | 0.2968 | -0.2089 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | -0.084608 | -0.25823 |  |  |  | 2026-27: #NAME?; 2028-29: Option 1 (base case)
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Workings_costs
Powercor
SHN transformer replacement
WORKINGS - COSTS
Option 1 - continue existing maintenance with no proactive replacement cost
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
Relay annual maintenance cost ($)
|  | Total opex cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - Replace transformer #2 completed in 2030-2031
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | Tx capex profile ($) | 2029-30: 4515047.3; 2030-31: 2257523.65
|  | Total capex ($) | 0 | 0 | 0 | 4515047.3 | 2257523.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
SWBD online monitoring annual cost ($)
|  | Total opex cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Refurbish transformer #2 completed in 2029-2030
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | Tx capex profile ($) | 2029-30: 500000
|  | Total capex ($) | 0 | 0 | 0 | 500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
SWBD online monitoring annual cost ($)
|  | Total opex cost ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Workings_risks
Powercor
SHN transformer replacement
WORKINGS - RISKS
Option 1 - continue existing maintenance with no proactive replacement cost
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Transformer risks
|  | Energy at Risk ($, Weighted) | 261320.5924 | 275273.7171 | 290699.4756 | 305387.7555 | 318262.5666 | 331870.3465 | 349435.5104 | 367531.6743 | 381910.2637 | 394526.7084 | 407313.9549 | 420271.1857 | 433397.6064 | 446692.4445 | 460154.9488 | 473784.3885 | 487580.0524 | 501541.248 | 515667.3013 | 529957.5555 | 544411.371 | 559028.1242 | 573807.2076 | 588748.0286 | 603850.0095
|  | Safety risk | 303.6386 | 315.4632 | 327.4732 | 339.6673 | 352.0445 | 364.6034 | 377.3431 | 390.2624 | 403.3602 | 416.6356 | 430.0875 | 443.7149 | 457.5168 | 471.4924 | 485.6406 | 499.9606 | 514.4516 | 529.1126 | 543.9429 | 558.9415 | 574.1077 | 589.4407 | 589.4407 | 589.4407 | 589.4407
|  | Unplanned replacement risk | 13904.2221 | 14445.6943 | 14995.6557 | 15554.0505 | 16120.8245 | 16695.9249 | 17279.3003 | 17870.9008 | 18470.6777 | 19078.5833 | 19694.5715 | 20318.597 | 20950.6157 | 21590.5845 | 22238.4613 | 22894.2049 | 23557.7751 | 24229.1325 | 24908.2386 | 25595.0557 | 26289.5469 | 26991.676 | 26991.676 | 26991.676 | 26991.676
|  | Unplanned fault risk | 1122.3175 | 1166.0239 | 1210.4155 | 1255.4879 | 1301.2366 | 1347.6574 | 1394.7462 | 1442.4988 | 1490.9115 | 1539.9803 | 1589.7014 | 1640.0714 | 1691.0865 | 1742.7433 | 1795.0385 | 1847.9686 | 1901.5305 | 1955.721 | 2010.5369 | 2065.9752 | 2122.033 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073
|  | Enviromental risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total transformer risks | 276650.7706 | 291200.8984 | 307233.02 | 322536.9612 | 336036.6722 | 350278.5322 | 368486.8999 | 387235.3363 | 402275.213 | 415561.9076 | 429028.3153 | 442673.569 | 456496.8254 | 470497.2647 | 484674.0892 | 499026.5227 | 513553.8096 | 528255.2141 | 543130.0196 | 558177.5279 | 573397.0586 | 588787.9482 | 603567.0315 | 618507.8525 | 633609.8334
Option 2 - Replace transformer #2 completed in 2030-2031
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Transformer risks
|  | Energy at Risk ($, Weighted) | 261320.5924 | 275273.7171 | 290699.4756 | 305387.7555 | 318262.5666 | 12104.0395 | 22580.7784 | 32962.8955 | 43024.0746 | 52863.6902 | 62719.4986 | 72630.995 | 82624.3523 | 92717.8391 | 102924.6923 | 113254.7731 | 123715.5845 | 134312.9282 | 145051.3461 | 155934.4264 | 166965.0229 | 178145.414 | 189477.4226 | 200962.5058 | 212601.8244
|  | Safety risk | 303.6386 | 315.4632 | 327.4732 | 339.6673 | 352.0445 | 182.5457 | 189.4644 | 196.7109 | 204.2562 | 212.0823 | 220.1761 | 228.5274 | 237.1281 | 245.9713 | 255.0512 | 264.3625 | 273.9008 | 283.6619 | 293.6422 | 303.8383 | 314.2471 | 324.8657 | 324.8657 | 324.8657 | 324.8657
|  | Unplanned replacement risk | 13904.2221 | 14445.6943 | 14995.6557 | 15554.0505 | 16120.8245 | 8359.1375 | 8675.9578 | 9007.7862 | 9353.3027 | 9711.6754 | 10082.3055 | 10464.73 | 10858.5737 | 11263.5224 | 11679.3069 | 12105.6918 | 12542.4688 | 12989.451 | 13446.4692 | 13913.3688 | 14390.0079 | 14876.255 | 14876.255 | 14876.255 | 14876.255
|  | Unplanned fault risk | 1122.3175 | 1166.0239 | 1210.4155 | 1255.4879 | 1301.2366 | 674.7307 | 700.3038 | 727.0882 | 754.9775 | 783.9046 | 813.821 | 844.6894 | 876.4796 | 909.1662 | 942.7273 | 977.1442 | 1012.3998 | 1048.4792 | 1085.3687 | 1123.0558 | 1161.529 | 1200.7778 | 1200.7778 | 1200.7778 | 1200.7778
|  | Enviromental risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total transformer risks | 276650.7706 | 291200.8984 | 307233.02 | 322536.9612 | 336036.6722 | 21320.4535 | 32146.5044 | 42894.4808 | 53336.611 | 63571.3524 | 73835.8011 | 84168.9418 | 94596.5337 | 105136.499 | 115801.7777 | 126601.9716 | 137544.3539 | 148634.5204 | 159876.8262 | 171274.6893 | 182830.8068 | 194547.3125 | 205879.3212 | 217364.4043 | 229003.723
Option 3 - Refurbish transformer #2 completed in 2029-2030
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Transformer risks
|  | Energy at Risk ($, Weighted) | 261320.5924 | 275273.7171 | 290699.4756 | 305387.7555 | 301881.3627 | 314786.9228 | 331445.958 | 348608.4301 | 362244.5237 | 374209.0269 | 386335.3581 | 398622.7363 | 411070.4022 | 423677.6174 | 436443.6635 | 449367.8415 | 462449.471 | 475687.8894 | 489082.4512 | 502632.5277 | 516337.5061 | 530196.7889 | 544209.7938 | 558375.9526 | 572694.7112
|  | Safety risk | 303.6386 | 315.4632 | 327.4732 | 339.6673 | 348.524 | 360.9574 | 373.5697 | 386.3598 | 399.3266 | 412.4692 | 425.7866 | 439.2777 | 452.9416 | 466.7774 | 480.7842 | 494.961 | 509.3071 | 523.8215 | 538.5034 | 553.3521 | 568.3666 | 583.5463 | 583.5463 | 583.5463 | 583.5463
|  | Unplanned replacement risk | 13904.2221 | 14445.6943 | 14995.6557 | 15554.0505 | 15314.7832 | 15861.1286 | 16415.3353 | 16977.3558 | 17547.1438 | 18124.6542 | 18709.843 | 19302.6672 | 19903.0849 | 20511.0553 | 21126.5382 | 21749.4946 | 22379.8863 | 23017.6759 | 23662.8267 | 24315.3029 | 24975.0695 | 25642.0922 | 25642.0922 | 25642.0922 | 25642.0922
|  | Unplanned fault risk | 1122.3175 | 1166.0239 | 1210.4155 | 1255.4879 | 1301.2366 | 1347.6574 | 1394.7462 | 1442.4988 | 1490.9115 | 1539.9803 | 1589.7014 | 1640.0714 | 1691.0865 | 1742.7433 | 1795.0385 | 1847.9686 | 1901.5305 | 1955.721 | 2010.5369 | 2065.9752 | 2122.033 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073
|  | Enviromental risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total transformer risks | 276650.7706 | 291200.8984 | 307233.02 | 322536.9612 | 318845.9065 | 332356.6662 | 349629.6091 | 367414.6445 | 381681.9056 | 394286.1306 | 407060.6891 | 420004.7526 | 433117.5153 | 446398.1934 | 459846.0244 | 473460.2658 | 487240.1949 | 501185.1077 | 515294.3182 | 529567.1579 | 544002.9752 | 558601.1347 | 572614.1395 | 586780.2983 | 601099.0569

## Tx risks
Powercor
SHN transformer replacement
Input Data - Station Configuration |  | Constants |  |  | POF METHOD | WEIBULL | Modifier (x) | Comment
Substation: | SHN | Major Failure CoC |  |  | PoF (#1) | 0.08226% | 100%
Asset Type | Transformer | Minor Failure CoC |  |  | PoF (#2) | 0.08226% | 100%
VCR | 47.127 | Major Failure CoC - used | 8127085.14 |  | PoF (#3) | 100% | 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 164000 |  | PoF (#4) | 0% | 100%
Scenario #1: SHN - Transformer | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 100% | 0 | Energy | 5693.444 | 5353.1857 | 5644.6614 | 5963.0635 | 6265.2871 | 6529.7855 | 6815.6738 | 7172.4241 | 7537.1652 | 7831.3419 | 8090.051 | 8352.2626 | 8617.9599 | 8887.1265 | 9159.7466 | 9435.8048 | 9715.2862 | 9998.1761 | 10284.4604 | 10574.1251 | 10867.157 | 11163.5428 | 11463.2697 | 11766.3253 | 12072.6975 | 12382.3744 | 12695.3444 | 13011.5963 | 13011.5963 | 13011.5963 | 13011.5963 | 13011.5963
Online Monitoring | 0% | 0 | Energy | 6325.0085 | 5992.6641 | 6299.4708 | 6647.6098 | 6981.336 | 7274.8195 | 7570.2368 | 7980.2186 | 8409.1134 | 8739.7111 | 9028.4284 | 9321.0543 | 9617.5702 | 9917.9578 | 10222.1996 | 10530.2782 | 10842.1771 | 11157.8798 | 11477.3706 | 11800.634 | 12127.6551 | 12458.4191 | 12792.9118 | 13131.1193 | 13473.0281 | 13818.6248 | 14167.8967 | 14520.8311 | 14520.8311 | 14520.8311 | 14520.8311 | 14520.8311
Physical Separation | 0% | 300000 | Energy | 5693.444 | 5353.1857 | 5644.6614 | 5963.0635 | 6265.2871 | 6529.7855 | 6815.6738 | 7172.4241 | 7537.1652 | 7831.3419 | 8090.051 | 8352.2626 | 8617.9599 | 8887.1265 | 9159.7466 | 9435.8048 | 9715.2862 | 9998.1761 | 10284.4604 | 10574.1251 | 10867.157 | 11163.5428 | 11463.2697 | 11766.3253 | 12072.6975 | 12382.3744 | 12695.3444 | 13011.5963 | 13011.5963 | 13011.5963 | 13011.5963 | 13011.5963
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.1645% | 0.1711% | 0.1777% | 0.1845% | 0.1914% | 0.1984% | 0.2054% | 0.2126% | 0.2199% | 0.2273% | 0.2348% | 0.2423% | 0.25% | 0.2578% | 0.2657% | 0.2736% | 0.2817% | 0.2899% | 0.2981% | 0.3065% | 0.3149% | 0.3235% | 0.3321% | 0.3321% | 0.3321% | 0.3321% | 0.3321% | 0.3321% | 0.3321% | 0.3321% | 0.3321% | 0.3321%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 0.6581% | 0.6843% | 0.711% | 0.7381% | 0.7655% | 0.7934% | 0.8217% | 0.8505% | 0.8796% | 0.9091% | 0.939% | 0.9693% | 1% | 1.031% | 1.063% | 1.095% | 1.127% | 1.159% | 1.193% | 1.226% | 1.26% | 1.294% | 1.328% | 1.328% | 1.328% | 1.328% | 1.328% | 1.328% | 1.328% | 1.328% | 1.328% | 1.328%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 277244.0583 | 261320.5924 | 275273.7171 | 290699.4756 | 305387.7555 | 318262.5666 | 331870.3465 | 349435.5104 | 367531.6743 | 381910.2637 | 394526.7084 | 407313.9549 | 420271.1857 | 433397.6064 | 446692.4445 | 460154.9488 | 473784.3885 | 487580.0524 | 501541.248 | 515667.3013 | 529957.5555 | 544411.371 | 559028.1242 | 573807.2076 | 588748.0286 | 603850.0095 | 619112.5867 | 634535.2105 | 634535.2105 | 634535.2105 | 634535.2105 | 634535.2105
Replace 1 Asset | 0% | 6772570.95 | Safety Risk | 292.0006 | 303.6386 | 315.4632 | 327.4732 | 339.6673 | 352.0445 | 364.6034 | 377.3431 | 390.2624 | 403.3602 | 416.6356 | 430.0875 | 443.7149 | 457.5168 | 471.4924 | 485.6406 | 499.9606 | 514.4516 | 529.1126 | 543.9429 | 558.9415 | 574.1077 | 589.4407 | 589.4407 | 589.4407 | 589.4407 | 589.4407 | 589.4407 | 589.4407 | 589.4407 | 589.4407 | 589.4407
Replace 2 Assets | 0% | 0 | Unplanned Replacement Risk | 13371.2965 | 13904.2221 | 14445.6943 | 14995.6557 | 15554.0505 | 16120.8245 | 16695.9249 | 17279.3003 | 17870.9008 | 18470.6777 | 19078.5833 | 19694.5715 | 20318.597 | 20950.6157 | 21590.5845 | 22238.4613 | 22894.2049 | 23557.7751 | 24229.1325 | 24908.2386 | 25595.0557 | 26289.5469 | 26991.676 | 26991.676 | 26991.676 | 26991.676 | 26991.676 | 26991.676 | 26991.676 | 26991.676 | 26991.676 | 26991.676
Replace 3 Assets | 0% | 0 | Unplanned Fault Risk | 1079.3009 | 1122.3175 | 1166.0239 | 1210.4155 | 1255.4879 | 1301.2366 | 1347.6574 | 1394.7462 | 1442.4988 | 1490.9115 | 1539.9803 | 1589.7014 | 1640.0714 | 1691.0865 | 1742.7433 | 1795.0385 | 1847.9686 | 1901.5305 | 1955.721 | 2010.5369 | 2065.9752 | 2122.033 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Total Life Cycle Cost | 291986.6564 | 276650.7706 | 291200.8984 | 307233.02 | 322536.9612 | 336036.6722 | 350278.5322 | 368486.8999 | 387235.3363 | 402275.213 | 415561.9076 | 429028.3153 | 442673.569 | 456496.8254 | 470497.2647 | 484674.0892 | 499026.5227 | 513553.8096 | 528255.2141 | 543130.0196 | 558177.5279 | 573397.0586 | 588787.9482 | 603567.0315 | 618507.8525 | 633609.8334 | 648872.4106 | 664295.0344 | 664295.0344 | 664295.0344 | 664295.0344 | 664295.0344
Input Data - Station Configuration |  | Constants |  | PoF (#4) 2026: POF METHOD; 0% 2027: WEIBULL; 100% 2028: Modifier (x); 100% 2029: Comment
Substation: | SHN | Major Failure CoC |  | PoF (#4) 2026: PoF (#1); 0% 2027: 0.08226%; 100% 2028: 100%
Asset Type | Transformer | Minor Failure CoC |  | PoF (#4) 2026: PoF (#2); 0% 2027: 0.08226%; 100% 2028: 100%
VCR | 47.127 | Major Failure CoC - used | 8127085.14 | PoF (#4) 2026: PoF (#3); 0% 2027: 100%; 100% 2028: 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 164000 | PoF (#4) 2026: PoF (#4); 0% 2027: 0%; 100% 2028: 100%
Scenario #2: SHN - Transformer | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 100% | 0 | Energy | 5693.444 | 5353.1857 | 5644.6614 | 5963.0635 | 6265.2871 | 6529.7855 | 248.5826 | 463.4873 | 675.9874 | 882.2393 | 1084.0076 | 1286.108 | 1489.3503 | 1694.2712 | 1901.2453 | 2110.5441 | 2322.3698 | 2536.8761 | 2754.1822 | 2974.3811 | 3197.5464 | 3423.7367 | 3652.9985 | 3885.3695 | 4120.8793 | 4359.5518 | 4601.4058 | 4846.4562 | 4846.4562 | 4846.4562 | 4846.4562 | 4846.4562
Online Monitoring | 0% | 0 | Energy | 6325.0085 | 5992.6641 | 6299.4708 | 6647.6098 | 6981.336 | 7274.8195 | 276.1031 | 515.6876 | 754.19 | 984.5716 | 1209.7433 | 1435.2856 | 1662.1023 | 1890.7923 | 2121.7736 | 2355.3493 | 2591.745 | 2831.1323 | 3073.644 | 3319.3841 | 3568.4347 | 3820.8611 | 4076.7154 | 4336.0394 | 4598.8663 | 4865.2228 | 5135.1299 | 5408.6041 | 5408.6041 | 5408.6041 | 5408.6041 | 5408.6041
Physical Separation | 0% | 300000 | Energy | 5693.444 | 5353.1857 | 5644.6614 | 5963.0635 | 6265.2871 | 6529.7855 | 248.5826 | 463.4873 | 675.9874 | 882.2393 | 1084.0076 | 1286.108 | 1489.3503 | 1694.2712 | 1901.2453 | 2110.5441 | 2322.3698 | 2536.8761 | 2754.1822 | 2974.3811 | 3197.5464 | 3423.7367 | 3652.9985 | 3885.3695 | 4120.8793 | 4359.5518 | 4601.4058 | 4846.4562 | 4846.4562 | 4846.4562 | 4846.4562 | 4846.4562
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.1645% | 0.1711% | 0.1777% | 0.1845% | 0.1914% | 0.1984% | 0.1029% | 0.1068% | 0.1108% | 0.1151% | 0.1195% | 0.1241% | 0.1288% | 0.1336% | 0.1386% | 0.1437% | 0.149% | 0.1543% | 0.1598% | 0.1655% | 0.1712% | 0.1771% | 0.183% | 0.183% | 0.183% | 0.183% | 0.183% | 0.183% | 0.183% | 0.183% | 0.183% | 0.183%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 0.6581% | 0.6843% | 0.711% | 0.7381% | 0.7655% | 0.7934% | 0.4114% | 0.427% | 0.4433% | 0.4604% | 0.478% | 0.4962% | 0.5151% | 0.5344% | 0.5544% | 0.5748% | 0.5958% | 0.6173% | 0.6393% | 0.6618% | 0.6848% | 0.7082% | 0.7322% | 0.7322% | 0.7322% | 0.7322% | 0.7322% | 0.7322% | 0.7322% | 0.7322% | 0.7322% | 0.7322%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 277244.0583 | 261320.5924 | 275273.7171 | 290699.4756 | 305387.7555 | 318262.5666 | 12104.0395 | 22580.7784 | 32962.8955 | 43024.0746 | 52863.6902 | 62719.4986 | 72630.995 | 82624.3523 | 92717.8391 | 102924.6923 | 113254.7731 | 123715.5845 | 134312.9282 | 145051.3461 | 155934.4264 | 166965.0229 | 178145.414 | 189477.4226 | 200962.5058 | 212601.8244 | 224396.2978 | 236346.6459 | 236346.6459 | 236346.6459 | 236346.6459 | 236346.6459
Replace 1 Asset | 100% | 6772570.95 | Safety Risk | 292.0006 | 303.6386 | 315.4632 | 327.4732 | 339.6673 | 352.0445 | 182.5457 | 189.4644 | 196.7109 | 204.2562 | 212.0823 | 220.1761 | 228.5274 | 237.1281 | 245.9713 | 255.0512 | 264.3625 | 273.9008 | 283.6619 | 293.6422 | 303.8383 | 314.2471 | 324.8657 | 324.8657 | 324.8657 | 324.8657 | 324.8657 | 324.8657 | 324.8657 | 324.8657 | 324.8657 | 324.8657
Replace 2 Assets | 0% | 0 | Unplanned Replacement Risk | 13371.2965 | 13904.2221 | 14445.6943 | 14995.6557 | 15554.0505 | 16120.8245 | 8359.1375 | 8675.9578 | 9007.7862 | 9353.3027 | 9711.6754 | 10082.3055 | 10464.73 | 10858.5737 | 11263.5224 | 11679.3069 | 12105.6918 | 12542.4688 | 12989.451 | 13446.4692 | 13913.3688 | 14390.0079 | 14876.255 | 14876.255 | 14876.255 | 14876.255 | 14876.255 | 14876.255 | 14876.255 | 14876.255 | 14876.255 | 14876.255
Replace 3 Assets | 0% | 0 | Unplanned Fault Risk | 1079.3009 | 1122.3175 | 1166.0239 | 1210.4155 | 1255.4879 | 1301.2366 | 674.7307 | 700.3038 | 727.0882 | 754.9775 | 783.9046 | 813.821 | 844.6894 | 876.4796 | 909.1662 | 942.7273 | 977.1442 | 1012.3998 | 1048.4792 | 1085.3687 | 1123.0558 | 1161.529 | 1200.7778 | 1200.7778 | 1200.7778 | 1200.7778 | 1200.7778 | 1200.7778 | 1200.7778 | 1200.7778 | 1200.7778 | 1200.7778
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 0 | 0 | 0 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229 | 288739.8229
|  |  | Total Life Cycle Cost | 291986.6564 | 276650.7706 | 291200.8984 | 307233.02 | 322536.9612 | 336036.6722 | 310060.2764 | 320886.3273 | 331634.3037 | 342076.4339 | 352311.1753 | 362575.624 | 372908.7648 | 383336.3566 | 393876.3219 | 404541.6006 | 415341.7945 | 426284.1768 | 437374.3433 | 448616.6491 | 460014.5122 | 471570.6297 | 483287.1354 | 494619.1441 | 506104.2272 | 517743.5459 | 529538.0192 | 541488.3673 | 541488.3673 | 541488.3673 | 541488.3673 | 541488.3673
Input Data - Station Configuration |  | Constants |  | PoF (#4) 2026: POF METHOD; 0% 2027: WEIBULL; 100% 2028: Modifier (x); 100% 2029: Comment
Substation: | SHN | Major Failure CoC |  | PoF (#4) 2026: PoF (#1); 0% 2027: 0.08226%; 100% 2028: 100%
Asset Type | Transformer | Minor Failure CoC |  | PoF (#4) 2026: PoF (#2); 0% 2027: 0.07404%; 100% 2028: 90%
VCR | 47.127 | Major Failure CoC - used | 8127085.14 | PoF (#4) 2026: PoF (#3); 0% 2027: 100%; 100% 2028: 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 164000 | PoF (#4) 2026: PoF (#4); 0% 2027: 0%; 100% 2028: 100%
Scenario #3: SHN - Transformer | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 100% | 0 | Energy | 5400.5475 | 5077.7664 | 5354.2167 | 5656.2042 | 5942.8421 | 6193.6927 | 6464.8288 | 6803.1751 | 7149.0963 | 7428.0819 | 7673.4225 | 7922.0816 | 8174.043 | 8429.2913 | 8687.8112 | 8949.5881 | 9214.6075 | 9482.8557 | 9754.3188 | 10028.9839 | 10306.8378 | 10587.8682 | 10872.0626 | 11159.4093 | 11449.8965 | 11743.5128 | 12040.2472 | 12340.0889 | 12340.0889 | 12340.0889 | 12340.0889 | 12340.0889
Online Monitoring | 0% | 0 | Energy | 5999.6215 | 5684.3439 | 5975.333 | 6305.5237 | 6622.0393 | 6900.3793 | 7180.5498 | 7569.383 | 7976.1501 | 8289.6764 | 8563.4745 | 8840.9759 | 9122.1627 | 9407.0176 | 9695.5236 | 9987.6644 | 10283.4239 | 10582.7865 | 10885.7372 | 11192.261 | 11502.3437 | 11815.9711 | 12133.1298 | 12453.8062 | 12777.9874 | 13105.6607 | 13436.8138 | 13771.4346 | 13771.4346 | 13771.4346 | 13771.4346 | 13771.4346
Physical Separation | 0% | 300000 | Energy | 5400.5475 | 5077.7664 | 5354.2167 | 5656.2042 | 5942.8421 | 6193.6927 | 6464.8288 | 6803.1751 | 7149.0963 | 7428.0819 | 7673.4225 | 7922.0816 | 8174.043 | 8429.2913 | 8687.8112 | 8949.5881 | 9214.6075 | 9482.8557 | 9754.3188 | 10028.9839 | 10306.8378 | 10587.8682 | 10872.0626 | 11159.4093 | 11449.8965 | 11743.5128 | 12040.2472 | 12340.0889 | 12340.0889 | 12340.0889 | 12340.0889 | 12340.0889
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.1563% | 0.1625% | 0.1689% | 0.1753% | 0.1818% | 0.1884% | 0.1952% | 0.202% | 0.2089% | 0.2159% | 0.223% | 0.2302% | 0.2375% | 0.2449% | 0.2524% | 0.26% | 0.2676% | 0.2754% | 0.2832% | 0.2912% | 0.2992% | 0.3073% | 0.3155% | 0.3155% | 0.3155% | 0.3155% | 0.3155% | 0.3155% | 0.3155% | 0.3155% | 0.3155% | 0.3155%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 0.6581% | 0.6843% | 0.711% | 0.7245% | 0.7655% | 0.7934% | 0.8217% | 0.8505% | 0.8796% | 0.9091% | 0.939% | 0.9693% | 1% | 1.031% | 1.063% | 1.095% | 1.127% | 1.159% | 1.193% | 1.226% | 1.26% | 1.294% | 1.328% | 1.328% | 1.328% | 1.328% | 1.328% | 1.328% | 1.328% | 1.328% | 1.328% | 1.328%
Bunded | 0 | 300000
Refurbish Assets | 1 | 500000 | Energy at Risk ($, Weighted) | 262981.3704 | 247875.752 | 261109.5733 | 275740.0796 | 289670.876 | 301881.3627 | 314786.9228 | 331445.958 | 348608.4301 | 362244.5237 | 374209.0269 | 386335.3581 | 398622.7363 | 411070.4022 | 423677.6174 | 436443.6635 | 449367.8415 | 462449.471 | 475687.8894 | 489082.4512 | 502632.5277 | 516337.5061 | 530196.7889 | 544209.7938 | 558375.9526 | 572694.7112 | 587165.529 | 601787.8782 | 601787.8782 | 601787.8782 | 601787.8782 | 601787.8782
Replace 1 Asset | 0% | 6772570.95 | Safety Risk | 289.0806 | 300.6022 | 312.3085 | 319.3944 | 336.2706 | 348.524 | 360.9574 | 373.5697 | 386.3598 | 399.3266 | 412.4692 | 425.7866 | 439.2777 | 452.9416 | 466.7774 | 480.7842 | 494.961 | 509.3071 | 523.8215 | 538.5034 | 553.3521 | 568.3666 | 583.5463 | 583.5463 | 583.5463 | 583.5463 | 583.5463 | 583.5463 | 583.5463 | 583.5463 | 583.5463 | 583.5463
Replace 2 Assets | 0% | 0 | Unplanned Replacement Risk | 12702.7317 | 13209.011 | 13723.4095 | 14245.8729 | 14776.3479 | 15314.7832 | 15861.1286 | 16415.3353 | 16977.3558 | 17547.1438 | 18124.6542 | 18709.843 | 19302.6672 | 19903.0849 | 20511.0553 | 21126.5382 | 21749.4946 | 22379.8863 | 23017.6759 | 23662.8267 | 24315.3029 | 24975.0695 | 25642.0922 | 25642.0922 | 25642.0922 | 25642.0922 | 25642.0922 | 25642.0922 | 25642.0922 | 25642.0922 | 25642.0922 | 25642.0922
Replace 3 Assets | 0% | 0 | Unplanned Fault Risk | 1079.3009 | 1122.3175 | 1166.0239 | 1188.2197 | 1255.4879 | 1301.2366 | 1347.6574 | 1394.7462 | 1442.4988 | 1490.9115 | 1539.9803 | 1589.7014 | 1640.0714 | 1691.0865 | 1742.7433 | 1795.0385 | 1847.9686 | 1901.5305 | 1955.721 | 2010.5369 | 2065.9752 | 2122.033 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073 | 2178.7073
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 0 | 0 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839
|  |  | Total Life Cycle Cost | 277052.4837 | 262507.6826 | 276311.3153 | 291493.5667 | 306038.9825 | 378966.5905 | 392477.3501 | 409750.293 | 427535.3284 | 441802.5895 | 454406.8145 | 467181.3731 | 480125.4365 | 493238.1992 | 506518.8773 | 519966.7083 | 533580.9498 | 547360.8789 | 561305.7917 | 575415.0021 | 589687.8419 | 604123.6592 | 618721.8186 | 632734.8235 | 646900.9823 | 661219.7409 | 675690.5586 | 690312.9078 | 690312.9078 | 690312.9078 | 690312.9078 | 690312.9078

## Misc_calcs
Powercor
SHN transformer replacement
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 4 | TRUE
| Option 3 | 4 | TRUE
| Option 4 | Not used | FALSE
| Option 5 | Not used | FALSE
| First year | 4
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
Powercor
SHN transformer replacement
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | TRUE | Not used |  | TRUE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
Powercor
| Reliability in worst-served areas | per MWh | 151432.8174
| Network resilience | per MWh | 24590
| Enabling solar exports | per MWh | 88.3577
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.35181
| Customer value of time - business | per minute customer time | 0.35181
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020