## Cover
Powercor
Regulatory proposal 2026-31
Relay replacement
| Model number: | 4.07
2025-01-31
15

## Summary
Powercor
Relay replacements
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Replace all ageing relays at zone substations |  | -18.4146 | 112.8335 | 94.4189
| Option 3 | Defer investment to 2032-33 |  | -13.202 | 104.5095 | 91.3076
| Option 4 | 0
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | Replace all ageing relays at zone substations |  | 94.4189
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 5.2233 | 4.3837 | 9.365 | 2.6999 | 2.7972 |  | 24.4692
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
Capex and risk ($M, 2026)
PREFERRED OPTION DATA
Select category for table:
Capital expenditure
|  | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Option 1 (base case) | No change to existing practices | 0 | 0 | 0 | 0 | 0 |  | 0
| Option 2 | Replace all ageing relays at zone substations | 5.2233 | 4.3837 | 9.365 | 2.6999 | 2.7972 |  | 24.4692
| Option 3 | Defer investment to 2032-33 | 0 | 0 | 0 | 0 | 0 |  | 0
| Option 4 | 0
| Option 5 | 0
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 94.4189 | 91.3076 |  |  |  | Option 2
| Capex 10% higher |  | 0 | 92.5775 | 89.9874 |  |  |  | Option 2
| Capex 10% lower |  | 0 | 96.2604 | 92.6278 |  |  |  | Option 2
| Total benefits 10% higher |  | 0 | 105.7023 | 101.7585 |  |  |  | Option 2
| Total benefits 10% lower |  | 0 | 83.1356 | 80.8566 |  |  |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  | 0 | 81.2941 | 79.5364 |  |  |  | Option 2
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
Powercor
Relay replacements
Project
|  | Business: | select > | Powercor
|  | Descripton: |  | Relay replacements
|  | Date of cost inputs: | select > | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Replace all ageing relays at zone substations
|  | Option 3 |  | Defer investment to 2032-33
Option 4
Option 5
|  | Compliance project |  | No
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 22 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | Network average |  | Network average | 43815.4862 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 151432.8174 | 2023-12-31 | per MWh
|  | Network resilience |  |  |  | 24590 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 88.3577 | 2023-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
Powercor
Relay replacements
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Relay replacement capex |  | 28 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety | (after DF) |  | 2023-12-31 |  | 33309.3002 | 38461.5729 | 44670.7987 | 52181.603 | 61275.53 | 72323.5019 | 85758.8579 | 102345.9582 | 122932.0639 | 148446.1175 | 180271.0669 | 220290.5974 | 270972.6038 | 333509.0777 | 410152.0636 | 506197.0843 | 615579.9261 | 726608.6804 | 828076.6658 | 912978.5325 | 960883.6424 | 992913.1681 | 1027463.7377 | 1067886.2805 | 1112792.7272
| Environment |  |  | 2023-12-31 |  | 3772.5283 | 4359.1759 | 5070.5201 | 5936.0199 | 6990.1612 | 8278.3689 | 9852.5884 | 11810.4203 | 14258.6992 | 17312.5468 | 21147.225 | 26003.6281 | 32198.8098 | 39872.3655 | 49303.7092 | 61342.2996 | 75386.0153 | 89934.7026 | 103144.4114 | 114133.5822 | 120058.6739 | 123699.5508 | 127588.6514 | 132179.418 | 137451.6592
| NP | (after DF) |  | 2023-12-31 |  | 589594.3624 | 679937.7921 | 787513.6029 | 916540.6623 | 1071030.1425 | 1256744.6667 | 1482959.2867 | 1758462.6863 | 2094721.9739 | 2507065.4055 | 3015200.7921 | 3644641.7336 | 4428405.8964 | 5406517.1899 | 6632352.0182 | 8127947.1542 | 9408805.3547 | 10299040.6803 | 11176077.0136 | 11963891.0141 | 12503631.4632 | 13086897.4386 | 13724115.9638 | 14416811.7948 | 15204525.0467
| Financial |  |  | 2023-12-31 |  | 453291.2424 | 520313.4711 | 598559.6937 | 690128.3359 | 797449.0311 | 923492.7206 | 1071858.2744 | 1247099.4879 | 1454577.2778 | 1700701.1889 | 1993529.6097 | 2343122.7953 | 2761896.042 | 3254079.0674 | 3827032.6338 | 4455693.4032 | 5090505.2705 | 5631435.6853 | 6185397.8295 | 6698775.4098 | 7141528.5849 | 7586409.882 | 8080194.2161 | 8639036.1706 | 9181819.8991
| 0 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 1079967.4334 | 1243072.012 | 1435814.6154 | 1664786.6211 | 1936744.8648 | 2260839.2582 | 2650429.0074 | 3119718.5527 | 3686490.0148 | 4373525.2588 | 5210148.6937 | 6234058.7544 | 7493473.352 | 9033977.7004 | 10918840.4248 | 13151179.9414 | 15190276.5666 | 16747019.7486 | 18292695.9202 | 19689778.5386 | 20726102.3643 | 21789920.0395 | 22959362.569 | 24255913.6639 | 25636589.3322
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| Relay replacement capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Relay replacement capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Relay replacement capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
Powercor
Relay replacements
OPTION 2 | Replace all ageing relays at zone substations
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Relay replacement capex |  | 28 | 2023-12-31 | 4693379 | 3938959 | 8414892 | 2425985 | 2513379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 4693379 | 3938959 | 8414892 | 2425985 | 2513379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety | (after DF) |  | 2023-12-31 | 33309.3002 | 30613.883 | 28476.0033 | 17920.3905 | 16945.0869 | 13174.3531 | 14808.2728 | 17079.9342 | 20240.3414 | 24465.2333 | 30184.6941 | 38072.8861 | 49054.1631 | 64429.8794 | 86174.7054 | 117004.9337 | 160803.4339 | 221645.4541 | 286306.3699 | 336358.7148 | 359586.2186 | 373492.5207 | 392380.7278 | 418220.216 | 452339.635
| Environment |  |  | 2023-12-31 | 3772.5283 | 3622.0119 | 3305.8949 | 2224.9773 | 2147.2113 | 1737.5603 | 1949.5441 | 2247.9484 | 2667.2804 | 3231.177 | 3998.7137 | 5062.747 | 6550.6735 | 8641.9224 | 11609.1889 | 15827.3882 | 21832.4813 | 30182.8875 | 39179.9869 | 46153.6673 | 49349.9131 | 51230.4652 | 53800.8665 | 57336.5375 | 62065.3945
| NP | (after DF) |  | 2023-12-31 | 589594.3624 | 515736.8697 | 477049.2183 | 191176.558 | 97708.8658 | 14367.8208 | 18823.4434 | 25050.7649 | 33811.2054 | 46150.8367 | 63613.5527 | 88506.2 | 124050.2401 | 174888.3085 | 247801.1372 | 352631.8027 | 503774.8906 | 722029.0887 | 775899.3026 | 792547.756 | 808570.5643 | 813986.1443 | 821209.1513 | 830936.6996 | 843545.2423
| Financial |  |  | 2023-12-31 | 453291.2424 | 362740.2611 | 372943.2375 | 161678.0349 | 147317.5706 | 91046.5887 | 103680.6259 | 118768.7966 | 136884.3789 | 158599.3473 | 184863.737 | 217058.6486 | 256969.7102 | 306980.7568 | 370523.4949 | 452291.3363 | 558557.995 | 693579.3069 | 830734.3098 | 946592.3078 | 1023808.7751 | 1093629.5824 | 1177817.7397 | 1280253.2742 | 1374912.274
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 1079967.4334 | 912713.0257 | 881774.3541 | 372999.9608 | 264118.7347 | 120326.3229 | 139261.8863 | 163147.4442 | 193603.2062 | 232446.5943 | 282660.6976 | 348700.4817 | 436624.7869 | 554940.8671 | 716108.5264 | 937755.4609 | 1244968.8008 | 1667436.7373 | 1932119.9691 | 2121652.4459 | 2241315.471 | 2332338.7126 | 2445208.4852 | 2586746.7272 | 2732862.5458
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 330358.9863 | 554040.2613 | 1291786.6603 | 1672626.1301 | 2140512.9353 | 2511167.1211 | 2956571.1085 | 3492886.8086 | 4141078.6645 | 4927487.9961 | 5885358.2728 | 7056848.5652 | 8479036.8333 | 10202731.8984 | 12213424.4805 | 13945307.7657 | 15079583.0113 | 16360575.9511 | 17568126.0927 | 18484786.8933 | 19457581.3268 | 20514154.0838 | 21669166.9366 | 22903726.7865
Capital expenditure
| Relay replacement capex |  |  | 2023-12-31 | -4693379 | -3938959 | -8414892 | -2425985 | -2513379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Relay replacement capex |  |  | 2023-12-31 | -4693379 | -8632338 | -17047230 | -19473215 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Relay replacement capex |  |  | 2023-12-31 | 0 | -265657.6665 | -488613.1653 | -964918.3118 | -1102235.4801 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -265657.6665 | -488613.1653 | -964918.3118 | -1102235.4801 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38
| Annualised capex |  |  | 2023-12-31 | 0 | -265657.6665 | -488613.1653 | -964918.3118 | -1102235.4801 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 330358.9863 | 554040.2613 | 1291786.6603 | 1672626.1301 | 2140512.9353 | 2511167.1211 | 2956571.1085 | 3492886.8086 | 4141078.6645 | 4927487.9961 | 5885358.2728 | 7056848.5652 | 8479036.8333 | 10202731.8984 | 12213424.4805 | 13945307.7657 | 15079583.0113 | 16360575.9511 | 17568126.0927 | 18484786.8933 | 19457581.3268 | 20514154.0838 | 21669166.9366 | 22903726.7865
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 64701.3198 | 65427.0959 | 326868.3484 | 570390.65 | 896013.5553 | 1266667.7411 | 1712071.7285 | 2248387.4286 | 2896579.2845 | 3682988.6161 | 4640858.8928 | 5812349.1852 | 7234537.4533 | 8958232.5184 | 10968925.1005 | 12700808.3858 | 13835083.6313 | 15116076.5711 | 16323626.7127 | 17240287.5133 | 18213081.9468 | 19269654.7038 | 20424667.5566 | 21659227.4065
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | 64701.3198 | 65427.0959 | 326868.3484 | 570390.65 | 896013.5553 | 1266667.7411 | 1712071.7285 | 2248387.4286 | 2896579.2845 | 3682988.6161 | 4640858.8928 | 5812349.1852 | 7234537.4533 | 8958232.5184 | 10968925.1005 | 12700808.3858 | 13835083.6313 | 15116076.5711 | 16323626.7127 | 17240287.5133 | 18213081.9468 | 19269654.7038 | 20424667.5566 | 21659227.4065
| Total annualised capex |  |  |  | 0 | -265657.6665 | -488613.1653 | -964918.3118 | -1102235.4801 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38
| Total benefits |  |  |  | 0 | 330358.9863 | 554040.2613 | 1291786.6603 | 1672626.1301 | 2140512.9353 | 2511167.1211 | 2956571.1085 | 3492886.8086 | 4141078.6645 | 4927487.9961 | 5885358.2728 | 7056848.5652 | 8479036.8333 | 10202731.8984 | 12213424.4805 | 13945307.7657 | 15079583.0113 | 16360575.9511 | 17568126.0927 | 18484786.8933 | 19457581.3268 | 20514154.0838 | 21669166.9366 | 22903726.7865
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | 38135.5532 | 16565.7794 | 230376.5172 | 460167.102 | 771563.6173 | 1142217.8031 | 1587621.7905 | 2123937.4906 | 2772129.3465 | 3558538.6781 | 4516408.9548 | 5687899.2472 | 7110087.5153 | 8833782.5804 | 10844475.1625 | 12576358.4478 | 13710633.6933 | 14991626.6331 | 16199176.7747 | 17115837.5753 | 18088632.0088 | 19145204.7658 | 20300217.6186 | 21534777.4685
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | 91267.0865 | 114288.4125 | 423360.1796 | 680614.198 | 1020463.4933 | 1391117.6791 | 1836521.6665 | 2372837.3666 | 3021029.2225 | 3807438.5541 | 4765308.8308 | 5936799.1232 | 7358987.3913 | 9082682.4564 | 11093375.0385 | 12825258.3238 | 13959533.5693 | 15240526.5091 | 16448076.6507 | 17364737.4513 | 18337531.8848 | 19394104.6418 | 20549117.4946 | 21783677.3445
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | 97737.2185 | 120831.1221 | 456047.0144 | 737653.263 | 1110064.8488 | 1517784.4532 | 2007728.8393 | 2597676.1095 | 3310687.1509 | 4175737.4157 | 5229394.7201 | 6518034.0417 | 8082441.1366 | 9978505.7083 | 12190267.5485 | 14095339.1623 | 15343041.9324 | 16752134.1662 | 18080439.3219 | 19088766.2026 | 20158840.0795 | 21321070.1122 | 22591584.2503 | 23949600.0851
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | 31665.4212 | 10023.0698 | 197689.6824 | 403128.037 | 681962.2617 | 1015551.029 | 1416414.6176 | 1899098.7478 | 2482471.418 | 3190239.8165 | 4052323.0655 | 5106664.3286 | 6386633.7699 | 7937959.3286 | 9747582.6524 | 11306277.6092 | 12327125.3302 | 13480018.976 | 14566814.1034 | 15391808.824 | 16267323.8142 | 17218239.2954 | 18257750.863 | 19368854.7278
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | 5099.6546 | -38838.2467 | 101197.8512 | 292904.4889 | 557512.3237 | 891101.091 | 1291964.6796 | 1774648.8098 | 2358021.48 | 3065789.8785 | 3927873.1275 | 4982214.3906 | 6262183.8319 | 7813509.3906 | 9623132.7144 | 11181827.6712 | 12202675.3922 | 13355569.038 | 14442364.1654 | 15267358.886 | 16142873.8762 | 17093789.3574 | 18133300.925 | 19244404.7898
sens | 0 | 0% | 0% | Option 2sens | 0 | 64701.3198 | 65427.0959 | 326868.3484 | 570390.65 | 896013.5553 | 1266667.7411 | 1712071.7285 | 2248387.4286 | 2896579.2845 | 3682988.6161 | 4640858.8928 | 5812349.1852 | 7234537.4533 | 8958232.5184 | 10968925.1005 | 12700808.3858 | 13835083.6313 | 15116076.5711 | 16323626.7127 | 17240287.5133 | 18213081.9468 | 19269654.7038 | 20424667.5566 | 21659227.4065
sens | 0 | 0% | 0% | Option 2sens | 0 | 64701.3198 | 65427.0959 | 326868.3484 | 570390.65 | 896013.5553 | 1266667.7411 | 1712071.7285 | 2248387.4286 | 2896579.2845 | 3682988.6161 | 4640858.8928 | 5812349.1852 | 7234537.4533 | 8958232.5184 | 10968925.1005 | 12700808.3858 | 13835083.6313 | 15116076.5711 | 16323626.7127 | 17240287.5133 | 18213081.9468 | 19269654.7038 | 20424667.5566 | 21659227.4065
sens | 0 | 0% | 0% | Option 2sens | 0 | 64701.3198 | 65427.0959 | 326868.3484 | 570390.65 | 896013.5553 | 1266667.7411 | 1712071.7285 | 2248387.4286 | 2896579.2845 | 3682988.6161 | 4640858.8928 | 5812349.1852 | 7234537.4533 | 8958232.5184 | 10968925.1005 | 12700808.3858 | 13835083.6313 | 15116076.5711 | 16323626.7127 | 17240287.5133 | 18213081.9468 | 19269654.7038 | 20424667.5566 | 21659227.4065

## Option3
Powercor
Relay replacements
OPTION 3 | Defer investment to 2032-33
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Relay replacement capex deferred tp FY33 |  | 28 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 21986594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 21986594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety | (after DF) |  | 2023-12-31 | 33309.3002 | 38461.5729 | 44670.7987 | 52181.603 | 61275.53 | 72323.5019 | 90323.346 | 17079.9342 | 20240.3414 | 24465.2333 | 30184.6941 | 38072.8861 | 49054.1631 | 64429.8794 | 86174.7054 | 117903.8517 | 162582.0963 | 224087.0127 | 289672.9794 | 341019.8274 | 366063.4229 | 382523.3643 | 405009.625 | 435928.0211 | 477228.4333
| Environment |  |  | 2023-12-31 | 3772.5283 | 4359.1759 | 5070.5201 | 5936.0199 | 6990.1612 | 8278.3689 | 10495.6443 | 2247.9484 | 2667.2804 | 3231.177 | 3998.7137 | 5062.747 | 6550.6735 | 8641.9224 | 11609.1889 | 15954.0299 | 22083.0635 | 30526.86 | 39654.2828 | 46810.3358 | 50262.4369 | 52502.7517 | 55580.0552 | 59831.2547 | 65571.7869
| NP | (after DF) |  | 2023-12-31 | 589594.3624 | 679937.7921 | 787513.6029 | 916540.6623 | 1071030.1425 | 1256744.6667 | 1483432.1657 | 25050.7649 | 33811.2054 | 46150.8367 | 63613.5527 | 88506.2 | 124050.2401 | 174888.3085 | 247801.1372 | 352724.9302 | 503959.1593 | 722282.0332 | 776248.0819 | 793030.6452 | 809241.5999 | 814921.7359 | 822517.4996 | 832771.2207 | 846123.7111
| Financial |  |  | 2023-12-31 | 453291.2424 | 520313.4711 | 598559.6937 | 690128.3359 | 797449.0311 | 923492.7206 | 1077940.883 | 118768.7966 | 136884.3789 | 158599.3473 | 184863.737 | 217058.6486 | 256969.7102 | 306980.7568 | 370523.4949 | 453489.229 | 560928.2296 | 696832.9128 | 835220.6328 | 952803.6777 | 1032440.2577 | 1105664.0289 | 1194646.9302 | 1303850.5862 | 1408078.9331
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 1079967.4334 | 1243072.012 | 1435814.6154 | 1664786.6211 | 1936744.8648 | 2260839.2582 | 2662192.0389 | 163147.4442 | 193603.2062 | 232446.5943 | 282660.6976 | 348700.4817 | 436624.7869 | 554940.8671 | 716108.5264 | 940072.0409 | 1249552.5486 | 1673728.8186 | 1940795.9769 | 2133664.4862 | 2258007.7173 | 2355611.8808 | 2477754.1101 | 2632381.0826 | 2797002.8644
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | -11763.0315 | 2956571.1085 | 3492886.8086 | 4141078.6645 | 4927487.9961 | 5885358.2728 | 7056848.5652 | 8479036.8333 | 10202731.8984 | 12211107.9005 | 13940724.018 | 15073290.9299 | 16351899.9433 | 17556114.0524 | 18468094.647 | 19434308.1587 | 20481608.4589 | 21623532.5812 | 22839586.4678
Capital expenditure
| Relay replacement capex deferred tp FY33 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | -21986594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Relay replacement capex deferred tp FY33 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594 | -21986594
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Relay replacement capex deferred tp FY33 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | -11763.0315 | 2956571.1085 | 3492886.8086 | 4141078.6645 | 4927487.9961 | 5885358.2728 | 7056848.5652 | 8479036.8333 | 10202731.8984 | 12211107.9005 | 13940724.018 | 15073290.9299 | 16351899.9433 | 17556114.0524 | 18468094.647 | 19434308.1587 | 20481608.4589 | 21623532.5812 | 22839586.4678
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | -11763.0315 | 1712071.7285 | 2248387.4286 | 2896579.2845 | 3682988.6161 | 4640858.8928 | 5812349.1852 | 7234537.4533 | 8958232.5184 | 10966608.5205 | 12696224.638 | 13828791.5499 | 15107400.5633 | 16311614.6724 | 17223595.267 | 18189808.7787 | 19237109.0789 | 20379033.2012 | 21595087.0878
| First capex year |  |  | 7
| First year |  |  | 7
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | 0 | 0 | 0 | 0 | 0 | -11763.0315 | 1712071.7285 | 2248387.4286 | 2896579.2845 | 3682988.6161 | 4640858.8928 | 5812349.1852 | 7234537.4533 | 8958232.5184 | 10966608.5205 | 12696224.638 | 13828791.5499 | 15107400.5633 | 16311614.6724 | 17223595.267 | 18189808.7787 | 19237109.0789 | 20379033.2012 | 21595087.0878
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38 | -1244499.38
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | -11763.0315 | 2956571.1085 | 3492886.8086 | 4141078.6645 | 4927487.9961 | 5885358.2728 | 7056848.5652 | 8479036.8333 | 10202731.8984 | 12211107.9005 | 13940724.018 | 15073290.9299 | 16351899.9433 | 17556114.0524 | 18468094.647 | 19434308.1587 | 20481608.4589 | 21623532.5812 | 22839586.4678
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | 0 | 0 | 0 | 0 | 0 | -11763.0315 | 1587621.7905 | 2123937.4906 | 2772129.3465 | 3558538.6781 | 4516408.9548 | 5687899.2472 | 7110087.5153 | 8833782.5804 | 10842158.5825 | 12571774.7 | 13704341.6119 | 14982950.6253 | 16187164.7344 | 17099145.329 | 18065358.8407 | 19112659.1409 | 20254583.2632 | 21470637.1498
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | 0 | 0 | 0 | 0 | 0 | -11763.0315 | 1836521.6665 | 2372837.3666 | 3021029.2225 | 3807438.5541 | 4765308.8308 | 5936799.1232 | 7358987.3913 | 9082682.4564 | 11091058.4585 | 12820674.576 | 13953241.4879 | 15231850.5013 | 16436064.6104 | 17348045.205 | 18314258.7167 | 19361559.0169 | 20503483.1392 | 21719537.0258
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | 0 | 0 | 0 | 0 | 0 | -12939.3347 | 2007728.8393 | 2597676.1095 | 3310687.1509 | 4175737.4157 | 5229394.7201 | 6518034.0417 | 8082441.1366 | 9978505.7083 | 12187719.3106 | 14090297.0397 | 15336120.6429 | 16742590.5577 | 18067226.0777 | 19070404.7317 | 20133239.5946 | 21285269.9248 | 22541386.4594 | 23879045.7346
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | 0 | 0 | 0 | 0 | 0 | -10586.7284 | 1416414.6176 | 1899098.7478 | 2482471.418 | 3190239.8165 | 4052323.0655 | 5106664.3286 | 6386633.7699 | 7937959.3286 | 9745497.7305 | 11302152.2362 | 12321462.4569 | 13472210.569 | 14556003.2672 | 15376785.8023 | 16246377.9628 | 17188948.233 | 18216679.9431 | 19311128.441
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | 0 | 0 | 0 | 0 | 0 | -10586.7284 | 1291964.6796 | 1774648.8098 | 2358021.48 | 3065789.8785 | 3927873.1275 | 4982214.3906 | 6262183.8319 | 7813509.3906 | 9621047.7925 | 11177702.2982 | 12197012.5189 | 13347760.631 | 14431553.3292 | 15252335.8643 | 16121928.0248 | 17064498.295 | 18092230.0051 | 19186678.503
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 0 | 0 | 0 | -11763.0315 | 1712071.7285 | 2248387.4286 | 2896579.2845 | 3682988.6161 | 4640858.8928 | 5812349.1852 | 7234537.4533 | 8958232.5184 | 10966608.5205 | 12696224.638 | 13828791.5499 | 15107400.5633 | 16311614.6724 | 17223595.267 | 18189808.7787 | 19237109.0789 | 20379033.2012 | 21595087.0878
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 0 | 0 | 0 | -11763.0315 | 1712071.7285 | 2248387.4286 | 2896579.2845 | 3682988.6161 | 4640858.8928 | 5812349.1852 | 7234537.4533 | 8958232.5184 | 10966608.5205 | 12696224.638 | 13828791.5499 | 15107400.5633 | 16311614.6724 | 17223595.267 | 18189808.7787 | 19237109.0789 | 20379033.2012 | 21595087.0878
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 0 | 0 | 0 | -11763.0315 | 1712071.7285 | 2248387.4286 | 2896579.2845 | 3682988.6161 | 4640858.8928 | 5812349.1852 | 7234537.4533 | 8958232.5184 | 10966608.5205 | 12696224.638 | 13828791.5499 | 15107400.5633 | 16311614.6724 | 17223595.267 | 18189808.7787 | 19237109.0789 | 20379033.2012 | 21595087.0878

## Option4
Powercor
Relay replacements
OPTION 4 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety Risk | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned Replacement Risk |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Financial consequence |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NP consequence |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option5
Powercor
Relay replacements
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
Powercor
Relay replacements
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 1 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 126565619.2074 | 2026-06-30 |  | 1201909.4143 | 1383430.5626 | 1597936.2433 | 1852762.0842 | 2155427.8529 | 2516116.6019 | 2949695.9608 | 3471974.2306 | 4102741.3584 | 4867351.5699 | 5798440.3709 | 6937962.8263 | 8339581.259 | 10054028.0302 | 12151715.5929 | 14636114.4721 | 16905450.8935 | 18637970.068 | 20358172.6267 | 21913003.5407 | 23066341.4322 | 24250277.5763 | 25551764.9567 | 26994713.0669 | 28531284.4788
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Capital expenditure | Option 2Capital expenditure | -23383596.5609 | 2026-06-30 |  | -5223320.8435 | -4383717.2848 | -9365039.725 | -2699909.3865 | -2797171.2743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 13732101.7799 | 2026-06-30 |  | 1201909.4143 | 1015769.8689 | 981337.83 | 415116.3735 | 293941.08 | 133912.6864 | 154986.3144 | 181568.8539 | 215463.4565 | 258692.7545 | 314576.665 | 388073.1758 | 485925.247 | 617600.7091 | 796966.2352 | 1043639.9117 | 1385541.5228 | 1855711.432 | 2150280.7481 | 2361213.8384 | 2494388.3323 | 2595689.249 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -18414569.1535 | 2026-06-30 |  | 0 | -295653.7766 | -543783.7709 | -1073869.792 | -1226691.8052 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 112833517.4275 | 2026-06-30 |  | 0 | 367660.6937 | 616598.4134 | 1437645.7107 | 1861486.7729 | 2382203.9155 | 2794709.6463 | 3290405.3766 | 3887277.9018 | 4608658.8155 | 5483863.7059 | 6549889.6505 | 7853656.012 | 9436427.3212 | 11354749.3577 | 13592474.5604 | 15519909.3707 | 16782258.636 | 18207891.8786 | 19551789.7024 | 20571953.0999 | 21654588.3273 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | 72006.9171 | 72814.6425 | 363775.9187 | 634794.9678 | 997184.817 | 1409690.5479 | 1905386.2782 | 2502258.8034 | 3223639.717 | 4098844.6075 | 5164870.552 | 6468636.9135 | 8051408.2227 | 9969730.2593 | 12207455.4619 | 14134890.2722 | 15397239.5375 | 16822872.7801 | 18166770.6039 | 19186934.0014 | 20269569.2289 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 94418948.2739 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -18414569.1535 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 112833517.4275 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Capital expenditure | Option 3Capital expenditure | -20251029.6961 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | -24469158.5142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 22056084.0957 | 2026-06-30 |  | 1201909.4143 | 1383430.5626 | 1597936.2433 | 1852762.0842 | 2155427.8529 | 2516116.6019 | 2962787.1873 | 181568.8539 | 215463.4565 | 258692.7545 | 314576.665 | 388073.1758 | 485925.247 | 617600.7091 | 796966.2352 | 1046218.0628 | 1390642.8337 | 1862713.9689 | 2159936.3868 | 2374582.1899 | 2512965.3443 | 2621590.2522 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -13201968.7148 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | -1385019.0985 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 104509535.1117 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | -13091.2265 | 3290405.3766 | 3887277.9018 | 4608658.8155 | 5483863.7059 | 6549889.6505 | 7853656.012 | 9436427.3212 | 11354749.3577 | 13589896.4092 | 15514808.0598 | 16775256.099 | 18198236.2399 | 19538421.3509 | 20553376.0879 | 21628687.3242 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | -13091.2265 | 1905386.2782 | 2502258.8034 | 3223639.717 | 4098844.6075 | 5164870.552 | 6468636.9135 | 8051408.2227 | 9969730.2593 | 12204877.3108 | 14129788.9613 | 15390237.0006 | 16813217.1414 | 18153402.2524 | 19168356.9894 | 20243668.2257 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | 91307566.3969 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -13201968.7148 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 104509535.1117 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 0 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | 0 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 0 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 1.385 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 1.2019 | 1.3834 | 1.5979 | 1.8528 | 2.1554 | 2.5161 | 2.9497 | 3.472 | 4.1027 | 4.8674 | 5.7984 | 6.938 | 8.3396 | 10.054 | 12.1517 | 14.6361 | 16.9055 | 18.638 | 20.3582 | 21.913 | 23.0663 | 24.2503 | 25.5518 | 26.9947 | 28.5313
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 0 |  |  | Energy at risk energy at risk (weighted) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Energy at risk value | 0 |  |  | Option 1 (base case) risk cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Sensitivity_calcs
Powercor
Relay replacements
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 1 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
[7 empty] | 46203 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 16822872.7801 | 18166770.6039 | 19186934.0014 | 20269569.2289 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 94418948.2739 |  | 0 | 0 | 72006.9171 | 72814.6425 | 363775.9187 | 634794.9678 | 997184.817 | 1409690.5479 | 1905386.2782 | 2502258.8034 | 3223639.717 | 4098844.6075 | 5164870.552 | 6468636.9135 | 8051408.2227 | 9969730.2593 | 12207455.4619 | 14134890.2722 | 15397239.5375 | 16822872.7801 | 18166770.6039 | 19186934.0014 | 20269569.2289 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 92577491.3586 |  | 0 | 0 | 42441.5394 | 18436.2654 | 256388.9395 | 512125.7872 | 858682.9072 | 1271188.638 | 1766884.3683 | 2363756.8935 | 3085137.8072 | 3960342.6976 | 5026368.6422 | 6330135.0037 | 7912906.3129 | 9831228.3494 | 12068953.5521 | 13996388.3624 | 15258737.6276 | 16684370.8703 | 18028268.6941 | 19048432.0916 | 20131067.319 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 96260405.1893 |  | 0 | 0 | 101572.2948 | 127193.0196 | 471162.8979 | 757464.1483 | 1135686.7269 | 1548192.4577 | 2043888.188 | 2640760.7132 | 3362141.6269 | 4237346.5173 | 5303372.4619 | 6607138.8234 | 8189910.1326 | 10108232.1691 | 12345957.3717 | 14273392.1821 | 15535741.4473 | 16961374.69 | 18305272.5138 | 19325435.9113 | 20408071.1387 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 105702300.0167 |  | 0 | 0 | 108772.9865 | 134474.4838 | 507540.4897 | 820943.645 | 1235405.2086 | 1689161.5125 | 2234426.8159 | 2890986.5936 | 3684505.5986 | 4647230.9781 | 5819859.5171 | 7254002.5147 | 8995050.9548 | 11105205.1951 | 13566702.9179 | 15686881.2093 | 17075465.4011 | 18643661.968 | 20121949.5741 | 21244129.3114 | 22435028.0616 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 83135596.5312 |  | 0 | 0 | 35240.8477 | 11154.8011 | 220011.3476 | 448646.2905 | 758964.4255 | 1130219.5833 | 1576345.7405 | 2113531.0132 | 2762773.8355 | 3550458.2369 | 4509881.587 | 5683271.3123 | 7107765.4906 | 8834255.3235 | 10848208.0059 | 12582899.3351 | 13719013.6739 | 15002083.5923 | 16211591.6337 | 17129738.6914 | 18104110.3961 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 81294139.6158 |  | 0 | 0 | 5675.4701 | -43223.5759 | 112624.3684 | 325977.1099 | 620462.5156 | 991717.6734 | 1437843.8307 | 1975029.1034 | 2624271.9256 | 3411956.327 | 4371379.6771 | 5544769.4025 | 6969263.5807 | 8695753.4137 | 10709706.096 | 12444397.4253 | 13580511.7641 | 14863581.6824 | 16073089.7238 | 16991236.7816 | 17965608.4863 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 94418948.2739 |  | 0 | 0 | 72006.9171 | 72814.6425 | 363775.9187 | 634794.9678 | 997184.817 | 1409690.5479 | 1905386.2782 | 2502258.8034 | 3223639.717 | 4098844.6075 | 5164870.552 | 6468636.9135 | 8051408.2227 | 9969730.2593 | 12207455.4619 | 14134890.2722 | 15397239.5375 | 16822872.7801 | 18166770.6039 | 19186934.0014 | 20269569.2289 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 94418948.2739 |  | 0 | 0 | 72006.9171 | 72814.6425 | 363775.9187 | 634794.9678 | 997184.817 | 1409690.5479 | 1905386.2782 | 2502258.8034 | 3223639.717 | 4098844.6075 | 5164870.552 | 6468636.9135 | 8051408.2227 | 9969730.2593 | 12207455.4619 | 14134890.2722 | 15397239.5375 | 16822872.7801 | 18166770.6039 | 19186934.0014 | 20269569.2289 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 94418948.2739 |  | 0 | 0 | 72006.9171 | 72814.6425 | 363775.9187 | 634794.9678 | 997184.817 | 1409690.5479 | 1905386.2782 | 2502258.8034 | 3223639.717 | 4098844.6075 | 5164870.552 | 6468636.9135 | 8051408.2227 | 9969730.2593 | 12207455.4619 | 14134890.2722 | 15397239.5375 | 16822872.7801 | 18166770.6039 | 19186934.0014 | 20269569.2289 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13091.2265 | 1905386.2782 | 2502258.8034 | 3223639.717 | 4098844.6075 | 5164870.552 | 6468636.9135 | 8051408.2227 | 9969730.2593 | 12204877.3108 | 14129788.9613 | 15390237.0006 | 16813217.1414 | 18153402.2524 | 19168356.9894 | 20243668.2257 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 91307566.3969 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13091.2265 | 1905386.2782 | 2502258.8034 | 3223639.717 | 4098844.6075 | 5164870.552 | 6468636.9135 | 8051408.2227 | 9969730.2593 | 12204877.3108 | 14129788.9613 | 15390237.0006 | 16813217.1414 | 18153402.2524 | 19168356.9894 | 20243668.2257 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 89987369.5254 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13091.2265 | 1766884.3683 | 2363756.8935 | 3085137.8072 | 3960342.6976 | 5026368.6422 | 6330135.0037 | 7912906.3129 | 9831228.3494 | 12066375.4009 | 13991287.0515 | 15251735.0907 | 16674715.2316 | 18014900.3426 | 19029855.0795 | 20105166.3159 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 92627763.2684 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13091.2265 | 2043888.188 | 2640760.7132 | 3362141.6269 | 4237346.5173 | 5303372.4619 | 6607138.8234 | 8189910.1326 | 10108232.1691 | 12343379.2206 | 14268290.8712 | 15528738.9104 | 16951719.0513 | 18291904.1623 | 19306858.8992 | 20382170.1356 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 101758519.9081 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -14400.3492 | 2234426.8159 | 2890986.5936 | 3684505.5986 | 4647230.9781 | 5819859.5171 | 7254002.5147 | 8995050.9548 | 11105205.1951 | 13563866.9517 | 15681269.7673 | 17067762.6105 | 18633040.7654 | 20107244.3875 | 21223694.5982 | 22406536.9581 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | 80856612.8857 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11782.1039 | 1576345.7405 | 2113531.0132 | 2762773.8355 | 3550458.2369 | 4509881.587 | 5683271.3123 | 7107765.4906 | 8834255.3235 | 10845887.6699 | 12578308.1553 | 13712711.3907 | 14993393.5174 | 16199560.1173 | 17113019.3806 | 18080799.4933 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | 79536416.0143 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11782.1039 | 1437843.8307 | 1975029.1034 | 2624271.9256 | 3411956.327 | 4371379.6771 | 5544769.4025 | 6969263.5807 | 8695753.4137 | 10707385.76 | 12439806.2455 | 13574209.4808 | 14854891.6076 | 16061058.2075 | 16974517.4708 | 17942297.5835 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 91307566.3969 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13091.2265 | 1905386.2782 | 2502258.8034 | 3223639.717 | 4098844.6075 | 5164870.552 | 6468636.9135 | 8051408.2227 | 9969730.2593 | 12204877.3108 | 14129788.9613 | 15390237.0006 | 16813217.1414 | 18153402.2524 | 19168356.9894 | 20243668.2257 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 91307566.3969 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13091.2265 | 1905386.2782 | 2502258.8034 | 3223639.717 | 4098844.6075 | 5164870.552 | 6468636.9135 | 8051408.2227 | 9969730.2593 | 12204877.3108 | 14129788.9613 | 15390237.0006 | 16813217.1414 | 18153402.2524 | 19168356.9894 | 20243668.2257 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 91307566.3969 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13091.2265 | 1905386.2782 | 2502258.8034 | 3223639.717 | 4098844.6075 | 5164870.552 | 6468636.9135 | 8051408.2227 | 9969730.2593 | 12204877.3108 | 14129788.9613 | 15390237.0006 | 16813217.1414 | 18153402.2524 | 19168356.9894 | 20243668.2257 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 1 | 1 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 94.4189 | 91.3076 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens1 | Capex 10% higher | 0 | 92.5775 | 89.9874 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens2 | Capex 10% lower | 0 | 96.2604 | 92.6278 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens3 | Total benefits 10% higher | 0 | 105.7023 | 101.7585 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens4 | Total benefits 10% lower | 0 | 83.1356 | 80.8566 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 81.2941 | 79.5364 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Workings_calcs
Powercor
Relay replacements
WORKINGS - COSTS
[8 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Replacement year
|  | ZSS | Option 1 | Option 2 | Option 3
|  | AC | 2373163 | 27 | 32
|  | BAN | 1335329 | 28 | 32
|  | DDL | 2320216 | 27 | 32
|  | ECA | 566523 | 30 | 32
|  | FDN | 720140 | 29 | 32
|  | GCY | 2906970 | 29 | 32
|  | MLN | 1859462 | 30 | 32
|  | SA | 3909308 | 29 | 32
|  | SHL | 276663 | 31 | 32
|  | SHN | 2236716 | 31 | 32
|  | TYA | 878474 | 29 | 32
|  | WBE | 2603630 | 28 | 32
Option 1 capex profile
|  | ZSS | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
|  | AC | 27: 2373163; 28: 0; 29: 0; 30: 0; 31: 0
|  | BAN | 27: 0; 28: 1335329; 29: 0; 30: 0; 31: 0
|  | DDL | 27: 2320216; 28: 0; 29: 0; 30: 0; 31: 0
|  | ECA | 27: 0; 28: 0; 29: 0; 30: 566523; 31: 0
|  | FDN | 27: 0; 28: 0; 29: 720140; 30: 0; 31: 0
|  | GCY | 27: 0; 28: 0; 29: 2906970; 30: 0; 31: 0
|  | MLN | 27: 0; 28: 0; 29: 0; 30: 1859462; 31: 0
|  | SA | 27: 0; 28: 0; 29: 3909308; 30: 0; 31: 0
|  | SHL | 27: 0; 28: 0; 29: 0; 30: 0; 31: 276663
|  | SHN | 27: 0; 28: 0; 29: 0; 30: 0; 31: 2236716
|  | TYA | 27: 0; 28: 0; 29: 878474; 30: 0; 31: 0
|  | WBE | 27: 0; 28: 2603630; 29: 0; 30: 0; 31: 0
|  | Total | 27: 4693379; 28: 3938959; 29: 8414892; 30: 2425985; 31: 2513379
Option 2 capex profile
|  | ZSS | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
|  | AC | 0 | 0 | 0 | 0 | 0 | 0 | 2373163 | 0 | 0
|  | BAN | 0 | 0 | 0 | 0 | 0 | 0 | 1335329 | 0 | 0
|  | DDL | 0 | 0 | 0 | 0 | 0 | 0 | 2320216 | 0 | 0
|  | ECA | 0 | 0 | 0 | 0 | 0 | 0 | 566523 | 0 | 0
|  | FDN | 0 | 0 | 0 | 0 | 0 | 0 | 720140 | 0 | 0
|  | GCY | 0 | 0 | 0 | 0 | 0 | 0 | 2906970 | 0 | 0
|  | MLN | 0 | 0 | 0 | 0 | 0 | 0 | 1859462 | 0 | 0
|  | SA | 0 | 0 | 0 | 0 | 0 | 0 | 3909308 | 0 | 0
|  | SHL | 0 | 0 | 0 | 0 | 0 | 0 | 276663 | 0 | 0
|  | SHN | 0 | 0 | 0 | 0 | 0 | 0 | 2236716 | 0 | 0
|  | TYA | 0 | 0 | 0 | 0 | 0 | 0 | 878474 | 0 | 0
|  | WBE | 0 | 0 | 0 | 0 | 0 | 0 | 2603630 | 0 | 0
|  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 21986594 | 0 | 0

## CBRM_data
Powercor
Relay replacements
Flags and data for calcs
Future: future risk of current assets
New assets: risk associated with new assets
|  | Year | [147 empty] | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
|  | Flags | [147 empty] | TotalFuture1 | TotalFuture2 | TotalFuture3 | TotalFuture4 | TotalFuture5 | TotalFuture6 | TotalFuture7 | TotalFuture8 | TotalFuture9 | TotalFuture10 | TotalFuture11 | TotalFuture12 | TotalFuture13 | TotalFuture14 | TotalFuture15 | TotalFuture16 | TotalFuture17 | TotalFuture18 | TotalFuture19 | TotalFuture20 | TotalFuture21 | TotalFuture22 | TotalFuture23 | TotalFuture24 | TotalFuture25 | TotalFuture26 | TotalFuture27 | TotalFuture28 | TotalFuture29 | TotalFuture30 | #NAME? | TotalNew1 | TotalNew2 | TotalNew3 | TotalNew4 | TotalNew5 | TotalNew6 | TotalNew7 | TotalNew8 | TotalNew9 | TotalNew10 | TotalNew11 | TotalNew12 | TotalNew13 | TotalNew14 | TotalNew15 | TotalNew16 | TotalNew17 | TotalNew18 | TotalNew19 | TotalNew20 | TotalNew21 | TotalNew22 | TotalNew23 | TotalNew24 | TotalNew25 | TotalNew26 | TotalNew27 | TotalNew28 | TotalNew29 | TotalNew30 | #NAME? | OpexFuture1 | OpexFuture2 | OpexFuture3 | OpexFuture4 | OpexFuture5 | OpexFuture6 | OpexFuture7 | OpexFuture8 | OpexFuture9 | OpexFuture10 | OpexFuture11 | OpexFuture12 | OpexFuture13 | OpexFuture14 | OpexFuture15 | OpexFuture16 | OpexFuture17 | OpexFuture18 | OpexFuture19 | OpexFuture20 | OpexFuture21 | OpexFuture22 | OpexFuture23 | OpexFuture24 | OpexFuture25 | OpexFuture26 | OpexFuture27 | OpexFuture28 | OpexFuture29 | OpexFuture30 | #NAME? | OpexNew1 | OpexNew2 | OpexNew3 | OpexNew4 | OpexNew5 | OpexNew6 | OpexNew7 | OpexNew8 | OpexNew9 | OpexNew10 | OpexNew11 | OpexNew12 | OpexNew13 | OpexNew14 | OpexNew15 | OpexNew16 | OpexNew17 | OpexNew18 | OpexNew19 | OpexNew20 | OpexNew21 | OpexNew22 | OpexNew23 | OpexNew24 | OpexNew25 | OpexNew26 | OpexNew27 | OpexNew28 | OpexNew29 | OpexNew30 | #NAME? | OpexDelta1 | OpexDelta2 | OpexDelta3 | OpexDelta4 | OpexDelta5 | OpexDelta6 | OpexDelta7 | OpexDelta8 | OpexDelta9 | OpexDelta10 | OpexDelta11 | OpexDelta12 | OpexDelta13 | OpexDelta14 | OpexDelta15 | OpexDelta16 | OpexDelta17 | OpexDelta18 | OpexDelta19 | OpexDelta20 | OpexDelta21 | OpexDelta22 | OpexDelta23 | OpexDelta24 | OpexDelta25 | OpexDelta26 | OpexDelta27 | OpexDelta28 | OpexDelta29 | OpexDelta30 | #NAME? | CapexFuture1 | CapexFuture2 | CapexFuture3 | CapexFuture4 | CapexFuture5 | CapexFuture6 | CapexFuture7 | CapexFuture8 | CapexFuture9 | CapexFuture10 | CapexFuture11 | CapexFuture12 | CapexFuture13 | CapexFuture14 | CapexFuture15 | CapexFuture16 | CapexFuture17 | CapexFuture18 | CapexFuture19 | CapexFuture20 | CapexFuture21 | CapexFuture22 | CapexFuture23 | CapexFuture24 | CapexFuture25 | CapexFuture26 | CapexFuture27 | CapexFuture28 | CapexFuture29 | CapexFuture30 | #NAME? | CapexNew1 | CapexNew2 | CapexNew3 | CapexNew4 | CapexNew5 | CapexNew6 | CapexNew7 | CapexNew8 | CapexNew9 | CapexNew10 | CapexNew11 | CapexNew12 | CapexNew13 | CapexNew14 | CapexNew15 | CapexNew16 | CapexNew17 | CapexNew18 | CapexNew19 | CapexNew20 | CapexNew21 | CapexNew22 | CapexNew23 | CapexNew24 | CapexNew25 | CapexNew26 | CapexNew27 | CapexNew28 | CapexNew29 | CapexNew30 | #NAME? | CapexDelta1 | CapexDelta2 | CapexDelta3 | CapexDelta4 | CapexDelta5 | CapexDelta6 | CapexDelta7 | CapexDelta8 | CapexDelta9 | CapexDelta10 | CapexDelta11 | CapexDelta12 | CapexDelta13 | CapexDelta14 | CapexDelta15 | CapexDelta16 | CapexDelta17 | CapexDelta18 | CapexDelta19 | CapexDelta20 | CapexDelta21 | CapexDelta22 | CapexDelta23 | CapexDelta24 | CapexDelta25 | CapexDelta26 | CapexDelta27 | CapexDelta28 | CapexDelta29 | CapexDelta30 | #NAME? | TotexDelta1 | TotexDelta2 | TotexDelta3 | TotexDelta4 | TotexDelta5 | TotexDelta6 | TotexDelta7 | TotexDelta8 | TotexDelta9 | TotexDelta10 | TotexDelta11 | TotexDelta12 | TotexDelta13 | TotexDelta14 | TotexDelta15 | TotexDelta16 | TotexDelta17 | TotexDelta18 | TotexDelta19 | TotexDelta20 | TotexDelta21 | TotexDelta22 | TotexDelta23 | TotexDelta24 | TotexDelta25 | TotexDelta26 | TotexDelta27 | TotexDelta28 | TotexDelta29 | TotexDelta30 | #NAME? | SafetyFuture1 | SafetyFuture2 | SafetyFuture3 | SafetyFuture4 | SafetyFuture5 | SafetyFuture6 | SafetyFuture7 | SafetyFuture8 | SafetyFuture9 | SafetyFuture10 | SafetyFuture11 | SafetyFuture12 | SafetyFuture13 | SafetyFuture14 | SafetyFuture15 | SafetyFuture16 | SafetyFuture17 | SafetyFuture18 | SafetyFuture19 | SafetyFuture20 | SafetyFuture21 | SafetyFuture22 | SafetyFuture23 | SafetyFuture24 | SafetyFuture25 | SafetyFuture26 | SafetyFuture27 | SafetyFuture28 | SafetyFuture29 | SafetyFuture30 | #NAME? | SafetyNew1 | SafetyNew2 | SafetyNew3 | SafetyNew4 | SafetyNew5 | SafetyNew6 | SafetyNew7 | SafetyNew8 | SafetyNew9 | SafetyNew10 | SafetyNew11 | SafetyNew12 | SafetyNew13 | SafetyNew14 | SafetyNew15 | SafetyNew16 | SafetyNew17 | SafetyNew18 | SafetyNew19 | SafetyNew20 | SafetyNew21 | SafetyNew22 | SafetyNew23 | SafetyNew24 | SafetyNew25 | SafetyNew26 | SafetyNew27 | SafetyNew28 | SafetyNew29 | SafetyNew30 | #NAME? | SafetyDelta1 | SafetyDelta2 | SafetyDelta3 | SafetyDelta4 | SafetyDelta5 | SafetyDelta6 | SafetyDelta7 | SafetyDelta8 | SafetyDelta9 | SafetyDelta10 | SafetyDelta11 | SafetyDelta12 | SafetyDelta13 | SafetyDelta14 | SafetyDelta15 | SafetyDelta16 | SafetyDelta17 | SafetyDelta18 | SafetyDelta19 | SafetyDelta20 | SafetyDelta21 | SafetyDelta22 | SafetyDelta23 | SafetyDelta24 | SafetyDelta25 | SafetyDelta26 | SafetyDelta27 | SafetyDelta28 | SafetyDelta29 | SafetyDelta30 | #NAME? | EnvironmentFuture1 | EnvironmentFuture2 | EnvironmentFuture3 | EnvironmentFuture4 | EnvironmentFuture5 | EnvironmentFuture6 | EnvironmentFuture7 | EnvironmentFuture8 | EnvironmentFuture9 | EnvironmentFuture10 | EnvironmentFuture11 | EnvironmentFuture12 | EnvironmentFuture13 | EnvironmentFuture14 | EnvironmentFuture15 | EnvironmentFuture16 | EnvironmentFuture17 | EnvironmentFuture18 | EnvironmentFuture19 | EnvironmentFuture20 | EnvironmentFuture21 | EnvironmentFuture22 | EnvironmentFuture23 | EnvironmentFuture24 | EnvironmentFuture25 | EnvironmentFuture26 | EnvironmentFuture27 | EnvironmentFuture28 | EnvironmentFuture29 | EnvironmentFuture30 | #NAME? | EnvironmentNew1 | EnvironmentNew2 | EnvironmentNew3 | EnvironmentNew4 | EnvironmentNew5 | EnvironmentNew6 | EnvironmentNew7 | EnvironmentNew8 | EnvironmentNew9 | EnvironmentNew10 | EnvironmentNew11 | EnvironmentNew12 | EnvironmentNew13 | EnvironmentNew14 | EnvironmentNew15 | EnvironmentNew16 | EnvironmentNew17 | EnvironmentNew18 | EnvironmentNew19 | EnvironmentNew20 | EnvironmentNew21 | EnvironmentNew22 | EnvironmentNew23 | EnvironmentNew24 | EnvironmentNew25 | EnvironmentNew26 | EnvironmentNew27 | EnvironmentNew28 | EnvironmentNew29 | EnvironmentNew30 | #NAME? | EnvironmentDelta1 | EnvironmentDelta2 | EnvironmentDelta3 | EnvironmentDelta4 | EnvironmentDelta5 | EnvironmentDelta6 | EnvironmentDelta7 | EnvironmentDelta8 | EnvironmentDelta9 | EnvironmentDelta10 | EnvironmentDelta11 | EnvironmentDelta12 | EnvironmentDelta13 | EnvironmentDelta14 | EnvironmentDelta15 | EnvironmentDelta16 | EnvironmentDelta17 | EnvironmentDelta18 | EnvironmentDelta19 | EnvironmentDelta20 | EnvironmentDelta21 | EnvironmentDelta22 | EnvironmentDelta23 | EnvironmentDelta24 | EnvironmentDelta25 | EnvironmentDelta26 | EnvironmentDelta27 | EnvironmentDelta28 | EnvironmentDelta29 | EnvironmentDelta30 | #NAME? | NPFuture1 | NPFuture2 | NPFuture3 | NPFuture4 | NPFuture5 | NPFuture6 | NPFuture7 | NPFuture8 | NPFuture9 | NPFuture10 | NPFuture11 | NPFuture12 | NPFuture13 | NPFuture14 | NPFuture15 | NPFuture16 | NPFuture17 | NPFuture18 | NPFuture19 | NPFuture20 | NPFuture21 | NPFuture22 | NPFuture23 | NPFuture24 | NPFuture25 | NPFuture26 | NPFuture27 | NPFuture28 | NPFuture29 | NPFuture30 | #NAME? | NPNew1 | NPNew2 | NPNew3 | NPNew4 | NPNew5 | NPNew6 | NPNew7 | NPNew8 | NPNew9 | NPNew10 | NPNew11 | NPNew12 | NPNew13 | NPNew14 | NPNew15 | NPNew16 | NPNew17 | NPNew18 | NPNew19 | NPNew20 | NPNew21 | NPNew22 | NPNew23 | NPNew24 | NPNew25 | NPNew26 | NPNew27 | NPNew28 | NPNew29 | NPNew30 | #NAME? | NPDelta1 | NPDelta2 | NPDelta3 | NPDelta4 | NPDelta5 | NPDelta6 | NPDelta7 | NPDelta8 | NPDelta9 | NPDelta10 | NPDelta11 | NPDelta12 | NPDelta13 | NPDelta14 | NPDelta15 | NPDelta16 | NPDelta17 | NPDelta18 | NPDelta19 | NPDelta20 | NPDelta21 | NPDelta22 | NPDelta23 | NPDelta24 | NPDelta25 | NPDelta26 | NPDelta27 | NPDelta28 | NPDelta29 | NPDelta30 | #NAME? | Delta1 | Delta2 | Delta3 | Delta4 | Delta5 | Delta6 | Delta7 | Delta8 | Delta9 | Delta10 | Delta11 | Delta12 | Delta13 | Delta14 | Delta15 | Delta16 | Delta17 | Delta18 | Delta19 | Delta20 | Delta21 | Delta22 | Delta23 | Delta24 | Delta25 | Delta26 | Delta27 | Delta28 | Delta29 | Delta30
|  | Risk | [147 empty] | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | #NAME? | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | #NAME? | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | #NAME? | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | #NAME? | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | Opex | #NAME? | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | #NAME? | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | #NAME? | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | Capex | #NAME? | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | Totex | #NAME? | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | #NAME? | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | #NAME? | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | Safety | #NAME? | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | #NAME? | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | #NAME? | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | Environment | #NAME? | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | #NAME? | [30 empty] | #NAME? | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | bar: NPNew1 to NPNew30
[150 empty] | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | New Asset | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta
[150 empty] | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | Future | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | New | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta | Delta
CBRM data extract
|  |  | Asset Description | [12 empty] | Essential Information |  |  | Current Condition Related Failure Risks (2024) | [10 empty] | Future Condition Related Failure Risks (2034) | [10 empty] | New Asset Condition Related Failure Risks | [9 empty] | Total Risk | [6 empty] | Future Health index | [30 empty] | Future PoF | [30 empty] | Future NP PoF | [29 empty] | Future Risk | [30 empty] | New Asset Risk | [30 empty] | Future Opex Risk | [30 empty] | New Asset Future Opex Risk | [30 empty] | Delta Opex Risk | [30 empty] | Future Capex Risk | [30 empty] | New Asset Capex Risk | [30 empty] | Delta Capex Risk | [30 empty] | Delta Totex Risk | [30 empty] | Future Safety Risk | [30 empty] | New Asset Safety Risk | [30 empty] | Delta Safety Risk | [30 empty] | Future Environment Risk | [30 empty] | New Asset Environment Risk | [30 empty] | Delta Environment Risk | [30 empty] | Future NP Risk | [30 empty] | NPNew1: New Asset NP Risk |  | Delta NP Risk | [30 empty] | Delta Risk
[58 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
| Replace | Asset Index | Asset ID | Substation ID | Feeder ID | Operating voltage | Asset Description | Protection Function | Relay Set | Manufacturer | Model | ManuModel | Class | Relay Type |  | Demand Distribution | Time Between Inspections Used |  | Current Health Index (2024) | Condition PoF (2024) | Condition PoF with NP Consequences | Condition PoF without NP Consequences | Financial Risk OPEX (2024) | Financial Risk CAPEX (2024) | Financial Risk TOTEX (2024) | Safety Risk (2024) | Envionmental Risk (2024) | Network Performance Risk (2024) |  | Future Health Index (2034) | Condition PoF (2034) | Condition PoF with NP Consequences | Condition PoF without NP Consequences | Financial Risk OPEX (2034) | Financial Risk CAPEX (2034) | Financial Risk TOTEX (2034) | Safety Risk (2034) | Envionmental Risk (2034) | Network Performance Risk (2034) |  | New Asset Condition PoF | Condition PoF with NP Consequences | Condition PoF without NP Consequences | New Asset Financial Risk OPEX | New Asset Financial Risk CAPEX | New Asset Financial Risk TOTEX | New Asset Safety Risk | New Asset Envionmental Risk | New Asset Network Performance Risk |  | Total Risk (2024) | Total Risk (2034) | New Asset Risk | Delta Risk |  | Forecast Ageing Constant (B2) |  | Health Index (2025) | Health Index (2026) | Health Index (2027) | Health Index (2028) | Health Index (2029) | Health Index (2030) | Health Index (2031) | Health Index (2032) | Health Index (2033) | Health Index (2034) | Health Index (2035) | Health Index (2036) | Health Index (2037) | Health Index (2038) | Health Index (2039) | Health Index (2040) | Health Index (2041) | Health Index (2042) | Health Index (2043) | Health Index (2044) | Health Index (2045) | Health Index (2046) | Health Index (2047) | Health Index (2048) | Health Index (2049) | Health Index (2050) | Health Index (2051) | Health Index (2052) | Health Index (2053) | Health Index (2054) |  | PoF (2025) | PoF (2026) | PoF (2027) | PoF (2028) | PoF (2029) | PoF (2030) | PoF (2031) | PoF (2032) | PoF (2033) | PoF (2034) | PoF (2035) | PoF (2036) | PoF (2037) | PoF (2038) | PoF (2039) | PoF (2040) | PoF (2041) | PoF (2042) | PoF (2043) | PoF (2044) | PoF (2045) | PoF (2046) | PoF (2047) | PoF (2048) | PoF (2049) | PoF (2050) | PoF (2051) | PoF (2052) | PoF (2053) | PoF (2054) |  | Future NP PoF (2025) | Future NP PoF (2026) | Future NP PoF (2027) | Future NP PoF (2028) | Future NP PoF (2029) | Future NP PoF (2030) | Future NP PoF (2031) | Future NP PoF (2032) | Future NP PoF (2033) | Future NP PoF (2034) | Future NP PoF (2035) | Future NP PoF (2036) | Future NP PoF (2037) | Future NP PoF (2038) | Future NP PoF (2039) | Future NP PoF (2040) | Future NP PoF (2041) | Future NP PoF (2042) | Future NP PoF (2043) | Future NP PoF (2044) | Future NP PoF (2045) | Future NP PoF (2046) | Future NP PoF (2047) | Future NP PoF (2048) | Future NP PoF (2049) | Future NP PoF (2050) | Future NP PoF (2051) | Future NP PoF (2052) | Future NP PoF (2053) | Future NP PoF (2054) | Future Total Risk (2025) | Future Total Risk (2026) | Future Total Risk (2027) | Future Total Risk (2028) | Future Total Risk (2029) | Future Total Risk (2030) | Future Total Risk (2031) | Future Total Risk (2032) | Future Total Risk (2033) | Future Total Risk (2034) | Future Total Risk (2035) | Future Total Risk (2036) | Future Total Risk (2037) | Future Total Risk (2038) | Future Total Risk (2039) | Future Total Risk (2040) | Future Total Risk (2041) | Future Total Risk (2042) | Future Total Risk (2043) | Future Total Risk (2044) | Future Total Risk (2045) | Future Total Risk (2046) | Future Total Risk (2047) | Future Total Risk (2048) | Future Total Risk (2049) | Future Total Risk (2050) | Future Total Risk (2051) | Future Total Risk (2052) | Future Total Risk (2053) | Future Total Risk (2054) |  | New Asset Total Risk (2025) | New Asset Total Risk (2026) | New Asset Total Risk (2027) | New Asset Total Risk (2028) | New Asset Total Risk (2029) | New Asset Total Risk (2030) | New Asset Total Risk (2031) | New Asset Total Risk (2032) | New Asset Total Risk (2033) | New Asset Total Risk (2034) | New Asset Total Risk (2035) | New Asset Total Risk (2036) | New Asset Total Risk (2037) | New Asset Total Risk (2038) | New Asset Total Risk (2039) | New Asset Total Risk (2040) | New Asset Total Risk (2041) | New Asset Total Risk (2042) | New Asset Total Risk (2043) | New Asset Total Risk (2044) | New Asset Total Risk (2045) | New Asset Total Risk (2046) | New Asset Total Risk (2047) | New Asset Total Risk (2048) | New Asset Total Risk (2049) | New Asset Total Risk (2050) | New Asset Total Risk (2051) | New Asset Total Risk (2052) | New Asset Total Risk (2053) | New Asset Total Risk (2054) |  | Future Opex Risk (2025) | Future Opex Risk (2026) | Future Opex Risk (2027) | Future Opex Risk (2028) | Future Opex Risk (2029) | Future Opex Risk (2030) | Future Opex Risk (2031) | Future Opex Risk (2032) | Future Opex Risk (2033) | Future Opex Risk (2034) | Future Opex Risk (2035) | Future Opex Risk (2036) | Future Opex Risk (2037) | Future Opex Risk (2038) | Future Opex Risk (2039) | Future Opex Risk (2040) | Future Opex Risk (2041) | Future Opex Risk (2042) | Future Opex Risk (2043) | Future Opex Risk (2044) | Future Opex Risk (2045) | Future Opex Risk (2046) | Future Opex Risk (2047) | Future Opex Risk (2048) | Future Opex Risk (2049) | Future Opex Risk (2050) | Future Opex Risk (2051) | Future Opex Risk (2052) | Future Opex Risk (2053) | Future Opex Risk (2054) |  | New Asset Opex Risk (2025) | New Asset Opex Risk (2026) | New Asset Opex Risk (2027) | New Asset Opex Risk (2028) | New Asset Opex Risk (2029) | New Asset Opex Risk (2030) | New Asset Opex Risk (2031) | New Asset Opex Risk (2032) | New Asset Opex Risk (2033) | New Asset Opex Risk (2034) | New Asset Opex Risk (2035) | New Asset Opex Risk (2036) | New Asset Opex Risk (2037) | New Asset Opex Risk (2038) | New Asset Opex Risk (2039) | New Asset Opex Risk (2040) | New Asset Opex Risk (2041) | New Asset Opex Risk (2042) | New Asset Opex Risk (2043) | New Asset Opex Risk (2044) | New Asset Opex Risk (2045) | New Asset Opex Risk (2046) | New Asset Opex Risk (2047) | New Asset Opex Risk (2048) | New Asset Opex Risk (2049) | New Asset Opex Risk (2050) | New Asset Opex Risk (2051) | New Asset Opex Risk (2052) | New Asset Opex Risk (2053) | New Asset Opex Risk (2054) |  | Delta Opex Risk (2025) | Delta Opex Risk (2026) | Delta Opex Risk (2027) | Delta Opex Risk (2028) | Delta Opex Risk (2029) | Delta Opex Risk (2030) | Delta Opex Risk (2031) | Delta Opex Risk (2032) | Delta Opex Risk (2033) | Delta Opex Risk (2034) | Delta Opex Risk (2035) | Delta Opex Risk (2036) | Delta Opex Risk (2037) | Delta Opex Risk (2038) | Delta Opex Risk (2039) | Delta Opex Risk (2040) | Delta Opex Risk (2041) | Delta Opex Risk (2042) | Delta Opex Risk (2043) | Delta Opex Risk (2044) | Delta Opex Risk (2045) | Delta Opex Risk (2046) | Delta Opex Risk (2047) | Delta Opex Risk (2048) | Delta Opex Risk (2049) | Delta Opex Risk (2050) | Delta Opex Risk (2051) | Delta Opex Risk (2052) | Delta Opex Risk (2053) | Delta Opex Risk (2054) |  | Future Capex Risk (2025) | Future Capex Risk (2026) | Future Capex Risk (2027) | Future Capex Risk (2028) | Future Capex Risk (2029) | Future Capex Risk (2030) | Future Capex Risk (2031) | Future Capex Risk (2032) | Future Capex Risk (2033) | Future Capex Risk (2034) | Future Capex Risk (2035) | Future Capex Risk (2036) | Future Capex Risk (2037) | Future Capex Risk (2038) | Future Capex Risk (2039) | Future Capex Risk (2040) | Future Capex Risk (2041) | Future Capex Risk (2042) | Future Capex Risk (2043) | Future Capex Risk (2044) | Future Capex Risk (2045) | Future Capex Risk (2046) | Future Capex Risk (2047) | Future Capex Risk (2048) | Future Capex Risk (2049) | Future Capex Risk (2050) | Future Capex Risk (2051) | Future Capex Risk (2052) | Future Capex Risk (2053) | Future Capex Risk (2054) |  | New Asset Capex Risk (2025) | New Asset Capex Risk (2026) | New Asset Capex Risk (2027) | New Asset Capex Risk (2028) | New Asset Capex Risk (2029) | New Asset Capex Risk (2030) | New Asset Capex Risk (2031) | New Asset Capex Risk (2032) | New Asset Capex Risk (2033) | New Asset Capex Risk (2034) | New Asset Capex Risk (2035) | New Asset Capex Risk (2036) | New Asset Capex Risk (2037) | New Asset Capex Risk (2038) | New Asset Capex Risk (2039) | New Asset Capex Risk (2040) | New Asset Capex Risk (2041) | New Asset Capex Risk (2042) | New Asset Capex Risk (2043) | New Asset Capex Risk (2044) | New Asset Capex Risk (2045) | New Asset Capex Risk (2046) | New Asset Capex Risk (2047) | New Asset Capex Risk (2048) | New Asset Capex Risk (2049) | New Asset Capex Risk (2050) | New Asset Capex Risk (2051) | New Asset Capex Risk (2052) | New Asset Capex Risk (2053) | New Asset Capex Risk (2054) |  | Delta Capex Risk (2025) | Delta Capex Risk (2026) | Delta Capex Risk (2027) | Delta Capex Risk (2028) | Delta Capex Risk (2029) | Delta Capex Risk (2030) | Delta Capex Risk (2031) | Delta Capex Risk (2032) | Delta Capex Risk (2033) | Delta Capex Risk (2034) | Delta Capex Risk (2035) | Delta Capex Risk (2036) | Delta Capex Risk (2037) | Delta Capex Risk (2038) | Delta Capex Risk (2039) | Delta Capex Risk (2040) | Delta Capex Risk (2041) | Delta Capex Risk (2042) | Delta Capex Risk (2043) | Delta Capex Risk (2044) | Delta Capex Risk (2045) | Delta Capex Risk (2046) | Delta Capex Risk (2047) | Delta Capex Risk (2048) | Delta Capex Risk (2049) | Delta Capex Risk (2050) | Delta Capex Risk (2051) | Delta Capex Risk (2052) | Delta Capex Risk (2053) | Delta Capex Risk (2054) |  | Delta Totex Risk (2025) | Delta Totex Risk (2026) | Delta Totex Risk (2027) | Delta Totex Risk (2028) | Delta Totex Risk (2029) | Delta Totex Risk (2030) | Delta Totex Risk (2031) | Delta Totex Risk (2032) | Delta Totex Risk (2033) | Delta Totex Risk (2034) | Delta Totex Risk (2035) | Delta Totex Risk (2036) | Delta Totex Risk (2037) | Delta Totex Risk (2038) | Delta Totex Risk (2039) | Delta Totex Risk (2040) | Delta Totex Risk (2041) | Delta Totex Risk (2042) | Delta Totex Risk (2043) | Delta Totex Risk (2044) | Delta Totex Risk (2045) | Delta Totex Risk (2046) | Delta Totex Risk (2047) | Delta Totex Risk (2048) | Delta Totex Risk (2049) | Delta Totex Risk (2050) | Delta Totex Risk (2051) | Delta Totex Risk (2052) | Delta Totex Risk (2053) | Delta Totex Risk (2054) |  | Future Safety Risk (2025) | Future Safety Risk (2026) | Future Safety Risk (2027) | Future Safety Risk (2028) | Future Safety Risk (2029) | Future Safety Risk (2030) | Future Safety Risk (2031) | Future Safety Risk (2032) | Future Safety Risk (2033) | Future Safety Risk (2034) | Future Safety Risk (2035) | Future Safety Risk (2036) | Future Safety Risk (2037) | Future Safety Risk (2038) | Future Safety Risk (2039) | Future Safety Risk (2040) | Future Safety Risk (2041) | Future Safety Risk (2042) | Future Safety Risk (2043) | Future Safety Risk (2044) | Future Safety Risk (2045) | Future Safety Risk (2046) | Future Safety Risk (2047) | Future Safety Risk (2048) | Future Safety Risk (2049) | Future Safety Risk (2050) | Future Safety Risk (2051) | Future Safety Risk (2052) | Future Safety Risk (2053) | Future Safety Risk (2054) |  | New Asset Safety Risk (2025) | New Asset Safety Risk (2026) | New Asset Safety Risk (2027) | New Asset Safety Risk (2028) | New Asset Safety Risk (2029) | New Asset Safety Risk (2030) | New Asset Safety Risk (2031) | New Asset Safety Risk (2032) | New Asset Safety Risk (2033) | New Asset Safety Risk (2034) | New Asset Safety Risk (2035) | New Asset Safety Risk (2036) | New Asset Safety Risk (2037) | New Asset Safety Risk (2038) | New Asset Safety Risk (2039) | New Asset Safety Risk (2040) | New Asset Safety Risk (2041) | New Asset Safety Risk (2042) | New Asset Safety Risk (2043) | New Asset Safety Risk (2044) | New Asset Safety Risk (2045) | New Asset Safety Risk (2046) | New Asset Safety Risk (2047) | New Asset Safety Risk (2048) | New Asset Safety Risk (2049) | New Asset Safety Risk (2050) | New Asset Safety Risk (2051) | New Asset Safety Risk (2052) | New Asset Safety Risk (2053) | New Asset Safety Risk (2054) |  | Delta Safety Risk (2025) | Delta Safety Risk (2026) | Delta Safety Risk (2027) | Delta Safety Risk (2028) | Delta Safety Risk (2029) | Delta Safety Risk (2030) | Delta Safety Risk (2031) | Delta Safety Risk (2032) | Delta Safety Risk (2033) | Delta Safety Risk (2034) | Delta Safety Risk (2035) | Delta Safety Risk (2036) | Delta Safety Risk (2037) | Delta Safety Risk (2038) | Delta Safety Risk (2039) | Delta Safety Risk (2040) | Delta Safety Risk (2041) | Delta Safety Risk (2042) | Delta Safety Risk (2043) | Delta Safety Risk (2044) | Delta Safety Risk (2045) | Delta Safety Risk (2046) | Delta Safety Risk (2047) | Delta Safety Risk (2048) | Delta Safety Risk (2049) | Delta Safety Risk (2050) | Delta Safety Risk (2051) | Delta Safety Risk (2052) | Delta Safety Risk (2053) | Delta Safety Risk (2054) |  | Future Environment Risk (2025) | Future Environment Risk (2026) | Future Environment Risk (2027) | Future Environment Risk (2028) | Future Environment Risk (2029) | Future Environment Risk (2030) | Future Environment Risk (2031) | Future Environment Risk (2032) | Future Environment Risk (2033) | Future Environment Risk (2034) | Future Environment Risk (2035) | Future Environment Risk (2036) | Future Environment Risk (2037) | Future Environment Risk (2038) | Future Environment Risk (2039) | Future Environment Risk (2040) | Future Environment Risk (2041) | Future Environment Risk (2042) | Future Environment Risk (2043) | Future Environment Risk (2044) | Future Environment Risk (2045) | Future Environment Risk (2046) | Future Environment Risk (2047) | Future Environment Risk (2048) | Future Environment Risk (2049) | Future Environment Risk (2050) | Future Environment Risk (2051) | Future Environment Risk (2052) | Future Environment Risk (2053) | Future Environment Risk (2054) |  | New Asset Environment Risk (2025) | New Asset Environment Risk (2026) | New Asset Environment Risk (2027) | New Asset Environment Risk (2028) | New Asset Environment Risk (2029) | New Asset Environment Risk (2030) | New Asset Environment Risk (2031) | New Asset Environment Risk (2032) | New Asset Environment Risk (2033) | New Asset Environment Risk (2034) | New Asset Environment Risk (2035) | New Asset Environment Risk (2036) | New Asset Environment Risk (2037) | New Asset Environment Risk (2038) | New Asset Environment Risk (2039) | New Asset Environment Risk (2040) | New Asset Environment Risk (2041) | New Asset Environment Risk (2042) | New Asset Environment Risk (2043) | New Asset Environment Risk (2044) | New Asset Environment Risk (2045) | New Asset Environment Risk (2046) | New Asset Environment Risk (2047) | New Asset Environment Risk (2048) | New Asset Environment Risk (2049) | New Asset Environment Risk (2050) | New Asset Environment Risk (2051) | New Asset Environment Risk (2052) | New Asset Environment Risk (2053) | New Asset Environment Risk (2054) |  | Delta Environment Risk (2025) | Delta Environment Risk (2026) | Delta Environment Risk (2027) | Delta Environment Risk (2028) | Delta Environment Risk (2029) | Delta Environment Risk (2030) | Delta Environment Risk (2031) | Delta Environment Risk (2032) | Delta Environment Risk (2033) | Delta Environment Risk (2034) | Delta Environment Risk (2035) | Delta Environment Risk (2036) | Delta Environment Risk (2037) | Delta Environment Risk (2038) | Delta Environment Risk (2039) | Delta Environment Risk (2040) | Delta Environment Risk (2041) | Delta Environment Risk (2042) | Delta Environment Risk (2043) | Delta Environment Risk (2044) | Delta Environment Risk (2045) | Delta Environment Risk (2046) | Delta Environment Risk (2047) | Delta Environment Risk (2048) | Delta Environment Risk (2049) | Delta Environment Risk (2050) | Delta Environment Risk (2051) | Delta Environment Risk (2052) | Delta Environment Risk (2053) | Delta Environment Risk (2054) |  | Future NP Risk (2025) | Future NP Risk (2026) | Future NP Risk (2027) | Future NP Risk (2028) | Future NP Risk (2029) | Future NP Risk (2030) | Future NP Risk (2031) | Future NP Risk (2032) | Future NP Risk (2033) | Future NP Risk (2034) | Future NP Risk (2035) | Future NP Risk (2036) | Future NP Risk (2037) | Future NP Risk (2038) | Future NP Risk (2039) | Future NP Risk (2040) | Future NP Risk (2041) | Future NP Risk (2042) | Future NP Risk (2043) | Future NP Risk (2044) | Future NP Risk (2045) | Future NP Risk (2046) | Future NP Risk (2047) | Future NP Risk (2048) | Future NP Risk (2049) | Future NP Risk (2050) | Future NP Risk (2051) | Future NP Risk (2052) | Future NP Risk (2053) | Future NP Risk (2054) |  | New Asset NP Risk (2025) | New Asset NP Risk (2026) | New Asset NP Risk (2027) | New Asset NP Risk (2028) | New Asset NP Risk (2029) | New Asset NP Risk (2030) | New Asset NP Risk (2031) | New Asset NP Risk (2032) | New Asset NP Risk (2033) | New Asset NP Risk (2034) | New Asset NP Risk (2035) | New Asset NP Risk (2036) | New Asset NP Risk (2037) | New Asset NP Risk (2038) | New Asset NP Risk (2039) | New Asset NP Risk (2040) | New Asset NP Risk (2041) | New Asset NP Risk (2042) | New Asset NP Risk (2043) | New Asset NP Risk (2044) | New Asset NP Risk (2045) | New Asset NP Risk (2046) | New Asset NP Risk (2047) | New Asset NP Risk (2048) | New Asset NP Risk (2049) | New Asset NP Risk (2050) | New Asset NP Risk (2051) | New Asset NP Risk (2052) | New Asset NP Risk (2053) | New Asset NP Risk (2054) |  | Delta NP Risk (2025) | Delta NP Risk (2026) | Delta NP Risk (2027) | Delta NP Risk (2028) | Delta NP Risk (2029) | Delta NP Risk (2030) | Delta NP Risk (2031) | Delta NP Risk (2032) | Delta NP Risk (2033) | Delta NP Risk (2034) | Delta NP Risk (2035) | Delta NP Risk (2036) | Delta NP Risk (2037) | Delta NP Risk (2038) | Delta NP Risk (2039) | Delta NP Risk (2040) | Delta NP Risk (2041) | Delta NP Risk (2042) | Delta NP Risk (2043) | Delta NP Risk (2044) | Delta NP Risk (2045) | Delta NP Risk (2046) | Delta NP Risk (2047) | Delta NP Risk (2048) | Delta NP Risk (2049) | Delta NP Risk (2050) | Delta NP Risk (2051) | Delta NP Risk (2052) | Delta NP Risk (2053) | Delta NP Risk (2054) |  | Delta Risk (2025) | Delta Risk (2026) | Delta Risk (2027) | Delta Risk (2028) | Delta Risk (2029) | Delta Risk (2030) | Delta Risk (2031) | Delta Risk (2032) | Delta Risk (2033) | Delta Risk (2034) | Delta Risk (2035) | Delta Risk (2036) | Delta Risk (2037) | Delta Risk (2038) | Delta Risk (2039) | Delta Risk (2040) | Delta Risk (2041) | Delta Risk (2042) | Delta Risk (2043) | Delta Risk (2044) | Delta Risk (2045) | Delta Risk (2046) | Delta Risk (2047) | Delta Risk (2048) | Delta Risk (2049) | Delta Risk (2050) | Delta Risk (2051) | Delta Risk (2052) | Delta Risk (2053) | Delta Risk (2054)
|  | Asset Index | Asset ID 1 | Asset ID 2 | Asset ID 3 | Asset Description 1 | Asset Description 2 | Asset Description 3 | Asset Description 4 | Asset Description 5 | Asset Description 6 | Asset Description 7 | Asset Description 8 | Relay Type | Blank 1 | Demand Dist | Time Between Inspections Used | Blank 2 | Current HI | Current PoF | Y0 POF Cons | Y0 POF No Cons | Current Financial Risk OPEX | Current Financial Risk CAPEX | Current Financial Risk TOTEX | Current Safety Risk | Current Environmental Risk | Current Network Performance Risk | Blank 22 | Future HI | Future PoF | YN POF Cons | YN POF No Cons | Future Financial Risk OPEX | Future Financial Risk CAPEX | Future Financial Risk TOTEX | Future Safety Risk | Future Environmental Risk | Future Network Performance Risk | Blank 3 | New PoF | NEW POF Cons | NEW POF No Cons | New Financial Risk OPEX | New Financial Risk CAPEX | New Financial Risk TOTEX | New Safety Risk | New Environmental Risk | New Network Performance Risk | Blank 4 | Current Total Risk | Future Total Risk | New Total Risk | Delta Risk | Column1 | Forecast Ageing Rate | Column3 | Health Index FY1 | Health Index FY2 | Health Index FY3 | Health Index FY4 | Health Index FY5 | Health Index FY6 | Health Index FY7 | Health Index FY8 | Health Index FY9 | Health Index FY10 | Health Index FY11 | Health Index FY12 | Health Index FY13 | Health Index FY14 | Health Index FY15 | Health Index FY16 | Health Index FY17 | Health Index FY18 | Health Index FY19 | Health Index FY20 | Health Index FY21 | Health Index FY22 | Health Index FY23 | Health Index FY24 | Health Index FY25 | Health Index FY26 | Health Index FY27 | Health Index FY28 | Health Index FY29 | Health Index FY30 | Delta Risk22 | PoF FY1 | PoF FY2 | PoF FY3 | PoF FY4 | PoF FY5 | PoF FY6 | PoF FY7 | PoF FY8 | PoF FY9 | PoF FY10 | PoF FY11 | PoF FY12 | PoF FY13 | PoF FY14 | PoF FY15 | PoF FY16 | PoF FY17 | PoF FY18 | PoF FY19 | PoF FY20 | PoF FY21 | PoF FY22 | PoF FY23 | PoF FY24 | PoF FY25 | PoF FY26 | PoF FY27 | PoF FY28 | PoF FY29 | PoF FY30 | Column2 | NP POF FY1 | NP POF FY2 | NP POF FY3 | NP POF FY4 | NP POF FY5 | NP POF FY6 | NP POF FY7 | NP POF FY8 | NP POF FY9 | NP POF FY10 | NP POF FY11 | NP POF FY12 | NP POF FY13 | NP POF FY14 | NP POF FY15 | NP POF FY16 | NP POF FY17 | NP POF FY18 | NP POF FY19 | NP POF FY20 | NP POF FY21 | NP POF FY22 | NP POF FY23 | NP POF FY24 | NP POF FY25 | NP POF FY26 | NP POF FY27 | NP POF FY28 | NP POF FY29 | NP POF FY30 | [63 empty] | Future Future Opex Risk (2026) | Future Future Opex Risk (2027) | Future Future Opex Risk (2028) | Future Future Opex Risk (2029) | Future Future Opex Risk (2030) | Future Future Opex Risk (2031) | Future Future Opex Risk (2032) | Future Future Opex Risk (2033) | Future Future Opex Risk (2034) | Future Future Opex Risk (2035) | Future Future Opex Risk (2036) | Future Future Opex Risk (2037) | Future Future Opex Risk (2038) | Future Future Opex Risk (2039) | Future Future Opex Risk (2040) | Future Future Opex Risk (2041) | Future Future Opex Risk (2042) | Future Future Opex Risk (2043) | Future Future Opex Risk (2044) | Future Future Opex Risk (2045) | Future Future Opex Risk (2046) | Future Future Opex Risk (2047) | Future Future Opex Risk (2048) | Future Future Opex Risk (2049) | Future Future Opex Risk (2050) | Future Future Opex Risk (2051) | Future Future Opex Risk (2052) | Future Future Opex Risk (2053) | Future Future Opex Risk (2054) | Delta Risk107 | New Asset Opex Risk FY1 | New Asset Opex Risk FY2 | New Asset Opex Risk FY3 | New Asset Opex Risk FY4 | New Asset Opex Risk FY5 | New Asset Opex Risk FY6 | New Asset Opex Risk FY7 | New Asset Opex Risk FY8 | New Asset Opex Risk FY9 | New Asset Opex Risk FY10 | New Asset Opex Risk FY11 | New Asset Opex Risk FY12 | New Asset Opex Risk FY13 | New Asset Opex Risk FY14 | New Asset Opex Risk FY15 | New Asset Opex Risk FY16 | New Asset Opex Risk FY17 | New Asset Opex Risk FY18 | New Asset Opex Risk FY19 | New Asset Opex Risk FY20 | New Asset Opex Risk FY21 | New Asset Opex Risk FY22 | New Asset Opex Risk FY23 | New Asset Opex Risk FY24 | New Asset Opex Risk FY25 | New Asset Opex Risk FY26 | New Asset Opex Risk FY27 | New Asset Opex Risk FY28 | New Asset Opex Risk FY29 | New Asset Opex Risk FY30 | Delta Risk126 | Delta Opex Risk FY1 | Delta Opex Risk FY2 | Delta Opex Risk FY3 | Delta Opex Risk FY4 | Delta Opex Risk FY5 | Delta Opex Risk FY6 | Delta Opex Risk FY7 | Delta Opex Risk FY8 | Delta Opex Risk FY9 | Delta Opex Risk FY10 | Delta Opex Risk FY11 | Delta Opex Risk FY12 | Delta Opex Risk FY13 | Delta Opex Risk FY14 | Delta Opex Risk FY15 | Delta Opex Risk FY16 | Delta Opex Risk FY17 | Delta Opex Risk FY18 | Delta Opex Risk FY19 | Delta Opex Risk FY20 | Delta Opex Risk FY21 | Delta Opex Risk FY22 | Delta Opex Risk FY23 | Delta Opex Risk FY24 | Delta Opex Risk FY25 | Delta Opex Risk FY26 | Delta Opex Risk FY27 | Delta Opex Risk FY28 | Delta Opex Risk FY29 | Delta Opex Risk FY30 | NewRisk FY21 | Future Capex Risk FY1 | Future Capex Risk FY2 | Future Capex Risk FY3 | Future Capex Risk FY4 | Future Capex Risk FY5 | Future Capex Risk FY6 | Future Capex Risk FY7 | Future Capex Risk FY8 | Future Capex Risk FY9 | Future Capex Risk FY10 | Future Capex Risk FY11 | Future Capex Risk FY12 | Future Capex Risk FY13 | Future Capex Risk FY14 | Future Capex Risk FY15 | Future Capex Risk FY16 | Future Capex Risk FY17 | Future Capex Risk FY18 | Future Capex Risk FY19 | Future Capex Risk FY20 | Future Capex Risk FY21 | Future Capex Risk FY22 | Future Capex Risk FY23 | Future Capex Risk FY24 | Future Capex Risk FY25 | Future Capex Risk FY26 | Future Capex Risk FY27 | Future Capex Risk FY28 | Future Capex Risk FY29 | Future Capex Risk FY30 | NewRisk FY2312 | New Asset Capex Risk FY1 | New Asset Capex Risk FY2 | New Asset Capex Risk FY3 | New Asset Capex Risk FY4 | New Asset Capex Risk FY5 | New Asset Capex Risk FY6 | New Asset Capex Risk FY7 | New Asset Capex Risk FY8 | New Asset Capex Risk FY9 | New Asset Capex Risk FY10 | New Asset Capex Risk FY11 | New Asset Capex Risk FY12 | New Asset Capex Risk FY13 | New Asset Capex Risk FY14 | New Asset Capex Risk FY15 | New Asset Capex Risk FY16 | New Asset Capex Risk FY17 | New Asset Capex Risk FY18 | New Asset Capex Risk FY19 | New Asset Capex Risk FY20 | New Asset Capex Risk FY21 | New Asset Capex Risk FY22 | New Asset Capex Risk FY23 | New Asset Capex Risk FY24 | New Asset Capex Risk FY25 | New Asset Capex Risk FY26 | New Asset Capex Risk FY27 | New Asset Capex Risk FY28 | New Asset Capex Risk FY29 | New Asset Capex Risk FY30 | NewRisk FY41 | Delta Capex Risk FY1 | Delta Capex Risk FY2 | Delta Capex Risk FY3 | Delta Capex Risk FY4 | Delta Capex Risk FY5 | Delta Capex Risk FY6 | Delta Capex Risk FY7 | Delta Capex Risk FY8 | Delta Capex Risk FY9 | Delta Capex Risk FY10 | Delta Capex Risk FY11 | Delta Capex Risk FY12 | Delta Capex Risk FY13 | Delta Capex Risk FY14 | Delta Capex Risk FY15 | Delta Capex Risk FY16 | Delta Capex Risk FY17 | Delta Capex Risk FY18 | Delta Capex Risk FY19 | Delta Capex Risk FY20 | Delta Capex Risk FY21 | Delta Capex Risk FY22 | Delta Capex Risk FY23 | Delta Capex Risk FY24 | Delta Capex Risk FY25 | Delta Capex Risk FY26 | Delta Capex Risk FY27 | Delta Capex Risk FY28 | Delta Capex Risk FY29 | Delta Capex Risk FY30 | Column8 | Delta Totex Risk FY1 | Delta Totex Risk FY2 | Delta Totex Risk FY3 | Delta Totex Risk FY4 | Delta Totex Risk FY5 | Delta Totex Risk FY6 | Delta Totex Risk FY7 | Delta Totex Risk FY8 | Delta Totex Risk FY9 | Delta Totex Risk FY10 | Delta Totex Risk FY11 | Delta Totex Risk FY12 | Delta Totex Risk FY13 | Delta Totex Risk FY14 | Delta Totex Risk FY15 | Delta Totex Risk FY16 | Delta Totex Risk FY17 | Delta Totex Risk FY18 | Delta Totex Risk FY19 | Delta Totex Risk FY20 | Delta Totex Risk FY21 | Delta Totex Risk FY22 | Delta Totex Risk FY23 | Delta Totex Risk FY24 | Delta Totex Risk FY25 | Delta Totex Risk FY26 | Delta Totex Risk FY27 | Delta Totex Risk FY28 | Delta Totex Risk FY29 | Delta Totex Risk FY30 | Delta Totex Risk FY212 | Future Safety Risk FY1 | Future Safety Risk FY2 | Future Safety Risk FY3 | Future Safety Risk FY4 | Future Safety Risk FY5 | Future Safety Risk FY6 | Future Safety Risk FY7 | Future Safety Risk FY8 | Future Safety Risk FY9 | Future Safety Risk FY10 | Future Safety Risk FY11 | Future Safety Risk FY12 | Future Safety Risk FY13 | Future Safety Risk FY14 | Future Safety Risk FY15 | Future Safety Risk FY16 | Future Safety Risk FY17 | Future Safety Risk FY18 | Future Safety Risk FY19 | Future Safety Risk FY20 | Future Safety Risk FY21 | Future Safety Risk FY22 | Future Safety Risk FY23 | Future Safety Risk FY24 | Future Safety Risk FY25 | Future Safety Risk FY26 | Future Safety Risk FY27 | Future Safety Risk FY28 | Future Safety Risk FY29 | Future Safety Risk FY30 | Column5 | New Asset Safety Risk FY1 | New Asset Safety Risk FY2 | New Asset Safety Risk FY3 | New Asset Safety Risk FY4 | New Asset Safety Risk FY5 | New Asset Safety Risk FY6 | New Asset Safety Risk FY7 | New Asset Safety Risk FY8 | New Asset Safety Risk FY9 | New Asset Safety Risk FY10 | New Asset Safety Risk FY11 | New Asset Safety Risk FY12 | New Asset Safety Risk FY13 | New Asset Safety Risk FY14 | New Asset Safety Risk FY15 | New Asset Safety Risk FY16 | New Asset Safety Risk FY17 | New Asset Safety Risk FY18 | New Asset Safety Risk FY19 | New Asset Safety Risk FY20 | New Asset Safety Risk FY21 | New Asset Safety Risk FY22 | New Asset Safety Risk FY23 | New Asset Safety Risk FY24 | New Asset Safety Risk FY25 | New Asset Safety Risk FY26 | New Asset Safety Risk FY27 | New Asset Safety Risk FY28 | New Asset Safety Risk FY29 | New Asset Safety Risk FY30 | Delta Risk FY42 | Delta Safety Risk FY1 | Delta Safety Risk FY2 | Delta Safety Risk FY3 | Delta Safety Risk FY4 | Delta Safety Risk FY5 | Delta Safety Risk FY6 | Delta Safety Risk FY7 | Delta Safety Risk FY8 | Delta Safety Risk FY9 | Delta Safety Risk FY10 | Delta Safety Risk FY11 | Delta Safety Risk FY12 | Delta Safety Risk FY13 | Delta Safety Risk FY14 | Delta Safety Risk FY15 | Delta Safety Risk FY16 | Delta Safety Risk FY17 | Delta Safety Risk FY18 | Delta Safety Risk FY19 | Delta Safety Risk FY20 | Delta Safety Risk FY21 | Delta Safety Risk FY22 | Delta Safety Risk FY23 | Delta Safety Risk FY24 | Delta Safety Risk FY25 | Delta Safety Risk FY26 | Delta Safety Risk FY27 | Delta Safety Risk FY28 | Delta Safety Risk FY29 | Delta Safety Risk FY30 | Delta Safety Risk FY2010 | Future Environment Risk FY1 | Future Environment Risk FY2 | Future Environment Risk FY3 | Future Environment Risk FY4 | Future Environment Risk FY5 | Future Environment Risk FY6 | Future Environment Risk FY7 | Future Environment Risk FY8 | Future Environment Risk FY9 | Future Environment Risk FY10 | Future Environment Risk FY11 | Future Environment Risk FY12 | Future Environment Risk FY13 | Future Environment Risk FY14 | Future Environment Risk FY15 | Future Environment Risk FY16 | Future Environment Risk FY17 | Future Environment Risk FY18 | Future Environment Risk FY19 | Future Environment Risk FY20 | Future Environment Risk FY21 | Future Environment Risk FY22 | Future Environment Risk FY23 | Future Environment Risk FY24 | Future Environment Risk FY25 | Future Environment Risk FY26 | Future Environment Risk FY27 | Future Environment Risk FY28 | Future Environment Risk FY29 | Future Environment Risk FY30 | Delta Safety Risk FY212 | New Asset Environment Risk FY1 | New Asset Environment Risk FY2 | New Asset Environment Risk FY3 | New Asset Environment Risk FY4 | New Asset Environment Risk FY5 | New Asset Environment Risk FY6 | New Asset Environment Risk FY7 | New Asset Environment Risk FY8 | New Asset Environment Risk FY9 | New Asset Environment Risk FY10 | New Asset Environment Risk FY11 | New Asset Environment Risk FY12 | New Asset Environment Risk FY13 | New Asset Environment Risk FY14 | New Asset Environment Risk FY15 | New Asset Environment Risk FY16 | New Asset Environment Risk FY17 | New Asset Environment Risk FY18 | New Asset Environment Risk FY19 | New Asset Environment Risk FY20 | New Asset Environment Risk FY21 | New Asset Environment Risk FY22 | New Asset Environment Risk FY23 | New Asset Environment Risk FY24 | New Asset Environment Risk FY25 | New Asset Environment Risk FY26 | New Asset Environment Risk FY27 | New Asset Environment Risk FY28 | New Asset Environment Risk FY29 | New Asset Environment Risk FY30 | Column4 | Delta Environment Risk FY1 | Delta Environment Risk FY2 | Delta Environment Risk FY3 | Delta Environment Risk FY4 | Delta Environment Risk FY5 | Delta Environment Risk FY6 | Delta Environment Risk FY7 | Delta Environment Risk FY8 | Delta Environment Risk FY9 | Delta Environment Risk FY10 | Delta Environment Risk FY11 | Delta Environment Risk FY12 | Delta Environment Risk FY13 | Delta Environment Risk FY14 | Delta Environment Risk FY15 | Delta Environment Risk FY16 | Delta Environment Risk FY17 | Delta Environment Risk FY18 | Delta Environment Risk FY19 | Delta Environment Risk FY20 | Delta Environment Risk FY21 | Delta Environment Risk FY22 | Delta Environment Risk FY23 | Delta Environment Risk FY24 | Delta Environment Risk FY25 | Delta Environment Risk FY26 | Delta Environment Risk FY27 | Delta Environment Risk FY28 | Delta Environment Risk FY29 | Delta Environment Risk FY30 | Delta Risk FY44 | Future NP Risk FY1 | Future NP Risk FY2 | Future NP Risk FY3 | Future NP Risk FY4 | Future NP Risk FY5 | Future NP Risk FY6 | Future NP Risk FY7 | Future NP Risk FY8 | Future NP Risk FY9 | Future NP Risk FY10 | Future NP Risk FY11 | Future NP Risk FY12 | Future NP Risk FY13 | Future NP Risk FY14 | Future NP Risk FY15 | Future NP Risk FY16 | Future NP Risk FY17 | Future NP Risk FY18 | Future NP Risk FY19 | Future NP Risk FY20 | Future NP Risk FY21 | Future NP Risk FY22 | Future NP Risk FY23 | Future NP Risk FY24 | Future NP Risk FY25 | Future NP Risk FY26 | Future NP Risk FY27 | Future NP Risk FY28 | Future NP Risk FY29 | Future NP Risk FY30 | Column6 | New Asset NP Risk FY1 | New Asset NP Risk FY2 | New Asset NP Risk FY3 | New Asset NP Risk FY4 | New Asset NP Risk FY5 | New Asset NP Risk FY6 | New Asset NP Risk FY7 | New Asset NP Risk FY8 | New Asset NP Risk FY9 | New Asset NP Risk FY10 | New Asset NP Risk FY11 | New Asset NP Risk FY12 | New Asset NP Risk FY13 | New Asset NP Risk FY14 | New Asset NP Risk FY15 | New Asset NP Risk FY16 | New Asset NP Risk FY17 | New Asset NP Risk FY18 | New Asset NP Risk FY19 | New Asset NP Risk FY20 | New Asset NP Risk FY21 | New Asset NP Risk FY22 | New Asset NP Risk FY23 | New Asset NP Risk FY24 | New Asset NP Risk FY25 | New Asset NP Risk FY26 | New Asset NP Risk FY27 | New Asset NP Risk FY28 | New Asset NP Risk FY29 | New Asset NP Risk FY30 | Delta Risk FY480 | Delta NP Risk FY1 | Delta NP Risk FY2 | Delta NP Risk FY3 | Delta NP Risk FY4 | Delta NP Risk FY5 | Delta NP Risk FY6 | Delta NP Risk FY7 | Delta NP Risk FY8 | Delta NP Risk FY9 | Delta NP Risk FY10 | Delta NP Risk FY11 | Delta NP Risk FY12 | Delta NP Risk FY13 | Delta NP Risk FY14 | Delta NP Risk FY15 | Delta NP Risk FY16 | Delta NP Risk FY17 | Delta NP Risk FY18 | Delta NP Risk FY19 | Delta NP Risk FY20 | Delta NP Risk FY21 | Delta NP Risk FY22 | Delta NP Risk FY23 | Delta NP Risk FY24 | Delta NP Risk FY25 | Delta NP Risk FY26 | Delta NP Risk FY27 | Delta NP Risk FY28 | Delta NP Risk FY29 | Delta NP Risk FY30 | Column7 | Delta Risk FY1 | Delta Risk FY2 | Delta Risk FY3 | Delta Risk FY4 | Delta Risk FY5 | Delta Risk FY6 | Delta Risk FY7 | Delta Risk FY8 | Delta Risk FY9 | Delta Risk FY10 | Delta Risk FY11 | Delta Risk FY12 | Delta Risk FY13 | Delta Risk FY14 | Delta Risk FY15 | Delta Risk FY16 | Delta Risk FY17 | Delta Risk FY18 | Delta Risk FY19 | Delta Risk FY20 | Delta Risk FY212 | Delta Risk FY22 | Delta Risk FY23 | Delta Risk FY24 | Delta Risk FY25 | Delta Risk FY26 | Delta Risk FY27 | Delta Risk FY28 | Delta Risk FY29 | Delta Risk FY30
| TRUE | 1 | 22009788 | AC | Blank | 11 | BUS ALL | VRR NO. 1 | C | RMS | 2V164S | 2V164 S | 2V164S | Digital |  | 0 | 1 |  | 3.0201 | 0.0051679 | 0 | 0.0051679 | 15.633 | 0 | 15.633 | 14.6698 | 2.0677 | 0 |  | 8.5997 | 0.034485 | 0 | 0.034485 | 104.3178 | 0 | 104.3178 | 97.8903 | 13.7975 | 0 |  | 0.0051679 | 0 | 0.0051679 | 15.633 | 0 | 15.633 | 14.6698 | 2.0677 | 0 |  | 32.3705 | 216.0057 | 32.3705 | 183.6352 |  | 0.10465 |  | 3.3532 | 3.7231 | 4.1339 | 4.5899 | 5.0962 | 5.6584 | 6.2827 | 6.9757 | 7.7453 | 8.5997 | 9.5484 | 10.6018 | 11.7713 | 13.0699 | 14.5117 | 16.1126 | 17.8901 | 19.8637 | 22.055 | 24.4881 | 27.1895 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0055688 | 0.0070961 | 0.0091055 | 0.011759 | 0.015274 | 0.019945 | 0.026169 | 0.034485 | 0.045621 | 0.060565 | 0.080656 | 0.10772 | 0.14422 | 0.19354 | 0.26025 | 0.35058 | 0.47305 | 0.63924 | 0.86494 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.3705 | 32.3705 | 34.8813 | 44.4481 | 57.0346 | 73.6538 | 95.671 | 124.9289 | 163.9175 | 216.0057 | 285.7572 | 379.3592 | 505.209 | 674.7114 | 903.3686 | 1212.2662 | 1630.1014 | 2195.9527 | 2963.0625 | 4004.0031 | 5417.7356 | 5898.9176 | 5898.9176 | 5898.9176 | 5898.9176 | 5898.9176 | 5898.9176 | 5898.9176 | 5898.9176 | 5898.9176 |  | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 38.7454 | 51.3594 | 68.6744 | 92.5498 | 125.6055 | 171.5406 | 235.5857 | 325.1474 | 450.7278 | 627.2344 | 875.8505 | 1226.7042 | 1722.6811 |  | 15.633 | 15.633 | 16.8456 | 21.4658 | 27.5443 | 35.5704 | 46.2034 | 60.3332 | 79.1623 | 104.3178 | 138.0036 | 183.2078 | 243.9857 | 325.8452 | 436.273 | 585.452 | 787.2414 | 1060.5137 | 1430.9819 | 1933.6939 | 2616.4421 | 2848.8242 | 2848.8242 | 2848.8242 | 2848.8242 | 2848.8242 | 2848.8242 | 2848.8242 | 2848.8242 | 2848.8242 |  | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 18.7117 | 24.8035 | 33.1656 | 44.696 | 60.66 | 82.8439 | 113.7738 | 157.0267 | 217.6746 | 302.9167 | 422.9834 | 592.4247 | 831.9519 |  | 0 | 0 | 1.2126 | 5.8328 | 11.9113 | 19.9374 | 30.5704 | 44.7002 | 63.5293 | 88.6848 | 122.3706 | 167.5748 | 228.3527 | 310.2122 | 420.64 | 569.819 | 771.6084 | 1041.802 | 1406.1784 | 1900.5283 | 2571.7461 | 2788.1643 | 2765.9804 | 2735.0504 | 2691.7975 | 2631.1497 | 2545.9075 | 2425.8408 | 2256.3995 | 2016.8723 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1.2126 | 5.8328 | 11.9113 | 19.9374 | 30.5704 | 44.7002 | 63.5293 | 88.6848 | 122.3706 | 167.5748 | 228.3527 | 310.2122 | 420.64 | 569.819 | 771.6084 | 1041.802 | 1406.1784 | 1900.5283 | 2571.7461 | 2788.1643 | 2765.9804 | 2735.0504 | 2691.7975 | 2631.1497 | 2545.9075 | 2425.8408 | 2256.3995 | 2016.8723 |  | 14.6698 | 14.6698 | 15.8077 | 20.1432 | 25.8471 | 33.3787 | 43.3566 | 56.6158 | 74.2848 | 97.8903 | 129.5006 | 171.9195 | 228.9526 | 305.7684 | 409.3922 | 549.3797 | 738.7359 | 995.1707 | 1342.8126 | 1814.5502 | 2455.2312 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 1.1379 | 5.4734 | 11.1774 | 18.7089 | 28.6868 | 41.946 | 59.615 | 83.2206 | 114.8308 | 157.2498 | 214.2828 | 291.0986 | 394.7224 | 534.7099 | 724.0661 | 977.6119 | 1319.5373 | 1783.4281 | 2413.2891 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.2281 | 2.8392 | 3.6431 | 4.7047 | 6.1111 | 7.9799 | 10.4704 | 13.7975 | 18.253 | 24.2319 | 32.2706 | 43.0977 | 57.7034 | 77.4345 | 104.1241 | 140.2683 | 189.2681 | 255.759 | 346.0623 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0.16038 | 0.77147 | 1.5754 | 2.637 | 4.0434 | 5.9122 | 8.4027 | 11.7299 | 16.1853 | 22.1642 | 30.2029 | 41.0301 | 55.6357 | 75.3668 | 102.0564 | 137.7934 | 185.9874 | 251.3723 | 340.1506 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2.5108 | 12.0776 | 24.6641 | 41.2833 | 63.3006 | 92.5584 | 131.547 | 183.6352 | 253.3867 | 346.9887 | 472.8385 | 642.3409 | 870.9981 | 1179.8957 | 1597.7309 | 2157.2073 | 2911.7032 | 3935.3287 | 5325.1858 | 5773.3121 | 5727.377 | 5663.332 | 5573.7702 | 5448.1898 | 5271.6832 | 5023.0672 | 4672.2135 | 4176.2365
| TRUE | 2 | 22003593 | AC | Blank | 11 | BUS ALL | OV-UV SUPERVISION | C | EMAIL | GROUP_3066 | GROUP 3066 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 258.8921 | 0 | 258.8921 | 121.4703 | 17.1211 | 0 |  | 16.4925 | 0.17586 | 0 | 0.17586 | 1063.9786 | 0 | 1063.9786 | 499.211 | 70.3633 | 0 |  | 0.0051679 | 0 | 0.0051679 | 31.266 | 0 | 31.266 | 14.6698 | 2.0677 | 0 |  | 397.4835 | 1633.5529 | 48.0035 | 1585.5494 |  | 0.051037 |  | 10.4184 | 10.9639 | 11.538 | 12.1422 | 12.778 | 13.447 | 14.1511 | 14.8921 | 15.6719 | 16.4925 | 17.3561 | 18.2649 | 19.2213 | 20.2278 | 21.287 | 22.4016 | 23.5746 | 24.809 | 26.108 | 27.4751 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049141 | 0.056475 | 0.06495 | 0.074748 | 0.086081 | 0.099192 | 0.11437 | 0.13194 | 0.15229 | 0.17586 | 0.20319 | 0.23486 | 0.27158 | 0.31417 | 0.36358 | 0.42091 | 0.48745 | 0.5647 | 0.65438 | 0.75852 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 456.4562 | 524.5779 | 603.3019 | 694.3158 | 799.5797 | 921.3702 | 1062.3322 | 1225.539 | 1414.5623 | 1633.5529 | 1887.3363 | 2181.5223 | 2522.6334 | 2918.2547 | 3377.2069 | 3909.75 | 4527.818 | 5245.2943 | 6078.3312 | 7045.7224 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 |  | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 38.7454 | 51.3594 | 68.6744 | 92.5498 | 125.6055 | 171.5406 | 235.5857 | 325.1474 | 450.7278 | 627.2344 | 875.8505 | 1226.7042 | 1722.6811 |  | 297.3027 | 341.6722 | 392.9474 | 452.2273 | 520.7886 | 600.1141 | 691.9266 | 798.2278 | 921.3439 | 1063.9786 | 1229.2748 | 1420.8863 | 1643.0616 | 1900.7407 | 2199.6691 | 2546.5293 | 2949.0942 | 3416.4066 | 3958.9868 | 4589.0756 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 |  | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 18.7117 | 24.8035 | 33.1656 | 44.696 | 60.66 | 82.8439 | 113.7738 | 157.0267 | 217.6746 | 302.9167 | 422.9834 | 592.4247 | 831.9519 |  | 281.6697 | 326.0392 | 377.3144 | 436.5943 | 505.1556 | 584.4811 | 676.2936 | 782.5948 | 905.7109 | 1048.3456 | 1213.6418 | 1405.2533 | 1627.4286 | 1885.1077 | 2184.0361 | 2530.8963 | 2933.4612 | 3397.6948 | 3934.1833 | 4555.91 | 4803.0355 | 4787.0716 | 4764.8877 | 4733.9578 | 4690.7048 | 4630.057 | 4544.8149 | 4424.7482 | 4255.3068 | 4015.7797 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 281.6697 | 326.0392 | 377.3144 | 436.5943 | 505.1556 | 584.4811 | 676.2936 | 782.5948 | 905.7109 | 1048.3456 | 1213.6418 | 1405.2533 | 1627.4286 | 1885.1077 | 2184.0361 | 2530.8963 | 2933.4612 | 3397.6948 | 3934.1833 | 4555.91 | 4803.0355 | 4787.0716 | 4764.8877 | 4733.9578 | 4690.7048 | 4630.057 | 4544.8149 | 4424.7482 | 4255.3068 | 4015.7797 |  | 139.4923 | 160.3101 | 184.368 | 212.1818 | 244.3502 | 281.5692 | 324.6469 | 374.5227 | 432.2878 | 499.211 | 576.7668 | 666.6695 | 770.9125 | 891.8137 | 1032.0688 | 1194.813 | 1383.6936 | 1602.9531 | 1857.5278 | 2153.1609 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 124.8225 | 145.6403 | 169.6983 | 197.512 | 229.6804 | 266.8994 | 309.9771 | 359.8529 | 417.6181 | 484.5412 | 562.097 | 651.9998 | 756.2428 | 877.1439 | 1017.399 | 1180.1432 | 1369.0238 | 1585.3943 | 1834.2526 | 2122.0388 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 19.6613 | 22.5955 | 25.9865 | 29.9068 | 34.4409 | 39.6869 | 45.7586 | 52.7886 | 60.9305 | 70.3633 | 81.2947 | 93.9664 | 108.6593 | 125.7002 | 145.469 | 168.4077 | 195.0302 | 225.9346 | 261.8166 | 303.4858 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 17.5936 | 20.5279 | 23.9188 | 27.8391 | 32.3732 | 37.6192 | 43.691 | 50.7209 | 58.8628 | 68.2956 | 79.227 | 91.8987 | 106.5916 | 123.6325 | 143.4013 | 166.34 | 192.9625 | 223.4597 | 258.536 | 299.0992 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 424.0857 | 492.2074 | 570.9314 | 661.9453 | 767.2092 | 888.9997 | 1029.9617 | 1193.1686 | 1382.1918 | 1601.1824 | 1854.9658 | 2149.1518 | 2490.263 | 2885.8842 | 3344.8365 | 3877.3795 | 4495.4475 | 5206.5488 | 6026.9718 | 6977.0479 | 7350.2935 | 7317.2377 | 7271.3026 | 7207.2576 | 7117.6959 | 6992.1155 | 6815.6088 | 6566.9928 | 6216.1391 | 5720.1622
| TRUE | 3 | 22003649 | AC | Blank | 11 | BUS NO.2 | OVERCURRENT | Y | ASEA | GROUP_2602 | GROUP 2602 | GROUP 2000s | Electronic |  | 0.0034106 | 2190 |  | 8.25 | 0.026286 | 0.00026713 | 0.026018 | 159.1896 | 82.2745 | 241.4641 | 76.1313 | 10.5195 | 0.24307 |  | 13.322 | 0.096648 | 0.00098218 | 0.095666 | 585.3148 | 302.5103 | 887.8251 | 279.9227 | 38.6787 | 0.89373 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 31.266 | 0.0074366 | 31.2735 | 14.6699 | 2.0677 | 2.1971e-05 |  | 328.358 | 1207.3202 | 48.0111 | 1159.3091 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00030329 | 0.00034464 | 0.00039192 | 0.00044602 | 0.00050794 | 0.00057885 | 0.00066007 | 0.00075314 | 0.00085983 | 0.00098218 | 0.0011225 | 0.0012835 | 0.0014683 | 0.0016805 | 0.0019242 | 0.002204 | 0.0025256 | 0.0028951 | 0.0033198 | 0.0038081 | 0.0043696 | 0.0050154 | 0.0057583 | 0.006613 | 0.0075965 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 372.8169 | 423.6388 | 481.7609 | 548.2607 | 624.3771 | 711.5356 | 811.3758 | 925.7844 | 1056.9329 | 1207.3202 | 1379.8233 | 1577.7543 | 1804.9271 | 2065.7338 | 2365.2329 | 2709.2511 | 3104.5009 | 3558.7157 | 4080.8064 | 4681.0413 | 5371.254 | 6165.0833 | 7078.2498 | 8128.8752 | 9337.8504 | 10009.5059 | 10009.5059 | 10009.5059 | 10009.5059 | 10009.5059 |  | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 38.7538 | 51.3705 | 68.6893 | 92.5698 | 125.6327 | 171.5777 | 235.6366 | 325.2176 | 450.8252 | 627.3699 | 876.0397 | 1226.9692 | 1723.0532 |  | 180.7435 | 205.3822 | 233.5601 | 265.7995 | 302.7011 | 344.956 | 393.359 | 448.8249 | 512.4063 | 585.3148 | 668.9451 | 764.9031 | 875.0376 | 1001.478 | 1146.6766 | 1313.4583 | 1505.0774 | 1725.283 | 1978.3952 | 2269.392 | 2604.0105 | 2988.8629 | 3431.5705 | 3940.9189 | 4527.0361 | 4852.658 | 4852.658 | 4852.658 | 4852.658 | 4852.658 |  | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 18.7117 | 24.8035 | 33.1657 | 44.696 | 60.66 | 82.8439 | 113.7738 | 157.0268 | 217.6747 | 302.9168 | 422.9836 | 592.425 | 831.9523 |  | 165.1104 | 189.7492 | 217.9271 | 250.1665 | 287.0681 | 329.3229 | 377.726 | 433.1919 | 496.7733 | 569.6818 | 653.3121 | 749.2701 | 859.4046 | 985.845 | 1131.0436 | 1297.8253 | 1489.4444 | 1706.5713 | 1953.5916 | 2236.2263 | 2559.3145 | 2928.2029 | 3348.7266 | 3827.1451 | 4370.0093 | 4634.9834 | 4549.7412 | 4429.6744 | 4260.233 | 4020.7057 |  | 93.4143 | 106.1484 | 120.7117 | 137.3741 | 156.4461 | 178.2848 | 203.3011 | 231.9677 | 264.8287 | 302.5103 | 345.7332 | 395.3275 | 452.2487 | 517.5973 | 592.6408 | 678.8392 | 777.8743 | 891.6839 | 1022.5008 | 1172.8977 | 1345.8397 | 1544.7443 | 1773.5504 | 2036.7987 | 2339.7236 | 2508.0159 | 2508.0159 | 2508.0159 | 2508.0159 | 2508.0159 |  | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.008092 | 0.010726 | 0.014343 | 0.019329 | 0.026233 | 0.035826 | 0.049202 | 0.067907 | 0.094134 | 0.131 | 0.18292 | 0.2562 | 0.35978 |  | 93.4075 | 106.1416 | 120.7049 | 137.3673 | 156.4393 | 178.278 | 203.2943 | 231.9609 | 264.8219 | 302.5035 | 345.7265 | 395.3207 | 452.2419 | 517.5905 | 592.6341 | 678.8324 | 777.8676 | 891.6758 | 1022.49 | 1172.8833 | 1345.8204 | 1544.718 | 1773.5146 | 2036.7495 | 2339.6557 | 2507.9218 | 2507.8849 | 2507.833 | 2507.7597 | 2507.6561 |  | 258.518 | 295.8908 | 338.632 | 387.5338 | 443.5074 | 507.601 | 581.0203 | 665.1528 | 761.5952 | 872.1853 | 999.0386 | 1144.5908 | 1311.6465 | 1503.4355 | 1723.6777 | 1976.6578 | 2267.3119 | 2598.2471 | 2976.0817 | 3409.1097 | 3905.1349 | 4472.9209 | 5122.2412 | 5863.8946 | 6709.665 | 7142.9051 | 7057.6261 | 6937.5074 | 6767.9928 | 6528.3619 |  | 86.4393 | 98.2226 | 111.6985 | 127.1167 | 144.7647 | 164.9728 | 188.1212 | 214.6473 | 245.0547 | 279.9227 | 319.9183 | 365.8095 | 418.4806 | 478.9498 | 548.39 | 628.1522 | 719.7927 | 825.1045 | 946.1536 | 1085.3208 | 1245.3497 | 1429.4027 | 1641.1245 | 1884.7168 | 2165.0232 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 71.7694 | 83.5527 | 97.0285 | 112.4468 | 130.0948 | 150.3028 | 173.4512 | 199.9774 | 230.3848 | 265.2528 | 305.2484 | 351.1396 | 403.8107 | 464.2799 | 533.7201 | 613.4823 | 705.1228 | 807.5455 | 922.8781 | 1054.1983 | 1203.4072 | 1372.4797 | 1563.3843 | 1777.9521 | 2017.6702 | 2116.485 | 2036.4943 | 1923.8244 | 1764.8217 | 1540.0507 |  | 11.9439 | 13.572 | 15.4341 | 17.5645 | 20.0031 | 22.7953 | 25.9939 | 29.6592 | 33.8608 | 38.6787 | 44.2051 | 50.5462 | 57.8241 | 66.1795 | 75.7745 | 86.7958 | 99.4583 | 114.0099 | 130.7361 | 149.9657 | 172.0779 | 197.5097 | 226.7646 | 260.4233 | 299.155 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.8762 | 11.5043 | 13.3664 | 15.4968 | 17.9354 | 20.7276 | 23.9262 | 27.5915 | 31.7931 | 36.611 | 42.1375 | 48.4785 | 55.7564 | 64.1119 | 73.7068 | 84.7281 | 97.3906 | 111.535 | 127.4554 | 145.579 | 166.1662 | 189.4865 | 215.8073 | 245.3751 | 278.386 | 291.8821 | 280.6076 | 264.7271 | 242.316 | 210.6351 |  | 0.27598 | 0.3136 | 0.35663 | 0.40586 | 0.4622 | 0.52672 | 0.60063 | 0.68532 | 0.78241 | 0.89373 | 1.0214 | 1.1679 | 1.3361 | 1.5292 | 1.7509 | 2.0056 | 2.2981 | 2.6344 | 3.0209 | 3.4652 | 3.9761 | 4.5638 | 5.2397 | 6.0175 | 6.9124 | 7.4096 | 7.4096 | 7.4096 | 7.4096 | 7.4096 |  | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.6297e-05 | 3.4859e-05 | 4.6611e-05 | 6.2816e-05 | 8.5251e-05 | 0.00011643 | 0.0001599 | 0.00022069 | 0.00030592 | 0.00042572 | 0.00059446 | 0.00083259 | 0.0011692 |  | 0.27596 | 0.31358 | 0.35661 | 0.40583 | 0.46218 | 0.5267 | 0.60061 | 0.6853 | 0.78238 | 0.89371 | 1.0214 | 1.1679 | 1.3361 | 1.5292 | 1.7509 | 2.0055 | 2.2981 | 2.6343 | 3.0208 | 3.4651 | 3.9761 | 4.5637 | 5.2396 | 6.0173 | 6.9122 | 7.4093 | 7.4092 | 7.409 | 7.4088 | 7.4085 |  | 340.4395 | 391.2614 | 449.3835 | 515.8833 | 591.9997 | 679.1582 | 778.9983 | 893.407 | 1024.5554 | 1174.9428 | 1347.4458 | 1545.3769 | 1772.5497 | 2033.3564 | 2332.8555 | 2676.8737 | 3072.1235 | 3519.962 | 4029.4361 | 4612.3522 | 5278.6844 | 6039.4509 | 6906.6724 | 7893.2391 | 9012.6335 | 9558.6816 | 9382.1372 | 9133.468 | 8782.5392 | 8286.4562
| TRUE | 4 | 22003648 | AC | Blank | 11 | BUS NO.2 | HIBP | X | ABB | RADHA_3108 | RADHA 3108 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 89.933 | 427.8223 | 517.7552 | 49.6875 | 5.9058 | 1.264 |  | 10.2588 | 0.047123 | 0.0044449 | 0.042678 | 287.783 | 1369.0195 | 1656.8025 | 158.9985 | 18.8983 | 4.0446 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 31.2662 | 0.073235 | 31.3394 | 14.6711 | 2.0677 | 0.00021636 |  | 574.6124 | 1838.7439 | 48.0784 | 1790.6655 |  | 0.044106 |  | 6.8976 | 7.2087 | 7.5337 | 7.8734 | 8.2285 | 8.5995 | 8.9873 | 9.3926 | 9.8161 | 10.2588 | 10.7214 | 11.2048 | 11.7101 | 12.2381 | 12.79 | 13.3667 | 13.9695 | 14.5994 | 15.2578 | 15.9458 | 16.6648 | 17.4163 | 18.2017 | 19.0225 | 19.8802 | 20.7767 | 21.7136 | 22.6927 | 23.716 | 24.7855 |  | 0.016485 | 0.018471 | 0.020712 | 0.023244 | 0.026105 | 0.029339 | 0.032997 | 0.037136 | 0.04182 | 0.047123 | 0.053129 | 0.059935 | 0.067647 | 0.076391 | 0.086306 | 0.097553 | 0.11031 | 0.1248 | 0.14124 | 0.15991 | 0.18111 | 0.20519 | 0.23255 | 0.26365 | 0.299 | 0.33918 | 0.38487 | 0.43682 | 0.49592 | 0.56315 |  | 0.001555 | 0.0017422 | 0.0019537 | 0.0021925 | 0.0024623 | 0.0027674 | 0.0031125 | 0.0035028 | 0.0039446 | 0.0044449 | 0.0050114 | 0.0056533 | 0.0063808 | 0.0072056 | 0.0081408 | 0.0092017 | 0.010405 | 0.011771 | 0.013322 | 0.015083 | 0.017083 | 0.019355 | 0.021936 | 0.024869 | 0.028203 | 0.031993 | 0.036302 | 0.041203 | 0.046778 | 0.053119 | 643.2597 | 720.7273 | 808.1897 | 906.9812 | 1018.6178 | 1144.8226 | 1287.5541 | 1449.039 | 1631.8091 | 1838.7439 | 2073.1185 | 2338.6588 | 2639.6039 | 2980.7775 | 3367.6697 | 3806.5288 | 4304.4681 | 4869.5856 | 5511.1018 | 6239.5164 | 7066.7869 | 8006.5322 | 9074.2653 | 10287.6576 | 11666.8418 | 13234.7558 | 15017.5362 | 17044.9665 | 19350.988 | 21974.2834 |  | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 38.8279 | 51.4686 | 68.8205 | 92.7467 | 125.8727 | 171.9056 | 236.0868 | 325.8391 | 451.6867 | 628.5688 | 877.7138 | 1229.3139 | 1726.346 |  | 100.677 | 112.8015 | 126.4903 | 141.9522 | 159.4245 | 179.1769 | 201.5159 | 226.79 | 255.3955 | 287.783 | 324.4651 | 366.025 | 413.1261 | 466.5234 | 527.0761 | 595.7622 | 673.695 | 762.1419 | 862.546 | 976.5507 | 1106.0273 | 1253.1075 | 1420.219 | 1610.1278 | 1825.9848 | 2071.38 | 2350.4042 | 2667.7185 | 3028.6354 | 3439.2091 |  | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 18.7118 | 24.8036 | 33.1658 | 44.6962 | 60.6602 | 82.8442 | 113.7743 | 157.0275 | 217.6756 | 302.9181 | 422.9853 | 592.4274 | 831.9557 |  | 85.0439 | 97.1684 | 110.8572 | 126.3191 | 143.7914 | 163.5438 | 185.8828 | 211.1569 | 239.7624 | 272.1499 | 308.832 | 350.3919 | 397.493 | 450.8903 | 511.443 | 580.1292 | 658.062 | 743.4301 | 837.7424 | 943.3849 | 1061.3311 | 1192.4472 | 1337.3748 | 1496.3535 | 1668.9574 | 1853.7045 | 2047.4861 | 2244.7332 | 2436.208 | 2607.2534 |  | 478.933 | 536.6108 | 601.7301 | 675.2843 | 758.4023 | 852.3669 | 958.6363 | 1078.8684 | 1214.9481 | 1369.0195 | 1543.5209 | 1741.2264 | 1965.2922 | 2219.3099 | 2507.3668 | 2834.1152 | 3204.8512 | 3625.6041 | 4103.239 | 4645.5732 | 5261.5097 | 5961.1883 | 6756.1588 | 7659.5787 | 8686.4373 | 9853.8129 | 11181.1653 | 12690.6694 | 14407.596 | 16360.7459 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 478.8664 | 536.5442 | 601.6635 | 675.2178 | 758.3358 | 852.3003 | 958.5697 | 1078.8018 | 1214.8816 | 1368.9529 | 1543.4543 | 1741.1598 | 1965.2256 | 2219.2433 | 2507.3002 | 2834.0487 | 3204.7846 | 3625.5244 | 4103.1333 | 4645.432 | 5261.3193 | 5960.9299 | 6755.806 | 7659.0941 | 8685.7685 | 9852.8859 | 11179.8753 | 12688.868 | 14405.073 | 16357.2028 |  | 563.9103 | 633.7126 | 712.5207 | 801.5369 | 902.1272 | 1015.8442 | 1144.4526 | 1289.9587 | 1454.644 | 1641.1028 | 1852.2863 | 2091.5517 | 2362.7186 | 2670.1336 | 3018.7432 | 3414.1778 | 3862.8466 | 4368.9546 | 4940.8758 | 5588.8169 | 6322.6504 | 7153.3771 | 8093.1808 | 9155.4477 | 10354.7259 | 11706.5904 | 13227.3613 | 14933.6013 | 16841.281 | 18964.4562 |  | 55.6235 | 62.3222 | 69.8852 | 78.4278 | 88.0812 | 98.9943 | 111.3364 | 125.3002 | 141.1046 | 158.9985 | 179.2652 | 202.2268 | 228.2499 | 257.7516 | 291.2066 | 329.1553 | 372.2128 | 421.0792 | 476.5519 | 539.5388 | 611.074 | 692.3349 | 784.6632 | 889.5867 | 1008.8465 | 1144.426 | 1298.5853 | 1473.8997 | 1673.3043 | 1900.144 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 40.9523 | 47.6511 | 55.2141 | 63.7567 | 73.41 | 84.3231 | 96.6653 | 110.6291 | 126.4335 | 144.3274 | 164.594 | 187.5556 | 213.5787 | 243.0805 | 276.5355 | 314.4842 | 357.5416 | 403.5188 | 453.2745 | 508.4138 | 569.128 | 635.4073 | 706.9165 | 782.8132 | 861.4813 | 940.1446 | 1014.3065 | 1076.9418 | 1117.3304 | 1119.3806 |  | 6.6113 | 7.4075 | 8.3065 | 9.3218 | 10.4692 | 11.7663 | 13.2333 | 14.893 | 16.7715 | 18.8983 | 21.3072 | 24.0364 | 27.1295 | 30.636 | 34.6124 | 39.1229 | 44.2407 | 50.0489 | 56.6423 | 64.1288 | 72.6314 | 82.29 | 93.264 | 105.735 | 119.9101 | 136.0249 | 154.348 | 175.1857 | 198.8866 | 225.8485 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 4.5436 | 5.3398 | 6.2388 | 7.2541 | 8.4015 | 9.6986 | 11.1656 | 12.8253 | 14.7038 | 16.8306 | 19.2395 | 21.9687 | 25.0618 | 28.5683 | 32.5447 | 37.0553 | 42.173 | 47.574 | 53.3617 | 59.7422 | 66.7197 | 74.2668 | 82.3067 | 90.6868 | 99.141 | 107.2342 | 114.2829 | 119.2399 | 120.5298 | 115.8107 |  | 1.415 | 1.5854 | 1.7777 | 1.995 | 2.2406 | 2.5182 | 2.8322 | 3.1874 | 3.5894 | 4.0446 | 4.5602 | 5.1442 | 5.8062 | 6.5567 | 7.4077 | 8.3731 | 9.4684 | 10.7114 | 12.1225 | 13.7248 | 15.5445 | 17.6116 | 19.9603 | 22.6293 | 25.6631 | 29.1119 | 33.0334 | 37.4931 | 42.5656 | 48.3359 |  | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00025897 | 0.00034329 | 0.00045902 | 0.0006186 | 0.00083955 | 0.0011466 | 0.0015747 | 0.0021733 | 0.0030127 | 0.0041924 | 0.0058542 | 0.0081993 | 0.011514 |  | 1.4147 | 1.5851 | 1.7775 | 1.9948 | 2.2404 | 2.518 | 2.832 | 3.1872 | 3.5892 | 4.0444 | 4.5599 | 5.144 | 5.806 | 6.5565 | 7.4075 | 8.3728 | 9.4681 | 10.7112 | 12.1222 | 13.7243 | 15.5439 | 17.6108 | 19.9591 | 22.6278 | 25.6609 | 29.1089 | 33.0293 | 37.4872 | 42.5574 | 48.3244 |  | 610.821 | 688.2886 | 775.751 | 874.5425 | 986.1791 | 1112.3839 | 1255.1154 | 1416.6003 | 1599.3704 | 1806.3052 | 2040.6798 | 2306.2201 | 2607.1652 | 2948.3388 | 3335.231 | 3774.0901 | 4272.0294 | 4830.7585 | 5459.6342 | 6170.6972 | 6974.0421 | 7880.662 | 8902.3631 | 10051.5755 | 11341.0091 | 12783.0781 | 14388.98 | 16167.2702 | 18121.6986 | 20247.9719
| TRUE | 5 | 22003588 | AC | Blank | 11 | BUS NO.3 | OVERCURRENT | Y | ASEA | GROUP_2602 | GROUP 2602 | GROUP 2000s | Electronic |  | 0.0034106 | 2190 |  | 8.25 | 0.026286 | 0.00026713 | 0.026018 | 159.1896 | 82.2745 | 241.4641 | 76.1313 | 10.5195 | 0.24307 |  | 13.322 | 0.096648 | 0.00098218 | 0.095666 | 585.3148 | 302.5103 | 887.8251 | 279.9227 | 38.6787 | 0.89373 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 31.266 | 0.0074366 | 31.2735 | 14.6699 | 2.0677 | 2.1971e-05 |  | 328.358 | 1207.3202 | 48.0111 | 1159.3091 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00030329 | 0.00034464 | 0.00039192 | 0.00044602 | 0.00050794 | 0.00057885 | 0.00066007 | 0.00075314 | 0.00085983 | 0.00098218 | 0.0011225 | 0.0012835 | 0.0014683 | 0.0016805 | 0.0019242 | 0.002204 | 0.0025256 | 0.0028951 | 0.0033198 | 0.0038081 | 0.0043696 | 0.0050154 | 0.0057583 | 0.006613 | 0.0075965 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 372.8169 | 423.6388 | 481.7609 | 548.2607 | 624.3771 | 711.5356 | 811.3758 | 925.7844 | 1056.9329 | 1207.3202 | 1379.8233 | 1577.7543 | 1804.9271 | 2065.7338 | 2365.2329 | 2709.2511 | 3104.5009 | 3558.7157 | 4080.8064 | 4681.0413 | 5371.254 | 6165.0833 | 7078.2498 | 8128.8752 | 9337.8504 | 10009.5059 | 10009.5059 | 10009.5059 | 10009.5059 | 10009.5059 |  | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 32.3775 | 38.7538 | 51.3705 | 68.6893 | 92.5698 | 125.6327 | 171.5777 | 235.6366 | 325.2176 | 450.8252 | 627.3699 | 876.0397 | 1226.9692 | 1723.0532 |  | 180.7435 | 205.3822 | 233.5601 | 265.7995 | 302.7011 | 344.956 | 393.359 | 448.8249 | 512.4063 | 585.3148 | 668.9451 | 764.9031 | 875.0376 | 1001.478 | 1146.6766 | 1313.4583 | 1505.0774 | 1725.283 | 1978.3952 | 2269.392 | 2604.0105 | 2988.8629 | 3431.5705 | 3940.9189 | 4527.0361 | 4852.658 | 4852.658 | 4852.658 | 4852.658 | 4852.658 |  | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 18.7117 | 24.8035 | 33.1657 | 44.696 | 60.66 | 82.8439 | 113.7738 | 157.0268 | 217.6747 | 302.9168 | 422.9836 | 592.425 | 831.9523 |  | 165.1104 | 189.7492 | 217.9271 | 250.1665 | 287.0681 | 329.3229 | 377.726 | 433.1919 | 496.7733 | 569.6818 | 653.3121 | 749.2701 | 859.4046 | 985.845 | 1131.0436 | 1297.8253 | 1489.4444 | 1706.5713 | 1953.5916 | 2236.2263 | 2559.3145 | 2928.2029 | 3348.7266 | 3827.1451 | 4370.0093 | 4634.9834 | 4549.7412 | 4429.6744 | 4260.233 | 4020.7057 |  | 93.4143 | 106.1484 | 120.7117 | 137.3741 | 156.4461 | 178.2848 | 203.3011 | 231.9677 | 264.8287 | 302.5103 | 345.7332 | 395.3275 | 452.2487 | 517.5973 | 592.6408 | 678.8392 | 777.8743 | 891.6839 | 1022.5008 | 1172.8977 | 1345.8397 | 1544.7443 | 1773.5504 | 2036.7987 | 2339.7236 | 2508.0159 | 2508.0159 | 2508.0159 | 2508.0159 | 2508.0159 |  | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.008092 | 0.010726 | 0.014343 | 0.019329 | 0.026233 | 0.035826 | 0.049202 | 0.067907 | 0.094134 | 0.131 | 0.18292 | 0.2562 | 0.35978 |  | 93.4075 | 106.1416 | 120.7049 | 137.3673 | 156.4393 | 178.278 | 203.2943 | 231.9609 | 264.8219 | 302.5035 | 345.7265 | 395.3207 | 452.2419 | 517.5905 | 592.6341 | 678.8324 | 777.8676 | 891.6758 | 1022.49 | 1172.8833 | 1345.8204 | 1544.718 | 1773.5146 | 2036.7495 | 2339.6557 | 2507.9218 | 2507.8849 | 2507.833 | 2507.7597 | 2507.6561 |  | 258.518 | 295.8908 | 338.632 | 387.5338 | 443.5074 | 507.601 | 581.0203 | 665.1528 | 761.5952 | 872.1853 | 999.0386 | 1144.5908 | 1311.6465 | 1503.4355 | 1723.6777 | 1976.6578 | 2267.3119 | 2598.2471 | 2976.0817 | 3409.1097 | 3905.1349 | 4472.9209 | 5122.2412 | 5863.8946 | 6709.665 | 7142.9051 | 7057.6261 | 6937.5074 | 6767.9928 | 6528.3619 |  | 86.4393 | 98.2226 | 111.6985 | 127.1167 | 144.7647 | 164.9728 | 188.1212 | 214.6473 | 245.0547 | 279.9227 | 319.9183 | 365.8095 | 418.4806 | 478.9498 | 548.39 | 628.1522 | 719.7927 | 825.1045 | 946.1536 | 1085.3208 | 1245.3497 | 1429.4027 | 1641.1245 | 1884.7168 | 2165.0232 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 71.7694 | 83.5527 | 97.0285 | 112.4468 | 130.0948 | 150.3028 | 173.4512 | 199.9774 | 230.3848 | 265.2528 | 305.2484 | 351.1396 | 403.8107 | 464.2799 | 533.7201 | 613.4823 | 705.1228 | 807.5455 | 922.8781 | 1054.1983 | 1203.4072 | 1372.4797 | 1563.3843 | 1777.9521 | 2017.6702 | 2116.485 | 2036.4943 | 1923.8244 | 1764.8217 | 1540.0507 |  | 11.9439 | 13.572 | 15.4341 | 17.5645 | 20.0031 | 22.7953 | 25.9939 | 29.6592 | 33.8608 | 38.6787 | 44.2051 | 50.5462 | 57.8241 | 66.1795 | 75.7745 | 86.7958 | 99.4583 | 114.0099 | 130.7361 | 149.9657 | 172.0779 | 197.5097 | 226.7646 | 260.4233 | 299.155 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.8762 | 11.5043 | 13.3664 | 15.4968 | 17.9354 | 20.7276 | 23.9262 | 27.5915 | 31.7931 | 36.611 | 42.1375 | 48.4785 | 55.7564 | 64.1119 | 73.7068 | 84.7281 | 97.3906 | 111.535 | 127.4554 | 145.579 | 166.1662 | 189.4865 | 215.8073 | 245.3751 | 278.386 | 291.8821 | 280.6076 | 264.7271 | 242.316 | 210.6351 |  | 0.27598 | 0.3136 | 0.35663 | 0.40586 | 0.4622 | 0.52672 | 0.60063 | 0.68532 | 0.78241 | 0.89373 | 1.0214 | 1.1679 | 1.3361 | 1.5292 | 1.7509 | 2.0056 | 2.2981 | 2.6344 | 3.0209 | 3.4652 | 3.9761 | 4.5638 | 5.2397 | 6.0175 | 6.9124 | 7.4096 | 7.4096 | 7.4096 | 7.4096 | 7.4096 |  | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.1971e-05 | 2.6297e-05 | 3.4859e-05 | 4.6611e-05 | 6.2816e-05 | 8.5251e-05 | 0.00011643 | 0.0001599 | 0.00022069 | 0.00030592 | 0.00042572 | 0.00059446 | 0.00083259 | 0.0011692 |  | 0.27596 | 0.31358 | 0.35661 | 0.40583 | 0.46218 | 0.5267 | 0.60061 | 0.6853 | 0.78238 | 0.89371 | 1.0214 | 1.1679 | 1.3361 | 1.5292 | 1.7509 | 2.0055 | 2.2981 | 2.6343 | 3.0208 | 3.4651 | 3.9761 | 4.5637 | 5.2396 | 6.0173 | 6.9122 | 7.4093 | 7.4092 | 7.409 | 7.4088 | 7.4085 |  | 340.4395 | 391.2614 | 449.3835 | 515.8833 | 591.9997 | 679.1582 | 778.9983 | 893.407 | 1024.5554 | 1174.9428 | 1347.4458 | 1545.3769 | 1772.5497 | 2033.3564 | 2332.8555 | 2676.8737 | 3072.1235 | 3519.962 | 4029.4361 | 4612.3522 | 5278.6844 | 6039.4509 | 6906.6724 | 7893.2391 | 9012.6335 | 9558.6816 | 9382.1372 | 9133.468 | 8782.5392 | 8286.4562
| TRUE | 6 | 22003589 | AC | Blank | 11 | BUS NO.3 | HIBP | X | ABB | RADHA_3108 | RADHA 3108 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 89.933 | 427.8223 | 517.7552 | 49.6875 | 5.9058 | 1.264 |  | 10.2588 | 0.047123 | 0.0044449 | 0.042678 | 287.783 | 1369.0195 | 1656.8025 | 158.9985 | 18.8983 | 4.0446 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 31.2662 | 0.073235 | 31.3394 | 14.6711 | 2.0677 | 0.00021636 |  | 574.6124 | 1838.7439 | 48.0784 | 1790.6655 |  | 0.044106 |  | 6.8976 | 7.2087 | 7.5337 | 7.8734 | 8.2285 | 8.5995 | 8.9873 | 9.3926 | 9.8161 | 10.2588 | 10.7214 | 11.2048 | 11.7101 | 12.2381 | 12.79 | 13.3667 | 13.9695 | 14.5994 | 15.2578 | 15.9458 | 16.6648 | 17.4163 | 18.2017 | 19.0225 | 19.8802 | 20.7767 | 21.7136 | 22.6927 | 23.716 | 24.7855 |  | 0.016485 | 0.018471 | 0.020712 | 0.023244 | 0.026105 | 0.029339 | 0.032997 | 0.037136 | 0.04182 | 0.047123 | 0.053129 | 0.059935 | 0.067647 | 0.076391 | 0.086306 | 0.097553 | 0.11031 | 0.1248 | 0.14124 | 0.15991 | 0.18111 | 0.20519 | 0.23255 | 0.26365 | 0.299 | 0.33918 | 0.38487 | 0.43682 | 0.49592 | 0.56315 |  | 0.001555 | 0.0017422 | 0.0019537 | 0.0021925 | 0.0024623 | 0.0027674 | 0.0031125 | 0.0035028 | 0.0039446 | 0.0044449 | 0.0050114 | 0.0056533 | 0.0063808 | 0.0072056 | 0.0081408 | 0.0092017 | 0.010405 | 0.011771 | 0.013322 | 0.015083 | 0.017083 | 0.019355 | 0.021936 | 0.024869 | 0.028203 | 0.031993 | 0.036302 | 0.041203 | 0.046778 | 0.053119 | 643.2597 | 720.7273 | 808.1897 | 906.9812 | 1018.6178 | 1144.8226 | 1287.5541 | 1449.039 | 1631.8091 | 1838.7439 | 2073.1185 | 2338.6588 | 2639.6039 | 2980.7775 | 3367.6697 | 3806.5288 | 4304.4681 | 4869.5856 | 5511.1018 | 6239.5164 | 7066.7869 | 8006.5322 | 9074.2653 | 10287.6576 | 11666.8418 | 13234.7558 | 15017.5362 | 17044.9665 | 19350.988 | 21974.2834 |  | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 32.4393 | 38.8279 | 51.4686 | 68.8205 | 92.7467 | 125.8727 | 171.9056 | 236.0868 | 325.8391 | 451.6867 | 628.5688 | 877.7138 | 1229.3139 | 1726.346 |  | 100.677 | 112.8015 | 126.4903 | 141.9522 | 159.4245 | 179.1769 | 201.5159 | 226.79 | 255.3955 | 287.783 | 324.4651 | 366.025 | 413.1261 | 466.5234 | 527.0761 | 595.7622 | 673.695 | 762.1419 | 862.546 | 976.5507 | 1106.0273 | 1253.1075 | 1420.219 | 1610.1278 | 1825.9848 | 2071.38 | 2350.4042 | 2667.7185 | 3028.6354 | 3439.2091 |  | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 15.6331 | 18.7118 | 24.8036 | 33.1658 | 44.6962 | 60.6602 | 82.8442 | 113.7743 | 157.0275 | 217.6756 | 302.9181 | 422.9853 | 592.4274 | 831.9557 |  | 85.0439 | 97.1684 | 110.8572 | 126.3191 | 143.7914 | 163.5438 | 185.8828 | 211.1569 | 239.7624 | 272.1499 | 308.832 | 350.3919 | 397.493 | 450.8903 | 511.443 | 580.1292 | 658.062 | 743.4301 | 837.7424 | 943.3849 | 1061.3311 | 1192.4472 | 1337.3748 | 1496.3535 | 1668.9574 | 1853.7045 | 2047.4861 | 2244.7332 | 2436.208 | 2607.2534 |  | 478.933 | 536.6108 | 601.7301 | 675.2843 | 758.4023 | 852.3669 | 958.6363 | 1078.8684 | 1214.9481 | 1369.0195 | 1543.5209 | 1741.2264 | 1965.2922 | 2219.3099 | 2507.3668 | 2834.1152 | 3204.8512 | 3625.6041 | 4103.239 | 4645.5732 | 5261.5097 | 5961.1883 | 6756.1588 | 7659.5787 | 8686.4373 | 9853.8129 | 11181.1653 | 12690.6694 | 14407.596 | 16360.7459 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 478.8664 | 536.5442 | 601.6635 | 675.2178 | 758.3358 | 852.3003 | 958.5697 | 1078.8018 | 1214.8816 | 1368.9529 | 1543.4543 | 1741.1598 | 1965.2256 | 2219.2433 | 2507.3002 | 2834.0487 | 3204.7846 | 3625.5244 | 4103.1333 | 4645.432 | 5261.3193 | 5960.9299 | 6755.806 | 7659.0941 | 8685.7685 | 9852.8859 | 11179.8753 | 12688.868 | 14405.073 | 16357.2028 |  | 563.9103 | 633.7126 | 712.5207 | 801.5369 | 902.1272 | 1015.8442 | 1144.4526 | 1289.9587 | 1454.644 | 1641.1028 | 1852.2863 | 2091.5517 | 2362.7186 | 2670.1336 | 3018.7432 | 3414.1778 | 3862.8466 | 4368.9546 | 4940.8758 | 5588.8169 | 6322.6504 | 7153.3771 | 8093.1808 | 9155.4477 | 10354.7259 | 11706.5904 | 13227.3613 | 14933.6013 | 16841.281 | 18964.4562 |  | 55.6235 | 62.3222 | 69.8852 | 78.4278 | 88.0812 | 98.9943 | 111.3364 | 125.3002 | 141.1046 | 158.9985 | 179.2652 | 202.2268 | 228.2499 | 257.7516 | 291.2066 | 329.1553 | 372.2128 | 421.0792 | 476.5519 | 539.5388 | 611.074 | 692.3349 | 784.6632 | 889.5867 | 1008.8465 | 1144.426 | 1298.5853 | 1473.8997 | 1673.3043 | 1900.144 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 40.9523 | 47.6511 | 55.2141 | 63.7567 | 73.41 | 84.3231 | 96.6653 | 110.6291 | 126.4335 | 144.3274 | 164.594 | 187.5556 | 213.5787 | 243.0805 | 276.5355 | 314.4842 | 357.5416 | 403.5188 | 453.2745 | 508.4138 | 569.128 | 635.4073 | 706.9165 | 782.8132 | 861.4813 | 940.1446 | 1014.3065 | 1076.9418 | 1117.3304 | 1119.3806 |  | 6.6113 | 7.4075 | 8.3065 | 9.3218 | 10.4692 | 11.7663 | 13.2333 | 14.893 | 16.7715 | 18.8983 | 21.3072 | 24.0364 | 27.1295 | 30.636 | 34.6124 | 39.1229 | 44.2407 | 50.0489 | 56.6423 | 64.1288 | 72.6314 | 82.29 | 93.264 | 105.735 | 119.9101 | 136.0249 | 154.348 | 175.1857 | 198.8866 | 225.8485 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 4.5436 | 5.3398 | 6.2388 | 7.2541 | 8.4015 | 9.6986 | 11.1656 | 12.8253 | 14.7038 | 16.8306 | 19.2395 | 21.9687 | 25.0618 | 28.5683 | 32.5447 | 37.0553 | 42.173 | 47.574 | 53.3617 | 59.7422 | 66.7197 | 74.2668 | 82.3067 | 90.6868 | 99.141 | 107.2342 | 114.2829 | 119.2399 | 120.5298 | 115.8107 |  | 1.415 | 1.5854 | 1.7777 | 1.995 | 2.2406 | 2.5182 | 2.8322 | 3.1874 | 3.5894 | 4.0446 | 4.5602 | 5.1442 | 5.8062 | 6.5567 | 7.4077 | 8.3731 | 9.4684 | 10.7114 | 12.1225 | 13.7248 | 15.5445 | 17.6116 | 19.9603 | 22.6293 | 25.6631 | 29.1119 | 33.0334 | 37.4931 | 42.5656 | 48.3359 |  | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00021636 | 0.00025897 | 0.00034329 | 0.00045902 | 0.0006186 | 0.00083955 | 0.0011466 | 0.0015747 | 0.0021733 | 0.0030127 | 0.0041924 | 0.0058542 | 0.0081993 | 0.011514 |  | 1.4147 | 1.5851 | 1.7775 | 1.9948 | 2.2404 | 2.518 | 2.832 | 3.1872 | 3.5892 | 4.0444 | 4.5599 | 5.144 | 5.806 | 6.5565 | 7.4075 | 8.3728 | 9.4681 | 10.7112 | 12.1222 | 13.7243 | 15.5439 | 17.6108 | 19.9591 | 22.6278 | 25.6609 | 29.1089 | 33.0293 | 37.4872 | 42.5574 | 48.3244 |  | 610.821 | 688.2886 | 775.751 | 874.5425 | 986.1791 | 1112.3839 | 1255.1154 | 1416.6003 | 1599.3704 | 1806.3052 | 2040.6798 | 2306.2201 | 2607.1652 | 2948.3388 | 3335.231 | 3774.0901 | 4272.0294 | 4830.7585 | 5459.6342 | 6170.6972 | 6974.0421 | 7880.662 | 8902.3631 | 10051.5755 | 11341.0091 | 12783.0781 | 14388.98 | 16167.2702 | 18121.6986 | 20247.9719
| TRUE | 7 | 22003623 | AC | Blank | 11 | CAP NO.2 | CAP CONTROL | C | Siemens | DED_760 | DED 760 | DED | Electronic |  | 0 | 2190 |  | 6.6 | 0.014726 | 0 | 0.014726 | 89.0926 | 0 | 89.0926 | 41.8016 | 5.8919 | 0 |  | 10.2588 | 0.047123 | 0 | 0.047123 | 285.0938 | 0 | 285.0938 | 133.764 | 18.8539 | 0 |  | 0.0051679 | 0 | 0.0051679 | 31.266 | 0 | 31.266 | 14.6698 | 2.0677 | 0 |  | 136.7861 | 437.7117 | 48.0035 | 389.7082 |  | 0.044106 |  | 6.8976 | 7.2087 | 7.5337 | 7.8734 | 8.2285 | 8.5995 | 8.9873 | 9.3926 | 9.8161 | 10.2588 | 10.7214 | 11.2048 | 11.7101 | 12.2381 | 12.79 | 13.3667 | 13.9695 | 14.5994 | 15.2578 | 15.9458 | 16.6648 | 17.4163 | 18.2017 | 19.0225 | 19.8802 | 20.7767 | 21.7136 | 22.6927 | 23.716 | 24.7855 |  | 0.016485 | 0.018471 | 0.020712 | 0.023244 | 0.026105 | 0.029339 | 0.032997 | 0.037136 | 0.04182 | 0.047123 | 0.053129 | 0.059935 | 0.067647 | 0.076391 | 0.086306 | 0.097553 | 0.11031 | 0.1248 | 0.14124 | 0.15991 | 0.18111 | 0.20519 | 0.23255 | 0.26365 | 0.299 | 0.33918 | 0.38487 | 0.43682 | 0.49592 | 0.56315 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153.1275 | 171.5686 | 192.389 | 215.9062 | 242.4813 | 272.5242 | 306.5013 | 344.9427 | 388.451 | 437.7117 | 493.5044 | 556.7161 | 628.3558 | 709.572 | 801.6714 | 906.1415 | 1024.6756 | 1159.2014 | 1311.9139 | 1485.3124 | 1682.2436 | 1905.9493 | 2160.1224 | 2448.9696 | 2777.2834 | 3150.5242 | 3574.9138 | 4057.5421 | 4606.4889 | 5230.9625 |  | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 38.7454 | 51.3594 | 68.6744 | 92.5498 | 125.6055 | 171.5406 | 235.5857 | 325.1474 | 450.7278 | 627.2344 | 875.8505 | 1226.7042 | 1722.6811 |  | 99.7362 | 111.7474 | 125.3083 | 140.6258 | 157.9348 | 177.5026 | 199.6329 | 224.6708 | 253.009 | 285.0938 | 321.4332 | 362.6047 | 409.2657 | 462.164 | 522.1509 | 590.1952 | 667.3998 | 755.0202 | 854.4861 | 967.4254 | 1095.6922 | 1241.398 | 1406.948 | 1595.0822 | 1808.9222 | 2052.0243 | 2328.4411 | 2642.7904 | 3000.3348 | 3407.0719 |  | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 18.7117 | 24.8035 | 33.1656 | 44.696 | 60.66 | 82.8439 | 113.7738 | 157.0267 | 217.6746 | 302.9167 | 422.9834 | 592.4247 | 831.9519 |  | 84.1032 | 96.1144 | 109.6753 | 124.9928 | 142.3018 | 161.8696 | 183.9999 | 209.0378 | 237.376 | 269.4608 | 305.8002 | 346.9717 | 393.6327 | 446.531 | 506.5179 | 574.5622 | 651.7668 | 736.3085 | 829.6826 | 934.2598 | 1050.9962 | 1180.738 | 1324.1041 | 1481.3085 | 1651.8954 | 1834.3498 | 2025.5245 | 2219.8071 | 2407.9101 | 2575.12 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 84.1032 | 96.1144 | 109.6753 | 124.9928 | 142.3018 | 161.8696 | 183.9999 | 209.0378 | 237.376 | 269.4608 | 305.8002 | 346.9717 | 393.6327 | 446.531 | 506.5179 | 574.5622 | 651.7668 | 736.3085 | 829.6826 | 934.2598 | 1050.9962 | 1180.738 | 1324.1041 | 1481.3085 | 1651.8954 | 1834.3498 | 2025.5245 | 2219.8071 | 2407.9101 | 2575.12 |  | 46.7955 | 52.4311 | 58.7938 | 65.9806 | 74.1019 | 83.2829 | 93.6663 | 105.4139 | 118.71 | 133.764 | 150.8141 | 170.1315 | 192.0245 | 216.844 | 244.9894 | 276.9153 | 313.1391 | 354.25 | 400.9187 | 453.909 | 514.0908 | 582.4549 | 660.1298 | 748.401 | 848.7331 | 962.7949 | 1092.4877 | 1239.9781 | 1407.7353 | 1598.5734 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 32.1257 | 37.7613 | 44.124 | 51.3108 | 59.4321 | 68.6132 | 78.9965 | 90.7441 | 104.0402 | 119.0942 | 136.1443 | 155.4617 | 177.3547 | 202.1742 | 230.3196 | 262.2455 | 298.4693 | 336.6912 | 377.6434 | 422.7868 | 472.1487 | 525.5325 | 582.3903 | 641.6373 | 701.3815 | 758.5323 | 808.235 | 843.0566 | 851.8125 | 817.8818 |  | 6.5958 | 7.3901 | 8.2869 | 9.2999 | 10.4446 | 11.7386 | 13.2022 | 14.858 | 16.732 | 18.8539 | 21.2571 | 23.9799 | 27.0657 | 30.5639 | 34.531 | 39.0309 | 44.1366 | 49.9312 | 56.5091 | 63.978 | 72.4606 | 82.0964 | 93.0446 | 105.4863 | 119.6281 | 135.7049 | 153.985 | 174.7736 | 198.4188 | 225.3173 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 4.5281 | 5.3224 | 6.2192 | 7.2322 | 8.3769 | 9.671 | 11.1345 | 12.7903 | 14.6644 | 16.7862 | 19.1894 | 21.9122 | 24.998 | 28.4962 | 32.4633 | 36.9632 | 42.0689 | 47.4563 | 53.2285 | 59.5914 | 66.5489 | 74.0733 | 82.0873 | 90.4381 | 98.859 | 106.9143 | 113.9199 | 118.828 | 120.0621 | 115.2796 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 120.757 | 139.1981 | 160.0185 | 183.5358 | 210.1108 | 240.1537 | 274.1309 | 312.5722 | 356.0805 | 405.3412 | 461.1339 | 524.3456 | 595.9853 | 677.2015 | 769.3009 | 873.771 | 992.3051 | 1120.4559 | 1260.5545 | 1416.638 | 1589.6938 | 1780.3438 | 1988.5818 | 2213.3839 | 2452.136 | 2699.7964 | 2947.6794 | 3181.6917 | 3379.7847 | 3508.2814
| TRUE | 8 | 22003621 | AC | Blank | 11 | CAP NO.2 | OVERCURRENT | X | ASEA | GROUP_2603 | GROUP 2603 | GROUP 2000s | Electronic |  | 0.2894 | 2190 |  | 8.25 | 0.026286 | 0.013817 | 0.012468 | 167.3874 | 4255.7221 | 4423.1095 | 153.0587 | 10.655 | 12.573 |  | 13.322 | 0.096648 | 0.050804 | 0.045844 | 615.457 | 15647.6125 | 16263.0695 | 562.7724 | 39.1769 | 46.229 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 31.2673 | 0.63102 | 31.8983 | 14.6814 | 2.0677 | 0.0018643 |  | 4599.3963 | 16911.2478 | 48.6493 | 16862.5986 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.015688 | 0.017827 | 0.020272 | 0.023071 | 0.026274 | 0.029941 | 0.034143 | 0.038957 | 0.044476 | 0.050804 | 0.058063 | 0.066392 | 0.075951 | 0.086926 | 0.099529 | 0.11401 | 0.13064 | 0.14975 | 0.17172 | 0.19698 | 0.22602 | 0.25943 | 0.29785 | 0.34206 | 0.39294 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 5222.1428 | 5934.0192 | 6748.1508 | 7679.6298 | 8745.8126 | 9966.6638 | 11365.1514 | 12967.7034 | 14804.7336 | 16911.2478 | 19327.5434 | 22100.0149 | 25282.0839 | 28935.2712 | 33130.4326 | 37949.1851 | 43485.5516 | 49847.8571 | 57160.9177 | 65568.5638 | 75236.5523 | 86355.9255 | 99146.8865 | 113863.2699 | 130797.7011 | 140205.7539 | 140205.7539 | 140205.7539 | 140205.7539 | 140205.7539 |  | 32.9638 | 32.9638 | 32.9638 | 32.9638 | 32.9638 | 32.9638 | 32.9638 | 32.9638 | 32.9638 | 32.9638 | 32.9638 | 32.9638 | 32.9638 | 32.9638 | 32.9638 | 32.9638 | 32.9638 | 39.4557 | 52.3008 | 69.9333 | 94.2463 | 127.9079 | 174.685 | 239.904 | 331.1075 | 458.9898 | 638.7319 | 891.9052 | 1249.1902 | 1754.2586 |  | 190.0513 | 215.9588 | 245.5878 | 279.4875 | 318.2894 | 362.7203 | 413.6159 | 471.9382 | 538.7939 | 615.457 | 703.3941 | 804.2936 | 920.0997 | 1053.0515 | 1205.7274 | 1381.098 | 1582.5849 | 1814.1305 | 2080.2773 | 2386.2597 | 2738.1102 | 3142.7814 | 3608.2873 | 4143.8658 | 4760.1665 | 5102.5571 | 5102.5571 | 5102.5571 | 5102.5571 | 5102.5571 |  | 15.6336 | 15.6336 | 15.6336 | 15.6336 | 15.6336 | 15.6336 | 15.6336 | 15.6336 | 15.6336 | 15.6336 | 15.6336 | 15.6336 | 15.6336 | 15.6336 | 15.6336 | 15.6336 | 15.6336 | 18.7125 | 24.8045 | 33.167 | 44.6978 | 60.6624 | 82.8471 | 113.7783 | 157.033 | 217.6832 | 302.9287 | 423.0001 | 592.4482 | 831.9849 |  | 174.4176 | 200.3252 | 229.9542 | 263.8538 | 302.6558 | 347.0867 | 397.9823 | 456.3045 | 523.1602 | 599.8233 | 687.7604 | 788.66 | 904.4661 | 1037.4178 | 1190.0938 | 1365.4644 | 1566.9513 | 1795.418 | 2055.4728 | 2353.0927 | 2693.4124 | 3082.1191 | 3525.4402 | 4030.0876 | 4603.1336 | 4884.8739 | 4799.6284 | 4679.5569 | 4510.1089 | 4270.5722 |  | 4831.936 | 5490.6198 | 6243.9183 | 7105.7956 | 8092.3116 | 9221.9388 | 10515.9292 | 11998.736 | 13698.5004 | 15647.6125 | 17883.3586 | 20448.6667 | 23392.9665 | 26773.1818 | 30654.874 | 35113.5617 | 40236.2421 | 46123.146 | 52889.7631 | 60669.1765 | 69614.7576 | 79903.2736 | 91738.4736 | 105355.2255 | 121024.2891 | 129729.3572 | 129729.3572 | 129729.3572 | 129729.3572 | 129729.3572 |  | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.68662 | 0.91016 | 1.217 | 1.6401 | 2.2259 | 3.0399 | 4.1749 | 5.7621 | 7.9875 | 11.1155 | 15.5213 | 21.7389 | 30.5284 |  | 4831.3624 | 5490.0462 | 6243.3446 | 7105.222 | 8091.7379 | 9221.3652 | 10515.3556 | 11998.1623 | 13697.9267 | 15647.0389 | 17882.785 | 20448.093 | 23392.3928 | 26772.6081 | 30654.3004 | 35112.9881 | 40235.6684 | 46122.4594 | 52888.8529 | 60667.9595 | 69613.1175 | 79901.0477 | 91735.4337 | 105351.0506 | 121018.527 | 129721.3697 | 129718.2418 | 129713.8359 | 129707.6183 | 129698.8289 |  | 5005.78 | 5690.3714 | 6473.2988 | 7369.0758 | 8394.3937 | 9568.4518 | 10913.3379 | 12454.4669 | 14221.0869 | 16246.8622 | 18570.5454 | 21236.753 | 24296.8589 | 27810.026 | 31844.3942 | 36478.4524 | 41802.6197 | 47917.8774 | 54944.3257 | 63021.0522 | 72306.5299 | 82983.1667 | 95260.8739 | 109381.1382 | 125621.6606 | 134606.2436 | 134517.8701 | 134393.3929 | 134217.7272 | 133969.4011 |  | 173.7824 | 197.4722 | 224.5649 | 255.5627 | 291.0431 | 331.6706 | 378.2094 | 431.5391 | 492.6718 | 562.7724 | 643.1818 | 735.4441 | 841.337 | 962.9077 | 1102.5143 | 1262.8727 | 1447.1119 | 1658.8366 | 1902.2006 | 2181.9902 | 2503.7214 | 2873.7519 | 3299.4094 | 3789.1411 | 4352.685 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 159.101 | 182.7908 | 209.8835 | 240.8812 | 276.3617 | 316.9891 | 363.528 | 416.8577 | 477.9904 | 548.091 | 628.5004 | 720.7627 | 826.6556 | 948.2263 | 1087.8329 | 1248.1913 | 1432.4305 | 1641.2639 | 1878.9069 | 2150.8434 | 2461.7461 | 2816.7843 | 3221.6083 | 3682.2928 | 4205.2165 | 4461.3415 | 4381.2881 | 4268.5299 | 4109.4026 | 3884.4555 |  | 12.0977 | 13.7469 | 15.6329 | 17.7908 | 20.2607 | 23.089 | 26.3287 | 30.0412 | 34.2969 | 39.1769 | 44.7746 | 51.1973 | 58.569 | 67.032 | 76.7506 | 87.9138 | 100.7394 | 115.4785 | 132.4201 | 151.8974 | 174.2944 | 200.0538 | 229.6855 | 263.7778 | 303.0084 | 324.8033 | 324.8033 | 324.8033 | 324.8033 | 324.8033 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 10.03 | 11.6791 | 13.5652 | 15.7231 | 18.193 | 21.0212 | 24.261 | 27.9735 | 32.2292 | 37.1092 | 42.7068 | 49.1296 | 56.5012 | 64.9643 | 74.6829 | 85.8461 | 98.6717 | 113.0036 | 129.1394 | 147.5107 | 168.3827 | 192.0305 | 218.7281 | 248.7294 | 282.2392 | 296.0124 | 284.7378 | 268.8571 | 246.4458 | 214.7645 |  | 14.2754 | 16.2214 | 18.4469 | 20.9932 | 23.9078 | 27.2451 | 31.0681 | 35.4489 | 40.4706 | 46.229 | 52.8343 | 60.4132 | 69.1118 | 79.0982 | 90.5662 | 103.7389 | 118.8733 | 136.2654 | 156.2566 | 179.24 | 205.6687 | 236.0649 | 271.0306 | 311.2597 | 357.5521 | 383.2702 | 383.2702 | 383.2702 | 383.2702 | 383.2702 |  | 0.0018643 | 0.0018643 | 0.0018643 | 0.0018643 | 0.0018643 | 0.0018643 | 0.0018643 | 0.0018643 | 0.0018643 | 0.0018643 | 0.0018643 | 0.0018643 | 0.0018643 | 0.0018643 | 0.0018643 | 0.0018643 | 0.0018643 | 0.0022314 | 0.0029579 | 0.0039551 | 0.0053301 | 0.0072338 | 0.0098793 | 0.013568 | 0.018726 | 0.025958 | 0.036123 | 0.050442 | 0.070648 | 0.099212 |  | 14.2735 | 16.2195 | 18.4451 | 20.9914 | 23.9059 | 27.2433 | 31.0662 | 35.447 | 40.4688 | 46.2272 | 52.8324 | 60.4113 | 69.1099 | 79.0964 | 90.5644 | 103.737 | 118.8714 | 136.2632 | 156.2537 | 179.236 | 205.6633 | 236.0576 | 271.0207 | 311.2461 | 357.5334 | 383.2443 | 383.2341 | 383.2198 | 383.1996 | 383.171 |  | 5189.1845 | 5901.0609 | 6715.1925 | 7646.6715 | 8712.8543 | 9933.7055 | 11332.1931 | 12934.7451 | 14771.7753 | 16878.2896 | 19294.5851 | 22067.0566 | 25249.1257 | 28902.3129 | 33097.4743 | 37916.2269 | 43452.5933 | 49808.4081 | 57108.6257 | 65498.6423 | 75142.322 | 86228.0392 | 98972.231 | 113623.4065 | 130466.6496 | 139746.8417 | 139567.1301 | 139313.9996 | 138956.7751 | 138451.7922
| TRUE | 9 | 22003645 | AC | Blank | 11 | CB BT 2-3 | CB FAIL | X | ASEA | GROUP_3095 | GROUP 3095 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 258.8921 | 0 | 258.8921 | 121.4703 | 17.1211 | 0 |  | 16.4925 | 0.17586 | 0 | 0.17586 | 1063.9786 | 0 | 1063.9786 | 499.211 | 70.3633 | 0 |  | 0.0051679 | 0 | 0.0051679 | 31.266 | 0 | 31.266 | 14.6698 | 2.0677 | 0 |  | 397.4835 | 1633.5529 | 48.0035 | 1585.5494 |  | 0.051037 |  | 10.4184 | 10.9639 | 11.538 | 12.1422 | 12.778 | 13.447 | 14.1511 | 14.8921 | 15.6719 | 16.4925 | 17.3561 | 18.2649 | 19.2213 | 20.2278 | 21.287 | 22.4016 | 23.5746 | 24.809 | 26.108 | 27.4751 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049141 | 0.056475 | 0.06495 | 0.074748 | 0.086081 | 0.099192 | 0.11437 | 0.13194 | 0.15229 | 0.17586 | 0.20319 | 0.23486 | 0.27158 | 0.31417 | 0.36358 | 0.42091 | 0.48745 | 0.5647 | 0.65438 | 0.75852 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 456.4562 | 524.5779 | 603.3019 | 694.3158 | 799.5797 | 921.3702 | 1062.3322 | 1225.539 | 1414.5623 | 1633.5529 | 1887.3363 | 2181.5223 | 2522.6334 | 2918.2547 | 3377.2069 | 3909.75 | 4527.818 | 5245.2943 | 6078.3312 | 7045.7224 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 |  | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 38.7454 | 51.3594 | 68.6744 | 92.5498 | 125.6055 | 171.5406 | 235.5857 | 325.1474 | 450.7278 | 627.2344 | 875.8505 | 1226.7042 | 1722.6811 |  | 297.3027 | 341.6722 | 392.9474 | 452.2273 | 520.7886 | 600.1141 | 691.9266 | 798.2278 | 921.3439 | 1063.9786 | 1229.2748 | 1420.8863 | 1643.0616 | 1900.7407 | 2199.6691 | 2546.5293 | 2949.0942 | 3416.4066 | 3958.9868 | 4589.0756 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 |  | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 18.7117 | 24.8035 | 33.1656 | 44.696 | 60.66 | 82.8439 | 113.7738 | 157.0267 | 217.6746 | 302.9167 | 422.9834 | 592.4247 | 831.9519 |  | 281.6697 | 326.0392 | 377.3144 | 436.5943 | 505.1556 | 584.4811 | 676.2936 | 782.5948 | 905.7109 | 1048.3456 | 1213.6418 | 1405.2533 | 1627.4286 | 1885.1077 | 2184.0361 | 2530.8963 | 2933.4612 | 3397.6948 | 3934.1833 | 4555.91 | 4803.0355 | 4787.0716 | 4764.8877 | 4733.9578 | 4690.7048 | 4630.057 | 4544.8149 | 4424.7482 | 4255.3068 | 4015.7797 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 281.6697 | 326.0392 | 377.3144 | 436.5943 | 505.1556 | 584.4811 | 676.2936 | 782.5948 | 905.7109 | 1048.3456 | 1213.6418 | 1405.2533 | 1627.4286 | 1885.1077 | 2184.0361 | 2530.8963 | 2933.4612 | 3397.6948 | 3934.1833 | 4555.91 | 4803.0355 | 4787.0716 | 4764.8877 | 4733.9578 | 4690.7048 | 4630.057 | 4544.8149 | 4424.7482 | 4255.3068 | 4015.7797 |  | 139.4923 | 160.3101 | 184.368 | 212.1818 | 244.3502 | 281.5692 | 324.6469 | 374.5227 | 432.2878 | 499.211 | 576.7668 | 666.6695 | 770.9125 | 891.8137 | 1032.0688 | 1194.813 | 1383.6936 | 1602.9531 | 1857.5278 | 2153.1609 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 124.8225 | 145.6403 | 169.6983 | 197.512 | 229.6804 | 266.8994 | 309.9771 | 359.8529 | 417.6181 | 484.5412 | 562.097 | 651.9998 | 756.2428 | 877.1439 | 1017.399 | 1180.1432 | 1369.0238 | 1585.3943 | 1834.2526 | 2122.0388 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 19.6613 | 22.5955 | 25.9865 | 29.9068 | 34.4409 | 39.6869 | 45.7586 | 52.7886 | 60.9305 | 70.3633 | 81.2947 | 93.9664 | 108.6593 | 125.7002 | 145.469 | 168.4077 | 195.0302 | 225.9346 | 261.8166 | 303.4858 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 17.5936 | 20.5279 | 23.9188 | 27.8391 | 32.3732 | 37.6192 | 43.691 | 50.7209 | 58.8628 | 68.2956 | 79.227 | 91.8987 | 106.5916 | 123.6325 | 143.4013 | 166.34 | 192.9625 | 223.4597 | 258.536 | 299.0992 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 424.0857 | 492.2074 | 570.9314 | 661.9453 | 767.2092 | 888.9997 | 1029.9617 | 1193.1686 | 1382.1918 | 1601.1824 | 1854.9658 | 2149.1518 | 2490.263 | 2885.8842 | 3344.8365 | 3877.3795 | 4495.4475 | 5206.5488 | 6026.9718 | 6977.0479 | 7350.2935 | 7317.2377 | 7271.3026 | 7207.2576 | 7117.6959 | 6992.1155 | 6815.6088 | 6566.9928 | 6216.1391 | 5720.1622
| TRUE | 10 | 22003643 | AC | Blank | 11 | CB TR NO.2 | CB FAIL | X | ASEA | GROUP_3095 | GROUP 3095 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 258.8921 | 0 | 258.8921 | 121.4703 | 17.1211 | 0 |  | 16.4925 | 0.17586 | 0 | 0.17586 | 1063.9786 | 0 | 1063.9786 | 499.211 | 70.3633 | 0 |  | 0.0051679 | 0 | 0.0051679 | 31.266 | 0 | 31.266 | 14.6698 | 2.0677 | 0 |  | 397.4835 | 1633.5529 | 48.0035 | 1585.5494 |  | 0.051037 |  | 10.4184 | 10.9639 | 11.538 | 12.1422 | 12.778 | 13.447 | 14.1511 | 14.8921 | 15.6719 | 16.4925 | 17.3561 | 18.2649 | 19.2213 | 20.2278 | 21.287 | 22.4016 | 23.5746 | 24.809 | 26.108 | 27.4751 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049141 | 0.056475 | 0.06495 | 0.074748 | 0.086081 | 0.099192 | 0.11437 | 0.13194 | 0.15229 | 0.17586 | 0.20319 | 0.23486 | 0.27158 | 0.31417 | 0.36358 | 0.42091 | 0.48745 | 0.5647 | 0.65438 | 0.75852 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 456.4562 | 524.5779 | 603.3019 | 694.3158 | 799.5797 | 921.3702 | 1062.3322 | 1225.539 | 1414.5623 | 1633.5529 | 1887.3363 | 2181.5223 | 2522.6334 | 2918.2547 | 3377.2069 | 3909.75 | 4527.818 | 5245.2943 | 6078.3312 | 7045.7224 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 |  | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 38.7454 | 51.3594 | 68.6744 | 92.5498 | 125.6055 | 171.5406 | 235.5857 | 325.1474 | 450.7278 | 627.2344 | 875.8505 | 1226.7042 | 1722.6811 |  | 297.3027 | 341.6722 | 392.9474 | 452.2273 | 520.7886 | 600.1141 | 691.9266 | 798.2278 | 921.3439 | 1063.9786 | 1229.2748 | 1420.8863 | 1643.0616 | 1900.7407 | 2199.6691 | 2546.5293 | 2949.0942 | 3416.4066 | 3958.9868 | 4589.0756 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 |  | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 18.7117 | 24.8035 | 33.1656 | 44.696 | 60.66 | 82.8439 | 113.7738 | 157.0267 | 217.6746 | 302.9167 | 422.9834 | 592.4247 | 831.9519 |  | 281.6697 | 326.0392 | 377.3144 | 436.5943 | 505.1556 | 584.4811 | 676.2936 | 782.5948 | 905.7109 | 1048.3456 | 1213.6418 | 1405.2533 | 1627.4286 | 1885.1077 | 2184.0361 | 2530.8963 | 2933.4612 | 3397.6948 | 3934.1833 | 4555.91 | 4803.0355 | 4787.0716 | 4764.8877 | 4733.9578 | 4690.7048 | 4630.057 | 4544.8149 | 4424.7482 | 4255.3068 | 4015.7797 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 281.6697 | 326.0392 | 377.3144 | 436.5943 | 505.1556 | 584.4811 | 676.2936 | 782.5948 | 905.7109 | 1048.3456 | 1213.6418 | 1405.2533 | 1627.4286 | 1885.1077 | 2184.0361 | 2530.8963 | 2933.4612 | 3397.6948 | 3934.1833 | 4555.91 | 4803.0355 | 4787.0716 | 4764.8877 | 4733.9578 | 4690.7048 | 4630.057 | 4544.8149 | 4424.7482 | 4255.3068 | 4015.7797 |  | 139.4923 | 160.3101 | 184.368 | 212.1818 | 244.3502 | 281.5692 | 324.6469 | 374.5227 | 432.2878 | 499.211 | 576.7668 | 666.6695 | 770.9125 | 891.8137 | 1032.0688 | 1194.813 | 1383.6936 | 1602.9531 | 1857.5278 | 2153.1609 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 124.8225 | 145.6403 | 169.6983 | 197.512 | 229.6804 | 266.8994 | 309.9771 | 359.8529 | 417.6181 | 484.5412 | 562.097 | 651.9998 | 756.2428 | 877.1439 | 1017.399 | 1180.1432 | 1369.0238 | 1585.3943 | 1834.2526 | 2122.0388 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 19.6613 | 22.5955 | 25.9865 | 29.9068 | 34.4409 | 39.6869 | 45.7586 | 52.7886 | 60.9305 | 70.3633 | 81.2947 | 93.9664 | 108.6593 | 125.7002 | 145.469 | 168.4077 | 195.0302 | 225.9346 | 261.8166 | 303.4858 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 17.5936 | 20.5279 | 23.9188 | 27.8391 | 32.3732 | 37.6192 | 43.691 | 50.7209 | 58.8628 | 68.2956 | 79.227 | 91.8987 | 106.5916 | 123.6325 | 143.4013 | 166.34 | 192.9625 | 223.4597 | 258.536 | 299.0992 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 424.0857 | 492.2074 | 570.9314 | 661.9453 | 767.2092 | 888.9997 | 1029.9617 | 1193.1686 | 1382.1918 | 1601.1824 | 1854.9658 | 2149.1518 | 2490.263 | 2885.8842 | 3344.8365 | 3877.3795 | 4495.4475 | 5206.5488 | 6026.9718 | 6977.0479 | 7350.2935 | 7317.2377 | 7271.3026 | 7207.2576 | 7117.6959 | 6992.1155 | 6815.6088 | 6566.9928 | 6216.1391 | 5720.1622
| TRUE | 11 | 22003646 | AC | Blank | 11 | CB TR NO.2 | CB FAIL | Y | ASEA | GROUP_3095 | GROUP 3095 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 258.8921 | 0 | 258.8921 | 121.4703 | 17.1211 | 0 |  | 16.4925 | 0.17586 | 0 | 0.17586 | 1063.9786 | 0 | 1063.9786 | 499.211 | 70.3633 | 0 |  | 0.0051679 | 0 | 0.0051679 | 31.266 | 0 | 31.266 | 14.6698 | 2.0677 | 0 |  | 397.4835 | 1633.5529 | 48.0035 | 1585.5494 |  | 0.051037 |  | 10.4184 | 10.9639 | 11.538 | 12.1422 | 12.778 | 13.447 | 14.1511 | 14.8921 | 15.6719 | 16.4925 | 17.3561 | 18.2649 | 19.2213 | 20.2278 | 21.287 | 22.4016 | 23.5746 | 24.809 | 26.108 | 27.4751 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049141 | 0.056475 | 0.06495 | 0.074748 | 0.086081 | 0.099192 | 0.11437 | 0.13194 | 0.15229 | 0.17586 | 0.20319 | 0.23486 | 0.27158 | 0.31417 | 0.36358 | 0.42091 | 0.48745 | 0.5647 | 0.65438 | 0.75852 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 456.4562 | 524.5779 | 603.3019 | 694.3158 | 799.5797 | 921.3702 | 1062.3322 | 1225.539 | 1414.5623 | 1633.5529 | 1887.3363 | 2181.5223 | 2522.6334 | 2918.2547 | 3377.2069 | 3909.75 | 4527.818 | 5245.2943 | 6078.3312 | 7045.7224 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 |  | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 38.7454 | 51.3594 | 68.6744 | 92.5498 | 125.6055 | 171.5406 | 235.5857 | 325.1474 | 450.7278 | 627.2344 | 875.8505 | 1226.7042 | 1722.6811 |  | 297.3027 | 341.6722 | 392.9474 | 452.2273 | 520.7886 | 600.1141 | 691.9266 | 798.2278 | 921.3439 | 1063.9786 | 1229.2748 | 1420.8863 | 1643.0616 | 1900.7407 | 2199.6691 | 2546.5293 | 2949.0942 | 3416.4066 | 3958.9868 | 4589.0756 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 |  | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 18.7117 | 24.8035 | 33.1656 | 44.696 | 60.66 | 82.8439 | 113.7738 | 157.0267 | 217.6746 | 302.9167 | 422.9834 | 592.4247 | 831.9519 |  | 281.6697 | 326.0392 | 377.3144 | 436.5943 | 505.1556 | 584.4811 | 676.2936 | 782.5948 | 905.7109 | 1048.3456 | 1213.6418 | 1405.2533 | 1627.4286 | 1885.1077 | 2184.0361 | 2530.8963 | 2933.4612 | 3397.6948 | 3934.1833 | 4555.91 | 4803.0355 | 4787.0716 | 4764.8877 | 4733.9578 | 4690.7048 | 4630.057 | 4544.8149 | 4424.7482 | 4255.3068 | 4015.7797 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 281.6697 | 326.0392 | 377.3144 | 436.5943 | 505.1556 | 584.4811 | 676.2936 | 782.5948 | 905.7109 | 1048.3456 | 1213.6418 | 1405.2533 | 1627.4286 | 1885.1077 | 2184.0361 | 2530.8963 | 2933.4612 | 3397.6948 | 3934.1833 | 4555.91 | 4803.0355 | 4787.0716 | 4764.8877 | 4733.9578 | 4690.7048 | 4630.057 | 4544.8149 | 4424.7482 | 4255.3068 | 4015.7797 |  | 139.4923 | 160.3101 | 184.368 | 212.1818 | 244.3502 | 281.5692 | 324.6469 | 374.5227 | 432.2878 | 499.211 | 576.7668 | 666.6695 | 770.9125 | 891.8137 | 1032.0688 | 1194.813 | 1383.6936 | 1602.9531 | 1857.5278 | 2153.1609 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 124.8225 | 145.6403 | 169.6983 | 197.512 | 229.6804 | 266.8994 | 309.9771 | 359.8529 | 417.6181 | 484.5412 | 562.097 | 651.9998 | 756.2428 | 877.1439 | 1017.399 | 1180.1432 | 1369.0238 | 1585.3943 | 1834.2526 | 2122.0388 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 19.6613 | 22.5955 | 25.9865 | 29.9068 | 34.4409 | 39.6869 | 45.7586 | 52.7886 | 60.9305 | 70.3633 | 81.2947 | 93.9664 | 108.6593 | 125.7002 | 145.469 | 168.4077 | 195.0302 | 225.9346 | 261.8166 | 303.4858 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 17.5936 | 20.5279 | 23.9188 | 27.8391 | 32.3732 | 37.6192 | 43.691 | 50.7209 | 58.8628 | 68.2956 | 79.227 | 91.8987 | 106.5916 | 123.6325 | 143.4013 | 166.34 | 192.9625 | 223.4597 | 258.536 | 299.0992 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 424.0857 | 492.2074 | 570.9314 | 661.9453 | 767.2092 | 888.9997 | 1029.9617 | 1193.1686 | 1382.1918 | 1601.1824 | 1854.9658 | 2149.1518 | 2490.263 | 2885.8842 | 3344.8365 | 3877.3795 | 4495.4475 | 5206.5488 | 6026.9718 | 6977.0479 | 7350.2935 | 7317.2377 | 7271.3026 | 7207.2576 | 7117.6959 | 6992.1155 | 6815.6088 | 6566.9928 | 6216.1391 | 5720.1622
| TRUE | 12 | 22003644 | AC | Blank | 11 | CB TR NO.3 | CB FAIL | X | ASEA | GROUP_3095 | GROUP 3095 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 258.8921 | 0 | 258.8921 | 121.4703 | 17.1211 | 0 |  | 16.4925 | 0.17586 | 0 | 0.17586 | 1063.9786 | 0 | 1063.9786 | 499.211 | 70.3633 | 0 |  | 0.0051679 | 0 | 0.0051679 | 31.266 | 0 | 31.266 | 14.6698 | 2.0677 | 0 |  | 397.4835 | 1633.5529 | 48.0035 | 1585.5494 |  | 0.051037 |  | 10.4184 | 10.9639 | 11.538 | 12.1422 | 12.778 | 13.447 | 14.1511 | 14.8921 | 15.6719 | 16.4925 | 17.3561 | 18.2649 | 19.2213 | 20.2278 | 21.287 | 22.4016 | 23.5746 | 24.809 | 26.108 | 27.4751 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049141 | 0.056475 | 0.06495 | 0.074748 | 0.086081 | 0.099192 | 0.11437 | 0.13194 | 0.15229 | 0.17586 | 0.20319 | 0.23486 | 0.27158 | 0.31417 | 0.36358 | 0.42091 | 0.48745 | 0.5647 | 0.65438 | 0.75852 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 456.4562 | 524.5779 | 603.3019 | 694.3158 | 799.5797 | 921.3702 | 1062.3322 | 1225.539 | 1414.5623 | 1633.5529 | 1887.3363 | 2181.5223 | 2522.6334 | 2918.2547 | 3377.2069 | 3909.75 | 4527.818 | 5245.2943 | 6078.3312 | 7045.7224 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 |  | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 38.7454 | 51.3594 | 68.6744 | 92.5498 | 125.6055 | 171.5406 | 235.5857 | 325.1474 | 450.7278 | 627.2344 | 875.8505 | 1226.7042 | 1722.6811 |  | 297.3027 | 341.6722 | 392.9474 | 452.2273 | 520.7886 | 600.1141 | 691.9266 | 798.2278 | 921.3439 | 1063.9786 | 1229.2748 | 1420.8863 | 1643.0616 | 1900.7407 | 2199.6691 | 2546.5293 | 2949.0942 | 3416.4066 | 3958.9868 | 4589.0756 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 |  | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 18.7117 | 24.8035 | 33.1656 | 44.696 | 60.66 | 82.8439 | 113.7738 | 157.0267 | 217.6746 | 302.9167 | 422.9834 | 592.4247 | 831.9519 |  | 281.6697 | 326.0392 | 377.3144 | 436.5943 | 505.1556 | 584.4811 | 676.2936 | 782.5948 | 905.7109 | 1048.3456 | 1213.6418 | 1405.2533 | 1627.4286 | 1885.1077 | 2184.0361 | 2530.8963 | 2933.4612 | 3397.6948 | 3934.1833 | 4555.91 | 4803.0355 | 4787.0716 | 4764.8877 | 4733.9578 | 4690.7048 | 4630.057 | 4544.8149 | 4424.7482 | 4255.3068 | 4015.7797 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 281.6697 | 326.0392 | 377.3144 | 436.5943 | 505.1556 | 584.4811 | 676.2936 | 782.5948 | 905.7109 | 1048.3456 | 1213.6418 | 1405.2533 | 1627.4286 | 1885.1077 | 2184.0361 | 2530.8963 | 2933.4612 | 3397.6948 | 3934.1833 | 4555.91 | 4803.0355 | 4787.0716 | 4764.8877 | 4733.9578 | 4690.7048 | 4630.057 | 4544.8149 | 4424.7482 | 4255.3068 | 4015.7797 |  | 139.4923 | 160.3101 | 184.368 | 212.1818 | 244.3502 | 281.5692 | 324.6469 | 374.5227 | 432.2878 | 499.211 | 576.7668 | 666.6695 | 770.9125 | 891.8137 | 1032.0688 | 1194.813 | 1383.6936 | 1602.9531 | 1857.5278 | 2153.1609 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 124.8225 | 145.6403 | 169.6983 | 197.512 | 229.6804 | 266.8994 | 309.9771 | 359.8529 | 417.6181 | 484.5412 | 562.097 | 651.9998 | 756.2428 | 877.1439 | 1017.399 | 1180.1432 | 1369.0238 | 1585.3943 | 1834.2526 | 2122.0388 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 19.6613 | 22.5955 | 25.9865 | 29.9068 | 34.4409 | 39.6869 | 45.7586 | 52.7886 | 60.9305 | 70.3633 | 81.2947 | 93.9664 | 108.6593 | 125.7002 | 145.469 | 168.4077 | 195.0302 | 225.9346 | 261.8166 | 303.4858 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 17.5936 | 20.5279 | 23.9188 | 27.8391 | 32.3732 | 37.6192 | 43.691 | 50.7209 | 58.8628 | 68.2956 | 79.227 | 91.8987 | 106.5916 | 123.6325 | 143.4013 | 166.34 | 192.9625 | 223.4597 | 258.536 | 299.0992 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 424.0857 | 492.2074 | 570.9314 | 661.9453 | 767.2092 | 888.9997 | 1029.9617 | 1193.1686 | 1382.1918 | 1601.1824 | 1854.9658 | 2149.1518 | 2490.263 | 2885.8842 | 3344.8365 | 3877.3795 | 4495.4475 | 5206.5488 | 6026.9718 | 6977.0479 | 7350.2935 | 7317.2377 | 7271.3026 | 7207.2576 | 7117.6959 | 6992.1155 | 6815.6088 | 6566.9928 | 6216.1391 | 5720.1622
| TRUE | 13 | 22003647 | AC | Blank | 11 | CB TR NO.3 | CB FAIL | Y | ASEA | GROUP_3095 | GROUP 3095 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 258.8921 | 0 | 258.8921 | 121.4703 | 17.1211 | 0 |  | 16.4925 | 0.17586 | 0 | 0.17586 | 1063.9786 | 0 | 1063.9786 | 499.211 | 70.3633 | 0 |  | 0.0051679 | 0 | 0.0051679 | 31.266 | 0 | 31.266 | 14.6698 | 2.0677 | 0 |  | 397.4835 | 1633.5529 | 48.0035 | 1585.5494 |  | 0.051037 |  | 10.4184 | 10.9639 | 11.538 | 12.1422 | 12.778 | 13.447 | 14.1511 | 14.8921 | 15.6719 | 16.4925 | 17.3561 | 18.2649 | 19.2213 | 20.2278 | 21.287 | 22.4016 | 23.5746 | 24.809 | 26.108 | 27.4751 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049141 | 0.056475 | 0.06495 | 0.074748 | 0.086081 | 0.099192 | 0.11437 | 0.13194 | 0.15229 | 0.17586 | 0.20319 | 0.23486 | 0.27158 | 0.31417 | 0.36358 | 0.42091 | 0.48745 | 0.5647 | 0.65438 | 0.75852 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 456.4562 | 524.5779 | 603.3019 | 694.3158 | 799.5797 | 921.3702 | 1062.3322 | 1225.539 | 1414.5623 | 1633.5529 | 1887.3363 | 2181.5223 | 2522.6334 | 2918.2547 | 3377.2069 | 3909.75 | 4527.818 | 5245.2943 | 6078.3312 | 7045.7224 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 | 7442.8433 |  | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 32.3705 | 38.7454 | 51.3594 | 68.6744 | 92.5498 | 125.6055 | 171.5406 | 235.5857 | 325.1474 | 450.7278 | 627.2344 | 875.8505 | 1226.7042 | 1722.6811 |  | 297.3027 | 341.6722 | 392.9474 | 452.2273 | 520.7886 | 600.1141 | 691.9266 | 798.2278 | 921.3439 | 1063.9786 | 1229.2748 | 1420.8863 | 1643.0616 | 1900.7407 | 2199.6691 | 2546.5293 | 2949.0942 | 3416.4066 | 3958.9868 | 4589.0756 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 | 4847.7316 |  | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 15.633 | 18.7117 | 24.8035 | 33.1656 | 44.696 | 60.66 | 82.8439 | 113.7738 | 157.0267 | 217.6746 | 302.9167 | 422.9834 | 592.4247 | 831.9519 |  | 281.6697 | 326.0392 | 377.3144 | 436.5943 | 505.1556 | 584.4811 | 676.2936 | 782.5948 | 905.7109 | 1048.3456 | 1213.6418 | 1405.2533 | 1627.4286 | 1885.1077 | 2184.0361 | 2530.8963 | 2933.4612 | 3397.6948 | 3934.1833 | 4555.91 | 4803.0355 | 4787.0716 | 4764.8877 | 4733.9578 | 4690.7048 | 4630.057 | 4544.8149 | 4424.7482 | 4255.3068 | 4015.7797 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 281.6697 | 326.0392 | 377.3144 | 436.5943 | 505.1556 | 584.4811 | 676.2936 | 782.5948 | 905.7109 | 1048.3456 | 1213.6418 | 1405.2533 | 1627.4286 | 1885.1077 | 2184.0361 | 2530.8963 | 2933.4612 | 3397.6948 | 3934.1833 | 4555.91 | 4803.0355 | 4787.0716 | 4764.8877 | 4733.9578 | 4690.7048 | 4630.057 | 4544.8149 | 4424.7482 | 4255.3068 | 4015.7797 |  | 139.4923 | 160.3101 | 184.368 | 212.1818 | 244.3502 | 281.5692 | 324.6469 | 374.5227 | 432.2878 | 499.211 | 576.7668 | 666.6695 | 770.9125 | 891.8137 | 1032.0688 | 1194.813 | 1383.6936 | 1602.9531 | 1857.5278 | 2153.1609 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 124.8225 | 145.6403 | 169.6983 | 197.512 | 229.6804 | 266.8994 | 309.9771 | 359.8529 | 417.6181 | 484.5412 | 562.097 | 651.9998 | 756.2428 | 877.1439 | 1017.399 | 1180.1432 | 1369.0238 | 1585.3943 | 1834.2526 | 2122.0388 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 19.6613 | 22.5955 | 25.9865 | 29.9068 | 34.4409 | 39.6869 | 45.7586 | 52.7886 | 60.9305 | 70.3633 | 81.2947 | 93.9664 | 108.6593 | 125.7002 | 145.469 | 168.4077 | 195.0302 | 225.9346 | 261.8166 | 303.4858 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 17.5936 | 20.5279 | 23.9188 | 27.8391 | 32.3732 | 37.6192 | 43.691 | 50.7209 | 58.8628 | 68.2956 | 79.227 | 91.8987 | 106.5916 | 123.6325 | 143.4013 | 166.34 | 192.9625 | 223.4597 | 258.536 | 299.0992 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 424.0857 | 492.2074 | 570.9314 | 661.9453 | 767.2092 | 888.9997 | 1029.9617 | 1193.1686 | 1382.1918 | 1601.1824 | 1854.9658 | 2149.1518 | 2490.263 | 2885.8842 | 3344.8365 | 3877.3795 | 4495.4475 | 5206.5488 | 6026.9718 | 6977.0479 | 7350.2935 | 7317.2377 | 7271.3026 | 7207.2576 | 7117.6959 | 6992.1155 | 6815.6088 | 6566.9928 | 6216.1391 | 5720.1622
| TRUE | 14 | 22003615 | AC | AC024 | 11 | AC24 | FEEDER MANAGEMENT | X | ABB | RACIB_0068 | RACIB 0068 | RACIB | Electronic |  | 0.57434 | 2190 |  | 8.25 | 0.026286 | 0.018906 | 0.0073796 | 170.4661 | 5823.0656 | 5993.5317 | 181.9488 | 10.7059 | 61.1872 |  | 17.4227 | 0.2054 | 0.14774 | 0.057666 | 1332.0763 | 45503.2728 | 46835.3491 | 1421.8057 | 83.6596 | 478.136 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 31.2685 | 1.2523 | 32.5208 | 14.6929 | 2.0677 | 0.013159 |  | 6247.3737 | 48818.9504 | 49.2945 | 48769.6559 |  | 0.074756 |  | 8.8904 | 9.5805 | 10.3241 | 11.1255 | 11.9891 | 12.9197 | 13.9225 | 15.0032 | 16.1678 | 17.4227 | 18.7751 | 20.2325 | 21.8029 | 23.4953 | 25.3191 | 27.2844 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.032056 | 0.039167 | 0.047942 | 0.05878 | 0.072178 | 0.088754 | 0.10928 | 0.13472 | 0.16626 | 0.2054 | 0.254 | 0.31438 | 0.38943 | 0.48275 | 0.59886 | 0.74337 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.023056 | 0.028171 | 0.034483 | 0.042278 | 0.051914 | 0.063837 | 0.078601 | 0.096897 | 0.11958 | 0.14774 | 0.18269 | 0.22612 | 0.2801 | 0.34722 | 0.43073 | 0.53467 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 7618.7408 | 9309.0106 | 11394.5571 | 13970.3706 | 17154.6469 | 21094.5142 | 25973.1834 | 32018.8764 | 39515.9756 | 48818.9504 | 60369.7538 | 74719.5571 | 92555.9066 | 114736.6607 | 142332.4019 | 176679.4467 | 190441.8948 | 190441.8948 | 190441.8948 | 190441.8948 | 190441.8948 | 190441.8948 | 190441.8948 | 190441.8948 | 190441.8948 | 190441.8948 | 190441.8948 | 190441.8948 | 190441.8948 | 190441.8948 |  | 33.5575 | 33.5575 | 33.5575 | 33.5575 | 33.5575 | 33.5575 | 33.5575 | 33.5575 | 33.5575 | 33.5575 | 33.5575 | 33.5575 | 33.5575 | 33.5575 | 33.5575 | 33.5575 | 33.5575 | 40.1663 | 53.2428 | 71.1928 | 95.9437 | 130.2116 | 177.8311 | 244.2247 | 337.0708 | 467.2563 | 650.2355 | 907.9685 | 1271.6882 | 1785.8529 |  | 207.8853 | 254.0061 | 310.9124 | 381.1962 | 468.0825 | 575.586 | 708.7056 | 873.6686 | 1078.2349 | 1332.0763 | 1647.2521 | 2038.8015 | 2525.4851 | 3130.7102 | 3883.689 | 4820.8841 | 5196.407 | 5196.407 | 5196.407 | 5196.407 | 5196.407 | 5196.407 | 5196.407 | 5196.407 | 5196.407 | 5196.407 | 5196.407 | 5196.407 | 5196.407 | 5196.407 |  | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 18.7132 | 24.8055 | 33.1683 | 44.6995 | 60.6647 | 82.8504 | 113.7827 | 157.0391 | 217.6917 | 302.9405 | 423.0167 | 592.4713 | 832.0173 |  | 192.2511 | 238.3719 | 295.2782 | 365.562 | 452.4483 | 559.9517 | 693.0713 | 858.0344 | 1062.6006 | 1316.4421 | 1631.6179 | 2023.1673 | 2509.8508 | 3115.076 | 3868.0547 | 4805.2499 | 5180.7728 | 5177.6938 | 5171.6015 | 5163.2387 | 5151.7075 | 5135.7423 | 5113.5566 | 5082.6243 | 5039.3679 | 4978.7153 | 4893.4665 | 4773.3903 | 4603.9357 | 4364.3896 |  | 7101.2923 | 8676.7628 | 10620.6634 | 13021.5332 | 15989.5403 | 19661.8204 | 24209.1409 | 29844.2235 | 36832.136 | 45503.2728 | 56269.5707 | 69644.7663 | 86269.7095 | 106943.9948 | 132665.4928 | 164679.7606 | 177507.493 | 177507.493 | 177507.493 | 177507.493 | 177507.493 | 177507.493 | 177507.493 | 177507.493 | 177507.493 | 177507.493 | 177507.493 | 177507.493 | 177507.493 | 177507.493 |  | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.3627 | 1.8063 | 2.4153 | 3.255 | 4.4175 | 6.033 | 8.2855 | 11.4354 | 15.852 | 22.0597 | 30.8035 | 43.1429 | 60.5863 |  | 7100.1539 | 8675.6243 | 10619.5249 | 13020.3948 | 15988.4019 | 19660.6819 | 24208.0025 | 29843.0851 | 36830.9975 | 45502.1344 | 56268.4322 | 69643.6278 | 86268.571 | 106942.8563 | 132664.3544 | 164678.6222 | 177506.3546 | 177506.1304 | 177505.6867 | 177505.0778 | 177504.2381 | 177503.0755 | 177501.46 | 177499.2075 | 177496.0577 | 177491.641 | 177485.4333 | 177476.6896 | 177464.3501 | 177446.9067 |  | 7292.405 | 8913.9962 | 10914.8031 | 13385.9568 | 16440.8502 | 20220.6336 | 24901.0738 | 30701.1195 | 37893.5981 | 46818.5764 | 57900.0501 | 71666.7951 | 88778.4219 | 110057.9323 | 136532.4091 | 169483.8721 | 182687.1273 | 182683.8241 | 182677.2883 | 182668.3165 | 182655.9455 | 182638.8178 | 182615.0166 | 182581.8318 | 182535.4256 | 182470.3563 | 182378.8998 | 182250.0799 | 182068.2858 | 181811.2963 |  | 221.8886 | 271.1161 | 331.8557 | 406.8738 | 499.6129 | 614.3578 | 756.4444 | 932.5195 | 1150.8654 | 1421.8057 | 1758.212 | 2176.1364 | 2695.6032 | 3341.5967 | 4145.2965 | 5145.6217 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 207.1957 | 256.4233 | 317.1628 | 392.181 | 484.92 | 599.6649 | 741.7515 | 917.8266 | 1136.1725 | 1407.1129 | 1743.5191 | 2161.4435 | 2680.9103 | 3326.9038 | 4130.6036 | 5130.9288 | 5531.7471 | 5528.8535 | 5523.1281 | 5515.2688 | 5504.4319 | 5489.428 | 5468.5782 | 5439.5083 | 5398.8565 | 5341.8559 | 5261.7401 | 5148.894 | 4989.6425 | 4764.52 |  | 13.056 | 15.9526 | 19.5265 | 23.9406 | 29.3974 | 36.149 | 44.5095 | 54.8698 | 67.7173 | 83.6596 | 103.4538 | 128.0447 | 158.6103 | 196.6208 | 243.9107 | 302.7702 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 10.9883 | 13.8848 | 17.4588 | 21.8729 | 27.3297 | 34.0813 | 42.4417 | 52.8021 | 65.6496 | 81.5918 | 101.3861 | 125.9769 | 156.5425 | 194.553 | 241.843 | 300.7025 | 324.2868 | 323.8796 | 323.0738 | 321.9678 | 320.4427 | 318.3312 | 315.397 | 311.306 | 305.5851 | 297.5634 | 286.2886 | 270.4078 | 247.9963 | 216.3147 |  | 74.6184 | 91.1731 | 111.599 | 136.8267 | 168.0137 | 206.601 | 254.3831 | 313.595 | 387.022 | 478.136 | 591.2653 | 731.8082 | 906.4986 | 1123.7383 | 1394.0128 | 1730.41 | 1865.2003 | 1865.2003 | 1865.2003 | 1865.2003 | 1865.2003 | 1865.2003 | 1865.2003 | 1865.2003 | 1865.2003 | 1865.2003 | 1865.2003 | 1865.2003 | 1865.2003 | 1865.2003 |  | 0.013159 | 0.013159 | 0.013159 | 0.013159 | 0.013159 | 0.013159 | 0.013159 | 0.013159 | 0.013159 | 0.013159 | 0.013159 | 0.013159 | 0.013159 | 0.013159 | 0.013159 | 0.013159 | 0.013159 | 0.01575 | 0.020878 | 0.027917 | 0.037622 | 0.05106 | 0.069733 | 0.095768 | 0.13218 | 0.18323 | 0.25498 | 0.35604 | 0.49867 | 0.70029 |  | 74.6053 | 91.1599 | 111.5859 | 136.8136 | 168.0006 | 206.5879 | 254.3699 | 313.5818 | 387.0089 | 478.1228 | 591.2521 | 731.7951 | 906.4854 | 1123.7252 | 1393.9997 | 1730.3969 | 1865.1872 | 1865.1846 | 1865.1794 | 1865.1724 | 1865.1627 | 1865.1493 | 1865.1306 | 1865.1046 | 1865.0681 | 1865.0171 | 1864.9453 | 1864.8443 | 1864.7017 | 1864.5 |  | 7585.1943 | 9275.4642 | 11361.0106 | 13936.8241 | 17121.1004 | 21060.9677 | 25939.6369 | 31985.3299 | 39482.4291 | 48785.404 | 60336.2074 | 74686.0106 | 92522.3601 | 114703.1143 | 142298.8554 | 176645.9003 | 190408.3484 | 190401.7418 | 190388.6697 | 190370.7256 | 190345.9828 | 190311.7262 | 190264.1224 | 190197.7507 | 190104.9353 | 189974.7927 | 189791.8738 | 189534.2259 | 189170.6262 | 188656.6311
| TRUE | 15 | 22003616 | AC | AC025 | 11 | AC25 | FEEDER MANAGEMENT | X | ABB | RACIB_3147 | RACIB 3147 | RACIB | Electronic |  | 0.57434 | 2190 |  | 8.25 | 0.026286 | 0.018906 | 0.0073796 | 170.4661 | 5823.0656 | 5993.5317 | 181.9488 | 10.7059 | 12.2374 |  | 13.322 | 0.096648 | 0.069515 | 0.027133 | 626.7769 | 21410.4851 | 22037.262 | 668.9969 | 39.364 | 44.9951 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 31.2685 | 1.2523 | 32.5208 | 14.6929 | 2.0677 | 0.0026318 |  | 6198.424 | 22790.6181 | 49.284 | 22741.3341 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.021466 | 0.024392 | 0.027739 | 0.031568 | 0.03595 | 0.040968 | 0.046717 | 0.053304 | 0.060856 | 0.069515 | 0.079447 | 0.090843 | 0.10392 | 0.11894 | 0.13618 | 0.15599 | 0.17875 | 0.2049 | 0.23496 | 0.26952 | 0.30926 | 0.35497 | 0.40755 | 0.46804 | 0.53765 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 7037.6748 | 7997.0423 | 9094.2152 | 10349.5325 | 11786.3848 | 13431.6775 | 15316.3638 | 17476.0596 | 19951.7523 | 22790.6181 | 26046.9638 | 29783.3136 | 34071.6619 | 38994.9176 | 44648.5702 | 51142.6119 | 58603.7534 | 67177.9803 | 77033.502 | 88364.1532 | 101393.318 | 116378.4563 | 133616.3272 | 153449.0136 | 176270.8749 | 188949.7346 | 188949.7346 | 188949.7346 | 188949.7346 | 188949.7346 |  | 33.547 | 33.547 | 33.547 | 33.547 | 33.547 | 33.547 | 33.547 | 33.547 | 33.547 | 33.547 | 33.547 | 33.547 | 33.547 | 33.547 | 33.547 | 33.547 | 33.547 | 40.1537 | 53.2261 | 71.1704 | 95.9136 | 130.1707 | 177.7753 | 244.1481 | 336.965 | 467.1097 | 650.0315 | 907.6836 | 1271.2892 | 1785.2926 |  | 193.5468 | 219.9309 | 250.1048 | 284.628 | 324.1436 | 369.3917 | 421.2235 | 480.6184 | 548.7037 | 626.7769 | 716.3314 | 819.0867 | 937.0229 | 1072.4199 | 1227.904 | 1406.5001 | 1611.6929 | 1847.4973 | 2118.5392 | 2430.1495 | 2788.4715 | 3200.5857 | 3674.6536 | 4220.0828 | 4847.7189 | 5196.407 | 5196.407 | 5196.407 | 5196.407 | 5196.407 |  | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 18.7132 | 24.8055 | 33.1683 | 44.6995 | 60.6647 | 82.8504 | 113.7827 | 157.0391 | 217.6917 | 302.9405 | 423.0167 | 592.4713 | 832.0173 |  | 177.9126 | 204.2967 | 234.4706 | 268.9938 | 308.5094 | 353.7575 | 405.5892 | 464.9842 | 533.0695 | 611.1427 | 700.6971 | 803.4525 | 921.3886 | 1056.7857 | 1212.2698 | 1390.8659 | 1596.0587 | 1828.7841 | 2093.7338 | 2396.9812 | 2743.7719 | 3139.921 | 3591.8032 | 4106.3001 | 4690.6798 | 4978.7153 | 4893.4665 | 4773.3903 | 4603.9357 | 4364.3896 |  | 6611.4938 | 7512.7649 | 8543.4963 | 9722.7952 | 11072.6359 | 12618.2945 | 14388.8498 | 16417.7607 | 18743.5328 | 21410.4851 | 24469.6361 | 27979.7236 | 32008.3821 | 36633.4998 | 41944.7838 | 48045.5654 | 55054.882 | 63109.8789 | 72368.5791 | 83013.0794 | 95253.2361 | 109330.9185 | 125524.9144 | 144156.5915 | 165596.4279 | 177507.493 | 177507.493 | 177507.493 | 177507.493 | 177507.493 |  | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.3627 | 1.8063 | 2.4153 | 3.255 | 4.4175 | 6.033 | 8.2855 | 11.4354 | 15.852 | 22.0597 | 30.8035 | 43.1429 | 60.5863 |  | 6610.3554 | 7511.6265 | 8542.3578 | 9721.6567 | 11071.4975 | 12617.1561 | 14387.7113 | 16416.6223 | 18742.3943 | 21409.3466 | 24468.4976 | 27978.5851 | 32007.2436 | 36632.3613 | 41943.6453 | 48044.4269 | 55053.7436 | 63108.5162 | 72366.7728 | 83010.6641 | 95249.9812 | 109326.5009 | 125518.8814 | 144148.306 | 165584.9925 | 177491.641 | 177485.4333 | 177476.6896 | 177464.3501 | 177446.9067 |  | 6788.268 | 7715.9231 | 8776.8284 | 9990.6505 | 11380.0069 | 12970.9135 | 14793.3005 | 16881.6064 | 19275.4638 | 22020.4893 | 25169.1947 | 28782.0376 | 32928.6322 | 37689.147 | 43155.9151 | 49435.2928 | 56649.8023 | 64937.3003 | 74460.5066 | 85407.6453 | 97993.7531 | 112466.4219 | 129110.6846 | 148254.6061 | 170275.6724 | 182470.3563 | 182378.8998 | 182250.0799 | 182068.2858 | 181811.2963 |  | 206.5843 | 234.7456 | 266.9521 | 303.8007 | 345.9781 | 394.2741 | 449.5973 | 512.9931 | 585.6647 | 668.9969 | 764.5839 | 874.2609 | 1000.1413 | 1144.6588 | 1310.6164 | 1501.2428 | 1720.2575 | 1971.9458 | 2261.2453 | 2593.8458 | 2976.3045 | 3416.179 | 3922.1804 | 4504.35 | 5174.2641 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 191.8914 | 220.0527 | 252.2592 | 289.1078 | 331.2853 | 379.5813 | 434.9044 | 498.3003 | 570.9719 | 654.3041 | 749.891 | 859.568 | 985.4484 | 1129.9659 | 1295.9235 | 1486.5499 | 1705.5646 | 1954.3594 | 2237.9334 | 2562.6746 | 2934.2964 | 3359.1671 | 3844.3186 | 4397.4184 | 5026.6806 | 5341.8559 | 5261.7401 | 5148.894 | 4989.6425 | 4764.52 |  | 12.1555 | 13.8125 | 15.7076 | 17.8757 | 20.3575 | 23.1992 | 26.4545 | 30.1847 | 34.4607 | 39.364 | 44.9884 | 51.4418 | 58.8487 | 67.3521 | 77.1171 | 88.3337 | 101.2206 | 116.03 | 133.0525 | 152.6228 | 175.1268 | 201.0092 | 230.7825 | 265.0376 | 304.4556 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 10.0878 | 11.7448 | 13.6398 | 15.808 | 18.2897 | 21.1315 | 24.3867 | 28.117 | 32.393 | 37.2963 | 42.9207 | 49.3741 | 56.7809 | 65.2844 | 75.0494 | 86.2659 | 99.1528 | 113.5551 | 129.7718 | 148.2361 | 169.215 | 192.9859 | 219.825 | 249.9891 | 283.6861 | 297.5634 | 286.2886 | 270.4078 | 247.9963 | 216.3147 |  | 13.8944 | 15.7884 | 17.9545 | 20.4329 | 23.2696 | 26.5179 | 30.2388 | 34.5027 | 39.3904 | 44.9951 | 51.4241 | 58.8007 | 67.2671 | 76.987 | 88.1489 | 100.9699 | 115.7003 | 132.6283 | 152.0859 | 174.4558 | 200.179 | 229.7639 | 263.7963 | 302.9516 | 348.0084 | 373.0401 | 373.0401 | 373.0401 | 373.0401 | 373.0401 |  | 0.0026318 | 0.0026318 | 0.0026318 | 0.0026318 | 0.0026318 | 0.0026318 | 0.0026318 | 0.0026318 | 0.0026318 | 0.0026318 | 0.0026318 | 0.0026318 | 0.0026318 | 0.0026318 | 0.0026318 | 0.0026318 | 0.0026318 | 0.0031501 | 0.0041756 | 0.0055834 | 0.0075245 | 0.010212 | 0.013947 | 0.019154 | 0.026435 | 0.036645 | 0.050995 | 0.071208 | 0.099733 | 0.14006 |  | 13.8917 | 15.7858 | 17.9519 | 20.4303 | 23.267 | 26.5153 | 30.2362 | 34.5 | 39.3878 | 44.9925 | 51.4214 | 58.798 | 67.2644 | 76.9843 | 88.1462 | 100.9673 | 115.6977 | 132.6251 | 152.0817 | 174.4502 | 200.1715 | 229.7537 | 263.7824 | 302.9325 | 347.982 | 373.0034 | 372.9891 | 372.9689 | 372.9403 | 372.9 |  | 7004.1389 | 7963.5064 | 9060.6793 | 10315.9966 | 11752.8489 | 13398.1416 | 15282.8279 | 17442.5237 | 19918.2164 | 22757.0821 | 26013.4278 | 29749.7777 | 34038.126 | 38961.3816 | 44615.0343 | 51109.076 | 58570.2174 | 67137.8399 | 76980.2935 | 88293.0063 | 101297.4361 | 116248.3286 | 133438.6105 | 153204.946 | 175934.0211 | 188482.779 | 188299.9176 | 188042.3505 | 187678.8648 | 187165.031
| TRUE | 16 | 22003617 | AC | AC026 | 11 | AC26 | FEEDER MANAGEMENT | X | ABB | RACIB_0068 | RACIB 0068 | RACIB | Electronic |  | 0.81881 | 2190 |  | 8.25 | 0.026286 | 0.02098 | 0.0053053 | 171.7211 | 6461.9364 | 6633.6575 | 193.7249 | 10.7267 | 13.5801 |  | 17.4227 | 0.2054 | 0.16395 | 0.041457 | 1341.8827 | 50495.611 | 51837.4936 | 1513.8274 | 83.8217 | 106.1188 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 31.2695 | 1.7854 | 33.0549 | 14.7027 | 2.0677 | 0.003752 |  | 6851.6891 | 53541.2615 | 49.8291 | 53491.4324 |  | 0.074756 |  | 8.8904 | 9.5805 | 10.3241 | 11.1255 | 11.9891 | 12.9197 | 13.9225 | 15.0032 | 16.1678 | 17.4227 | 18.7751 | 20.2325 | 21.8029 | 23.4953 | 25.3191 | 27.2844 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.032056 | 0.039167 | 0.047942 | 0.05878 | 0.072178 | 0.088754 | 0.10928 | 0.13472 | 0.16626 | 0.2054 | 0.254 | 0.31438 | 0.38943 | 0.48275 | 0.59886 | 0.74337 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.025586 | 0.031262 | 0.038266 | 0.046916 | 0.05761 | 0.070841 | 0.087225 | 0.10753 | 0.1327 | 0.16395 | 0.20274 | 0.25093 | 0.31083 | 0.38532 | 0.47799 | 0.59334 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 8355.71 | 10209.4815 | 12496.7652 | 15321.74 | 18814.0348 | 23135.0098 | 28485.5981 | 35116.0977 | 43338.3996 | 53541.2615 | 66209.3869 | 81947.2625 | 101508.9418 | 125835.2648 | 156100.3725 | 193769.845 | 208863.5499 | 208863.5499 | 208863.5499 | 208863.5499 | 208863.5499 | 208863.5499 | 208863.5499 | 208863.5499 | 208863.5499 | 208863.5499 | 208863.5499 | 208863.5499 | 208863.5499 | 208863.5499 |  | 34.0478 | 34.0478 | 34.0478 | 34.0478 | 34.0478 | 34.0478 | 34.0478 | 34.0478 | 34.0478 | 34.0478 | 34.0478 | 34.0478 | 34.0478 | 34.0478 | 34.0478 | 34.0478 | 34.0478 | 40.7531 | 54.0206 | 72.2329 | 97.3454 | 132.1139 | 180.4292 | 247.7928 | 341.9953 | 474.0828 | 659.7354 | 921.2338 | 1290.2675 | 1811.9441 |  | 209.4157 | 255.876 | 313.2013 | 384.0025 | 471.5284 | 579.8233 | 713.9229 | 880.1004 | 1086.1725 | 1341.8827 | 1659.3787 | 2053.8106 | 2544.077 | 3153.7576 | 3912.2796 | 4856.3742 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 |  | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 18.7138 | 24.8063 | 33.1694 | 44.701 | 60.6668 | 82.8532 | 113.7865 | 157.0444 | 217.699 | 302.9507 | 423.0308 | 592.4912 | 832.0452 |  | 193.781 | 240.2413 | 297.5665 | 368.3677 | 455.8937 | 564.1885 | 698.2881 | 864.4656 | 1070.5378 | 1326.2479 | 1643.744 | 2038.1759 | 2528.4422 | 3138.1229 | 3896.6449 | 4840.7394 | 5219.0267 | 5215.9477 | 5209.8552 | 5201.4921 | 5189.9605 | 5173.9947 | 5151.8084 | 5120.875 | 5077.6172 | 5016.9625 | 4931.7108 | 4811.6307 | 4642.1703 | 4402.6163 |  | 7880.4023 | 9628.7236 | 11785.897 | 14450.1754 | 17743.814 | 21818.9939 | 26865.2184 | 33118.5475 | 40873.1305 | 50495.611 | 62443.1205 | 77285.76 | 95734.6893 | 118677.2295 | 147220.7315 | 182747.4071 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 |  | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.9427 | 2.5752 | 3.4434 | 4.6405 | 6.2979 | 8.6011 | 11.8123 | 16.303 | 22.5996 | 31.4497 | 43.9154 | 61.5073 | 86.3757 |  | 7878.7792 | 9627.1005 | 11784.2739 | 14448.5524 | 17742.1909 | 21817.3708 | 26863.5953 | 33116.9244 | 40871.5074 | 50493.9879 | 62441.4974 | 77284.1369 | 95733.0663 | 118675.6065 | 147219.1085 | 182745.7841 | 196980.896 | 196980.5764 | 196979.9439 | 196979.0757 | 196977.8786 | 196976.2212 | 196973.918 | 196970.7068 | 196966.2161 | 196959.9195 | 196951.0694 | 196938.6037 | 196921.0118 | 196896.1434 |  | 8072.5602 | 9867.3418 | 12081.8405 | 14816.9201 | 18198.0846 | 22381.5593 | 27561.8834 | 33981.39 | 41942.0452 | 51820.2358 | 64085.2414 | 79322.3128 | 98261.5085 | 121813.7293 | 151115.7533 | 187586.5235 | 202199.9228 | 202196.5241 | 202189.7991 | 202180.5679 | 202167.8391 | 202150.2159 | 202125.7264 | 202091.5817 | 202043.8333 | 201976.882 | 201882.7802 | 201750.2344 | 201563.1822 | 201298.7597 |  | 236.2496 | 288.6632 | 353.3339 | 433.2074 | 531.9486 | 654.12 | 805.4027 | 992.8737 | 1225.3513 | 1513.8274 | 1872.0064 | 2316.9796 | 2870.0671 | 3557.8704 | 4413.587 | 5478.6549 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 221.5469 | 273.9605 | 338.6312 | 418.5047 | 517.2459 | 639.4173 | 790.7 | 978.171 | 1210.6486 | 1499.1247 | 1857.3037 | 2302.2769 | 2855.3644 | 3543.1677 | 4398.8843 | 5463.9522 | 5890.7121 | 5887.8166 | 5882.0873 | 5874.2228 | 5863.3786 | 5848.3647 | 5827.5009 | 5798.4116 | 5757.7326 | 5700.6939 | 5620.5245 | 5507.6029 | 5348.2449 | 5122.9719 |  | 13.0813 | 15.9835 | 19.5643 | 23.987 | 29.4544 | 36.2191 | 44.5957 | 54.9761 | 67.8485 | 83.8217 | 103.6543 | 128.2927 | 158.9176 | 197.0017 | 244.3833 | 303.3569 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 11.0136 | 13.9157 | 17.4966 | 21.9192 | 27.3866 | 34.1513 | 42.5279 | 52.9083 | 65.7808 | 81.7539 | 101.5865 | 126.225 | 156.8498 | 194.934 | 242.3156 | 301.2891 | 324.9191 | 324.5119 | 323.7061 | 322.6001 | 321.075 | 318.9635 | 316.0292 | 311.9382 | 306.2172 | 298.1954 | 286.9206 | 271.0396 | 248.6279 | 216.9461 |  | 16.561 | 20.2352 | 24.7686 | 30.3677 | 37.2894 | 45.8536 | 56.4585 | 69.6001 | 85.8967 | 106.1188 | 131.2271 | 162.4195 | 201.1908 | 249.4056 | 309.3911 | 384.052 | 413.9677 | 413.9677 | 413.9677 | 413.9677 | 413.9677 | 413.9677 | 413.9677 | 413.9677 | 413.9677 | 413.9677 | 413.9677 | 413.9677 | 413.9677 | 413.9677 |  | 0.003752 | 0.003752 | 0.003752 | 0.003752 | 0.003752 | 0.003752 | 0.003752 | 0.003752 | 0.003752 | 0.003752 | 0.003752 | 0.003752 | 0.003752 | 0.003752 | 0.003752 | 0.003752 | 0.003752 | 0.004491 | 0.005953 | 0.00796 | 0.010727 | 0.014559 | 0.019883 | 0.027307 | 0.037688 | 0.052244 | 0.072702 | 0.10152 | 0.14219 | 0.19967 |  | 16.5573 | 20.2314 | 24.7648 | 30.3639 | 37.2857 | 45.8499 | 56.4547 | 69.5964 | 85.893 | 106.1151 | 131.2233 | 162.4158 | 201.187 | 249.4018 | 309.3873 | 384.0482 | 413.964 | 413.9632 | 413.9618 | 413.9598 | 413.957 | 413.9532 | 413.9478 | 413.9404 | 413.93 | 413.9155 | 413.895 | 413.8662 | 413.8255 | 413.768 |  | 8321.6779 | 10175.4495 | 12462.7332 | 15287.708 | 18780.0028 | 23100.9778 | 28451.5661 | 35082.0657 | 43304.3676 | 53507.2295 | 66175.3549 | 81913.2304 | 101474.9098 | 125801.2328 | 156066.3405 | 193735.813 | 208829.5179 | 208822.8157 | 208809.5544 | 208791.3505 | 208766.2497 | 208731.4972 | 208683.2043 | 208615.872 | 208521.7131 | 208389.6868 | 208204.1203 | 207942.7431 | 207573.8805 | 207052.4457
| TRUE | 17 | 22003618 | AC | AC031 | 11 | AC31 | FEEDER MANAGEMENT | X | ABB | RACIB_0068 | RACIB 0068 | RACIB | Electronic |  | 0.57434 | 2190 |  | 8.25 | 0.026286 | 0.018906 | 0.0073796 | 170.4661 | 5823.0656 | 5993.5317 | 181.9488 | 10.7059 | 44.3394 |  | 13.322 | 0.096648 | 0.069515 | 0.027133 | 626.7769 | 21410.4851 | 22037.262 | 668.9969 | 39.364 | 163.0289 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 31.2685 | 1.2523 | 32.5208 | 14.6929 | 2.0677 | 0.0095356 |  | 6230.5259 | 22908.6518 | 49.2909 | 22859.3609 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.021466 | 0.024392 | 0.027739 | 0.031568 | 0.03595 | 0.040968 | 0.046717 | 0.053304 | 0.060856 | 0.069515 | 0.079447 | 0.090843 | 0.10392 | 0.11894 | 0.13618 | 0.15599 | 0.17875 | 0.2049 | 0.23496 | 0.26952 | 0.30926 | 0.35497 | 0.40755 | 0.46804 | 0.53765 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 0.57632 | 7074.1233 | 8038.4594 | 9141.3147 | 10403.1332 | 11847.4271 | 13501.2409 | 15395.6881 | 17566.569 | 20055.0835 | 22908.6518 | 26181.8623 | 29937.563 | 34248.1208 | 39196.8742 | 44879.8074 | 51407.4821 | 58907.2652 | 67525.8985 | 77432.4624 | 88821.7957 | 101918.4392 | 116981.1863 | 134308.333 | 154243.7339 | 177183.7908 | 189928.315 | 189928.315 | 189928.315 | 189928.315 | 189928.315 |  | 33.5539 | 33.5539 | 33.5539 | 33.5539 | 33.5539 | 33.5539 | 33.5539 | 33.5539 | 33.5539 | 33.5539 | 33.5539 | 33.5539 | 33.5539 | 33.5539 | 33.5539 | 33.5539 | 33.5539 | 40.1619 | 53.237 | 71.1851 | 95.9333 | 130.1975 | 177.8119 | 244.1984 | 337.0344 | 467.2058 | 650.1653 | 907.8704 | 1271.5509 | 1785.66 |  | 193.5468 | 219.9309 | 250.1048 | 284.628 | 324.1436 | 369.3917 | 421.2235 | 480.6184 | 548.7037 | 626.7769 | 716.3314 | 819.0867 | 937.0229 | 1072.4199 | 1227.904 | 1406.5001 | 1611.6929 | 1847.4973 | 2118.5392 | 2430.1495 | 2788.4715 | 3200.5857 | 3674.6536 | 4220.0828 | 4847.7189 | 5196.407 | 5196.407 | 5196.407 | 5196.407 | 5196.407 |  | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 15.6342 | 18.7132 | 24.8055 | 33.1683 | 44.6995 | 60.6647 | 82.8504 | 113.7827 | 157.0391 | 217.6917 | 302.9405 | 423.0167 | 592.4713 | 832.0173 |  | 177.9126 | 204.2967 | 234.4706 | 268.9938 | 308.5094 | 353.7575 | 405.5892 | 464.9842 | 533.0695 | 611.1427 | 700.6971 | 803.4525 | 921.3886 | 1056.7857 | 1212.2698 | 1390.8659 | 1596.0587 | 1828.7841 | 2093.7338 | 2396.9812 | 2743.7719 | 3139.921 | 3591.8032 | 4106.3001 | 4690.6798 | 4978.7153 | 4893.4665 | 4773.3903 | 4603.9357 | 4364.3896 |  | 6611.4938 | 7512.7649 | 8543.4963 | 9722.7952 | 11072.6359 | 12618.2945 | 14388.8498 | 16417.7607 | 18743.5328 | 21410.4851 | 24469.6361 | 27979.7236 | 32008.3821 | 36633.4998 | 41944.7838 | 48045.5654 | 55054.882 | 63109.8789 | 72368.5791 | 83013.0794 | 95253.2361 | 109330.9185 | 125524.9144 | 144156.5915 | 165596.4279 | 177507.493 | 177507.493 | 177507.493 | 177507.493 | 177507.493 |  | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.1385 | 1.3627 | 1.8063 | 2.4153 | 3.255 | 4.4175 | 6.033 | 8.2855 | 11.4354 | 15.852 | 22.0597 | 30.8035 | 43.1429 | 60.5863 |  | 6610.3554 | 7511.6265 | 8542.3578 | 9721.6567 | 11071.4975 | 12617.1561 | 14387.7113 | 16416.6223 | 18742.3943 | 21409.3466 | 24468.4976 | 27978.5851 | 32007.2436 | 36632.3613 | 41943.6453 | 48044.4269 | 55053.7436 | 63108.5162 | 72366.7728 | 83010.6641 | 95249.9812 | 109326.5009 | 125518.8814 | 144148.306 | 165584.9925 | 177491.641 | 177485.4333 | 177476.6896 | 177464.3501 | 177446.9067 |  | 6788.268 | 7715.9231 | 8776.8284 | 9990.6505 | 11380.0069 | 12970.9135 | 14793.3005 | 16881.6064 | 19275.4638 | 22020.4893 | 25169.1947 | 28782.0376 | 32928.6322 | 37689.147 | 43155.9151 | 49435.2928 | 56649.8023 | 64937.3003 | 74460.5066 | 85407.6453 | 97993.7531 | 112466.4219 | 129110.6846 | 148254.6061 | 170275.6724 | 182470.3563 | 182378.8998 | 182250.0799 | 182068.2858 | 181811.2963 |  | 206.5843 | 234.7456 | 266.9521 | 303.8007 | 345.9781 | 394.2741 | 449.5973 | 512.9931 | 585.6647 | 668.9969 | 764.5839 | 874.2609 | 1000.1413 | 1144.6588 | 1310.6164 | 1501.2428 | 1720.2575 | 1971.9458 | 2261.2453 | 2593.8458 | 2976.3045 | 3416.179 | 3922.1804 | 4504.35 | 5174.2641 | 5546.44 | 5546.44 | 5546.44 | 5546.44 | 5546.44 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 191.8914 | 220.0527 | 252.2592 | 289.1078 | 331.2853 | 379.5813 | 434.9044 | 498.3003 | 570.9719 | 654.3041 | 749.891 | 859.568 | 985.4484 | 1129.9659 | 1295.9235 | 1486.5499 | 1705.5646 | 1954.3594 | 2237.9334 | 2562.6746 | 2934.2964 | 3359.1671 | 3844.3186 | 4397.4184 | 5026.6806 | 5341.8559 | 5261.7401 | 5148.894 | 4989.6425 | 4764.52 |  | 12.1555 | 13.8125 | 15.7076 | 17.8757 | 20.3575 | 23.1992 | 26.4545 | 30.1847 | 34.4607 | 39.364 | 44.9884 | 51.4418 | 58.8487 | 67.3521 | 77.1171 | 88.3337 | 101.2206 | 116.03 | 133.0525 | 152.6228 | 175.1268 | 201.0092 | 230.7825 | 265.0376 | 304.4556 | 326.3545 | 326.3545 | 326.3545 | 326.3545 | 326.3545 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 10.0878 | 11.7448 | 13.6398 | 15.808 | 18.2897 | 21.1315 | 24.3867 | 28.117 | 32.393 | 37.2963 | 42.9207 | 49.3741 | 56.7809 | 65.2844 | 75.0494 | 86.2659 | 99.1528 | 113.5551 | 129.7718 | 148.2361 | 169.215 | 192.9859 | 219.825 | 249.9891 | 283.6861 | 297.5634 | 286.2886 | 270.4078 | 247.9963 | 216.3147 |  | 50.3428 | 57.2055 | 65.054 | 74.0337 | 84.3119 | 96.0813 | 109.5631 | 125.0121 | 142.7215 | 163.0289 | 186.3226 | 213.05 | 243.726 | 278.9436 | 319.3861 | 365.8401 | 419.2122 | 480.5465 | 551.0463 | 632.0982 | 725.3002 | 832.4939 | 955.8021 | 1097.6719 | 1260.9243 | 1351.6204 | 1351.6204 | 1351.6204 | 1351.6204 | 1351.6204 |  | 0.0095356 | 0.0095356 | 0.0095356 | 0.0095356 | 0.0095356 | 0.0095356 | 0.0095356 | 0.0095356 | 0.0095356 | 0.0095356 | 0.0095356 | 0.0095356 | 0.0095356 | 0.0095356 | 0.0095356 | 0.0095356 | 0.0095356 | 0.011414 | 0.015129 | 0.02023 | 0.027263 | 0.037001 | 0.050532 | 0.069398 | 0.095781 | 0.13277 | 0.18477 | 0.25801 | 0.36136 | 0.50746 |  | 50.3333 | 57.196 | 65.0444 | 74.0241 | 84.3024 | 96.0717 | 109.5535 | 125.0025 | 142.712 | 163.0194 | 186.3131 | 213.0404 | 243.7164 | 278.9341 | 319.3766 | 365.8306 | 419.2026 | 480.5351 | 551.0312 | 632.078 | 725.2729 | 832.4569 | 955.7516 | 1097.6025 | 1260.8285 | 1351.4877 | 1351.4357 | 1351.3624 | 1351.2591 | 1351.113 |  | 7040.5804 | 8004.9166 | 9107.7718 | 10369.5904 | 11813.8843 | 13467.698 | 15362.1452 | 17533.0262 | 20021.5406 | 22875.109 | 26148.3195 | 29904.0201 | 34214.578 | 39163.3314 | 44846.2646 | 51373.9393 | 58873.7224 | 67485.7498 | 77379.243 | 88750.6341 | 101822.5375 | 116851.0318 | 134130.5797 | 153999.6161 | 176846.8676 | 189461.2633 | 189278.3642 | 189020.744 | 188657.1836 | 188143.244
| TRUE | 18 | 22003619 | AC | AC032 | 11 | AC32 | FEEDER MANAGEMENT | X | ABB | RACIB_3147 | RACIB 3147 | RACIB | Electronic |  | 0.81881 | 2190 |  | 8.25 | 0.026286 | 0.02098 | 0.0053053 | 171.7211 | 6461.9364 | 6633.6575 | 193.7249 | 10.7267 | 24.602 |  | 13.322 | 0.096648 | 0.077141 | 0.019507 | 631.391 | 23759.5113 | 24390.9024 | 712.2955 | 39.4403 | 90.4577 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 31.2695 | 1.7854 | 33.0549 | 14.7027 | 2.0677 | 0.0067973 |  | 6862.711 | 25233.0959 | 49.8321 | 25183.2638 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.023821 | 0.027068 | 0.030782 | 0.035031 | 0.039894 | 0.045463 | 0.051843 | 0.059153 | 0.067532 | 0.077141 | 0.088163 | 0.10081 | 0.11533 | 0.13199 | 0.15113 | 0.17311 | 0.19836 | 0.22738 | 0.26074 | 0.29909 | 0.34319 | 0.39392 | 0.45226 | 0.51939 | 0.59664 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 7791.9046 | 8854.0879 | 10068.8452 | 11458.6952 | 13049.5354 | 14871.1547 | 16957.8234 | 19348.9745 | 22089.988 | 25233.0959 | 28838.4252 | 32975.2009 | 37723.1329 | 43174.0154 | 49433.5718 | 56623.582 | 64884.3364 | 74377.4659 | 85289.2071 | 97834.1678 | 112259.6723 | 128850.7728 | 147936.0317 | 169894.1935 | 195161.881 | 209199.5382 | 209199.5382 | 209199.5382 | 209199.5382 | 209199.5382 |  | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 40.7567 | 54.0255 | 72.2394 | 97.3541 | 132.1258 | 180.4454 | 247.815 | 342.0259 | 474.1252 | 659.7944 | 921.3162 | 1290.3829 | 1812.1061 |  | 194.9717 | 221.55 | 251.946 | 286.7233 | 326.5299 | 372.1111 | 424.3244 | 484.1566 | 552.7431 | 631.391 | 721.6048 | 825.1166 | 943.921 | 1080.3148 | 1236.9435 | 1416.8544 | 1623.5578 | 1861.0981 | 2134.1353 | 2448.0396 | 2808.9994 | 3224.1476 | 3701.7054 | 4251.1499 | 4883.4065 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 |  | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 18.7138 | 24.8063 | 33.1694 | 44.701 | 60.6668 | 82.8532 | 113.7865 | 157.0444 | 217.699 | 302.9507 | 423.0308 | 592.4912 | 832.0452 |  | 179.3369 | 205.9152 | 236.3113 | 271.0886 | 310.8951 | 356.4763 | 408.6896 | 468.5218 | 537.1084 | 615.7563 | 705.9701 | 809.4819 | 928.2862 | 1064.68 | 1221.3088 | 1401.2196 | 1607.923 | 1842.3842 | 2109.3291 | 2414.8702 | 2764.2984 | 3163.4808 | 3618.8522 | 4137.3634 | 4726.3622 | 5016.9625 | 4931.7108 | 4811.6307 | 4642.1703 | 4402.6163 |  | 7336.8661 | 8337.0191 | 9480.8359 | 10789.5202 | 12287.4572 | 14002.6959 | 15967.5055 | 18219.0161 | 20799.9574 | 23759.5113 | 27154.2934 | 31049.4861 | 35520.1441 | 40652.7012 | 46546.7065 | 53316.8282 | 61095.1637 | 70033.9051 | 80308.4128 | 92120.7618 | 105703.833 | 121326.0318 | 139296.7329 | 159972.5626 | 183764.6454 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 |  | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.9427 | 2.5752 | 3.4434 | 4.6405 | 6.2979 | 8.6011 | 11.8123 | 16.303 | 22.5996 | 31.4497 | 43.9154 | 61.5073 | 86.3757 |  | 7335.2431 | 8335.396 | 9479.2128 | 10787.8971 | 12285.8341 | 14001.0728 | 15965.8825 | 18217.393 | 20798.3344 | 23757.8883 | 27152.6704 | 31047.863 | 35518.521 | 40651.0781 | 46545.0834 | 53315.2051 | 61093.5407 | 70031.9624 | 80305.8376 | 92117.3185 | 105699.1926 | 121319.7339 | 139288.1318 | 159960.7503 | 183748.3425 | 196959.9195 | 196951.0694 | 196938.6037 | 196921.0118 | 196896.1434 |  | 7514.58 | 8541.3112 | 9715.5241 | 11058.9857 | 12596.7292 | 14357.5491 | 16374.5721 | 18685.9148 | 21335.4427 | 24373.6445 | 27858.6404 | 31857.3448 | 36446.8072 | 41715.7581 | 47766.3922 | 54716.4247 | 62701.4637 | 71874.3466 | 82415.1666 | 94532.1887 | 108463.491 | 124483.2147 | 142906.984 | 164098.1136 | 188474.7046 | 201976.882 | 201882.7802 | 201750.2344 | 201563.1822 | 201298.7597 |  | 219.9547 | 249.9387 | 284.2296 | 323.4632 | 368.3704 | 419.7922 | 478.696 | 546.1949 | 623.5699 | 712.2955 | 814.069 | 930.8445 | 1064.8721 | 1218.743 | 1395.4416 | 1598.4057 | 1831.5954 | 2099.5734 | 2407.5968 | 2761.7238 | 3168.9359 | 3637.2798 | 4176.0304 | 4795.8791 | 5509.1511 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 205.252 | 235.236 | 269.5269 | 308.7605 | 353.6677 | 405.0895 | 463.9933 | 531.4922 | 608.8672 | 697.5928 | 799.3663 | 916.1418 | 1050.1694 | 1204.0403 | 1380.7389 | 1583.703 | 1816.8927 | 2081.9752 | 2384.2694 | 2730.5318 | 3126.8997 | 3580.2297 | 4098.1165 | 4688.8759 | 5361.4689 | 5700.6939 | 5620.5245 | 5507.6029 | 5348.2449 | 5122.9719 |  | 12.179 | 13.8393 | 15.738 | 17.9104 | 20.3969 | 23.2442 | 26.5057 | 30.2432 | 34.5275 | 39.4403 | 45.0756 | 51.5415 | 58.9627 | 67.4826 | 77.2666 | 88.5048 | 101.4167 | 116.2548 | 133.3103 | 152.9185 | 175.4661 | 201.3987 | 231.2296 | 265.5511 | 305.0454 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 10.1113 | 11.7715 | 13.6702 | 15.8426 | 18.3292 | 21.1764 | 24.438 | 28.1754 | 32.4597 | 37.3725 | 43.0078 | 49.4737 | 56.8949 | 65.4149 | 75.1988 | 86.4371 | 99.3489 | 113.7798 | 130.0296 | 148.5318 | 169.5543 | 193.3753 | 220.272 | 250.5024 | 284.2758 | 298.1954 | 286.9206 | 271.0396 | 248.6279 | 216.9461 |  | 27.9331 | 31.7409 | 36.0956 | 41.0781 | 46.7811 | 53.3114 | 60.7918 | 69.3638 | 79.19 | 90.4577 | 103.3824 | 118.2122 | 135.233 | 154.7738 | 177.2136 | 202.9889 | 232.6028 | 266.6345 | 305.7519 | 350.7241 | 402.4378 | 461.915 | 530.3334 | 609.0509 | 699.6326 | 749.9559 | 749.9559 | 749.9559 | 749.9559 | 749.9559 |  | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0081359 | 0.010785 | 0.014421 | 0.019434 | 0.026375 | 0.036021 | 0.049469 | 0.068276 | 0.094646 | 0.13171 | 0.18392 | 0.25759 | 0.36174 |  | 27.9263 | 31.7341 | 36.0888 | 41.0713 | 46.7743 | 53.3046 | 60.785 | 69.357 | 79.1832 | 90.4509 | 103.3756 | 118.2055 | 135.2262 | 154.767 | 177.2068 | 202.9821 | 232.596 | 266.6264 | 305.7411 | 350.7097 | 402.4184 | 461.8886 | 530.2974 | 609.0014 | 699.5643 | 749.8613 | 749.8242 | 749.772 | 749.6984 | 749.5942 |  | 7757.8696 | 8820.0529 | 10034.8101 | 11424.6601 | 13015.5004 | 14837.1196 | 16923.7884 | 19314.9395 | 22055.953 | 25199.0608 | 28804.3901 | 32941.1658 | 37689.0978 | 43139.9803 | 49399.5367 | 56589.547 | 64850.3013 | 74336.7281 | 85235.2066 | 97761.962 | 112162.3634 | 128718.7083 | 147755.67 | 169646.4934 | 194820.0136 | 208725.6327 | 208540.0496 | 208278.6489 | 207909.7534 | 207388.2719
| TRUE | 19 | 22003620 | AC | AC033 | 11 | AC33 | FEEDER MANAGEMENT | X | ABB | RACIB_3147 | RACIB 3147 | RACIB | Electronic |  | 0.81881 | 2190 |  | 8.25 | 0.026286 | 0.02098 | 0.0053053 | 171.7211 | 6461.9364 | 6633.6575 | 193.7249 | 10.7267 | 24.602 |  | 13.322 | 0.096648 | 0.077141 | 0.019507 | 631.391 | 23759.5113 | 24390.9024 | 712.2955 | 39.4403 | 90.4577 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 31.2695 | 1.7854 | 33.0549 | 14.7027 | 2.0677 | 0.0067973 |  | 6862.711 | 25233.0959 | 49.8321 | 25183.2638 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.023821 | 0.027068 | 0.030782 | 0.035031 | 0.039894 | 0.045463 | 0.051843 | 0.059153 | 0.067532 | 0.077141 | 0.088163 | 0.10081 | 0.11533 | 0.13199 | 0.15113 | 0.17311 | 0.19836 | 0.22738 | 0.26074 | 0.29909 | 0.34319 | 0.39392 | 0.45226 | 0.51939 | 0.59664 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 7791.9046 | 8854.0879 | 10068.8452 | 11458.6952 | 13049.5354 | 14871.1547 | 16957.8234 | 19348.9745 | 22089.988 | 25233.0959 | 28838.4252 | 32975.2009 | 37723.1329 | 43174.0154 | 49433.5718 | 56623.582 | 64884.3364 | 74377.4659 | 85289.2071 | 97834.1678 | 112259.6723 | 128850.7728 | 147936.0317 | 169894.1935 | 195161.881 | 209199.5382 | 209199.5382 | 209199.5382 | 209199.5382 | 209199.5382 |  | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 34.0508 | 40.7567 | 54.0255 | 72.2394 | 97.3541 | 132.1258 | 180.4454 | 247.815 | 342.0259 | 474.1252 | 659.7944 | 921.3162 | 1290.3829 | 1812.1061 |  | 194.9717 | 221.55 | 251.946 | 286.7233 | 326.5299 | 372.1111 | 424.3244 | 484.1566 | 552.7431 | 631.391 | 721.6048 | 825.1166 | 943.921 | 1080.3148 | 1236.9435 | 1416.8544 | 1623.5578 | 1861.0981 | 2134.1353 | 2448.0396 | 2808.9994 | 3224.1476 | 3701.7054 | 4251.1499 | 4883.4065 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 |  | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 18.7138 | 24.8063 | 33.1694 | 44.701 | 60.6668 | 82.8532 | 113.7865 | 157.0444 | 217.699 | 302.9507 | 423.0308 | 592.4912 | 832.0452 |  | 179.3369 | 205.9152 | 236.3113 | 271.0886 | 310.8951 | 356.4763 | 408.6896 | 468.5218 | 537.1084 | 615.7563 | 705.9701 | 809.4819 | 928.2862 | 1064.68 | 1221.3088 | 1401.2196 | 1607.923 | 1842.3842 | 2109.3291 | 2414.8702 | 2764.2984 | 3163.4808 | 3618.8522 | 4137.3634 | 4726.3622 | 5016.9625 | 4931.7108 | 4811.6307 | 4642.1703 | 4402.6163 |  | 7336.8661 | 8337.0191 | 9480.8359 | 10789.5202 | 12287.4572 | 14002.6959 | 15967.5055 | 18219.0161 | 20799.9574 | 23759.5113 | 27154.2934 | 31049.4861 | 35520.1441 | 40652.7012 | 46546.7065 | 53316.8282 | 61095.1637 | 70033.9051 | 80308.4128 | 92120.7618 | 105703.833 | 121326.0318 | 139296.7329 | 159972.5626 | 183764.6454 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 |  | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.9427 | 2.5752 | 3.4434 | 4.6405 | 6.2979 | 8.6011 | 11.8123 | 16.303 | 22.5996 | 31.4497 | 43.9154 | 61.5073 | 86.3757 |  | 7335.2431 | 8335.396 | 9479.2128 | 10787.8971 | 12285.8341 | 14001.0728 | 15965.8825 | 18217.393 | 20798.3344 | 23757.8883 | 27152.6704 | 31047.863 | 35518.521 | 40651.0781 | 46545.0834 | 53315.2051 | 61093.5407 | 70031.9624 | 80305.8376 | 92117.3185 | 105699.1926 | 121319.7339 | 139288.1318 | 159960.7503 | 183748.3425 | 196959.9195 | 196951.0694 | 196938.6037 | 196921.0118 | 196896.1434 |  | 7514.58 | 8541.3112 | 9715.5241 | 11058.9857 | 12596.7292 | 14357.5491 | 16374.5721 | 18685.9148 | 21335.4427 | 24373.6445 | 27858.6404 | 31857.3448 | 36446.8072 | 41715.7581 | 47766.3922 | 54716.4247 | 62701.4637 | 71874.3466 | 82415.1666 | 94532.1887 | 108463.491 | 124483.2147 | 142906.984 | 164098.1136 | 188474.7046 | 201976.882 | 201882.7802 | 201750.2344 | 201563.1822 | 201298.7597 |  | 219.9547 | 249.9387 | 284.2296 | 323.4632 | 368.3704 | 419.7922 | 478.696 | 546.1949 | 623.5699 | 712.2955 | 814.069 | 930.8445 | 1064.8721 | 1218.743 | 1395.4416 | 1598.4057 | 1831.5954 | 2099.5734 | 2407.5968 | 2761.7238 | 3168.9359 | 3637.2798 | 4176.0304 | 4795.8791 | 5509.1511 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 205.252 | 235.236 | 269.5269 | 308.7605 | 353.6677 | 405.0895 | 463.9933 | 531.4922 | 608.8672 | 697.5928 | 799.3663 | 916.1418 | 1050.1694 | 1204.0403 | 1380.7389 | 1583.703 | 1816.8927 | 2081.9752 | 2384.2694 | 2730.5318 | 3126.8997 | 3580.2297 | 4098.1165 | 4688.8759 | 5361.4689 | 5700.6939 | 5620.5245 | 5507.6029 | 5348.2449 | 5122.9719 |  | 12.179 | 13.8393 | 15.738 | 17.9104 | 20.3969 | 23.2442 | 26.5057 | 30.2432 | 34.5275 | 39.4403 | 45.0756 | 51.5415 | 58.9627 | 67.4826 | 77.2666 | 88.5048 | 101.4167 | 116.2548 | 133.3103 | 152.9185 | 175.4661 | 201.3987 | 231.2296 | 265.5511 | 305.0454 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 10.1113 | 11.7715 | 13.6702 | 15.8426 | 18.3292 | 21.1764 | 24.438 | 28.1754 | 32.4597 | 37.3725 | 43.0078 | 49.4737 | 56.8949 | 65.4149 | 75.1988 | 86.4371 | 99.3489 | 113.7798 | 130.0296 | 148.5318 | 169.5543 | 193.3753 | 220.272 | 250.5024 | 284.2758 | 298.1954 | 286.9206 | 271.0396 | 248.6279 | 216.9461 |  | 27.9331 | 31.7409 | 36.0956 | 41.0781 | 46.7811 | 53.3114 | 60.7918 | 69.3638 | 79.19 | 90.4577 | 103.3824 | 118.2122 | 135.233 | 154.7738 | 177.2136 | 202.9889 | 232.6028 | 266.6345 | 305.7519 | 350.7241 | 402.4378 | 461.915 | 530.3334 | 609.0509 | 699.6326 | 749.9559 | 749.9559 | 749.9559 | 749.9559 | 749.9559 |  | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0067973 | 0.0081359 | 0.010785 | 0.014421 | 0.019434 | 0.026375 | 0.036021 | 0.049469 | 0.068276 | 0.094646 | 0.13171 | 0.18392 | 0.25759 | 0.36174 |  | 27.9263 | 31.7341 | 36.0888 | 41.0713 | 46.7743 | 53.3046 | 60.785 | 69.357 | 79.1832 | 90.4509 | 103.3756 | 118.2055 | 135.2262 | 154.767 | 177.2068 | 202.9821 | 232.596 | 266.6264 | 305.7411 | 350.7097 | 402.4184 | 461.8886 | 530.2974 | 609.0014 | 699.5643 | 749.8613 | 749.8242 | 749.772 | 749.6984 | 749.5942 |  | 7757.8696 | 8820.0529 | 10034.8101 | 11424.6601 | 13015.5004 | 14837.1196 | 16923.7884 | 19314.9395 | 22055.953 | 25199.0608 | 28804.3901 | 32941.1658 | 37689.0978 | 43139.9803 | 49399.5367 | 56589.547 | 64850.3013 | 74336.7281 | 85235.2066 | 97761.962 | 112162.3634 | 128718.7083 | 147755.67 | 169646.4934 | 194820.0136 | 208725.6327 | 208540.0496 | 208278.6489 | 207909.7534 | 207388.2719
| TRUE | 20 | 22003595 | AC | Blank | 11 | ALL FEEDERS | BACKUP EARTH FAULT | BU | ASEA | GROUP_3094 | GROUP 3094 | GROUP 3000s | Electronic |  | 0.15703 | 2190 |  | 9.9 | 0.042792 | 0.015079 | 0.027713 | 268.0149 | 4644.3638 | 4912.3788 | 207.0778 | 17.2719 | 13.7212 |  | 16.4925 | 0.17586 | 0.061971 | 0.11389 | 1101.4711 | 19087.1183 | 20188.5895 | 851.0357 | 70.983 | 56.3907 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 31.2667 | 0.34239 | 31.6091 | 14.6761 | 2.0677 | 0.0010116 |  | 5150.4498 | 21166.9988 | 48.3539 | 21118.645 |  | 0.051037 |  | 10.4184 | 10.9639 | 11.538 | 12.1422 | 12.778 | 13.447 | 14.1511 | 14.8921 | 15.6719 | 16.4925 | 17.3561 | 18.2649 | 19.2213 | 20.2278 | 21.287 | 22.4016 | 23.5746 | 24.809 | 26.108 | 27.4751 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049141 | 0.056475 | 0.06495 | 0.074748 | 0.086081 | 0.099192 | 0.11437 | 0.13194 | 0.15229 | 0.17586 | 0.20319 | 0.23486 | 0.27158 | 0.31417 | 0.36358 | 0.42091 | 0.48745 | 0.5647 | 0.65438 | 0.75852 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.017316 | 0.019901 | 0.022887 | 0.02634 | 0.030333 | 0.034953 | 0.040301 | 0.046493 | 0.053663 | 0.061971 | 0.071599 | 0.082759 | 0.0957 | 0.11071 | 0.12812 | 0.14832 | 0.17177 | 0.19899 | 0.23059 | 0.26729 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 5914.5978 | 6797.2943 | 7817.3719 | 8996.6981 | 10360.6699 | 11938.7876 | 13765.3234 | 15880.1001 | 18329.3958 | 21166.9988 | 24455.4341 | 28267.3915 | 32687.3891 | 37813.7086 | 43760.6494 | 50661.1531 | 58669.8589 | 67966.6624 | 78760.8594 | 91295.9707 | 96441.7224 | 96441.7224 | 96441.7224 | 96441.7224 | 96441.7224 | 96441.7224 | 96441.7224 | 96441.7224 | 96441.7224 | 96441.7224 |  | 32.6924 | 32.6924 | 32.6924 | 32.6924 | 32.6924 | 32.6924 | 32.6924 | 32.6924 | 32.6924 | 32.6924 | 32.6924 | 32.6924 | 32.6924 | 32.6924 | 32.6924 | 32.6924 | 32.6924 | 39.1308 | 51.8702 | 69.3575 | 93.4703 | 126.8548 | 173.2468 | 237.9288 | 328.3814 | 455.2108 | 633.473 | 884.5618 | 1238.9051 | 1739.8151 |  | 307.779 | 353.7121 | 406.7941 | 468.1629 | 539.1402 | 621.261 | 716.3088 | 826.3558 | 953.8103 | 1101.4711 | 1272.5921 | 1470.9556 | 1700.9599 | 1967.7192 | 2277.1812 | 2636.2641 | 3053.0146 | 3536.7941 | 4098.4938 | 4750.7858 | 5018.5563 | 5018.5563 | 5018.5563 | 5018.5563 | 5018.5563 | 5018.5563 | 5018.5563 | 5018.5563 | 5018.5563 | 5018.5563 |  | 15.6333 | 15.6333 | 15.6333 | 15.6333 | 15.6333 | 15.6333 | 15.6333 | 15.6333 | 15.6333 | 15.6333 | 15.6333 | 15.6333 | 15.6333 | 15.6333 | 15.6333 | 15.6333 | 15.6333 | 18.7121 | 24.804 | 33.1664 | 44.697 | 60.6613 | 82.8456 | 113.7762 | 157.0301 | 217.6792 | 302.9232 | 422.9925 | 592.4375 | 831.9698 |  | 292.1457 | 338.0788 | 391.1607 | 452.5296 | 523.5068 | 605.6276 | 700.6754 | 810.7224 | 938.1769 | 1085.8378 | 1256.9587 | 1455.3223 | 1685.3265 | 1952.0858 | 2261.5479 | 2620.6307 | 3037.3813 | 3518.082 | 4073.6898 | 4717.6194 | 4973.8593 | 4957.895 | 4935.7106 | 4904.78 | 4861.5261 | 4800.877 | 4715.6331 | 4595.5638 | 4426.1188 | 4186.5865 |  | 5333.4263 | 6129.3886 | 7049.2328 | 8112.6778 | 9342.625 | 10765.676 | 12412.7355 | 14319.713 | 16528.3397 | 19087.1183 | 22052.4302 | 25489.8227 | 29475.509 | 34098.1136 | 39460.7049 | 45683.1614 | 52904.9275 | 61288.2223 | 71021.7757 | 82325.1804 | 86965.3078 | 86965.3078 | 86965.3078 | 86965.3078 | 86965.3078 | 86965.3078 | 86965.3078 | 86965.3078 | 86965.3078 | 86965.3078 |  | 0.31126 | 0.31126 | 0.31126 | 0.31126 | 0.31126 | 0.31126 | 0.31126 | 0.31126 | 0.31126 | 0.31126 | 0.31126 | 0.31126 | 0.31126 | 0.31126 | 0.31126 | 0.31126 | 0.31126 | 0.37256 | 0.49386 | 0.66035 | 0.88993 | 1.2078 | 1.6495 | 2.2653 | 3.1265 | 4.3341 | 6.0313 | 8.4219 | 11.7956 | 16.5647 |  | 5333.115 | 6129.0773 | 7048.9215 | 8112.3666 | 9342.3138 | 10765.3647 | 12412.4242 | 14319.4018 | 16528.0284 | 19086.8071 | 22052.1189 | 25489.5114 | 29475.1977 | 34097.8024 | 39460.3936 | 45682.8501 | 52904.6163 | 61287.8497 | 71021.2818 | 82324.52 | 86964.4179 | 86964.1 | 86963.6583 | 86963.0425 | 86962.1813 | 86960.9738 | 86959.2765 | 86956.8859 | 86953.5122 | 86948.7431 |  | 5625.2607 | 6467.1561 | 7440.0822 | 8564.8961 | 9865.8206 | 11370.9923 | 13113.0996 | 15130.1242 | 17466.2053 | 20172.6449 | 23309.0776 | 26944.8337 | 31160.5243 | 36049.8882 | 41721.9415 | 48303.4808 | 55941.9975 | 64805.9317 | 75094.9716 | 87042.1395 | 91938.2772 | 91921.995 | 91899.369 | 91867.8225 | 91823.7075 | 91761.8508 | 91674.9096 | 91552.4497 | 91379.631 | 91135.3296 |  | 237.801 | 273.2905 | 314.3035 | 361.7193 | 416.5588 | 480.0083 | 553.4456 | 638.4718 | 736.9477 | 851.0357 | 983.2498 | 1136.5125 | 1314.222 | 1520.3296 | 1759.431 | 2036.8712 | 2358.8674 | 2732.6527 | 3166.6418 | 3670.6257 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 223.1249 | 258.6144 | 299.6274 | 347.0432 | 401.8827 | 465.3322 | 538.7695 | 623.7957 | 722.2716 | 836.3596 | 968.5737 | 1121.8364 | 1299.5459 | 1505.6535 | 1744.7549 | 2022.1951 | 2344.1913 | 2715.0863 | 3143.3565 | 3639.4902 | 3835.5545 | 3820.5678 | 3799.7417 | 3770.7051 | 3730.0997 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 19.8345 | 22.7946 | 26.2154 | 30.1702 | 34.7442 | 40.0364 | 46.1617 | 53.2535 | 61.4672 | 70.983 | 82.0107 | 94.794 | 109.6163 | 126.8073 | 146.7502 | 169.8909 | 196.7479 | 227.9245 | 264.1225 | 306.1587 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 17.7668 | 20.7269 | 24.1477 | 28.1025 | 32.6765 | 37.9687 | 44.094 | 51.1858 | 59.3995 | 68.9153 | 79.943 | 92.7263 | 107.5486 | 124.7396 | 144.6825 | 167.8232 | 194.6802 | 225.4496 | 260.8419 | 301.772 | 317.5031 | 315.3917 | 312.4575 | 308.3665 | 302.6457 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 15.757 | 18.1086 | 20.8261 | 23.968 | 27.6017 | 31.8059 | 36.672 | 42.3059 | 48.831 | 56.3907 | 65.1513 | 75.3067 | 87.0819 | 100.7389 | 116.582 | 134.9656 | 156.3014 | 181.0689 | 209.8255 | 243.2201 | 256.9288 | 256.9288 | 256.9288 | 256.9288 | 256.9288 | 256.9288 | 256.9288 | 256.9288 | 256.9288 | 256.9288 |  | 0.0010116 | 0.0010116 | 0.0010116 | 0.0010116 | 0.0010116 | 0.0010116 | 0.0010116 | 0.0010116 | 0.0010116 | 0.0010116 | 0.0010116 | 0.0010116 | 0.0010116 | 0.0010116 | 0.0010116 | 0.0010116 | 0.0010116 | 0.0012108 | 0.0016049 | 0.002146 | 0.0028921 | 0.0039251 | 0.0053605 | 0.0073619 | 0.010161 | 0.014085 | 0.019601 | 0.02737 | 0.038334 | 0.053832 |  | 15.756 | 18.1076 | 20.8251 | 23.9669 | 27.6007 | 31.8049 | 36.671 | 42.3049 | 48.83 | 56.3896 | 65.1503 | 75.3057 | 87.0809 | 100.7379 | 116.581 | 134.9645 | 156.3004 | 181.0677 | 209.8239 | 243.218 | 256.9259 | 256.9249 | 256.9235 | 256.9215 | 256.9187 | 256.9148 | 256.9092 | 256.9015 | 256.8905 | 256.875 |  | 5881.9084 | 6764.6049 | 7784.6824 | 8964.0087 | 10327.9805 | 11906.0981 | 13732.634 | 15847.4106 | 18296.7064 | 21134.3094 | 24422.7446 | 28234.7021 | 32654.6997 | 37781.0192 | 43727.96 | 50628.4636 | 58637.1694 | 67927.5353 | 78708.994 | 91226.6196 | 96348.2608 | 96314.8794 | 96268.4917 | 96203.8156 | 96113.3715 | 95986.5538 | 95808.3081 | 95557.2425 | 95202.932 | 94702.0684
| TRUE | 21 | 22003594 | AC | Blank | 11 | ALL FEEDERS | MASTER EARTH FAULT | X | ASEA | GROUP_3101 | GROUP 3101 | GROUP 3000s | Electronic |  | 0.81881 | 2190 |  | 9.9 | 0.042792 | 0.034155 | 0.0086369 | 279.556 | 10519.8097 | 10799.3657 | 315.3774 | 17.4627 | 31.0795 |  | 16.4925 | 0.17586 | 0.14037 | 0.035495 | 1148.9019 | 43233.6612 | 44382.563 | 1296.1186 | 71.767 | 127.7288 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 31.2695 | 1.7854 | 33.0549 | 14.7027 | 2.0677 | 0.0052747 |  | 11163.2853 | 45878.1774 | 49.8306 | 45828.3468 |  | 0.051037 |  | 10.4184 | 10.9639 | 11.538 | 12.1422 | 12.778 | 13.447 | 14.1511 | 14.8921 | 15.6719 | 16.4925 | 17.3561 | 18.2649 | 19.2213 | 20.2278 | 21.287 | 22.4016 | 23.5746 | 24.809 | 26.108 | 27.4751 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049141 | 0.056475 | 0.06495 | 0.074748 | 0.086081 | 0.099192 | 0.11437 | 0.13194 | 0.15229 | 0.17586 | 0.20319 | 0.23486 | 0.27158 | 0.31417 | 0.36358 | 0.42091 | 0.48745 | 0.5647 | 0.65438 | 0.75852 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.039223 | 0.045076 | 0.051841 | 0.059662 | 0.068707 | 0.079172 | 0.091285 | 0.10531 | 0.12155 | 0.14037 | 0.16218 | 0.18746 | 0.21677 | 0.25076 | 0.2902 | 0.33596 | 0.38907 | 0.45072 | 0.5223 | 0.60543 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 12819.5295 | 14732.7204 | 16943.6761 | 19499.7938 | 22456.1194 | 25876.593 | 29835.4979 | 34419.1471 | 39727.8461 | 45878.1774 | 53005.6599 | 61267.8449 | 70847.9198 | 81958.9043 | 94848.5354 | 109804.9556 | 127163.3363 | 147313.5904 | 170709.3531 | 197878.4414 | 209031.5441 | 209031.5441 | 209031.5441 | 209031.5441 | 209031.5441 | 209031.5441 | 209031.5441 | 209031.5441 | 209031.5441 | 209031.5441 |  | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 40.7549 | 54.023 | 72.2361 | 97.3497 | 132.1198 | 180.4373 | 247.8039 | 342.0106 | 474.104 | 659.7649 | 921.275 | 1290.3252 | 1812.0251 |  | 321.0324 | 368.9434 | 424.3111 | 488.3226 | 562.3562 | 648.0132 | 747.1539 | 861.9397 | 994.8825 | 1148.9019 | 1327.3915 | 1534.2968 | 1774.2053 | 2052.4516 | 2375.2395 | 2749.7849 | 3184.4812 | 3689.0929 | 4274.98 | 4955.3605 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 |  | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 18.7138 | 24.8063 | 33.1694 | 44.701 | 60.6668 | 82.8532 | 113.7865 | 157.0444 | 217.699 | 302.9507 | 423.0308 | 592.4912 | 832.0452 |  | 305.3976 | 353.3086 | 408.6764 | 472.6878 | 546.7214 | 632.3785 | 731.5191 | 846.3049 | 979.2477 | 1133.2671 | 1311.7567 | 1518.662 | 1758.5706 | 2036.8168 | 2359.6047 | 2734.1501 | 3168.8464 | 3670.379 | 4250.1738 | 4922.1911 | 5189.9605 | 5173.9947 | 5151.8084 | 5120.875 | 5077.6172 | 5016.9625 | 4931.7108 | 4811.6307 | 4642.1703 | 4402.6163 |  | 12080.5844 | 13883.4949 | 15967.0064 | 18375.784 | 21161.7007 | 24385.0109 | 28115.716 | 32435.1539 | 37437.8482 | 43233.6612 | 49950.3004 | 57736.2354 | 66764.0943 | 77234.6179 | 89381.2631 | 103475.5632 | 119833.3698 | 138822.1202 | 160869.3011 | 186472.3051 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 |  | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.9427 | 2.5752 | 3.4434 | 4.6405 | 6.2979 | 8.6011 | 11.8123 | 16.303 | 22.5996 | 31.4497 | 43.9154 | 61.5073 | 86.3757 |  | 12078.9613 | 13881.8718 | 15965.3834 | 18374.161 | 21160.0776 | 24383.3878 | 28114.093 | 32433.5309 | 37436.2251 | 43232.0381 | 49948.6773 | 57734.6123 | 66762.4712 | 77232.9948 | 89379.64 | 103473.9402 | 119831.7468 | 138820.1775 | 160866.7259 | 186468.8618 | 196977.8786 | 196976.2212 | 196973.918 | 196970.7068 | 196966.2161 | 196959.9195 | 196951.0694 | 196938.6037 | 196921.0118 | 196896.1434 |  | 12384.359 | 14235.1804 | 16374.0597 | 18846.8488 | 21706.7991 | 25015.7663 | 28845.6121 | 33279.8358 | 38415.4728 | 44365.3052 | 51260.434 | 59253.2743 | 68521.0418 | 79269.8116 | 91739.2447 | 106208.0903 | 123000.5932 | 142490.5565 | 165116.8997 | 191391.0529 | 202167.8391 | 202150.2159 | 202125.7264 | 202091.5817 | 202043.8333 | 201976.882 | 201882.7802 | 201750.2344 | 201563.1822 | 201298.7597 |  | 362.1685 | 416.2186 | 478.681 | 550.8947 | 634.4148 | 731.0476 | 842.8919 | 972.386 | 1122.3637 | 1296.1186 | 1497.4793 | 1730.8968 | 2001.5465 | 2315.4463 | 2679.5953 | 3102.1338 | 3592.5307 | 4161.8018 | 4822.7627 | 5590.325 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 347.4658 | 401.5159 | 463.9783 | 536.192 | 619.7121 | 716.3449 | 828.1892 | 957.6833 | 1107.661 | 1281.4159 | 1482.7766 | 1716.1941 | 1986.8438 | 2300.7437 | 2664.8926 | 3087.4311 | 3577.828 | 4144.2036 | 4799.4353 | 5559.1331 | 5863.3786 | 5848.3647 | 5827.5009 | 5798.4116 | 5757.7326 | 5700.6939 | 5620.5245 | 5507.6029 | 5348.2449 | 5122.9719 |  | 20.0535 | 23.0463 | 26.5049 | 30.5034 | 35.128 | 40.4786 | 46.6715 | 53.8417 | 62.146 | 71.767 | 82.9164 | 95.8409 | 110.827 | 128.2078 | 148.371 | 171.7673 | 198.9209 | 230.4418 | 267.0397 | 309.5401 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 17.9858 | 20.9786 | 24.4371 | 28.4357 | 33.0602 | 38.4109 | 44.6037 | 51.7739 | 60.0783 | 69.6992 | 80.8487 | 93.7732 | 108.7592 | 126.1401 | 146.3033 | 169.6995 | 196.8531 | 227.9668 | 263.7589 | 305.1533 | 321.075 | 318.9635 | 316.0292 | 311.9382 | 306.2172 | 298.1954 | 286.9206 | 271.0396 | 248.6279 | 216.9461 |  | 35.6907 | 41.0172 | 47.1727 | 54.2891 | 62.5198 | 72.0427 | 83.0646 | 95.8259 | 110.6057 | 127.7288 | 147.5723 | 170.575 | 197.2467 | 228.1807 | 264.0665 | 305.7065 | 354.0337 | 410.1337 | 475.2695 | 550.9106 | 581.9618 | 581.9618 | 581.9618 | 581.9618 | 581.9618 | 581.9618 | 581.9618 | 581.9618 | 581.9618 | 581.9618 |  | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0063135 | 0.0083689 | 0.01119 | 0.015081 | 0.020467 | 0.027952 | 0.038388 | 0.052982 | 0.073445 | 0.10221 | 0.14272 | 0.19989 | 0.28071 |  | 35.6854 | 41.0119 | 47.1674 | 54.2838 | 62.5145 | 72.0374 | 83.0593 | 95.8206 | 110.6005 | 127.7235 | 147.567 | 170.5697 | 197.2414 | 228.1754 | 264.0612 | 305.7012 | 354.0284 | 410.1274 | 475.2612 | 550.8994 | 581.9467 | 581.9414 | 581.9339 | 581.9234 | 581.9088 | 581.8884 | 581.8596 | 581.8191 | 581.7619 | 581.6811 |  | 12785.4959 | 14698.6868 | 16909.6426 | 19465.7603 | 22422.0859 | 25842.5594 | 29801.4644 | 34385.1136 | 39693.8126 | 45844.1438 | 52971.6264 | 61233.8114 | 70813.8863 | 81924.8708 | 94814.5018 | 109770.922 | 127129.3028 | 147272.8544 | 170655.3551 | 197806.2387 | 208934.2394 | 208899.4854 | 208851.1904 | 208783.855 | 208689.6919 | 208557.6597 | 208372.0849 | 208110.696 | 207741.8169 | 207220.3588
| TRUE | 22 | 22015634 | AC | Blank | 11 | ALL FEEDERS | MASTER EARTH FAULT | X | ABB | SPAJ_3330 | SPAJ 3330 | SPAJ | Electronic |  | 0.81881 | 2190 |  | 9.9 | 0.042792 | 0.034155 | 0.0086369 | 279.556 | 10519.8097 | 10799.3657 | 315.3774 | 17.4627 | 31.0795 |  | 16.4925 | 0.17586 | 0.14037 | 0.035495 | 1148.9019 | 43233.6612 | 44382.563 | 1296.1186 | 71.767 | 127.7288 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 31.2695 | 1.7854 | 33.0549 | 14.7027 | 2.0677 | 0.0052747 |  | 11163.2853 | 45878.1774 | 49.8306 | 45828.3468 |  | 0.051037 |  | 10.4184 | 10.9639 | 11.538 | 12.1422 | 12.778 | 13.447 | 14.1511 | 14.8921 | 15.6719 | 16.4925 | 17.3561 | 18.2649 | 19.2213 | 20.2278 | 21.287 | 22.4016 | 23.5746 | 24.809 | 26.108 | 27.4751 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049141 | 0.056475 | 0.06495 | 0.074748 | 0.086081 | 0.099192 | 0.11437 | 0.13194 | 0.15229 | 0.17586 | 0.20319 | 0.23486 | 0.27158 | 0.31417 | 0.36358 | 0.42091 | 0.48745 | 0.5647 | 0.65438 | 0.75852 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.039223 | 0.045076 | 0.051841 | 0.059662 | 0.068707 | 0.079172 | 0.091285 | 0.10531 | 0.12155 | 0.14037 | 0.16218 | 0.18746 | 0.21677 | 0.25076 | 0.2902 | 0.33596 | 0.38907 | 0.45072 | 0.5223 | 0.60543 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 12819.5295 | 14732.7204 | 16943.6761 | 19499.7938 | 22456.1194 | 25876.593 | 29835.4979 | 34419.1471 | 39727.8461 | 45878.1774 | 53005.6599 | 61267.8449 | 70847.9198 | 81958.9043 | 94848.5354 | 109804.9556 | 127163.3363 | 147313.5904 | 170709.3531 | 197878.4414 | 209031.5441 | 209031.5441 | 209031.5441 | 209031.5441 | 209031.5441 | 209031.5441 | 209031.5441 | 209031.5441 | 209031.5441 | 209031.5441 |  | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 34.0493 | 40.7549 | 54.023 | 72.2361 | 97.3497 | 132.1198 | 180.4373 | 247.8039 | 342.0106 | 474.104 | 659.7649 | 921.275 | 1290.3252 | 1812.0251 |  | 321.0324 | 368.9434 | 424.3111 | 488.3226 | 562.3562 | 648.0132 | 747.1539 | 861.9397 | 994.8825 | 1148.9019 | 1327.3915 | 1534.2968 | 1774.2053 | 2052.4516 | 2375.2395 | 2749.7849 | 3184.4812 | 3689.0929 | 4274.98 | 4955.3605 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 | 5234.6615 |  | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 15.6348 | 18.7138 | 24.8063 | 33.1694 | 44.701 | 60.6668 | 82.8532 | 113.7865 | 157.0444 | 217.699 | 302.9507 | 423.0308 | 592.4912 | 832.0452 |  | 305.3976 | 353.3086 | 408.6764 | 472.6878 | 546.7214 | 632.3785 | 731.5191 | 846.3049 | 979.2477 | 1133.2671 | 1311.7567 | 1518.662 | 1758.5706 | 2036.8168 | 2359.6047 | 2734.1501 | 3168.8464 | 3670.379 | 4250.1738 | 4922.1911 | 5189.9605 | 5173.9947 | 5151.8084 | 5120.875 | 5077.6172 | 5016.9625 | 4931.7108 | 4811.6307 | 4642.1703 | 4402.6163 |  | 12080.5844 | 13883.4949 | 15967.0064 | 18375.784 | 21161.7007 | 24385.0109 | 28115.716 | 32435.1539 | 37437.8482 | 43233.6612 | 49950.3004 | 57736.2354 | 66764.0943 | 77234.6179 | 89381.2631 | 103475.5632 | 119833.3698 | 138822.1202 | 160869.3011 | 186472.3051 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 | 196982.5191 |  | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.9427 | 2.5752 | 3.4434 | 4.6405 | 6.2979 | 8.6011 | 11.8123 | 16.303 | 22.5996 | 31.4497 | 43.9154 | 61.5073 | 86.3757 |  | 12078.9613 | 13881.8718 | 15965.3834 | 18374.161 | 21160.0776 | 24383.3878 | 28114.093 | 32433.5309 | 37436.2251 | 43232.0381 | 49948.6773 | 57734.6123 | 66762.4712 | 77232.9948 | 89379.64 | 103473.9402 | 119831.7468 | 138820.1775 | 160866.7259 | 186468.8618 | 196977.8786 | 196976.2212 | 196973.918 | 196970.7068 | 196966.2161 | 196959.9195 | 196951.0694 | 196938.6037 | 196921.0118 | 196896.1434 |  | 12384.359 | 14235.1804 | 16374.0597 | 18846.8488 | 21706.7991 | 25015.7663 | 28845.6121 | 33279.8358 | 38415.4728 | 44365.3052 | 51260.434 | 59253.2743 | 68521.0418 | 79269.8116 | 91739.2447 | 106208.0903 | 123000.5932 | 142490.5565 | 165116.8997 | 191391.0529 | 202167.8391 | 202150.2159 | 202125.7264 | 202091.5817 | 202043.8333 | 201976.882 | 201882.7802 | 201750.2344 | 201563.1822 | 201298.7597 |  | 362.1685 | 416.2186 | 478.681 | 550.8947 | 634.4148 | 731.0476 | 842.8919 | 972.386 | 1122.3637 | 1296.1186 | 1497.4793 | 1730.8968 | 2001.5465 | 2315.4463 | 2679.5953 | 3102.1338 | 3592.5307 | 4161.8018 | 4822.7627 | 5590.325 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 347.4658 | 401.5159 | 463.9783 | 536.192 | 619.7121 | 716.3449 | 828.1892 | 957.6833 | 1107.661 | 1281.4159 | 1482.7766 | 1716.1941 | 1986.8438 | 2300.7437 | 2664.8926 | 3087.4311 | 3577.828 | 4144.2036 | 4799.4353 | 5559.1331 | 5863.3786 | 5848.3647 | 5827.5009 | 5798.4116 | 5757.7326 | 5700.6939 | 5620.5245 | 5507.6029 | 5348.2449 | 5122.9719 |  | 20.0535 | 23.0463 | 26.5049 | 30.5034 | 35.128 | 40.4786 | 46.6715 | 53.8417 | 62.146 | 71.767 | 82.9164 | 95.8409 | 110.827 | 128.2078 | 148.371 | 171.7673 | 198.9209 | 230.4418 | 267.0397 | 309.5401 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 17.9858 | 20.9786 | 24.4371 | 28.4357 | 33.0602 | 38.4109 | 44.6037 | 51.7739 | 60.0783 | 69.6992 | 80.8487 | 93.7732 | 108.7592 | 126.1401 | 146.3033 | 169.6995 | 196.8531 | 227.9668 | 263.7589 | 305.1533 | 321.075 | 318.9635 | 316.0292 | 311.9382 | 306.2172 | 298.1954 | 286.9206 | 271.0396 | 248.6279 | 216.9461 |  | 35.6907 | 41.0172 | 47.1727 | 54.2891 | 62.5198 | 72.0427 | 83.0646 | 95.8259 | 110.6057 | 127.7288 | 147.5723 | 170.575 | 197.2467 | 228.1807 | 264.0665 | 305.7065 | 354.0337 | 410.1337 | 475.2695 | 550.9106 | 581.9618 | 581.9618 | 581.9618 | 581.9618 | 581.9618 | 581.9618 | 581.9618 | 581.9618 | 581.9618 | 581.9618 |  | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0052747 | 0.0063135 | 0.0083689 | 0.01119 | 0.015081 | 0.020467 | 0.027952 | 0.038388 | 0.052982 | 0.073445 | 0.10221 | 0.14272 | 0.19989 | 0.28071 |  | 35.6854 | 41.0119 | 47.1674 | 54.2838 | 62.5145 | 72.0374 | 83.0593 | 95.8206 | 110.6005 | 127.7235 | 147.567 | 170.5697 | 197.2414 | 228.1754 | 264.0612 | 305.7012 | 354.0284 | 410.1274 | 475.2612 | 550.8994 | 581.9467 | 581.9414 | 581.9339 | 581.9234 | 581.9088 | 581.8884 | 581.8596 | 581.8191 | 581.7619 | 581.6811 |  | 12785.4959 | 14698.6868 | 16909.6426 | 19465.7603 | 22422.0859 | 25842.5594 | 29801.4644 | 34385.1136 | 39693.8126 | 45844.1438 | 52971.6264 | 61233.8114 | 70813.8863 | 81924.8708 | 94814.5018 | 109770.922 | 127129.3028 | 147272.8544 | 170655.3551 | 197806.2387 | 208934.2394 | 208899.4854 | 208851.1904 | 208783.855 | 208689.6919 | 208557.6597 | 208372.0849 | 208110.696 | 207741.8169 | 207220.3588
| TRUE | 23 | 22003641 | AC | Blank | 66 | CB B | CB FAIL | X | ASEA | GROUP_3095 | GROUP 3095 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 494.2485 | 0 | 494.2485 | 121.4703 | 17.1211 | 0 |  | 16.4925 | 0.17586 | 0 | 0.17586 | 2031.2319 | 0 | 2031.2319 | 499.211 | 70.3633 | 0 |  | 0.0051679 | 0 | 0.0051679 | 59.6897 | 0 | 59.6897 | 14.6698 | 2.0677 | 0 |  | 632.8399 | 2600.8062 | 76.4271 | 2524.379 |  | 0.051037 |  | 10.4184 | 10.9639 | 11.538 | 12.1422 | 12.778 | 13.447 | 14.1511 | 14.8921 | 15.6719 | 16.4925 | 17.3561 | 18.2649 | 19.2213 | 20.2278 | 21.287 | 22.4016 | 23.5746 | 24.809 | 26.108 | 27.4751 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049141 | 0.056475 | 0.06495 | 0.074748 | 0.086081 | 0.099192 | 0.11437 | 0.13194 | 0.15229 | 0.17586 | 0.20319 | 0.23486 | 0.27158 | 0.31417 | 0.36358 | 0.42091 | 0.48745 | 0.5647 | 0.65438 | 0.75852 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726.7314 | 835.189 | 960.5268 | 1105.4315 | 1273.0238 | 1466.9284 | 1691.3564 | 1951.2007 | 2252.1476 | 2600.8062 | 3004.8588 | 3473.2371 | 4016.3258 | 4646.2008 | 5376.9062 | 6224.7766 | 7208.8127 | 8351.1184 | 9677.4101 | 11217.6093 | 11849.872 | 11849.872 | 11849.872 | 11849.872 | 11849.872 | 11849.872 | 11849.872 | 11849.872 | 11849.872 | 11849.872 |  | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 55.7561 | 73.908 | 98.825 | 133.1825 | 180.7509 | 246.8532 | 339.0164 | 467.899 | 648.6138 | 902.6132 | 1260.3808 | 1765.2721 | 2479.001 |  | 567.5778 | 652.2833 | 750.1722 | 863.343 | 994.2327 | 1145.6724 | 1320.9508 | 1523.8894 | 1758.9292 | 2031.2319 | 2346.7974 | 2712.6012 | 3136.7539 | 3628.6868 | 4199.3684 | 4861.5559 | 5630.089 | 6522.2307 | 7558.0657 | 8760.9626 | 9254.7602 | 9254.7602 | 9254.7602 | 9254.7602 | 9254.7602 | 9254.7602 | 9254.7602 | 9254.7602 | 9254.7602 | 9254.7602 |  | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 35.7224 | 47.3521 | 63.3162 | 85.3288 | 115.8054 | 158.1565 | 217.2045 | 299.7783 | 415.5605 | 578.2955 | 807.5137 | 1130.9926 | 1588.2718 |  | 537.733 | 622.4385 | 720.3274 | 833.4982 | 964.3879 | 1115.8275 | 1291.1059 | 1494.0446 | 1729.0844 | 2001.387 | 2316.9525 | 2682.7564 | 3106.9091 | 3598.842 | 4169.5235 | 4831.7111 | 5600.2441 | 6486.5083 | 7510.7135 | 8697.6463 | 9169.4315 | 9138.9549 | 9096.6038 | 9037.5558 | 8954.9819 | 8839.1997 | 8676.4647 | 8447.2465 | 8123.7676 | 7666.4885 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 537.733 | 622.4385 | 720.3274 | 833.4982 | 964.3879 | 1115.8275 | 1291.1059 | 1494.0446 | 1729.0844 | 2001.387 | 2316.9525 | 2682.7564 | 3106.9091 | 3598.842 | 4169.5235 | 4831.7111 | 5600.2441 | 6486.5083 | 7510.7135 | 8697.6463 | 9169.4315 | 9138.9549 | 9096.6038 | 9037.5558 | 8954.9819 | 8839.1997 | 8676.4647 | 8447.2465 | 8123.7676 | 7666.4885 |  | 139.4923 | 160.3101 | 184.368 | 212.1818 | 244.3502 | 281.5692 | 324.6469 | 374.5227 | 432.2878 | 499.211 | 576.7668 | 666.6695 | 770.9125 | 891.8137 | 1032.0688 | 1194.813 | 1383.6936 | 1602.9531 | 1857.5278 | 2153.1609 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 124.8225 | 145.6403 | 169.6983 | 197.512 | 229.6804 | 266.8994 | 309.9771 | 359.8529 | 417.6181 | 484.5412 | 562.097 | 651.9998 | 756.2428 | 877.1439 | 1017.399 | 1180.1432 | 1369.0238 | 1585.3943 | 1834.2526 | 2122.0388 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 19.6613 | 22.5955 | 25.9865 | 29.9068 | 34.4409 | 39.6869 | 45.7586 | 52.7886 | 60.9305 | 70.3633 | 81.2947 | 93.9664 | 108.6593 | 125.7002 | 145.469 | 168.4077 | 195.0302 | 225.9346 | 261.8166 | 303.4858 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 17.5936 | 20.5279 | 23.9188 | 27.8391 | 32.3732 | 37.6192 | 43.691 | 50.7209 | 58.8628 | 68.2956 | 79.227 | 91.8987 | 106.5916 | 123.6325 | 143.4013 | 166.34 | 192.9625 | 223.4597 | 258.536 | 299.0992 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 680.1491 | 788.6067 | 913.9445 | 1058.8492 | 1226.4415 | 1420.3461 | 1644.774 | 1904.6184 | 2205.5653 | 2554.2239 | 2958.2765 | 3426.6548 | 3969.7435 | 4599.6185 | 5330.3239 | 6178.1943 | 7162.2304 | 8295.3623 | 9603.5021 | 11118.7843 | 11716.6894 | 11669.121 | 11603.0187 | 11510.8556 | 11381.973 | 11201.2582 | 10947.2587 | 10589.4911 | 10084.5998 | 9370.871
| TRUE | 24 | 22003642 | AC | Blank | 66 | CB B | CB FAIL | Y | ASEA | GROUP_3095 | GROUP 3095 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 494.2485 | 0 | 494.2485 | 121.4703 | 17.1211 | 0 |  | 16.4925 | 0.17586 | 0 | 0.17586 | 2031.2319 | 0 | 2031.2319 | 499.211 | 70.3633 | 0 |  | 0.0051679 | 0 | 0.0051679 | 59.6897 | 0 | 59.6897 | 14.6698 | 2.0677 | 0 |  | 632.8399 | 2600.8062 | 76.4271 | 2524.379 |  | 0.051037 |  | 10.4184 | 10.9639 | 11.538 | 12.1422 | 12.778 | 13.447 | 14.1511 | 14.8921 | 15.6719 | 16.4925 | 17.3561 | 18.2649 | 19.2213 | 20.2278 | 21.287 | 22.4016 | 23.5746 | 24.809 | 26.108 | 27.4751 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049141 | 0.056475 | 0.06495 | 0.074748 | 0.086081 | 0.099192 | 0.11437 | 0.13194 | 0.15229 | 0.17586 | 0.20319 | 0.23486 | 0.27158 | 0.31417 | 0.36358 | 0.42091 | 0.48745 | 0.5647 | 0.65438 | 0.75852 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726.7314 | 835.189 | 960.5268 | 1105.4315 | 1273.0238 | 1466.9284 | 1691.3564 | 1951.2007 | 2252.1476 | 2600.8062 | 3004.8588 | 3473.2371 | 4016.3258 | 4646.2008 | 5376.9062 | 6224.7766 | 7208.8127 | 8351.1184 | 9677.4101 | 11217.6093 | 11849.872 | 11849.872 | 11849.872 | 11849.872 | 11849.872 | 11849.872 | 11849.872 | 11849.872 | 11849.872 | 11849.872 |  | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 46.5823 | 55.7561 | 73.908 | 98.825 | 133.1825 | 180.7509 | 246.8532 | 339.0164 | 467.899 | 648.6138 | 902.6132 | 1260.3808 | 1765.2721 | 2479.001 |  | 567.5778 | 652.2833 | 750.1722 | 863.343 | 994.2327 | 1145.6724 | 1320.9508 | 1523.8894 | 1758.9292 | 2031.2319 | 2346.7974 | 2712.6012 | 3136.7539 | 3628.6868 | 4199.3684 | 4861.5559 | 5630.089 | 6522.2307 | 7558.0657 | 8760.9626 | 9254.7602 | 9254.7602 | 9254.7602 | 9254.7602 | 9254.7602 | 9254.7602 | 9254.7602 | 9254.7602 | 9254.7602 | 9254.7602 |  | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 29.8448 | 35.7224 | 47.3521 | 63.3162 | 85.3288 | 115.8054 | 158.1565 | 217.2045 | 299.7783 | 415.5605 | 578.2955 | 807.5137 | 1130.9926 | 1588.2718 |  | 537.733 | 622.4385 | 720.3274 | 833.4982 | 964.3879 | 1115.8275 | 1291.1059 | 1494.0446 | 1729.0844 | 2001.387 | 2316.9525 | 2682.7564 | 3106.9091 | 3598.842 | 4169.5235 | 4831.7111 | 5600.2441 | 6486.5083 | 7510.7135 | 8697.6463 | 9169.4315 | 9138.9549 | 9096.6038 | 9037.5558 | 8954.9819 | 8839.1997 | 8676.4647 | 8447.2465 | 8123.7676 | 7666.4885 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 537.733 | 622.4385 | 720.3274 | 833.4982 | 964.3879 | 1115.8275 | 1291.1059 | 1494.0446 | 1729.0844 | 2001.387 | 2316.9525 | 2682.7564 | 3106.9091 | 3598.842 | 4169.5235 | 4831.7111 | 5600.2441 | 6486.5083 | 7510.7135 | 8697.6463 | 9169.4315 | 9138.9549 | 9096.6038 | 9037.5558 | 8954.9819 | 8839.1997 | 8676.4647 | 8447.2465 | 8123.7676 | 7666.4885 |  | 139.4923 | 160.3101 | 184.368 | 212.1818 | 244.3502 | 281.5692 | 324.6469 | 374.5227 | 432.2878 | 499.211 | 576.7668 | 666.6695 | 770.9125 | 891.8137 | 1032.0688 | 1194.813 | 1383.6936 | 1602.9531 | 1857.5278 | 2153.1609 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 124.8225 | 145.6403 | 169.6983 | 197.512 | 229.6804 | 266.8994 | 309.9771 | 359.8529 | 417.6181 | 484.5412 | 562.097 | 651.9998 | 756.2428 | 877.1439 | 1017.399 | 1180.1432 | 1369.0238 | 1585.3943 | 1834.2526 | 2122.0388 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 19.6613 | 22.5955 | 25.9865 | 29.9068 | 34.4409 | 39.6869 | 45.7586 | 52.7886 | 60.9305 | 70.3633 | 81.2947 | 93.9664 | 108.6593 | 125.7002 | 145.469 | 168.4077 | 195.0302 | 225.9346 | 261.8166 | 303.4858 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 17.5936 | 20.5279 | 23.9188 | 27.8391 | 32.3732 | 37.6192 | 43.691 | 50.7209 | 58.8628 | 68.2956 | 79.227 | 91.8987 | 106.5916 | 123.6325 | 143.4013 | 166.34 | 192.9625 | 223.4597 | 258.536 | 299.0992 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 680.1491 | 788.6067 | 913.9445 | 1058.8492 | 1226.4415 | 1420.3461 | 1644.774 | 1904.6184 | 2205.5653 | 2554.2239 | 2958.2765 | 3426.6548 | 3969.7435 | 4599.6185 | 5330.3239 | 6178.1943 | 7162.2304 | 8295.3623 | 9603.5021 | 11118.7843 | 11716.6894 | 11669.121 | 11603.0187 | 11510.8556 | 11381.973 | 11201.2582 | 10947.2587 | 10589.4911 | 10084.5998 | 9370.871
| FALSE | 25 | 22003627 | AC | Blank | 66 | 66KV LINES | EARTH FAULT | Y | ASEA | GROUP_2890 | GROUP 2890 | GROUP 2000s | Electronic |  | 0.016937 | 2190 |  | 8.25 | 0.026286 | 0.0012915 | 0.024994 | 305.0906 | 625.0939 | 930.1845 | 81.947 | 10.5298 | 14.3264 |  | 13.322 | 0.096648 | 0.0047487 | 0.091899 | 1121.7695 | 2298.3708 | 3420.1403 | 301.3061 | 38.7164 | 52.6759 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 59.6898 | 0.058033 | 59.7478 | 14.6705 | 2.0677 | 0.0013301 |  | 1036.9877 | 3812.8387 | 76.4873 | 3736.3514 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0014664 | 0.0016663 | 0.0018949 | 0.0021564 | 0.0024558 | 0.0027987 | 0.0031913 | 0.0036413 | 0.0041572 | 0.0047487 | 0.0054272 | 0.0062057 | 0.0070992 | 0.0081251 | 0.0093031 | 0.010656 | 0.012211 | 0.013997 | 0.016051 | 0.018412 | 0.021127 | 0.024249 | 0.027841 | 0.031973 | 0.036728 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 1177.3932 | 1337.8941 | 1521.4496 | 1731.4624 | 1971.8458 | 2247.101 | 2562.4064 | 2923.7205 | 3337.9004 | 3812.8387 | 4357.6208 | 4982.707 | 5700.1417 | 6523.7955 | 7469.6438 | 8556.0879 | 9804.3265 | 11238.7828 | 12887.5978 | 14783.2001 | 16962.9612 | 19469.954 | 22353.8259 | 25671.8068 | 29489.8724 | 31611.0281 | 31611.0281 | 31611.0281 | 31611.0281 | 31611.0281 |  | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 55.8225 | 73.996 | 98.9427 | 133.3411 | 180.9661 | 247.1471 | 339.42 | 468.4561 | 649.386 | 903.6879 | 1261.8815 | 1767.3739 | 2481.9526 |  | 346.3991 | 393.6198 | 447.6234 | 509.4109 | 580.1338 | 661.1162 | 753.8817 | 860.1834 | 982.0386 | 1121.7695 | 1282.049 | 1465.9547 | 1677.03 | 1919.356 | 2197.6325 | 2517.2736 | 2884.516 | 3306.5452 | 3791.6406 | 4349.3428 | 4990.647 | 5728.2256 | 6576.6851 | 7552.8633 | 8676.1706 | 9300.2325 | 9300.2325 | 9300.2325 | 9300.2325 | 9300.2325 |  | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 35.7225 | 47.3523 | 63.3164 | 85.329 | 115.8056 | 158.1568 | 217.205 | 299.779 | 415.5615 | 578.2969 | 807.5156 | 1130.9953 | 1588.2755 |  | 316.5542 | 363.7749 | 417.7785 | 479.566 | 550.2889 | 631.2713 | 724.0368 | 830.3385 | 952.1937 | 1091.9246 | 1252.2041 | 1436.1098 | 1647.1851 | 1889.5111 | 2167.7876 | 2487.4287 | 2854.6711 | 3270.8227 | 3744.2883 | 4286.0264 | 4905.3181 | 5612.42 | 6418.5283 | 7335.6583 | 8376.3916 | 8884.6711 | 8721.9357 | 8492.717 | 8169.2373 | 7711.9571 |  | 709.7301 | 806.4796 | 917.1265 | 1043.7217 | 1188.6243 | 1354.5476 | 1544.613 | 1762.4123 | 2012.0791 | 2298.3708 | 2626.7643 | 3003.5649 | 3436.0329 | 3932.5297 | 4502.6849 | 5157.5911 | 5910.0266 | 6774.7136 | 7768.6158 | 8911.2806 | 10225.2359 | 11736.4457 | 13474.8373 | 15474.9089 | 17776.4306 | 19055.0585 | 19055.0585 | 19055.0585 | 19055.0585 | 19055.0585 |  | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.063148 | 0.083706 | 0.11193 | 0.15084 | 0.20471 | 0.27958 | 0.38396 | 0.52993 | 0.7346 | 1.0223 | 1.4275 | 1.9993 | 2.8076 |  | 709.6773 | 806.4269 | 917.0737 | 1043.669 | 1188.5716 | 1354.4948 | 1544.5602 | 1762.3596 | 2012.0263 | 2298.3181 | 2626.7115 | 3003.5121 | 3435.9802 | 3932.4769 | 4502.6321 | 5157.5383 | 5909.9738 | 6774.6505 | 7768.5321 | 8911.1687 | 10225.085 | 11736.241 | 13474.5577 | 15474.525 | 17775.9006 | 19054.3239 | 19054.0362 | 19053.631 | 19053.0592 | 19052.2509 |  | 1026.2315 | 1170.2017 | 1334.8522 | 1523.235 | 1738.8604 | 1985.7661 | 2268.597 | 2592.698 | 2964.22 | 3390.2427 | 3878.9157 | 4439.6219 | 5083.1653 | 5821.988 | 6670.4198 | 7644.967 | 8764.6449 | 10045.4732 | 11512.8204 | 13197.1952 | 15130.4031 | 17348.6609 | 19893.0861 | 22810.1832 | 26152.2922 | 27938.995 | 27775.9719 | 27546.348 | 27222.2965 | 26764.208 |  | 93.0424 | 105.7259 | 120.2312 | 136.8272 | 155.8233 | 177.5751 | 202.4918 | 231.0444 | 263.7746 | 301.3061 | 344.357 | 393.7539 | 450.4485 | 515.537 | 590.2818 | 676.1371 | 774.778 | 888.1346 | 1018.4307 | 1168.229 | 1340.4826 | 1538.5954 | 1766.4908 | 2028.6912 | 2330.4104 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 78.372 | 91.0554 | 105.5607 | 122.1568 | 141.1529 | 162.9046 | 187.8214 | 216.3739 | 249.1041 | 286.6357 | 329.6866 | 379.0834 | 435.7781 | 500.8665 | 575.6113 | 661.4666 | 760.1075 | 870.575 | 995.1544 | 1137.1054 | 1298.5386 | 1481.6704 | 1688.7477 | 1921.9226 | 2183.0519 | 2293.7607 | 2213.767 | 2101.0929 | 1942.0842 | 1717.305 |  | 11.9555 | 13.5853 | 15.4491 | 17.5816 | 20.0225 | 22.8175 | 26.0192 | 29.6881 | 33.8937 | 38.7164 | 44.2482 | 50.5955 | 57.8804 | 66.244 | 75.8483 | 86.8803 | 99.5552 | 114.121 | 130.8634 | 150.1117 | 172.2455 | 197.702 | 226.9854 | 260.6769 | 299.4463 | 320.985 | 320.985 | 320.985 | 320.985 | 320.985 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 9.8878 | 11.5176 | 13.3814 | 15.5139 | 17.9548 | 20.7498 | 23.9515 | 27.6204 | 31.826 | 36.6487 | 42.1805 | 48.5278 | 55.8127 | 64.1763 | 73.7806 | 84.8126 | 97.4875 | 111.6461 | 127.5827 | 145.7251 | 166.3338 | 189.6788 | 216.0281 | 245.6287 | 278.6773 | 292.1944 | 280.9199 | 265.0393 | 242.6282 | 210.9473 |  | 16.2662 | 18.4836 | 21.0194 | 23.9209 | 27.2419 | 31.0446 | 35.4007 | 40.3924 | 46.1145 | 52.6759 | 60.2023 | 68.8381 | 78.7498 | 90.1289 | 103.1962 | 118.2058 | 135.4508 | 155.2684 | 178.0474 | 204.2359 | 234.3502 | 268.9853 | 308.8272 | 354.6665 | 407.4146 | 436.7192 | 436.7192 | 436.7192 | 436.7192 | 436.7192 |  | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.001592 | 0.0021103 | 0.0028217 | 0.0038027 | 0.0051609 | 0.0070484 | 0.0096799 | 0.01336 | 0.01852 | 0.025772 | 0.035987 | 0.050403 | 0.070782 |  | 16.2648 | 18.4822 | 21.0181 | 23.9195 | 27.2405 | 31.0433 | 35.3994 | 40.3911 | 46.1131 | 52.6746 | 60.201 | 68.8368 | 78.7484 | 90.1276 | 103.1948 | 118.2045 | 135.4494 | 155.2668 | 178.0453 | 204.2331 | 234.3464 | 268.9802 | 308.8202 | 354.6568 | 407.4012 | 436.7007 | 436.6934 | 436.6832 | 436.6688 | 436.6484 |  | 1130.7561 | 1291.2569 | 1474.8124 | 1684.8253 | 1925.2087 | 2200.4638 | 2515.7692 | 2877.0833 | 3291.2633 | 3766.2016 | 4310.9837 | 4936.0698 | 5653.5046 | 6477.1584 | 7423.0066 | 8509.4508 | 9757.6894 | 11182.961 | 12813.6028 | 14684.2587 | 16829.6219 | 19288.9903 | 22106.682 | 25332.3913 | 29021.4226 | 30961.6507 | 30707.3522 | 30349.1634 | 29843.6778 | 29129.1087
| FALSE | 26 | 22003625 | AC | AC-ATS | 66 | ATS LINE | PILOT WIRE | X | Brown Boveri | GROUP_2372 | GROUP 2372 | GROUP 2000s | Electronic |  | 0.15703 | 2190 |  | 8.25 | 0.026286 | 0.0092625 | 0.017023 | 314.2971 | 4483.0716 | 4797.3687 | 127.2004 | 10.6095 | 102.7467 |  | 13.322 | 0.096648 | 0.034057 | 0.062591 | 1155.6205 | 16483.5405 | 17639.161 | 467.6956 | 39.0094 | 377.7831 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 59.6909 | 0.53804 | 60.229 | 14.6761 | 2.0677 | 0.012331 |  | 5037.9253 | 18523.6491 | 76.9851 | 18446.664 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.010517 | 0.01195 | 0.01359 | 0.015466 | 0.017613 | 0.020071 | 0.022888 | 0.026115 | 0.029815 | 0.034057 | 0.038923 | 0.044506 | 0.050915 | 0.058272 | 0.06672 | 0.076424 | 0.087574 | 0.10039 | 0.11511 | 0.13205 | 0.15152 | 0.17391 | 0.19967 | 0.2293 | 0.26341 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 5720.0475 | 6499.7977 | 7391.5526 | 8411.8433 | 9579.6813 | 10916.9344 | 12448.7606 | 14204.1078 | 16216.2895 | 18523.6491 | 21170.3261 | 24207.1387 | 27692.6018 | 31694.1019 | 36289.2505 | 41567.4466 | 47631.6773 | 54600.5962 | 62610.9199 | 71820.1922 | 82409.9741 | 94589.523 | 108600.0368 | 124719.5525 | 143268.5954 | 153573.658 | 153573.658 | 153573.658 | 153573.658 | 153573.658 |  | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 56.3716 | 74.7239 | 99.9159 | 134.6527 | 182.7462 | 249.5781 | 342.7586 | 473.0639 | 655.7735 | 912.5768 | 1274.2936 | 1784.7582 | 2506.3656 |  | 356.8521 | 405.4978 | 461.131 | 524.7831 | 597.6401 | 681.0663 | 776.6311 | 886.1406 | 1011.673 | 1155.6205 | 1320.7366 | 1510.1919 | 1727.6368 | 1977.2752 | 2263.9492 | 2593.2359 | 2971.5603 | 3406.3249 | 3906.0587 | 4480.5904 | 5141.2468 | 5901.0829 | 6775.1459 | 7780.7815 | 8937.9862 | 9580.8801 | 9580.8801 | 9580.8801 | 9580.8801 | 9580.8801 |  | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 35.7232 | 47.3532 | 63.3176 | 85.3306 | 115.8079 | 158.1599 | 217.2092 | 299.7848 | 415.5695 | 578.3079 | 807.5311 | 1131.017 | 1588.3059 |  | 327.0067 | 375.6523 | 431.2856 | 494.9376 | 567.7946 | 651.2208 | 746.7857 | 856.2951 | 981.8275 | 1125.775 | 1290.8912 | 1480.3464 | 1697.7913 | 1947.4298 | 2234.1037 | 2563.3904 | 2941.7149 | 3370.6017 | 3858.7055 | 4417.2728 | 5055.9163 | 5785.275 | 6616.986 | 7563.5724 | 8638.2015 | 9165.3107 | 9002.5722 | 8773.3491 | 8449.8632 | 7992.5742 |  | 5090.0681 | 5783.9402 | 6577.4814 | 7485.402 | 8524.6197 | 9714.594 | 11077.712 | 12639.7334 | 14430.3027 | 16483.5405 | 18838.7249 | 21541.077 | 24642.6674 | 28203.4609 | 32292.5212 | 36989.4013 | 42385.7458 | 48587.1405 | 55715.2443 | 63910.2502 | 73333.7228 | 84171.8727 | 96639.3337 | 110983.5209 | 127489.6584 | 136659.7694 | 136659.7694 | 136659.7694 | 136659.7694 | 136659.7694 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 5089.579 | 5783.4511 | 6576.9922 | 7484.9129 | 8524.1306 | 9714.1048 | 11077.2229 | 12639.2443 | 14429.8136 | 16483.0514 | 18838.2357 | 21540.5878 | 24642.1783 | 28202.9717 | 32292.0321 | 36988.9121 | 42385.2567 | 48586.555 | 55714.4682 | 63909.2125 | 73332.3243 | 84169.9748 | 96636.7417 | 110979.9611 | 127484.7453 | 136652.9588 | 136650.2917 | 136646.535 | 136641.2335 | 136633.7391 |  | 5416.5856 | 6159.1034 | 7008.2778 | 7979.8505 | 9091.9252 | 10365.3257 | 11824.0086 | 13495.5394 | 15411.6412 | 17608.8264 | 20129.1269 | 23020.9343 | 26339.9696 | 30150.4015 | 34526.1358 | 39552.3026 | 45326.9716 | 51957.1567 | 59573.1737 | 68326.4852 | 78388.2406 | 89955.2498 | 103253.7277 | 118543.5335 | 136122.9468 | 145818.2695 | 145652.8639 | 145419.8841 | 145091.0967 | 144626.3133 |  | 144.423 | 164.1106 | 186.6261 | 212.387 | 241.8732 | 275.6369 | 314.3134 | 358.6334 | 409.4381 | 467.6956 | 534.5204 | 611.1955 | 699.1985 | 800.2306 | 916.2515 | 1049.5184 | 1202.6316 | 1378.5868 | 1580.836 | 1813.3569 | 2080.7337 | 2388.2498 | 2741.9952 | 3148.9899 | 3617.3266 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 129.7469 | 149.4345 | 171.95 | 197.7109 | 227.1971 | 260.9608 | 299.6373 | 343.9573 | 394.762 | 453.0195 | 519.8443 | 596.5194 | 684.5224 | 785.5545 | 901.5754 | 1034.8423 | 1187.9555 | 1361.0204 | 1557.5507 | 1782.2213 | 2038.7735 | 2331.3029 | 2664.2223 | 3042.1803 | 3469.9116 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 12.046 | 13.6881 | 15.5661 | 17.7147 | 20.1741 | 22.9903 | 26.2162 | 29.9128 | 34.1503 | 39.0094 | 44.5832 | 50.9785 | 58.3186 | 66.7455 | 76.4225 | 87.538 | 100.3088 | 114.9848 | 131.854 | 151.2481 | 173.5494 | 199.1986 | 228.7037 | 262.6502 | 301.7131 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 9.9783 | 11.6204 | 13.4984 | 15.647 | 18.1064 | 20.9226 | 24.1485 | 27.8451 | 32.0826 | 36.9417 | 42.5155 | 48.9108 | 56.2509 | 64.6778 | 74.3548 | 85.4703 | 98.2411 | 112.5099 | 128.5734 | 146.8614 | 167.6376 | 191.1754 | 217.7464 | 247.6019 | 280.944 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 116.6583 | 132.561 | 150.748 | 171.5565 | 195.3741 | 222.6469 | 253.8879 | 289.6876 | 330.7253 | 377.7831 | 431.7611 | 493.6958 | 564.7806 | 646.3897 | 740.1061 | 847.753 | 971.4307 | 1113.5593 | 1276.927 | 1464.7467 | 1680.7215 | 1929.1189 | 2214.8583 | 2543.61 | 2921.9109 | 3132.079 | 3132.079 | 3132.079 | 3132.079 | 3132.079 |  | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.01476 | 0.019565 | 0.026161 | 0.035256 | 0.047848 | 0.065347 | 0.089745 | 0.12386 | 0.1717 | 0.23894 | 0.33365 | 0.4673 | 0.65624 |  | 116.646 | 132.5487 | 150.7357 | 171.5442 | 195.3618 | 222.6346 | 253.8756 | 289.6753 | 330.713 | 377.7708 | 431.7488 | 493.6835 | 564.7682 | 646.3774 | 740.0937 | 847.7406 | 971.4184 | 1113.5446 | 1276.9074 | 1464.7206 | 1680.6862 | 1929.0711 | 2214.7929 | 2543.5202 | 2921.7871 | 3131.9072 | 3131.84 | 3131.7453 | 3131.6116 | 3131.4227 |  | 5672.9568 | 6452.7069 | 7344.4619 | 8364.7526 | 9532.5905 | 10869.8436 | 12401.6699 | 14157.0171 | 16169.1987 | 18476.5584 | 21123.2354 | 24160.0479 | 27645.5111 | 31647.0111 | 36242.1598 | 41520.3558 | 47584.5866 | 54544.2316 | 62536.2052 | 71720.2885 | 82275.338 | 94406.7992 | 108350.4893 | 124376.8359 | 142795.5895 | 152917.965 | 152661.1932 | 152299.5207 | 151789.1188 | 151067.5999
| FALSE | 27 | 22003626 | AC | AC-ATS | 66 | ATS LINE | PILOT WIRE CURR INTLK | Y | English Electric | GROUP_2375 | GROUP 2375 | GROUP 2000s | Electronic |  | 0.016937 | 2190 |  | 8.25 | 0.026286 | 0.0012915 | 0.024994 | 305.0906 | 625.0939 | 930.1845 | 81.947 | 10.5298 | 14.3264 |  | 13.322 | 0.096648 | 0.0047487 | 0.091899 | 1121.7695 | 2298.3708 | 3420.1403 | 301.3061 | 38.7164 | 52.6759 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 59.6898 | 0.058033 | 59.7478 | 14.6705 | 2.0677 | 0.0013301 |  | 1036.9877 | 3812.8387 | 76.4873 | 3736.3514 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0014664 | 0.0016663 | 0.0018949 | 0.0021564 | 0.0024558 | 0.0027987 | 0.0031913 | 0.0036413 | 0.0041572 | 0.0047487 | 0.0054272 | 0.0062057 | 0.0070992 | 0.0081251 | 0.0093031 | 0.010656 | 0.012211 | 0.013997 | 0.016051 | 0.018412 | 0.021127 | 0.024249 | 0.027841 | 0.031973 | 0.036728 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 1177.3932 | 1337.8941 | 1521.4496 | 1731.4624 | 1971.8458 | 2247.101 | 2562.4064 | 2923.7205 | 3337.9004 | 3812.8387 | 4357.6208 | 4982.707 | 5700.1417 | 6523.7955 | 7469.6438 | 8556.0879 | 9804.3265 | 11238.7828 | 12887.5978 | 14783.2001 | 16962.9612 | 19469.954 | 22353.8259 | 25671.8068 | 29489.8724 | 31611.0281 | 31611.0281 | 31611.0281 | 31611.0281 | 31611.0281 |  | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 55.8225 | 73.996 | 98.9427 | 133.3411 | 180.9661 | 247.1471 | 339.42 | 468.4561 | 649.386 | 903.6879 | 1261.8815 | 1767.3739 | 2481.9526 |  | 346.3991 | 393.6198 | 447.6234 | 509.4109 | 580.1338 | 661.1162 | 753.8817 | 860.1834 | 982.0386 | 1121.7695 | 1282.049 | 1465.9547 | 1677.03 | 1919.356 | 2197.6325 | 2517.2736 | 2884.516 | 3306.5452 | 3791.6406 | 4349.3428 | 4990.647 | 5728.2256 | 6576.6851 | 7552.8633 | 8676.1706 | 9300.2325 | 9300.2325 | 9300.2325 | 9300.2325 | 9300.2325 |  | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 35.7225 | 47.3523 | 63.3164 | 85.329 | 115.8056 | 158.1568 | 217.205 | 299.779 | 415.5615 | 578.2969 | 807.5156 | 1130.9953 | 1588.2755 |  | 316.5542 | 363.7749 | 417.7785 | 479.566 | 550.2889 | 631.2713 | 724.0368 | 830.3385 | 952.1937 | 1091.9246 | 1252.2041 | 1436.1098 | 1647.1851 | 1889.5111 | 2167.7876 | 2487.4287 | 2854.6711 | 3270.8227 | 3744.2883 | 4286.0264 | 4905.3181 | 5612.42 | 6418.5283 | 7335.6583 | 8376.3916 | 8884.6711 | 8721.9357 | 8492.717 | 8169.2373 | 7711.9571 |  | 709.7301 | 806.4796 | 917.1265 | 1043.7217 | 1188.6243 | 1354.5476 | 1544.613 | 1762.4123 | 2012.0791 | 2298.3708 | 2626.7643 | 3003.5649 | 3436.0329 | 3932.5297 | 4502.6849 | 5157.5911 | 5910.0266 | 6774.7136 | 7768.6158 | 8911.2806 | 10225.2359 | 11736.4457 | 13474.8373 | 15474.9089 | 17776.4306 | 19055.0585 | 19055.0585 | 19055.0585 | 19055.0585 | 19055.0585 |  | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.063148 | 0.083706 | 0.11193 | 0.15084 | 0.20471 | 0.27958 | 0.38396 | 0.52993 | 0.7346 | 1.0223 | 1.4275 | 1.9993 | 2.8076 |  | 709.6773 | 806.4269 | 917.0737 | 1043.669 | 1188.5716 | 1354.4948 | 1544.5602 | 1762.3596 | 2012.0263 | 2298.3181 | 2626.7115 | 3003.5121 | 3435.9802 | 3932.4769 | 4502.6321 | 5157.5383 | 5909.9738 | 6774.6505 | 7768.5321 | 8911.1687 | 10225.085 | 11736.241 | 13474.5577 | 15474.525 | 17775.9006 | 19054.3239 | 19054.0362 | 19053.631 | 19053.0592 | 19052.2509 |  | 1026.2315 | 1170.2017 | 1334.8522 | 1523.235 | 1738.8604 | 1985.7661 | 2268.597 | 2592.698 | 2964.22 | 3390.2427 | 3878.9157 | 4439.6219 | 5083.1653 | 5821.988 | 6670.4198 | 7644.967 | 8764.6449 | 10045.4732 | 11512.8204 | 13197.1952 | 15130.4031 | 17348.6609 | 19893.0861 | 22810.1832 | 26152.2922 | 27938.995 | 27775.9719 | 27546.348 | 27222.2965 | 26764.208 |  | 93.0424 | 105.7259 | 120.2312 | 136.8272 | 155.8233 | 177.5751 | 202.4918 | 231.0444 | 263.7746 | 301.3061 | 344.357 | 393.7539 | 450.4485 | 515.537 | 590.2818 | 676.1371 | 774.778 | 888.1346 | 1018.4307 | 1168.229 | 1340.4826 | 1538.5954 | 1766.4908 | 2028.6912 | 2330.4104 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 78.372 | 91.0554 | 105.5607 | 122.1568 | 141.1529 | 162.9046 | 187.8214 | 216.3739 | 249.1041 | 286.6357 | 329.6866 | 379.0834 | 435.7781 | 500.8665 | 575.6113 | 661.4666 | 760.1075 | 870.575 | 995.1544 | 1137.1054 | 1298.5386 | 1481.6704 | 1688.7477 | 1921.9226 | 2183.0519 | 2293.7607 | 2213.767 | 2101.0929 | 1942.0842 | 1717.305 |  | 11.9555 | 13.5853 | 15.4491 | 17.5816 | 20.0225 | 22.8175 | 26.0192 | 29.6881 | 33.8937 | 38.7164 | 44.2482 | 50.5955 | 57.8804 | 66.244 | 75.8483 | 86.8803 | 99.5552 | 114.121 | 130.8634 | 150.1117 | 172.2455 | 197.702 | 226.9854 | 260.6769 | 299.4463 | 320.985 | 320.985 | 320.985 | 320.985 | 320.985 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 9.8878 | 11.5176 | 13.3814 | 15.5139 | 17.9548 | 20.7498 | 23.9515 | 27.6204 | 31.826 | 36.6487 | 42.1805 | 48.5278 | 55.8127 | 64.1763 | 73.7806 | 84.8126 | 97.4875 | 111.6461 | 127.5827 | 145.7251 | 166.3338 | 189.6788 | 216.0281 | 245.6287 | 278.6773 | 292.1944 | 280.9199 | 265.0393 | 242.6282 | 210.9473 |  | 16.2662 | 18.4836 | 21.0194 | 23.9209 | 27.2419 | 31.0446 | 35.4007 | 40.3924 | 46.1145 | 52.6759 | 60.2023 | 68.8381 | 78.7498 | 90.1289 | 103.1962 | 118.2058 | 135.4508 | 155.2684 | 178.0474 | 204.2359 | 234.3502 | 268.9853 | 308.8272 | 354.6665 | 407.4146 | 436.7192 | 436.7192 | 436.7192 | 436.7192 | 436.7192 |  | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.001592 | 0.0021103 | 0.0028217 | 0.0038027 | 0.0051609 | 0.0070484 | 0.0096799 | 0.01336 | 0.01852 | 0.025772 | 0.035987 | 0.050403 | 0.070782 |  | 16.2648 | 18.4822 | 21.0181 | 23.9195 | 27.2405 | 31.0433 | 35.3994 | 40.3911 | 46.1131 | 52.6746 | 60.201 | 68.8368 | 78.7484 | 90.1276 | 103.1948 | 118.2045 | 135.4494 | 155.2668 | 178.0453 | 204.2331 | 234.3464 | 268.9802 | 308.8202 | 354.6568 | 407.4012 | 436.7007 | 436.6934 | 436.6832 | 436.6688 | 436.6484 |  | 1130.7561 | 1291.2569 | 1474.8124 | 1684.8253 | 1925.2087 | 2200.4638 | 2515.7692 | 2877.0833 | 3291.2633 | 3766.2016 | 4310.9837 | 4936.0698 | 5653.5046 | 6477.1584 | 7423.0066 | 8509.4508 | 9757.6894 | 11182.961 | 12813.6028 | 14684.2587 | 16829.6219 | 19288.9903 | 22106.682 | 25332.3913 | 29021.4226 | 30961.6507 | 30707.3522 | 30349.1634 | 29843.6778 | 29129.1087
| FALSE | 28 | 22003629 | AC | AC-ATS | 66 | ATS LINE | NEUTRAL DISPLACEMENT | Y | ASEA | GROUP_2605 | GROUP 2605 | GROUP 2000s | Electronic |  | 0.016937 | 2190 |  | 8.25 | 0.026286 | 0.0012915 | 0.024994 | 305.0906 | 625.0939 | 930.1845 | 81.947 | 10.5298 | 14.3264 |  | 13.322 | 0.096648 | 0.0047487 | 0.091899 | 1121.7695 | 2298.3708 | 3420.1403 | 301.3061 | 38.7164 | 52.6759 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 59.6898 | 0.058033 | 59.7478 | 14.6705 | 2.0677 | 0.0013301 |  | 1036.9877 | 3812.8387 | 76.4873 | 3736.3514 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0014664 | 0.0016663 | 0.0018949 | 0.0021564 | 0.0024558 | 0.0027987 | 0.0031913 | 0.0036413 | 0.0041572 | 0.0047487 | 0.0054272 | 0.0062057 | 0.0070992 | 0.0081251 | 0.0093031 | 0.010656 | 0.012211 | 0.013997 | 0.016051 | 0.018412 | 0.021127 | 0.024249 | 0.027841 | 0.031973 | 0.036728 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 1177.3932 | 1337.8941 | 1521.4496 | 1731.4624 | 1971.8458 | 2247.101 | 2562.4064 | 2923.7205 | 3337.9004 | 3812.8387 | 4357.6208 | 4982.707 | 5700.1417 | 6523.7955 | 7469.6438 | 8556.0879 | 9804.3265 | 11238.7828 | 12887.5978 | 14783.2001 | 16962.9612 | 19469.954 | 22353.8259 | 25671.8068 | 29489.8724 | 31611.0281 | 31611.0281 | 31611.0281 | 31611.0281 | 31611.0281 |  | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 55.8225 | 73.996 | 98.9427 | 133.3411 | 180.9661 | 247.1471 | 339.42 | 468.4561 | 649.386 | 903.6879 | 1261.8815 | 1767.3739 | 2481.9526 |  | 346.3991 | 393.6198 | 447.6234 | 509.4109 | 580.1338 | 661.1162 | 753.8817 | 860.1834 | 982.0386 | 1121.7695 | 1282.049 | 1465.9547 | 1677.03 | 1919.356 | 2197.6325 | 2517.2736 | 2884.516 | 3306.5452 | 3791.6406 | 4349.3428 | 4990.647 | 5728.2256 | 6576.6851 | 7552.8633 | 8676.1706 | 9300.2325 | 9300.2325 | 9300.2325 | 9300.2325 | 9300.2325 |  | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 35.7225 | 47.3523 | 63.3164 | 85.329 | 115.8056 | 158.1568 | 217.205 | 299.779 | 415.5615 | 578.2969 | 807.5156 | 1130.9953 | 1588.2755 |  | 316.5542 | 363.7749 | 417.7785 | 479.566 | 550.2889 | 631.2713 | 724.0368 | 830.3385 | 952.1937 | 1091.9246 | 1252.2041 | 1436.1098 | 1647.1851 | 1889.5111 | 2167.7876 | 2487.4287 | 2854.6711 | 3270.8227 | 3744.2883 | 4286.0264 | 4905.3181 | 5612.42 | 6418.5283 | 7335.6583 | 8376.3916 | 8884.6711 | 8721.9357 | 8492.717 | 8169.2373 | 7711.9571 |  | 709.7301 | 806.4796 | 917.1265 | 1043.7217 | 1188.6243 | 1354.5476 | 1544.613 | 1762.4123 | 2012.0791 | 2298.3708 | 2626.7643 | 3003.5649 | 3436.0329 | 3932.5297 | 4502.6849 | 5157.5911 | 5910.0266 | 6774.7136 | 7768.6158 | 8911.2806 | 10225.2359 | 11736.4457 | 13474.8373 | 15474.9089 | 17776.4306 | 19055.0585 | 19055.0585 | 19055.0585 | 19055.0585 | 19055.0585 |  | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.063148 | 0.083706 | 0.11193 | 0.15084 | 0.20471 | 0.27958 | 0.38396 | 0.52993 | 0.7346 | 1.0223 | 1.4275 | 1.9993 | 2.8076 |  | 709.6773 | 806.4269 | 917.0737 | 1043.669 | 1188.5716 | 1354.4948 | 1544.5602 | 1762.3596 | 2012.0263 | 2298.3181 | 2626.7115 | 3003.5121 | 3435.9802 | 3932.4769 | 4502.6321 | 5157.5383 | 5909.9738 | 6774.6505 | 7768.5321 | 8911.1687 | 10225.085 | 11736.241 | 13474.5577 | 15474.525 | 17775.9006 | 19054.3239 | 19054.0362 | 19053.631 | 19053.0592 | 19052.2509 |  | 1026.2315 | 1170.2017 | 1334.8522 | 1523.235 | 1738.8604 | 1985.7661 | 2268.597 | 2592.698 | 2964.22 | 3390.2427 | 3878.9157 | 4439.6219 | 5083.1653 | 5821.988 | 6670.4198 | 7644.967 | 8764.6449 | 10045.4732 | 11512.8204 | 13197.1952 | 15130.4031 | 17348.6609 | 19893.0861 | 22810.1832 | 26152.2922 | 27938.995 | 27775.9719 | 27546.348 | 27222.2965 | 26764.208 |  | 93.0424 | 105.7259 | 120.2312 | 136.8272 | 155.8233 | 177.5751 | 202.4918 | 231.0444 | 263.7746 | 301.3061 | 344.357 | 393.7539 | 450.4485 | 515.537 | 590.2818 | 676.1371 | 774.778 | 888.1346 | 1018.4307 | 1168.229 | 1340.4826 | 1538.5954 | 1766.4908 | 2028.6912 | 2330.4104 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 78.372 | 91.0554 | 105.5607 | 122.1568 | 141.1529 | 162.9046 | 187.8214 | 216.3739 | 249.1041 | 286.6357 | 329.6866 | 379.0834 | 435.7781 | 500.8665 | 575.6113 | 661.4666 | 760.1075 | 870.575 | 995.1544 | 1137.1054 | 1298.5386 | 1481.6704 | 1688.7477 | 1921.9226 | 2183.0519 | 2293.7607 | 2213.767 | 2101.0929 | 1942.0842 | 1717.305 |  | 11.9555 | 13.5853 | 15.4491 | 17.5816 | 20.0225 | 22.8175 | 26.0192 | 29.6881 | 33.8937 | 38.7164 | 44.2482 | 50.5955 | 57.8804 | 66.244 | 75.8483 | 86.8803 | 99.5552 | 114.121 | 130.8634 | 150.1117 | 172.2455 | 197.702 | 226.9854 | 260.6769 | 299.4463 | 320.985 | 320.985 | 320.985 | 320.985 | 320.985 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 9.8878 | 11.5176 | 13.3814 | 15.5139 | 17.9548 | 20.7498 | 23.9515 | 27.6204 | 31.826 | 36.6487 | 42.1805 | 48.5278 | 55.8127 | 64.1763 | 73.7806 | 84.8126 | 97.4875 | 111.6461 | 127.5827 | 145.7251 | 166.3338 | 189.6788 | 216.0281 | 245.6287 | 278.6773 | 292.1944 | 280.9199 | 265.0393 | 242.6282 | 210.9473 |  | 16.2662 | 18.4836 | 21.0194 | 23.9209 | 27.2419 | 31.0446 | 35.4007 | 40.3924 | 46.1145 | 52.6759 | 60.2023 | 68.8381 | 78.7498 | 90.1289 | 103.1962 | 118.2058 | 135.4508 | 155.2684 | 178.0474 | 204.2359 | 234.3502 | 268.9853 | 308.8272 | 354.6665 | 407.4146 | 436.7192 | 436.7192 | 436.7192 | 436.7192 | 436.7192 |  | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.001592 | 0.0021103 | 0.0028217 | 0.0038027 | 0.0051609 | 0.0070484 | 0.0096799 | 0.01336 | 0.01852 | 0.025772 | 0.035987 | 0.050403 | 0.070782 |  | 16.2648 | 18.4822 | 21.0181 | 23.9195 | 27.2405 | 31.0433 | 35.3994 | 40.3911 | 46.1131 | 52.6746 | 60.201 | 68.8368 | 78.7484 | 90.1276 | 103.1948 | 118.2045 | 135.4494 | 155.2668 | 178.0453 | 204.2331 | 234.3464 | 268.9802 | 308.8202 | 354.6568 | 407.4012 | 436.7007 | 436.6934 | 436.6832 | 436.6688 | 436.6484 |  | 1130.7561 | 1291.2569 | 1474.8124 | 1684.8253 | 1925.2087 | 2200.4638 | 2515.7692 | 2877.0833 | 3291.2633 | 3766.2016 | 4310.9837 | 4936.0698 | 5653.5046 | 6477.1584 | 7423.0066 | 8509.4508 | 9757.6894 | 11182.961 | 12813.6028 | 14684.2587 | 16829.6219 | 19288.9903 | 22106.682 | 25332.3913 | 29021.4226 | 30961.6507 | 30707.3522 | 30349.1634 | 29843.6778 | 29129.1087
| FALSE | 29 | 22003628 | AC | AC-ATS | 66 | ATS LINE | PILOT WIRE | X | SEC | GROUP_3385 | GROUP 3385 | GROUP 3000s | Electronic |  | 0.15703 | 2190 |  | 9.9 | 0.042792 | 0.015079 | 0.027713 | 511.6649 | 7298.286 | 7809.9509 | 207.0778 | 17.2719 | 167.268 |  | 16.4925 | 0.17586 | 0.061971 | 0.11389 | 2102.8086 | 29994.0431 | 32096.8517 | 851.0357 | 70.983 | 687.4277 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 59.6909 | 0.53804 | 60.229 | 14.6761 | 2.0677 | 0.012331 |  | 8201.5687 | 33706.2981 | 76.9851 | 33629.3129 |  | 0.051037 |  | 10.4184 | 10.9639 | 11.538 | 12.1422 | 12.778 | 13.447 | 14.1511 | 14.8921 | 15.6719 | 16.4925 | 17.3561 | 18.2649 | 19.2213 | 20.2278 | 21.287 | 22.4016 | 23.5746 | 24.809 | 26.108 | 27.4751 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049141 | 0.056475 | 0.06495 | 0.074748 | 0.086081 | 0.099192 | 0.11437 | 0.13194 | 0.15229 | 0.17586 | 0.20319 | 0.23486 | 0.27158 | 0.31417 | 0.36358 | 0.42091 | 0.48745 | 0.5647 | 0.65438 | 0.75852 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.017316 | 0.019901 | 0.022887 | 0.02634 | 0.030333 | 0.034953 | 0.040301 | 0.046493 | 0.053663 | 0.061971 | 0.071599 | 0.082759 | 0.0957 | 0.11071 | 0.12812 | 0.14832 | 0.17177 | 0.19899 | 0.23059 | 0.26729 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 9418.3969 | 10824.0016 | 12448.3715 | 14326.329 | 16498.3157 | 19011.3079 | 21919.8809 | 25287.4481 | 29187.7031 | 33706.2981 | 38942.7975 | 45012.953 | 52051.3507 | 60214.4944 | 69684.3943 | 80672.7462 | 93425.7976 | 108230.0141 | 125418.6775 | 145379.5705 | 153573.658 | 153573.658 | 153573.658 | 153573.658 | 153573.658 | 153573.658 | 153573.658 | 153573.658 | 153573.658 | 153573.658 |  | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 56.3716 | 74.7239 | 99.9159 | 134.6527 | 182.7462 | 249.5781 | 342.7586 | 473.0639 | 655.7735 | 912.5768 | 1274.2936 | 1784.7582 | 2506.3656 |  | 587.5782 | 675.2686 | 776.6069 | 893.7655 | 1029.2676 | 1186.0437 | 1367.4985 | 1577.5883 | 1820.9105 | 2102.8086 | 2429.494 | 2808.188 | 3247.2871 | 3756.5547 | 4347.346 | 5032.8678 | 5828.4824 | 6752.0616 | 7824.3973 | 9069.682 | 9580.8801 | 9580.8801 | 9580.8801 | 9580.8801 | 9580.8801 | 9580.8801 | 9580.8801 | 9580.8801 | 9580.8801 | 9580.8801 |  | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 35.7232 | 47.3532 | 63.3176 | 85.3306 | 115.8079 | 158.1599 | 217.2092 | 299.7848 | 415.5695 | 578.3079 | 807.5311 | 1131.017 | 1588.3059 |  | 557.7327 | 645.4231 | 746.7614 | 863.9201 | 999.4221 | 1156.1982 | 1337.6531 | 1547.7429 | 1791.065 | 2072.9631 | 2399.6485 | 2778.3426 | 3217.4416 | 3726.7093 | 4317.5005 | 5003.0223 | 5798.637 | 6716.3384 | 7777.0441 | 9006.3644 | 9495.5496 | 9465.0723 | 9422.7203 | 9363.671 | 9281.0954 | 9165.3107 | 9002.5722 | 8773.3491 | 8449.8632 | 7992.5742 |  | 8381.0984 | 9631.8964 | 11077.3658 | 12748.4937 | 14681.2679 | 16917.4908 | 19505.7271 | 22502.4062 | 25973.1052 | 29994.0431 | 34653.8189 | 40055.4356 | 46318.657 | 53582.75 | 62009.6791 | 71787.825 | 83136.3147 | 96310.0636 | 111605.6475 | 129368.1406 | 136659.7694 | 136659.7694 | 136659.7694 | 136659.7694 | 136659.7694 | 136659.7694 | 136659.7694 | 136659.7694 | 136659.7694 | 136659.7694 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 8380.6093 | 9631.4072 | 11076.8767 | 12748.0046 | 14680.7788 | 16917.0017 | 19505.238 | 22501.9171 | 25972.6161 | 29993.554 | 34653.3297 | 40054.9465 | 46318.1679 | 53582.2609 | 62009.19 | 71787.3359 | 83135.8255 | 96309.4781 | 111604.8715 | 129367.1029 | 136658.371 | 136657.8715 | 136657.1774 | 136656.2096 | 136654.8563 | 136652.9588 | 136650.2917 | 136646.535 | 136641.2335 | 136633.7391 |  | 8938.342 | 10276.8303 | 11823.638 | 13611.9246 | 15680.2009 | 18073.1999 | 20842.8911 | 24049.6599 | 27763.6811 | 32066.5171 | 37052.9782 | 42833.2891 | 49535.6094 | 57308.9701 | 66326.6905 | 76790.3582 | 88934.4625 | 103025.8165 | 119381.9156 | 138373.4673 | 146153.9205 | 146122.9438 | 146079.8977 | 146019.8806 | 145935.9517 | 145818.2695 | 145652.8639 | 145419.8841 | 145091.0967 | 144626.3133 |  | 237.801 | 273.2905 | 314.3035 | 361.7193 | 416.5588 | 480.0083 | 553.4456 | 638.4718 | 736.9477 | 851.0357 | 983.2498 | 1136.5125 | 1314.222 | 1520.3296 | 1759.431 | 2036.8712 | 2358.8674 | 2732.6527 | 3166.6418 | 3670.6257 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 223.1249 | 258.6144 | 299.6274 | 347.0432 | 401.8827 | 465.3322 | 538.7695 | 623.7957 | 722.2716 | 836.3596 | 968.5737 | 1121.8364 | 1299.5459 | 1505.6535 | 1744.7549 | 2022.1951 | 2344.1913 | 2715.0863 | 3143.3565 | 3639.4902 | 3835.5545 | 3820.5678 | 3799.7417 | 3770.7051 | 3730.0997 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 19.8345 | 22.7946 | 26.2154 | 30.1702 | 34.7442 | 40.0364 | 46.1617 | 53.2535 | 61.4672 | 70.983 | 82.0107 | 94.794 | 109.6163 | 126.8073 | 146.7502 | 169.8909 | 196.7479 | 227.9245 | 264.1225 | 306.1587 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 17.7668 | 20.7269 | 24.1477 | 28.1025 | 32.6765 | 37.9687 | 44.094 | 51.1858 | 59.3995 | 68.9153 | 79.943 | 92.7263 | 107.5486 | 124.7396 | 144.6825 | 167.8232 | 194.6802 | 225.4496 | 260.8419 | 301.772 | 317.5031 | 315.3917 | 312.4575 | 308.3665 | 302.6457 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 192.0848 | 220.7516 | 253.88 | 292.1803 | 336.4772 | 387.7287 | 447.048 | 515.7283 | 595.2726 | 687.4277 | 794.2242 | 918.0228 | 1061.5684 | 1228.0527 | 1421.1879 | 1645.2913 | 1905.3852 | 2207.3118 | 2557.8684 | 2964.9635 | 3132.079 | 3132.079 | 3132.079 | 3132.079 | 3132.079 | 3132.079 | 3132.079 | 3132.079 | 3132.079 | 3132.079 |  | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.01476 | 0.019565 | 0.026161 | 0.035256 | 0.047848 | 0.065347 | 0.089745 | 0.12386 | 0.1717 | 0.23894 | 0.33365 | 0.4673 | 0.65624 |  | 192.0725 | 220.7392 | 253.8677 | 292.1679 | 336.4648 | 387.7164 | 447.0357 | 515.716 | 595.2603 | 687.4154 | 794.2119 | 918.0105 | 1061.5561 | 1228.0404 | 1421.1756 | 1645.279 | 1905.3729 | 2207.297 | 2557.8488 | 2964.9374 | 3132.0437 | 3132.0311 | 3132.0136 | 3131.9892 | 3131.9551 | 3131.9072 | 3131.84 | 3131.7453 | 3131.6116 | 3131.4227 |  | 9371.3061 | 10776.9108 | 12401.2808 | 14279.2383 | 16451.225 | 18964.2172 | 21872.7902 | 25240.3574 | 29140.6124 | 33659.2073 | 38895.7068 | 44965.8622 | 52004.26 | 60167.4037 | 69637.3036 | 80625.6554 | 93378.7069 | 108173.6494 | 125343.9628 | 145279.6668 | 153439.0219 | 153390.9343 | 153324.1105 | 153230.9415 | 153100.6521 | 152917.965 | 152661.1932 | 152299.5207 | 151789.1188 | 151067.5999
| FALSE | 30 | 22003631 | AC | AC-ATS | 66 | ATS LINE | AUTO RECLOSE | C | LOCUS | LAR_3156 | LAR 3156 | LAR | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 111.5394 | 1590.9756 | 1702.515 | 45.1415 | 3.7652 | 36.4633 |  | 8.2866 | 0.026595 | 0.0093716 | 0.017224 | 317.9985 | 4535.8669 | 4853.8653 | 128.6984 | 10.7344 | 103.9567 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 59.6909 | 0.53804 | 60.229 | 14.6761 | 2.0677 | 0.012331 |  | 1787.8849 | 5097.2548 | 76.9851 | 5020.2697 |  | 0.04099 |  | 5.7301 | 5.9699 | 6.2197 | 6.4799 | 6.751 | 7.0335 | 7.3278 | 7.6344 | 7.9538 | 8.2866 | 8.6334 | 8.9946 | 9.3709 | 9.763 | 10.1715 | 10.5971 | 11.0405 | 11.5025 | 11.9838 | 12.4852 | 13.0076 | 13.5518 | 14.1188 | 14.7096 | 15.3251 | 15.9663 | 16.6343 | 17.3303 | 18.0555 | 18.8109 |  | 0.010321 | 0.01143 | 0.012669 | 0.014054 | 0.015602 | 0.017334 | 0.019272 | 0.021442 | 0.023872 | 0.026595 | 0.029647 | 0.033069 | 0.036906 | 0.041212 | 0.046044 | 0.051469 | 0.05756 | 0.064402 | 0.07209 | 0.080729 | 0.09044 | 0.10136 | 0.11364 | 0.12745 | 0.143 | 0.16048 | 0.18017 | 0.20233 | 0.22728 | 0.25539 |  | 0.0036371 | 0.0040279 | 0.0044644 | 0.0049523 | 0.0054979 | 0.0061081 | 0.0067911 | 0.0075558 | 0.0084121 | 0.0093716 | 0.010447 | 0.011653 | 0.013005 | 0.014522 | 0.016225 | 0.018137 | 0.020283 | 0.022694 | 0.025403 | 0.028447 | 0.031869 | 0.035717 | 0.040045 | 0.044912 | 0.050389 | 0.056552 | 0.063489 | 0.071298 | 0.080091 | 0.089993 | 1978.2248 | 2190.7619 | 2428.1978 | 2693.5717 | 2990.3031 | 3322.2399 | 3693.7131 | 4109.5981 | 4575.3848 | 5097.2548 | 5682.1711 | 6337.9769 | 7073.5091 | 7898.7247 | 8824.8455 | 9864.5192 | 11032.0033 | 12343.3717 | 13816.7483 | 15472.5704 | 17333.8873 | 19426.6961 | 21780.3223 | 24427.8486 | 27406.6004 | 30758.6933 | 34531.652 | 38779.1098 | 43561.5986 | 48947.441 |  | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 56.3716 | 74.7239 | 99.9159 | 134.6527 | 182.7462 | 249.5781 | 342.7586 | 473.0639 | 655.7735 | 912.5768 | 1274.2936 | 1784.7582 | 2506.3656 |  | 123.414 | 136.6734 | 151.4861 | 168.0418 | 186.5537 | 207.262 | 230.4368 | 256.3823 | 285.441 | 317.9985 | 354.4892 | 395.4024 | 441.2895 | 492.7716 | 550.5488 | 615.4101 | 688.245 | 770.0563 | 861.9747 | 965.2752 | 1081.3957 | 1211.9582 | 1358.792 | 1523.9612 | 1709.7942 | 1918.9186 | 2154.2993 | 2419.2821 | 2717.6435 | 3053.6459 |  | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 35.7232 | 47.3532 | 63.3176 | 85.3306 | 115.8079 | 158.1599 | 217.2092 | 299.7848 | 415.5695 | 578.3079 | 807.5311 | 1131.017 | 1588.3059 |  | 93.5685 | 106.8279 | 121.6406 | 138.1963 | 156.7082 | 177.4165 | 200.5913 | 226.5368 | 255.5955 | 288.153 | 324.6437 | 365.557 | 411.444 | 462.9261 | 520.7033 | 585.5646 | 658.3995 | 734.3332 | 814.6215 | 901.9576 | 996.0651 | 1096.1503 | 1200.6321 | 1306.752 | 1410.0095 | 1503.3492 | 1575.9913 | 1611.751 | 1586.6265 | 1465.3399 |  | 1760.3524 | 1949.4815 | 2160.7674 | 2396.9143 | 2660.9651 | 2956.3439 | 3286.9047 | 3656.9861 | 4071.4732 | 4535.8669 | 5056.3632 | 5639.9416 | 6294.4657 | 7028.7959 | 7852.918 | 8778.0869 | 9816.9897 | 10983.9302 | 12295.0359 | 13768.4935 | 15424.8136 | 17287.1302 | 19381.5389 | 21737.479 | 24388.1649 | 27371.0738 | 30728.4964 | 34508.159 | 38763.9267 | 43556.5974 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 1759.8632 | 1948.9924 | 2160.2782 | 2396.4251 | 2660.4759 | 2955.8547 | 3286.4155 | 3656.497 | 4070.984 | 4535.3778 | 5055.8741 | 5639.4525 | 6293.9765 | 7028.3068 | 7852.4289 | 8777.5978 | 9816.5006 | 10983.3447 | 12294.2598 | 13767.4558 | 15423.4151 | 17285.2322 | 19378.9468 | 21733.9192 | 24383.2518 | 27364.2632 | 30719.0187 | 34494.9246 | 38745.3907 | 43530.5671 |  | 1853.4317 | 2055.8203 | 2281.9189 | 2534.6214 | 2817.1842 | 3133.2712 | 3487.0069 | 3883.0338 | 4326.5795 | 4823.5307 | 5380.5178 | 6005.0095 | 6705.4206 | 7491.2329 | 8373.1322 | 9363.1623 | 10474.9001 | 11717.6779 | 13108.8814 | 14669.4134 | 16419.4802 | 18381.3825 | 20579.579 | 23040.6712 | 25793.2613 | 28867.6124 | 32295.01 | 36106.6756 | 40332.0173 | 44995.907 |  | 49.9473 | 55.3136 | 61.3085 | 68.0088 | 75.5009 | 83.8818 | 93.261 | 103.7615 | 115.5219 | 128.6984 | 143.4667 | 160.0248 | 178.596 | 199.4315 | 222.8147 | 249.065 | 278.5423 | 311.6524 | 348.8531 | 390.6602 | 437.6558 | 490.4962 | 549.9219 | 616.7682 | 691.9774 | 776.6129 | 871.8747 | 979.1169 | 1099.8679 | 1235.8527 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 35.2712 | 40.6375 | 46.6324 | 53.3327 | 60.8248 | 69.2057 | 78.5849 | 89.0854 | 100.8458 | 114.0223 | 128.7906 | 145.3487 | 163.9199 | 184.7554 | 208.1386 | 234.3889 | 263.8662 | 294.0861 | 325.5678 | 359.5247 | 395.6957 | 433.5493 | 472.149 | 509.9586 | 544.5624 | 572.2624 | 587.4998 | 582.0247 | 543.706 | 454.8253 |  | 4.166 | 4.6136 | 5.1136 | 5.6725 | 6.2974 | 6.9964 | 7.7787 | 8.6545 | 9.6354 | 10.7344 | 11.9662 | 13.3473 | 14.8963 | 16.6341 | 18.5845 | 20.774 | 23.2326 | 25.9942 | 29.0971 | 32.5841 | 36.5039 | 40.9112 | 45.8678 | 51.4433 | 57.7163 | 64.7756 | 72.7211 | 81.666 | 91.7375 | 103.0797 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 2.0983 | 2.5459 | 3.0459 | 3.6048 | 4.2297 | 4.9287 | 5.711 | 6.5868 | 7.5677 | 8.6667 | 9.8985 | 11.2796 | 12.8286 | 14.5664 | 16.5168 | 18.7063 | 21.1649 | 23.5193 | 25.8164 | 28.1974 | 30.5922 | 32.888 | 34.9104 | 36.3949 | 36.9471 | 35.9848 | 32.6558 | 25.72 | 13.3804 | -6.9585 |  | 40.3452 | 44.6798 | 49.5222 | 54.9344 | 60.9861 | 67.7559 | 75.3319 | 83.8138 | 93.3133 | 103.9567 | 115.8858 | 129.2607 | 144.2616 | 161.0916 | 179.9795 | 201.1833 | 224.9937 | 251.7386 | 281.7876 | 315.5575 | 353.5183 | 396.2004 | 444.2018 | 498.1971 | 558.9477 | 627.3124 | 704.2605 | 790.8859 | 888.423 | 998.2653 |  | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.01476 | 0.019565 | 0.026161 | 0.035256 | 0.047848 | 0.065347 | 0.089745 | 0.12386 | 0.1717 | 0.23894 | 0.33365 | 0.4673 | 0.65624 |  | 40.3328 | 44.6675 | 49.5099 | 54.9221 | 60.9738 | 67.7435 | 75.3196 | 83.8014 | 93.301 | 103.9443 | 115.8735 | 129.2484 | 144.2493 | 161.0793 | 179.9672 | 201.171 | 224.9814 | 251.7238 | 281.768 | 315.5313 | 353.4831 | 396.1526 | 444.1364 | 498.1074 | 558.8238 | 627.1407 | 704.0216 | 790.5522 | 887.9557 | 997.609 |  | 1931.1341 | 2143.6711 | 2381.1071 | 2646.481 | 2943.2124 | 3275.1492 | 3646.6223 | 4062.5074 | 4528.294 | 5050.1641 | 5635.0804 | 6290.8862 | 7026.4183 | 7851.634 | 8777.7547 | 9817.4284 | 10984.9126 | 12287.0071 | 13742.0336 | 15372.6668 | 17199.2511 | 19243.9724 | 21530.7748 | 24085.132 | 26933.5945 | 30103.0002 | 33619.1871 | 37504.9725 | 41777.0593 | 46441.3828
| FALSE | 31 | 22003586 | AC | AC-CPL | 66 | CPL LINE | PILOT WIRE | X | Brown Boveri | GROUP_2372 | GROUP 2372 | GROUP 2000s | Electronic |  | 0.15703 | 2190 |  | 8.25 | 0.026286 | 0.0092625 | 0.017023 | 314.2971 | 4483.0716 | 4797.3687 | 127.2004 | 10.6095 | 102.7467 |  | 13.322 | 0.096648 | 0.034057 | 0.062591 | 1155.6205 | 16483.5405 | 17639.161 | 467.6956 | 39.0094 | 377.7831 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 59.6909 | 0.53804 | 60.229 | 14.6761 | 2.0677 | 0.012331 |  | 5037.9253 | 18523.6491 | 76.9851 | 18446.664 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.010517 | 0.01195 | 0.01359 | 0.015466 | 0.017613 | 0.020071 | 0.022888 | 0.026115 | 0.029815 | 0.034057 | 0.038923 | 0.044506 | 0.050915 | 0.058272 | 0.06672 | 0.076424 | 0.087574 | 0.10039 | 0.11511 | 0.13205 | 0.15152 | 0.17391 | 0.19967 | 0.2293 | 0.26341 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 5720.0475 | 6499.7977 | 7391.5526 | 8411.8433 | 9579.6813 | 10916.9344 | 12448.7606 | 14204.1078 | 16216.2895 | 18523.6491 | 21170.3261 | 24207.1387 | 27692.6018 | 31694.1019 | 36289.2505 | 41567.4466 | 47631.6773 | 54600.5962 | 62610.9199 | 71820.1922 | 82409.9741 | 94589.523 | 108600.0368 | 124719.5525 | 143268.5954 | 153573.658 | 153573.658 | 153573.658 | 153573.658 | 153573.658 |  | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 56.3716 | 74.7239 | 99.9159 | 134.6527 | 182.7462 | 249.5781 | 342.7586 | 473.0639 | 655.7735 | 912.5768 | 1274.2936 | 1784.7582 | 2506.3656 |  | 356.8521 | 405.4978 | 461.131 | 524.7831 | 597.6401 | 681.0663 | 776.6311 | 886.1406 | 1011.673 | 1155.6205 | 1320.7366 | 1510.1919 | 1727.6368 | 1977.2752 | 2263.9492 | 2593.2359 | 2971.5603 | 3406.3249 | 3906.0587 | 4480.5904 | 5141.2468 | 5901.0829 | 6775.1459 | 7780.7815 | 8937.9862 | 9580.8801 | 9580.8801 | 9580.8801 | 9580.8801 | 9580.8801 |  | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 35.7232 | 47.3532 | 63.3176 | 85.3306 | 115.8079 | 158.1599 | 217.2092 | 299.7848 | 415.5695 | 578.3079 | 807.5311 | 1131.017 | 1588.3059 |  | 327.0067 | 375.6523 | 431.2856 | 494.9376 | 567.7946 | 651.2208 | 746.7857 | 856.2951 | 981.8275 | 1125.775 | 1290.8912 | 1480.3464 | 1697.7913 | 1947.4298 | 2234.1037 | 2563.3904 | 2941.7149 | 3370.6017 | 3858.7055 | 4417.2728 | 5055.9163 | 5785.275 | 6616.986 | 7563.5724 | 8638.2015 | 9165.3107 | 9002.5722 | 8773.3491 | 8449.8632 | 7992.5742 |  | 5090.0681 | 5783.9402 | 6577.4814 | 7485.402 | 8524.6197 | 9714.594 | 11077.712 | 12639.7334 | 14430.3027 | 16483.5405 | 18838.7249 | 21541.077 | 24642.6674 | 28203.4609 | 32292.5212 | 36989.4013 | 42385.7458 | 48587.1405 | 55715.2443 | 63910.2502 | 73333.7228 | 84171.8727 | 96639.3337 | 110983.5209 | 127489.6584 | 136659.7694 | 136659.7694 | 136659.7694 | 136659.7694 | 136659.7694 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 5089.579 | 5783.4511 | 6576.9922 | 7484.9129 | 8524.1306 | 9714.1048 | 11077.2229 | 12639.2443 | 14429.8136 | 16483.0514 | 18838.2357 | 21540.5878 | 24642.1783 | 28202.9717 | 32292.0321 | 36988.9121 | 42385.2567 | 48586.555 | 55714.4682 | 63909.2125 | 73332.3243 | 84169.9748 | 96636.7417 | 110979.9611 | 127484.7453 | 136652.9588 | 136650.2917 | 136646.535 | 136641.2335 | 136633.7391 |  | 5416.5856 | 6159.1034 | 7008.2778 | 7979.8505 | 9091.9252 | 10365.3257 | 11824.0086 | 13495.5394 | 15411.6412 | 17608.8264 | 20129.1269 | 23020.9343 | 26339.9696 | 30150.4015 | 34526.1358 | 39552.3026 | 45326.9716 | 51957.1567 | 59573.1737 | 68326.4852 | 78388.2406 | 89955.2498 | 103253.7277 | 118543.5335 | 136122.9468 | 145818.2695 | 145652.8639 | 145419.8841 | 145091.0967 | 144626.3133 |  | 144.423 | 164.1106 | 186.6261 | 212.387 | 241.8732 | 275.6369 | 314.3134 | 358.6334 | 409.4381 | 467.6956 | 534.5204 | 611.1955 | 699.1985 | 800.2306 | 916.2515 | 1049.5184 | 1202.6316 | 1378.5868 | 1580.836 | 1813.3569 | 2080.7337 | 2388.2498 | 2741.9952 | 3148.9899 | 3617.3266 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 129.7469 | 149.4345 | 171.95 | 197.7109 | 227.1971 | 260.9608 | 299.6373 | 343.9573 | 394.762 | 453.0195 | 519.8443 | 596.5194 | 684.5224 | 785.5545 | 901.5754 | 1034.8423 | 1187.9555 | 1361.0204 | 1557.5507 | 1782.2213 | 2038.7735 | 2331.3029 | 2664.2223 | 3042.1803 | 3469.9116 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 12.046 | 13.6881 | 15.5661 | 17.7147 | 20.1741 | 22.9903 | 26.2162 | 29.9128 | 34.1503 | 39.0094 | 44.5832 | 50.9785 | 58.3186 | 66.7455 | 76.4225 | 87.538 | 100.3088 | 114.9848 | 131.854 | 151.2481 | 173.5494 | 199.1986 | 228.7037 | 262.6502 | 301.7131 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 9.9783 | 11.6204 | 13.4984 | 15.647 | 18.1064 | 20.9226 | 24.1485 | 27.8451 | 32.0826 | 36.9417 | 42.5155 | 48.9108 | 56.2509 | 64.6778 | 74.3548 | 85.4703 | 98.2411 | 112.5099 | 128.5734 | 146.8614 | 167.6376 | 191.1754 | 217.7464 | 247.6019 | 280.944 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 116.6583 | 132.561 | 150.748 | 171.5565 | 195.3741 | 222.6469 | 253.8879 | 289.6876 | 330.7253 | 377.7831 | 431.7611 | 493.6958 | 564.7806 | 646.3897 | 740.1061 | 847.753 | 971.4307 | 1113.5593 | 1276.927 | 1464.7467 | 1680.7215 | 1929.1189 | 2214.8583 | 2543.61 | 2921.9109 | 3132.079 | 3132.079 | 3132.079 | 3132.079 | 3132.079 |  | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.01476 | 0.019565 | 0.026161 | 0.035256 | 0.047848 | 0.065347 | 0.089745 | 0.12386 | 0.1717 | 0.23894 | 0.33365 | 0.4673 | 0.65624 |  | 116.646 | 132.5487 | 150.7357 | 171.5442 | 195.3618 | 222.6346 | 253.8756 | 289.6753 | 330.713 | 377.7708 | 431.7488 | 493.6835 | 564.7682 | 646.3774 | 740.0937 | 847.7406 | 971.4184 | 1113.5446 | 1276.9074 | 1464.7206 | 1680.6862 | 1929.0711 | 2214.7929 | 2543.5202 | 2921.7871 | 3131.9072 | 3131.84 | 3131.7453 | 3131.6116 | 3131.4227 |  | 5672.9568 | 6452.7069 | 7344.4619 | 8364.7526 | 9532.5905 | 10869.8436 | 12401.6699 | 14157.0171 | 16169.1987 | 18476.5584 | 21123.2354 | 24160.0479 | 27645.5111 | 31647.0111 | 36242.1598 | 41520.3558 | 47584.5866 | 54544.2316 | 62536.2052 | 71720.2885 | 82275.338 | 94406.7992 | 108350.4893 | 124376.8359 | 142795.5895 | 152917.965 | 152661.1932 | 152299.5207 | 151789.1188 | 151067.5999
| FALSE | 32 | 22003587 | AC | AC-CPL | 66 | CPL LINE | PILOT WIRE CURR INTLK | Y | English Electric | GROUP_2375 | GROUP 2375 | GROUP 2000s | Electronic |  | 0.016937 | 2190 |  | 8.25 | 0.026286 | 0.0012915 | 0.024994 | 305.0906 | 625.0939 | 930.1845 | 81.947 | 10.5298 | 14.3264 |  | 13.322 | 0.096648 | 0.0047487 | 0.091899 | 1121.7695 | 2298.3708 | 3420.1403 | 301.3061 | 38.7164 | 52.6759 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 59.6898 | 0.058033 | 59.7478 | 14.6705 | 2.0677 | 0.0013301 |  | 1036.9877 | 3812.8387 | 76.4873 | 3736.3514 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0014664 | 0.0016663 | 0.0018949 | 0.0021564 | 0.0024558 | 0.0027987 | 0.0031913 | 0.0036413 | 0.0041572 | 0.0047487 | 0.0054272 | 0.0062057 | 0.0070992 | 0.0081251 | 0.0093031 | 0.010656 | 0.012211 | 0.013997 | 0.016051 | 0.018412 | 0.021127 | 0.024249 | 0.027841 | 0.031973 | 0.036728 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 1177.3932 | 1337.8941 | 1521.4496 | 1731.4624 | 1971.8458 | 2247.101 | 2562.4064 | 2923.7205 | 3337.9004 | 3812.8387 | 4357.6208 | 4982.707 | 5700.1417 | 6523.7955 | 7469.6438 | 8556.0879 | 9804.3265 | 11238.7828 | 12887.5978 | 14783.2001 | 16962.9612 | 19469.954 | 22353.8259 | 25671.8068 | 29489.8724 | 31611.0281 | 31611.0281 | 31611.0281 | 31611.0281 | 31611.0281 |  | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 55.8225 | 73.996 | 98.9427 | 133.3411 | 180.9661 | 247.1471 | 339.42 | 468.4561 | 649.386 | 903.6879 | 1261.8815 | 1767.3739 | 2481.9526 |  | 346.3991 | 393.6198 | 447.6234 | 509.4109 | 580.1338 | 661.1162 | 753.8817 | 860.1834 | 982.0386 | 1121.7695 | 1282.049 | 1465.9547 | 1677.03 | 1919.356 | 2197.6325 | 2517.2736 | 2884.516 | 3306.5452 | 3791.6406 | 4349.3428 | 4990.647 | 5728.2256 | 6576.6851 | 7552.8633 | 8676.1706 | 9300.2325 | 9300.2325 | 9300.2325 | 9300.2325 | 9300.2325 |  | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 35.7225 | 47.3523 | 63.3164 | 85.329 | 115.8056 | 158.1568 | 217.205 | 299.779 | 415.5615 | 578.2969 | 807.5156 | 1130.9953 | 1588.2755 |  | 316.5542 | 363.7749 | 417.7785 | 479.566 | 550.2889 | 631.2713 | 724.0368 | 830.3385 | 952.1937 | 1091.9246 | 1252.2041 | 1436.1098 | 1647.1851 | 1889.5111 | 2167.7876 | 2487.4287 | 2854.6711 | 3270.8227 | 3744.2883 | 4286.0264 | 4905.3181 | 5612.42 | 6418.5283 | 7335.6583 | 8376.3916 | 8884.6711 | 8721.9357 | 8492.717 | 8169.2373 | 7711.9571 |  | 709.7301 | 806.4796 | 917.1265 | 1043.7217 | 1188.6243 | 1354.5476 | 1544.613 | 1762.4123 | 2012.0791 | 2298.3708 | 2626.7643 | 3003.5649 | 3436.0329 | 3932.5297 | 4502.6849 | 5157.5911 | 5910.0266 | 6774.7136 | 7768.6158 | 8911.2806 | 10225.2359 | 11736.4457 | 13474.8373 | 15474.9089 | 17776.4306 | 19055.0585 | 19055.0585 | 19055.0585 | 19055.0585 | 19055.0585 |  | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.063148 | 0.083706 | 0.11193 | 0.15084 | 0.20471 | 0.27958 | 0.38396 | 0.52993 | 0.7346 | 1.0223 | 1.4275 | 1.9993 | 2.8076 |  | 709.6773 | 806.4269 | 917.0737 | 1043.669 | 1188.5716 | 1354.4948 | 1544.5602 | 1762.3596 | 2012.0263 | 2298.3181 | 2626.7115 | 3003.5121 | 3435.9802 | 3932.4769 | 4502.6321 | 5157.5383 | 5909.9738 | 6774.6505 | 7768.5321 | 8911.1687 | 10225.085 | 11736.241 | 13474.5577 | 15474.525 | 17775.9006 | 19054.3239 | 19054.0362 | 19053.631 | 19053.0592 | 19052.2509 |  | 1026.2315 | 1170.2017 | 1334.8522 | 1523.235 | 1738.8604 | 1985.7661 | 2268.597 | 2592.698 | 2964.22 | 3390.2427 | 3878.9157 | 4439.6219 | 5083.1653 | 5821.988 | 6670.4198 | 7644.967 | 8764.6449 | 10045.4732 | 11512.8204 | 13197.1952 | 15130.4031 | 17348.6609 | 19893.0861 | 22810.1832 | 26152.2922 | 27938.995 | 27775.9719 | 27546.348 | 27222.2965 | 26764.208 |  | 93.0424 | 105.7259 | 120.2312 | 136.8272 | 155.8233 | 177.5751 | 202.4918 | 231.0444 | 263.7746 | 301.3061 | 344.357 | 393.7539 | 450.4485 | 515.537 | 590.2818 | 676.1371 | 774.778 | 888.1346 | 1018.4307 | 1168.229 | 1340.4826 | 1538.5954 | 1766.4908 | 2028.6912 | 2330.4104 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 78.372 | 91.0554 | 105.5607 | 122.1568 | 141.1529 | 162.9046 | 187.8214 | 216.3739 | 249.1041 | 286.6357 | 329.6866 | 379.0834 | 435.7781 | 500.8665 | 575.6113 | 661.4666 | 760.1075 | 870.575 | 995.1544 | 1137.1054 | 1298.5386 | 1481.6704 | 1688.7477 | 1921.9226 | 2183.0519 | 2293.7607 | 2213.767 | 2101.0929 | 1942.0842 | 1717.305 |  | 11.9555 | 13.5853 | 15.4491 | 17.5816 | 20.0225 | 22.8175 | 26.0192 | 29.6881 | 33.8937 | 38.7164 | 44.2482 | 50.5955 | 57.8804 | 66.244 | 75.8483 | 86.8803 | 99.5552 | 114.121 | 130.8634 | 150.1117 | 172.2455 | 197.702 | 226.9854 | 260.6769 | 299.4463 | 320.985 | 320.985 | 320.985 | 320.985 | 320.985 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 9.8878 | 11.5176 | 13.3814 | 15.5139 | 17.9548 | 20.7498 | 23.9515 | 27.6204 | 31.826 | 36.6487 | 42.1805 | 48.5278 | 55.8127 | 64.1763 | 73.7806 | 84.8126 | 97.4875 | 111.6461 | 127.5827 | 145.7251 | 166.3338 | 189.6788 | 216.0281 | 245.6287 | 278.6773 | 292.1944 | 280.9199 | 265.0393 | 242.6282 | 210.9473 |  | 16.2662 | 18.4836 | 21.0194 | 23.9209 | 27.2419 | 31.0446 | 35.4007 | 40.3924 | 46.1145 | 52.6759 | 60.2023 | 68.8381 | 78.7498 | 90.1289 | 103.1962 | 118.2058 | 135.4508 | 155.2684 | 178.0474 | 204.2359 | 234.3502 | 268.9853 | 308.8272 | 354.6665 | 407.4146 | 436.7192 | 436.7192 | 436.7192 | 436.7192 | 436.7192 |  | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.001592 | 0.0021103 | 0.0028217 | 0.0038027 | 0.0051609 | 0.0070484 | 0.0096799 | 0.01336 | 0.01852 | 0.025772 | 0.035987 | 0.050403 | 0.070782 |  | 16.2648 | 18.4822 | 21.0181 | 23.9195 | 27.2405 | 31.0433 | 35.3994 | 40.3911 | 46.1131 | 52.6746 | 60.201 | 68.8368 | 78.7484 | 90.1276 | 103.1948 | 118.2045 | 135.4494 | 155.2668 | 178.0453 | 204.2331 | 234.3464 | 268.9802 | 308.8202 | 354.6568 | 407.4012 | 436.7007 | 436.6934 | 436.6832 | 436.6688 | 436.6484 |  | 1130.7561 | 1291.2569 | 1474.8124 | 1684.8253 | 1925.2087 | 2200.4638 | 2515.7692 | 2877.0833 | 3291.2633 | 3766.2016 | 4310.9837 | 4936.0698 | 5653.5046 | 6477.1584 | 7423.0066 | 8509.4508 | 9757.6894 | 11182.961 | 12813.6028 | 14684.2587 | 16829.6219 | 19288.9903 | 22106.682 | 25332.3913 | 29021.4226 | 30961.6507 | 30707.3522 | 30349.1634 | 29843.6778 | 29129.1087
| FALSE | 33 | 22015633 | AC | AC-CPL | 66 | CPL LINE | NEUTRAL DISPLACEMENT | Y | ASEA | GROUP_2605 | GROUP 2605 | GROUP 2000s | Electronic |  | 0.016937 | 2190 |  | 8.25 | 0.026286 | 0.0012915 | 0.024994 | 305.0906 | 625.0939 | 930.1845 | 81.947 | 10.5298 | 14.3264 |  | 13.322 | 0.096648 | 0.0047487 | 0.091899 | 1121.7695 | 2298.3708 | 3420.1403 | 301.3061 | 38.7164 | 52.6759 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 59.6898 | 0.058033 | 59.7478 | 14.6705 | 2.0677 | 0.0013301 |  | 1036.9877 | 3812.8387 | 76.4873 | 3736.3514 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0014664 | 0.0016663 | 0.0018949 | 0.0021564 | 0.0024558 | 0.0027987 | 0.0031913 | 0.0036413 | 0.0041572 | 0.0047487 | 0.0054272 | 0.0062057 | 0.0070992 | 0.0081251 | 0.0093031 | 0.010656 | 0.012211 | 0.013997 | 0.016051 | 0.018412 | 0.021127 | 0.024249 | 0.027841 | 0.031973 | 0.036728 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 1177.3932 | 1337.8941 | 1521.4496 | 1731.4624 | 1971.8458 | 2247.101 | 2562.4064 | 2923.7205 | 3337.9004 | 3812.8387 | 4357.6208 | 4982.707 | 5700.1417 | 6523.7955 | 7469.6438 | 8556.0879 | 9804.3265 | 11238.7828 | 12887.5978 | 14783.2001 | 16962.9612 | 19469.954 | 22353.8259 | 25671.8068 | 29489.8724 | 31611.0281 | 31611.0281 | 31611.0281 | 31611.0281 | 31611.0281 |  | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 55.8225 | 73.996 | 98.9427 | 133.3411 | 180.9661 | 247.1471 | 339.42 | 468.4561 | 649.386 | 903.6879 | 1261.8815 | 1767.3739 | 2481.9526 |  | 346.3991 | 393.6198 | 447.6234 | 509.4109 | 580.1338 | 661.1162 | 753.8817 | 860.1834 | 982.0386 | 1121.7695 | 1282.049 | 1465.9547 | 1677.03 | 1919.356 | 2197.6325 | 2517.2736 | 2884.516 | 3306.5452 | 3791.6406 | 4349.3428 | 4990.647 | 5728.2256 | 6576.6851 | 7552.8633 | 8676.1706 | 9300.2325 | 9300.2325 | 9300.2325 | 9300.2325 | 9300.2325 |  | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 35.7225 | 47.3523 | 63.3164 | 85.329 | 115.8056 | 158.1568 | 217.205 | 299.779 | 415.5615 | 578.2969 | 807.5156 | 1130.9953 | 1588.2755 |  | 316.5542 | 363.7749 | 417.7785 | 479.566 | 550.2889 | 631.2713 | 724.0368 | 830.3385 | 952.1937 | 1091.9246 | 1252.2041 | 1436.1098 | 1647.1851 | 1889.5111 | 2167.7876 | 2487.4287 | 2854.6711 | 3270.8227 | 3744.2883 | 4286.0264 | 4905.3181 | 5612.42 | 6418.5283 | 7335.6583 | 8376.3916 | 8884.6711 | 8721.9357 | 8492.717 | 8169.2373 | 7711.9571 |  | 709.7301 | 806.4796 | 917.1265 | 1043.7217 | 1188.6243 | 1354.5476 | 1544.613 | 1762.4123 | 2012.0791 | 2298.3708 | 2626.7643 | 3003.5649 | 3436.0329 | 3932.5297 | 4502.6849 | 5157.5911 | 5910.0266 | 6774.7136 | 7768.6158 | 8911.2806 | 10225.2359 | 11736.4457 | 13474.8373 | 15474.9089 | 17776.4306 | 19055.0585 | 19055.0585 | 19055.0585 | 19055.0585 | 19055.0585 |  | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.063148 | 0.083706 | 0.11193 | 0.15084 | 0.20471 | 0.27958 | 0.38396 | 0.52993 | 0.7346 | 1.0223 | 1.4275 | 1.9993 | 2.8076 |  | 709.6773 | 806.4269 | 917.0737 | 1043.669 | 1188.5716 | 1354.4948 | 1544.5602 | 1762.3596 | 2012.0263 | 2298.3181 | 2626.7115 | 3003.5121 | 3435.9802 | 3932.4769 | 4502.6321 | 5157.5383 | 5909.9738 | 6774.6505 | 7768.5321 | 8911.1687 | 10225.085 | 11736.241 | 13474.5577 | 15474.525 | 17775.9006 | 19054.3239 | 19054.0362 | 19053.631 | 19053.0592 | 19052.2509 |  | 1026.2315 | 1170.2017 | 1334.8522 | 1523.235 | 1738.8604 | 1985.7661 | 2268.597 | 2592.698 | 2964.22 | 3390.2427 | 3878.9157 | 4439.6219 | 5083.1653 | 5821.988 | 6670.4198 | 7644.967 | 8764.6449 | 10045.4732 | 11512.8204 | 13197.1952 | 15130.4031 | 17348.6609 | 19893.0861 | 22810.1832 | 26152.2922 | 27938.995 | 27775.9719 | 27546.348 | 27222.2965 | 26764.208 |  | 93.0424 | 105.7259 | 120.2312 | 136.8272 | 155.8233 | 177.5751 | 202.4918 | 231.0444 | 263.7746 | 301.3061 | 344.357 | 393.7539 | 450.4485 | 515.537 | 590.2818 | 676.1371 | 774.778 | 888.1346 | 1018.4307 | 1168.229 | 1340.4826 | 1538.5954 | 1766.4908 | 2028.6912 | 2330.4104 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 78.372 | 91.0554 | 105.5607 | 122.1568 | 141.1529 | 162.9046 | 187.8214 | 216.3739 | 249.1041 | 286.6357 | 329.6866 | 379.0834 | 435.7781 | 500.8665 | 575.6113 | 661.4666 | 760.1075 | 870.575 | 995.1544 | 1137.1054 | 1298.5386 | 1481.6704 | 1688.7477 | 1921.9226 | 2183.0519 | 2293.7607 | 2213.767 | 2101.0929 | 1942.0842 | 1717.305 |  | 11.9555 | 13.5853 | 15.4491 | 17.5816 | 20.0225 | 22.8175 | 26.0192 | 29.6881 | 33.8937 | 38.7164 | 44.2482 | 50.5955 | 57.8804 | 66.244 | 75.8483 | 86.8803 | 99.5552 | 114.121 | 130.8634 | 150.1117 | 172.2455 | 197.702 | 226.9854 | 260.6769 | 299.4463 | 320.985 | 320.985 | 320.985 | 320.985 | 320.985 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 9.8878 | 11.5176 | 13.3814 | 15.5139 | 17.9548 | 20.7498 | 23.9515 | 27.6204 | 31.826 | 36.6487 | 42.1805 | 48.5278 | 55.8127 | 64.1763 | 73.7806 | 84.8126 | 97.4875 | 111.6461 | 127.5827 | 145.7251 | 166.3338 | 189.6788 | 216.0281 | 245.6287 | 278.6773 | 292.1944 | 280.9199 | 265.0393 | 242.6282 | 210.9473 |  | 16.2662 | 18.4836 | 21.0194 | 23.9209 | 27.2419 | 31.0446 | 35.4007 | 40.3924 | 46.1145 | 52.6759 | 60.2023 | 68.8381 | 78.7498 | 90.1289 | 103.1962 | 118.2058 | 135.4508 | 155.2684 | 178.0474 | 204.2359 | 234.3502 | 268.9853 | 308.8272 | 354.6665 | 407.4146 | 436.7192 | 436.7192 | 436.7192 | 436.7192 | 436.7192 |  | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.0013301 | 0.001592 | 0.0021103 | 0.0028217 | 0.0038027 | 0.0051609 | 0.0070484 | 0.0096799 | 0.01336 | 0.01852 | 0.025772 | 0.035987 | 0.050403 | 0.070782 |  | 16.2648 | 18.4822 | 21.0181 | 23.9195 | 27.2405 | 31.0433 | 35.3994 | 40.3911 | 46.1131 | 52.6746 | 60.201 | 68.8368 | 78.7484 | 90.1276 | 103.1948 | 118.2045 | 135.4494 | 155.2668 | 178.0453 | 204.2331 | 234.3464 | 268.9802 | 308.8202 | 354.6568 | 407.4012 | 436.7007 | 436.6934 | 436.6832 | 436.6688 | 436.6484 |  | 1130.7561 | 1291.2569 | 1474.8124 | 1684.8253 | 1925.2087 | 2200.4638 | 2515.7692 | 2877.0833 | 3291.2633 | 3766.2016 | 4310.9837 | 4936.0698 | 5653.5046 | 6477.1584 | 7423.0066 | 8509.4508 | 9757.6894 | 11182.961 | 12813.6028 | 14684.2587 | 16829.6219 | 19288.9903 | 22106.682 | 25332.3913 | 29021.4226 | 30961.6507 | 30707.3522 | 30349.1634 | 29843.6778 | 29129.1087
| FALSE | 34 | 22003630 | AC | AC-CPL | 66 | CPL LINE | AUTO RECLOSE | C | LOCUS | LAR_3156 | LAR 3156 | LAR | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 111.5394 | 1590.9756 | 1702.515 | 45.1415 | 3.7652 | 36.4633 |  | 8.2866 | 0.026595 | 0.0093716 | 0.017224 | 317.9985 | 4535.8669 | 4853.8653 | 128.6984 | 10.7344 | 103.9567 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 59.6909 | 0.53804 | 60.229 | 14.6761 | 2.0677 | 0.012331 |  | 1787.8849 | 5097.2548 | 76.9851 | 5020.2697 |  | 0.04099 |  | 5.7301 | 5.9699 | 6.2197 | 6.4799 | 6.751 | 7.0335 | 7.3278 | 7.6344 | 7.9538 | 8.2866 | 8.6334 | 8.9946 | 9.3709 | 9.763 | 10.1715 | 10.5971 | 11.0405 | 11.5025 | 11.9838 | 12.4852 | 13.0076 | 13.5518 | 14.1188 | 14.7096 | 15.3251 | 15.9663 | 16.6343 | 17.3303 | 18.0555 | 18.8109 |  | 0.010321 | 0.01143 | 0.012669 | 0.014054 | 0.015602 | 0.017334 | 0.019272 | 0.021442 | 0.023872 | 0.026595 | 0.029647 | 0.033069 | 0.036906 | 0.041212 | 0.046044 | 0.051469 | 0.05756 | 0.064402 | 0.07209 | 0.080729 | 0.09044 | 0.10136 | 0.11364 | 0.12745 | 0.143 | 0.16048 | 0.18017 | 0.20233 | 0.22728 | 0.25539 |  | 0.0036371 | 0.0040279 | 0.0044644 | 0.0049523 | 0.0054979 | 0.0061081 | 0.0067911 | 0.0075558 | 0.0084121 | 0.0093716 | 0.010447 | 0.011653 | 0.013005 | 0.014522 | 0.016225 | 0.018137 | 0.020283 | 0.022694 | 0.025403 | 0.028447 | 0.031869 | 0.035717 | 0.040045 | 0.044912 | 0.050389 | 0.056552 | 0.063489 | 0.071298 | 0.080091 | 0.089993 | 1978.2248 | 2190.7619 | 2428.1978 | 2693.5717 | 2990.3031 | 3322.2399 | 3693.7131 | 4109.5981 | 4575.3848 | 5097.2548 | 5682.1711 | 6337.9769 | 7073.5091 | 7898.7247 | 8824.8455 | 9864.5192 | 11032.0033 | 12343.3717 | 13816.7483 | 15472.5704 | 17333.8873 | 19426.6961 | 21780.3223 | 24427.8486 | 27406.6004 | 30758.6933 | 34531.652 | 38779.1098 | 43561.5986 | 48947.441 |  | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 47.0965 | 56.3716 | 74.7239 | 99.9159 | 134.6527 | 182.7462 | 249.5781 | 342.7586 | 473.0639 | 655.7735 | 912.5768 | 1274.2936 | 1784.7582 | 2506.3656 |  | 123.414 | 136.6734 | 151.4861 | 168.0418 | 186.5537 | 207.262 | 230.4368 | 256.3823 | 285.441 | 317.9985 | 354.4892 | 395.4024 | 441.2895 | 492.7716 | 550.5488 | 615.4101 | 688.245 | 770.0563 | 861.9747 | 965.2752 | 1081.3957 | 1211.9582 | 1358.792 | 1523.9612 | 1709.7942 | 1918.9186 | 2154.2993 | 2419.2821 | 2717.6435 | 3053.6459 |  | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 29.8455 | 35.7232 | 47.3532 | 63.3176 | 85.3306 | 115.8079 | 158.1599 | 217.2092 | 299.7848 | 415.5695 | 578.3079 | 807.5311 | 1131.017 | 1588.3059 |  | 93.5685 | 106.8279 | 121.6406 | 138.1963 | 156.7082 | 177.4165 | 200.5913 | 226.5368 | 255.5955 | 288.153 | 324.6437 | 365.557 | 411.444 | 462.9261 | 520.7033 | 585.5646 | 658.3995 | 734.3332 | 814.6215 | 901.9576 | 996.0651 | 1096.1503 | 1200.6321 | 1306.752 | 1410.0095 | 1503.3492 | 1575.9913 | 1611.751 | 1586.6265 | 1465.3399 |  | 1760.3524 | 1949.4815 | 2160.7674 | 2396.9143 | 2660.9651 | 2956.3439 | 3286.9047 | 3656.9861 | 4071.4732 | 4535.8669 | 5056.3632 | 5639.9416 | 6294.4657 | 7028.7959 | 7852.918 | 8778.0869 | 9816.9897 | 10983.9302 | 12295.0359 | 13768.4935 | 15424.8136 | 17287.1302 | 19381.5389 | 21737.479 | 24388.1649 | 27371.0738 | 30728.4964 | 34508.159 | 38763.9267 | 43556.5974 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 1759.8632 | 1948.9924 | 2160.2782 | 2396.4251 | 2660.4759 | 2955.8547 | 3286.4155 | 3656.497 | 4070.984 | 4535.3778 | 5055.8741 | 5639.4525 | 6293.9765 | 7028.3068 | 7852.4289 | 8777.5978 | 9816.5006 | 10983.3447 | 12294.2598 | 13767.4558 | 15423.4151 | 17285.2322 | 19378.9468 | 21733.9192 | 24383.2518 | 27364.2632 | 30719.0187 | 34494.9246 | 38745.3907 | 43530.5671 |  | 1853.4317 | 2055.8203 | 2281.9189 | 2534.6214 | 2817.1842 | 3133.2712 | 3487.0069 | 3883.0338 | 4326.5795 | 4823.5307 | 5380.5178 | 6005.0095 | 6705.4206 | 7491.2329 | 8373.1322 | 9363.1623 | 10474.9001 | 11717.6779 | 13108.8814 | 14669.4134 | 16419.4802 | 18381.3825 | 20579.579 | 23040.6712 | 25793.2613 | 28867.6124 | 32295.01 | 36106.6756 | 40332.0173 | 44995.907 |  | 49.9473 | 55.3136 | 61.3085 | 68.0088 | 75.5009 | 83.8818 | 93.261 | 103.7615 | 115.5219 | 128.6984 | 143.4667 | 160.0248 | 178.596 | 199.4315 | 222.8147 | 249.065 | 278.5423 | 311.6524 | 348.8531 | 390.6602 | 437.6558 | 490.4962 | 549.9219 | 616.7682 | 691.9774 | 776.6129 | 871.8747 | 979.1169 | 1099.8679 | 1235.8527 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 35.2712 | 40.6375 | 46.6324 | 53.3327 | 60.8248 | 69.2057 | 78.5849 | 89.0854 | 100.8458 | 114.0223 | 128.7906 | 145.3487 | 163.9199 | 184.7554 | 208.1386 | 234.3889 | 263.8662 | 294.0861 | 325.5678 | 359.5247 | 395.6957 | 433.5493 | 472.149 | 509.9586 | 544.5624 | 572.2624 | 587.4998 | 582.0247 | 543.706 | 454.8253 |  | 4.166 | 4.6136 | 5.1136 | 5.6725 | 6.2974 | 6.9964 | 7.7787 | 8.6545 | 9.6354 | 10.7344 | 11.9662 | 13.3473 | 14.8963 | 16.6341 | 18.5845 | 20.774 | 23.2326 | 25.9942 | 29.0971 | 32.5841 | 36.5039 | 40.9112 | 45.8678 | 51.4433 | 57.7163 | 64.7756 | 72.7211 | 81.666 | 91.7375 | 103.0797 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 2.0983 | 2.5459 | 3.0459 | 3.6048 | 4.2297 | 4.9287 | 5.711 | 6.5868 | 7.5677 | 8.6667 | 9.8985 | 11.2796 | 12.8286 | 14.5664 | 16.5168 | 18.7063 | 21.1649 | 23.5193 | 25.8164 | 28.1974 | 30.5922 | 32.888 | 34.9104 | 36.3949 | 36.9471 | 35.9848 | 32.6558 | 25.72 | 13.3804 | -6.9585 |  | 40.3452 | 44.6798 | 49.5222 | 54.9344 | 60.9861 | 67.7559 | 75.3319 | 83.8138 | 93.3133 | 103.9567 | 115.8858 | 129.2607 | 144.2616 | 161.0916 | 179.9795 | 201.1833 | 224.9937 | 251.7386 | 281.7876 | 315.5575 | 353.5183 | 396.2004 | 444.2018 | 498.1971 | 558.9477 | 627.3124 | 704.2605 | 790.8859 | 888.423 | 998.2653 |  | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.012331 | 0.01476 | 0.019565 | 0.026161 | 0.035256 | 0.047848 | 0.065347 | 0.089745 | 0.12386 | 0.1717 | 0.23894 | 0.33365 | 0.4673 | 0.65624 |  | 40.3328 | 44.6675 | 49.5099 | 54.9221 | 60.9738 | 67.7435 | 75.3196 | 83.8014 | 93.301 | 103.9443 | 115.8735 | 129.2484 | 144.2493 | 161.0793 | 179.9672 | 201.171 | 224.9814 | 251.7238 | 281.768 | 315.5313 | 353.4831 | 396.1526 | 444.1364 | 498.1074 | 558.8238 | 627.1407 | 704.0216 | 790.5522 | 887.9557 | 997.609 |  | 1931.1341 | 2143.6711 | 2381.1071 | 2646.481 | 2943.2124 | 3275.1492 | 3646.6223 | 4062.5074 | 4528.294 | 5050.1641 | 5635.0804 | 6290.8862 | 7026.4183 | 7851.634 | 8777.7547 | 9817.4284 | 10984.9126 | 12287.0071 | 13742.0336 | 15372.6668 | 17199.2511 | 19243.9724 | 21530.7748 | 24085.132 | 26933.5945 | 30103.0002 | 33619.1871 | 37504.9725 | 41777.0593 | 46441.3828
| TRUE | 35 | 22003638 | AC | Blank | 66 | TRANS NO.2 | DIFFERENTIAL | Y | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.0068096 | 2190 |  | 8.25 | 0.026286 | 0.00052975 | 0.025756 | 304.2107 | 256.3973 | 560.608 | 77.6223 | 10.5222 | 5.8763 |  | 13.322 | 0.096648 | 0.0019478 | 0.0947 | 1118.5344 | 942.732 | 2061.2664 | 285.4047 | 38.6884 | 21.6063 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 59.6897 | 0.023332 | 59.713 | 14.6701 | 2.0677 | 0.00053475 |  | 654.6288 | 2406.9658 | 76.4513 | 2330.5145 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00060147 | 0.00068346 | 0.00077723 | 0.00088452 | 0.0010073 | 0.0011479 | 0.001309 | 0.0014936 | 0.0017052 | 0.0019478 | 0.0022261 | 0.0025454 | 0.0029119 | 0.0033327 | 0.0038159 | 0.0043709 | 0.0050086 | 0.0057413 | 0.0065836 | 0.007552 | 0.0086655 | 0.0099462 | 0.011419 | 0.013114 | 0.015065 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 743.2638 | 844.5847 | 960.4595 | 1093.0362 | 1244.7852 | 1418.5481 | 1617.5939 | 1845.6839 | 2107.1471 | 2406.9658 | 2750.8754 | 3145.4793 | 3598.3809 | 4118.3364 | 4715.4308 | 5401.2804 | 6189.2674 | 7094.8098 | 8135.6725 | 9332.3268 | 10708.3646 | 12290.9771 | 14111.5054 | 16206.0777 | 18616.3432 | 19955.3846 | 19955.3846 | 19955.3846 | 19955.3846 | 19955.3846 |  | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 55.7828 | 73.9434 | 98.8723 | 133.2463 | 180.8375 | 246.9714 | 339.1787 | 468.123 | 648.9242 | 903.0453 | 1260.9842 | 1766.1171 | 2480.1877 |  | 345.4001 | 392.4846 | 446.3325 | 507.9418 | 578.4607 | 659.2096 | 751.7076 | 857.7027 | 979.2065 | 1118.5344 | 1278.3517 | 1461.727 | 1672.1937 | 1913.8208 | 2191.2948 | 2510.0141 | 2876.1974 | 3297.0095 | 3780.706 | 4336.7999 | 4976.2546 | 5711.7061 | 6557.7188 | 7531.0817 | 8651.1495 | 9273.4118 | 9273.4118 | 9273.4118 | 9273.4118 | 9273.4118 |  | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 35.7224 | 47.3522 | 63.3163 | 85.3288 | 115.8055 | 158.1566 | 217.2047 | 299.7786 | 415.5609 | 578.296 | 807.5145 | 1130.9937 | 1588.2733 |  | 315.5552 | 362.6398 | 416.4876 | 478.097 | 548.6159 | 629.3647 | 721.8627 | 827.8578 | 949.3617 | 1088.6896 | 1248.5069 | 1431.8822 | 1642.3488 | 1883.9759 | 2161.45 | 2480.1693 | 2846.3526 | 3261.2871 | 3733.3538 | 4273.4836 | 4890.9258 | 5595.9006 | 6399.5622 | 7313.877 | 8351.3709 | 8857.8509 | 8695.1157 | 8465.8973 | 8142.4181 | 7685.1385 |  | 291.1128 | 330.797 | 376.1814 | 428.1075 | 487.5428 | 555.6002 | 633.5601 | 722.8957 | 825.3025 | 942.732 | 1077.4305 | 1231.9842 | 1409.3714 | 1613.0215 | 1846.8843 | 2115.5098 | 2424.1393 | 2778.8115 | 3186.4843 | 3655.1757 | 4194.126 | 4813.985 | 5527.0281 | 6347.4055 | 7291.4298 | 7815.8898 | 7815.8898 | 7815.8898 | 7815.8898 | 7815.8898 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 291.0916 | 330.7758 | 376.1602 | 428.0863 | 487.5216 | 555.579 | 633.5389 | 722.8745 | 825.2813 | 942.7108 | 1077.4092 | 1231.963 | 1409.3502 | 1613.0003 | 1846.8631 | 2115.4886 | 2424.1181 | 2778.7861 | 3186.4506 | 3655.1307 | 4194.0654 | 4813.9027 | 5526.9157 | 6347.2511 | 7291.2168 | 7815.5944 | 7815.4788 | 7815.3159 | 7815.086 | 7814.761 |  | 606.6468 | 693.4155 | 792.6479 | 906.1833 | 1036.1375 | 1184.9437 | 1355.4016 | 1550.7324 | 1774.643 | 2031.4004 | 2325.9161 | 2663.8452 | 3051.699 | 3496.9762 | 4008.3131 | 4595.6579 | 5270.4706 | 6040.0732 | 6919.8044 | 7928.6143 | 9084.9912 | 10409.8033 | 11926.4778 | 13661.1281 | 15642.5877 | 16673.4453 | 16510.5945 | 16281.2132 | 15957.5041 | 15499.8995 |  | 88.1321 | 100.1462 | 113.886 | 129.6062 | 147.5998 | 168.2036 | 191.8054 | 218.851 | 249.8539 | 285.4047 | 326.1836 | 372.9736 | 426.6761 | 488.3296 | 559.1298 | 640.454 | 733.8892 | 841.2634 | 964.6831 | 1106.5758 | 1269.7388 | 1457.3962 | 1673.2644 | 1921.6273 | 2207.4232 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 73.4621 | 85.4761 | 99.2159 | 114.9361 | 132.9297 | 153.5335 | 177.1353 | 204.181 | 235.1838 | 270.7347 | 311.5136 | 358.3035 | 412.0061 | 473.6595 | 544.4597 | 625.784 | 719.2191 | 823.7043 | 941.4075 | 1075.4531 | 1227.7959 | 1400.4727 | 1595.5235 | 1814.8616 | 2060.0689 | 2161.9329 | 2081.9414 | 1969.2705 | 1810.2663 | 1585.4933 |  | 11.9468 | 13.5754 | 15.4379 | 17.5689 | 20.0081 | 22.801 | 26.0004 | 29.6666 | 33.8692 | 38.6884 | 44.2162 | 50.5588 | 57.8386 | 66.1961 | 75.7935 | 86.8175 | 99.4832 | 114.0384 | 130.7687 | 150.0031 | 172.1209 | 197.559 | 226.8212 | 260.4883 | 299.2297 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 9.8792 | 11.5077 | 13.3702 | 15.5012 | 17.9404 | 20.7333 | 23.9327 | 27.5989 | 31.8015 | 36.6207 | 42.1485 | 48.4912 | 55.7709 | 64.1284 | 73.7258 | 84.7498 | 97.4155 | 111.5635 | 127.4881 | 145.6165 | 166.2092 | 189.5358 | 215.8639 | 245.4401 | 278.4607 | 291.9622 | 280.6877 | 264.8071 | 242.396 | 210.7151 |  | 6.672 | 7.5815 | 8.6216 | 9.8117 | 11.1739 | 12.7337 | 14.5204 | 16.5679 | 18.915 | 21.6063 | 24.6934 | 28.2356 | 32.3011 | 36.9685 | 42.3284 | 48.485 | 55.5584 | 63.687 | 73.0304 | 83.7723 | 96.1244 | 110.3308 | 126.6729 | 145.475 | 167.1109 | 179.1309 | 179.1309 | 179.1309 | 179.1309 | 179.1309 |  | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00064006 | 0.00084844 | 0.0011345 | 0.0015289 | 0.002075 | 0.0028338 | 0.0038918 | 0.0053713 | 0.0074459 | 0.010362 | 0.014469 | 0.020265 | 0.028458 |  | 6.6714 | 7.5809 | 8.6211 | 9.8112 | 11.1734 | 12.7332 | 14.5199 | 16.5674 | 18.9144 | 21.6058 | 24.6929 | 28.2351 | 32.3006 | 36.968 | 42.3279 | 48.4844 | 55.5578 | 63.6864 | 73.0296 | 83.7711 | 96.1228 | 110.3287 | 126.6701 | 145.4711 | 167.1055 | 179.1234 | 179.1205 | 179.1164 | 179.1106 | 179.1024 |  | 696.6595 | 797.9803 | 913.8551 | 1046.4319 | 1198.1809 | 1371.9438 | 1570.9895 | 1799.0796 | 2060.5428 | 2360.3614 | 2704.2711 | 3098.8749 | 3551.7766 | 4071.7321 | 4668.8264 | 5354.676 | 6142.6631 | 7039.0273 | 8061.7295 | 9233.4549 | 10575.1191 | 12110.1406 | 13864.5353 | 15866.9009 | 18148.2227 | 19306.4638 | 19052.3441 | 18694.4072 | 18189.277 | 17475.2103
| TRUE | 36 | 22003637 | AC | Blank | 66 | TRANS NO.2 | DIFFERENTIAL | X | ABB | RADSB_3057 | RADSB 3057 | RADSB | Electronic |  | 0.066046 | 2190 |  | 6.6 | 0.014726 | 0.0025679 | 0.012158 | 173.0518 | 1242.8812 | 1415.933 | 56.3804 | 5.9176 | 28.4854 |  | 10.2588 | 0.047123 | 0.0082173 | 0.038906 | 553.7611 | 3977.1855 | 4530.9466 | 180.4156 | 18.9361 | 91.1523 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 59.6902 | 0.2263 | 59.9165 | 14.6724 | 2.0677 | 0.0051866 |  | 1506.7163 | 4821.4506 | 76.6618 | 4744.7888 |  | 0.044106 |  | 6.8976 | 7.2087 | 7.5337 | 7.8734 | 8.2285 | 8.5995 | 8.9873 | 9.3926 | 9.8161 | 10.2588 | 10.7214 | 11.2048 | 11.7101 | 12.2381 | 12.79 | 13.3667 | 13.9695 | 14.5994 | 15.2578 | 15.9458 | 16.6648 | 17.4163 | 18.2017 | 19.0225 | 19.8802 | 20.7767 | 21.7136 | 22.6927 | 23.716 | 24.7855 |  | 0.016485 | 0.018471 | 0.020712 | 0.023244 | 0.026105 | 0.029339 | 0.032997 | 0.037136 | 0.04182 | 0.047123 | 0.053129 | 0.059935 | 0.067647 | 0.076391 | 0.086306 | 0.097553 | 0.11031 | 0.1248 | 0.14124 | 0.15991 | 0.18111 | 0.20519 | 0.23255 | 0.26365 | 0.299 | 0.33918 | 0.38487 | 0.43682 | 0.49592 | 0.56315 |  | 0.0028747 | 0.0032209 | 0.0036118 | 0.0040533 | 0.0045522 | 0.0051162 | 0.0057541 | 0.0064757 | 0.0072925 | 0.0082173 | 0.0092647 | 0.010451 | 0.011796 | 0.013321 | 0.01505 | 0.017011 | 0.019237 | 0.021762 | 0.024629 | 0.027884 | 0.031581 | 0.035781 | 0.040553 | 0.045975 | 0.052139 | 0.059146 | 0.067113 | 0.076174 | 0.086479 | 0.098203 | 1686.7193 | 1889.8506 | 2119.1896 | 2378.235 | 2670.9623 | 3001.8894 | 3376.1519 | 3799.5884 | 4278.8379 | 4821.4506 | 5436.0145 | 6132.2992 | 6921.4205 | 7816.0269 | 8830.5136 | 9981.2653 | 11286.9336 | 12768.7528 | 14450.9004 | 16360.9082 | 18530.1303 | 20994.2775 | 23794.0269 | 26975.7159 | 30592.1348 | 34703.4306 | 39378.137 | 44694.3503 | 50741.0699 | 57619.7272 |  | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 56.015 | 74.2512 | 99.2839 | 133.8009 | 181.5901 | 247.9993 | 340.5904 | 470.0714 | 651.6252 | 906.804 | 1266.2326 | 1773.468 | 2490.5107 |  | 193.7258 | 217.0562 | 243.3966 | 273.1489 | 306.7697 | 344.7779 | 387.7633 | 436.3965 | 491.44 | 553.7611 | 624.3459 | 704.3168 | 794.9502 | 897.699 | 1014.2164 | 1146.3845 | 1296.3452 | 1466.5375 | 1659.7382 | 1879.1095 | 2128.2525 | 2411.2688 | 2732.8301 | 3098.2586 | 3513.6174 | 3985.8146 | 4522.7216 | 5133.3079 | 5827.7955 | 6617.8342 |  | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 35.7227 | 47.3526 | 63.3168 | 85.3295 | 115.8064 | 158.1579 | 217.2064 | 299.781 | 415.5643 | 578.3007 | 807.521 | 1131.0029 | 1588.2861 |  | 163.8807 | 187.2111 | 213.5515 | 243.3038 | 276.9246 | 314.9328 | 357.9182 | 406.5514 | 461.5949 | 523.916 | 594.5008 | 674.4717 | 765.1051 | 867.8539 | 984.3713 | 1116.5394 | 1266.5001 | 1430.8148 | 1612.3856 | 1815.7927 | 2042.923 | 2295.4624 | 2574.6722 | 2881.0522 | 3213.8364 | 3570.2503 | 3944.4208 | 4325.7869 | 4696.7927 | 5029.5481 |  | 1391.3646 | 1558.9263 | 1748.1067 | 1961.7917 | 2203.2607 | 2476.2404 | 2784.9673 | 3134.2576 | 3529.5876 | 3977.1855 | 4484.1356 | 5058.4967 | 5709.438 | 6447.3934 | 7284.2374 | 8233.4856 | 9310.5235 | 10532.8671 | 11920.4606 | 13496.0145 | 15285.3927 | 17318.0529 | 19627.5493 | 22252.1053 | 25235.2675 | 28626.6506 | 32482.7877 | 36868.1 | 41856.0025 | 47530.1654 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 1391.1589 | 1558.7206 | 1747.901 | 1961.586 | 2203.055 | 2476.0347 | 2784.7616 | 3134.0518 | 3529.3818 | 3976.9798 | 4483.9298 | 5058.2909 | 5709.2323 | 6447.1877 | 7284.0317 | 8233.2798 | 9310.3177 | 10532.6209 | 11920.1342 | 13495.578 | 15284.8045 | 17317.2546 | 19626.4591 | 22250.6081 | 25233.201 | 28623.786 | 32478.8013 | 36862.5336 | 41848.2062 | 47519.217 |  | 1555.0396 | 1745.9317 | 1961.4525 | 2204.8898 | 2479.9795 | 2790.9675 | 3142.6798 | 3540.6032 | 3990.9768 | 4500.8958 | 5078.4307 | 5732.7626 | 6474.3373 | 7315.0416 | 8268.403 | 9349.8192 | 10576.8178 | 11963.4357 | 13532.5198 | 15311.3707 | 17327.7275 | 19612.717 | 22201.1313 | 25131.6602 | 28447.0374 | 32194.0363 | 36423.2222 | 41188.3205 | 46544.9989 | 52548.7651 |  | 63.116 | 70.717 | 79.2987 | 88.992 | 99.9457 | 112.3288 | 126.3335 | 142.1782 | 160.1114 | 180.4156 | 203.4122 | 229.4667 | 258.9952 | 292.4708 | 330.4322 | 373.4926 | 422.3499 | 477.7986 | 540.7435 | 612.2148 | 693.3857 | 785.5925 | 890.3574 | 1009.4141 | 1144.7382 | 1298.5803 | 1473.5049 | 1672.4342 | 1898.6986 | 2156.0936 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 48.4435 | 56.0446 | 64.6263 | 74.3196 | 85.2733 | 97.6564 | 111.661 | 127.5057 | 145.439 | 165.7432 | 188.7398 | 214.7943 | 244.3227 | 277.7983 | 315.7598 | 358.8202 | 407.6774 | 460.2366 | 517.464 | 581.087 | 651.436 | 728.6598 | 812.6038 | 902.6312 | 997.36 | 1094.2807 | 1189.2008 | 1275.4409 | 1342.6753 | 1375.2607 |  | 6.6245 | 7.4223 | 8.323 | 9.3404 | 10.4901 | 11.7898 | 13.2597 | 14.9227 | 16.805 | 18.9361 | 21.3497 | 24.0844 | 27.1836 | 30.6971 | 34.6815 | 39.201 | 44.329 | 50.1488 | 56.7554 | 64.2568 | 72.7764 | 82.4542 | 93.4501 | 105.9461 | 120.1495 | 136.2964 | 154.6561 | 175.5354 | 199.2836 | 226.2993 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 4.5568 | 5.3546 | 6.2553 | 7.2727 | 8.4224 | 9.7221 | 11.192 | 12.855 | 14.7373 | 16.8684 | 19.282 | 22.0167 | 25.1159 | 28.6295 | 32.6138 | 37.1333 | 42.2613 | 47.6739 | 53.4747 | 59.8702 | 66.8647 | 74.4311 | 82.4928 | 90.8978 | 99.3803 | 107.5057 | 114.5909 | 119.5896 | 120.9267 | 116.2614 |  | 31.8884 | 35.7287 | 40.0645 | 44.9619 | 50.4961 | 56.7525 | 63.8281 | 71.8334 | 80.8939 | 91.1523 | 102.771 | 115.9347 | 130.8535 | 147.7666 | 166.946 | 188.7017 | 213.3861 | 241.4008 | 273.2027 | 309.3126 | 350.323 | 396.9091 | 449.84 | 509.9917 | 578.3622 | 656.0887 | 744.4668 | 844.9729 | 959.2897 | 1089.3347 |  | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.006208 | 0.0082291 | 0.011003 | 0.014829 | 0.020125 | 0.027485 | 0.037747 | 0.052097 | 0.072218 | 0.1005 | 0.14033 | 0.19655 | 0.27602 |  | 31.8832 | 35.7235 | 40.0593 | 44.9567 | 50.4909 | 56.7473 | 63.8229 | 71.8283 | 80.8888 | 91.1472 | 102.7659 | 115.9295 | 130.8483 | 147.7614 | 166.9408 | 188.6965 | 213.3809 | 241.3945 | 273.1945 | 309.3016 | 350.3081 | 396.889 | 449.8125 | 509.954 | 578.3101 | 656.0165 | 744.3663 | 844.8326 | 959.0931 | 1089.0587 |  | 1639.9232 | 1843.0544 | 2072.3934 | 2331.4389 | 2624.1661 | 2955.0932 | 3329.3557 | 3752.7923 | 4232.0417 | 4774.6545 | 5389.2184 | 6085.5031 | 6874.6243 | 7769.2307 | 8783.7174 | 9934.4692 | 11240.1375 | 12712.7407 | 14376.6531 | 16261.6295 | 18396.3363 | 20812.6968 | 23546.0405 | 26635.1432 | 30122.0879 | 34051.8393 | 38471.3801 | 43428.1835 | 48967.694 | 55129.3459
| TRUE | 37 | 22003640 | AC | Blank | 66 | TRANS NO.3 | DIFFERENTIAL | Y | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.0068096 | 2190 |  | 8.25 | 0.026286 | 0.00052975 | 0.025756 | 304.2107 | 256.3973 | 560.608 | 77.6223 | 10.5222 | 5.8763 |  | 13.322 | 0.096648 | 0.0019478 | 0.0947 | 1118.5344 | 942.732 | 2061.2664 | 285.4047 | 38.6884 | 21.6063 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 59.6897 | 0.023332 | 59.713 | 14.6701 | 2.0677 | 0.00053475 |  | 654.6288 | 2406.9658 | 76.4513 | 2330.5145 |  | 0.047921 |  | 8.655 | 9.0798 | 9.5255 | 9.9931 | 10.4836 | 10.9983 | 11.5381 | 12.1045 | 12.6987 | 13.322 | 13.976 | 14.662 | 15.3818 | 16.1368 | 16.9289 | 17.7599 | 18.6317 | 19.5463 | 20.5058 | 21.5123 | 22.5683 | 23.6762 | 24.8384 | 26.0576 | 27.3367 | 28 | 28 | 28 | 28 | 28 |  | 0.029845 | 0.033913 | 0.038566 | 0.043889 | 0.049982 | 0.05696 | 0.064952 | 0.074111 | 0.084609 | 0.096648 | 0.11046 | 0.1263 | 0.14449 | 0.16537 | 0.18934 | 0.21688 | 0.24852 | 0.28488 | 0.32668 | 0.37473 | 0.42998 | 0.49353 | 0.56663 | 0.65073 | 0.74751 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00060147 | 0.00068346 | 0.00077723 | 0.00088452 | 0.0010073 | 0.0011479 | 0.001309 | 0.0014936 | 0.0017052 | 0.0019478 | 0.0022261 | 0.0025454 | 0.0029119 | 0.0033327 | 0.0038159 | 0.0043709 | 0.0050086 | 0.0057413 | 0.0065836 | 0.007552 | 0.0086655 | 0.0099462 | 0.011419 | 0.013114 | 0.015065 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 743.2638 | 844.5847 | 960.4595 | 1093.0362 | 1244.7852 | 1418.5481 | 1617.5939 | 1845.6839 | 2107.1471 | 2406.9658 | 2750.8754 | 3145.4793 | 3598.3809 | 4118.3364 | 4715.4308 | 5401.2804 | 6189.2674 | 7094.8098 | 8135.6725 | 9332.3268 | 10708.3646 | 12290.9771 | 14111.5054 | 16206.0777 | 18616.3432 | 19955.3846 | 19955.3846 | 19955.3846 | 19955.3846 | 19955.3846 |  | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 46.6046 | 55.7828 | 73.9434 | 98.8723 | 133.2463 | 180.8375 | 246.9714 | 339.1787 | 468.123 | 648.9242 | 903.0453 | 1260.9842 | 1766.1171 | 2480.1877 |  | 345.4001 | 392.4846 | 446.3325 | 507.9418 | 578.4607 | 659.2096 | 751.7076 | 857.7027 | 979.2065 | 1118.5344 | 1278.3517 | 1461.727 | 1672.1937 | 1913.8208 | 2191.2948 | 2510.0141 | 2876.1974 | 3297.0095 | 3780.706 | 4336.7999 | 4976.2546 | 5711.7061 | 6557.7188 | 7531.0817 | 8651.1495 | 9273.4118 | 9273.4118 | 9273.4118 | 9273.4118 | 9273.4118 |  | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 29.8449 | 35.7224 | 47.3522 | 63.3163 | 85.3288 | 115.8055 | 158.1566 | 217.2047 | 299.7786 | 415.5609 | 578.296 | 807.5145 | 1130.9937 | 1588.2733 |  | 315.5552 | 362.6398 | 416.4876 | 478.097 | 548.6159 | 629.3647 | 721.8627 | 827.8578 | 949.3617 | 1088.6896 | 1248.5069 | 1431.8822 | 1642.3488 | 1883.9759 | 2161.45 | 2480.1693 | 2846.3526 | 3261.2871 | 3733.3538 | 4273.4836 | 4890.9258 | 5595.9006 | 6399.5622 | 7313.877 | 8351.3709 | 8857.8509 | 8695.1157 | 8465.8973 | 8142.4181 | 7685.1385 |  | 291.1128 | 330.797 | 376.1814 | 428.1075 | 487.5428 | 555.6002 | 633.5601 | 722.8957 | 825.3025 | 942.732 | 1077.4305 | 1231.9842 | 1409.3714 | 1613.0215 | 1846.8843 | 2115.5098 | 2424.1393 | 2778.8115 | 3186.4843 | 3655.1757 | 4194.126 | 4813.985 | 5527.0281 | 6347.4055 | 7291.4298 | 7815.8898 | 7815.8898 | 7815.8898 | 7815.8898 | 7815.8898 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 291.0916 | 330.7758 | 376.1602 | 428.0863 | 487.5216 | 555.579 | 633.5389 | 722.8745 | 825.2813 | 942.7108 | 1077.4092 | 1231.963 | 1409.3502 | 1613.0003 | 1846.8631 | 2115.4886 | 2424.1181 | 2778.7861 | 3186.4506 | 3655.1307 | 4194.0654 | 4813.9027 | 5526.9157 | 6347.2511 | 7291.2168 | 7815.5944 | 7815.4788 | 7815.3159 | 7815.086 | 7814.761 |  | 606.6468 | 693.4155 | 792.6479 | 906.1833 | 1036.1375 | 1184.9437 | 1355.4016 | 1550.7324 | 1774.643 | 2031.4004 | 2325.9161 | 2663.8452 | 3051.699 | 3496.9762 | 4008.3131 | 4595.6579 | 5270.4706 | 6040.0732 | 6919.8044 | 7928.6143 | 9084.9912 | 10409.8033 | 11926.4778 | 13661.1281 | 15642.5877 | 16673.4453 | 16510.5945 | 16281.2132 | 15957.5041 | 15499.8995 |  | 88.1321 | 100.1462 | 113.886 | 129.6062 | 147.5998 | 168.2036 | 191.8054 | 218.851 | 249.8539 | 285.4047 | 326.1836 | 372.9736 | 426.6761 | 488.3296 | 559.1298 | 640.454 | 733.8892 | 841.2634 | 964.6831 | 1106.5758 | 1269.7388 | 1457.3962 | 1673.2644 | 1921.6273 | 2207.4232 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 73.4621 | 85.4761 | 99.2159 | 114.9361 | 132.9297 | 153.5335 | 177.1353 | 204.181 | 235.1838 | 270.7347 | 311.5136 | 358.3035 | 412.0061 | 473.6595 | 544.4597 | 625.784 | 719.2191 | 823.7043 | 941.4075 | 1075.4531 | 1227.7959 | 1400.4727 | 1595.5235 | 1814.8616 | 2060.0689 | 2161.9329 | 2081.9414 | 1969.2705 | 1810.2663 | 1585.4933 |  | 11.9468 | 13.5754 | 15.4379 | 17.5689 | 20.0081 | 22.801 | 26.0004 | 29.6666 | 33.8692 | 38.6884 | 44.2162 | 50.5588 | 57.8386 | 66.1961 | 75.7935 | 86.8175 | 99.4832 | 114.0384 | 130.7687 | 150.0031 | 172.1209 | 197.559 | 226.8212 | 260.4883 | 299.2297 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 9.8792 | 11.5077 | 13.3702 | 15.5012 | 17.9404 | 20.7333 | 23.9327 | 27.5989 | 31.8015 | 36.6207 | 42.1485 | 48.4912 | 55.7709 | 64.1284 | 73.7258 | 84.7498 | 97.4155 | 111.5635 | 127.4881 | 145.6165 | 166.2092 | 189.5358 | 215.8639 | 245.4401 | 278.4607 | 291.9622 | 280.6877 | 264.8071 | 242.396 | 210.7151 |  | 6.672 | 7.5815 | 8.6216 | 9.8117 | 11.1739 | 12.7337 | 14.5204 | 16.5679 | 18.915 | 21.6063 | 24.6934 | 28.2356 | 32.3011 | 36.9685 | 42.3284 | 48.485 | 55.5584 | 63.687 | 73.0304 | 83.7723 | 96.1244 | 110.3308 | 126.6729 | 145.475 | 167.1109 | 179.1309 | 179.1309 | 179.1309 | 179.1309 | 179.1309 |  | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00053475 | 0.00064006 | 0.00084844 | 0.0011345 | 0.0015289 | 0.002075 | 0.0028338 | 0.0038918 | 0.0053713 | 0.0074459 | 0.010362 | 0.014469 | 0.020265 | 0.028458 |  | 6.6714 | 7.5809 | 8.6211 | 9.8112 | 11.1734 | 12.7332 | 14.5199 | 16.5674 | 18.9144 | 21.6058 | 24.6929 | 28.2351 | 32.3006 | 36.968 | 42.3279 | 48.4844 | 55.5578 | 63.6864 | 73.0296 | 83.7711 | 96.1228 | 110.3287 | 126.6701 | 145.4711 | 167.1055 | 179.1234 | 179.1205 | 179.1164 | 179.1106 | 179.1024 |  | 696.6595 | 797.9803 | 913.8551 | 1046.4319 | 1198.1809 | 1371.9438 | 1570.9895 | 1799.0796 | 2060.5428 | 2360.3614 | 2704.2711 | 3098.8749 | 3551.7766 | 4071.7321 | 4668.8264 | 5354.676 | 6142.6631 | 7039.0273 | 8061.7295 | 9233.4549 | 10575.1191 | 12110.1406 | 13864.5353 | 15866.9009 | 18148.2227 | 19306.4638 | 19052.3441 | 18694.4072 | 18189.277 | 17475.2103
| TRUE | 38 | 22003639 | AC | Blank | 66 | TRANS NO.3 | DIFFERENTIAL | X | ABB | RADSB_3057 | RADSB 3057 | RADSB | Electronic |  | 0.066046 | 2190 |  | 6.6 | 0.014726 | 0.0025679 | 0.012158 | 173.0518 | 1242.8812 | 1415.933 | 56.3804 | 5.9176 | 28.4854 |  | 10.2588 | 0.047123 | 0.0082173 | 0.038906 | 553.7611 | 3977.1855 | 4530.9466 | 180.4156 | 18.9361 | 91.1523 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 59.6902 | 0.2263 | 59.9165 | 14.6724 | 2.0677 | 0.0051866 |  | 1506.7163 | 4821.4506 | 76.6618 | 4744.7888 |  | 0.044106 |  | 6.8976 | 7.2087 | 7.5337 | 7.8734 | 8.2285 | 8.5995 | 8.9873 | 9.3926 | 9.8161 | 10.2588 | 10.7214 | 11.2048 | 11.7101 | 12.2381 | 12.79 | 13.3667 | 13.9695 | 14.5994 | 15.2578 | 15.9458 | 16.6648 | 17.4163 | 18.2017 | 19.0225 | 19.8802 | 20.7767 | 21.7136 | 22.6927 | 23.716 | 24.7855 |  | 0.016485 | 0.018471 | 0.020712 | 0.023244 | 0.026105 | 0.029339 | 0.032997 | 0.037136 | 0.04182 | 0.047123 | 0.053129 | 0.059935 | 0.067647 | 0.076391 | 0.086306 | 0.097553 | 0.11031 | 0.1248 | 0.14124 | 0.15991 | 0.18111 | 0.20519 | 0.23255 | 0.26365 | 0.299 | 0.33918 | 0.38487 | 0.43682 | 0.49592 | 0.56315 |  | 0.0028747 | 0.0032209 | 0.0036118 | 0.0040533 | 0.0045522 | 0.0051162 | 0.0057541 | 0.0064757 | 0.0072925 | 0.0082173 | 0.0092647 | 0.010451 | 0.011796 | 0.013321 | 0.01505 | 0.017011 | 0.019237 | 0.021762 | 0.024629 | 0.027884 | 0.031581 | 0.035781 | 0.040553 | 0.045975 | 0.052139 | 0.059146 | 0.067113 | 0.076174 | 0.086479 | 0.098203 | 1686.7193 | 1889.8506 | 2119.1896 | 2378.235 | 2670.9623 | 3001.8894 | 3376.1519 | 3799.5884 | 4278.8379 | 4821.4506 | 5436.0145 | 6132.2992 | 6921.4205 | 7816.0269 | 8830.5136 | 9981.2653 | 11286.9336 | 12768.7528 | 14450.9004 | 16360.9082 | 18530.1303 | 20994.2775 | 23794.0269 | 26975.7159 | 30592.1348 | 34703.4306 | 39378.137 | 44694.3503 | 50741.0699 | 57619.7272 |  | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 46.7986 | 56.015 | 74.2512 | 99.2839 | 133.8009 | 181.5901 | 247.9993 | 340.5904 | 470.0714 | 651.6252 | 906.804 | 1266.2326 | 1773.468 | 2490.5107 |  | 193.7258 | 217.0562 | 243.3966 | 273.1489 | 306.7697 | 344.7779 | 387.7633 | 436.3965 | 491.44 | 553.7611 | 624.3459 | 704.3168 | 794.9502 | 897.699 | 1014.2164 | 1146.3845 | 1296.3452 | 1466.5375 | 1659.7382 | 1879.1095 | 2128.2525 | 2411.2688 | 2732.8301 | 3098.2586 | 3513.6174 | 3985.8146 | 4522.7216 | 5133.3079 | 5827.7955 | 6617.8342 |  | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 29.8451 | 35.7227 | 47.3526 | 63.3168 | 85.3295 | 115.8064 | 158.1579 | 217.2064 | 299.781 | 415.5643 | 578.3007 | 807.521 | 1131.0029 | 1588.2861 |  | 163.8807 | 187.2111 | 213.5515 | 243.3038 | 276.9246 | 314.9328 | 357.9182 | 406.5514 | 461.5949 | 523.916 | 594.5008 | 674.4717 | 765.1051 | 867.8539 | 984.3713 | 1116.5394 | 1266.5001 | 1430.8148 | 1612.3856 | 1815.7927 | 2042.923 | 2295.4624 | 2574.6722 | 2881.0522 | 3213.8364 | 3570.2503 | 3944.4208 | 4325.7869 | 4696.7927 | 5029.5481 |  | 1391.3646 | 1558.9263 | 1748.1067 | 1961.7917 | 2203.2607 | 2476.2404 | 2784.9673 | 3134.2576 | 3529.5876 | 3977.1855 | 4484.1356 | 5058.4967 | 5709.438 | 6447.3934 | 7284.2374 | 8233.4856 | 9310.5235 | 10532.8671 | 11920.4606 | 13496.0145 | 15285.3927 | 17318.0529 | 19627.5493 | 22252.1053 | 25235.2675 | 28626.6506 | 32482.7877 | 36868.1 | 41856.0025 | 47530.1654 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 1391.1589 | 1558.7206 | 1747.901 | 1961.586 | 2203.055 | 2476.0347 | 2784.7616 | 3134.0518 | 3529.3818 | 3976.9798 | 4483.9298 | 5058.2909 | 5709.2323 | 6447.1877 | 7284.0317 | 8233.2798 | 9310.3177 | 10532.6209 | 11920.1342 | 13495.578 | 15284.8045 | 17317.2546 | 19626.4591 | 22250.6081 | 25233.201 | 28623.786 | 32478.8013 | 36862.5336 | 41848.2062 | 47519.217 |  | 1555.0396 | 1745.9317 | 1961.4525 | 2204.8898 | 2479.9795 | 2790.9675 | 3142.6798 | 3540.6032 | 3990.9768 | 4500.8958 | 5078.4307 | 5732.7626 | 6474.3373 | 7315.0416 | 8268.403 | 9349.8192 | 10576.8178 | 11963.4357 | 13532.5198 | 15311.3707 | 17327.7275 | 19612.717 | 22201.1313 | 25131.6602 | 28447.0374 | 32194.0363 | 36423.2222 | 41188.3205 | 46544.9989 | 52548.7651 |  | 63.116 | 70.717 | 79.2987 | 88.992 | 99.9457 | 112.3288 | 126.3335 | 142.1782 | 160.1114 | 180.4156 | 203.4122 | 229.4667 | 258.9952 | 292.4708 | 330.4322 | 373.4926 | 422.3499 | 477.7986 | 540.7435 | 612.2148 | 693.3857 | 785.5925 | 890.3574 | 1009.4141 | 1144.7382 | 1298.5803 | 1473.5049 | 1672.4342 | 1898.6986 | 2156.0936 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 48.4435 | 56.0446 | 64.6263 | 74.3196 | 85.2733 | 97.6564 | 111.661 | 127.5057 | 145.439 | 165.7432 | 188.7398 | 214.7943 | 244.3227 | 277.7983 | 315.7598 | 358.8202 | 407.6774 | 460.2366 | 517.464 | 581.087 | 651.436 | 728.6598 | 812.6038 | 902.6312 | 997.36 | 1094.2807 | 1189.2008 | 1275.4409 | 1342.6753 | 1375.2607 |  | 6.6245 | 7.4223 | 8.323 | 9.3404 | 10.4901 | 11.7898 | 13.2597 | 14.9227 | 16.805 | 18.9361 | 21.3497 | 24.0844 | 27.1836 | 30.6971 | 34.6815 | 39.201 | 44.329 | 50.1488 | 56.7554 | 64.2568 | 72.7764 | 82.4542 | 93.4501 | 105.9461 | 120.1495 | 136.2964 | 154.6561 | 175.5354 | 199.2836 | 226.2993 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 4.5568 | 5.3546 | 6.2553 | 7.2727 | 8.4224 | 9.7221 | 11.192 | 12.855 | 14.7373 | 16.8684 | 19.282 | 22.0167 | 25.1159 | 28.6295 | 32.6138 | 37.1333 | 42.2613 | 47.6739 | 53.4747 | 59.8702 | 66.8647 | 74.4311 | 82.4928 | 90.8978 | 99.3803 | 107.5057 | 114.5909 | 119.5896 | 120.9267 | 116.2614 |  | 31.8884 | 35.7287 | 40.0645 | 44.9619 | 50.4961 | 56.7525 | 63.8281 | 71.8334 | 80.8939 | 91.1523 | 102.771 | 115.9347 | 130.8535 | 147.7666 | 166.946 | 188.7017 | 213.3861 | 241.4008 | 273.2027 | 309.3126 | 350.323 | 396.9091 | 449.84 | 509.9917 | 578.3622 | 656.0887 | 744.4668 | 844.9729 | 959.2897 | 1089.3347 |  | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.0051866 | 0.006208 | 0.0082291 | 0.011003 | 0.014829 | 0.020125 | 0.027485 | 0.037747 | 0.052097 | 0.072218 | 0.1005 | 0.14033 | 0.19655 | 0.27602 |  | 31.8832 | 35.7235 | 40.0593 | 44.9567 | 50.4909 | 56.7473 | 63.8229 | 71.8283 | 80.8888 | 91.1472 | 102.7659 | 115.9295 | 130.8483 | 147.7614 | 166.9408 | 188.6965 | 213.3809 | 241.3945 | 273.1945 | 309.3016 | 350.3081 | 396.889 | 449.8125 | 509.954 | 578.3101 | 656.0165 | 744.3663 | 844.8326 | 959.0931 | 1089.0587 |  | 1639.9232 | 1843.0544 | 2072.3934 | 2331.4389 | 2624.1661 | 2955.0932 | 3329.3557 | 3752.7923 | 4232.0417 | 4774.6545 | 5389.2184 | 6085.5031 | 6874.6243 | 7769.2307 | 8783.7174 | 9934.4692 | 11240.1375 | 12712.7407 | 14376.6531 | 16261.6295 | 18396.3363 | 20812.6968 | 23546.0405 | 26635.1432 | 30122.0879 | 34051.8393 | 38471.3801 | 43428.1835 | 48967.694 | 55129.3459
| FALSE | 300 | 22016050 | BAN | Blank | 22 | BUS NO.1 | LOW IMP BUS PROT | X | GE | GE_B90 | GE B90 | GE RELAYS | Digital |  | 0.033587 | 1 |  | 0.96924 | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.3143 |  | 5.0708 | 0.0089964 | 4.1392e-07 | 0.008996 | 24.7403 | 0.028975 | 24.7692 | 25.5397 | 3.5995 | 0.54714 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.3143 |  | 31.2817 | 54.4556 | 31.2817 | 23.1739 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.8009e-07 | 4.1392e-07 | 6.2161e-07 | 9.4651e-07 | 1.4584e-06 | 2.2699e-06 | 3.5631e-06 | 5.6335e-06 | 8.9608e-06 | 1.4326e-05 | 2.3001e-05 | 3.7064e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 36.8478 | 54.4556 | 81.7783 | 124.5223 | 191.8675 | 298.6264 | 468.7632 | 741.1354 | 1178.8726 | 1884.7066 | 3026.0528 | 4876.0666 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 |  | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 37.4422 | 49.6318 | 66.3645 | 89.4368 | 121.3806 | 165.7707 | 227.6615 | 314.2107 | 435.5671 | 606.1367 | 846.3903 | 1185.4426 | 1664.7368 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 16.7407 | 24.7403 | 37.1535 | 56.573 | 87.1693 | 135.672 | 212.9685 | 336.7127 | 535.5855 | 856.2601 | 1374.7966 | 2215.295 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5288 | 10.5284 | 22.9416 | 42.3611 | 72.9574 | 121.4601 | 198.7566 | 322.5008 | 521.3736 | 839.2493 | 1352.2478 | 2185.1443 | 2549.2192 | 2534.7064 | 2514.5392 | 2486.4209 | 2447.0999 | 2391.9652 | 2314.472 | 2205.32 | 2051.2817 | 1833.5287 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019606 | 0.028975 | 0.043513 | 0.066256 | 0.10209 | 0.15889 | 0.24942 | 0.39434 | 0.62725 | 1.0028 | 1.6101 | 2.5945 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019922 | 0.026408 | 0.035311 | 0.047588 | 0.064584 | 0.088203 | 0.12113 | 0.16719 | 0.23176 | 0.32251 | 0.45035 | 0.63075 | 0.88577 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029616 | 0.01233 | 0.026868 | 0.049611 | 0.085445 | 0.14225 | 0.23278 | 0.3777 | 0.61061 | 0.98289 | 1.5837 | 2.5591 | 2.9855 | 2.9685 | 2.9449 | 2.912 | 2.8659 | 2.8014 | 2.7106 | 2.5828 | 2.4024 | 2.1473 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5318 | 10.5407 | 22.9685 | 42.4107 | 73.0428 | 121.6023 | 198.9894 | 322.8785 | 521.9842 | 840.2322 | 1353.8315 | 2187.7034 | 2552.2047 | 2537.675 | 2517.4841 | 2489.3329 | 2449.9658 | 2394.7666 | 2317.1826 | 2207.9028 | 2053.6841 | 1835.6761 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.2816 | 25.5397 | 38.3541 | 58.4011 | 89.9861 | 140.0561 | 219.8504 | 347.5933 | 552.8925 | 883.9294 | 1419.2221 | 2286.8806 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6105 | 10.8686 | 23.683 | 43.73 | 75.3149 | 125.385 | 205.1793 | 332.9222 | 538.2214 | 866.369 | 1395.9447 | 2255.7556 | 2631.5953 | 2616.6136 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2308 | 12.6823 | 19.739 | 30.9849 | 48.9885 | 77.9225 | 124.5776 | 200.0197 | 322.3042 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1631 | 10.6146 | 17.6713 | 28.9172 | 46.9208 | 75.8549 | 122.1027 | 196.7391 | 317.9175 | 370.8869 | 368.7755 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.37023 | 0.54714 | 0.82167 | 1.2511 | 1.9278 | 3.0005 | 4.7099 | 7.4466 | 11.8448 | 18.9366 | 30.4043 | 48.9924 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 |  | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3762 | 0.49868 | 0.6668 | 0.89862 | 1.2196 | 1.6656 | 2.2874 | 3.157 | 4.3764 | 6.0902 | 8.5041 | 11.9108 | 16.7265 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055926 | 0.23284 | 0.50737 | 0.93684 | 1.6135 | 2.6862 | 4.3956 | 7.1323 | 11.5305 | 18.5604 | 29.9057 | 48.3256 | 56.3773 | 56.0564 | 55.6104 | 54.9885 | 54.1189 | 52.8996 | 51.1858 | 48.7718 | 45.3652 | 40.5494 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5661 | 23.1739 | 50.4966 | 93.2406 | 160.5858 | 267.3448 | 437.4815 | 709.8538 | 1147.5909 | 1847.2644 | 2976.421 | 4809.7021 | 5611.0642 | 5579.1204 | 5534.7304 | 5472.8395 | 5386.2903 | 5264.934 | 5094.3643 | 4854.1107 | 4515.0584 | 4035.7642
| FALSE | 301 | 22016147 | BAN | Blank | 22 | BUS NO.1 | POWER QUALITY | I | Schneider | ION_7650 | ION 7650 | ION 7000s | Digital |  | 0.033587 | 1 |  | 0.96924 | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.3143 |  | 5.0708 | 0.0089964 | 4.1392e-07 | 0.008996 | 24.7403 | 0.028975 | 24.7692 | 25.5397 | 3.5995 | 0.54714 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.3143 |  | 31.2817 | 54.4556 | 31.2817 | 23.1739 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.8009e-07 | 4.1392e-07 | 6.2161e-07 | 9.4651e-07 | 1.4584e-06 | 2.2699e-06 | 3.5631e-06 | 5.6335e-06 | 8.9608e-06 | 1.4326e-05 | 2.3001e-05 | 3.7064e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 36.8478 | 54.4556 | 81.7783 | 124.5223 | 191.8675 | 298.6264 | 468.7632 | 741.1354 | 1178.8726 | 1884.7066 | 3026.0528 | 4876.0666 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 |  | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 37.4422 | 49.6318 | 66.3645 | 89.4368 | 121.3806 | 165.7707 | 227.6615 | 314.2107 | 435.5671 | 606.1367 | 846.3903 | 1185.4426 | 1664.7368 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 16.7407 | 24.7403 | 37.1535 | 56.573 | 87.1693 | 135.672 | 212.9685 | 336.7127 | 535.5855 | 856.2601 | 1374.7966 | 2215.295 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5288 | 10.5284 | 22.9416 | 42.3611 | 72.9574 | 121.4601 | 198.7566 | 322.5008 | 521.3736 | 839.2493 | 1352.2478 | 2185.1443 | 2549.2192 | 2534.7064 | 2514.5392 | 2486.4209 | 2447.0999 | 2391.9652 | 2314.472 | 2205.32 | 2051.2817 | 1833.5287 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019606 | 0.028975 | 0.043513 | 0.066256 | 0.10209 | 0.15889 | 0.24942 | 0.39434 | 0.62725 | 1.0028 | 1.6101 | 2.5945 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019922 | 0.026408 | 0.035311 | 0.047588 | 0.064584 | 0.088203 | 0.12113 | 0.16719 | 0.23176 | 0.32251 | 0.45035 | 0.63075 | 0.88577 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029616 | 0.01233 | 0.026868 | 0.049611 | 0.085445 | 0.14225 | 0.23278 | 0.3777 | 0.61061 | 0.98289 | 1.5837 | 2.5591 | 2.9855 | 2.9685 | 2.9449 | 2.912 | 2.8659 | 2.8014 | 2.7106 | 2.5828 | 2.4024 | 2.1473 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5318 | 10.5407 | 22.9685 | 42.4107 | 73.0428 | 121.6023 | 198.9894 | 322.8785 | 521.9842 | 840.2322 | 1353.8315 | 2187.7034 | 2552.2047 | 2537.675 | 2517.4841 | 2489.3329 | 2449.9658 | 2394.7666 | 2317.1826 | 2207.9028 | 2053.6841 | 1835.6761 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.2816 | 25.5397 | 38.3541 | 58.4011 | 89.9861 | 140.0561 | 219.8504 | 347.5933 | 552.8925 | 883.9294 | 1419.2221 | 2286.8806 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6105 | 10.8686 | 23.683 | 43.73 | 75.3149 | 125.385 | 205.1793 | 332.9222 | 538.2214 | 866.369 | 1395.9447 | 2255.7556 | 2631.5953 | 2616.6136 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2308 | 12.6823 | 19.739 | 30.9849 | 48.9885 | 77.9225 | 124.5776 | 200.0197 | 322.3042 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1631 | 10.6146 | 17.6713 | 28.9172 | 46.9208 | 75.8549 | 122.1027 | 196.7391 | 317.9175 | 370.8869 | 368.7755 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.37023 | 0.54714 | 0.82167 | 1.2511 | 1.9278 | 3.0005 | 4.7099 | 7.4466 | 11.8448 | 18.9366 | 30.4043 | 48.9924 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 |  | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3762 | 0.49868 | 0.6668 | 0.89862 | 1.2196 | 1.6656 | 2.2874 | 3.157 | 4.3764 | 6.0902 | 8.5041 | 11.9108 | 16.7265 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055926 | 0.23284 | 0.50737 | 0.93684 | 1.6135 | 2.6862 | 4.3956 | 7.1323 | 11.5305 | 18.5604 | 29.9057 | 48.3256 | 56.3773 | 56.0564 | 55.6104 | 54.9885 | 54.1189 | 52.8996 | 51.1858 | 48.7718 | 45.3652 | 40.5494 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5661 | 23.1739 | 50.4966 | 93.2406 | 160.5858 | 267.3448 | 437.4815 | 709.8538 | 1147.5909 | 1847.2644 | 2976.421 | 4809.7021 | 5611.0642 | 5579.1204 | 5534.7304 | 5472.8395 | 5386.2903 | 5264.934 | 5094.3643 | 4854.1107 | 4515.0584 | 4035.7642
| FALSE | 302 | 22016132 | BAN | Blank | 22 | BUS NO.1 | SINGLE ZONE BUS DIST | Y | Schweitzer | SEL_311C_1 | SEL 311C | SEL 300s | Digital |  | 0.0034106 | 1 |  | 0.96924 | 0.0051679 | 2.4145e-08 | 0.0051679 | 14.2118 | 0.0016901 | 14.2135 | 14.6699 | 2.0677 | 0.031916 |  | 5.0708 | 0.0089964 | 4.2032e-08 | 0.0089964 | 24.7402 | 0.0029422 | 24.7431 | 25.5376 | 3.5995 | 0.055559 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 14.2118 | 0.0016901 | 14.2135 | 14.6699 | 2.0677 | 0.031916 |  | 30.9831 | 53.9358 | 30.9831 | 22.9527 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.8441e-08 | 4.2032e-08 | 6.3121e-08 | 9.6113e-08 | 1.4809e-07 | 2.305e-07 | 3.6182e-07 | 5.7205e-07 | 9.0992e-07 | 1.4547e-06 | 2.3357e-06 | 3.7636e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 36.496 | 53.9358 | 80.9976 | 123.3336 | 190.0359 | 295.7757 | 464.2884 | 734.0605 | 1167.619 | 1866.7151 | 2997.1661 | 4829.5196 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 |  | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 37.0848 | 49.1581 | 65.731 | 88.583 | 120.2219 | 164.1882 | 225.4882 | 311.2112 | 431.4091 | 600.3505 | 838.3106 | 1174.1264 | 1648.8452 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 16.7406 | 24.7402 | 37.1534 | 56.5728 | 87.1689 | 135.6714 | 212.9676 | 336.7113 | 535.5833 | 856.2565 | 1374.7909 | 2215.2858 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5288 | 10.5283 | 22.9415 | 42.3609 | 72.9571 | 121.4596 | 198.7558 | 322.4995 | 521.3714 | 839.2458 | 1352.2423 | 2185.1352 | 2549.2086 | 2534.696 | 2514.5288 | 2486.4106 | 2447.0898 | 2391.9554 | 2314.4625 | 2205.3109 | 2051.2732 | 1833.5212 |  | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0019909 | 0.0029422 | 0.0044185 | 0.0067279 | 0.010367 | 0.016135 | 0.025327 | 0.040043 | 0.063694 | 0.10183 | 0.1635 | 0.26345 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 |  | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.002023 | 0.0026816 | 0.0035857 | 0.0048322 | 0.0065582 | 0.0089565 | 0.0123 | 0.016977 | 0.023534 | 0.032749 | 0.04573 | 0.064049 | 0.089945 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00030074 | 0.0012521 | 0.0027283 | 0.0050378 | 0.0086764 | 0.014445 | 0.023637 | 0.038353 | 0.062004 | 0.099807 | 0.16082 | 0.25987 | 0.30316 | 0.30144 | 0.29904 | 0.2957 | 0.29102 | 0.28446 | 0.27525 | 0.26227 | 0.24395 | 0.21805 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5291 | 10.5296 | 22.9443 | 42.366 | 72.9658 | 121.474 | 198.7795 | 322.5378 | 521.4334 | 839.3457 | 1352.4031 | 2185.3951 | 2549.5118 | 2534.9974 | 2514.8278 | 2486.7063 | 2447.3808 | 2392.2398 | 2314.7377 | 2205.5732 | 2051.5172 | 1833.7392 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.2802 | 25.5376 | 38.3509 | 58.3963 | 89.9786 | 140.0445 | 219.8323 | 347.5646 | 552.8468 | 883.8564 | 1419.1048 | 2286.6915 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6103 | 10.8677 | 23.681 | 43.7263 | 75.3087 | 125.3746 | 205.1623 | 332.8947 | 538.1769 | 866.2974 | 1395.8293 | 2255.5691 | 2631.3777 | 2616.3973 | 2595.58 | 2566.5555 | 2525.9672 | 2469.0557 | 2389.0649 | 2276.395 | 2117.3923 | 1892.6214 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2308 | 12.6823 | 19.739 | 30.9848 | 48.9884 | 77.9225 | 124.5775 | 200.0195 | 322.3038 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36791 | 1.5318 | 3.3378 | 6.1631 | 10.6146 | 17.6713 | 28.9172 | 46.9207 | 75.8548 | 122.1026 | 196.7389 | 317.9172 | 370.8866 | 368.7751 | 365.8409 | 361.75 | 356.0292 | 348.0076 | 336.7331 | 320.8526 | 298.4415 | 266.7606 |  | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.037595 | 0.055559 | 0.083436 | 0.12705 | 0.19576 | 0.30468 | 0.47826 | 0.75616 | 1.2028 | 1.9229 | 3.0874 | 4.9749 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 |  | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.038201 | 0.050638 | 0.06771 | 0.09125 | 0.12384 | 0.16913 | 0.23228 | 0.32058 | 0.4444 | 0.61842 | 0.86355 | 1.2095 | 1.6985 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0056789 | 0.023644 | 0.05152 | 0.095131 | 0.16384 | 0.27276 | 0.44635 | 0.72424 | 1.1709 | 1.8847 | 3.0368 | 4.9072 | 5.7248 | 5.6922 | 5.6469 | 5.5838 | 5.4955 | 5.3717 | 5.1976 | 4.9525 | 4.6066 | 4.1176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.513 | 22.9527 | 50.0146 | 92.3506 | 159.0529 | 264.7927 | 433.3053 | 703.0775 | 1136.636 | 1829.6304 | 2948.008 | 4763.7886 | 5557.5009 | 5525.862 | 5481.8957 | 5420.5957 | 5334.8727 | 5214.6748 | 5045.7334 | 4807.7733 | 4471.9575 | 3997.2387
| FALSE | 303 | 22016051 | BAN | Blank | 22 | BUS NO.2 | LOW IMP BUS PROT | X | GE | GE_B90 | GE B90 | GE RELAYS | Digital |  | 0.033587 | 1 |  | 0.96924 | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.3143 |  | 5.0708 | 0.0089964 | 4.1392e-07 | 0.008996 | 24.7403 | 0.028975 | 24.7692 | 25.5397 | 3.5995 | 0.54714 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.3143 |  | 31.2817 | 54.4556 | 31.2817 | 23.1739 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.8009e-07 | 4.1392e-07 | 6.2161e-07 | 9.4651e-07 | 1.4584e-06 | 2.2699e-06 | 3.5631e-06 | 5.6335e-06 | 8.9608e-06 | 1.4326e-05 | 2.3001e-05 | 3.7064e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 36.8478 | 54.4556 | 81.7783 | 124.5223 | 191.8675 | 298.6264 | 468.7632 | 741.1354 | 1178.8726 | 1884.7066 | 3026.0528 | 4876.0666 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 |  | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 37.4422 | 49.6318 | 66.3645 | 89.4368 | 121.3806 | 165.7707 | 227.6615 | 314.2107 | 435.5671 | 606.1367 | 846.3903 | 1185.4426 | 1664.7368 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 16.7407 | 24.7403 | 37.1535 | 56.573 | 87.1693 | 135.672 | 212.9685 | 336.7127 | 535.5855 | 856.2601 | 1374.7966 | 2215.295 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5288 | 10.5284 | 22.9416 | 42.3611 | 72.9574 | 121.4601 | 198.7566 | 322.5008 | 521.3736 | 839.2493 | 1352.2478 | 2185.1443 | 2549.2192 | 2534.7064 | 2514.5392 | 2486.4209 | 2447.0999 | 2391.9652 | 2314.472 | 2205.32 | 2051.2817 | 1833.5287 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019606 | 0.028975 | 0.043513 | 0.066256 | 0.10209 | 0.15889 | 0.24942 | 0.39434 | 0.62725 | 1.0028 | 1.6101 | 2.5945 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019922 | 0.026408 | 0.035311 | 0.047588 | 0.064584 | 0.088203 | 0.12113 | 0.16719 | 0.23176 | 0.32251 | 0.45035 | 0.63075 | 0.88577 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029616 | 0.01233 | 0.026868 | 0.049611 | 0.085445 | 0.14225 | 0.23278 | 0.3777 | 0.61061 | 0.98289 | 1.5837 | 2.5591 | 2.9855 | 2.9685 | 2.9449 | 2.912 | 2.8659 | 2.8014 | 2.7106 | 2.5828 | 2.4024 | 2.1473 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5318 | 10.5407 | 22.9685 | 42.4107 | 73.0428 | 121.6023 | 198.9894 | 322.8785 | 521.9842 | 840.2322 | 1353.8315 | 2187.7034 | 2552.2047 | 2537.675 | 2517.4841 | 2489.3329 | 2449.9658 | 2394.7666 | 2317.1826 | 2207.9028 | 2053.6841 | 1835.6761 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.2816 | 25.5397 | 38.3541 | 58.4011 | 89.9861 | 140.0561 | 219.8504 | 347.5933 | 552.8925 | 883.9294 | 1419.2221 | 2286.8806 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6105 | 10.8686 | 23.683 | 43.73 | 75.3149 | 125.385 | 205.1793 | 332.9222 | 538.2214 | 866.369 | 1395.9447 | 2255.7556 | 2631.5953 | 2616.6136 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2308 | 12.6823 | 19.739 | 30.9849 | 48.9885 | 77.9225 | 124.5776 | 200.0197 | 322.3042 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1631 | 10.6146 | 17.6713 | 28.9172 | 46.9208 | 75.8549 | 122.1027 | 196.7391 | 317.9175 | 370.8869 | 368.7755 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.37023 | 0.54714 | 0.82167 | 1.2511 | 1.9278 | 3.0005 | 4.7099 | 7.4466 | 11.8448 | 18.9366 | 30.4043 | 48.9924 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 |  | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3762 | 0.49868 | 0.6668 | 0.89862 | 1.2196 | 1.6656 | 2.2874 | 3.157 | 4.3764 | 6.0902 | 8.5041 | 11.9108 | 16.7265 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055926 | 0.23284 | 0.50737 | 0.93684 | 1.6135 | 2.6862 | 4.3956 | 7.1323 | 11.5305 | 18.5604 | 29.9057 | 48.3256 | 56.3773 | 56.0564 | 55.6104 | 54.9885 | 54.1189 | 52.8996 | 51.1858 | 48.7718 | 45.3652 | 40.5494 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5661 | 23.1739 | 50.4966 | 93.2406 | 160.5858 | 267.3448 | 437.4815 | 709.8538 | 1147.5909 | 1847.2644 | 2976.421 | 4809.7021 | 5611.0642 | 5579.1204 | 5534.7304 | 5472.8395 | 5386.2903 | 5264.934 | 5094.3643 | 4854.1107 | 4515.0584 | 4035.7642
| FALSE | 304 | 22015679 | BAN | Blank | 22 | BUS NO.2 | POWER QUALITY | I | Schneider | ION_7400 | ION 7400 | ION 7000s | Digital |  | 0.033587 | 1 |  | 0.96924 | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.3143 |  | 5.0708 | 0.0089964 | 4.1392e-07 | 0.008996 | 24.7403 | 0.028975 | 24.7692 | 25.5397 | 3.5995 | 0.54714 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.3143 |  | 31.2817 | 54.4556 | 31.2817 | 23.1739 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.8009e-07 | 4.1392e-07 | 6.2161e-07 | 9.4651e-07 | 1.4584e-06 | 2.2699e-06 | 3.5631e-06 | 5.6335e-06 | 8.9608e-06 | 1.4326e-05 | 2.3001e-05 | 3.7064e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 36.8478 | 54.4556 | 81.7783 | 124.5223 | 191.8675 | 298.6264 | 468.7632 | 741.1354 | 1178.8726 | 1884.7066 | 3026.0528 | 4876.0666 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 |  | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 37.4422 | 49.6318 | 66.3645 | 89.4368 | 121.3806 | 165.7707 | 227.6615 | 314.2107 | 435.5671 | 606.1367 | 846.3903 | 1185.4426 | 1664.7368 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 16.7407 | 24.7403 | 37.1535 | 56.573 | 87.1693 | 135.672 | 212.9685 | 336.7127 | 535.5855 | 856.2601 | 1374.7966 | 2215.295 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5288 | 10.5284 | 22.9416 | 42.3611 | 72.9574 | 121.4601 | 198.7566 | 322.5008 | 521.3736 | 839.2493 | 1352.2478 | 2185.1443 | 2549.2192 | 2534.7064 | 2514.5392 | 2486.4209 | 2447.0999 | 2391.9652 | 2314.472 | 2205.32 | 2051.2817 | 1833.5287 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019606 | 0.028975 | 0.043513 | 0.066256 | 0.10209 | 0.15889 | 0.24942 | 0.39434 | 0.62725 | 1.0028 | 1.6101 | 2.5945 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019922 | 0.026408 | 0.035311 | 0.047588 | 0.064584 | 0.088203 | 0.12113 | 0.16719 | 0.23176 | 0.32251 | 0.45035 | 0.63075 | 0.88577 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029616 | 0.01233 | 0.026868 | 0.049611 | 0.085445 | 0.14225 | 0.23278 | 0.3777 | 0.61061 | 0.98289 | 1.5837 | 2.5591 | 2.9855 | 2.9685 | 2.9449 | 2.912 | 2.8659 | 2.8014 | 2.7106 | 2.5828 | 2.4024 | 2.1473 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5318 | 10.5407 | 22.9685 | 42.4107 | 73.0428 | 121.6023 | 198.9894 | 322.8785 | 521.9842 | 840.2322 | 1353.8315 | 2187.7034 | 2552.2047 | 2537.675 | 2517.4841 | 2489.3329 | 2449.9658 | 2394.7666 | 2317.1826 | 2207.9028 | 2053.6841 | 1835.6761 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.2816 | 25.5397 | 38.3541 | 58.4011 | 89.9861 | 140.0561 | 219.8504 | 347.5933 | 552.8925 | 883.9294 | 1419.2221 | 2286.8806 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6105 | 10.8686 | 23.683 | 43.73 | 75.3149 | 125.385 | 205.1793 | 332.9222 | 538.2214 | 866.369 | 1395.9447 | 2255.7556 | 2631.5953 | 2616.6136 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2308 | 12.6823 | 19.739 | 30.9849 | 48.9885 | 77.9225 | 124.5776 | 200.0197 | 322.3042 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1631 | 10.6146 | 17.6713 | 28.9172 | 46.9208 | 75.8549 | 122.1027 | 196.7391 | 317.9175 | 370.8869 | 368.7755 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.37023 | 0.54714 | 0.82167 | 1.2511 | 1.9278 | 3.0005 | 4.7099 | 7.4466 | 11.8448 | 18.9366 | 30.4043 | 48.9924 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 |  | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3762 | 0.49868 | 0.6668 | 0.89862 | 1.2196 | 1.6656 | 2.2874 | 3.157 | 4.3764 | 6.0902 | 8.5041 | 11.9108 | 16.7265 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055926 | 0.23284 | 0.50737 | 0.93684 | 1.6135 | 2.6862 | 4.3956 | 7.1323 | 11.5305 | 18.5604 | 29.9057 | 48.3256 | 56.3773 | 56.0564 | 55.6104 | 54.9885 | 54.1189 | 52.8996 | 51.1858 | 48.7718 | 45.3652 | 40.5494 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5661 | 23.1739 | 50.4966 | 93.2406 | 160.5858 | 267.3448 | 437.4815 | 709.8538 | 1147.5909 | 1847.2644 | 2976.421 | 4809.7021 | 5611.0642 | 5579.1204 | 5534.7304 | 5472.8395 | 5386.2903 | 5264.934 | 5094.3643 | 4854.1107 | 4515.0584 | 4035.7642
| FALSE | 305 | 22016133 | BAN | Blank | 22 | BUS NO.2 | SINGLE ZONE BUS DIST | Y | Schweitzer | SEL_311C_1 | SEL 311C | SEL 300s | Digital |  | 0.0034106 | 1 |  | 0.96924 | 0.0051679 | 2.4145e-08 | 0.0051679 | 14.2118 | 0.0016901 | 14.2135 | 14.6699 | 2.0677 | 0.031916 |  | 5.0708 | 0.0089964 | 4.2032e-08 | 0.0089964 | 24.7402 | 0.0029422 | 24.7431 | 25.5376 | 3.5995 | 0.055559 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 14.2118 | 0.0016901 | 14.2135 | 14.6699 | 2.0677 | 0.031916 |  | 30.9831 | 53.9358 | 30.9831 | 22.9527 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.8441e-08 | 4.2032e-08 | 6.3121e-08 | 9.6113e-08 | 1.4809e-07 | 2.305e-07 | 3.6182e-07 | 5.7205e-07 | 9.0992e-07 | 1.4547e-06 | 2.3357e-06 | 3.7636e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 36.496 | 53.9358 | 80.9976 | 123.3336 | 190.0359 | 295.7757 | 464.2884 | 734.0605 | 1167.619 | 1866.7151 | 2997.1661 | 4829.5196 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 |  | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 37.0848 | 49.1581 | 65.731 | 88.583 | 120.2219 | 164.1882 | 225.4882 | 311.2112 | 431.4091 | 600.3505 | 838.3106 | 1174.1264 | 1648.8452 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 16.7406 | 24.7402 | 37.1534 | 56.5728 | 87.1689 | 135.6714 | 212.9676 | 336.7113 | 535.5833 | 856.2565 | 1374.7909 | 2215.2858 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5288 | 10.5283 | 22.9415 | 42.3609 | 72.9571 | 121.4596 | 198.7558 | 322.4995 | 521.3714 | 839.2458 | 1352.2423 | 2185.1352 | 2549.2086 | 2534.696 | 2514.5288 | 2486.4106 | 2447.0898 | 2391.9554 | 2314.4625 | 2205.3109 | 2051.2732 | 1833.5212 |  | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0019909 | 0.0029422 | 0.0044185 | 0.0067279 | 0.010367 | 0.016135 | 0.025327 | 0.040043 | 0.063694 | 0.10183 | 0.1635 | 0.26345 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 |  | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.002023 | 0.0026816 | 0.0035857 | 0.0048322 | 0.0065582 | 0.0089565 | 0.0123 | 0.016977 | 0.023534 | 0.032749 | 0.04573 | 0.064049 | 0.089945 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00030074 | 0.0012521 | 0.0027283 | 0.0050378 | 0.0086764 | 0.014445 | 0.023637 | 0.038353 | 0.062004 | 0.099807 | 0.16082 | 0.25987 | 0.30316 | 0.30144 | 0.29904 | 0.2957 | 0.29102 | 0.28446 | 0.27525 | 0.26227 | 0.24395 | 0.21805 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5291 | 10.5296 | 22.9443 | 42.366 | 72.9658 | 121.474 | 198.7795 | 322.5378 | 521.4334 | 839.3457 | 1352.4031 | 2185.3951 | 2549.5118 | 2534.9974 | 2514.8278 | 2486.7063 | 2447.3808 | 2392.2398 | 2314.7377 | 2205.5732 | 2051.5172 | 1833.7392 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.2802 | 25.5376 | 38.3509 | 58.3963 | 89.9786 | 140.0445 | 219.8323 | 347.5646 | 552.8468 | 883.8564 | 1419.1048 | 2286.6915 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6103 | 10.8677 | 23.681 | 43.7263 | 75.3087 | 125.3746 | 205.1623 | 332.8947 | 538.1769 | 866.2974 | 1395.8293 | 2255.5691 | 2631.3777 | 2616.3973 | 2595.58 | 2566.5555 | 2525.9672 | 2469.0557 | 2389.0649 | 2276.395 | 2117.3923 | 1892.6214 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2308 | 12.6823 | 19.739 | 30.9848 | 48.9884 | 77.9225 | 124.5775 | 200.0195 | 322.3038 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36791 | 1.5318 | 3.3378 | 6.1631 | 10.6146 | 17.6713 | 28.9172 | 46.9207 | 75.8548 | 122.1026 | 196.7389 | 317.9172 | 370.8866 | 368.7751 | 365.8409 | 361.75 | 356.0292 | 348.0076 | 336.7331 | 320.8526 | 298.4415 | 266.7606 |  | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.037595 | 0.055559 | 0.083436 | 0.12705 | 0.19576 | 0.30468 | 0.47826 | 0.75616 | 1.2028 | 1.9229 | 3.0874 | 4.9749 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 |  | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.038201 | 0.050638 | 0.06771 | 0.09125 | 0.12384 | 0.16913 | 0.23228 | 0.32058 | 0.4444 | 0.61842 | 0.86355 | 1.2095 | 1.6985 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0056789 | 0.023644 | 0.05152 | 0.095131 | 0.16384 | 0.27276 | 0.44635 | 0.72424 | 1.1709 | 1.8847 | 3.0368 | 4.9072 | 5.7248 | 5.6922 | 5.6469 | 5.5838 | 5.4955 | 5.3717 | 5.1976 | 4.9525 | 4.6066 | 4.1176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.513 | 22.9527 | 50.0146 | 92.3506 | 159.0529 | 264.7927 | 433.3053 | 703.0775 | 1136.636 | 1829.6304 | 2948.008 | 4763.7886 | 5557.5009 | 5525.862 | 5481.8957 | 5420.5957 | 5334.8727 | 5214.6748 | 5045.7334 | 4807.7733 | 4471.9575 | 3997.2387
| FALSE | 306 | 22016052 | BAN | Blank | 22 | BUS NO.3 | LOW IMP BUS PROT | X | GE | GE_B90 | GE B90 | GE RELAYS | Digital |  | 0.033587 | 1 |  | 0.96924 | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.3143 |  | 5.0708 | 0.0089964 | 4.1392e-07 | 0.008996 | 24.7403 | 0.028975 | 24.7692 | 25.5397 | 3.5995 | 0.54714 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.3143 |  | 31.2817 | 54.4556 | 31.2817 | 23.1739 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.8009e-07 | 4.1392e-07 | 6.2161e-07 | 9.4651e-07 | 1.4584e-06 | 2.2699e-06 | 3.5631e-06 | 5.6335e-06 | 8.9608e-06 | 1.4326e-05 | 2.3001e-05 | 3.7064e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 36.8478 | 54.4556 | 81.7783 | 124.5223 | 191.8675 | 298.6264 | 468.7632 | 741.1354 | 1178.8726 | 1884.7066 | 3026.0528 | 4876.0666 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 |  | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 37.4422 | 49.6318 | 66.3645 | 89.4368 | 121.3806 | 165.7707 | 227.6615 | 314.2107 | 435.5671 | 606.1367 | 846.3903 | 1185.4426 | 1664.7368 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 16.7407 | 24.7403 | 37.1535 | 56.573 | 87.1693 | 135.672 | 212.9685 | 336.7127 | 535.5855 | 856.2601 | 1374.7966 | 2215.295 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5288 | 10.5284 | 22.9416 | 42.3611 | 72.9574 | 121.4601 | 198.7566 | 322.5008 | 521.3736 | 839.2493 | 1352.2478 | 2185.1443 | 2549.2192 | 2534.7064 | 2514.5392 | 2486.4209 | 2447.0999 | 2391.9652 | 2314.472 | 2205.32 | 2051.2817 | 1833.5287 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019606 | 0.028975 | 0.043513 | 0.066256 | 0.10209 | 0.15889 | 0.24942 | 0.39434 | 0.62725 | 1.0028 | 1.6101 | 2.5945 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019922 | 0.026408 | 0.035311 | 0.047588 | 0.064584 | 0.088203 | 0.12113 | 0.16719 | 0.23176 | 0.32251 | 0.45035 | 0.63075 | 0.88577 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029616 | 0.01233 | 0.026868 | 0.049611 | 0.085445 | 0.14225 | 0.23278 | 0.3777 | 0.61061 | 0.98289 | 1.5837 | 2.5591 | 2.9855 | 2.9685 | 2.9449 | 2.912 | 2.8659 | 2.8014 | 2.7106 | 2.5828 | 2.4024 | 2.1473 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5318 | 10.5407 | 22.9685 | 42.4107 | 73.0428 | 121.6023 | 198.9894 | 322.8785 | 521.9842 | 840.2322 | 1353.8315 | 2187.7034 | 2552.2047 | 2537.675 | 2517.4841 | 2489.3329 | 2449.9658 | 2394.7666 | 2317.1826 | 2207.9028 | 2053.6841 | 1835.6761 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.2816 | 25.5397 | 38.3541 | 58.4011 | 89.9861 | 140.0561 | 219.8504 | 347.5933 | 552.8925 | 883.9294 | 1419.2221 | 2286.8806 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6105 | 10.8686 | 23.683 | 43.73 | 75.3149 | 125.385 | 205.1793 | 332.9222 | 538.2214 | 866.369 | 1395.9447 | 2255.7556 | 2631.5953 | 2616.6136 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2308 | 12.6823 | 19.739 | 30.9849 | 48.9885 | 77.9225 | 124.5776 | 200.0197 | 322.3042 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1631 | 10.6146 | 17.6713 | 28.9172 | 46.9208 | 75.8549 | 122.1027 | 196.7391 | 317.9175 | 370.8869 | 368.7755 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.37023 | 0.54714 | 0.82167 | 1.2511 | 1.9278 | 3.0005 | 4.7099 | 7.4466 | 11.8448 | 18.9366 | 30.4043 | 48.9924 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 |  | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3762 | 0.49868 | 0.6668 | 0.89862 | 1.2196 | 1.6656 | 2.2874 | 3.157 | 4.3764 | 6.0902 | 8.5041 | 11.9108 | 16.7265 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055926 | 0.23284 | 0.50737 | 0.93684 | 1.6135 | 2.6862 | 4.3956 | 7.1323 | 11.5305 | 18.5604 | 29.9057 | 48.3256 | 56.3773 | 56.0564 | 55.6104 | 54.9885 | 54.1189 | 52.8996 | 51.1858 | 48.7718 | 45.3652 | 40.5494 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5661 | 23.1739 | 50.4966 | 93.2406 | 160.5858 | 267.3448 | 437.4815 | 709.8538 | 1147.5909 | 1847.2644 | 2976.421 | 4809.7021 | 5611.0642 | 5579.1204 | 5534.7304 | 5472.8395 | 5386.2903 | 5264.934 | 5094.3643 | 4854.1107 | 4515.0584 | 4035.7642
| FALSE | 307 | 22015678 | BAN | Blank | 22 | BUS NO.3 | POWER QUALITY | I | Schneider | ION_7400 | ION 7400 | ION 7000s | Digital |  | 0.033587 | 1 |  | 0.96924 | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.3143 |  | 5.0708 | 0.0089964 | 4.1392e-07 | 0.008996 | 24.7403 | 0.028975 | 24.7692 | 25.5397 | 3.5995 | 0.54714 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.3143 |  | 31.2817 | 54.4556 | 31.2817 | 23.1739 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.8009e-07 | 4.1392e-07 | 6.2161e-07 | 9.4651e-07 | 1.4584e-06 | 2.2699e-06 | 3.5631e-06 | 5.6335e-06 | 8.9608e-06 | 1.4326e-05 | 2.3001e-05 | 3.7064e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 36.8478 | 54.4556 | 81.7783 | 124.5223 | 191.8675 | 298.6264 | 468.7632 | 741.1354 | 1178.8726 | 1884.7066 | 3026.0528 | 4876.0666 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 | 5700.501 |  | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 31.2817 | 37.4422 | 49.6318 | 66.3645 | 89.4368 | 121.3806 | 165.7707 | 227.6615 | 314.2107 | 435.5671 | 606.1367 | 846.3903 | 1185.4426 | 1664.7368 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 16.7407 | 24.7403 | 37.1535 | 56.573 | 87.1693 | 135.672 | 212.9685 | 336.7127 | 535.5855 | 856.2601 | 1374.7966 | 2215.295 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5288 | 10.5284 | 22.9416 | 42.3611 | 72.9574 | 121.4601 | 198.7566 | 322.5008 | 521.3736 | 839.2493 | 1352.2478 | 2185.1443 | 2549.2192 | 2534.7064 | 2514.5392 | 2486.4209 | 2447.0999 | 2391.9652 | 2314.472 | 2205.32 | 2051.2817 | 1833.5287 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019606 | 0.028975 | 0.043513 | 0.066256 | 0.10209 | 0.15889 | 0.24942 | 0.39434 | 0.62725 | 1.0028 | 1.6101 | 2.5945 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019922 | 0.026408 | 0.035311 | 0.047588 | 0.064584 | 0.088203 | 0.12113 | 0.16719 | 0.23176 | 0.32251 | 0.45035 | 0.63075 | 0.88577 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029616 | 0.01233 | 0.026868 | 0.049611 | 0.085445 | 0.14225 | 0.23278 | 0.3777 | 0.61061 | 0.98289 | 1.5837 | 2.5591 | 2.9855 | 2.9685 | 2.9449 | 2.912 | 2.8659 | 2.8014 | 2.7106 | 2.5828 | 2.4024 | 2.1473 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5318 | 10.5407 | 22.9685 | 42.4107 | 73.0428 | 121.6023 | 198.9894 | 322.8785 | 521.9842 | 840.2322 | 1353.8315 | 2187.7034 | 2552.2047 | 2537.675 | 2517.4841 | 2489.3329 | 2449.9658 | 2394.7666 | 2317.1826 | 2207.9028 | 2053.6841 | 1835.6761 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.2816 | 25.5397 | 38.3541 | 58.4011 | 89.9861 | 140.0561 | 219.8504 | 347.5933 | 552.8925 | 883.9294 | 1419.2221 | 2286.8806 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6105 | 10.8686 | 23.683 | 43.73 | 75.3149 | 125.385 | 205.1793 | 332.9222 | 538.2214 | 866.369 | 1395.9447 | 2255.7556 | 2631.5953 | 2616.6136 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2308 | 12.6823 | 19.739 | 30.9849 | 48.9885 | 77.9225 | 124.5776 | 200.0197 | 322.3042 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1631 | 10.6146 | 17.6713 | 28.9172 | 46.9208 | 75.8549 | 122.1027 | 196.7391 | 317.9175 | 370.8869 | 368.7755 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.37023 | 0.54714 | 0.82167 | 1.2511 | 1.9278 | 3.0005 | 4.7099 | 7.4466 | 11.8448 | 18.9366 | 30.4043 | 48.9924 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 | 57.2759 |  | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3143 | 0.3762 | 0.49868 | 0.6668 | 0.89862 | 1.2196 | 1.6656 | 2.2874 | 3.157 | 4.3764 | 6.0902 | 8.5041 | 11.9108 | 16.7265 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055926 | 0.23284 | 0.50737 | 0.93684 | 1.6135 | 2.6862 | 4.3956 | 7.1323 | 11.5305 | 18.5604 | 29.9057 | 48.3256 | 56.3773 | 56.0564 | 55.6104 | 54.9885 | 54.1189 | 52.8996 | 51.1858 | 48.7718 | 45.3652 | 40.5494 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5661 | 23.1739 | 50.4966 | 93.2406 | 160.5858 | 267.3448 | 437.4815 | 709.8538 | 1147.5909 | 1847.2644 | 2976.421 | 4809.7021 | 5611.0642 | 5579.1204 | 5534.7304 | 5472.8395 | 5386.2903 | 5264.934 | 5094.3643 | 4854.1107 | 4515.0584 | 4035.7642
| FALSE | 308 | 22016134 | BAN | Blank | 22 | BUS NO.3 | SINGLE ZONE BUS DIST | Y | Schweitzer | SEL_311C_1 | SEL 311C | SEL 300s | Digital |  | 0.0034106 | 1 |  | 0.96924 | 0.0051679 | 2.4145e-08 | 0.0051679 | 14.2118 | 0.0016901 | 14.2135 | 14.6699 | 2.0677 | 0.031916 |  | 5.0708 | 0.0089964 | 4.2032e-08 | 0.0089964 | 24.7402 | 0.0029422 | 24.7431 | 25.5376 | 3.5995 | 0.055559 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 14.2118 | 0.0016901 | 14.2135 | 14.6699 | 2.0677 | 0.031916 |  | 30.9831 | 53.9358 | 30.9831 | 22.9527 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.8441e-08 | 4.2032e-08 | 6.3121e-08 | 9.6113e-08 | 1.4809e-07 | 2.305e-07 | 3.6182e-07 | 5.7205e-07 | 9.0992e-07 | 1.4547e-06 | 2.3357e-06 | 3.7636e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 36.496 | 53.9358 | 80.9976 | 123.3336 | 190.0359 | 295.7757 | 464.2884 | 734.0605 | 1167.619 | 1866.7151 | 2997.1661 | 4829.5196 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 | 5646.0839 |  | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 30.9831 | 37.0848 | 49.1581 | 65.731 | 88.583 | 120.2219 | 164.1882 | 225.4882 | 311.2112 | 431.4091 | 600.3505 | 838.3106 | 1174.1264 | 1648.8452 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 16.7406 | 24.7402 | 37.1534 | 56.5728 | 87.1689 | 135.6714 | 212.9676 | 336.7113 | 535.5833 | 856.2565 | 1374.7909 | 2215.2858 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5288 | 10.5283 | 22.9415 | 42.3609 | 72.9571 | 121.4596 | 198.7558 | 322.4995 | 521.3714 | 839.2458 | 1352.2423 | 2185.1352 | 2549.2086 | 2534.696 | 2514.5288 | 2486.4106 | 2447.0898 | 2391.9554 | 2314.4625 | 2205.3109 | 2051.2732 | 1833.5212 |  | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0019909 | 0.0029422 | 0.0044185 | 0.0067279 | 0.010367 | 0.016135 | 0.025327 | 0.040043 | 0.063694 | 0.10183 | 0.1635 | 0.26345 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 |  | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.002023 | 0.0026816 | 0.0035857 | 0.0048322 | 0.0065582 | 0.0089565 | 0.0123 | 0.016977 | 0.023534 | 0.032749 | 0.04573 | 0.064049 | 0.089945 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00030074 | 0.0012521 | 0.0027283 | 0.0050378 | 0.0086764 | 0.014445 | 0.023637 | 0.038353 | 0.062004 | 0.099807 | 0.16082 | 0.25987 | 0.30316 | 0.30144 | 0.29904 | 0.2957 | 0.29102 | 0.28446 | 0.27525 | 0.26227 | 0.24395 | 0.21805 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5291 | 10.5296 | 22.9443 | 42.366 | 72.9658 | 121.474 | 198.7795 | 322.5378 | 521.4334 | 839.3457 | 1352.4031 | 2185.3951 | 2549.5118 | 2534.9974 | 2514.8278 | 2486.7063 | 2447.3808 | 2392.2398 | 2314.7377 | 2205.5732 | 2051.5172 | 1833.7392 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.2802 | 25.5376 | 38.3509 | 58.3963 | 89.9786 | 140.0445 | 219.8323 | 347.5646 | 552.8468 | 883.8564 | 1419.1048 | 2286.6915 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6103 | 10.8677 | 23.681 | 43.7263 | 75.3087 | 125.3746 | 205.1623 | 332.8947 | 538.1769 | 866.2974 | 1395.8293 | 2255.5691 | 2631.3777 | 2616.3973 | 2595.58 | 2566.5555 | 2525.9672 | 2469.0557 | 2389.0649 | 2276.395 | 2117.3923 | 1892.6214 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2308 | 12.6823 | 19.739 | 30.9848 | 48.9884 | 77.9225 | 124.5775 | 200.0195 | 322.3038 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36791 | 1.5318 | 3.3378 | 6.1631 | 10.6146 | 17.6713 | 28.9172 | 46.9207 | 75.8548 | 122.1026 | 196.7389 | 317.9172 | 370.8866 | 368.7751 | 365.8409 | 361.75 | 356.0292 | 348.0076 | 336.7331 | 320.8526 | 298.4415 | 266.7606 |  | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.037595 | 0.055559 | 0.083436 | 0.12705 | 0.19576 | 0.30468 | 0.47826 | 0.75616 | 1.2028 | 1.9229 | 3.0874 | 4.9749 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 | 5.816 |  | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.031916 | 0.038201 | 0.050638 | 0.06771 | 0.09125 | 0.12384 | 0.16913 | 0.23228 | 0.32058 | 0.4444 | 0.61842 | 0.86355 | 1.2095 | 1.6985 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0056789 | 0.023644 | 0.05152 | 0.095131 | 0.16384 | 0.27276 | 0.44635 | 0.72424 | 1.1709 | 1.8847 | 3.0368 | 4.9072 | 5.7248 | 5.6922 | 5.6469 | 5.5838 | 5.4955 | 5.3717 | 5.1976 | 4.9525 | 4.6066 | 4.1176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.513 | 22.9527 | 50.0146 | 92.3506 | 159.0529 | 264.7927 | 433.3053 | 703.0775 | 1136.636 | 1829.6304 | 2948.008 | 4763.7886 | 5557.5009 | 5525.862 | 5481.8957 | 5420.5957 | 5334.8727 | 5214.6748 | 5045.7334 | 4807.7733 | 4471.9575 | 3997.2387
| FALSE | 309 | 22016140 | BAN | Blank | 22 | CAP NO.1 | OC & EF & CB MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.2894 | 1 |  | 0.96924 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.7081 |  | 5.0708 | 0.0089964 | 3.5665e-06 | 0.0089929 | 24.7411 | 0.24966 | 24.9908 | 25.5576 | 3.5995 | 4.7144 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.7081 |  | 33.8131 | 58.8623 | 33.8131 | 25.0492 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.4133e-06 | 3.5665e-06 | 5.356e-06 | 8.1554e-06 | 1.2566e-05 | 1.9558e-05 | 3.0701e-05 | 4.854e-05 | 7.7209e-05 | 0.00012344 | 0.00019819 | 0.00031935 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 39.8296 | 58.8623 | 88.396 | 134.599 | 207.3939 | 322.7921 | 506.6967 | 801.1101 | 1274.27 | 2037.222 | 3270.929 | 5270.6508 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 |  | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 40.4721 | 53.6482 | 71.7349 | 96.6742 | 131.2031 | 179.1853 | 246.0844 | 339.6375 | 470.8143 | 655.1869 | 914.8824 | 1281.3718 | 1799.4517 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 16.7413 | 24.7411 | 37.1548 | 56.575 | 87.1723 | 135.6767 | 212.976 | 336.7245 | 535.6043 | 856.2901 | 1374.8448 | 2215.3726 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5289 | 10.5288 | 22.9424 | 42.3626 | 72.9599 | 121.4643 | 198.7636 | 322.5121 | 521.3919 | 839.2787 | 1352.2952 | 2185.2208 | 2549.3085 | 2534.7953 | 2514.6273 | 2486.5081 | 2447.1856 | 2392.0491 | 2314.5531 | 2205.3973 | 2051.3536 | 1833.593 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.16893 | 0.24966 | 0.37492 | 0.57088 | 0.87963 | 1.3691 | 2.1491 | 3.3978 | 5.4046 | 8.6406 | 13.8731 | 22.3546 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025518 | 0.10624 | 0.2315 | 0.42747 | 0.73622 | 1.2257 | 2.0057 | 3.2544 | 5.2612 | 8.4689 | 13.6456 | 22.0504 | 25.7243 | 25.5778 | 25.3743 | 25.0906 | 24.6938 | 24.1374 | 23.3554 | 22.254 | 20.6996 | 18.5022 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5544 | 10.635 | 23.1739 | 42.79 | 73.6961 | 122.69 | 200.7693 | 325.7665 | 526.6531 | 847.7476 | 1365.9408 | 2207.2712 | 2575.0328 | 2560.3731 | 2540.0016 | 2511.5986 | 2471.8794 | 2416.1865 | 2337.9086 | 2227.6513 | 2072.0532 | 1852.0952 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.2938 | 25.5576 | 38.381 | 58.442 | 90.0491 | 140.1543 | 220.0045 | 347.8369 | 553.28 | 884.5489 | 1420.2167 | 2288.4832 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6123 | 10.8762 | 23.6996 | 43.7606 | 75.3677 | 125.4728 | 205.3231 | 333.1555 | 538.5986 | 866.9762 | 1396.923 | 2257.3364 | 2633.4395 | 2618.4473 | 2597.6137 | 2568.5665 | 2527.9464 | 2470.9902 | 2390.9368 | 2278.1786 | 2119.0513 | 1894.1043 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2309 | 12.6824 | 19.7391 | 30.9851 | 48.9889 | 77.9232 | 124.5787 | 200.0215 | 322.307 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6147 | 17.6714 | 28.9174 | 46.9212 | 75.8555 | 122.1038 | 196.7408 | 317.9203 | 370.8902 | 368.7787 | 365.8445 | 361.7536 | 356.0327 | 348.011 | 336.7364 | 320.8557 | 298.4444 | 266.7632 |  | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 3.19 | 4.7144 | 7.0798 | 10.7802 | 16.6105 | 25.8528 | 40.582 | 64.162 | 102.058 | 163.1638 | 261.973 | 422.1333 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 |  | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 3.2415 | 4.2968 | 5.7453 | 7.7428 | 10.5082 | 14.3512 | 19.7092 | 27.202 | 37.7081 | 52.4748 | 73.2741 | 102.6267 | 144.1204 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48187 | 2.0062 | 4.3716 | 8.0721 | 13.9023 | 23.1447 | 37.8739 | 61.4538 | 99.3498 | 159.9223 | 257.6762 | 416.388 | 485.7639 | 482.9985 | 479.1555 | 473.7975 | 466.3047 | 455.7986 | 441.0319 | 420.2326 | 390.8799 | 349.3862 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0165 | 25.0492 | 54.5829 | 100.7859 | 173.5809 | 288.979 | 472.8837 | 767.297 | 1240.457 | 1996.7499 | 3217.2808 | 5198.9159 | 6065.1263 | 6030.5975 | 5982.6153 | 5915.7161 | 5822.1631 | 5690.9863 | 5506.6137 | 5246.9182 | 4880.4288 | 4362.3489
| FALSE | 310 | 22016130 | BAN | Blank | 22 | CAP NO.2 | CURRENT BAL+STEP SW CTRL | X | GE | GE_F35 | GE F35 | GE RELAYS | Digital |  | 0.2894 | 1 |  | 0.96924 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.7081 |  | 5.0708 | 0.0089964 | 3.5665e-06 | 0.0089929 | 24.7411 | 0.24966 | 24.9908 | 25.5576 | 3.5995 | 4.7144 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.7081 |  | 33.8131 | 58.8623 | 33.8131 | 25.0492 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.4133e-06 | 3.5665e-06 | 5.356e-06 | 8.1554e-06 | 1.2566e-05 | 1.9558e-05 | 3.0701e-05 | 4.854e-05 | 7.7209e-05 | 0.00012344 | 0.00019819 | 0.00031935 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 39.8296 | 58.8623 | 88.396 | 134.599 | 207.3939 | 322.7921 | 506.6967 | 801.1101 | 1274.27 | 2037.222 | 3270.929 | 5270.6508 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 |  | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 40.4721 | 53.6482 | 71.7349 | 96.6742 | 131.2031 | 179.1853 | 246.0844 | 339.6375 | 470.8143 | 655.1869 | 914.8824 | 1281.3718 | 1799.4517 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 16.7413 | 24.7411 | 37.1548 | 56.575 | 87.1723 | 135.6767 | 212.976 | 336.7245 | 535.6043 | 856.2901 | 1374.8448 | 2215.3726 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5289 | 10.5288 | 22.9424 | 42.3626 | 72.9599 | 121.4643 | 198.7636 | 322.5121 | 521.3919 | 839.2787 | 1352.2952 | 2185.2208 | 2549.3085 | 2534.7953 | 2514.6273 | 2486.5081 | 2447.1856 | 2392.0491 | 2314.5531 | 2205.3973 | 2051.3536 | 1833.593 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.16893 | 0.24966 | 0.37492 | 0.57088 | 0.87963 | 1.3691 | 2.1491 | 3.3978 | 5.4046 | 8.6406 | 13.8731 | 22.3546 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025518 | 0.10624 | 0.2315 | 0.42747 | 0.73622 | 1.2257 | 2.0057 | 3.2544 | 5.2612 | 8.4689 | 13.6456 | 22.0504 | 25.7243 | 25.5778 | 25.3743 | 25.0906 | 24.6938 | 24.1374 | 23.3554 | 22.254 | 20.6996 | 18.5022 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5544 | 10.635 | 23.1739 | 42.79 | 73.6961 | 122.69 | 200.7693 | 325.7665 | 526.6531 | 847.7476 | 1365.9408 | 2207.2712 | 2575.0328 | 2560.3731 | 2540.0016 | 2511.5986 | 2471.8794 | 2416.1865 | 2337.9086 | 2227.6513 | 2072.0532 | 1852.0952 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.2938 | 25.5576 | 38.381 | 58.442 | 90.0491 | 140.1543 | 220.0045 | 347.8369 | 553.28 | 884.5489 | 1420.2167 | 2288.4832 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6123 | 10.8762 | 23.6996 | 43.7606 | 75.3677 | 125.4728 | 205.3231 | 333.1555 | 538.5986 | 866.9762 | 1396.923 | 2257.3364 | 2633.4395 | 2618.4473 | 2597.6137 | 2568.5665 | 2527.9464 | 2470.9902 | 2390.9368 | 2278.1786 | 2119.0513 | 1894.1043 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2309 | 12.6824 | 19.7391 | 30.9851 | 48.9889 | 77.9232 | 124.5787 | 200.0215 | 322.307 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6147 | 17.6714 | 28.9174 | 46.9212 | 75.8555 | 122.1038 | 196.7408 | 317.9203 | 370.8902 | 368.7787 | 365.8445 | 361.7536 | 356.0327 | 348.011 | 336.7364 | 320.8557 | 298.4444 | 266.7632 |  | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 3.19 | 4.7144 | 7.0798 | 10.7802 | 16.6105 | 25.8528 | 40.582 | 64.162 | 102.058 | 163.1638 | 261.973 | 422.1333 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 |  | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 3.2415 | 4.2968 | 5.7453 | 7.7428 | 10.5082 | 14.3512 | 19.7092 | 27.202 | 37.7081 | 52.4748 | 73.2741 | 102.6267 | 144.1204 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48187 | 2.0062 | 4.3716 | 8.0721 | 13.9023 | 23.1447 | 37.8739 | 61.4538 | 99.3498 | 159.9223 | 257.6762 | 416.388 | 485.7639 | 482.9985 | 479.1555 | 473.7975 | 466.3047 | 455.7986 | 441.0319 | 420.2326 | 390.8799 | 349.3862 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0165 | 25.0492 | 54.5829 | 100.7859 | 173.5809 | 288.979 | 472.8837 | 767.297 | 1240.457 | 1996.7499 | 3217.2808 | 5198.9159 | 6065.1263 | 6030.5975 | 5982.6153 | 5915.7161 | 5822.1631 | 5690.9863 | 5506.6137 | 5246.9182 | 4880.4288 | 4362.3489
| FALSE | 311 | 20038268 | BAN | Blank | 22 | CAP NO.2 | OC & EF & CB MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.2894 | 1 |  | 0.96924 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.7081 |  | 5.0708 | 0.0089964 | 3.5665e-06 | 0.0089929 | 24.7411 | 0.24966 | 24.9908 | 25.5576 | 3.5995 | 4.7144 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.7081 |  | 33.8131 | 58.8623 | 33.8131 | 25.0492 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.4133e-06 | 3.5665e-06 | 5.356e-06 | 8.1554e-06 | 1.2566e-05 | 1.9558e-05 | 3.0701e-05 | 4.854e-05 | 7.7209e-05 | 0.00012344 | 0.00019819 | 0.00031935 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 39.8296 | 58.8623 | 88.396 | 134.599 | 207.3939 | 322.7921 | 506.6967 | 801.1101 | 1274.27 | 2037.222 | 3270.929 | 5270.6508 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 |  | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 40.4721 | 53.6482 | 71.7349 | 96.6742 | 131.2031 | 179.1853 | 246.0844 | 339.6375 | 470.8143 | 655.1869 | 914.8824 | 1281.3718 | 1799.4517 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 16.7413 | 24.7411 | 37.1548 | 56.575 | 87.1723 | 135.6767 | 212.976 | 336.7245 | 535.6043 | 856.2901 | 1374.8448 | 2215.3726 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5289 | 10.5288 | 22.9424 | 42.3626 | 72.9599 | 121.4643 | 198.7636 | 322.5121 | 521.3919 | 839.2787 | 1352.2952 | 2185.2208 | 2549.3085 | 2534.7953 | 2514.6273 | 2486.5081 | 2447.1856 | 2392.0491 | 2314.5531 | 2205.3973 | 2051.3536 | 1833.593 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.16893 | 0.24966 | 0.37492 | 0.57088 | 0.87963 | 1.3691 | 2.1491 | 3.3978 | 5.4046 | 8.6406 | 13.8731 | 22.3546 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025518 | 0.10624 | 0.2315 | 0.42747 | 0.73622 | 1.2257 | 2.0057 | 3.2544 | 5.2612 | 8.4689 | 13.6456 | 22.0504 | 25.7243 | 25.5778 | 25.3743 | 25.0906 | 24.6938 | 24.1374 | 23.3554 | 22.254 | 20.6996 | 18.5022 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5544 | 10.635 | 23.1739 | 42.79 | 73.6961 | 122.69 | 200.7693 | 325.7665 | 526.6531 | 847.7476 | 1365.9408 | 2207.2712 | 2575.0328 | 2560.3731 | 2540.0016 | 2511.5986 | 2471.8794 | 2416.1865 | 2337.9086 | 2227.6513 | 2072.0532 | 1852.0952 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.2938 | 25.5576 | 38.381 | 58.442 | 90.0491 | 140.1543 | 220.0045 | 347.8369 | 553.28 | 884.5489 | 1420.2167 | 2288.4832 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6123 | 10.8762 | 23.6996 | 43.7606 | 75.3677 | 125.4728 | 205.3231 | 333.1555 | 538.5986 | 866.9762 | 1396.923 | 2257.3364 | 2633.4395 | 2618.4473 | 2597.6137 | 2568.5665 | 2527.9464 | 2470.9902 | 2390.9368 | 2278.1786 | 2119.0513 | 1894.1043 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2309 | 12.6824 | 19.7391 | 30.9851 | 48.9889 | 77.9232 | 124.5787 | 200.0215 | 322.307 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6147 | 17.6714 | 28.9174 | 46.9212 | 75.8555 | 122.1038 | 196.7408 | 317.9203 | 370.8902 | 368.7787 | 365.8445 | 361.7536 | 356.0327 | 348.011 | 336.7364 | 320.8557 | 298.4444 | 266.7632 |  | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 3.19 | 4.7144 | 7.0798 | 10.7802 | 16.6105 | 25.8528 | 40.582 | 64.162 | 102.058 | 163.1638 | 261.973 | 422.1333 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 |  | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 3.2415 | 4.2968 | 5.7453 | 7.7428 | 10.5082 | 14.3512 | 19.7092 | 27.202 | 37.7081 | 52.4748 | 73.2741 | 102.6267 | 144.1204 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48187 | 2.0062 | 4.3716 | 8.0721 | 13.9023 | 23.1447 | 37.8739 | 61.4538 | 99.3498 | 159.9223 | 257.6762 | 416.388 | 485.7639 | 482.9985 | 479.1555 | 473.7975 | 466.3047 | 455.7986 | 441.0319 | 420.2326 | 390.8799 | 349.3862 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0165 | 25.0492 | 54.5829 | 100.7859 | 173.5809 | 288.979 | 472.8837 | 767.297 | 1240.457 | 1996.7499 | 3217.2808 | 5198.9159 | 6065.1263 | 6030.5975 | 5982.6153 | 5915.7161 | 5822.1631 | 5690.9863 | 5506.6137 | 5246.9182 | 4880.4288 | 4362.3489
| FALSE | 312 | 22016131 | BAN | Blank | 22 | CAP NO.3 | OC & EF & CB MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.2894 | 1 |  | 0.96924 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.7081 |  | 5.0708 | 0.0089964 | 3.5665e-06 | 0.0089929 | 24.7411 | 0.24966 | 24.9908 | 25.5576 | 3.5995 | 4.7144 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.7081 |  | 33.8131 | 58.8623 | 33.8131 | 25.0492 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.4133e-06 | 3.5665e-06 | 5.356e-06 | 8.1554e-06 | 1.2566e-05 | 1.9558e-05 | 3.0701e-05 | 4.854e-05 | 7.7209e-05 | 0.00012344 | 0.00019819 | 0.00031935 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 39.8296 | 58.8623 | 88.396 | 134.599 | 207.3939 | 322.7921 | 506.6967 | 801.1101 | 1274.27 | 2037.222 | 3270.929 | 5270.6508 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 | 6161.8006 |  | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 33.8131 | 40.4721 | 53.6482 | 71.7349 | 96.6742 | 131.2031 | 179.1853 | 246.0844 | 339.6375 | 470.8143 | 655.1869 | 914.8824 | 1281.3718 | 1799.4517 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 16.7413 | 24.7411 | 37.1548 | 56.575 | 87.1723 | 135.6767 | 212.976 | 336.7245 | 535.6043 | 856.2901 | 1374.8448 | 2215.3726 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5289 | 10.5288 | 22.9424 | 42.3626 | 72.9599 | 121.4643 | 198.7636 | 322.5121 | 521.3919 | 839.2787 | 1352.2952 | 2185.2208 | 2549.3085 | 2534.7953 | 2514.6273 | 2486.5081 | 2447.1856 | 2392.0491 | 2314.5531 | 2205.3973 | 2051.3536 | 1833.593 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.16893 | 0.24966 | 0.37492 | 0.57088 | 0.87963 | 1.3691 | 2.1491 | 3.3978 | 5.4046 | 8.6406 | 13.8731 | 22.3546 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025518 | 0.10624 | 0.2315 | 0.42747 | 0.73622 | 1.2257 | 2.0057 | 3.2544 | 5.2612 | 8.4689 | 13.6456 | 22.0504 | 25.7243 | 25.5778 | 25.3743 | 25.0906 | 24.6938 | 24.1374 | 23.3554 | 22.254 | 20.6996 | 18.5022 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5544 | 10.635 | 23.1739 | 42.79 | 73.6961 | 122.69 | 200.7693 | 325.7665 | 526.6531 | 847.7476 | 1365.9408 | 2207.2712 | 2575.0328 | 2560.3731 | 2540.0016 | 2511.5986 | 2471.8794 | 2416.1865 | 2337.9086 | 2227.6513 | 2072.0532 | 1852.0952 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.2938 | 25.5576 | 38.381 | 58.442 | 90.0491 | 140.1543 | 220.0045 | 347.8369 | 553.28 | 884.5489 | 1420.2167 | 2288.4832 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6123 | 10.8762 | 23.6996 | 43.7606 | 75.3677 | 125.4728 | 205.3231 | 333.1555 | 538.5986 | 866.9762 | 1396.923 | 2257.3364 | 2633.4395 | 2618.4473 | 2597.6137 | 2568.5665 | 2527.9464 | 2470.9902 | 2390.9368 | 2278.1786 | 2119.0513 | 1894.1043 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2309 | 12.6824 | 19.7391 | 30.9851 | 48.9889 | 77.9232 | 124.5787 | 200.0215 | 322.307 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6147 | 17.6714 | 28.9174 | 46.9212 | 75.8555 | 122.1038 | 196.7408 | 317.9203 | 370.8902 | 368.7787 | 365.8445 | 361.7536 | 356.0327 | 348.011 | 336.7364 | 320.8557 | 298.4444 | 266.7632 |  | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 3.19 | 4.7144 | 7.0798 | 10.7802 | 16.6105 | 25.8528 | 40.582 | 64.162 | 102.058 | 163.1638 | 261.973 | 422.1333 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 | 493.5067 |  | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 2.7081 | 3.2415 | 4.2968 | 5.7453 | 7.7428 | 10.5082 | 14.3512 | 19.7092 | 27.202 | 37.7081 | 52.4748 | 73.2741 | 102.6267 | 144.1204 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48187 | 2.0062 | 4.3716 | 8.0721 | 13.9023 | 23.1447 | 37.8739 | 61.4538 | 99.3498 | 159.9223 | 257.6762 | 416.388 | 485.7639 | 482.9985 | 479.1555 | 473.7975 | 466.3047 | 455.7986 | 441.0319 | 420.2326 | 390.8799 | 349.3862 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0165 | 25.0492 | 54.5829 | 100.7859 | 173.5809 | 288.979 | 472.8837 | 767.297 | 1240.457 | 1996.7499 | 3217.2808 | 5198.9159 | 6065.1263 | 6030.5975 | 5982.6153 | 5915.7161 | 5822.1631 | 5690.9863 | 5506.6137 | 5246.9182 | 4880.4288 | 4362.3489
| FALSE | 313 | 22015680 | BAN | Blank | 22 | CB BT 1-2 | CB MGMT & CB FAIL | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0 | 1 |  | 1.0927 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 5.2187 | 0.0096441 | 0 | 0.0096441 | 26.5213 | 0 | 26.5213 | 27.376 | 3.8586 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 57.7559 | 30.9493 | 26.8066 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 39.8022 | 57.7559 | 84.9868 | 126.5842 | 190.526 | 289.3521 | 442.8194 | 682.1182 | 1056.5751 | 1644.3167 | 2569.2462 | 4028.0865 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 18.277 | 26.5213 | 39.0257 | 58.1271 | 87.4889 | 132.8696 | 203.3413 | 313.2266 | 485.176 | 755.0652 | 1179.79 | 1849.6849 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0652 | 12.3095 | 24.8139 | 43.9153 | 73.2771 | 118.6578 | 189.1295 | 299.0148 | 470.9642 | 738.0545 | 1157.2413 | 1819.5343 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0652 | 12.3095 | 24.8139 | 43.9153 | 73.2771 | 118.6578 | 189.1295 | 299.0148 | 470.9642 | 738.0545 | 1157.2413 | 1819.5343 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 18.866 | 27.376 | 40.2833 | 60.0002 | 90.3082 | 137.1512 | 209.8938 | 323.32 | 500.8103 | 779.3964 | 1217.8075 | 1909.2892 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1962 | 12.7062 | 25.6135 | 45.3304 | 75.6384 | 122.4814 | 195.224 | 308.6502 | 486.1406 | 761.8376 | 1194.5323 | 1878.167 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6591 | 3.8586 | 5.6779 | 8.457 | 12.7288 | 19.3313 | 29.5843 | 45.5716 | 70.5887 | 109.8551 | 171.6487 | 269.1123 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59145 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2636 | 27.5166 | 43.5039 | 68.521 | 107.3802 | 168.3681 | 264.7257 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8529 | 26.8066 | 54.0375 | 95.6349 | 159.5767 | 258.4028 | 411.8701 | 651.1689 | 1025.6258 | 1607.2723 | 2520.1417 | 3962.4271 | 5551.4471 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 314 | 22015681 | BAN | Blank | 22 | CB BT 1-3 | CB MGMT & CB FAIL | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0 | 1 |  | 1.0927 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 5.2187 | 0.0096441 | 0 | 0.0096441 | 26.5213 | 0 | 26.5213 | 27.376 | 3.8586 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 57.7559 | 30.9493 | 26.8066 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 39.8022 | 57.7559 | 84.9868 | 126.5842 | 190.526 | 289.3521 | 442.8194 | 682.1182 | 1056.5751 | 1644.3167 | 2569.2462 | 4028.0865 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 18.277 | 26.5213 | 39.0257 | 58.1271 | 87.4889 | 132.8696 | 203.3413 | 313.2266 | 485.176 | 755.0652 | 1179.79 | 1849.6849 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0652 | 12.3095 | 24.8139 | 43.9153 | 73.2771 | 118.6578 | 189.1295 | 299.0148 | 470.9642 | 738.0545 | 1157.2413 | 1819.5343 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0652 | 12.3095 | 24.8139 | 43.9153 | 73.2771 | 118.6578 | 189.1295 | 299.0148 | 470.9642 | 738.0545 | 1157.2413 | 1819.5343 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 18.866 | 27.376 | 40.2833 | 60.0002 | 90.3082 | 137.1512 | 209.8938 | 323.32 | 500.8103 | 779.3964 | 1217.8075 | 1909.2892 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1962 | 12.7062 | 25.6135 | 45.3304 | 75.6384 | 122.4814 | 195.224 | 308.6502 | 486.1406 | 761.8376 | 1194.5323 | 1878.167 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6591 | 3.8586 | 5.6779 | 8.457 | 12.7288 | 19.3313 | 29.5843 | 45.5716 | 70.5887 | 109.8551 | 171.6487 | 269.1123 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59145 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2636 | 27.5166 | 43.5039 | 68.521 | 107.3802 | 168.3681 | 264.7257 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8529 | 26.8066 | 54.0375 | 95.6349 | 159.5767 | 258.4028 | 411.8701 | 651.1689 | 1025.6258 | 1607.2723 | 2520.1417 | 3962.4271 | 5551.4471 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 315 | 22015684 | BAN | Blank | 22 | CB TR NO.1 | CB MGMT & CB FAIL | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0 | 1 |  | 0.96924 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 5.0708 | 0.0089964 | 0 | 0.0089964 | 24.7402 | 0 | 24.7402 | 25.5374 | 3.5995 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 53.877 | 30.9493 | 22.9277 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 36.4563 | 53.877 | 80.9094 | 123.1993 | 189.8289 | 295.4535 | 463.7826 | 733.2609 | 1166.3471 | 1864.6817 | 2993.9013 | 4824.2588 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 16.7406 | 24.7402 | 37.1533 | 56.5727 | 87.1689 | 135.6714 | 212.9675 | 336.7112 | 535.583 | 856.2561 | 1374.7903 | 2215.2848 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5288 | 10.5283 | 22.9415 | 42.3609 | 72.957 | 121.4595 | 198.7557 | 322.4993 | 521.3712 | 839.2455 | 1352.2416 | 2185.1342 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5288 | 10.5283 | 22.9415 | 42.3609 | 72.957 | 121.4595 | 198.7557 | 322.4993 | 521.3712 | 839.2455 | 1352.2416 | 2185.1342 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.2801 | 25.5374 | 38.3506 | 58.3957 | 89.9778 | 140.0432 | 219.8302 | 347.5613 | 552.8417 | 883.8481 | 1419.0915 | 2286.6702 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6103 | 10.8676 | 23.6808 | 43.7259 | 75.308 | 125.3734 | 205.1604 | 332.8916 | 538.1719 | 866.2893 | 1395.8163 | 2255.548 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2308 | 12.6823 | 19.7389 | 30.9848 | 48.9884 | 77.9225 | 124.5775 | 200.0195 | 322.3038 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36791 | 1.5318 | 3.3378 | 6.1631 | 10.6146 | 17.6713 | 28.9172 | 46.9207 | 75.8548 | 122.1026 | 196.7389 | 317.9172 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.507 | 22.9277 | 49.9601 | 92.25 | 158.8796 | 264.5042 | 432.8333 | 702.3116 | 1135.3978 | 1827.6373 | 2944.7967 | 4758.5994 | 5551.4471 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 316 | 22015683 | BAN | Blank | 22 | CB TR NO.2 | CB MGMT & CB FAIL | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0 | 1 |  | 0.96924 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 5.0708 | 0.0089964 | 0 | 0.0089964 | 24.7402 | 0 | 24.7402 | 25.5374 | 3.5995 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 53.877 | 30.9493 | 22.9277 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 36.4563 | 53.877 | 80.9094 | 123.1993 | 189.8289 | 295.4535 | 463.7826 | 733.2609 | 1166.3471 | 1864.6817 | 2993.9013 | 4824.2588 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 16.7406 | 24.7402 | 37.1533 | 56.5727 | 87.1689 | 135.6714 | 212.9675 | 336.7112 | 535.583 | 856.2561 | 1374.7903 | 2215.2848 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5288 | 10.5283 | 22.9415 | 42.3609 | 72.957 | 121.4595 | 198.7557 | 322.4993 | 521.3712 | 839.2455 | 1352.2416 | 2185.1342 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5288 | 10.5283 | 22.9415 | 42.3609 | 72.957 | 121.4595 | 198.7557 | 322.4993 | 521.3712 | 839.2455 | 1352.2416 | 2185.1342 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.2801 | 25.5374 | 38.3506 | 58.3957 | 89.9778 | 140.0432 | 219.8302 | 347.5613 | 552.8417 | 883.8481 | 1419.0915 | 2286.6702 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6103 | 10.8676 | 23.6808 | 43.7259 | 75.308 | 125.3734 | 205.1604 | 332.8916 | 538.1719 | 866.2893 | 1395.8163 | 2255.548 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2308 | 12.6823 | 19.7389 | 30.9848 | 48.9884 | 77.9225 | 124.5775 | 200.0195 | 322.3038 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36791 | 1.5318 | 3.3378 | 6.1631 | 10.6146 | 17.6713 | 28.9172 | 46.9207 | 75.8548 | 122.1026 | 196.7389 | 317.9172 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.507 | 22.9277 | 49.9601 | 92.25 | 158.8796 | 264.5042 | 432.8333 | 702.3116 | 1135.3978 | 1827.6373 | 2944.7967 | 4758.5994 | 5551.4471 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 317 | 22015682 | BAN | Blank | 22 | CB TR NO.3 | CB MGMT & CB FAIL | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0 | 1 |  | 0.96924 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 5.0708 | 0.0089964 | 0 | 0.0089964 | 24.7402 | 0 | 24.7402 | 25.5374 | 3.5995 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 53.877 | 30.9493 | 22.9277 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 36.4563 | 53.877 | 80.9094 | 123.1993 | 189.8289 | 295.4535 | 463.7826 | 733.2609 | 1166.3471 | 1864.6817 | 2993.9013 | 4824.2588 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 16.7406 | 24.7402 | 37.1533 | 56.5727 | 87.1689 | 135.6714 | 212.9675 | 336.7112 | 535.583 | 856.2561 | 1374.7903 | 2215.2848 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5288 | 10.5283 | 22.9415 | 42.3609 | 72.957 | 121.4595 | 198.7557 | 322.4993 | 521.3712 | 839.2455 | 1352.2416 | 2185.1342 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5288 | 10.5283 | 22.9415 | 42.3609 | 72.957 | 121.4595 | 198.7557 | 322.4993 | 521.3712 | 839.2455 | 1352.2416 | 2185.1342 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.2801 | 25.5374 | 38.3506 | 58.3957 | 89.9778 | 140.0432 | 219.8302 | 347.5613 | 552.8417 | 883.8481 | 1419.0915 | 2286.6702 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6103 | 10.8676 | 23.6808 | 43.7259 | 75.308 | 125.3734 | 205.1604 | 332.8916 | 538.1719 | 866.2893 | 1395.8163 | 2255.548 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2308 | 12.6823 | 19.7389 | 30.9848 | 48.9884 | 77.9225 | 124.5775 | 200.0195 | 322.3038 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36791 | 1.5318 | 3.3378 | 6.1631 | 10.6146 | 17.6713 | 28.9172 | 46.9207 | 75.8548 | 122.1026 | 196.7389 | 317.9172 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.507 | 22.9277 | 49.9601 | 92.25 | 158.8796 | 264.5042 | 432.8333 | 702.3116 | 1135.3978 | 1827.6373 | 2944.7967 | 4758.5994 | 5551.4471 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 318 | 22004455 | BAN | Blank | 22 | ALL FEEDERS | BUEF BUS2 | BU | RMS | 2C137 | RMS - 2C137 | RMS 2C13X | Electronic |  | 0.15703 | 2190 |  | 6.6 | 0.014726 | 0.0051892 | 0.0095369 | 52.4046 | 544.8634 | 597.268 | 71.2617 | 5.9438 | 6859.28 |  | 15.598 | 0.15027 | 0.052954 | 0.097321 | 534.7719 | 5560.1567 | 6094.9286 | 727.2033 | 60.6544 | 69996.7597 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 17.7652 | 0.11672 | 17.8819 | 14.6761 | 2.0677 | 1.4694 |  | 7533.7535 | 76879.546 | 36.0951 | 76843.4509 |  | 0.086007 |  | 7.1928 | 7.8388 | 8.5428 | 9.3101 | 10.1463 | 11.0575 | 12.0507 | 13.133 | 14.3125 | 15.598 | 16.9989 | 18.5257 | 20.1895 | 22.0028 | 23.979 | 26.1326 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.018366 | 0.022977 | 0.028828 | 0.036267 | 0.045735 | 0.057803 | 0.073205 | 0.092883 | 0.11805 | 0.15027 | 0.19156 | 0.24452 | 0.31248 | 0.39976 | 0.51193 | 0.65616 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0064717 | 0.0080965 | 0.010159 | 0.01278 | 0.016116 | 0.020369 | 0.025796 | 0.03273 | 0.041599 | 0.052954 | 0.067504 | 0.086163 | 0.11011 | 0.14087 | 0.18039 | 0.23122 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 9395.7087 | 11754.6908 | 14748.4407 | 18553.7286 | 23397.5675 | 29571.6743 | 37451.129 | 47518.4534 | 60394.693 | 76879.546 | 98003.1861 | 125093.196 | 159861.0354 | 204513.7605 | 261898.3915 | 335688.4934 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 |  | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 38.9518 | 51.633 | 69.0403 | 93.0428 | 126.2747 | 172.4545 | 236.8407 | 326.8796 | 453.129 | 630.5759 | 880.5164 | 1233.2392 | 1731.8584 |  | 65.3563 | 81.7653 | 102.5897 | 129.0592 | 162.7528 | 205.6997 | 260.5089 | 330.537 | 420.1037 | 534.7719 | 681.7073 | 870.1446 | 1111.9887 | 1422.5917 | 1821.7575 | 2335.0393 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 51.1441 | 67.5532 | 88.3776 | 114.8471 | 148.5407 | 191.4876 | 246.2968 | 316.3248 | 405.8916 | 520.5597 | 667.4951 | 855.9325 | 1097.7765 | 1408.3796 | 1807.5454 | 2320.8271 | 2837.2403 | 2834.4414 | 2828.9033 | 2821.3012 | 2810.8188 | 2796.3058 | 2776.1382 | 2748.0195 | 2708.6978 | 2653.5622 | 2576.0677 | 2466.9138 | 2312.8729 | 2095.1163 |  | 679.5255 | 850.1341 | 1066.651 | 1341.8607 | 1692.1815 | 2138.7112 | 2708.5767 | 3436.6755 | 4367.9233 | 5560.1567 | 7087.881 | 9047.1109 | 11561.6241 | 14791.0416 | 18941.2683 | 24277.9873 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 |  | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.13971 | 0.1852 | 0.24763 | 0.33372 | 0.45292 | 0.61855 | 0.84949 | 1.1724 | 1.6253 | 2.2617 | 3.1582 | 4.4233 | 6.2118 |  | 679.4088 | 850.0174 | 1066.5342 | 1341.7439 | 1692.0647 | 2138.5944 | 2708.46 | 3436.5587 | 4367.8066 | 5560.04 | 7087.7643 | 9046.9942 | 11561.5074 | 14790.9249 | 18941.1516 | 24277.8706 | 29647.1473 | 29647.1243 | 29647.0788 | 29647.0164 | 29646.9303 | 29646.8111 | 29646.6455 | 29646.4145 | 29646.0916 | 29645.6388 | 29645.0023 | 29644.1058 | 29642.8407 | 29641.0522 |  | 730.5529 | 917.5705 | 1154.9118 | 1456.591 | 1840.6054 | 2330.082 | 2954.7568 | 3752.8836 | 4773.6981 | 6080.5997 | 7755.2595 | 9902.9266 | 12659.2839 | 16199.3045 | 20748.6969 | 26598.6977 | 32484.3876 | 32481.5657 | 32475.9821 | 32468.3176 | 32457.7491 | 32443.1169 | 32422.7837 | 32394.434 | 32354.7894 | 32299.201 | 32221.07 | 32111.0196 | 31955.7136 | 31736.1685 |  | 88.874 | 111.1876 | 139.5054 | 175.4996 | 221.3175 | 279.7184 | 354.2501 | 449.4769 | 571.2732 | 727.2033 | 927.0118 | 1183.2561 | 1512.1249 | 1934.4949 | 2477.2959 | 3175.2762 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 74.1979 | 96.5115 | 124.8293 | 160.8236 | 206.6414 | 265.0423 | 339.574 | 434.8008 | 556.5971 | 712.5272 | 912.3357 | 1168.58 | 1497.4488 | 1919.8188 | 2462.6198 | 3160.6001 | 3862.8386 | 3859.9483 | 3854.2294 | 3846.3791 | 3835.5545 | 3820.5678 | 3799.7417 | 3770.7051 | 3730.0997 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 7.4128 | 9.2739 | 11.6358 | 14.638 | 18.4596 | 23.3307 | 29.5472 | 37.4899 | 47.6486 | 60.6544 | 77.32 | 98.6928 | 126.123 | 161.3519 | 206.6257 | 264.8427 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 5.3451 | 7.2062 | 9.5681 | 12.5703 | 16.3919 | 21.263 | 27.4795 | 35.4222 | 45.5809 | 58.5867 | 75.2523 | 96.625 | 124.0553 | 159.2842 | 204.558 | 262.775 | 321.3472 | 320.9399 | 320.1342 | 319.0282 | 317.5031 | 315.3917 | 312.4575 | 308.3665 | 302.6457 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 8554.5402 | 10702.33 | 13428.0587 | 16892.6711 | 21302.8561 | 26924.2144 | 34098.246 | 43264.2743 | 54987.7442 | 69996.7597 | 89229.266 | 113893.9917 | 145549.1747 | 186204.2804 | 238451.4441 | 305635.348 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 |  | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.7588 | 2.3314 | 3.1174 | 4.2012 | 5.7018 | 7.787 | 10.6943 | 14.7599 | 20.4605 | 28.4729 | 39.7587 | 55.6855 | 78.2 |  | 8553.0707 | 10700.8605 | 13426.5893 | 16891.2016 | 21301.3867 | 26922.7449 | 34096.7766 | 43262.8048 | 54986.2748 | 69995.2902 | 89227.7966 | 113892.5223 | 145547.7053 | 186202.811 | 238449.9746 | 305633.8785 | 373227.6519 | 373227.3625 | 373226.7899 | 373226.0039 | 373224.92 | 373223.4195 | 373221.3343 | 373218.427 | 373214.3614 | 373208.6608 | 373200.6484 | 373189.3626 | 373173.4358 | 373150.9213 |  | 9363.1666 | 11722.1488 | 14715.8986 | 18521.1865 | 23365.0254 | 29539.1322 | 37418.5869 | 47485.9114 | 60362.1509 | 76847.0039 | 97970.644 | 125060.6539 | 159828.4933 | 204481.2184 | 261865.8494 | 335655.9513 | 409896.2252 | 409889.8164 | 409877.1356 | 409859.7287 | 409835.7268 | 409802.4959 | 409756.3172 | 409691.9327 | 409601.8961 | 409475.65 | 409298.2076 | 409048.2736 | 408695.5599 | 408196.9536
| TRUE | 319 | 22004456 | BAN | Blank | 22 | ALL FEEDERS | BUEF BUS3 | BU | RMS | 2C137 | RMS - 2C137 | RMS 2C13X | Electronic |  | 0.15703 | 2190 |  | 6.6 | 0.014726 | 0.0051892 | 0.0095369 | 52.4046 | 544.8634 | 597.268 | 71.2617 | 5.9438 | 6859.28 |  | 15.598 | 0.15027 | 0.052954 | 0.097321 | 534.7719 | 5560.1567 | 6094.9286 | 727.2033 | 60.6544 | 69996.7597 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 17.7652 | 0.11672 | 17.8819 | 14.6761 | 2.0677 | 1.4694 |  | 7533.7535 | 76879.546 | 36.0951 | 76843.4509 |  | 0.086007 |  | 7.1928 | 7.8388 | 8.5428 | 9.3101 | 10.1463 | 11.0575 | 12.0507 | 13.133 | 14.3125 | 15.598 | 16.9989 | 18.5257 | 20.1895 | 22.0028 | 23.979 | 26.1326 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.018366 | 0.022977 | 0.028828 | 0.036267 | 0.045735 | 0.057803 | 0.073205 | 0.092883 | 0.11805 | 0.15027 | 0.19156 | 0.24452 | 0.31248 | 0.39976 | 0.51193 | 0.65616 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0064717 | 0.0080965 | 0.010159 | 0.01278 | 0.016116 | 0.020369 | 0.025796 | 0.03273 | 0.041599 | 0.052954 | 0.067504 | 0.086163 | 0.11011 | 0.14087 | 0.18039 | 0.23122 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 9395.7087 | 11754.6908 | 14748.4407 | 18553.7286 | 23397.5675 | 29571.6743 | 37451.129 | 47518.4534 | 60394.693 | 76879.546 | 98003.1861 | 125093.196 | 159861.0354 | 204513.7605 | 261898.3915 | 335688.4934 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 |  | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 38.9518 | 51.633 | 69.0403 | 93.0428 | 126.2747 | 172.4545 | 236.8407 | 326.8796 | 453.129 | 630.5759 | 880.5164 | 1233.2392 | 1731.8584 |  | 65.3563 | 81.7653 | 102.5897 | 129.0592 | 162.7528 | 205.6997 | 260.5089 | 330.537 | 420.1037 | 534.7719 | 681.7073 | 870.1446 | 1111.9887 | 1422.5917 | 1821.7575 | 2335.0393 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 51.1441 | 67.5532 | 88.3776 | 114.8471 | 148.5407 | 191.4876 | 246.2968 | 316.3248 | 405.8916 | 520.5597 | 667.4951 | 855.9325 | 1097.7765 | 1408.3796 | 1807.5454 | 2320.8271 | 2837.2403 | 2834.4414 | 2828.9033 | 2821.3012 | 2810.8188 | 2796.3058 | 2776.1382 | 2748.0195 | 2708.6978 | 2653.5622 | 2576.0677 | 2466.9138 | 2312.8729 | 2095.1163 |  | 679.5255 | 850.1341 | 1066.651 | 1341.8607 | 1692.1815 | 2138.7112 | 2708.5767 | 3436.6755 | 4367.9233 | 5560.1567 | 7087.881 | 9047.1109 | 11561.6241 | 14791.0416 | 18941.2683 | 24277.9873 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 |  | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.13971 | 0.1852 | 0.24763 | 0.33372 | 0.45292 | 0.61855 | 0.84949 | 1.1724 | 1.6253 | 2.2617 | 3.1582 | 4.4233 | 6.2118 |  | 679.4088 | 850.0174 | 1066.5342 | 1341.7439 | 1692.0647 | 2138.5944 | 2708.46 | 3436.5587 | 4367.8066 | 5560.04 | 7087.7643 | 9046.9942 | 11561.5074 | 14790.9249 | 18941.1516 | 24277.8706 | 29647.1473 | 29647.1243 | 29647.0788 | 29647.0164 | 29646.9303 | 29646.8111 | 29646.6455 | 29646.4145 | 29646.0916 | 29645.6388 | 29645.0023 | 29644.1058 | 29642.8407 | 29641.0522 |  | 730.5529 | 917.5705 | 1154.9118 | 1456.591 | 1840.6054 | 2330.082 | 2954.7568 | 3752.8836 | 4773.6981 | 6080.5997 | 7755.2595 | 9902.9266 | 12659.2839 | 16199.3045 | 20748.6969 | 26598.6977 | 32484.3876 | 32481.5657 | 32475.9821 | 32468.3176 | 32457.7491 | 32443.1169 | 32422.7837 | 32394.434 | 32354.7894 | 32299.201 | 32221.07 | 32111.0196 | 31955.7136 | 31736.1685 |  | 88.874 | 111.1876 | 139.5054 | 175.4996 | 221.3175 | 279.7184 | 354.2501 | 449.4769 | 571.2732 | 727.2033 | 927.0118 | 1183.2561 | 1512.1249 | 1934.4949 | 2477.2959 | 3175.2762 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 74.1979 | 96.5115 | 124.8293 | 160.8236 | 206.6414 | 265.0423 | 339.574 | 434.8008 | 556.5971 | 712.5272 | 912.3357 | 1168.58 | 1497.4488 | 1919.8188 | 2462.6198 | 3160.6001 | 3862.8386 | 3859.9483 | 3854.2294 | 3846.3791 | 3835.5545 | 3820.5678 | 3799.7417 | 3770.7051 | 3730.0997 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 7.4128 | 9.2739 | 11.6358 | 14.638 | 18.4596 | 23.3307 | 29.5472 | 37.4899 | 47.6486 | 60.6544 | 77.32 | 98.6928 | 126.123 | 161.3519 | 206.6257 | 264.8427 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 5.3451 | 7.2062 | 9.5681 | 12.5703 | 16.3919 | 21.263 | 27.4795 | 35.4222 | 45.5809 | 58.5867 | 75.2523 | 96.625 | 124.0553 | 159.2842 | 204.558 | 262.775 | 321.3472 | 320.9399 | 320.1342 | 319.0282 | 317.5031 | 315.3917 | 312.4575 | 308.3665 | 302.6457 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 8554.5402 | 10702.33 | 13428.0587 | 16892.6711 | 21302.8561 | 26924.2144 | 34098.246 | 43264.2743 | 54987.7442 | 69996.7597 | 89229.266 | 113893.9917 | 145549.1747 | 186204.2804 | 238451.4441 | 305635.348 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 |  | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.7588 | 2.3314 | 3.1174 | 4.2012 | 5.7018 | 7.787 | 10.6943 | 14.7599 | 20.4605 | 28.4729 | 39.7587 | 55.6855 | 78.2 |  | 8553.0707 | 10700.8605 | 13426.5893 | 16891.2016 | 21301.3867 | 26922.7449 | 34096.7766 | 43262.8048 | 54986.2748 | 69995.2902 | 89227.7966 | 113892.5223 | 145547.7053 | 186202.811 | 238449.9746 | 305633.8785 | 373227.6519 | 373227.3625 | 373226.7899 | 373226.0039 | 373224.92 | 373223.4195 | 373221.3343 | 373218.427 | 373214.3614 | 373208.6608 | 373200.6484 | 373189.3626 | 373173.4358 | 373150.9213 |  | 9363.1666 | 11722.1488 | 14715.8986 | 18521.1865 | 23365.0254 | 29539.1322 | 37418.5869 | 47485.9114 | 60362.1509 | 76847.0039 | 97970.644 | 125060.6539 | 159828.4933 | 204481.2184 | 261865.8494 | 335655.9513 | 409896.2252 | 409889.8164 | 409877.1356 | 409859.7287 | 409835.7268 | 409802.4959 | 409756.3172 | 409691.9327 | 409601.8961 | 409475.65 | 409298.2076 | 409048.2736 | 408695.5599 | 408196.9536
| TRUE | 320 | 22004454 | BAN | Blank | 22 | ALL FEEDERS | BUEF BUS1 | BU | RMS | 2C137 | RMS - 2C137 | RMS 2C13X | Electronic |  | 0.15703 | 2190 |  | 6.6 | 0.014726 | 0.0051892 | 0.0095369 | 52.4046 | 544.8634 | 597.268 | 71.2617 | 5.9438 | 6859.28 |  | 15.598 | 0.15027 | 0.052954 | 0.097321 | 534.7719 | 5560.1567 | 6094.9286 | 727.2033 | 60.6544 | 69996.7597 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 17.7652 | 0.11672 | 17.8819 | 14.6761 | 2.0677 | 1.4694 |  | 7533.7535 | 76879.546 | 36.0951 | 76843.4509 |  | 0.086007 |  | 7.1928 | 7.8388 | 8.5428 | 9.3101 | 10.1463 | 11.0575 | 12.0507 | 13.133 | 14.3125 | 15.598 | 16.9989 | 18.5257 | 20.1895 | 22.0028 | 23.979 | 26.1326 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.018366 | 0.022977 | 0.028828 | 0.036267 | 0.045735 | 0.057803 | 0.073205 | 0.092883 | 0.11805 | 0.15027 | 0.19156 | 0.24452 | 0.31248 | 0.39976 | 0.51193 | 0.65616 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0064717 | 0.0080965 | 0.010159 | 0.01278 | 0.016116 | 0.020369 | 0.025796 | 0.03273 | 0.041599 | 0.052954 | 0.067504 | 0.086163 | 0.11011 | 0.14087 | 0.18039 | 0.23122 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 9395.7087 | 11754.6908 | 14748.4407 | 18553.7286 | 23397.5675 | 29571.6743 | 37451.129 | 47518.4534 | 60394.693 | 76879.546 | 98003.1861 | 125093.196 | 159861.0354 | 204513.7605 | 261898.3915 | 335688.4934 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 | 409928.7673 |  | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 32.5429 | 38.9518 | 51.633 | 69.0403 | 93.0428 | 126.2747 | 172.4545 | 236.8407 | 326.8796 | 453.129 | 630.5759 | 880.5164 | 1233.2392 | 1731.8584 |  | 65.3563 | 81.7653 | 102.5897 | 129.0592 | 162.7528 | 205.6997 | 260.5089 | 330.537 | 420.1037 | 534.7719 | 681.7073 | 870.1446 | 1111.9887 | 1422.5917 | 1821.7575 | 2335.0393 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 | 2851.4524 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 51.1441 | 67.5532 | 88.3776 | 114.8471 | 148.5407 | 191.4876 | 246.2968 | 316.3248 | 405.8916 | 520.5597 | 667.4951 | 855.9325 | 1097.7765 | 1408.3796 | 1807.5454 | 2320.8271 | 2837.2403 | 2834.4414 | 2828.9033 | 2821.3012 | 2810.8188 | 2796.3058 | 2776.1382 | 2748.0195 | 2708.6978 | 2653.5622 | 2576.0677 | 2466.9138 | 2312.8729 | 2095.1163 |  | 679.5255 | 850.1341 | 1066.651 | 1341.8607 | 1692.1815 | 2138.7112 | 2708.5767 | 3436.6755 | 4367.9233 | 5560.1567 | 7087.881 | 9047.1109 | 11561.6241 | 14791.0416 | 18941.2683 | 24277.9873 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 | 29647.264 |  | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.13971 | 0.1852 | 0.24763 | 0.33372 | 0.45292 | 0.61855 | 0.84949 | 1.1724 | 1.6253 | 2.2617 | 3.1582 | 4.4233 | 6.2118 |  | 679.4088 | 850.0174 | 1066.5342 | 1341.7439 | 1692.0647 | 2138.5944 | 2708.46 | 3436.5587 | 4367.8066 | 5560.04 | 7087.7643 | 9046.9942 | 11561.5074 | 14790.9249 | 18941.1516 | 24277.8706 | 29647.1473 | 29647.1243 | 29647.0788 | 29647.0164 | 29646.9303 | 29646.8111 | 29646.6455 | 29646.4145 | 29646.0916 | 29645.6388 | 29645.0023 | 29644.1058 | 29642.8407 | 29641.0522 |  | 730.5529 | 917.5705 | 1154.9118 | 1456.591 | 1840.6054 | 2330.082 | 2954.7568 | 3752.8836 | 4773.6981 | 6080.5997 | 7755.2595 | 9902.9266 | 12659.2839 | 16199.3045 | 20748.6969 | 26598.6977 | 32484.3876 | 32481.5657 | 32475.9821 | 32468.3176 | 32457.7491 | 32443.1169 | 32422.7837 | 32394.434 | 32354.7894 | 32299.201 | 32221.07 | 32111.0196 | 31955.7136 | 31736.1685 |  | 88.874 | 111.1876 | 139.5054 | 175.4996 | 221.3175 | 279.7184 | 354.2501 | 449.4769 | 571.2732 | 727.2033 | 927.0118 | 1183.2561 | 1512.1249 | 1934.4949 | 2477.2959 | 3175.2762 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 74.1979 | 96.5115 | 124.8293 | 160.8236 | 206.6414 | 265.0423 | 339.574 | 434.8008 | 556.5971 | 712.5272 | 912.3357 | 1168.58 | 1497.4488 | 1919.8188 | 2462.6198 | 3160.6001 | 3862.8386 | 3859.9483 | 3854.2294 | 3846.3791 | 3835.5545 | 3820.5678 | 3799.7417 | 3770.7051 | 3730.0997 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 7.4128 | 9.2739 | 11.6358 | 14.638 | 18.4596 | 23.3307 | 29.5472 | 37.4899 | 47.6486 | 60.6544 | 77.32 | 98.6928 | 126.123 | 161.3519 | 206.6257 | 264.8427 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 5.3451 | 7.2062 | 9.5681 | 12.5703 | 16.3919 | 21.263 | 27.4795 | 35.4222 | 45.5809 | 58.5867 | 75.2523 | 96.625 | 124.0553 | 159.2842 | 204.558 | 262.775 | 321.3472 | 320.9399 | 320.1342 | 319.0282 | 317.5031 | 315.3917 | 312.4575 | 308.3665 | 302.6457 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 8554.5402 | 10702.33 | 13428.0587 | 16892.6711 | 21302.8561 | 26924.2144 | 34098.246 | 43264.2743 | 54987.7442 | 69996.7597 | 89229.266 | 113893.9917 | 145549.1747 | 186204.2804 | 238451.4441 | 305635.348 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 | 373229.1213 |  | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.7588 | 2.3314 | 3.1174 | 4.2012 | 5.7018 | 7.787 | 10.6943 | 14.7599 | 20.4605 | 28.4729 | 39.7587 | 55.6855 | 78.2 |  | 8553.0707 | 10700.8605 | 13426.5893 | 16891.2016 | 21301.3867 | 26922.7449 | 34096.7766 | 43262.8048 | 54986.2748 | 69995.2902 | 89227.7966 | 113892.5223 | 145547.7053 | 186202.811 | 238449.9746 | 305633.8785 | 373227.6519 | 373227.3625 | 373226.7899 | 373226.0039 | 373224.92 | 373223.4195 | 373221.3343 | 373218.427 | 373214.3614 | 373208.6608 | 373200.6484 | 373189.3626 | 373173.4358 | 373150.9213 |  | 9363.1666 | 11722.1488 | 14715.8986 | 18521.1865 | 23365.0254 | 29539.1322 | 37418.5869 | 47485.9114 | 60362.1509 | 76847.0039 | 97970.644 | 125060.6539 | 159828.4933 | 204481.2184 | 261865.8494 | 335655.9513 | 409896.2252 | 409889.8164 | 409877.1356 | 409859.7287 | 409835.7268 | 409802.4959 | 409756.3172 | 409691.9327 | 409601.8961 | 409475.65 | 409298.2076 | 409048.2736 | 408695.5599 | 408196.9536
| FALSE | 321 | 22016139 | BAN | Blank | 22 | ALL FEEDERS | NEUT BUS MGMT IO EXT. | C | GE | GE_C30 | GE C30 | GE RELAYS | Digital |  | 0.81881 | 1 |  | 0.96924 | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 7.6623 |  | 5.0708 | 0.0089964 | 1.0091e-05 | 0.0089863 | 24.7429 | 0.70636 | 25.4493 | 25.5947 | 3.5996 | 13.3386 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 7.6623 |  | 39.0519 | 67.9822 | 39.0519 | 28.9302 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 6.8281e-06 | 1.0091e-05 | 1.5154e-05 | 2.3075e-05 | 3.5554e-05 | 5.5337e-05 | 8.6864e-05 | 0.00013734 | 0.00021845 | 0.00034925 | 0.00056074 | 0.00090356 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 46.0006 | 67.9822 | 102.0917 | 155.4532 | 239.5266 | 372.804 | 585.2021 | 925.2305 | 1471.6998 | 2352.8602 | 3777.7124 | 6087.2623 | 7116.4829 | 7116.4829 | 7116.4829 | 7116.4829 | 7116.4829 | 7116.4829 | 7116.4829 | 7116.4829 | 7116.4829 | 7116.4829 |  | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 46.7427 | 61.9602 | 82.8492 | 111.6525 | 151.5311 | 206.9475 | 284.2117 | 392.2594 | 543.7602 | 756.6987 | 1056.6303 | 1479.9019 | 2078.2508 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 16.7425 | 24.7429 | 37.1575 | 56.5791 | 87.1786 | 135.6866 | 212.9914 | 336.7489 | 535.6431 | 856.3522 | 1374.9445 | 2215.5333 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5291 | 10.5295 | 22.9441 | 42.3657 | 72.9652 | 121.4732 | 198.778 | 322.5355 | 521.4297 | 839.3396 | 1352.3933 | 2185.3793 | 2549.4934 | 2534.9791 | 2514.8096 | 2486.6884 | 2447.3631 | 2392.2225 | 2314.721 | 2205.5572 | 2051.5024 | 1833.726 |  | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.47797 | 0.70636 | 1.0608 | 1.6152 | 2.4888 | 3.8736 | 6.0805 | 9.6135 | 15.2916 | 24.4472 | 39.2521 | 63.2493 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 |  | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.48568 | 0.64379 | 0.86084 | 1.1601 | 1.5745 | 2.1503 | 2.9531 | 4.0757 | 5.6499 | 7.8624 | 10.9788 | 15.3768 | 21.5939 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0722 | 0.3006 | 0.65501 | 1.2095 | 2.083 | 3.4678 | 5.6747 | 9.2078 | 14.8858 | 23.9616 | 38.6083 | 62.3884 | 72.7832 | 72.3689 | 71.7931 | 70.9902 | 69.8676 | 68.2934 | 66.0809 | 62.9645 | 58.5665 | 52.3494 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6013 | 10.8301 | 23.5991 | 43.5751 | 75.0482 | 124.941 | 204.4528 | 331.7433 | 536.3155 | 863.3011 | 1391.0016 | 2247.7678 | 2622.2766 | 2607.3479 | 2586.6027 | 2557.6786 | 2517.2307 | 2460.516 | 2380.8019 | 2268.5217 | 2110.0689 | 1886.0754 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.3188 | 25.5947 | 38.4366 | 58.5267 | 90.1796 | 140.3574 | 220.3234 | 348.341 | 554.0818 | 885.8309 | 1422.275 | 2291.7999 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6161 | 10.892 | 23.7339 | 43.824 | 75.4769 | 125.6547 | 205.6207 | 333.6383 | 539.3792 | 868.2327 | 1398.9475 | 2260.6079 | 2637.2561 | 2622.2422 | 2601.3784 | 2572.2891 | 2531.6101 | 2474.5714 | 2394.402 | 2281.4804 | 2122.1224 | 1896.8494 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5996 | 5.4056 | 8.231 | 12.6826 | 19.7395 | 30.9857 | 48.9898 | 77.9246 | 124.581 | 200.0251 | 322.3128 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36793 | 1.5318 | 3.3379 | 6.1633 | 10.6149 | 17.6718 | 28.918 | 46.922 | 75.8569 | 122.106 | 196.7444 | 317.9261 | 370.8969 | 368.7854 | 365.8512 | 361.7601 | 356.0391 | 348.0174 | 336.7425 | 320.8615 | 298.4498 | 266.768 |  | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 9.0257 | 13.3386 | 20.0312 | 30.5011 | 46.9969 | 73.147 | 114.8211 | 181.5372 | 288.7587 | 461.649 | 741.2158 | 1194.3669 | 1396.3078 | 1396.3078 | 1396.3078 | 1396.3078 | 1396.3078 | 1396.3078 | 1396.3078 | 1396.3078 | 1396.3078 | 1396.3078 |  | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 9.1713 | 12.1571 | 16.2556 | 21.9071 | 29.7316 | 40.6047 | 55.7645 | 76.9643 | 106.6899 | 148.47 | 207.3189 | 290.368 | 407.7686 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3634 | 5.6763 | 12.3689 | 22.8388 | 39.3347 | 65.4847 | 107.1588 | 173.875 | 281.0964 | 452.4777 | 729.0587 | 1178.1113 | 1374.4008 | 1366.5763 | 1355.7032 | 1340.5433 | 1319.3436 | 1289.618 | 1247.8378 | 1188.989 | 1105.9399 | 988.5393 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9487 | 28.9302 | 63.0398 | 116.4012 | 200.4747 | 333.7521 | 546.1502 | 886.1786 | 1432.6479 | 2306.1175 | 3715.7522 | 6004.4131 | 7004.8304 | 6964.9518 | 6909.5354 | 6832.2712 | 6724.2235 | 6572.7227 | 6359.7842 | 6059.8526 | 5636.581 | 5038.232
| FALSE | 322 | 22016138 | BAN | Blank | 22 | ALL FEEDERS | MEF & NEUT. BUS MGMT | X | GE | GE_F35 | GE F35 | GE RELAYS | Digital |  | 0.81881 | 1 |  | 0.96924 | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 7.6623 |  | 5.0708 | 0.0089964 | 1.0091e-05 | 0.0089863 | 24.7429 | 0.70636 | 25.4493 | 25.5947 | 3.5996 | 13.3386 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 7.6623 |  | 39.0519 | 67.9822 | 39.0519 | 28.9302 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 6.8281e-06 | 1.0091e-05 | 1.5154e-05 | 2.3075e-05 | 3.5554e-05 | 5.5337e-05 | 8.6864e-05 | 0.00013734 | 0.00021845 | 0.00034925 | 0.00056074 | 0.00090356 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 46.0006 | 67.9822 | 102.0917 | 155.4532 | 239.5266 | 372.804 | 585.2021 | 925.2305 | 1471.6998 | 2352.8602 | 3777.7124 | 6087.2623 | 7116.4829 | 7116.4829 | 7116.4829 | 7116.4829 | 7116.4829 | 7116.4829 | 7116.4829 | 7116.4829 | 7116.4829 | 7116.4829 |  | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 46.7427 | 61.9602 | 82.8492 | 111.6525 | 151.5311 | 206.9475 | 284.2117 | 392.2594 | 543.7602 | 756.6987 | 1056.6303 | 1479.9019 | 2078.2508 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 16.7425 | 24.7429 | 37.1575 | 56.5791 | 87.1786 | 135.6866 | 212.9914 | 336.7489 | 535.6431 | 856.3522 | 1374.9445 | 2215.5333 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5291 | 10.5295 | 22.9441 | 42.3657 | 72.9652 | 121.4732 | 198.778 | 322.5355 | 521.4297 | 839.3396 | 1352.3933 | 2185.3793 | 2549.4934 | 2534.9791 | 2514.8096 | 2486.6884 | 2447.3631 | 2392.2225 | 2314.721 | 2205.5572 | 2051.5024 | 1833.726 |  | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.47797 | 0.70636 | 1.0608 | 1.6152 | 2.4888 | 3.8736 | 6.0805 | 9.6135 | 15.2916 | 24.4472 | 39.2521 | 63.2493 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 |  | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.48568 | 0.64379 | 0.86084 | 1.1601 | 1.5745 | 2.1503 | 2.9531 | 4.0757 | 5.6499 | 7.8624 | 10.9788 | 15.3768 | 21.5939 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0722 | 0.3006 | 0.65501 | 1.2095 | 2.083 | 3.4678 | 5.6747 | 9.2078 | 14.8858 | 23.9616 | 38.6083 | 62.3884 | 72.7832 | 72.3689 | 71.7931 | 70.9902 | 69.8676 | 68.2934 | 66.0809 | 62.9645 | 58.5665 | 52.3494 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6013 | 10.8301 | 23.5991 | 43.5751 | 75.0482 | 124.941 | 204.4528 | 331.7433 | 536.3155 | 863.3011 | 1391.0016 | 2247.7678 | 2622.2766 | 2607.3479 | 2586.6027 | 2557.6786 | 2517.2307 | 2460.516 | 2380.8019 | 2268.5217 | 2110.0689 | 1886.0754 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.3188 | 25.5947 | 38.4366 | 58.5267 | 90.1796 | 140.3574 | 220.3234 | 348.341 | 554.0818 | 885.8309 | 1422.275 | 2291.7999 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6161 | 10.892 | 23.7339 | 43.824 | 75.4769 | 125.6547 | 205.6207 | 333.6383 | 539.3792 | 868.2327 | 1398.9475 | 2260.6079 | 2637.2561 | 2622.2422 | 2601.3784 | 2572.2891 | 2531.6101 | 2474.5714 | 2394.402 | 2281.4804 | 2122.1224 | 1896.8494 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5996 | 5.4056 | 8.231 | 12.6826 | 19.7395 | 30.9857 | 48.9898 | 77.9246 | 124.581 | 200.0251 | 322.3128 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36793 | 1.5318 | 3.3379 | 6.1633 | 10.6149 | 17.6718 | 28.918 | 46.922 | 75.8569 | 122.106 | 196.7444 | 317.9261 | 370.8969 | 368.7854 | 365.8512 | 361.7601 | 356.0391 | 348.0174 | 336.7425 | 320.8615 | 298.4498 | 266.768 |  | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 9.0257 | 13.3386 | 20.0312 | 30.5011 | 46.9969 | 73.147 | 114.8211 | 181.5372 | 288.7587 | 461.649 | 741.2158 | 1194.3669 | 1396.3078 | 1396.3078 | 1396.3078 | 1396.3078 | 1396.3078 | 1396.3078 | 1396.3078 | 1396.3078 | 1396.3078 | 1396.3078 |  | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 9.1713 | 12.1571 | 16.2556 | 21.9071 | 29.7316 | 40.6047 | 55.7645 | 76.9643 | 106.6899 | 148.47 | 207.3189 | 290.368 | 407.7686 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3634 | 5.6763 | 12.3689 | 22.8388 | 39.3347 | 65.4847 | 107.1588 | 173.875 | 281.0964 | 452.4777 | 729.0587 | 1178.1113 | 1374.4008 | 1366.5763 | 1355.7032 | 1340.5433 | 1319.3436 | 1289.618 | 1247.8378 | 1188.989 | 1105.9399 | 988.5393 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9487 | 28.9302 | 63.0398 | 116.4012 | 200.4747 | 333.7521 | 546.1502 | 886.1786 | 1432.6479 | 2306.1175 | 3715.7522 | 6004.4131 | 7004.8304 | 6964.9518 | 6909.5354 | 6832.2712 | 6724.2235 | 6572.7227 | 6359.7842 | 6059.8526 | 5636.581 | 5038.232
| TRUE | 323 | 22009336 | BAN | Blank | 22 | ALL FEEDERS | BUEF & Y MEF | BU | Schweitzer | SEL_351A | SEL 351 | SEL 300s | Digital |  | 0.15703 | 1 |  | 4.6061 | 0.0071552 | 1.5391e-06 | 0.0071537 | 19.6774 | 0.10774 | 19.7851 | 20.3197 | 2.8628 | 2.0345 |  | 11.9319 | 0.083722 | 1.8009e-05 | 0.083703 | 230.2391 | 1.2606 | 231.4997 | 237.7554 | 33.4972 | 23.8052 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 14.2121 | 0.077816 | 14.2899 | 14.6761 | 2.0677 | 1.4694 |  | 45.0022 | 526.5575 | 32.5032 | 494.0543 |  | 0.095183 |  | 5.0661 | 5.572 | 6.1284 | 6.7404 | 7.4135 | 8.1538 | 8.968 | 9.8636 | 10.8485 | 11.9319 | 13.1234 | 14.4339 | 15.8753 | 17.4606 | 19.2042 | 21.1219 | 23.2311 | 25.551 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0089761 | 0.01132 | 0.014347 | 0.018263 | 0.023345 | 0.029952 | 0.03856 | 0.049796 | 0.064486 | 0.083722 | 0.10895 | 0.14207 | 0.18561 | 0.2429 | 0.31838 | 0.4179 | 0.54922 | 0.72263 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.9308e-06 | 2.4351e-06 | 3.086e-06 | 3.9286e-06 | 5.0217e-06 | 6.4429e-06 | 8.2946e-06 | 1.0711e-05 | 1.3871e-05 | 1.8009e-05 | 2.3435e-05 | 3.0559e-05 | 3.9925e-05 | 5.225e-05 | 6.8486e-05 | 8.9893e-05 | 0.00011814 | 0.00015544 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 56.4544 | 71.1979 | 90.2313 | 114.8661 | 146.8266 | 188.3819 | 242.5213 | 313.1858 | 405.5756 | 526.5575 | 685.2045 | 893.5125 | 1167.3506 | 1527.722 | 2002.4387 | 2628.3434 | 3454.2618 | 4544.9219 | 5923.0996 | 5923.0996 | 5923.0996 | 5923.0996 | 5923.0996 | 5923.0996 | 5923.0996 | 5923.0996 | 5923.0996 | 5923.0996 | 5923.0996 | 5923.0996 |  | 32.5032 | 32.5032 | 32.5032 | 32.5032 | 32.5032 | 32.5032 | 32.5032 | 32.5032 | 32.5032 | 32.5032 | 32.5032 | 32.5032 | 32.5032 | 32.5032 | 32.5032 | 32.5032 | 32.5032 | 38.9043 | 51.5699 | 68.956 | 92.9292 | 126.1204 | 172.2438 | 236.5514 | 326.4803 | 452.5755 | 629.8057 | 879.4409 | 1231.7329 | 1729.743 |  | 24.6849 | 31.1315 | 39.4539 | 50.2256 | 64.2004 | 82.3706 | 106.0433 | 136.9416 | 177.3393 | 230.2391 | 299.608 | 390.6915 | 510.4281 | 668.0018 | 875.5733 | 1149.2523 | 1510.388 | 1987.2829 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 10.4727 | 16.9194 | 25.2418 | 36.0135 | 49.9883 | 68.1585 | 91.8311 | 122.7294 | 163.1272 | 216.027 | 285.3959 | 376.4793 | 496.216 | 653.7896 | 861.3611 | 1135.0402 | 1496.1759 | 1970.2719 | 2567.3468 | 2559.7447 | 2549.2623 | 2534.7493 | 2514.5817 | 2486.463 | 2447.1413 | 2392.0057 | 2314.5112 | 2205.3573 | 2051.3164 | 1833.5597 |  | 0.13516 | 0.17046 | 0.21602 | 0.275 | 0.35152 | 0.45101 | 0.58062 | 0.7498 | 0.97099 | 1.2606 | 1.6405 | 2.1392 | 2.7948 | 3.6575 | 4.794 | 6.2925 | 8.2699 | 10.881 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 |  | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.093141 | 0.12346 | 0.16509 | 0.22248 | 0.30195 | 0.41237 | 0.56633 | 0.78163 | 1.0835 | 1.5078 | 2.1055 | 2.9489 | 4.1412 |  | 0.057342 | 0.092639 | 0.13821 | 0.19719 | 0.2737 | 0.37319 | 0.50281 | 0.67198 | 0.89317 | 1.1828 | 1.5626 | 2.0613 | 2.7169 | 3.5797 | 4.7162 | 6.2147 | 8.192 | 10.7879 | 14.0571 | 14.0154 | 13.958 | 13.8786 | 13.7681 | 13.6142 | 13.3989 | 13.097 | 12.6727 | 12.075 | 11.2316 | 10.0393 |  | 10.5301 | 17.012 | 25.38 | 36.2107 | 50.262 | 68.5317 | 92.3339 | 123.4014 | 164.0204 | 217.2098 | 286.9586 | 378.5407 | 498.9329 | 657.3694 | 866.0774 | 1141.2549 | 1504.3679 | 1981.0598 | 2581.4038 | 2573.7601 | 2563.2203 | 2548.6279 | 2528.3498 | 2500.0772 | 2460.5401 | 2405.1027 | 2327.1839 | 2217.4323 | 2062.548 | 1843.5991 |  | 25.4907 | 32.1478 | 40.7419 | 51.8653 | 66.2963 | 85.0597 | 109.5051 | 141.4121 | 183.1287 | 237.7554 | 309.389 | 403.4459 | 527.0915 | 689.8093 | 904.1571 | 1186.7706 | 1559.6959 | 2052.1595 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 10.8146 | 17.4717 | 26.0658 | 37.1892 | 51.6202 | 70.3836 | 94.829 | 126.736 | 168.4526 | 223.0793 | 294.7129 | 388.7698 | 512.4154 | 675.1332 | 889.481 | 1172.0946 | 1545.0198 | 2034.5931 | 2651.16 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 3.5914 | 4.5293 | 5.7401 | 7.3073 | 9.3404 | 11.984 | 15.4281 | 19.9234 | 25.8008 | 33.4972 | 43.5895 | 56.8411 | 74.2615 | 97.1866 | 127.3859 | 167.2031 | 219.7442 | 289.1269 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 1.5237 | 2.4616 | 3.6724 | 5.2395 | 7.2727 | 9.9163 | 13.3604 | 17.8557 | 23.7331 | 31.4295 | 41.5218 | 54.7734 | 72.1937 | 95.1189 | 125.3182 | 165.1354 | 217.6765 | 286.652 | 373.5196 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 2.5522 | 3.2188 | 4.0793 | 5.193 | 6.6379 | 8.5166 | 10.9642 | 14.1588 | 18.3357 | 23.8052 | 30.9774 | 40.3948 | 52.7748 | 69.0668 | 90.5283 | 118.8249 | 156.1638 | 205.4715 | 267.7776 | 267.7776 | 267.7776 | 267.7776 | 267.7776 | 267.7776 | 267.7776 | 267.7776 | 267.7776 | 267.7776 | 267.7776 | 267.7776 |  | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.4694 | 1.7588 | 2.3314 | 3.1174 | 4.2012 | 5.7018 | 7.787 | 10.6943 | 14.7599 | 20.4605 | 28.4729 | 39.7587 | 55.6855 | 78.2 |  | 1.0828 | 1.7493 | 2.6098 | 3.7235 | 5.1685 | 7.0471 | 9.4947 | 12.6894 | 16.8662 | 22.3357 | 29.508 | 38.9254 | 51.3054 | 67.5974 | 89.0589 | 117.3554 | 154.6944 | 203.7127 | 265.4462 | 264.6602 | 263.5764 | 262.0758 | 259.9906 | 257.0834 | 253.0178 | 247.3171 | 239.3047 | 228.0189 | 212.0922 | 189.5776 |  | 23.9512 | 38.6947 | 57.7281 | 82.3629 | 114.3234 | 155.8787 | 210.0181 | 280.6826 | 373.0724 | 494.0543 | 652.7013 | 861.0093 | 1134.8474 | 1495.2188 | 1969.9355 | 2595.8402 | 3421.7586 | 4506.0177 | 5871.5297 | 5854.1436 | 5830.1704 | 5796.9791 | 5750.8557 | 5686.5482 | 5596.6193 | 5470.5241 | 5293.2939 | 5043.6586 | 4691.3667 | 4193.3565
| FALSE | 324 | 22015692 | BAN | BAN015 | 22 | BAN15 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 0.96924 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 13.2077 |  | 5.0708 | 0.0089964 | 7.078e-06 | 0.0089893 | 24.7421 | 0.49546 | 25.2376 | 25.5776 | 3.5995 | 22.9921 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 13.2077 |  | 44.4658 | 77.4068 | 44.4658 | 32.941 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.7894e-06 | 7.078e-06 | 1.0629e-05 | 1.6185e-05 | 2.4939e-05 | 3.8815e-05 | 6.0929e-05 | 9.6332e-05 | 0.00015323 | 0.00024497 | 0.00039332 | 0.00063378 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 52.3779 | 77.4068 | 116.2451 | 177.0042 | 272.7332 | 424.4873 | 666.331 | 1053.4989 | 1675.7274 | 2679.0465 | 4301.4315 | 6931.1633 | 8103.0688 | 8103.0688 | 8103.0688 | 8103.0688 | 8103.0688 | 8103.0688 | 8103.0688 | 8103.0688 | 8103.0688 | 8103.0688 |  | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 44.4658 | 53.2228 | 70.55 | 94.3349 | 127.1314 | 172.5385 | 235.6374 | 323.6131 | 446.6399 | 619.1438 | 861.6028 | 1203.1151 | 1685.0665 | 2366.3669 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.7419 | 24.7421 | 37.1563 | 56.5772 | 87.1757 | 135.682 | 212.9843 | 336.7377 | 535.6252 | 856.3235 | 1374.8984 | 2215.4591 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.529 | 10.5292 | 22.9433 | 42.3642 | 72.9628 | 121.4691 | 198.7714 | 322.5247 | 521.4122 | 839.3115 | 1352.348 | 2185.3061 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.33526 | 0.49546 | 0.74406 | 1.133 | 1.7457 | 2.717 | 4.265 | 6.7432 | 10.726 | 17.148 | 27.5325 | 44.3648 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050643 | 0.21085 | 0.45944 | 0.84835 | 1.4611 | 2.4324 | 3.9804 | 6.4586 | 10.4413 | 16.8073 | 27.0809 | 43.761 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5796 | 10.74 | 23.4028 | 43.2126 | 74.4239 | 123.9015 | 202.7518 | 328.9833 | 531.8536 | 856.1188 | 1379.4289 | 2229.0671 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.3072 | 25.5776 | 38.4109 | 58.4876 | 90.1194 | 140.2636 | 220.1761 | 348.1082 | 553.7116 | 885.2389 | 1421.3245 | 2290.2683 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6144 | 10.8847 | 23.7181 | 43.7947 | 75.4265 | 125.5707 | 205.4833 | 333.4154 | 539.0187 | 867.6524 | 1398.0126 | 2259.0972 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5995 | 5.4056 | 8.231 | 12.6825 | 19.7393 | 30.9855 | 48.9894 | 77.924 | 124.5799 | 200.0234 | 322.3101 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6148 | 17.6716 | 28.9177 | 46.9216 | 75.8563 | 122.105 | 196.7427 | 317.9234 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 15.5578 | 22.9921 | 34.5282 | 52.5755 | 81.0098 | 126.0853 | 197.92 | 312.9204 | 497.7407 | 795.7562 | 1277.6526 | 2058.761 | 2406.8516 | 2406.8516 | 2406.8516 | 2406.8516 | 2406.8516 | 2406.8516 | 2406.8516 | 2406.8516 | 2406.8516 | 2406.8516 |  | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 13.2077 | 15.8088 | 20.9554 | 28.0203 | 37.7618 | 51.249 | 69.9913 | 96.1227 | 132.6653 | 183.9041 | 255.9216 | 357.3608 | 500.5147 | 702.8811 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3501 | 9.7844 | 21.3206 | 39.3678 | 67.8022 | 112.8776 | 184.7124 | 299.7127 | 484.533 | 779.9475 | 1256.6972 | 2030.7407 | 2369.0899 | 2355.6026 | 2336.8603 | 2310.729 | 2274.1864 | 2222.9476 | 2150.9301 | 2049.4908 | 1906.3369 | 1703.9705 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.912 | 32.941 | 71.7792 | 132.5384 | 228.2673 | 380.0215 | 621.8651 | 1009.0331 | 1631.2615 | 2625.8237 | 4230.8815 | 6836.8284 | 7975.9375 | 7930.5304 | 7867.4315 | 7779.4558 | 7656.429 | 7483.925 | 7241.4661 | 6899.9538 | 6418.0023 | 5736.7019
| FALSE | 325 | 22015685 | BAN | BAN002 | 22 | BAN2 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 0.96924 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 9.721 |  | 5.0708 | 0.0089964 | 7.078e-06 | 0.0089893 | 24.7421 | 0.49546 | 25.2376 | 25.5776 | 3.5995 | 16.9225 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 9.721 |  | 40.9792 | 71.3372 | 40.9792 | 30.358 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.7894e-06 | 7.078e-06 | 1.0629e-05 | 1.6185e-05 | 2.4939e-05 | 3.8815e-05 | 6.0929e-05 | 9.6332e-05 | 0.00015323 | 0.00024497 | 0.00039332 | 0.00063378 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 48.2708 | 71.3372 | 107.13 | 163.125 | 251.3476 | 391.2024 | 614.0826 | 970.8919 | 1544.3301 | 2468.9769 | 3964.1473 | 6387.6764 | 7467.6904 | 7467.6904 | 7467.6904 | 7467.6904 | 7467.6904 | 7467.6904 | 7467.6904 | 7467.6904 | 7467.6904 | 7467.6904 |  | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 49.0495 | 65.018 | 86.9379 | 117.1627 | 159.0094 | 217.1606 | 298.2379 | 411.6179 | 570.5955 | 794.0427 | 1108.7763 | 1552.9369 | 2180.8152 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.7419 | 24.7421 | 37.1563 | 56.5772 | 87.1757 | 135.682 | 212.9843 | 336.7377 | 535.6252 | 856.3235 | 1374.8984 | 2215.4591 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.529 | 10.5292 | 22.9433 | 42.3642 | 72.9628 | 121.4691 | 198.7714 | 322.5247 | 521.4122 | 839.3115 | 1352.348 | 2185.3061 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.33526 | 0.49546 | 0.74406 | 1.133 | 1.7457 | 2.717 | 4.265 | 6.7432 | 10.726 | 17.148 | 27.5325 | 44.3648 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050643 | 0.21085 | 0.45944 | 0.84835 | 1.4611 | 2.4324 | 3.9804 | 6.4586 | 10.4413 | 16.8073 | 27.0809 | 43.761 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5796 | 10.74 | 23.4028 | 43.2126 | 74.4239 | 123.9015 | 202.7518 | 328.9833 | 531.8536 | 856.1188 | 1379.4289 | 2229.0671 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.3072 | 25.5776 | 38.4109 | 58.4876 | 90.1194 | 140.2636 | 220.1761 | 348.1082 | 553.7116 | 885.2389 | 1421.3245 | 2290.2683 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6144 | 10.8847 | 23.7181 | 43.7947 | 75.4265 | 125.5707 | 205.4833 | 333.4154 | 539.0187 | 867.6524 | 1398.0126 | 2259.0972 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5995 | 5.4056 | 8.231 | 12.6825 | 19.7393 | 30.9855 | 48.9894 | 77.924 | 124.5799 | 200.0234 | 322.3101 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6148 | 17.6716 | 28.9177 | 46.9216 | 75.8563 | 122.105 | 196.7427 | 317.9234 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 11.4507 | 16.9225 | 25.4132 | 38.6962 | 59.6243 | 92.8004 | 145.6717 | 230.3134 | 366.3434 | 585.6866 | 940.3685 | 1515.2741 | 1771.4732 | 1771.4732 | 1771.4732 | 1771.4732 | 1771.4732 | 1771.4732 | 1771.4732 | 1771.4732 | 1771.4732 | 1771.4732 |  | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 11.6354 | 15.4235 | 20.6233 | 27.7931 | 37.7199 | 51.5145 | 70.7475 | 97.6433 | 135.3557 | 188.3615 | 263.0221 | 368.3851 | 517.3294 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7297 | 7.2015 | 15.6922 | 28.9752 | 49.9033 | 83.0794 | 135.9506 | 220.5924 | 356.6224 | 574.0512 | 924.945 | 1494.6508 | 1743.6801 | 1733.7533 | 1719.9588 | 1700.7257 | 1673.8299 | 1636.1175 | 1583.1117 | 1508.4511 | 1403.0881 | 1254.1438 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2916 | 30.358 | 66.1509 | 122.1458 | 210.3684 | 350.2232 | 573.1034 | 929.9127 | 1503.3509 | 2419.9274 | 3899.1293 | 6300.7385 | 7350.5277 | 7308.6811 | 7250.5299 | 7169.4525 | 7056.0725 | 6897.095 | 6673.6477 | 6358.9141 | 5914.7535 | 5286.8752
| FALSE | 326 | 22015686 | BAN | BAN004 | 22 | BAN4 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 0.96924 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 9.721 |  | 5.0708 | 0.0089964 | 7.078e-06 | 0.0089893 | 24.7421 | 0.49546 | 25.2376 | 25.5776 | 3.5995 | 16.9225 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 9.721 |  | 40.9792 | 71.3372 | 40.9792 | 30.358 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.7894e-06 | 7.078e-06 | 1.0629e-05 | 1.6185e-05 | 2.4939e-05 | 3.8815e-05 | 6.0929e-05 | 9.6332e-05 | 0.00015323 | 0.00024497 | 0.00039332 | 0.00063378 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 48.2708 | 71.3372 | 107.13 | 163.125 | 251.3476 | 391.2024 | 614.0826 | 970.8919 | 1544.3301 | 2468.9769 | 3964.1473 | 6387.6764 | 7467.6904 | 7467.6904 | 7467.6904 | 7467.6904 | 7467.6904 | 7467.6904 | 7467.6904 | 7467.6904 | 7467.6904 | 7467.6904 |  | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 40.9792 | 49.0495 | 65.018 | 86.9379 | 117.1627 | 159.0094 | 217.1606 | 298.2379 | 411.6179 | 570.5955 | 794.0427 | 1108.7763 | 1552.9369 | 2180.8152 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.7419 | 24.7421 | 37.1563 | 56.5772 | 87.1757 | 135.682 | 212.9843 | 336.7377 | 535.6252 | 856.3235 | 1374.8984 | 2215.4591 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.529 | 10.5292 | 22.9433 | 42.3642 | 72.9628 | 121.4691 | 198.7714 | 322.5247 | 521.4122 | 839.3115 | 1352.348 | 2185.3061 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.33526 | 0.49546 | 0.74406 | 1.133 | 1.7457 | 2.717 | 4.265 | 6.7432 | 10.726 | 17.148 | 27.5325 | 44.3648 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050643 | 0.21085 | 0.45944 | 0.84835 | 1.4611 | 2.4324 | 3.9804 | 6.4586 | 10.4413 | 16.8073 | 27.0809 | 43.761 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5796 | 10.74 | 23.4028 | 43.2126 | 74.4239 | 123.9015 | 202.7518 | 328.9833 | 531.8536 | 856.1188 | 1379.4289 | 2229.0671 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.3072 | 25.5776 | 38.4109 | 58.4876 | 90.1194 | 140.2636 | 220.1761 | 348.1082 | 553.7116 | 885.2389 | 1421.3245 | 2290.2683 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6144 | 10.8847 | 23.7181 | 43.7947 | 75.4265 | 125.5707 | 205.4833 | 333.4154 | 539.0187 | 867.6524 | 1398.0126 | 2259.0972 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5995 | 5.4056 | 8.231 | 12.6825 | 19.7393 | 30.9855 | 48.9894 | 77.924 | 124.5799 | 200.0234 | 322.3101 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6148 | 17.6716 | 28.9177 | 46.9216 | 75.8563 | 122.105 | 196.7427 | 317.9234 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 11.4507 | 16.9225 | 25.4132 | 38.6962 | 59.6243 | 92.8004 | 145.6717 | 230.3134 | 366.3434 | 585.6866 | 940.3685 | 1515.2741 | 1771.4732 | 1771.4732 | 1771.4732 | 1771.4732 | 1771.4732 | 1771.4732 | 1771.4732 | 1771.4732 | 1771.4732 | 1771.4732 |  | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 9.721 | 11.6354 | 15.4235 | 20.6233 | 27.7931 | 37.7199 | 51.5145 | 70.7475 | 97.6433 | 135.3557 | 188.3615 | 263.0221 | 368.3851 | 517.3294 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7297 | 7.2015 | 15.6922 | 28.9752 | 49.9033 | 83.0794 | 135.9506 | 220.5924 | 356.6224 | 574.0512 | 924.945 | 1494.6508 | 1743.6801 | 1733.7533 | 1719.9588 | 1700.7257 | 1673.8299 | 1636.1175 | 1583.1117 | 1508.4511 | 1403.0881 | 1254.1438 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2916 | 30.358 | 66.1509 | 122.1458 | 210.3684 | 350.2232 | 573.1034 | 929.9127 | 1503.3509 | 2419.9274 | 3899.1293 | 6300.7385 | 7350.5277 | 7308.6811 | 7250.5299 | 7169.4525 | 7056.0725 | 6897.095 | 6673.6477 | 6358.9141 | 5914.7535 | 5286.8752
| FALSE | 327 | 22015687 | BAN | BAN005 | 22 | BAN5 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 0.96924 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 9.3185 |  | 5.0708 | 0.0089964 | 7.078e-06 | 0.0089893 | 24.7421 | 0.49546 | 25.2376 | 25.5776 | 3.5995 | 16.2219 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 9.3185 |  | 40.5767 | 70.6365 | 40.5767 | 30.0598 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.7894e-06 | 7.078e-06 | 1.0629e-05 | 1.6185e-05 | 2.4939e-05 | 3.8815e-05 | 6.0929e-05 | 9.6332e-05 | 0.00015323 | 0.00024497 | 0.00039332 | 0.00063378 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 47.7967 | 70.6365 | 106.0779 | 161.5229 | 248.879 | 387.3603 | 608.0515 | 961.3564 | 1529.1628 | 2444.7283 | 3925.2143 | 6324.9412 | 7394.348 | 7394.348 | 7394.348 | 7394.348 | 7394.348 | 7394.348 | 7394.348 | 7394.348 | 7394.348 | 7394.348 |  | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 40.5767 | 48.5678 | 64.3795 | 86.0841 | 116.012 | 157.4477 | 215.0278 | 295.3088 | 407.5753 | 564.9915 | 786.2442 | 1097.8867 | 1537.6851 | 2159.3968 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.7419 | 24.7421 | 37.1563 | 56.5772 | 87.1757 | 135.682 | 212.9843 | 336.7377 | 535.6252 | 856.3235 | 1374.8984 | 2215.4591 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.529 | 10.5292 | 22.9433 | 42.3642 | 72.9628 | 121.4691 | 198.7714 | 322.5247 | 521.4122 | 839.3115 | 1352.348 | 2185.3061 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.33526 | 0.49546 | 0.74406 | 1.133 | 1.7457 | 2.717 | 4.265 | 6.7432 | 10.726 | 17.148 | 27.5325 | 44.3648 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050643 | 0.21085 | 0.45944 | 0.84835 | 1.4611 | 2.4324 | 3.9804 | 6.4586 | 10.4413 | 16.8073 | 27.0809 | 43.761 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5796 | 10.74 | 23.4028 | 43.2126 | 74.4239 | 123.9015 | 202.7518 | 328.9833 | 531.8536 | 856.1188 | 1379.4289 | 2229.0671 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.3072 | 25.5776 | 38.4109 | 58.4876 | 90.1194 | 140.2636 | 220.1761 | 348.1082 | 553.7116 | 885.2389 | 1421.3245 | 2290.2683 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6144 | 10.8847 | 23.7181 | 43.7947 | 75.4265 | 125.5707 | 205.4833 | 333.4154 | 539.0187 | 867.6524 | 1398.0126 | 2259.0972 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5995 | 5.4056 | 8.231 | 12.6825 | 19.7393 | 30.9855 | 48.9894 | 77.924 | 124.5799 | 200.0234 | 322.3101 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6148 | 17.6716 | 28.9177 | 46.9216 | 75.8563 | 122.105 | 196.7427 | 317.9234 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 10.9766 | 16.2219 | 24.3611 | 37.0941 | 57.1557 | 88.9583 | 139.6406 | 220.778 | 351.1761 | 561.4381 | 901.4354 | 1452.5388 | 1698.1308 | 1698.1308 | 1698.1308 | 1698.1308 | 1698.1308 | 1698.1308 | 1698.1308 | 1698.1308 | 1698.1308 | 1698.1308 |  | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 9.3185 | 11.1537 | 14.7849 | 19.7694 | 26.6425 | 36.1583 | 49.3817 | 67.8184 | 93.6007 | 129.7517 | 180.563 | 252.1325 | 353.1333 | 495.911 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6581 | 6.9033 | 15.0425 | 27.7756 | 47.8372 | 79.6397 | 130.322 | 211.4594 | 341.8576 | 550.2844 | 886.6505 | 1432.7694 | 1671.4884 | 1661.9726 | 1648.7492 | 1630.3124 | 1604.5301 | 1568.3791 | 1517.5679 | 1445.9984 | 1344.9975 | 1202.2199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.22 | 30.0598 | 65.5012 | 120.9462 | 208.3023 | 346.7836 | 567.4748 | 920.7797 | 1488.5861 | 2396.1606 | 3860.8348 | 6238.8571 | 7278.336 | 7236.9003 | 7179.3203 | 7099.0392 | 6986.7727 | 6829.3566 | 6608.1038 | 6296.4613 | 5856.6629 | 5234.9513
| FALSE | 328 | 22015688 | BAN | BAN006 | 22 | BAN6 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 0.96924 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 4.8605 |  | 5.0708 | 0.0089964 | 7.078e-06 | 0.0089893 | 24.7421 | 0.49546 | 25.2376 | 25.5776 | 3.5995 | 8.4612 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 4.8605 |  | 36.1187 | 62.8759 | 36.1187 | 26.7573 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.7894e-06 | 7.078e-06 | 1.0629e-05 | 1.6185e-05 | 2.4939e-05 | 3.8815e-05 | 6.0929e-05 | 9.6332e-05 | 0.00015323 | 0.00024497 | 0.00039332 | 0.00063378 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 42.5454 | 62.8759 | 94.4234 | 143.7768 | 221.5355 | 344.8022 | 541.2467 | 855.7352 | 1361.1584 | 2176.1336 | 3493.9631 | 5630.0394 | 6581.9538 | 6581.9538 | 6581.9538 | 6581.9538 | 6581.9538 | 6581.9538 | 6581.9538 | 6581.9538 | 6581.9538 | 6581.9538 |  | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 43.2318 | 57.3063 | 76.6263 | 103.2662 | 140.1494 | 191.4033 | 262.8641 | 362.7962 | 502.9176 | 699.862 | 977.2653 | 1368.7444 | 1922.1505 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.7419 | 24.7421 | 37.1563 | 56.5772 | 87.1757 | 135.682 | 212.9843 | 336.7377 | 535.6252 | 856.3235 | 1374.8984 | 2215.4591 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.529 | 10.5292 | 22.9433 | 42.3642 | 72.9628 | 121.4691 | 198.7714 | 322.5247 | 521.4122 | 839.3115 | 1352.348 | 2185.3061 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.33526 | 0.49546 | 0.74406 | 1.133 | 1.7457 | 2.717 | 4.265 | 6.7432 | 10.726 | 17.148 | 27.5325 | 44.3648 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050643 | 0.21085 | 0.45944 | 0.84835 | 1.4611 | 2.4324 | 3.9804 | 6.4586 | 10.4413 | 16.8073 | 27.0809 | 43.761 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5796 | 10.74 | 23.4028 | 43.2126 | 74.4239 | 123.9015 | 202.7518 | 328.9833 | 531.8536 | 856.1188 | 1379.4289 | 2229.0671 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.3072 | 25.5776 | 38.4109 | 58.4876 | 90.1194 | 140.2636 | 220.1761 | 348.1082 | 553.7116 | 885.2389 | 1421.3245 | 2290.2683 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6144 | 10.8847 | 23.7181 | 43.7947 | 75.4265 | 125.5707 | 205.4833 | 333.4154 | 539.0187 | 867.6524 | 1398.0126 | 2259.0972 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5995 | 5.4056 | 8.231 | 12.6825 | 19.7393 | 30.9855 | 48.9894 | 77.924 | 124.5799 | 200.0234 | 322.3101 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6148 | 17.6716 | 28.9177 | 46.9216 | 75.8563 | 122.105 | 196.7427 | 317.9234 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 5.7254 | 8.4612 | 12.7066 | 19.3481 | 29.8121 | 46.4002 | 72.8358 | 115.1567 | 183.1717 | 292.8433 | 470.1843 | 757.637 | 885.7366 | 885.7366 | 885.7366 | 885.7366 | 885.7366 | 885.7366 | 885.7366 | 885.7366 | 885.7366 | 885.7366 |  | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 5.8177 | 7.7117 | 10.3116 | 13.8966 | 18.86 | 25.7572 | 35.3738 | 48.8217 | 67.6779 | 94.1808 | 131.511 | 184.1926 | 258.6647 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86485 | 3.6007 | 7.8461 | 14.4876 | 24.9516 | 41.5397 | 67.9753 | 110.2962 | 178.3112 | 287.0256 | 462.4725 | 747.3254 | 871.84 | 866.8766 | 859.9794 | 850.3629 | 836.915 | 818.0588 | 791.5559 | 754.2256 | 701.544 | 627.0719 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4268 | 26.7573 | 58.3048 | 107.6582 | 185.4168 | 308.6835 | 505.1281 | 819.6165 | 1325.0397 | 2132.9018 | 3436.6568 | 5553.4131 | 6478.6877 | 6441.8044 | 6390.5505 | 6319.0897 | 6219.1576 | 6079.0362 | 5882.0919 | 5604.6885 | 5213.2095 | 4659.8033
| FALSE | 329 | 22016128 | BAN | BAN007 | 22 | BAN7 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 0.96924 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 4.6593 |  | 5.0708 | 0.0089964 | 7.078e-06 | 0.0089893 | 24.7421 | 0.49546 | 25.2376 | 25.5776 | 3.5995 | 8.1109 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 4.6593 |  | 35.9174 | 62.5256 | 35.9174 | 26.6082 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.7894e-06 | 7.078e-06 | 1.0629e-05 | 1.6185e-05 | 2.4939e-05 | 3.8815e-05 | 6.0929e-05 | 9.6332e-05 | 0.00015323 | 0.00024497 | 0.00039332 | 0.00063378 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 42.3084 | 62.5256 | 93.8974 | 142.9758 | 220.3012 | 342.8811 | 538.2312 | 850.9675 | 1353.5747 | 2164.0093 | 3474.4965 | 5598.6718 | 6545.2826 | 6545.2826 | 6545.2826 | 6545.2826 | 6545.2826 | 6545.2826 | 6545.2826 | 6545.2826 | 6545.2826 | 6545.2826 |  | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 35.9174 | 42.9909 | 56.987 | 76.1993 | 102.6908 | 139.3686 | 190.3369 | 261.3996 | 360.7749 | 500.1156 | 695.9627 | 971.8205 | 1361.1184 | 1911.4413 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.7419 | 24.7421 | 37.1563 | 56.5772 | 87.1757 | 135.682 | 212.9843 | 336.7377 | 535.6252 | 856.3235 | 1374.8984 | 2215.4591 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.529 | 10.5292 | 22.9433 | 42.3642 | 72.9628 | 121.4691 | 198.7714 | 322.5247 | 521.4122 | 839.3115 | 1352.348 | 2185.3061 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.33526 | 0.49546 | 0.74406 | 1.133 | 1.7457 | 2.717 | 4.265 | 6.7432 | 10.726 | 17.148 | 27.5325 | 44.3648 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050643 | 0.21085 | 0.45944 | 0.84835 | 1.4611 | 2.4324 | 3.9804 | 6.4586 | 10.4413 | 16.8073 | 27.0809 | 43.761 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5796 | 10.74 | 23.4028 | 43.2126 | 74.4239 | 123.9015 | 202.7518 | 328.9833 | 531.8536 | 856.1188 | 1379.4289 | 2229.0671 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.3072 | 25.5776 | 38.4109 | 58.4876 | 90.1194 | 140.2636 | 220.1761 | 348.1082 | 553.7116 | 885.2389 | 1421.3245 | 2290.2683 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6144 | 10.8847 | 23.7181 | 43.7947 | 75.4265 | 125.5707 | 205.4833 | 333.4154 | 539.0187 | 867.6524 | 1398.0126 | 2259.0972 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5995 | 5.4056 | 8.231 | 12.6825 | 19.7393 | 30.9855 | 48.9894 | 77.924 | 124.5799 | 200.0234 | 322.3101 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6148 | 17.6716 | 28.9177 | 46.9216 | 75.8563 | 122.105 | 196.7427 | 317.9234 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 5.4883 | 8.1109 | 12.1805 | 18.5471 | 28.5779 | 44.4791 | 69.8203 | 110.389 | 175.5881 | 280.719 | 450.7177 | 726.2694 | 849.0654 | 849.0654 | 849.0654 | 849.0654 | 849.0654 | 849.0654 | 849.0654 | 849.0654 | 849.0654 | 849.0654 |  | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 4.6593 | 5.5769 | 7.3925 | 9.8847 | 13.3212 | 18.0791 | 24.6908 | 33.9092 | 46.8004 | 64.8759 | 90.2815 | 126.0662 | 176.5666 | 247.9555 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82905 | 3.4517 | 7.5213 | 13.8878 | 23.9186 | 39.8199 | 65.161 | 105.7297 | 170.9288 | 275.1422 | 443.3253 | 716.3847 | 835.7442 | 830.9863 | 824.3746 | 815.1562 | 802.2651 | 784.1895 | 758.7839 | 722.9992 | 672.4988 | 601.1099 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.391 | 26.6082 | 57.9799 | 107.0584 | 184.3838 | 306.9637 | 502.3138 | 815.05 | 1317.6573 | 2121.0184 | 3417.5095 | 5522.4724 | 6442.5918 | 6405.9141 | 6354.9457 | 6283.883 | 6184.5077 | 6045.167 | 5849.3199 | 5573.4621 | 5184.1642 | 4633.8413
| FALSE | 330 | 22015689 | BAN | BAN008 | 22 | BAN8 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 0.96924 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 4.8605 |  | 5.0708 | 0.0089964 | 7.078e-06 | 0.0089893 | 24.7421 | 0.49546 | 25.2376 | 25.5776 | 3.5995 | 8.4612 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 4.8605 |  | 36.1187 | 62.8759 | 36.1187 | 26.7573 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.7894e-06 | 7.078e-06 | 1.0629e-05 | 1.6185e-05 | 2.4939e-05 | 3.8815e-05 | 6.0929e-05 | 9.6332e-05 | 0.00015323 | 0.00024497 | 0.00039332 | 0.00063378 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 42.5454 | 62.8759 | 94.4234 | 143.7768 | 221.5355 | 344.8022 | 541.2467 | 855.7352 | 1361.1584 | 2176.1336 | 3493.9631 | 5630.0394 | 6581.9538 | 6581.9538 | 6581.9538 | 6581.9538 | 6581.9538 | 6581.9538 | 6581.9538 | 6581.9538 | 6581.9538 | 6581.9538 |  | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 36.1187 | 43.2318 | 57.3063 | 76.6263 | 103.2662 | 140.1494 | 191.4033 | 262.8641 | 362.7962 | 502.9176 | 699.862 | 977.2653 | 1368.7444 | 1922.1505 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.7419 | 24.7421 | 37.1563 | 56.5772 | 87.1757 | 135.682 | 212.9843 | 336.7377 | 535.6252 | 856.3235 | 1374.8984 | 2215.4591 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.529 | 10.5292 | 22.9433 | 42.3642 | 72.9628 | 121.4691 | 198.7714 | 322.5247 | 521.4122 | 839.3115 | 1352.348 | 2185.3061 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.33526 | 0.49546 | 0.74406 | 1.133 | 1.7457 | 2.717 | 4.265 | 6.7432 | 10.726 | 17.148 | 27.5325 | 44.3648 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050643 | 0.21085 | 0.45944 | 0.84835 | 1.4611 | 2.4324 | 3.9804 | 6.4586 | 10.4413 | 16.8073 | 27.0809 | 43.761 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5796 | 10.74 | 23.4028 | 43.2126 | 74.4239 | 123.9015 | 202.7518 | 328.9833 | 531.8536 | 856.1188 | 1379.4289 | 2229.0671 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.3072 | 25.5776 | 38.4109 | 58.4876 | 90.1194 | 140.2636 | 220.1761 | 348.1082 | 553.7116 | 885.2389 | 1421.3245 | 2290.2683 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6144 | 10.8847 | 23.7181 | 43.7947 | 75.4265 | 125.5707 | 205.4833 | 333.4154 | 539.0187 | 867.6524 | 1398.0126 | 2259.0972 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5995 | 5.4056 | 8.231 | 12.6825 | 19.7393 | 30.9855 | 48.9894 | 77.924 | 124.5799 | 200.0234 | 322.3101 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6148 | 17.6716 | 28.9177 | 46.9216 | 75.8563 | 122.105 | 196.7427 | 317.9234 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 5.7254 | 8.4612 | 12.7066 | 19.3481 | 29.8121 | 46.4002 | 72.8358 | 115.1567 | 183.1717 | 292.8433 | 470.1843 | 757.637 | 885.7366 | 885.7366 | 885.7366 | 885.7366 | 885.7366 | 885.7366 | 885.7366 | 885.7366 | 885.7366 | 885.7366 |  | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 4.8605 | 5.8177 | 7.7117 | 10.3116 | 13.8966 | 18.86 | 25.7572 | 35.3738 | 48.8217 | 67.6779 | 94.1808 | 131.511 | 184.1926 | 258.6647 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86485 | 3.6007 | 7.8461 | 14.4876 | 24.9516 | 41.5397 | 67.9753 | 110.2962 | 178.3112 | 287.0256 | 462.4725 | 747.3254 | 871.84 | 866.8766 | 859.9794 | 850.3629 | 836.915 | 818.0588 | 791.5559 | 754.2256 | 701.544 | 627.0719 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4268 | 26.7573 | 58.3048 | 107.6582 | 185.4168 | 308.6835 | 505.1281 | 819.6165 | 1325.0397 | 2132.9018 | 3436.6568 | 5553.4131 | 6478.6877 | 6441.8044 | 6390.5505 | 6319.0897 | 6219.1576 | 6079.0362 | 5882.0919 | 5604.6885 | 5213.2095 | 4659.8033
| FALSE | 331 | 22016137 | BAN | Blank | 22 | STATION EARTH FAULT MGMT | STATION EARTH FAULT MGMT EXTENSION | Blank | Schweitzer | SEL_451 | SEL 451 | SEL 400s | Digital |  | 0.81881 | 1 |  | 0.8077 | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 7.6623 |  | 2.6788 | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 7.6623 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 7.6623 |  | 39.0519 | 39.0519 | 39.0519 | 0 |  | 0.11989 |  | 0.91058 | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 |  | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 6.9382e-06 | 9.197e-06 | 1.2298e-05 | 1.6573e-05 | 2.2492e-05 | 3.0718e-05 | 4.2187e-05 | 5.8225e-05 | 8.0713e-05 | 0.00011232 | 0.00015684 | 0.00021967 | 0.00030848 | 0.00043423 | 0.00061249 | 0.00086551 | 0.0010563 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 46.7427 | 61.9602 | 82.8492 | 111.6525 | 151.5311 | 206.9475 | 284.2117 | 392.2594 | 543.7602 | 756.6987 | 1056.6303 | 1479.9019 | 2078.2508 | 2925.3758 | 4126.3274 | 5830.9318 | 7116.4829 |  | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 46.7427 | 61.9602 | 82.8492 | 111.6525 | 151.5311 | 206.9475 | 284.2117 | 392.2594 | 543.7602 | 756.6987 | 1056.6303 | 1479.9019 | 2078.2508 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 | 1064.7262 | 1501.8271 | 2122.2387 | 2590.1307 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7992 | 8.3378 | 15.9406 | 26.4239 | 38.139 | 52.7699 | 73.2883 | 102.1303 | 142.7566 | 200.0887 | 281.1312 | 395.8607 | 558.4966 | 789.3165 | 1117.2537 | 1583.6104 | 1833.726 |  | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.48568 | 0.64379 | 0.86084 | 1.1601 | 1.5745 | 2.1503 | 2.9531 | 4.0757 | 5.6499 | 7.8624 | 10.9788 | 15.3768 | 21.5939 | 30.3959 | 42.8743 | 60.5859 | 73.9433 |  | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.48568 | 0.64379 | 0.86084 | 1.1601 | 1.5745 | 2.1503 | 2.9531 | 4.0757 | 5.6499 | 7.8624 | 10.9788 | 15.3768 | 21.5939 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079911 | 0.23803 | 0.45507 | 0.75435 | 1.0888 | 1.5065 | 2.0922 | 2.9156 | 4.0754 | 5.7122 | 8.0258 | 11.3011 | 15.944 | 22.5335 | 31.8955 | 45.2091 | 52.3494 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8791 | 8.5758 | 16.3956 | 27.1782 | 39.2278 | 54.2764 | 75.3806 | 105.0459 | 146.832 | 205.8008 | 289.1569 | 407.1618 | 574.4406 | 811.85 | 1149.1491 | 1628.8195 | 1886.0754 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 | 1101.3779 | 1553.5254 | 2195.2938 | 2679.2923 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8955 | 8.6248 | 16.4893 | 27.3335 | 39.4519 | 54.5864 | 75.8112 | 105.646 | 147.6707 | 206.9764 | 290.8087 | 409.4877 | 577.722 | 816.4876 | 1155.7135 | 1638.1239 | 1896.8494 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 | 154.895 | 218.4838 | 308.7405 | 376.8088 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40722 | 1.213 | 2.319 | 3.8441 | 5.5484 | 7.6769 | 10.6619 | 14.8578 | 20.768 | 29.1086 | 40.8986 | 57.5893 | 81.2493 | 114.8287 | 162.5366 | 230.3815 | 266.768 |  | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 9.1713 | 12.1571 | 16.2556 | 21.9071 | 29.7316 | 40.6047 | 55.7645 | 76.9643 | 106.6899 | 148.47 | 207.3189 | 290.368 | 407.7686 | 573.9809 | 809.6167 | 1144.073 | 1396.3078 |  | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 9.1713 | 12.1571 | 16.2556 | 21.9071 | 29.7316 | 40.6047 | 55.7645 | 76.9643 | 106.6899 | 148.47 | 207.3189 | 290.368 | 407.7686 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.509 | 4.4948 | 8.5934 | 14.2448 | 20.5603 | 28.4476 | 39.5088 | 55.0572 | 76.9583 | 107.8654 | 151.5544 | 213.4037 | 301.0787 | 425.5109 | 602.2978 | 853.705 | 988.5393 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6908 | 22.9083 | 43.7973 | 72.6006 | 104.7884 | 144.9873 | 201.3625 | 280.6069 | 392.2291 | 549.7512 | 772.4186 | 1087.6425 | 1534.4906 | 2168.6772 | 3069.6971 | 4351.03 | 5038.232
| FALSE | 332 | 22016136 | BAN | Blank | 22 | STATION EARTH FAULT MGMT | STATION EARTH FAULT MGMT | Blank | Schweitzer | SEL_451 | SEL 451 | SEL 400s | Digital |  | 0.81881 | 1 |  | 0.8077 | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 7.6623 |  | 2.6788 | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 7.6623 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 7.6623 |  | 39.0519 | 39.0519 | 39.0519 | 0 |  | 0.11989 |  | 0.91058 | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 |  | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 6.9382e-06 | 9.197e-06 | 1.2298e-05 | 1.6573e-05 | 2.2492e-05 | 3.0718e-05 | 4.2187e-05 | 5.8225e-05 | 8.0713e-05 | 0.00011232 | 0.00015684 | 0.00021967 | 0.00030848 | 0.00043423 | 0.00061249 | 0.00086551 | 0.0010563 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 46.7427 | 61.9602 | 82.8492 | 111.6525 | 151.5311 | 206.9475 | 284.2117 | 392.2594 | 543.7602 | 756.6987 | 1056.6303 | 1479.9019 | 2078.2508 | 2925.3758 | 4126.3274 | 5830.9318 | 7116.4829 |  | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 39.0519 | 46.7427 | 61.9602 | 82.8492 | 111.6525 | 151.5311 | 206.9475 | 284.2117 | 392.2594 | 543.7602 | 756.6987 | 1056.6303 | 1479.9019 | 2078.2508 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 | 1064.7262 | 1501.8271 | 2122.2387 | 2590.1307 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7992 | 8.3378 | 15.9406 | 26.4239 | 38.139 | 52.7699 | 73.2883 | 102.1303 | 142.7566 | 200.0887 | 281.1312 | 395.8607 | 558.4966 | 789.3165 | 1117.2537 | 1583.6104 | 1833.726 |  | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.48568 | 0.64379 | 0.86084 | 1.1601 | 1.5745 | 2.1503 | 2.9531 | 4.0757 | 5.6499 | 7.8624 | 10.9788 | 15.3768 | 21.5939 | 30.3959 | 42.8743 | 60.5859 | 73.9433 |  | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.48568 | 0.64379 | 0.86084 | 1.1601 | 1.5745 | 2.1503 | 2.9531 | 4.0757 | 5.6499 | 7.8624 | 10.9788 | 15.3768 | 21.5939 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079911 | 0.23803 | 0.45507 | 0.75435 | 1.0888 | 1.5065 | 2.0922 | 2.9156 | 4.0754 | 5.7122 | 8.0258 | 11.3011 | 15.944 | 22.5335 | 31.8955 | 45.2091 | 52.3494 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8791 | 8.5758 | 16.3956 | 27.1782 | 39.2278 | 54.2764 | 75.3806 | 105.0459 | 146.832 | 205.8008 | 289.1569 | 407.1618 | 574.4406 | 811.85 | 1149.1491 | 1628.8195 | 1886.0754 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 | 1101.3779 | 1553.5254 | 2195.2938 | 2679.2923 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8955 | 8.6248 | 16.4893 | 27.3335 | 39.4519 | 54.5864 | 75.8112 | 105.646 | 147.6707 | 206.9764 | 290.8087 | 409.4877 | 577.722 | 816.4876 | 1155.7135 | 1638.1239 | 1896.8494 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 | 154.895 | 218.4838 | 308.7405 | 376.8088 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40722 | 1.213 | 2.319 | 3.8441 | 5.5484 | 7.6769 | 10.6619 | 14.8578 | 20.768 | 29.1086 | 40.8986 | 57.5893 | 81.2493 | 114.8287 | 162.5366 | 230.3815 | 266.768 |  | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 9.1713 | 12.1571 | 16.2556 | 21.9071 | 29.7316 | 40.6047 | 55.7645 | 76.9643 | 106.6899 | 148.47 | 207.3189 | 290.368 | 407.7686 | 573.9809 | 809.6167 | 1144.073 | 1396.3078 |  | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 7.6623 | 9.1713 | 12.1571 | 16.2556 | 21.9071 | 29.7316 | 40.6047 | 55.7645 | 76.9643 | 106.6899 | 148.47 | 207.3189 | 290.368 | 407.7686 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.509 | 4.4948 | 8.5934 | 14.2448 | 20.5603 | 28.4476 | 39.5088 | 55.0572 | 76.9583 | 107.8654 | 151.5544 | 213.4037 | 301.0787 | 425.5109 | 602.2978 | 853.705 | 988.5393 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6908 | 22.9083 | 43.7973 | 72.6006 | 104.7884 | 144.9873 | 201.3625 | 280.6069 | 392.2291 | 549.7512 | 772.4186 | 1087.6425 | 1534.4906 | 2168.6772 | 3069.6971 | 4351.03 | 5038.232
| FALSE | 333 | 22015677 | BAN | Blank | 22 | STATION STATION CONTROL | VRR & TRANS CONTROL | C | Schweitzer | SEL_451 | SEL 451 | SEL 400s | Digital |  | 0 | 1 |  | 0.8077 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 2.6788 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 30.9493 | 30.9493 | 0 |  | 0.11989 |  | 0.91058 | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 38.1347 | 52.764 | 73.2801 | 102.1188 | 142.7405 | 200.0662 | 281.0996 | 395.8163 | 558.4339 | 789.228 | 1117.1284 | 1583.4328 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 38.1347 | 52.764 | 73.2801 | 102.1188 | 142.7405 | 200.0662 | 281.0996 | 395.8163 | 558.4339 | 789.228 | 1117.1284 | 1583.4328 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 39.3636 | 54.4642 | 75.6415 | 105.4095 | 147.3402 | 206.5131 | 290.1578 | 408.5711 | 576.4289 | 814.6601 | 1153.1267 | 1634.4573 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.5483 | 7.6767 | 10.6616 | 14.8574 | 20.7675 | 29.1078 | 40.8974 | 57.5877 | 81.2471 | 114.8255 | 162.532 | 230.3751 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 83.0466 | 114.9049 | 159.5832 | 222.3857 | 310.8482 | 435.6872 | 612.1549 | 861.9751 | 1216.1099 | 1718.7135 | 2432.7871 | 3448.2652 | 3992.8845
| TRUE | 334 | 22004423 | BAN | Blank | 22 | TRANS NO.1 | DIFFERENTIAL | Y | Brown Boveri | D21SE3_2195 | D21SE3 2195 | D21 | Electronic |  | 0.0068096 | 2190 |  | 5.5 | 0.0093284 | 0.000188 | 0.0091404 | 98.1453 | 82.7196 | 180.865 | 27.547 | 3.7342 | 10.8106 |  | 7.9766 | 0.024052 | 0.00048474 | 0.023568 | 253.0588 | 213.285 | 466.3438 | 71.0274 | 9.6282 | 27.8741 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.0027721 |  | 222.9567 | 574.8735 | 71.0251 | 503.8484 |  | 0.037177 |  | 5.7083 | 5.9245 | 6.1489 | 6.3818 | 6.6235 | 6.8744 | 7.1348 | 7.405 | 7.6855 | 7.9766 | 8.2787 | 8.5923 | 8.9178 | 9.2555 | 9.6061 | 9.9699 | 10.3476 | 10.7395 | 11.1463 | 11.5684 | 12.0066 | 12.4614 | 12.9334 | 13.4232 | 13.9317 | 14.4594 | 15.007 | 15.5754 | 16.1654 | 16.7777 |  | 0.010224 | 0.011215 | 0.01231 | 0.013521 | 0.01486 | 0.016343 | 0.017985 | 0.019804 | 0.021819 | 0.024052 | 0.026528 | 0.029274 | 0.03232 | 0.035699 | 0.03945 | 0.043614 | 0.048239 | 0.053375 | 0.059081 | 0.065422 | 0.072469 | 0.080304 | 0.089016 | 0.098705 | 0.10948 | 0.12147 | 0.13481 | 0.14966 | 0.16619 | 0.18459 |  | 0.00020606 | 0.00022602 | 0.00024808 | 0.00027249 | 0.00029949 | 0.00032938 | 0.00036247 | 0.00039912 | 0.00043973 | 0.00048474 | 0.00053464 | 0.00058997 | 0.00065135 | 0.00071946 | 0.00079506 | 0.00087898 | 0.00097218 | 0.0010757 | 0.0011907 | 0.0013185 | 0.0014605 | 0.0016184 | 0.001794 | 0.0019892 | 0.0022064 | 0.0024481 | 0.002717 | 0.0030162 | 0.0033494 | 0.0037202 | 244.373 | 268.0416 | 294.2099 | 323.1529 | 355.1766 | 390.6217 | 429.8673 | 473.3355 | 521.4965 | 574.8735 | 634.0497 | 699.6744 | 772.4711 | 853.2458 | 942.8969 | 1042.4254 | 1152.9471 | 1275.7058 | 1412.088 | 1563.6397 | 1732.0847 | 1919.3452 | 2127.565 | 2359.1353 | 2616.723 | 2903.3033 | 3222.1955 | 3577.1027 | 3972.1569 | 4411.9686 |  | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 52.538 | 69.6422 | 93.1211 | 125.4956 | 170.3185 | 232.6055 | 319.4493 | 440.8931 | 611.1775 | 850.5168 | 1187.635 | 1663.3854 | 2335.9197 |  | 107.5728 | 117.9917 | 129.511 | 142.2516 | 156.3484 | 171.9513 | 189.2272 | 208.3619 | 229.5623 | 253.0588 | 279.1081 | 307.9961 | 340.0411 | 375.5981 | 415.0624 | 458.8748 | 507.5263 | 561.5646 | 621.5999 | 688.3128 | 762.4622 | 844.8941 | 936.5523 | 1038.4893 | 1151.8791 | 1278.0316 | 1418.4076 | 1574.6375 | 1748.5399 | 1942.1447 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 80.4411 | 90.86 | 102.3793 | 115.1199 | 129.2167 | 144.8196 | 162.0955 | 181.2302 | 202.4306 | 225.9271 | 251.9764 | 280.8644 | 312.9094 | 348.4664 | 387.9307 | 431.7431 | 480.3946 | 529.0896 | 578.5525 | 630.7526 | 684.8905 | 739.6164 | 792.7735 | 841.0305 | 879.3531 | 900.2489 | 892.6839 | 840.5334 | 720.3639 | 498.2599 |  | 90.6653 | 99.4467 | 109.1554 | 119.8936 | 131.7748 | 144.9254 | 159.486 | 175.6132 | 193.4815 | 213.285 | 235.2401 | 259.5877 | 286.5961 | 316.5645 | 349.8261 | 386.7524 | 427.7573 | 473.3023 | 523.9017 | 580.1292 | 642.6244 | 712.1003 | 789.3523 | 875.2677 | 970.8358 | 1077.1606 | 1195.4735 | 1327.1483 | 1473.7182 | 1636.8937 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 90.6441 | 99.4255 | 109.1342 | 119.8724 | 131.7536 | 144.9042 | 159.4647 | 175.592 | 193.4603 | 213.2638 | 235.2189 | 259.5664 | 286.5749 | 316.5433 | 349.8049 | 386.7312 | 427.7361 | 473.2769 | 523.8681 | 580.0842 | 642.5637 | 712.018 | 789.2399 | 875.1133 | 970.6228 | 1076.8653 | 1195.0624 | 1326.5744 | 1472.9144 | 1635.7648 |  | 171.0852 | 190.2855 | 211.5135 | 234.9924 | 260.9704 | 289.7238 | 321.5603 | 356.8222 | 395.8909 | 439.1909 | 487.1953 | 540.4308 | 599.4843 | 665.0097 | 737.7356 | 818.4743 | 908.1307 | 1002.3665 | 1102.4205 | 1210.8368 | 1327.4542 | 1451.6343 | 1582.0135 | 1716.1438 | 1849.9759 | 1977.1142 | 2087.7464 | 2167.1078 | 2193.2782 | 2134.0248 |  | 30.193 | 33.1174 | 36.3506 | 39.9265 | 43.8832 | 48.2625 | 53.1114 | 58.4821 | 64.4325 | 71.0274 | 78.3388 | 86.4469 | 95.4412 | 105.4212 | 116.4978 | 128.7949 | 142.4502 | 157.6174 | 174.4679 | 193.1925 | 214.0044 | 237.1411 | 262.8673 | 291.4785 | 323.3042 | 358.7121 | 398.1122 | 441.9621 | 490.7723 | 545.1124 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 15.523 | 18.4473 | 21.6805 | 25.2565 | 29.2131 | 33.5925 | 38.4414 | 43.812 | 49.7624 | 56.3573 | 63.6687 | 71.7769 | 80.7711 | 90.7511 | 101.8278 | 114.1248 | 127.7801 | 140.0583 | 151.1922 | 162.0698 | 172.0616 | 180.2176 | 185.1263 | 184.7128 | 175.9499 | 154.4457 | 113.8543 | 45.0333 | -65.1608 | -235.5937 |  | 4.0929 | 4.4893 | 4.9275 | 5.4123 | 5.9486 | 6.5423 | 7.1996 | 7.9276 | 8.7342 | 9.6282 | 10.6193 | 11.7184 | 12.9376 | 14.2905 | 15.792 | 17.4589 | 19.31 | 21.366 | 23.6502 | 26.1884 | 29.0096 | 32.1459 | 35.6333 | 39.5117 | 43.8259 | 48.6256 | 53.9665 | 59.9107 | 66.5272 | 73.8933 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 2.0252 | 2.4216 | 2.8598 | 3.3446 | 3.8809 | 4.4746 | 5.1319 | 5.8599 | 6.6665 | 7.5605 | 8.5516 | 9.6507 | 10.8699 | 12.2228 | 13.7243 | 15.3912 | 17.2423 | 18.8911 | 20.3696 | 21.8018 | 23.0979 | 24.1228 | 24.676 | 24.4635 | 23.0568 | 19.835 | 13.9014 | 3.965 | -11.8296 | -36.1444 |  | 11.849 | 12.9966 | 14.2655 | 15.6688 | 17.2216 | 18.9402 | 20.8431 | 22.9508 | 25.286 | 27.8741 | 30.7434 | 33.9253 | 37.4551 | 41.3716 | 45.7185 | 50.5444 | 55.9033 | 61.8556 | 68.4684 | 75.8167 | 83.9842 | 93.0639 | 103.1599 | 114.3882 | 126.8779 | 140.7734 | 156.2356 | 173.4441 | 192.5993 | 213.9246 |  | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.003318 | 0.0043982 | 0.005881 | 0.0079256 | 0.010756 | 0.01469 | 0.020175 | 0.027844 | 0.038599 | 0.053714 | 0.075004 | 0.10505 | 0.14752 |  | 11.8462 | 12.9938 | 14.2627 | 15.666 | 17.2188 | 18.9374 | 20.8403 | 22.948 | 25.2832 | 27.8713 | 30.7406 | 33.9226 | 37.4523 | 41.3688 | 45.7158 | 50.5416 | 55.9005 | 61.8522 | 68.464 | 75.8108 | 83.9762 | 93.0532 | 103.1452 | 114.368 | 126.85 | 140.7348 | 156.1819 | 173.3691 | 192.4942 | 213.777 |  | 200.4795 | 224.1482 | 250.3165 | 279.2595 | 311.2832 | 346.7283 | 385.9739 | 429.4421 | 477.603 | 530.9801 | 590.1563 | 655.781 | 728.5776 | 809.3524 | 899.0035 | 998.532 | 1109.0537 | 1223.1681 | 1342.4462 | 1470.5192 | 1606.5899 | 1749.0278 | 1894.961 | 2039.688 | 2175.8326 | 2292.1297 | 2371.684 | 2389.4752 | 2308.782 | 2076.0637
| FALSE | 335 | 22015676 | BAN | Blank | 22 | TRANS NO.1 | DIFFERENTIAL & REF | X | Schweitzer | SEL_787 | SEL 787 | SEL 700s | Digital |  | 0.066046 | 1 |  | 0.8077 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 2.6788 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 43.9504 | 43.9504 | 43.9504 | 0 |  | 0.11989 |  | 0.91058 | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 | 3292.3189 | 4643.9111 | 6562.3318 | 8009.1353 |  | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 72.8034 | 100.7321 | 139.8997 | 194.9559 | 272.5071 | 381.948 | 536.6496 | 755.6562 | 1066.1108 | 1506.7216 | 2132.7189 | 3022.9445 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.13801 | 0.19095 | 0.2652 | 0.36957 | 0.51658 | 0.72404 | 1.0173 | 1.4325 | 2.021 | 2.8562 | 4.0429 | 5.7304 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 72.9414 | 100.9231 | 140.1649 | 195.3255 | 273.0237 | 382.6721 | 537.6669 | 757.0887 | 1068.1318 | 1509.5778 | 2136.7618 | 3028.6749 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 39.3707 | 54.4741 | 75.6552 | 105.4286 | 147.3669 | 206.5505 | 290.2103 | 408.6451 | 576.5332 | 814.8075 | 1153.3354 | 1634.7531 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.5483 | 7.6767 | 10.6616 | 14.8574 | 20.7675 | 29.1079 | 40.8975 | 57.5878 | 81.2472 | 114.8258 | 162.5324 | 230.3756 | 266.7611 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 | 2.0141 | 2.8409 | 4.0145 | 4.8996 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005295 | 0.015772 | 0.030154 | 0.049984 | 0.072145 | 0.099821 | 0.13863 | 0.19319 | 0.27004 | 0.3785 | 0.5318 | 0.74882 | 1.0565 | 1.4931 | 2.1134 | 2.9956 | 3.4687 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6555 | 25.7818 | 49.291 | 81.7072 | 117.9325 | 163.1737 | 226.6203 | 315.8047 | 441.4281 | 618.709 | 869.3065 | 1224.0704 | 1726.9687 | 2440.7041 | 3454.743 | 4896.7992 | 5670.2001
| FALSE | 336 | 22015675 | BAN | Blank | 22 | TRANS NO.1 | TX MECH. PROT. & COOLING | X | Schweitzer | SEL_2414 | SEL 2414 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 0.8077 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 2.6788 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 43.9504 | 43.9504 | 43.9504 | 0 |  | 0.11989 |  | 0.91058 | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 | 3292.3189 | 4643.9111 | 6562.3318 | 8009.1353 |  | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 72.8034 | 100.7321 | 139.8997 | 194.9559 | 272.5071 | 381.948 | 536.6496 | 755.6562 | 1066.1108 | 1506.7216 | 2132.7189 | 3022.9445 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.13801 | 0.19095 | 0.2652 | 0.36957 | 0.51658 | 0.72404 | 1.0173 | 1.4325 | 2.021 | 2.8562 | 4.0429 | 5.7304 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 72.9414 | 100.9231 | 140.1649 | 195.3255 | 273.0237 | 382.6721 | 537.6669 | 757.0887 | 1068.1318 | 1509.5778 | 2136.7618 | 3028.6749 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 39.3707 | 54.4741 | 75.6552 | 105.4286 | 147.3669 | 206.5505 | 290.2103 | 408.6451 | 576.5332 | 814.8075 | 1153.3354 | 1634.7531 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.5483 | 7.6767 | 10.6616 | 14.8574 | 20.7675 | 29.1079 | 40.8975 | 57.5878 | 81.2472 | 114.8258 | 162.5324 | 230.3756 | 266.7611 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 | 2.0141 | 2.8409 | 4.0145 | 4.8996 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005295 | 0.015772 | 0.030154 | 0.049984 | 0.072145 | 0.099821 | 0.13863 | 0.19319 | 0.27004 | 0.3785 | 0.5318 | 0.74882 | 1.0565 | 1.4931 | 2.1134 | 2.9956 | 3.4687 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6555 | 25.7818 | 49.291 | 81.7072 | 117.9325 | 163.1737 | 226.6203 | 315.8047 | 441.4281 | 618.709 | 869.3065 | 1224.0704 | 1726.9687 | 2440.7041 | 3454.743 | 4896.7992 | 5670.2001
| FALSE | 337 | 22015674 | BAN | Blank | 22 | TRANS NO.1 | TRANS MGMT | X | Schweitzer | SEL_2440 | SEL 2440 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 0.8077 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 2.6788 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 43.9504 | 43.9504 | 43.9504 | 0 |  | 0.11989 |  | 0.91058 | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 | 3292.3189 | 4643.9111 | 6562.3318 | 8009.1353 |  | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 72.8034 | 100.7321 | 139.8997 | 194.9559 | 272.5071 | 381.948 | 536.6496 | 755.6562 | 1066.1108 | 1506.7216 | 2132.7189 | 3022.9445 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.13801 | 0.19095 | 0.2652 | 0.36957 | 0.51658 | 0.72404 | 1.0173 | 1.4325 | 2.021 | 2.8562 | 4.0429 | 5.7304 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 72.9414 | 100.9231 | 140.1649 | 195.3255 | 273.0237 | 382.6721 | 537.6669 | 757.0887 | 1068.1318 | 1509.5778 | 2136.7618 | 3028.6749 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 39.3707 | 54.4741 | 75.6552 | 105.4286 | 147.3669 | 206.5505 | 290.2103 | 408.6451 | 576.5332 | 814.8075 | 1153.3354 | 1634.7531 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.5483 | 7.6767 | 10.6616 | 14.8574 | 20.7675 | 29.1079 | 40.8975 | 57.5878 | 81.2472 | 114.8258 | 162.5324 | 230.3756 | 266.7611 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 | 2.0141 | 2.8409 | 4.0145 | 4.8996 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005295 | 0.015772 | 0.030154 | 0.049984 | 0.072145 | 0.099821 | 0.13863 | 0.19319 | 0.27004 | 0.3785 | 0.5318 | 0.74882 | 1.0565 | 1.4931 | 2.1134 | 2.9956 | 3.4687 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6555 | 25.7818 | 49.291 | 81.7072 | 117.9325 | 163.1737 | 226.6203 | 315.8047 | 441.4281 | 618.709 | 869.3065 | 1224.0704 | 1726.9687 | 2440.7041 | 3454.743 | 4896.7992 | 5670.2001
| TRUE | 338 | 22004425 | BAN | Blank | 22 | TRANS NO.2 | DIFFERENTIAL | Y | Brown Boveri | D21SE3_2195 | D21SE3 2195 | D21 | Electronic |  | 0.0068096 | 2190 |  | 5.5 | 0.0093284 | 0.000188 | 0.0091404 | 98.1453 | 82.7196 | 180.865 | 27.547 | 3.7342 | 10.8106 |  | 7.9766 | 0.024052 | 0.00048474 | 0.023568 | 253.0588 | 213.285 | 466.3438 | 71.0274 | 9.6282 | 27.8741 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.0027721 |  | 222.9567 | 574.8735 | 71.0251 | 503.8484 |  | 0.037177 |  | 5.7083 | 5.9245 | 6.1489 | 6.3818 | 6.6235 | 6.8744 | 7.1348 | 7.405 | 7.6855 | 7.9766 | 8.2787 | 8.5923 | 8.9178 | 9.2555 | 9.6061 | 9.9699 | 10.3476 | 10.7395 | 11.1463 | 11.5684 | 12.0066 | 12.4614 | 12.9334 | 13.4232 | 13.9317 | 14.4594 | 15.007 | 15.5754 | 16.1654 | 16.7777 |  | 0.010224 | 0.011215 | 0.01231 | 0.013521 | 0.01486 | 0.016343 | 0.017985 | 0.019804 | 0.021819 | 0.024052 | 0.026528 | 0.029274 | 0.03232 | 0.035699 | 0.03945 | 0.043614 | 0.048239 | 0.053375 | 0.059081 | 0.065422 | 0.072469 | 0.080304 | 0.089016 | 0.098705 | 0.10948 | 0.12147 | 0.13481 | 0.14966 | 0.16619 | 0.18459 |  | 0.00020606 | 0.00022602 | 0.00024808 | 0.00027249 | 0.00029949 | 0.00032938 | 0.00036247 | 0.00039912 | 0.00043973 | 0.00048474 | 0.00053464 | 0.00058997 | 0.00065135 | 0.00071946 | 0.00079506 | 0.00087898 | 0.00097218 | 0.0010757 | 0.0011907 | 0.0013185 | 0.0014605 | 0.0016184 | 0.001794 | 0.0019892 | 0.0022064 | 0.0024481 | 0.002717 | 0.0030162 | 0.0033494 | 0.0037202 | 244.373 | 268.0416 | 294.2099 | 323.1529 | 355.1766 | 390.6217 | 429.8673 | 473.3355 | 521.4965 | 574.8735 | 634.0497 | 699.6744 | 772.4711 | 853.2458 | 942.8969 | 1042.4254 | 1152.9471 | 1275.7058 | 1412.088 | 1563.6397 | 1732.0847 | 1919.3452 | 2127.565 | 2359.1353 | 2616.723 | 2903.3033 | 3222.1955 | 3577.1027 | 3972.1569 | 4411.9686 |  | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 52.538 | 69.6422 | 93.1211 | 125.4956 | 170.3185 | 232.6055 | 319.4493 | 440.8931 | 611.1775 | 850.5168 | 1187.635 | 1663.3854 | 2335.9197 |  | 107.5728 | 117.9917 | 129.511 | 142.2516 | 156.3484 | 171.9513 | 189.2272 | 208.3619 | 229.5623 | 253.0588 | 279.1081 | 307.9961 | 340.0411 | 375.5981 | 415.0624 | 458.8748 | 507.5263 | 561.5646 | 621.5999 | 688.3128 | 762.4622 | 844.8941 | 936.5523 | 1038.4893 | 1151.8791 | 1278.0316 | 1418.4076 | 1574.6375 | 1748.5399 | 1942.1447 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 80.4411 | 90.86 | 102.3793 | 115.1199 | 129.2167 | 144.8196 | 162.0955 | 181.2302 | 202.4306 | 225.9271 | 251.9764 | 280.8644 | 312.9094 | 348.4664 | 387.9307 | 431.7431 | 480.3946 | 529.0896 | 578.5525 | 630.7526 | 684.8905 | 739.6164 | 792.7735 | 841.0305 | 879.3531 | 900.2489 | 892.6839 | 840.5334 | 720.3639 | 498.2599 |  | 90.6653 | 99.4467 | 109.1554 | 119.8936 | 131.7748 | 144.9254 | 159.486 | 175.6132 | 193.4815 | 213.285 | 235.2401 | 259.5877 | 286.5961 | 316.5645 | 349.8261 | 386.7524 | 427.7573 | 473.3023 | 523.9017 | 580.1292 | 642.6244 | 712.1003 | 789.3523 | 875.2677 | 970.8358 | 1077.1606 | 1195.4735 | 1327.1483 | 1473.7182 | 1636.8937 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 90.6441 | 99.4255 | 109.1342 | 119.8724 | 131.7536 | 144.9042 | 159.4647 | 175.592 | 193.4603 | 213.2638 | 235.2189 | 259.5664 | 286.5749 | 316.5433 | 349.8049 | 386.7312 | 427.7361 | 473.2769 | 523.8681 | 580.0842 | 642.5637 | 712.018 | 789.2399 | 875.1133 | 970.6228 | 1076.8653 | 1195.0624 | 1326.5744 | 1472.9144 | 1635.7648 |  | 171.0852 | 190.2855 | 211.5135 | 234.9924 | 260.9704 | 289.7238 | 321.5603 | 356.8222 | 395.8909 | 439.1909 | 487.1953 | 540.4308 | 599.4843 | 665.0097 | 737.7356 | 818.4743 | 908.1307 | 1002.3665 | 1102.4205 | 1210.8368 | 1327.4542 | 1451.6343 | 1582.0135 | 1716.1438 | 1849.9759 | 1977.1142 | 2087.7464 | 2167.1078 | 2193.2782 | 2134.0248 |  | 30.193 | 33.1174 | 36.3506 | 39.9265 | 43.8832 | 48.2625 | 53.1114 | 58.4821 | 64.4325 | 71.0274 | 78.3388 | 86.4469 | 95.4412 | 105.4212 | 116.4978 | 128.7949 | 142.4502 | 157.6174 | 174.4679 | 193.1925 | 214.0044 | 237.1411 | 262.8673 | 291.4785 | 323.3042 | 358.7121 | 398.1122 | 441.9621 | 490.7723 | 545.1124 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 15.523 | 18.4473 | 21.6805 | 25.2565 | 29.2131 | 33.5925 | 38.4414 | 43.812 | 49.7624 | 56.3573 | 63.6687 | 71.7769 | 80.7711 | 90.7511 | 101.8278 | 114.1248 | 127.7801 | 140.0583 | 151.1922 | 162.0698 | 172.0616 | 180.2176 | 185.1263 | 184.7128 | 175.9499 | 154.4457 | 113.8543 | 45.0333 | -65.1608 | -235.5937 |  | 4.0929 | 4.4893 | 4.9275 | 5.4123 | 5.9486 | 6.5423 | 7.1996 | 7.9276 | 8.7342 | 9.6282 | 10.6193 | 11.7184 | 12.9376 | 14.2905 | 15.792 | 17.4589 | 19.31 | 21.366 | 23.6502 | 26.1884 | 29.0096 | 32.1459 | 35.6333 | 39.5117 | 43.8259 | 48.6256 | 53.9665 | 59.9107 | 66.5272 | 73.8933 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 2.0252 | 2.4216 | 2.8598 | 3.3446 | 3.8809 | 4.4746 | 5.1319 | 5.8599 | 6.6665 | 7.5605 | 8.5516 | 9.6507 | 10.8699 | 12.2228 | 13.7243 | 15.3912 | 17.2423 | 18.8911 | 20.3696 | 21.8018 | 23.0979 | 24.1228 | 24.676 | 24.4635 | 23.0568 | 19.835 | 13.9014 | 3.965 | -11.8296 | -36.1444 |  | 11.849 | 12.9966 | 14.2655 | 15.6688 | 17.2216 | 18.9402 | 20.8431 | 22.9508 | 25.286 | 27.8741 | 30.7434 | 33.9253 | 37.4551 | 41.3716 | 45.7185 | 50.5444 | 55.9033 | 61.8556 | 68.4684 | 75.8167 | 83.9842 | 93.0639 | 103.1599 | 114.3882 | 126.8779 | 140.7734 | 156.2356 | 173.4441 | 192.5993 | 213.9246 |  | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.003318 | 0.0043982 | 0.005881 | 0.0079256 | 0.010756 | 0.01469 | 0.020175 | 0.027844 | 0.038599 | 0.053714 | 0.075004 | 0.10505 | 0.14752 |  | 11.8462 | 12.9938 | 14.2627 | 15.666 | 17.2188 | 18.9374 | 20.8403 | 22.948 | 25.2832 | 27.8713 | 30.7406 | 33.9226 | 37.4523 | 41.3688 | 45.7158 | 50.5416 | 55.9005 | 61.8522 | 68.464 | 75.8108 | 83.9762 | 93.0532 | 103.1452 | 114.368 | 126.85 | 140.7348 | 156.1819 | 173.3691 | 192.4942 | 213.777 |  | 200.4795 | 224.1482 | 250.3165 | 279.2595 | 311.2832 | 346.7283 | 385.9739 | 429.4421 | 477.603 | 530.9801 | 590.1563 | 655.781 | 728.5776 | 809.3524 | 899.0035 | 998.532 | 1109.0537 | 1223.1681 | 1342.4462 | 1470.5192 | 1606.5899 | 1749.0278 | 1894.961 | 2039.688 | 2175.8326 | 2292.1297 | 2371.684 | 2389.4752 | 2308.782 | 2076.0637
| FALSE | 339 | 22016047 | BAN | Blank | 22 | TRANS NO.2 | DIFFERENTIAL & REF | X | Schweitzer | SEL_787 | SEL 787 | SEL 700s | Digital |  | 0.066046 | 1 |  | 0.8077 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 2.6788 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 43.9504 | 43.9504 | 43.9504 | 0 |  | 0.11989 |  | 0.91058 | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 | 3292.3189 | 4643.9111 | 6562.3318 | 8009.1353 |  | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 72.8034 | 100.7321 | 139.8997 | 194.9559 | 272.5071 | 381.948 | 536.6496 | 755.6562 | 1066.1108 | 1506.7216 | 2132.7189 | 3022.9445 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.13801 | 0.19095 | 0.2652 | 0.36957 | 0.51658 | 0.72404 | 1.0173 | 1.4325 | 2.021 | 2.8562 | 4.0429 | 5.7304 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 72.9414 | 100.9231 | 140.1649 | 195.3255 | 273.0237 | 382.6721 | 537.6669 | 757.0887 | 1068.1318 | 1509.5778 | 2136.7618 | 3028.6749 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 39.3707 | 54.4741 | 75.6552 | 105.4286 | 147.3669 | 206.5505 | 290.2103 | 408.6451 | 576.5332 | 814.8075 | 1153.3354 | 1634.7531 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.5483 | 7.6767 | 10.6616 | 14.8574 | 20.7675 | 29.1079 | 40.8975 | 57.5878 | 81.2472 | 114.8258 | 162.5324 | 230.3756 | 266.7611 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 | 2.0141 | 2.8409 | 4.0145 | 4.8996 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005295 | 0.015772 | 0.030154 | 0.049984 | 0.072145 | 0.099821 | 0.13863 | 0.19319 | 0.27004 | 0.3785 | 0.5318 | 0.74882 | 1.0565 | 1.4931 | 2.1134 | 2.9956 | 3.4687 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6555 | 25.7818 | 49.291 | 81.7072 | 117.9325 | 163.1737 | 226.6203 | 315.8047 | 441.4281 | 618.709 | 869.3065 | 1224.0704 | 1726.9687 | 2440.7041 | 3454.743 | 4896.7992 | 5670.2001
| FALSE | 340 | 22016046 | BAN | Blank | 22 | TRANS NO.2 | TX MECH. PROT. & COOLING | X | Schweitzer | SEL_2414 | SEL 2414 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 0.8077 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 2.6788 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 43.9504 | 43.9504 | 43.9504 | 0 |  | 0.11989 |  | 0.91058 | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 | 3292.3189 | 4643.9111 | 6562.3318 | 8009.1353 |  | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 72.8034 | 100.7321 | 139.8997 | 194.9559 | 272.5071 | 381.948 | 536.6496 | 755.6562 | 1066.1108 | 1506.7216 | 2132.7189 | 3022.9445 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.13801 | 0.19095 | 0.2652 | 0.36957 | 0.51658 | 0.72404 | 1.0173 | 1.4325 | 2.021 | 2.8562 | 4.0429 | 5.7304 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 72.9414 | 100.9231 | 140.1649 | 195.3255 | 273.0237 | 382.6721 | 537.6669 | 757.0887 | 1068.1318 | 1509.5778 | 2136.7618 | 3028.6749 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 39.3707 | 54.4741 | 75.6552 | 105.4286 | 147.3669 | 206.5505 | 290.2103 | 408.6451 | 576.5332 | 814.8075 | 1153.3354 | 1634.7531 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.5483 | 7.6767 | 10.6616 | 14.8574 | 20.7675 | 29.1079 | 40.8975 | 57.5878 | 81.2472 | 114.8258 | 162.5324 | 230.3756 | 266.7611 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 | 2.0141 | 2.8409 | 4.0145 | 4.8996 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005295 | 0.015772 | 0.030154 | 0.049984 | 0.072145 | 0.099821 | 0.13863 | 0.19319 | 0.27004 | 0.3785 | 0.5318 | 0.74882 | 1.0565 | 1.4931 | 2.1134 | 2.9956 | 3.4687 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6555 | 25.7818 | 49.291 | 81.7072 | 117.9325 | 163.1737 | 226.6203 | 315.8047 | 441.4281 | 618.709 | 869.3065 | 1224.0704 | 1726.9687 | 2440.7041 | 3454.743 | 4896.7992 | 5670.2001
| FALSE | 341 | 22015673 | BAN | Blank | 22 | TRANS NO.2 | TRANS MGMT | X | Schweitzer | SEL_2440 | SEL 2440 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 0.8077 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 2.6788 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 43.9504 | 43.9504 | 43.9504 | 0 |  | 0.11989 |  | 0.91058 | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 | 3292.3189 | 4643.9111 | 6562.3318 | 8009.1353 |  | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 72.8034 | 100.7321 | 139.8997 | 194.9559 | 272.5071 | 381.948 | 536.6496 | 755.6562 | 1066.1108 | 1506.7216 | 2132.7189 | 3022.9445 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.13801 | 0.19095 | 0.2652 | 0.36957 | 0.51658 | 0.72404 | 1.0173 | 1.4325 | 2.021 | 2.8562 | 4.0429 | 5.7304 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 72.9414 | 100.9231 | 140.1649 | 195.3255 | 273.0237 | 382.6721 | 537.6669 | 757.0887 | 1068.1318 | 1509.5778 | 2136.7618 | 3028.6749 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 39.3707 | 54.4741 | 75.6552 | 105.4286 | 147.3669 | 206.5505 | 290.2103 | 408.6451 | 576.5332 | 814.8075 | 1153.3354 | 1634.7531 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.5483 | 7.6767 | 10.6616 | 14.8574 | 20.7675 | 29.1079 | 40.8975 | 57.5878 | 81.2472 | 114.8258 | 162.5324 | 230.3756 | 266.7611 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 | 2.0141 | 2.8409 | 4.0145 | 4.8996 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005295 | 0.015772 | 0.030154 | 0.049984 | 0.072145 | 0.099821 | 0.13863 | 0.19319 | 0.27004 | 0.3785 | 0.5318 | 0.74882 | 1.0565 | 1.4931 | 2.1134 | 2.9956 | 3.4687 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6555 | 25.7818 | 49.291 | 81.7072 | 117.9325 | 163.1737 | 226.6203 | 315.8047 | 441.4281 | 618.709 | 869.3065 | 1224.0704 | 1726.9687 | 2440.7041 | 3454.743 | 4896.7992 | 5670.2001
| TRUE | 342 | 22004427 | BAN | Blank | 22 | TRANS NO.3 | DIFFERENTIAL | Y | Brown Boveri | D21SE3_2195 | D21SE3 2195 | D21 | Electronic |  | 0.0068096 | 2190 |  | 5.5 | 0.0093284 | 0.000188 | 0.0091404 | 98.1453 | 82.7196 | 180.865 | 27.547 | 3.7342 | 10.8106 |  | 7.9766 | 0.024052 | 0.00048474 | 0.023568 | 253.0588 | 213.285 | 466.3438 | 71.0274 | 9.6282 | 27.8741 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.0027721 |  | 222.9567 | 574.8735 | 71.0251 | 503.8484 |  | 0.037177 |  | 5.7083 | 5.9245 | 6.1489 | 6.3818 | 6.6235 | 6.8744 | 7.1348 | 7.405 | 7.6855 | 7.9766 | 8.2787 | 8.5923 | 8.9178 | 9.2555 | 9.6061 | 9.9699 | 10.3476 | 10.7395 | 11.1463 | 11.5684 | 12.0066 | 12.4614 | 12.9334 | 13.4232 | 13.9317 | 14.4594 | 15.007 | 15.5754 | 16.1654 | 16.7777 |  | 0.010224 | 0.011215 | 0.01231 | 0.013521 | 0.01486 | 0.016343 | 0.017985 | 0.019804 | 0.021819 | 0.024052 | 0.026528 | 0.029274 | 0.03232 | 0.035699 | 0.03945 | 0.043614 | 0.048239 | 0.053375 | 0.059081 | 0.065422 | 0.072469 | 0.080304 | 0.089016 | 0.098705 | 0.10948 | 0.12147 | 0.13481 | 0.14966 | 0.16619 | 0.18459 |  | 0.00020606 | 0.00022602 | 0.00024808 | 0.00027249 | 0.00029949 | 0.00032938 | 0.00036247 | 0.00039912 | 0.00043973 | 0.00048474 | 0.00053464 | 0.00058997 | 0.00065135 | 0.00071946 | 0.00079506 | 0.00087898 | 0.00097218 | 0.0010757 | 0.0011907 | 0.0013185 | 0.0014605 | 0.0016184 | 0.001794 | 0.0019892 | 0.0022064 | 0.0024481 | 0.002717 | 0.0030162 | 0.0033494 | 0.0037202 | 244.373 | 268.0416 | 294.2099 | 323.1529 | 355.1766 | 390.6217 | 429.8673 | 473.3355 | 521.4965 | 574.8735 | 634.0497 | 699.6744 | 772.4711 | 853.2458 | 942.8969 | 1042.4254 | 1152.9471 | 1275.7058 | 1412.088 | 1563.6397 | 1732.0847 | 1919.3452 | 2127.565 | 2359.1353 | 2616.723 | 2903.3033 | 3222.1955 | 3577.1027 | 3972.1569 | 4411.9686 |  | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 52.538 | 69.6422 | 93.1211 | 125.4956 | 170.3185 | 232.6055 | 319.4493 | 440.8931 | 611.1775 | 850.5168 | 1187.635 | 1663.3854 | 2335.9197 |  | 107.5728 | 117.9917 | 129.511 | 142.2516 | 156.3484 | 171.9513 | 189.2272 | 208.3619 | 229.5623 | 253.0588 | 279.1081 | 307.9961 | 340.0411 | 375.5981 | 415.0624 | 458.8748 | 507.5263 | 561.5646 | 621.5999 | 688.3128 | 762.4622 | 844.8941 | 936.5523 | 1038.4893 | 1151.8791 | 1278.0316 | 1418.4076 | 1574.6375 | 1748.5399 | 1942.1447 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 80.4411 | 90.86 | 102.3793 | 115.1199 | 129.2167 | 144.8196 | 162.0955 | 181.2302 | 202.4306 | 225.9271 | 251.9764 | 280.8644 | 312.9094 | 348.4664 | 387.9307 | 431.7431 | 480.3946 | 529.0896 | 578.5525 | 630.7526 | 684.8905 | 739.6164 | 792.7735 | 841.0305 | 879.3531 | 900.2489 | 892.6839 | 840.5334 | 720.3639 | 498.2599 |  | 90.6653 | 99.4467 | 109.1554 | 119.8936 | 131.7748 | 144.9254 | 159.486 | 175.6132 | 193.4815 | 213.285 | 235.2401 | 259.5877 | 286.5961 | 316.5645 | 349.8261 | 386.7524 | 427.7573 | 473.3023 | 523.9017 | 580.1292 | 642.6244 | 712.1003 | 789.3523 | 875.2677 | 970.8358 | 1077.1606 | 1195.4735 | 1327.1483 | 1473.7182 | 1636.8937 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 90.6441 | 99.4255 | 109.1342 | 119.8724 | 131.7536 | 144.9042 | 159.4647 | 175.592 | 193.4603 | 213.2638 | 235.2189 | 259.5664 | 286.5749 | 316.5433 | 349.8049 | 386.7312 | 427.7361 | 473.2769 | 523.8681 | 580.0842 | 642.5637 | 712.018 | 789.2399 | 875.1133 | 970.6228 | 1076.8653 | 1195.0624 | 1326.5744 | 1472.9144 | 1635.7648 |  | 171.0852 | 190.2855 | 211.5135 | 234.9924 | 260.9704 | 289.7238 | 321.5603 | 356.8222 | 395.8909 | 439.1909 | 487.1953 | 540.4308 | 599.4843 | 665.0097 | 737.7356 | 818.4743 | 908.1307 | 1002.3665 | 1102.4205 | 1210.8368 | 1327.4542 | 1451.6343 | 1582.0135 | 1716.1438 | 1849.9759 | 1977.1142 | 2087.7464 | 2167.1078 | 2193.2782 | 2134.0248 |  | 30.193 | 33.1174 | 36.3506 | 39.9265 | 43.8832 | 48.2625 | 53.1114 | 58.4821 | 64.4325 | 71.0274 | 78.3388 | 86.4469 | 95.4412 | 105.4212 | 116.4978 | 128.7949 | 142.4502 | 157.6174 | 174.4679 | 193.1925 | 214.0044 | 237.1411 | 262.8673 | 291.4785 | 323.3042 | 358.7121 | 398.1122 | 441.9621 | 490.7723 | 545.1124 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 15.523 | 18.4473 | 21.6805 | 25.2565 | 29.2131 | 33.5925 | 38.4414 | 43.812 | 49.7624 | 56.3573 | 63.6687 | 71.7769 | 80.7711 | 90.7511 | 101.8278 | 114.1248 | 127.7801 | 140.0583 | 151.1922 | 162.0698 | 172.0616 | 180.2176 | 185.1263 | 184.7128 | 175.9499 | 154.4457 | 113.8543 | 45.0333 | -65.1608 | -235.5937 |  | 4.0929 | 4.4893 | 4.9275 | 5.4123 | 5.9486 | 6.5423 | 7.1996 | 7.9276 | 8.7342 | 9.6282 | 10.6193 | 11.7184 | 12.9376 | 14.2905 | 15.792 | 17.4589 | 19.31 | 21.366 | 23.6502 | 26.1884 | 29.0096 | 32.1459 | 35.6333 | 39.5117 | 43.8259 | 48.6256 | 53.9665 | 59.9107 | 66.5272 | 73.8933 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 2.0252 | 2.4216 | 2.8598 | 3.3446 | 3.8809 | 4.4746 | 5.1319 | 5.8599 | 6.6665 | 7.5605 | 8.5516 | 9.6507 | 10.8699 | 12.2228 | 13.7243 | 15.3912 | 17.2423 | 18.8911 | 20.3696 | 21.8018 | 23.0979 | 24.1228 | 24.676 | 24.4635 | 23.0568 | 19.835 | 13.9014 | 3.965 | -11.8296 | -36.1444 |  | 11.849 | 12.9966 | 14.2655 | 15.6688 | 17.2216 | 18.9402 | 20.8431 | 22.9508 | 25.286 | 27.8741 | 30.7434 | 33.9253 | 37.4551 | 41.3716 | 45.7185 | 50.5444 | 55.9033 | 61.8556 | 68.4684 | 75.8167 | 83.9842 | 93.0639 | 103.1599 | 114.3882 | 126.8779 | 140.7734 | 156.2356 | 173.4441 | 192.5993 | 213.9246 |  | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.0027721 | 0.003318 | 0.0043982 | 0.005881 | 0.0079256 | 0.010756 | 0.01469 | 0.020175 | 0.027844 | 0.038599 | 0.053714 | 0.075004 | 0.10505 | 0.14752 |  | 11.8462 | 12.9938 | 14.2627 | 15.666 | 17.2188 | 18.9374 | 20.8403 | 22.948 | 25.2832 | 27.8713 | 30.7406 | 33.9226 | 37.4523 | 41.3688 | 45.7158 | 50.5416 | 55.9005 | 61.8522 | 68.464 | 75.8108 | 83.9762 | 93.0532 | 103.1452 | 114.368 | 126.85 | 140.7348 | 156.1819 | 173.3691 | 192.4942 | 213.777 |  | 200.4795 | 224.1482 | 250.3165 | 279.2595 | 311.2832 | 346.7283 | 385.9739 | 429.4421 | 477.603 | 530.9801 | 590.1563 | 655.781 | 728.5776 | 809.3524 | 899.0035 | 998.532 | 1109.0537 | 1223.1681 | 1342.4462 | 1470.5192 | 1606.5899 | 1749.0278 | 1894.961 | 2039.688 | 2175.8326 | 2292.1297 | 2371.684 | 2389.4752 | 2308.782 | 2076.0637
| TRUE | 343 | 22004429 | BAN | Blank | 22 | TRANS NO.3 | HIBP | Y | ABB | RADHA_3110 | RADHA 3110 | RADHA | Electronic |  | 0.0034106 | 2190 |  | 6.6 | 0.014726 | 0.00014965 | 0.014576 | 154.7806 | 65.8469 | 220.6275 | 42.6512 | 5.8934 | 43.0274 |  | 9.8464 | 0.042169 | 0.00042853 | 0.04174 | 443.2208 | 188.5553 | 631.7762 | 122.1335 | 16.876 | 123.2109 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 54.2634 | 0.010624 | 54.274 | 14.6699 | 2.0677 | 0.006942 |  | 312.1995 | 893.9965 | 71.0185 | 822.978 |  | 0.040003 |  | 6.8694 | 7.1497 | 7.4416 | 7.7453 | 8.0614 | 8.3904 | 8.7329 | 9.0893 | 9.4603 | 9.8464 | 10.2482 | 10.6665 | 11.1019 | 11.555 | 12.0266 | 12.5174 | 13.0283 | 13.5601 | 14.1135 | 14.6896 | 15.2891 | 15.9131 | 16.5626 | 17.2386 | 17.9422 | 18.6745 | 19.4366 | 20.2299 | 21.0556 | 21.915 |  | 0.016313 | 0.018083 | 0.020059 | 0.022266 | 0.024731 | 0.027485 | 0.030564 | 0.034008 | 0.037859 | 0.042169 | 0.046992 | 0.052392 | 0.058439 | 0.065213 | 0.072802 | 0.081308 | 0.090842 | 0.10153 | 0.11352 | 0.12697 | 0.14205 | 0.15898 | 0.17798 | 0.19931 | 0.22326 | 0.25015 | 0.28035 | 0.31427 | 0.35238 | 0.3952 |  | 0.00016577 | 0.00018377 | 0.00020385 | 0.00022627 | 0.00025132 | 0.00027932 | 0.00031061 | 0.0003456 | 0.00038474 | 0.00042853 | 0.00047755 | 0.00053243 | 0.00059388 | 0.00066272 | 0.00073985 | 0.00082628 | 0.00092317 | 0.0010318 | 0.0011536 | 0.0012903 | 0.0014436 | 0.0016157 | 0.0018087 | 0.0020255 | 0.0022688 | 0.0025421 | 0.002849 | 0.0031937 | 0.003581 | 0.0040161 | 345.8346 | 383.3654 | 425.2594 | 472.0415 | 524.3011 | 582.6998 | 647.981 | 720.9795 | 802.6334 | 893.9965 | 996.2533 | 1110.7348 | 1238.9374 | 1382.543 | 1543.4427 | 1723.763 | 1925.895 | 2152.5279 | 2406.6866 | 2691.7735 | 3011.6163 | 3370.5213 | 3773.3337 | 4225.5059 | 4733.1731 | 5303.2405 | 5943.4796 | 6662.6378 | 7470.5616 | 8378.3354 |  | 43.887 | 43.887 | 43.887 | 43.887 | 43.887 | 43.887 | 43.887 | 43.887 | 43.887 | 43.887 | 43.887 | 43.887 | 43.887 | 43.887 | 43.887 | 43.887 | 43.887 | 52.53 | 69.6316 | 93.1069 | 125.4764 | 170.2925 | 232.57 | 319.4005 | 440.8258 | 611.0841 | 850.3869 | 1187.4536 | 1663.1312 | 2335.5629 |  | 171.456 | 190.0628 | 210.8328 | 234.0262 | 259.9352 | 288.8878 | 321.2526 | 357.4434 | 397.9253 | 443.2208 | 493.9172 | 550.6742 | 614.2338 | 685.4298 | 765.1998 | 854.5981 | 954.81 | 1067.1689 | 1193.1743 | 1334.5132 | 1493.0831 | 1671.0191 | 1870.7234 | 2094.8989 | 2346.5875 | 2629.2124 | 2946.6268 | 3303.1672 | 3703.7154 | 4153.7666 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2777 | 143.7787 | 197.4587 | 272.5259 | 377.7825 | 525.7234 | 734.1037 | 1028.1756 | 1443.8841 |  | 144.3244 | 162.9312 | 183.7012 | 206.8946 | 232.8035 | 261.7561 | 294.1209 | 330.3117 | 370.7936 | 416.0892 | 466.7855 | 523.5425 | 587.1021 | 658.2982 | 738.0682 | 827.4664 | 927.6783 | 1034.6939 | 1150.1269 | 1276.9529 | 1415.5115 | 1565.7415 | 1726.9447 | 1897.4402 | 2074.0616 | 2251.43 | 2420.9033 | 2569.0635 | 2675.5397 | 2709.8825 |  | 72.941 | 80.8567 | 89.6927 | 99.5596 | 110.5818 | 122.8989 | 136.6675 | 152.0638 | 169.2857 | 188.5553 | 210.1226 | 234.2682 | 261.3078 | 291.5961 | 325.5319 | 363.5637 | 406.1959 | 453.9957 | 507.6011 | 567.7296 | 635.1885 | 710.8862 | 795.8445 | 891.2134 | 998.2869 | 1118.5215 | 1253.5561 | 1405.2358 | 1575.6373 | 1767.0984 |  | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.012716 | 0.016856 | 0.022538 | 0.030374 | 0.041223 | 0.056298 | 0.077317 | 0.10671 | 0.14793 | 0.20585 | 0.28745 | 0.40259 | 0.56537 |  | 72.9303 | 80.846 | 89.682 | 99.549 | 110.5712 | 122.8882 | 136.6569 | 152.0532 | 169.275 | 188.5447 | 210.112 | 234.2576 | 261.2972 | 291.5854 | 325.5212 | 363.5531 | 406.1853 | 453.983 | 507.5842 | 567.707 | 635.1581 | 710.8449 | 795.7882 | 891.1361 | 998.1802 | 1118.3735 | 1253.3502 | 1404.9483 | 1575.2347 | 1766.533 |  | 217.2547 | 243.7772 | 273.3832 | 306.4436 | 343.3747 | 384.6444 | 430.7778 | 482.3649 | 540.0687 | 604.6339 | 676.8975 | 757.8001 | 848.3993 | 949.8836 | 1063.5894 | 1191.0195 | 1333.8636 | 1488.677 | 1657.7111 | 1844.66 | 2050.6696 | 2276.5864 | 2522.7329 | 2788.5762 | 3072.2418 | 3369.8035 | 3674.2536 | 3974.0118 | 4250.7744 | 4476.4156 |  | 47.2463 | 52.3735 | 58.0969 | 64.488 | 71.6275 | 79.6057 | 88.5241 | 98.4968 | 109.6519 | 122.1335 | 136.1033 | 151.7433 | 169.2577 | 188.8764 | 210.8577 | 235.4922 | 263.1065 | 294.068 | 328.79 | 367.7372 | 411.4326 | 460.4644 | 515.4947 | 577.2683 | 646.6234 | 724.5033 | 811.9697 | 910.2176 | 1020.5923 | 1144.608 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 32.5763 | 37.7036 | 43.427 | 49.8181 | 56.9576 | 64.9357 | 73.8541 | 83.8268 | 94.982 | 107.4636 | 121.4334 | 137.0733 | 154.5878 | 174.2065 | 196.1878 | 220.8223 | 248.4366 | 276.5091 | 305.5145 | 336.6147 | 369.4901 | 403.5415 | 437.7545 | 470.5037 | 499.2704 | 520.2387 | 527.7144 | 513.2924 | 464.6643 | 363.9091 |  | 6.5283 | 7.2368 | 8.0276 | 8.9107 | 9.8972 | 10.9996 | 12.2319 | 13.6099 | 15.1513 | 16.876 | 18.8063 | 20.9673 | 23.3874 | 26.0983 | 29.1356 | 32.5395 | 36.3551 | 40.6333 | 45.431 | 50.8126 | 56.8503 | 63.6253 | 71.2292 | 79.7648 | 89.3481 | 100.1092 | 112.195 | 125.7706 | 141.0217 | 158.1578 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 4.4606 | 5.1691 | 5.9599 | 6.843 | 7.8295 | 8.9319 | 10.1642 | 11.5422 | 13.0836 | 14.8083 | 16.7386 | 18.8996 | 21.3197 | 24.0306 | 27.0679 | 30.4718 | 34.2874 | 38.1584 | 42.1504 | 46.4259 | 50.9386 | 55.6021 | 60.2719 | 64.7166 | 68.579 | 71.3186 | 72.1299 | 69.8249 | 62.665 | 48.1201 |  | 47.663 | 52.8355 | 58.6094 | 65.0569 | 72.2593 | 80.3079 | 89.3049 | 99.3656 | 110.6192 | 123.2109 | 137.3039 | 153.0818 | 170.7507 | 190.5425 | 212.7177 | 237.5695 | 265.4274 | 296.662 | 331.6902 | 370.981 | 415.0618 | 464.5262 | 520.0419 | 582.3604 | 652.3273 | 730.8941 | 819.1321 | 918.2467 | 1029.595 | 1154.7046 |  | 0.006942 | 0.006942 | 0.006942 | 0.006942 | 0.006942 | 0.006942 | 0.006942 | 0.006942 | 0.006942 | 0.006942 | 0.006942 | 0.006942 | 0.006942 | 0.006942 | 0.006942 | 0.006942 | 0.006942 | 0.0083092 | 0.011014 | 0.014728 | 0.019848 | 0.026937 | 0.036788 | 0.050523 | 0.06973 | 0.096661 | 0.13451 | 0.18783 | 0.26307 | 0.36944 |  | 47.6561 | 52.8286 | 58.6024 | 65.05 | 72.2524 | 80.3009 | 89.298 | 99.3587 | 110.6122 | 123.2039 | 137.297 | 153.0749 | 170.7438 | 190.5355 | 212.7108 | 237.5626 | 265.4205 | 296.6537 | 331.6792 | 370.9663 | 415.042 | 464.4993 | 520.0052 | 582.3099 | 652.2576 | 730.7975 | 818.9976 | 918.0588 | 1029.3319 | 1154.3352 |  | 301.9477 | 339.4785 | 381.3725 | 428.1547 | 480.4142 | 538.813 | 604.0941 | 677.0927 | 758.7465 | 850.1096 | 952.3664 | 1066.848 | 1195.0506 | 1338.6562 | 1499.5559 | 1679.8761 | 1882.0081 | 2099.9981 | 2337.0552 | 2598.6669 | 2886.1403 | 3200.2293 | 3540.7645 | 3906.1064 | 4292.3488 | 4692.1583 | 5093.0954 | 5475.1879 | 5807.4356 | 6042.78
| TRUE | 344 | 22004428 | BAN | Blank | 22 | TRANS NO.3 | HIBP | X | ABB | RADHA_3110 | RADHA 3110 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 156.082 | 611.1747 | 767.2566 | 49.6875 | 5.9058 | 399.3701 |  | 9.8464 | 0.042169 | 0.0039776 | 0.038191 | 446.9473 | 1750.1243 | 2197.0716 | 142.2821 | 16.9115 | 1143.6129 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 54.2636 | 0.10462 | 54.3682 | 14.6711 | 2.0677 | 0.068365 |  | 1222.2199 | 3499.8781 | 71.1754 | 3428.7027 |  | 0.040003 |  | 6.8694 | 7.1497 | 7.4416 | 7.7453 | 8.0614 | 8.3904 | 8.7329 | 9.0893 | 9.4603 | 9.8464 | 10.2482 | 10.6665 | 11.1019 | 11.555 | 12.0266 | 12.5174 | 13.0283 | 13.5601 | 14.1135 | 14.6896 | 15.2891 | 15.9131 | 16.5626 | 17.2386 | 17.9422 | 18.6745 | 19.4366 | 20.2299 | 21.0556 | 21.915 |  | 0.016313 | 0.018083 | 0.020059 | 0.022266 | 0.024731 | 0.027485 | 0.030564 | 0.034008 | 0.037859 | 0.042169 | 0.046992 | 0.052392 | 0.058439 | 0.065213 | 0.072802 | 0.081308 | 0.090842 | 0.10153 | 0.11352 | 0.12697 | 0.14205 | 0.15898 | 0.17798 | 0.19931 | 0.22326 | 0.25015 | 0.28035 | 0.31427 | 0.35238 | 0.3952 |  | 0.0015387 | 0.0017057 | 0.0018921 | 0.0021002 | 0.0023327 | 0.0025925 | 0.002883 | 0.0032078 | 0.0035711 | 0.0039776 | 0.0044325 | 0.0049419 | 0.0055123 | 0.0061512 | 0.0068671 | 0.0076693 | 0.0085687 | 0.009577 | 0.010708 | 0.011976 | 0.013399 | 0.014996 | 0.016788 | 0.0188 | 0.021059 | 0.023595 | 0.026444 | 0.029643 | 0.033238 | 0.037277 | 1353.8967 | 1500.8247 | 1664.8343 | 1847.9802 | 2052.5694 | 2281.1927 | 2536.7599 | 2822.5394 | 3142.2035 | 3499.8781 | 3900.1999 | 4348.38 | 4850.2761 | 5412.4731 | 6042.3742 | 6748.3042 | 7539.6241 | 8426.8621 | 9421.8598 | 10537.9374 | 11790.0795 | 13195.145 | 14772.1026 | 16542.2967 | 18529.7469 | 20761.4854 | 23267.9367 | 26083.3458 | 29246.2606 | 32800.0751 |  | 44.045 | 44.045 | 44.045 | 44.045 | 44.045 | 44.045 | 44.045 | 44.045 | 44.045 | 44.045 | 44.045 | 44.045 | 44.045 | 44.045 | 44.045 | 44.045 | 44.045 | 52.7191 | 69.8823 | 93.4421 | 125.9281 | 170.9055 | 233.4072 | 320.5502 | 442.4126 | 613.2839 | 853.4481 | 1191.7281 | 1669.1181 | 2343.9703 |  | 172.8976 | 191.6608 | 212.6055 | 235.9939 | 262.1207 | 291.3167 | 323.9536 | 360.4487 | 401.2709 | 446.9473 | 498.0699 | 555.3041 | 619.3981 | 691.1927 | 771.6334 | 861.7833 | 962.8377 | 1076.1413 | 1203.2062 | 1345.7334 | 1505.6365 | 1685.0686 | 1886.4519 | 2112.5122 | 2366.3169 | 2651.3181 | 2971.4011 | 3330.9393 | 3734.8551 | 4188.6903 |  | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 32.4751 | 43.0476 | 57.5605 | 77.572 | 105.2781 | 143.7793 | 197.4595 | 272.527 | 377.784 | 525.7256 | 734.1068 | 1028.1799 | 1443.8901 |  | 145.7658 | 164.5291 | 185.4737 | 208.8621 | 234.9889 | 264.1849 | 296.8218 | 333.3169 | 374.1392 | 419.8155 | 470.9381 | 528.1723 | 592.2663 | 664.0609 | 744.5016 | 834.6515 | 935.706 | 1043.6663 | 1160.1586 | 1288.1729 | 1428.0646 | 1579.7905 | 1742.6726 | 1915.0526 | 2093.7899 | 2273.5341 | 2445.6755 | 2596.8325 | 2706.6753 | 2744.8002 |  | 677.02 | 750.4918 | 832.5053 | 924.0879 | 1026.3933 | 1140.7171 | 1268.5142 | 1411.4191 | 1571.268 | 1750.1243 | 1950.3063 | 2174.4201 | 2425.3948 | 2706.523 | 3021.5069 | 3374.5092 | 3770.2111 | 4213.877 | 4711.4286 | 5269.5264 | 5895.6638 | 6598.2709 | 7386.8331 | 8272.0238 | 9265.8541 | 10381.8415 | 11635.1998 | 13043.0534 | 14624.6781 | 16401.7735 |  | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.12523 | 0.16599 | 0.22196 | 0.29912 | 0.40596 | 0.55442 | 0.76141 | 1.0509 | 1.4568 | 2.0272 | 2.8308 | 3.9647 | 5.5677 |  | 676.9154 | 750.3872 | 832.4006 | 923.9833 | 1026.2887 | 1140.6125 | 1268.4096 | 1411.3145 | 1571.1634 | 1750.0196 | 1950.2017 | 2174.3155 | 2425.2901 | 2706.4184 | 3021.4023 | 3374.4046 | 3770.1065 | 4213.7518 | 4711.2626 | 5269.3045 | 5895.3646 | 6597.8649 | 7386.2787 | 8271.2624 | 9264.8033 | 10380.3848 | 11633.1726 | 13040.2226 | 14620.7134 | 16396.2058 |  | 822.6812 | 914.9162 | 1017.8743 | 1132.8454 | 1261.2776 | 1404.7974 | 1565.2314 | 1744.6314 | 1945.3026 | 2169.8352 | 2421.1398 | 2702.4879 | 3017.5565 | 3370.4793 | 3765.9039 | 4209.0561 | 4705.8124 | 5257.4181 | 5871.4211 | 6557.4774 | 7323.4292 | 8177.6554 | 9128.9513 | 10186.315 | 11358.5931 | 12653.9188 | 14078.8481 | 15637.0551 | 17327.3887 | 19141.006 |  | 55.0406 | 61.0137 | 67.6813 | 75.1268 | 83.444 | 92.7384 | 103.128 | 114.746 | 127.7414 | 142.2821 | 158.5566 | 176.7767 | 197.1805 | 220.0357 | 245.6434 | 274.3419 | 306.5117 | 342.581 | 383.0311 | 428.4035 | 479.3074 | 536.4282 | 600.537 | 672.5015 | 753.2982 | 844.026 | 945.9219 | 1060.378 | 1188.9614 | 1333.4363 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 40.3694 | 46.3426 | 53.0101 | 60.4556 | 68.7729 | 78.0672 | 88.4569 | 100.0748 | 113.0703 | 127.611 | 143.8854 | 162.1055 | 182.5093 | 205.3646 | 230.9722 | 259.6707 | 291.8406 | 325.0206 | 359.7537 | 397.2785 | 437.3615 | 479.5005 | 522.7903 | 565.728 | 605.933 | 639.7446 | 661.6432 | 663.4201 | 632.9875 | 552.6729 |  | 6.542 | 7.252 | 8.0445 | 8.9295 | 9.918 | 11.0228 | 12.2577 | 13.6385 | 15.1832 | 16.9115 | 18.8458 | 21.0114 | 23.4366 | 26.1531 | 29.1968 | 32.6079 | 36.4316 | 40.7187 | 45.5265 | 50.9194 | 56.9698 | 63.7591 | 71.379 | 79.9326 | 89.536 | 100.3198 | 112.431 | 126.0351 | 141.3183 | 158.4904 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 4.4744 | 5.1843 | 5.9768 | 6.8618 | 7.8503 | 8.9551 | 10.19 | 11.5709 | 13.1155 | 14.8438 | 16.7781 | 18.9437 | 21.3689 | 24.0854 | 27.1291 | 30.5402 | 34.3639 | 38.2438 | 42.2459 | 46.5328 | 51.0581 | 55.7359 | 60.4217 | 64.8843 | 68.7669 | 71.5291 | 72.3658 | 70.0893 | 62.9615 | 48.4526 |  | 442.3965 | 490.4064 | 543.9978 | 603.8422 | 670.6933 | 745.3978 | 828.9064 | 922.2871 | 1026.7399 | 1143.6129 | 1274.4212 | 1420.8677 | 1584.8662 | 1768.5685 | 1974.3937 | 2205.0619 | 2463.632 | 2753.544 | 3078.6674 | 3443.3546 | 3852.502 | 4311.6183 | 4826.9017 | 5405.3266 | 6054.7418 | 6783.98 | 7602.9829 | 8522.9401 | 9556.4476 | 10717.6847 |  | 0.068365 | 0.068365 | 0.068365 | 0.068365 | 0.068365 | 0.068365 | 0.068365 | 0.068365 | 0.068365 | 0.068365 | 0.068365 | 0.068365 | 0.068365 | 0.068365 | 0.068365 | 0.068365 | 0.068365 | 0.081828 | 0.10847 | 0.14504 | 0.19546 | 0.26527 | 0.36228 | 0.49754 | 0.68669 | 0.95191 | 1.3247 | 1.8497 | 2.5907 | 3.6382 |  | 442.3281 | 490.338 | 543.9294 | 603.7738 | 670.625 | 745.3294 | 828.838 | 922.2188 | 1026.6715 | 1143.5446 | 1274.3529 | 1420.7993 | 1584.7978 | 1768.5001 | 1974.3253 | 2204.9935 | 2463.5636 | 2753.4622 | 3078.559 | 3443.2096 | 3852.3065 | 4311.353 | 4826.5394 | 5404.8291 | 6054.0551 | 6783.0281 | 7601.6582 | 8521.0904 | 9553.8569 | 10714.0465 |  | 1309.8531 | 1456.7811 | 1620.7907 | 1803.9366 | 2008.5258 | 2237.1491 | 2492.7163 | 2778.4958 | 3098.1599 | 3455.8345 | 3856.1563 | 4304.3364 | 4806.2325 | 5368.4295 | 5998.3306 | 6704.2606 | 7495.5805 | 8374.1447 | 9351.9797 | 10444.4982 | 11664.1553 | 13024.2449 | 14538.7027 | 16221.7565 | 18087.3481 | 20148.2207 | 22414.5153 | 24891.6549 | 27577.1946 | 30456.178
| FALSE | 345 | 22016049 | BAN | Blank | 22 | TRANS NO.3 | DIFFERENTIAL & REF | X | Schweitzer | SEL_787 | SEL 787 | SEL 700s | Digital |  | 0.066046 | 1 |  | 0.8077 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 2.6788 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 43.9504 | 43.9504 | 43.9504 | 0 |  | 0.11989 |  | 0.91058 | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 | 3292.3189 | 4643.9111 | 6562.3318 | 8009.1353 |  | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 72.8034 | 100.7321 | 139.8997 | 194.9559 | 272.5071 | 381.948 | 536.6496 | 755.6562 | 1066.1108 | 1506.7216 | 2132.7189 | 3022.9445 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.13801 | 0.19095 | 0.2652 | 0.36957 | 0.51658 | 0.72404 | 1.0173 | 1.4325 | 2.021 | 2.8562 | 4.0429 | 5.7304 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 72.9414 | 100.9231 | 140.1649 | 195.3255 | 273.0237 | 382.6721 | 537.6669 | 757.0887 | 1068.1318 | 1509.5778 | 2136.7618 | 3028.6749 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 39.3707 | 54.4741 | 75.6552 | 105.4286 | 147.3669 | 206.5505 | 290.2103 | 408.6451 | 576.5332 | 814.8075 | 1153.3354 | 1634.7531 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.5483 | 7.6767 | 10.6616 | 14.8574 | 20.7675 | 29.1079 | 40.8975 | 57.5878 | 81.2472 | 114.8258 | 162.5324 | 230.3756 | 266.7611 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 | 2.0141 | 2.8409 | 4.0145 | 4.8996 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005295 | 0.015772 | 0.030154 | 0.049984 | 0.072145 | 0.099821 | 0.13863 | 0.19319 | 0.27004 | 0.3785 | 0.5318 | 0.74882 | 1.0565 | 1.4931 | 2.1134 | 2.9956 | 3.4687 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6555 | 25.7818 | 49.291 | 81.7072 | 117.9325 | 163.1737 | 226.6203 | 315.8047 | 441.4281 | 618.709 | 869.3065 | 1224.0704 | 1726.9687 | 2440.7041 | 3454.743 | 4896.7992 | 5670.2001
| FALSE | 346 | 22016048 | BAN | Blank | 22 | TRANS NO.3 | TX MECH. PROT. & COOLING | X | Schweitzer | SEL_2414 | SEL 2414 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 0.8077 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 2.6788 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 43.9504 | 43.9504 | 43.9504 | 0 |  | 0.11989 |  | 0.91058 | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 | 3292.3189 | 4643.9111 | 6562.3318 | 8009.1353 |  | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 72.8034 | 100.7321 | 139.8997 | 194.9559 | 272.5071 | 381.948 | 536.6496 | 755.6562 | 1066.1108 | 1506.7216 | 2132.7189 | 3022.9445 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.13801 | 0.19095 | 0.2652 | 0.36957 | 0.51658 | 0.72404 | 1.0173 | 1.4325 | 2.021 | 2.8562 | 4.0429 | 5.7304 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 72.9414 | 100.9231 | 140.1649 | 195.3255 | 273.0237 | 382.6721 | 537.6669 | 757.0887 | 1068.1318 | 1509.5778 | 2136.7618 | 3028.6749 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 39.3707 | 54.4741 | 75.6552 | 105.4286 | 147.3669 | 206.5505 | 290.2103 | 408.6451 | 576.5332 | 814.8075 | 1153.3354 | 1634.7531 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.5483 | 7.6767 | 10.6616 | 14.8574 | 20.7675 | 29.1079 | 40.8975 | 57.5878 | 81.2472 | 114.8258 | 162.5324 | 230.3756 | 266.7611 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 | 2.0141 | 2.8409 | 4.0145 | 4.8996 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005295 | 0.015772 | 0.030154 | 0.049984 | 0.072145 | 0.099821 | 0.13863 | 0.19319 | 0.27004 | 0.3785 | 0.5318 | 0.74882 | 1.0565 | 1.4931 | 2.1134 | 2.9956 | 3.4687 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6555 | 25.7818 | 49.291 | 81.7072 | 117.9325 | 163.1737 | 226.6203 | 315.8047 | 441.4281 | 618.709 | 869.3065 | 1224.0704 | 1726.9687 | 2440.7041 | 3454.743 | 4896.7992 | 5670.2001
| FALSE | 347 | 22015672 | BAN | Blank | 22 | TRANS NO.3 | TRANS MGMT | X | Schweitzer | SEL_2440 | SEL 2440 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 0.8077 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 2.6788 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.026887 |  | 43.9504 | 43.9504 | 43.9504 | 0 |  | 0.11989 |  | 0.91058 | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 | 3292.3189 | 4643.9111 | 6562.3318 | 8009.1353 |  | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 43.9504 | 52.6058 | 69.7321 | 93.2413 | 125.6576 | 170.5383 | 232.9058 | 319.8616 | 441.4623 | 611.9665 | 851.6148 | 1189.1682 | 1665.5326 | 2338.9352 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 72.8034 | 100.7321 | 139.8997 | 194.9559 | 272.5071 | 381.948 | 536.6496 | 755.6562 | 1066.1108 | 1506.7216 | 2132.7189 | 3022.9445 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.13801 | 0.19095 | 0.2652 | 0.36957 | 0.51658 | 0.72404 | 1.0173 | 1.4325 | 2.021 | 2.8562 | 4.0429 | 5.7304 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 72.9414 | 100.9231 | 140.1649 | 195.3255 | 273.0237 | 382.6721 | 537.6669 | 757.0887 | 1068.1318 | 1509.5778 | 2136.7618 | 3028.6749 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 39.3707 | 54.4741 | 75.6552 | 105.4286 | 147.3669 | 206.5505 | 290.2103 | 408.6451 | 576.5332 | 814.8075 | 1153.3354 | 1634.7531 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.5483 | 7.6767 | 10.6616 | 14.8574 | 20.7675 | 29.1079 | 40.8975 | 57.5878 | 81.2472 | 114.8258 | 162.5324 | 230.3756 | 266.7611 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 | 2.0141 | 2.8409 | 4.0145 | 4.8996 |  | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.026887 | 0.032182 | 0.042659 | 0.05704 | 0.076871 | 0.10433 | 0.14248 | 0.19568 | 0.27006 | 0.37437 | 0.52098 | 0.72747 | 1.0189 | 1.4308 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005295 | 0.015772 | 0.030154 | 0.049984 | 0.072145 | 0.099821 | 0.13863 | 0.19319 | 0.27004 | 0.3785 | 0.5318 | 0.74882 | 1.0565 | 1.4931 | 2.1134 | 2.9956 | 3.4687 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6555 | 25.7818 | 49.291 | 81.7072 | 117.9325 | 163.1737 | 226.6203 | 315.8047 | 441.4281 | 618.709 | 869.3065 | 1224.0704 | 1726.9687 | 2440.7041 | 3454.743 | 4896.7992 | 5670.2001
| TRUE | 348 | 22004419 | BAN | Blank | 66 | BUS NO.1 | HIBP | X | ABB | RADHA_3110 | RADHA 3110 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 156.082 | 611.1747 | 767.2566 | 49.6875 | 5.9058 | 79.874 |  | 9.8464 | 0.042169 | 0.0039776 | 0.038191 | 446.9473 | 1750.1243 | 2197.0716 | 142.2821 | 16.9115 | 228.7226 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 54.2636 | 0.10462 | 54.3682 | 14.6711 | 2.0677 | 0.013673 |  | 902.7239 | 2584.9877 | 71.1207 | 2513.867 |  | 0.040003 |  | 6.8694 | 7.1497 | 7.4416 | 7.7453 | 8.0614 | 8.3904 | 8.7329 | 9.0893 | 9.4603 | 9.8464 | 10.2482 | 10.6665 | 11.1019 | 11.555 | 12.0266 | 12.5174 | 13.0283 | 13.5601 | 14.1135 | 14.6896 | 15.2891 | 15.9131 | 16.5626 | 17.2386 | 17.9422 | 18.6745 | 19.4366 | 20.2299 | 21.0556 | 21.915 |  | 0.016313 | 0.018083 | 0.020059 | 0.022266 | 0.024731 | 0.027485 | 0.030564 | 0.034008 | 0.037859 | 0.042169 | 0.046992 | 0.052392 | 0.058439 | 0.065213 | 0.072802 | 0.081308 | 0.090842 | 0.10153 | 0.11352 | 0.12697 | 0.14205 | 0.15898 | 0.17798 | 0.19931 | 0.22326 | 0.25015 | 0.28035 | 0.31427 | 0.35238 | 0.3952 |  | 0.0015387 | 0.0017057 | 0.0018921 | 0.0021002 | 0.0023327 | 0.0025925 | 0.002883 | 0.0032078 | 0.0035711 | 0.0039776 | 0.0044325 | 0.0049419 | 0.0055123 | 0.0061512 | 0.0068671 | 0.0076693 | 0.0085687 | 0.009577 | 0.010708 | 0.011976 | 0.013399 | 0.014996 | 0.016788 | 0.0188 | 0.021059 | 0.023595 | 0.026444 | 0.029643 | 0.033238 | 0.037277 | 999.9795 | 1108.4996 | 1229.6361 | 1364.9064 | 1516.0147 | 1684.8745 | 1873.6347 | 2084.7097 | 2320.8116 | 2584.9877 | 2880.6629 | 3211.6859 | 3582.3832 | 3997.6183 | 4462.8593 | 4984.2546 | 5568.7185 | 6224.0269 | 6958.9259 | 7783.2537 | 8708.0779 | 9745.8504 | 10910.5812 | 12218.0354 | 13685.9535 | 15334.3014 | 17185.5504 | 19264.9937 | 21601.1025 | 24225.9274 |  | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 52.6536 | 69.7955 | 93.326 | 125.7717 | 170.6933 | 233.1174 | 320.1522 | 441.8633 | 612.5224 | 852.3883 | 1190.2483 | 1667.0455 | 2341.0597 |  | 172.8976 | 191.6608 | 212.6055 | 235.9939 | 262.1207 | 291.3167 | 323.9536 | 360.4487 | 401.2709 | 446.9473 | 498.0699 | 555.3041 | 619.3981 | 691.1927 | 771.6334 | 861.7833 | 962.8377 | 1076.1413 | 1203.2062 | 1345.7334 | 1505.6365 | 1685.0686 | 1886.4519 | 2112.5122 | 2366.3169 | 2651.3181 | 2971.4011 | 3330.9393 | 3734.8551 | 4188.6903 |  | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 32.4751 | 43.0476 | 57.5605 | 77.572 | 105.2781 | 143.7793 | 197.4595 | 272.527 | 377.784 | 525.7256 | 734.1068 | 1028.1799 | 1443.8901 |  | 145.7658 | 164.5291 | 185.4737 | 208.8621 | 234.9889 | 264.1849 | 296.8218 | 333.3169 | 374.1392 | 419.8155 | 470.9381 | 528.1723 | 592.2663 | 664.0609 | 744.5016 | 834.6515 | 935.706 | 1043.6663 | 1160.1586 | 1288.1729 | 1428.0646 | 1579.7905 | 1742.6726 | 1915.0526 | 2093.7899 | 2273.5341 | 2445.6755 | 2596.8325 | 2706.6753 | 2744.8002 |  | 677.02 | 750.4918 | 832.5053 | 924.0879 | 1026.3933 | 1140.7171 | 1268.5142 | 1411.4191 | 1571.268 | 1750.1243 | 1950.3063 | 2174.4201 | 2425.3948 | 2706.523 | 3021.5069 | 3374.5092 | 3770.2111 | 4213.877 | 4711.4286 | 5269.5264 | 5895.6638 | 6598.2709 | 7386.8331 | 8272.0238 | 9265.8541 | 10381.8415 | 11635.1998 | 13043.0534 | 14624.6781 | 16401.7735 |  | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.12523 | 0.16599 | 0.22196 | 0.29912 | 0.40596 | 0.55442 | 0.76141 | 1.0509 | 1.4568 | 2.0272 | 2.8308 | 3.9647 | 5.5677 |  | 676.9154 | 750.3872 | 832.4006 | 923.9833 | 1026.2887 | 1140.6125 | 1268.4096 | 1411.3145 | 1571.1634 | 1750.0196 | 1950.2017 | 2174.3155 | 2425.2901 | 2706.4184 | 3021.4023 | 3374.4046 | 3770.1065 | 4213.7518 | 4711.2626 | 5269.3045 | 5895.3646 | 6597.8649 | 7386.2787 | 8271.2624 | 9264.8033 | 10380.3848 | 11633.1726 | 13040.2226 | 14620.7134 | 16396.2058 |  | 822.6812 | 914.9162 | 1017.8743 | 1132.8454 | 1261.2776 | 1404.7974 | 1565.2314 | 1744.6314 | 1945.3026 | 2169.8352 | 2421.1398 | 2702.4879 | 3017.5565 | 3370.4793 | 3765.9039 | 4209.0561 | 4705.8124 | 5257.4181 | 5871.4211 | 6557.4774 | 7323.4292 | 8177.6554 | 9128.9513 | 10186.315 | 11358.5931 | 12653.9188 | 14078.8481 | 15637.0551 | 17327.3887 | 19141.006 |  | 55.0406 | 61.0137 | 67.6813 | 75.1268 | 83.444 | 92.7384 | 103.128 | 114.746 | 127.7414 | 142.2821 | 158.5566 | 176.7767 | 197.1805 | 220.0357 | 245.6434 | 274.3419 | 306.5117 | 342.581 | 383.0311 | 428.4035 | 479.3074 | 536.4282 | 600.537 | 672.5015 | 753.2982 | 844.026 | 945.9219 | 1060.378 | 1188.9614 | 1333.4363 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 40.3694 | 46.3426 | 53.0101 | 60.4556 | 68.7729 | 78.0672 | 88.4569 | 100.0748 | 113.0703 | 127.611 | 143.8854 | 162.1055 | 182.5093 | 205.3646 | 230.9722 | 259.6707 | 291.8406 | 325.0206 | 359.7537 | 397.2785 | 437.3615 | 479.5005 | 522.7903 | 565.728 | 605.933 | 639.7446 | 661.6432 | 663.4201 | 632.9875 | 552.6729 |  | 6.542 | 7.252 | 8.0445 | 8.9295 | 9.918 | 11.0228 | 12.2577 | 13.6385 | 15.1832 | 16.9115 | 18.8458 | 21.0114 | 23.4366 | 26.1531 | 29.1968 | 32.6079 | 36.4316 | 40.7187 | 45.5265 | 50.9194 | 56.9698 | 63.7591 | 71.379 | 79.9326 | 89.536 | 100.3198 | 112.431 | 126.0351 | 141.3183 | 158.4904 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 4.4744 | 5.1843 | 5.9768 | 6.8618 | 7.8503 | 8.9551 | 10.19 | 11.5709 | 13.1155 | 14.8438 | 16.7781 | 18.9437 | 21.3689 | 24.0854 | 27.1291 | 30.5402 | 34.3639 | 38.2438 | 42.2459 | 46.5328 | 51.0581 | 55.7359 | 60.4217 | 64.8843 | 68.7669 | 71.5291 | 72.3658 | 70.0893 | 62.9615 | 48.4526 |  | 88.4793 | 98.0813 | 108.7996 | 120.7684 | 134.1387 | 149.0796 | 165.7813 | 184.4574 | 205.348 | 228.7226 | 254.8842 | 284.1735 | 316.9732 | 353.7137 | 394.8787 | 441.0124 | 492.7264 | 550.7088 | 615.7335 | 688.6709 | 770.5004 | 862.3237 | 965.3803 | 1081.0653 | 1210.9484 | 1356.796 | 1520.5966 | 1704.588 | 1911.2895 | 2143.5369 |  | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.016366 | 0.021694 | 0.029007 | 0.039092 | 0.053054 | 0.072457 | 0.099509 | 0.13734 | 0.19038 | 0.26494 | 0.36995 | 0.51815 | 0.72764 |  | 88.4656 | 98.0676 | 108.7859 | 120.7548 | 134.125 | 149.0659 | 165.7676 | 184.4438 | 205.3343 | 228.7089 | 254.8706 | 284.1599 | 316.9596 | 353.7 | 394.8651 | 440.9987 | 492.7127 | 550.6924 | 615.7118 | 688.6419 | 770.4613 | 862.2706 | 965.3079 | 1080.9658 | 1210.811 | 1356.6056 | 1520.3316 | 1704.2181 | 1910.7714 | 2142.8093 |  | 955.9906 | 1064.5107 | 1185.6471 | 1320.9175 | 1472.0258 | 1640.8856 | 1829.6458 | 2040.7208 | 2276.8226 | 2540.9988 | 2836.674 | 3167.697 | 3538.3943 | 3953.6293 | 4418.8704 | 4940.2657 | 5524.7296 | 6171.3749 | 6889.1326 | 7689.9306 | 8582.3101 | 9575.1625 | 10677.4712 | 11897.8932 | 13244.104 | 14721.7982 | 16333.1887 | 18074.7826 | 19934.1091 | 21884.9408
| TRUE | 349 | 22004420 | BAN | Blank | 66 | BUS NO.2 | HIBP | X | ABB | RADHA_3110 | RADHA 3110 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 156.082 | 611.1747 | 767.2566 | 49.6875 | 5.9058 | 79.874 |  | 9.8464 | 0.042169 | 0.0039776 | 0.038191 | 446.9473 | 1750.1243 | 2197.0716 | 142.2821 | 16.9115 | 228.7226 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 54.2636 | 0.10462 | 54.3682 | 14.6711 | 2.0677 | 0.013673 |  | 902.7239 | 2584.9877 | 71.1207 | 2513.867 |  | 0.040003 |  | 6.8694 | 7.1497 | 7.4416 | 7.7453 | 8.0614 | 8.3904 | 8.7329 | 9.0893 | 9.4603 | 9.8464 | 10.2482 | 10.6665 | 11.1019 | 11.555 | 12.0266 | 12.5174 | 13.0283 | 13.5601 | 14.1135 | 14.6896 | 15.2891 | 15.9131 | 16.5626 | 17.2386 | 17.9422 | 18.6745 | 19.4366 | 20.2299 | 21.0556 | 21.915 |  | 0.016313 | 0.018083 | 0.020059 | 0.022266 | 0.024731 | 0.027485 | 0.030564 | 0.034008 | 0.037859 | 0.042169 | 0.046992 | 0.052392 | 0.058439 | 0.065213 | 0.072802 | 0.081308 | 0.090842 | 0.10153 | 0.11352 | 0.12697 | 0.14205 | 0.15898 | 0.17798 | 0.19931 | 0.22326 | 0.25015 | 0.28035 | 0.31427 | 0.35238 | 0.3952 |  | 0.0015387 | 0.0017057 | 0.0018921 | 0.0021002 | 0.0023327 | 0.0025925 | 0.002883 | 0.0032078 | 0.0035711 | 0.0039776 | 0.0044325 | 0.0049419 | 0.0055123 | 0.0061512 | 0.0068671 | 0.0076693 | 0.0085687 | 0.009577 | 0.010708 | 0.011976 | 0.013399 | 0.014996 | 0.016788 | 0.0188 | 0.021059 | 0.023595 | 0.026444 | 0.029643 | 0.033238 | 0.037277 | 999.9795 | 1108.4996 | 1229.6361 | 1364.9064 | 1516.0147 | 1684.8745 | 1873.6347 | 2084.7097 | 2320.8116 | 2584.9877 | 2880.6629 | 3211.6859 | 3582.3832 | 3997.6183 | 4462.8593 | 4984.2546 | 5568.7185 | 6224.0269 | 6958.9259 | 7783.2537 | 8708.0779 | 9745.8504 | 10910.5812 | 12218.0354 | 13685.9535 | 15334.3014 | 17185.5504 | 19264.9937 | 21601.1025 | 24225.9274 |  | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 43.9903 | 52.6536 | 69.7955 | 93.326 | 125.7717 | 170.6933 | 233.1174 | 320.1522 | 441.8633 | 612.5224 | 852.3883 | 1190.2483 | 1667.0455 | 2341.0597 |  | 172.8976 | 191.6608 | 212.6055 | 235.9939 | 262.1207 | 291.3167 | 323.9536 | 360.4487 | 401.2709 | 446.9473 | 498.0699 | 555.3041 | 619.3981 | 691.1927 | 771.6334 | 861.7833 | 962.8377 | 1076.1413 | 1203.2062 | 1345.7334 | 1505.6365 | 1685.0686 | 1886.4519 | 2112.5122 | 2366.3169 | 2651.3181 | 2971.4011 | 3330.9393 | 3734.8551 | 4188.6903 |  | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 32.4751 | 43.0476 | 57.5605 | 77.572 | 105.2781 | 143.7793 | 197.4595 | 272.527 | 377.784 | 525.7256 | 734.1068 | 1028.1799 | 1443.8901 |  | 145.7658 | 164.5291 | 185.4737 | 208.8621 | 234.9889 | 264.1849 | 296.8218 | 333.3169 | 374.1392 | 419.8155 | 470.9381 | 528.1723 | 592.2663 | 664.0609 | 744.5016 | 834.6515 | 935.706 | 1043.6663 | 1160.1586 | 1288.1729 | 1428.0646 | 1579.7905 | 1742.6726 | 1915.0526 | 2093.7899 | 2273.5341 | 2445.6755 | 2596.8325 | 2706.6753 | 2744.8002 |  | 677.02 | 750.4918 | 832.5053 | 924.0879 | 1026.3933 | 1140.7171 | 1268.5142 | 1411.4191 | 1571.268 | 1750.1243 | 1950.3063 | 2174.4201 | 2425.3948 | 2706.523 | 3021.5069 | 3374.5092 | 3770.2111 | 4213.877 | 4711.4286 | 5269.5264 | 5895.6638 | 6598.2709 | 7386.8331 | 8272.0238 | 9265.8541 | 10381.8415 | 11635.1998 | 13043.0534 | 14624.6781 | 16401.7735 |  | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.10462 | 0.12523 | 0.16599 | 0.22196 | 0.29912 | 0.40596 | 0.55442 | 0.76141 | 1.0509 | 1.4568 | 2.0272 | 2.8308 | 3.9647 | 5.5677 |  | 676.9154 | 750.3872 | 832.4006 | 923.9833 | 1026.2887 | 1140.6125 | 1268.4096 | 1411.3145 | 1571.1634 | 1750.0196 | 1950.2017 | 2174.3155 | 2425.2901 | 2706.4184 | 3021.4023 | 3374.4046 | 3770.1065 | 4213.7518 | 4711.2626 | 5269.3045 | 5895.3646 | 6597.8649 | 7386.2787 | 8271.2624 | 9264.8033 | 10380.3848 | 11633.1726 | 13040.2226 | 14620.7134 | 16396.2058 |  | 822.6812 | 914.9162 | 1017.8743 | 1132.8454 | 1261.2776 | 1404.7974 | 1565.2314 | 1744.6314 | 1945.3026 | 2169.8352 | 2421.1398 | 2702.4879 | 3017.5565 | 3370.4793 | 3765.9039 | 4209.0561 | 4705.8124 | 5257.4181 | 5871.4211 | 6557.4774 | 7323.4292 | 8177.6554 | 9128.9513 | 10186.315 | 11358.5931 | 12653.9188 | 14078.8481 | 15637.0551 | 17327.3887 | 19141.006 |  | 55.0406 | 61.0137 | 67.6813 | 75.1268 | 83.444 | 92.7384 | 103.128 | 114.746 | 127.7414 | 142.2821 | 158.5566 | 176.7767 | 197.1805 | 220.0357 | 245.6434 | 274.3419 | 306.5117 | 342.581 | 383.0311 | 428.4035 | 479.3074 | 536.4282 | 600.537 | 672.5015 | 753.2982 | 844.026 | 945.9219 | 1060.378 | 1188.9614 | 1333.4363 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 40.3694 | 46.3426 | 53.0101 | 60.4556 | 68.7729 | 78.0672 | 88.4569 | 100.0748 | 113.0703 | 127.611 | 143.8854 | 162.1055 | 182.5093 | 205.3646 | 230.9722 | 259.6707 | 291.8406 | 325.0206 | 359.7537 | 397.2785 | 437.3615 | 479.5005 | 522.7903 | 565.728 | 605.933 | 639.7446 | 661.6432 | 663.4201 | 632.9875 | 552.6729 |  | 6.542 | 7.252 | 8.0445 | 8.9295 | 9.918 | 11.0228 | 12.2577 | 13.6385 | 15.1832 | 16.9115 | 18.8458 | 21.0114 | 23.4366 | 26.1531 | 29.1968 | 32.6079 | 36.4316 | 40.7187 | 45.5265 | 50.9194 | 56.9698 | 63.7591 | 71.379 | 79.9326 | 89.536 | 100.3198 | 112.431 | 126.0351 | 141.3183 | 158.4904 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 4.4744 | 5.1843 | 5.9768 | 6.8618 | 7.8503 | 8.9551 | 10.19 | 11.5709 | 13.1155 | 14.8438 | 16.7781 | 18.9437 | 21.3689 | 24.0854 | 27.1291 | 30.5402 | 34.3639 | 38.2438 | 42.2459 | 46.5328 | 51.0581 | 55.7359 | 60.4217 | 64.8843 | 68.7669 | 71.5291 | 72.3658 | 70.0893 | 62.9615 | 48.4526 |  | 88.4793 | 98.0813 | 108.7996 | 120.7684 | 134.1387 | 149.0796 | 165.7813 | 184.4574 | 205.348 | 228.7226 | 254.8842 | 284.1735 | 316.9732 | 353.7137 | 394.8787 | 441.0124 | 492.7264 | 550.7088 | 615.7335 | 688.6709 | 770.5004 | 862.3237 | 965.3803 | 1081.0653 | 1210.9484 | 1356.796 | 1520.5966 | 1704.588 | 1911.2895 | 2143.5369 |  | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.013673 | 0.016366 | 0.021694 | 0.029007 | 0.039092 | 0.053054 | 0.072457 | 0.099509 | 0.13734 | 0.19038 | 0.26494 | 0.36995 | 0.51815 | 0.72764 |  | 88.4656 | 98.0676 | 108.7859 | 120.7548 | 134.125 | 149.0659 | 165.7676 | 184.4438 | 205.3343 | 228.7089 | 254.8706 | 284.1599 | 316.9596 | 353.7 | 394.8651 | 440.9987 | 492.7127 | 550.6924 | 615.7118 | 688.6419 | 770.4613 | 862.2706 | 965.3079 | 1080.9658 | 1210.811 | 1356.6056 | 1520.3316 | 1704.2181 | 1910.7714 | 2142.8093 |  | 955.9906 | 1064.5107 | 1185.6471 | 1320.9175 | 1472.0258 | 1640.8856 | 1829.6458 | 2040.7208 | 2276.8226 | 2540.9988 | 2836.674 | 3167.697 | 3538.3943 | 3953.6293 | 4418.8704 | 4940.2657 | 5524.7296 | 6171.3749 | 6889.1326 | 7689.9306 | 8582.3101 | 9575.1625 | 10677.4712 | 11897.8932 | 13244.104 | 14721.7982 | 16333.1887 | 18074.7826 | 19934.1091 | 21884.9408
| TRUE | 350 | 22004439 | BAN | Blank | 66 | CB A | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 275.999 | 0 | 275.999 | 74.6148 | 10.5169 | 0 |  | 12.7412 | 0.085397 | 0 | 0.085397 | 896.6656 | 0 | 896.6656 | 242.4085 | 34.1672 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 361.1306 | 1173.2413 | 71.0008 | 1102.2405 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405.1978 | 454.9471 | 511.1323 | 574.6089 | 646.3479 | 727.4518 | 819.1723 | 922.9311 | 1040.3428 | 1173.2413 | 1323.7103 | 1494.117 | 1687.1515 | 1905.8708 | 2153.7495 | 2434.7369 | 2753.3224 | 3114.6103 | 3524.4036 | 3989.3011 | 4516.8065 | 5115.4537 | 5794.9482 | 6566.3297 | 7442.1556 | 8436.7107 | 9566.2462 | 10849.2512 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 309.6779 | 347.6995 | 390.6398 | 439.1526 | 493.9801 | 555.9649 | 626.0635 | 705.3626 | 795.0961 | 896.6656 | 1011.6635 | 1141.8992 | 1289.4284 | 1456.5876 | 1646.0323 | 1860.7807 | 2104.264 | 2380.3831 | 2693.5732 | 3048.8774 | 3452.0306 | 3909.5548 | 4428.8678 | 5018.4065 | 5687.7683 | 6447.8705 | 7311.1334 | 8291.6873 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 282.5463 | 320.5678 | 363.5082 | 412.021 | 466.8485 | 528.8332 | 598.9319 | 678.231 | 767.9644 | 869.5339 | 984.5319 | 1114.7675 | 1262.2967 | 1429.456 | 1618.9006 | 1833.649 | 2077.1323 | 2347.9082 | 2650.5258 | 2991.3172 | 3374.459 | 3804.2772 | 4285.0892 | 4820.9479 | 5415.2426 | 6070.0883 | 6785.4102 | 7557.584 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 282.5463 | 320.5678 | 363.5082 | 412.021 | 466.8485 | 528.8332 | 598.9319 | 678.231 | 767.9644 | 869.5339 | 984.5319 | 1114.7675 | 1262.2967 | 1429.456 | 1618.9006 | 1833.649 | 2077.1323 | 2347.9082 | 2650.5258 | 2991.3172 | 3374.459 | 3804.2772 | 4285.0892 | 4820.9479 | 5415.2426 | 6070.0883 | 6785.4102 | 7557.584 | 7385.2433 | 6969.535 |  | 83.7197 | 93.9986 | 105.6073 | 118.7225 | 133.5448 | 150.302 | 169.2528 | 190.6908 | 214.9498 | 242.4085 | 273.4975 | 308.706 | 348.5897 | 393.7803 | 444.9956 | 503.0516 | 568.876 | 643.5232 | 728.1924 | 824.2469 | 933.2371 | 1056.9262 | 1197.3195 | 1356.698 | 1537.6562 | 1743.1456 | 1976.5238 | 2241.6111 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.0499 | 79.3288 | 90.9375 | 104.0527 | 118.875 | 135.6322 | 154.583 | 176.021 | 200.28 | 227.7387 | 258.8278 | 294.0362 | 333.9199 | 379.1105 | 430.3258 | 488.3818 | 554.2062 | 625.9644 | 704.9171 | 793.1247 | 891.295 | 1000.0038 | 1119.58 | 1249.9344 | 1390.3046 | 1538.8829 | 1692.2712 | 1844.6897 | 1718.5977 | 1493.8289 |  | 11.8002 | 13.249 | 14.8852 | 16.7338 | 18.823 | 21.1849 | 23.856 | 26.8777 | 30.2969 | 34.1672 | 38.5492 | 43.5118 | 49.1334 | 55.5029 | 62.7217 | 70.9046 | 80.1825 | 90.7039 | 102.638 | 116.1767 | 131.5388 | 148.9727 | 168.761 | 191.2252 | 216.7311 | 245.6946 | 278.589 | 315.9528 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7325 | 11.1813 | 12.8175 | 14.6661 | 16.7553 | 19.1172 | 21.7883 | 24.81 | 28.2293 | 32.0995 | 36.4815 | 41.4441 | 47.0657 | 53.4352 | 60.654 | 68.8369 | 78.1148 | 88.229 | 99.3573 | 111.7901 | 125.6271 | 140.9495 | 157.8037 | 176.177 | 195.962 | 216.904 | 238.5239 | 260.0071 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 361.3287 | 411.078 | 467.2632 | 530.7398 | 602.4788 | 683.5826 | 775.3032 | 879.062 | 996.4736 | 1129.3722 | 1279.8411 | 1450.2478 | 1643.2824 | 1862.0017 | 2109.8804 | 2390.8677 | 2709.4533 | 3062.1017 | 3454.8003 | 3896.2321 | 4391.3811 | 4945.2305 | 5562.4729 | 6247.0592 | 7001.5092 | 7825.8752 | 8716.2053 | 9662.2807 | 9346.0755 | 8673.9175
| TRUE | 351 | 22004440 | BAN | Blank | 66 | CB B | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 275.999 | 0 | 275.999 | 74.6148 | 10.5169 | 0 |  | 12.7412 | 0.085397 | 0 | 0.085397 | 896.6656 | 0 | 896.6656 | 242.4085 | 34.1672 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 361.1306 | 1173.2413 | 71.0008 | 1102.2405 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405.1978 | 454.9471 | 511.1323 | 574.6089 | 646.3479 | 727.4518 | 819.1723 | 922.9311 | 1040.3428 | 1173.2413 | 1323.7103 | 1494.117 | 1687.1515 | 1905.8708 | 2153.7495 | 2434.7369 | 2753.3224 | 3114.6103 | 3524.4036 | 3989.3011 | 4516.8065 | 5115.4537 | 5794.9482 | 6566.3297 | 7442.1556 | 8436.7107 | 9566.2462 | 10849.2512 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 309.6779 | 347.6995 | 390.6398 | 439.1526 | 493.9801 | 555.9649 | 626.0635 | 705.3626 | 795.0961 | 896.6656 | 1011.6635 | 1141.8992 | 1289.4284 | 1456.5876 | 1646.0323 | 1860.7807 | 2104.264 | 2380.3831 | 2693.5732 | 3048.8774 | 3452.0306 | 3909.5548 | 4428.8678 | 5018.4065 | 5687.7683 | 6447.8705 | 7311.1334 | 8291.6873 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 282.5463 | 320.5678 | 363.5082 | 412.021 | 466.8485 | 528.8332 | 598.9319 | 678.231 | 767.9644 | 869.5339 | 984.5319 | 1114.7675 | 1262.2967 | 1429.456 | 1618.9006 | 1833.649 | 2077.1323 | 2347.9082 | 2650.5258 | 2991.3172 | 3374.459 | 3804.2772 | 4285.0892 | 4820.9479 | 5415.2426 | 6070.0883 | 6785.4102 | 7557.584 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 282.5463 | 320.5678 | 363.5082 | 412.021 | 466.8485 | 528.8332 | 598.9319 | 678.231 | 767.9644 | 869.5339 | 984.5319 | 1114.7675 | 1262.2967 | 1429.456 | 1618.9006 | 1833.649 | 2077.1323 | 2347.9082 | 2650.5258 | 2991.3172 | 3374.459 | 3804.2772 | 4285.0892 | 4820.9479 | 5415.2426 | 6070.0883 | 6785.4102 | 7557.584 | 7385.2433 | 6969.535 |  | 83.7197 | 93.9986 | 105.6073 | 118.7225 | 133.5448 | 150.302 | 169.2528 | 190.6908 | 214.9498 | 242.4085 | 273.4975 | 308.706 | 348.5897 | 393.7803 | 444.9956 | 503.0516 | 568.876 | 643.5232 | 728.1924 | 824.2469 | 933.2371 | 1056.9262 | 1197.3195 | 1356.698 | 1537.6562 | 1743.1456 | 1976.5238 | 2241.6111 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.0499 | 79.3288 | 90.9375 | 104.0527 | 118.875 | 135.6322 | 154.583 | 176.021 | 200.28 | 227.7387 | 258.8278 | 294.0362 | 333.9199 | 379.1105 | 430.3258 | 488.3818 | 554.2062 | 625.9644 | 704.9171 | 793.1247 | 891.295 | 1000.0038 | 1119.58 | 1249.9344 | 1390.3046 | 1538.8829 | 1692.2712 | 1844.6897 | 1718.5977 | 1493.8289 |  | 11.8002 | 13.249 | 14.8852 | 16.7338 | 18.823 | 21.1849 | 23.856 | 26.8777 | 30.2969 | 34.1672 | 38.5492 | 43.5118 | 49.1334 | 55.5029 | 62.7217 | 70.9046 | 80.1825 | 90.7039 | 102.638 | 116.1767 | 131.5388 | 148.9727 | 168.761 | 191.2252 | 216.7311 | 245.6946 | 278.589 | 315.9528 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7325 | 11.1813 | 12.8175 | 14.6661 | 16.7553 | 19.1172 | 21.7883 | 24.81 | 28.2293 | 32.0995 | 36.4815 | 41.4441 | 47.0657 | 53.4352 | 60.654 | 68.8369 | 78.1148 | 88.229 | 99.3573 | 111.7901 | 125.6271 | 140.9495 | 157.8037 | 176.177 | 195.962 | 216.904 | 238.5239 | 260.0071 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 361.3287 | 411.078 | 467.2632 | 530.7398 | 602.4788 | 683.5826 | 775.3032 | 879.062 | 996.4736 | 1129.3722 | 1279.8411 | 1450.2478 | 1643.2824 | 1862.0017 | 2109.8804 | 2390.8677 | 2709.4533 | 3062.1017 | 3454.8003 | 3896.2321 | 4391.3811 | 4945.2305 | 5562.4729 | 6247.0592 | 7001.5092 | 7825.8752 | 8716.2053 | 9662.2807 | 9346.0755 | 8673.9175
| TRUE | 352 | 22004441 | BAN | Blank | 66 | CB C | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 275.999 | 0 | 275.999 | 74.6148 | 10.5169 | 0 |  | 12.7412 | 0.085397 | 0 | 0.085397 | 896.6656 | 0 | 896.6656 | 242.4085 | 34.1672 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 361.1306 | 1173.2413 | 71.0008 | 1102.2405 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405.1978 | 454.9471 | 511.1323 | 574.6089 | 646.3479 | 727.4518 | 819.1723 | 922.9311 | 1040.3428 | 1173.2413 | 1323.7103 | 1494.117 | 1687.1515 | 1905.8708 | 2153.7495 | 2434.7369 | 2753.3224 | 3114.6103 | 3524.4036 | 3989.3011 | 4516.8065 | 5115.4537 | 5794.9482 | 6566.3297 | 7442.1556 | 8436.7107 | 9566.2462 | 10849.2512 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 309.6779 | 347.6995 | 390.6398 | 439.1526 | 493.9801 | 555.9649 | 626.0635 | 705.3626 | 795.0961 | 896.6656 | 1011.6635 | 1141.8992 | 1289.4284 | 1456.5876 | 1646.0323 | 1860.7807 | 2104.264 | 2380.3831 | 2693.5732 | 3048.8774 | 3452.0306 | 3909.5548 | 4428.8678 | 5018.4065 | 5687.7683 | 6447.8705 | 7311.1334 | 8291.6873 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 282.5463 | 320.5678 | 363.5082 | 412.021 | 466.8485 | 528.8332 | 598.9319 | 678.231 | 767.9644 | 869.5339 | 984.5319 | 1114.7675 | 1262.2967 | 1429.456 | 1618.9006 | 1833.649 | 2077.1323 | 2347.9082 | 2650.5258 | 2991.3172 | 3374.459 | 3804.2772 | 4285.0892 | 4820.9479 | 5415.2426 | 6070.0883 | 6785.4102 | 7557.584 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 282.5463 | 320.5678 | 363.5082 | 412.021 | 466.8485 | 528.8332 | 598.9319 | 678.231 | 767.9644 | 869.5339 | 984.5319 | 1114.7675 | 1262.2967 | 1429.456 | 1618.9006 | 1833.649 | 2077.1323 | 2347.9082 | 2650.5258 | 2991.3172 | 3374.459 | 3804.2772 | 4285.0892 | 4820.9479 | 5415.2426 | 6070.0883 | 6785.4102 | 7557.584 | 7385.2433 | 6969.535 |  | 83.7197 | 93.9986 | 105.6073 | 118.7225 | 133.5448 | 150.302 | 169.2528 | 190.6908 | 214.9498 | 242.4085 | 273.4975 | 308.706 | 348.5897 | 393.7803 | 444.9956 | 503.0516 | 568.876 | 643.5232 | 728.1924 | 824.2469 | 933.2371 | 1056.9262 | 1197.3195 | 1356.698 | 1537.6562 | 1743.1456 | 1976.5238 | 2241.6111 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.0499 | 79.3288 | 90.9375 | 104.0527 | 118.875 | 135.6322 | 154.583 | 176.021 | 200.28 | 227.7387 | 258.8278 | 294.0362 | 333.9199 | 379.1105 | 430.3258 | 488.3818 | 554.2062 | 625.9644 | 704.9171 | 793.1247 | 891.295 | 1000.0038 | 1119.58 | 1249.9344 | 1390.3046 | 1538.8829 | 1692.2712 | 1844.6897 | 1718.5977 | 1493.8289 |  | 11.8002 | 13.249 | 14.8852 | 16.7338 | 18.823 | 21.1849 | 23.856 | 26.8777 | 30.2969 | 34.1672 | 38.5492 | 43.5118 | 49.1334 | 55.5029 | 62.7217 | 70.9046 | 80.1825 | 90.7039 | 102.638 | 116.1767 | 131.5388 | 148.9727 | 168.761 | 191.2252 | 216.7311 | 245.6946 | 278.589 | 315.9528 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7325 | 11.1813 | 12.8175 | 14.6661 | 16.7553 | 19.1172 | 21.7883 | 24.81 | 28.2293 | 32.0995 | 36.4815 | 41.4441 | 47.0657 | 53.4352 | 60.654 | 68.8369 | 78.1148 | 88.229 | 99.3573 | 111.7901 | 125.6271 | 140.9495 | 157.8037 | 176.177 | 195.962 | 216.904 | 238.5239 | 260.0071 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 361.3287 | 411.078 | 467.2632 | 530.7398 | 602.4788 | 683.5826 | 775.3032 | 879.062 | 996.4736 | 1129.3722 | 1279.8411 | 1450.2478 | 1643.2824 | 1862.0017 | 2109.8804 | 2390.8677 | 2709.4533 | 3062.1017 | 3454.8003 | 3896.2321 | 4391.3811 | 4945.2305 | 5562.4729 | 6247.0592 | 7001.5092 | 7825.8752 | 8716.2053 | 9662.2807 | 9346.0755 | 8673.9175
| TRUE | 353 | 22004442 | BAN | Blank | 66 | CB E | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 275.999 | 0 | 275.999 | 74.6148 | 10.5169 | 0 |  | 12.7412 | 0.085397 | 0 | 0.085397 | 896.6656 | 0 | 896.6656 | 242.4085 | 34.1672 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 361.1306 | 1173.2413 | 71.0008 | 1102.2405 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405.1978 | 454.9471 | 511.1323 | 574.6089 | 646.3479 | 727.4518 | 819.1723 | 922.9311 | 1040.3428 | 1173.2413 | 1323.7103 | 1494.117 | 1687.1515 | 1905.8708 | 2153.7495 | 2434.7369 | 2753.3224 | 3114.6103 | 3524.4036 | 3989.3011 | 4516.8065 | 5115.4537 | 5794.9482 | 6566.3297 | 7442.1556 | 8436.7107 | 9566.2462 | 10849.2512 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 309.6779 | 347.6995 | 390.6398 | 439.1526 | 493.9801 | 555.9649 | 626.0635 | 705.3626 | 795.0961 | 896.6656 | 1011.6635 | 1141.8992 | 1289.4284 | 1456.5876 | 1646.0323 | 1860.7807 | 2104.264 | 2380.3831 | 2693.5732 | 3048.8774 | 3452.0306 | 3909.5548 | 4428.8678 | 5018.4065 | 5687.7683 | 6447.8705 | 7311.1334 | 8291.6873 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 282.5463 | 320.5678 | 363.5082 | 412.021 | 466.8485 | 528.8332 | 598.9319 | 678.231 | 767.9644 | 869.5339 | 984.5319 | 1114.7675 | 1262.2967 | 1429.456 | 1618.9006 | 1833.649 | 2077.1323 | 2347.9082 | 2650.5258 | 2991.3172 | 3374.459 | 3804.2772 | 4285.0892 | 4820.9479 | 5415.2426 | 6070.0883 | 6785.4102 | 7557.584 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 282.5463 | 320.5678 | 363.5082 | 412.021 | 466.8485 | 528.8332 | 598.9319 | 678.231 | 767.9644 | 869.5339 | 984.5319 | 1114.7675 | 1262.2967 | 1429.456 | 1618.9006 | 1833.649 | 2077.1323 | 2347.9082 | 2650.5258 | 2991.3172 | 3374.459 | 3804.2772 | 4285.0892 | 4820.9479 | 5415.2426 | 6070.0883 | 6785.4102 | 7557.584 | 7385.2433 | 6969.535 |  | 83.7197 | 93.9986 | 105.6073 | 118.7225 | 133.5448 | 150.302 | 169.2528 | 190.6908 | 214.9498 | 242.4085 | 273.4975 | 308.706 | 348.5897 | 393.7803 | 444.9956 | 503.0516 | 568.876 | 643.5232 | 728.1924 | 824.2469 | 933.2371 | 1056.9262 | 1197.3195 | 1356.698 | 1537.6562 | 1743.1456 | 1976.5238 | 2241.6111 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.0499 | 79.3288 | 90.9375 | 104.0527 | 118.875 | 135.6322 | 154.583 | 176.021 | 200.28 | 227.7387 | 258.8278 | 294.0362 | 333.9199 | 379.1105 | 430.3258 | 488.3818 | 554.2062 | 625.9644 | 704.9171 | 793.1247 | 891.295 | 1000.0038 | 1119.58 | 1249.9344 | 1390.3046 | 1538.8829 | 1692.2712 | 1844.6897 | 1718.5977 | 1493.8289 |  | 11.8002 | 13.249 | 14.8852 | 16.7338 | 18.823 | 21.1849 | 23.856 | 26.8777 | 30.2969 | 34.1672 | 38.5492 | 43.5118 | 49.1334 | 55.5029 | 62.7217 | 70.9046 | 80.1825 | 90.7039 | 102.638 | 116.1767 | 131.5388 | 148.9727 | 168.761 | 191.2252 | 216.7311 | 245.6946 | 278.589 | 315.9528 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7325 | 11.1813 | 12.8175 | 14.6661 | 16.7553 | 19.1172 | 21.7883 | 24.81 | 28.2293 | 32.0995 | 36.4815 | 41.4441 | 47.0657 | 53.4352 | 60.654 | 68.8369 | 78.1148 | 88.229 | 99.3573 | 111.7901 | 125.6271 | 140.9495 | 157.8037 | 176.177 | 195.962 | 216.904 | 238.5239 | 260.0071 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 361.3287 | 411.078 | 467.2632 | 530.7398 | 602.4788 | 683.5826 | 775.3032 | 879.062 | 996.4736 | 1129.3722 | 1279.8411 | 1450.2478 | 1643.2824 | 1862.0017 | 2109.8804 | 2390.8677 | 2709.4533 | 3062.1017 | 3454.8003 | 3896.2321 | 4391.3811 | 4945.2305 | 5562.4729 | 6247.0592 | 7001.5092 | 7825.8752 | 8716.2053 | 9662.2807 | 9346.0755 | 8673.9175
| TRUE | 354 | 22004443 | BAN | Blank | 66 | CB F | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 275.999 | 0 | 275.999 | 74.6148 | 10.5169 | 0 |  | 12.7412 | 0.085397 | 0 | 0.085397 | 896.6656 | 0 | 896.6656 | 242.4085 | 34.1672 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 361.1306 | 1173.2413 | 71.0008 | 1102.2405 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405.1978 | 454.9471 | 511.1323 | 574.6089 | 646.3479 | 727.4518 | 819.1723 | 922.9311 | 1040.3428 | 1173.2413 | 1323.7103 | 1494.117 | 1687.1515 | 1905.8708 | 2153.7495 | 2434.7369 | 2753.3224 | 3114.6103 | 3524.4036 | 3989.3011 | 4516.8065 | 5115.4537 | 5794.9482 | 6566.3297 | 7442.1556 | 8436.7107 | 9566.2462 | 10849.2512 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 309.6779 | 347.6995 | 390.6398 | 439.1526 | 493.9801 | 555.9649 | 626.0635 | 705.3626 | 795.0961 | 896.6656 | 1011.6635 | 1141.8992 | 1289.4284 | 1456.5876 | 1646.0323 | 1860.7807 | 2104.264 | 2380.3831 | 2693.5732 | 3048.8774 | 3452.0306 | 3909.5548 | 4428.8678 | 5018.4065 | 5687.7683 | 6447.8705 | 7311.1334 | 8291.6873 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 282.5463 | 320.5678 | 363.5082 | 412.021 | 466.8485 | 528.8332 | 598.9319 | 678.231 | 767.9644 | 869.5339 | 984.5319 | 1114.7675 | 1262.2967 | 1429.456 | 1618.9006 | 1833.649 | 2077.1323 | 2347.9082 | 2650.5258 | 2991.3172 | 3374.459 | 3804.2772 | 4285.0892 | 4820.9479 | 5415.2426 | 6070.0883 | 6785.4102 | 7557.584 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 282.5463 | 320.5678 | 363.5082 | 412.021 | 466.8485 | 528.8332 | 598.9319 | 678.231 | 767.9644 | 869.5339 | 984.5319 | 1114.7675 | 1262.2967 | 1429.456 | 1618.9006 | 1833.649 | 2077.1323 | 2347.9082 | 2650.5258 | 2991.3172 | 3374.459 | 3804.2772 | 4285.0892 | 4820.9479 | 5415.2426 | 6070.0883 | 6785.4102 | 7557.584 | 7385.2433 | 6969.535 |  | 83.7197 | 93.9986 | 105.6073 | 118.7225 | 133.5448 | 150.302 | 169.2528 | 190.6908 | 214.9498 | 242.4085 | 273.4975 | 308.706 | 348.5897 | 393.7803 | 444.9956 | 503.0516 | 568.876 | 643.5232 | 728.1924 | 824.2469 | 933.2371 | 1056.9262 | 1197.3195 | 1356.698 | 1537.6562 | 1743.1456 | 1976.5238 | 2241.6111 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.0499 | 79.3288 | 90.9375 | 104.0527 | 118.875 | 135.6322 | 154.583 | 176.021 | 200.28 | 227.7387 | 258.8278 | 294.0362 | 333.9199 | 379.1105 | 430.3258 | 488.3818 | 554.2062 | 625.9644 | 704.9171 | 793.1247 | 891.295 | 1000.0038 | 1119.58 | 1249.9344 | 1390.3046 | 1538.8829 | 1692.2712 | 1844.6897 | 1718.5977 | 1493.8289 |  | 11.8002 | 13.249 | 14.8852 | 16.7338 | 18.823 | 21.1849 | 23.856 | 26.8777 | 30.2969 | 34.1672 | 38.5492 | 43.5118 | 49.1334 | 55.5029 | 62.7217 | 70.9046 | 80.1825 | 90.7039 | 102.638 | 116.1767 | 131.5388 | 148.9727 | 168.761 | 191.2252 | 216.7311 | 245.6946 | 278.589 | 315.9528 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7325 | 11.1813 | 12.8175 | 14.6661 | 16.7553 | 19.1172 | 21.7883 | 24.81 | 28.2293 | 32.0995 | 36.4815 | 41.4441 | 47.0657 | 53.4352 | 60.654 | 68.8369 | 78.1148 | 88.229 | 99.3573 | 111.7901 | 125.6271 | 140.9495 | 157.8037 | 176.177 | 195.962 | 216.904 | 238.5239 | 260.0071 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 361.3287 | 411.078 | 467.2632 | 530.7398 | 602.4788 | 683.5826 | 775.3032 | 879.062 | 996.4736 | 1129.3722 | 1279.8411 | 1450.2478 | 1643.2824 | 1862.0017 | 2109.8804 | 2390.8677 | 2709.4533 | 3062.1017 | 3454.8003 | 3896.2321 | 4391.3811 | 4945.2305 | 5562.4729 | 6247.0592 | 7001.5092 | 7825.8752 | 8716.2053 | 9662.2807 | 9346.0755 | 8673.9175
| TRUE | 355 | 22004444 | BAN | Blank | 66 | CB G | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 275.999 | 0 | 275.999 | 74.6148 | 10.5169 | 0 |  | 12.7412 | 0.085397 | 0 | 0.085397 | 896.6656 | 0 | 896.6656 | 242.4085 | 34.1672 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 361.1306 | 1173.2413 | 71.0008 | 1102.2405 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405.1978 | 454.9471 | 511.1323 | 574.6089 | 646.3479 | 727.4518 | 819.1723 | 922.9311 | 1040.3428 | 1173.2413 | 1323.7103 | 1494.117 | 1687.1515 | 1905.8708 | 2153.7495 | 2434.7369 | 2753.3224 | 3114.6103 | 3524.4036 | 3989.3011 | 4516.8065 | 5115.4537 | 5794.9482 | 6566.3297 | 7442.1556 | 8436.7107 | 9566.2462 | 10849.2512 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 309.6779 | 347.6995 | 390.6398 | 439.1526 | 493.9801 | 555.9649 | 626.0635 | 705.3626 | 795.0961 | 896.6656 | 1011.6635 | 1141.8992 | 1289.4284 | 1456.5876 | 1646.0323 | 1860.7807 | 2104.264 | 2380.3831 | 2693.5732 | 3048.8774 | 3452.0306 | 3909.5548 | 4428.8678 | 5018.4065 | 5687.7683 | 6447.8705 | 7311.1334 | 8291.6873 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 282.5463 | 320.5678 | 363.5082 | 412.021 | 466.8485 | 528.8332 | 598.9319 | 678.231 | 767.9644 | 869.5339 | 984.5319 | 1114.7675 | 1262.2967 | 1429.456 | 1618.9006 | 1833.649 | 2077.1323 | 2347.9082 | 2650.5258 | 2991.3172 | 3374.459 | 3804.2772 | 4285.0892 | 4820.9479 | 5415.2426 | 6070.0883 | 6785.4102 | 7557.584 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 282.5463 | 320.5678 | 363.5082 | 412.021 | 466.8485 | 528.8332 | 598.9319 | 678.231 | 767.9644 | 869.5339 | 984.5319 | 1114.7675 | 1262.2967 | 1429.456 | 1618.9006 | 1833.649 | 2077.1323 | 2347.9082 | 2650.5258 | 2991.3172 | 3374.459 | 3804.2772 | 4285.0892 | 4820.9479 | 5415.2426 | 6070.0883 | 6785.4102 | 7557.584 | 7385.2433 | 6969.535 |  | 83.7197 | 93.9986 | 105.6073 | 118.7225 | 133.5448 | 150.302 | 169.2528 | 190.6908 | 214.9498 | 242.4085 | 273.4975 | 308.706 | 348.5897 | 393.7803 | 444.9956 | 503.0516 | 568.876 | 643.5232 | 728.1924 | 824.2469 | 933.2371 | 1056.9262 | 1197.3195 | 1356.698 | 1537.6562 | 1743.1456 | 1976.5238 | 2241.6111 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.0499 | 79.3288 | 90.9375 | 104.0527 | 118.875 | 135.6322 | 154.583 | 176.021 | 200.28 | 227.7387 | 258.8278 | 294.0362 | 333.9199 | 379.1105 | 430.3258 | 488.3818 | 554.2062 | 625.9644 | 704.9171 | 793.1247 | 891.295 | 1000.0038 | 1119.58 | 1249.9344 | 1390.3046 | 1538.8829 | 1692.2712 | 1844.6897 | 1718.5977 | 1493.8289 |  | 11.8002 | 13.249 | 14.8852 | 16.7338 | 18.823 | 21.1849 | 23.856 | 26.8777 | 30.2969 | 34.1672 | 38.5492 | 43.5118 | 49.1334 | 55.5029 | 62.7217 | 70.9046 | 80.1825 | 90.7039 | 102.638 | 116.1767 | 131.5388 | 148.9727 | 168.761 | 191.2252 | 216.7311 | 245.6946 | 278.589 | 315.9528 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7325 | 11.1813 | 12.8175 | 14.6661 | 16.7553 | 19.1172 | 21.7883 | 24.81 | 28.2293 | 32.0995 | 36.4815 | 41.4441 | 47.0657 | 53.4352 | 60.654 | 68.8369 | 78.1148 | 88.229 | 99.3573 | 111.7901 | 125.6271 | 140.9495 | 157.8037 | 176.177 | 195.962 | 216.904 | 238.5239 | 260.0071 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 361.3287 | 411.078 | 467.2632 | 530.7398 | 602.4788 | 683.5826 | 775.3032 | 879.062 | 996.4736 | 1129.3722 | 1279.8411 | 1450.2478 | 1643.2824 | 1862.0017 | 2109.8804 | 2390.8677 | 2709.4533 | 3062.1017 | 3454.8003 | 3896.2321 | 4391.3811 | 4945.2305 | 5562.4729 | 6247.0592 | 7001.5092 | 7825.8752 | 8716.2053 | 9662.2807 | 9346.0755 | 8673.9175
| TRUE | 356 | 22004445 | BAN | Blank | 66 | CB H | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 275.999 | 0 | 275.999 | 74.6148 | 10.5169 | 0 |  | 12.7412 | 0.085397 | 0 | 0.085397 | 896.6656 | 0 | 896.6656 | 242.4085 | 34.1672 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 361.1306 | 1173.2413 | 71.0008 | 1102.2405 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405.1978 | 454.9471 | 511.1323 | 574.6089 | 646.3479 | 727.4518 | 819.1723 | 922.9311 | 1040.3428 | 1173.2413 | 1323.7103 | 1494.117 | 1687.1515 | 1905.8708 | 2153.7495 | 2434.7369 | 2753.3224 | 3114.6103 | 3524.4036 | 3989.3011 | 4516.8065 | 5115.4537 | 5794.9482 | 6566.3297 | 7442.1556 | 8436.7107 | 9566.2462 | 10849.2512 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 309.6779 | 347.6995 | 390.6398 | 439.1526 | 493.9801 | 555.9649 | 626.0635 | 705.3626 | 795.0961 | 896.6656 | 1011.6635 | 1141.8992 | 1289.4284 | 1456.5876 | 1646.0323 | 1860.7807 | 2104.264 | 2380.3831 | 2693.5732 | 3048.8774 | 3452.0306 | 3909.5548 | 4428.8678 | 5018.4065 | 5687.7683 | 6447.8705 | 7311.1334 | 8291.6873 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 282.5463 | 320.5678 | 363.5082 | 412.021 | 466.8485 | 528.8332 | 598.9319 | 678.231 | 767.9644 | 869.5339 | 984.5319 | 1114.7675 | 1262.2967 | 1429.456 | 1618.9006 | 1833.649 | 2077.1323 | 2347.9082 | 2650.5258 | 2991.3172 | 3374.459 | 3804.2772 | 4285.0892 | 4820.9479 | 5415.2426 | 6070.0883 | 6785.4102 | 7557.584 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 282.5463 | 320.5678 | 363.5082 | 412.021 | 466.8485 | 528.8332 | 598.9319 | 678.231 | 767.9644 | 869.5339 | 984.5319 | 1114.7675 | 1262.2967 | 1429.456 | 1618.9006 | 1833.649 | 2077.1323 | 2347.9082 | 2650.5258 | 2991.3172 | 3374.459 | 3804.2772 | 4285.0892 | 4820.9479 | 5415.2426 | 6070.0883 | 6785.4102 | 7557.584 | 7385.2433 | 6969.535 |  | 83.7197 | 93.9986 | 105.6073 | 118.7225 | 133.5448 | 150.302 | 169.2528 | 190.6908 | 214.9498 | 242.4085 | 273.4975 | 308.706 | 348.5897 | 393.7803 | 444.9956 | 503.0516 | 568.876 | 643.5232 | 728.1924 | 824.2469 | 933.2371 | 1056.9262 | 1197.3195 | 1356.698 | 1537.6562 | 1743.1456 | 1976.5238 | 2241.6111 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.0499 | 79.3288 | 90.9375 | 104.0527 | 118.875 | 135.6322 | 154.583 | 176.021 | 200.28 | 227.7387 | 258.8278 | 294.0362 | 333.9199 | 379.1105 | 430.3258 | 488.3818 | 554.2062 | 625.9644 | 704.9171 | 793.1247 | 891.295 | 1000.0038 | 1119.58 | 1249.9344 | 1390.3046 | 1538.8829 | 1692.2712 | 1844.6897 | 1718.5977 | 1493.8289 |  | 11.8002 | 13.249 | 14.8852 | 16.7338 | 18.823 | 21.1849 | 23.856 | 26.8777 | 30.2969 | 34.1672 | 38.5492 | 43.5118 | 49.1334 | 55.5029 | 62.7217 | 70.9046 | 80.1825 | 90.7039 | 102.638 | 116.1767 | 131.5388 | 148.9727 | 168.761 | 191.2252 | 216.7311 | 245.6946 | 278.589 | 315.9528 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7325 | 11.1813 | 12.8175 | 14.6661 | 16.7553 | 19.1172 | 21.7883 | 24.81 | 28.2293 | 32.0995 | 36.4815 | 41.4441 | 47.0657 | 53.4352 | 60.654 | 68.8369 | 78.1148 | 88.229 | 99.3573 | 111.7901 | 125.6271 | 140.9495 | 157.8037 | 176.177 | 195.962 | 216.904 | 238.5239 | 260.0071 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 361.3287 | 411.078 | 467.2632 | 530.7398 | 602.4788 | 683.5826 | 775.3032 | 879.062 | 996.4736 | 1129.3722 | 1279.8411 | 1450.2478 | 1643.2824 | 1862.0017 | 2109.8804 | 2390.8677 | 2709.4533 | 3062.1017 | 3454.8003 | 3896.2321 | 4391.3811 | 4945.2305 | 5562.4729 | 6247.0592 | 7001.5092 | 7825.8752 | 8716.2053 | 9662.2807 | 9346.0755 | 8673.9175
| FALSE | 357 | 22004907 | BAN | BAN-BATS NO.1 | 66 | BATS NO.1 LINE | DIR OC & DIR EF | Y | Schweitzer | SEL_351A | SEL 351 | SEL 300s | Digital |  | 0.016937 | 1 |  | 6.6 | 0.017308 | 4.0157e-07 | 0.017307 | 113.5831 | 0.066259 | 113.6493 | 49.1326 | 6.9249 | 0.023091 |  | 14.9721 | 0.15742 | 3.6523e-06 | 0.15741 | 1033.0517 | 0.60263 | 1033.6544 | 446.8673 | 62.9826 | 0.21002 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 33.9147 | 0.019784 | 33.9344 | 14.6705 | 2.0677 | 0.0068949 |  | 169.7299 | 1543.7143 | 50.6795 | 1493.0348 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021358 | 0.026432 | 0.032797 | 0.040794 | 0.050854 | 0.063527 | 0.079507 | 0.099681 | 0.12517 | 0.15742 | 0.19823 | 0.24994 | 0.31549 | 0.39864 | 0.5042 | 0.63826 | 0.80862 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.9554e-07 | 6.1325e-07 | 7.6093e-07 | 9.4647e-07 | 1.1799e-06 | 1.4739e-06 | 1.8447e-06 | 2.3128e-06 | 2.9042e-06 | 3.6523e-06 | 4.5993e-06 | 5.7989e-06 | 7.3198e-06 | 9.2491e-06 | 1.1698e-05 | 1.4809e-05 | 1.8761e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 209.4485 | 259.2016 | 321.6207 | 400.0428 | 498.7023 | 622.9751 | 779.6904 | 977.5277 | 1227.5229 | 1543.7143 | 1943.9662 | 2451.0202 | 3093.836 | 3909.3035 | 4944.4274 | 6259.1166 | 7929.7458 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 |  | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 52.5416 | 69.6471 | 93.1276 | 125.5043 | 170.3303 | 232.6216 | 319.4713 | 440.9236 | 611.2198 | 850.5757 | 1187.7172 | 1663.5004 | 2336.0813 |  | 140.1627 | 173.4574 | 215.2282 | 267.7082 | 333.731 | 416.8942 | 521.7679 | 654.1604 | 821.4569 | 1033.0517 | 1300.8999 | 1640.2198 | 2070.3914 | 2616.1012 | 3308.8049 | 4188.5934 | 5306.5764 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 113.031 | 146.3257 | 188.0965 | 240.5765 | 306.5992 | 389.7625 | 494.6362 | 627.0287 | 794.3251 | 1005.92 | 1273.7681 | 1613.088 | 2043.2596 | 2588.9695 | 3281.6732 | 4161.4617 | 5279.4447 | 6147.8398 | 6137.2673 | 6122.7545 | 6102.743 | 6075.037 | 6036.5359 | 5982.8557 | 5907.7884 | 5802.5316 | 5654.5904 | 5446.2097 | 5152.1373 | 4736.428 |  | 0.081764 | 0.10119 | 0.12555 | 0.15617 | 0.19468 | 0.2432 | 0.30437 | 0.3816 | 0.4792 | 0.60263 | 0.75888 | 0.95682 | 1.2078 | 1.5261 | 1.9302 | 2.4434 | 3.0956 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 |  | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.02368 | 0.03139 | 0.041972 | 0.056564 | 0.076767 | 0.10484 | 0.14398 | 0.19872 | 0.27547 | 0.38335 | 0.5353 | 0.74973 | 1.0529 |  | 0.06198 | 0.081402 | 0.10577 | 0.13638 | 0.1749 | 0.22341 | 0.28459 | 0.36182 | 0.45941 | 0.58285 | 0.7391 | 0.93704 | 1.188 | 1.5063 | 1.9104 | 2.4236 | 3.0758 | 3.5816 | 3.5739 | 3.5633 | 3.5487 | 3.5285 | 3.5004 | 3.4613 | 3.4066 | 3.3298 | 3.2219 | 3.07 | 2.8556 | 2.5524 |  | 113.0929 | 146.4071 | 188.2022 | 240.7128 | 306.7741 | 389.9859 | 494.9208 | 627.3905 | 794.7845 | 1006.5029 | 1274.5072 | 1614.0251 | 2044.4476 | 2590.4758 | 3283.5836 | 4163.8853 | 5282.5205 | 6151.4214 | 6140.8412 | 6126.3178 | 6106.2917 | 6078.5655 | 6040.0363 | 5986.317 | 5911.195 | 5805.8615 | 5657.8123 | 5449.2797 | 5154.9928 | 4738.9804 |  | 60.6302 | 75.0325 | 93.1013 | 115.8025 | 144.362 | 180.336 | 225.7012 | 282.9702 | 355.3377 | 446.8673 | 562.7304 | 709.51 | 895.5894 | 1131.6471 | 1431.29 | 1811.8602 | 2295.4662 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 45.9597 | 60.362 | 78.4308 | 101.1321 | 129.6916 | 165.6655 | 211.0307 | 268.2997 | 340.6672 | 432.1968 | 548.0599 | 694.8395 | 880.9189 | 1116.9766 | 1416.6195 | 1797.1897 | 2280.7957 | 2655.8596 | 2650.1429 | 2642.2957 | 2631.4752 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 8.5454 | 10.5753 | 13.1219 | 16.3215 | 20.3467 | 25.417 | 31.8109 | 39.8825 | 50.0822 | 62.9826 | 79.3126 | 100.0001 | 126.2266 | 159.4972 | 201.7296 | 255.3681 | 323.5288 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 6.4777 | 8.5076 | 11.0542 | 14.2538 | 18.2791 | 23.3493 | 29.7432 | 37.8148 | 48.0145 | 60.9149 | 77.2449 | 97.9324 | 124.1589 | 157.4295 | 199.6619 | 253.3004 | 321.4611 | 374.3235 | 373.5178 | 372.4118 | 370.8867 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.028495 | 0.035264 | 0.043756 | 0.054425 | 0.067848 | 0.084755 | 0.10608 | 0.13299 | 0.167 | 0.21002 | 0.26447 | 0.33346 | 0.42091 | 0.53185 | 0.67268 | 0.85154 | 1.0788 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 |  | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0082527 | 0.010939 | 0.014628 | 0.019713 | 0.026754 | 0.036538 | 0.050179 | 0.069256 | 0.096004 | 0.1336 | 0.18655 | 0.26129 | 0.36693 |  | 0.0216 | 0.028369 | 0.036861 | 0.04753 | 0.060953 | 0.07786 | 0.099181 | 0.1261 | 0.16011 | 0.20312 | 0.25758 | 0.32656 | 0.41402 | 0.52496 | 0.66579 | 0.84465 | 1.0719 | 1.2482 | 1.2455 | 1.2418 | 1.2367 | 1.2297 | 1.2199 | 1.2063 | 1.1872 | 1.1605 | 1.1229 | 1.0699 | 0.99517 | 0.88953 |  | 165.5519 | 215.305 | 277.7241 | 356.1463 | 454.8057 | 579.0785 | 735.7939 | 933.6312 | 1183.6263 | 1499.8177 | 1900.0696 | 2407.1236 | 3049.9394 | 3865.4069 | 4900.5308 | 6215.2201 | 7885.8492 | 9182.8528 | 9165.7475 | 9142.267 | 9109.8904 | 9065.0646 | 9002.7735 | 8915.9241 | 8794.4724 | 8624.1769 | 8384.8219 | 8047.6817 | 7571.9004 | 6899.3222
| FALSE | 358 | 22015669 | BAN | BAN-BATS NO.1 | 66 | BATS NO.1 LINE | REM TRIP SEND/RCVE | Y | Schweitzer | SEL_2505 | SEL 2505 | SEL 2000s | Digital |  | 0.016937 | 1 |  | 5.5 | 0.010964 | 2.5438e-07 | 0.010964 | 71.9504 | 0.041972 | 71.9924 | 31.1236 | 4.3866 | 0.014628 |  | 11.7751 | 0.080727 | 1.873e-06 | 0.080725 | 529.7716 | 0.30904 | 530.0806 | 229.1633 | 32.2989 | 0.1077 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 33.9147 | 0.019784 | 33.9344 | 14.6705 | 2.0677 | 0.0068949 |  | 107.5173 | 791.6505 | 50.6795 | 740.971 |  | 0.076124 |  | 5.935 | 6.4045 | 6.911 | 7.4577 | 8.0475 | 8.6841 | 9.3709 | 10.1121 | 10.912 | 11.7751 | 12.7064 | 13.7115 | 14.796 | 15.9663 | 17.2292 | 18.5919 | 20.0625 | 21.6493 | 23.3617 | 25.2095 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.013239 | 0.016034 | 0.019473 | 0.023709 | 0.028935 | 0.035391 | 0.043377 | 0.053265 | 0.065521 | 0.080727 | 0.099611 | 0.12308 | 0.15228 | 0.18862 | 0.23389 | 0.29032 | 0.36069 | 0.44851 | 0.55815 | 0.6951 | 0.86622 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 3.0717e-07 | 3.7202e-07 | 4.5179e-07 | 5.5008e-07 | 6.7134e-07 | 8.2113e-07 | 1.0064e-06 | 1.2358e-06 | 1.5202e-06 | 1.873e-06 | 2.3111e-06 | 2.8557e-06 | 3.5331e-06 | 4.3763e-06 | 5.4266e-06 | 6.7358e-06 | 8.3686e-06 | 1.0406e-05 | 1.295e-05 | 1.6127e-05 | 2.0098e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 129.8314 | 157.2396 | 190.958 | 232.5004 | 283.7532 | 347.0676 | 425.3766 | 522.3404 | 642.5289 | 791.6505 | 976.8388 | 1207.0117 | 1493.3222 | 1849.7226 | 2293.6731 | 2847.0304 | 3537.1617 | 4398.3426 | 5473.512 | 6816.4726 | 8494.6537 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 |  | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 52.5416 | 69.6471 | 93.1276 | 125.5043 | 170.3303 | 232.6216 | 319.4713 | 440.9236 | 611.2198 | 850.5757 | 1187.7172 | 1663.5004 | 2336.0813 |  | 86.883 | 105.2245 | 127.7888 | 155.589 | 189.8873 | 232.2572 | 284.6615 | 349.5496 | 429.9796 | 529.7716 | 653.6993 | 807.7308 | 999.3294 | 1237.8321 | 1534.9233 | 1905.2294 | 2367.0644 | 2943.3656 | 3662.8677 | 4561.5753 | 5684.6121 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 59.7513 | 78.0928 | 100.6571 | 128.4573 | 162.7555 | 205.1255 | 257.5298 | 322.4179 | 402.8478 | 502.6398 | 626.5676 | 780.5991 | 972.1977 | 1210.7004 | 1507.7916 | 1878.0976 | 2339.9326 | 2910.8907 | 3619.8202 | 4504.015 | 5607.0404 | 6075.037 | 6036.5359 | 5982.8557 | 5907.7884 | 5802.5316 | 5654.5904 | 5446.2097 | 5152.1373 | 4736.428 |  | 0.050683 | 0.061383 | 0.074546 | 0.090763 | 0.11077 | 0.13549 | 0.16606 | 0.20391 | 0.25083 | 0.30904 | 0.38134 | 0.47119 | 0.58296 | 0.72209 | 0.8954 | 1.1114 | 1.3808 | 1.717 | 2.1367 | 2.661 | 3.3161 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 |  | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.02368 | 0.03139 | 0.041972 | 0.056564 | 0.076767 | 0.10484 | 0.14398 | 0.19872 | 0.27547 | 0.38335 | 0.5353 | 0.74973 | 1.0529 |  | 0.030899 | 0.041599 | 0.054761 | 0.070979 | 0.090987 | 0.1157 | 0.14627 | 0.18413 | 0.23104 | 0.28926 | 0.36155 | 0.45141 | 0.56317 | 0.7023 | 0.87561 | 1.0916 | 1.361 | 1.6933 | 2.1053 | 2.619 | 3.2596 | 3.5285 | 3.5004 | 3.4613 | 3.4066 | 3.3298 | 3.2219 | 3.07 | 2.8556 | 2.5524 |  | 59.7822 | 78.1344 | 100.7119 | 128.5282 | 162.8465 | 205.2412 | 257.6761 | 322.602 | 403.0789 | 502.9291 | 626.9292 | 781.0505 | 972.7609 | 1211.4027 | 1508.6672 | 1879.1893 | 2341.2937 | 2912.584 | 3621.9255 | 4506.634 | 5610.2999 | 6078.5655 | 6040.0363 | 5986.317 | 5911.195 | 5805.8615 | 5657.8123 | 5449.2797 | 5154.9928 | 4738.9804 |  | 37.583 | 45.517 | 55.2776 | 67.3031 | 82.1396 | 100.4675 | 123.1361 | 151.2047 | 185.9963 | 229.1633 | 282.7708 | 349.4002 | 432.28 | 535.4491 | 663.9619 | 824.1452 | 1023.9212 | 1273.2119 | 1584.447 | 1973.201 | 2458.9931 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 22.9125 | 30.8465 | 40.6072 | 52.6327 | 67.4691 | 85.7971 | 108.4656 | 136.5342 | 171.3258 | 214.4929 | 268.1003 | 334.7297 | 417.6095 | 520.7787 | 649.2914 | 809.4748 | 1009.2508 | 1255.6523 | 1561.1707 | 1942.0774 | 2417.0491 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 5.297 | 6.4153 | 7.791 | 9.4859 | 11.577 | 14.1601 | 17.3551 | 21.3112 | 26.2148 | 32.2989 | 39.8544 | 49.2453 | 60.9266 | 75.4675 | 93.5805 | 116.1571 | 144.314 | 179.4497 | 223.3159 | 278.1079 | 346.5767 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 3.2293 | 4.3476 | 5.7233 | 7.4182 | 9.5093 | 12.0925 | 15.2874 | 19.2435 | 24.1471 | 30.2312 | 37.7867 | 47.1776 | 58.8589 | 73.3999 | 91.5128 | 114.0894 | 142.2463 | 176.9748 | 220.0353 | 273.7213 | 340.665 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.017663 | 0.021392 | 0.025979 | 0.031631 | 0.038604 | 0.047218 | 0.057872 | 0.071063 | 0.087415 | 0.1077 | 0.1329 | 0.16421 | 0.20316 | 0.25165 | 0.31205 | 0.38733 | 0.48122 | 0.59839 | 0.74466 | 0.92737 | 1.1557 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 |  | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0082527 | 0.010939 | 0.014628 | 0.019713 | 0.026754 | 0.036538 | 0.050179 | 0.069256 | 0.096004 | 0.1336 | 0.18655 | 0.26129 | 0.36693 |  | 0.010768 | 0.014497 | 0.019085 | 0.024736 | 0.031709 | 0.040323 | 0.050977 | 0.064169 | 0.08052 | 0.10081 | 0.126 | 0.15732 | 0.19627 | 0.24476 | 0.30516 | 0.38044 | 0.47433 | 0.59013 | 0.73372 | 0.91274 | 1.136 | 1.2297 | 1.2199 | 1.2063 | 1.1872 | 1.1605 | 1.1229 | 1.0699 | 0.99517 | 0.88953 |  | 85.9348 | 113.343 | 147.0614 | 188.6038 | 239.8566 | 303.171 | 381.4801 | 478.4438 | 598.6323 | 747.7539 | 932.9422 | 1163.1152 | 1449.4256 | 1805.826 | 2249.7766 | 2803.1339 | 3493.2651 | 4345.8012 | 5403.8652 | 6723.3454 | 8369.15 | 9065.0646 | 9002.7735 | 8915.9241 | 8794.4724 | 8624.1769 | 8384.8219 | 8047.6817 | 7571.9004 | 6899.3222
| FALSE | 359 | 22004408 | BAN | BAN-BATS NO.1 | 66 | BATS NO.1 LINE | DIRECTIONAL OC | X | GE | SR760 | SR760 | SR760 | Digital |  | 0.15703 | 1 |  | 6.6 | 0.017308 | 3.723e-06 | 0.017304 | 113.5853 | 0.6143 | 114.1996 | 49.1515 | 6.9249 | 0.21409 |  | 13.133 | 0.10917 | 2.3483e-05 | 0.10914 | 716.4285 | 3.8746 | 720.3031 | 310.0185 | 43.6782 | 1.3503 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 33.9153 | 0.18342 | 34.0987 | 14.6761 | 2.0677 | 0.063924 |  | 170.49 | 1075.3502 | 50.9065 | 1024.4437 |  | 0.068806 |  | 7.0701 | 7.5737 | 8.1132 | 8.691 | 9.3101 | 9.9732 | 10.6836 | 11.4446 | 12.2598 | 13.133 | 14.0684 | 15.0705 | 16.1439 | 17.2938 | 18.5257 | 19.8452 | 21.2587 | 22.773 | 24.395 | 26.1326 | 27.994 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.020647 | 0.024682 | 0.029561 | 0.035467 | 0.042625 | 0.051307 | 0.061847 | 0.074652 | 0.090222 | 0.10917 | 0.13224 | 0.16034 | 0.1946 | 0.23639 | 0.28739 | 0.34965 | 0.4257 | 0.51864 | 0.63226 | 0.7712 | 0.94118 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.4414e-06 | 5.3092e-06 | 6.3587e-06 | 7.6292e-06 | 9.1689e-06 | 1.1036e-05 | 1.3304e-05 | 1.6058e-05 | 1.9407e-05 | 2.3483e-05 | 2.8445e-05 | 3.449e-05 | 4.186e-05 | 5.0849e-05 | 6.1819e-05 | 7.5212e-05 | 9.1572e-05 | 0.00011156 | 0.000136 | 0.00016589 | 0.00020245 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 203.3859 | 243.1251 | 291.1846 | 349.367 | 419.8738 | 505.3944 | 609.2155 | 735.3557 | 888.7296 | 1075.3502 | 1302.5761 | 1579.4155 | 1916.8988 | 2328.5362 | 2830.879 | 3444.2083 | 4193.3812 | 5108.8691 | 6228.032 | 7596.6842 | 9271.0161 | 9276.7534 | 9276.7534 | 9276.7534 | 9276.7534 | 9276.7534 | 9276.7534 | 9276.7534 | 9276.7534 | 9276.7534 |  | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 52.8149 | 70.0092 | 93.6118 | 126.1569 | 171.216 | 233.8312 | 321.1326 | 443.2164 | 614.3981 | 854.9986 | 1193.8933 | 1672.1505 | 2348.2288 |  | 135.5014 | 161.9767 | 193.9953 | 232.7581 | 279.7317 | 336.7079 | 405.8765 | 489.9146 | 592.0966 | 716.4285 | 867.8127 | 1052.2509 | 1277.0918 | 1551.3362 | 1886.011 | 2294.6282 | 2793.7482 | 3403.6719 | 4149.2896 | 5061.1241 | 6176.6111 | 6180.4334 | 6180.4334 | 6180.4334 | 6180.4334 | 6180.4334 | 6180.4334 | 6180.4334 | 6180.4334 | 6180.4334 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 108.3691 | 134.8445 | 166.8631 | 205.6259 | 252.5995 | 309.5757 | 378.7442 | 462.7823 | 564.9643 | 689.2962 | 840.6805 | 1025.1187 | 1249.9595 | 1524.2039 | 1858.8788 | 2267.496 | 2766.616 | 3371.1963 | 4106.2413 | 5003.5627 | 6099.0378 | 6075.1535 | 6036.6517 | 5982.9705 | 5907.9018 | 5802.643 | 5654.6989 | 5446.3142 | 5152.2362 | 4736.5189 |  | 0.73283 | 0.87602 | 1.0492 | 1.2588 | 1.5129 | 1.821 | 2.1951 | 2.6496 | 3.2022 | 3.8746 | 4.6934 | 5.6909 | 6.9069 | 8.3901 | 10.2001 | 12.41 | 15.1094 | 18.408 | 22.4405 | 27.372 | 33.4048 | 33.4255 | 33.4255 | 33.4255 | 33.4255 | 33.4255 | 33.4255 | 33.4255 | 33.4255 | 33.4255 |  | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.21955 | 0.29102 | 0.38914 | 0.52442 | 0.71173 | 0.97201 | 1.3349 | 1.8424 | 2.554 | 3.5541 | 4.9629 | 6.951 | 9.7614 |  | 0.54941 | 0.69259 | 0.86576 | 1.0754 | 1.3294 | 1.6376 | 2.0117 | 2.4662 | 3.0188 | 3.6912 | 4.5099 | 5.5074 | 6.7234 | 8.2066 | 10.0167 | 12.2266 | 14.9259 | 18.1885 | 22.1495 | 26.9828 | 32.8804 | 32.7138 | 32.4535 | 32.0906 | 31.5831 | 30.8715 | 29.8714 | 28.4626 | 26.4745 | 23.6641 |  | 108.9185 | 135.5371 | 167.7288 | 206.7013 | 253.9289 | 311.2133 | 380.7559 | 465.2485 | 567.9831 | 692.9874 | 845.1904 | 1030.6261 | 1256.683 | 1532.4106 | 1868.8954 | 2279.7225 | 2781.5419 | 3389.3848 | 4128.3908 | 5030.5455 | 6131.9182 | 6107.8673 | 6069.1052 | 6015.0611 | 5939.4849 | 5833.5145 | 5684.5703 | 5474.7768 | 5178.7107 | 4760.1831 |  | 58.6352 | 70.0918 | 83.9472 | 100.7209 | 121.0477 | 145.7029 | 175.634 | 211.9997 | 256.2166 | 310.0185 | 375.5267 | 455.3382 | 552.6331 | 671.3063 | 816.1294 | 992.9494 | 1208.9325 | 1472.8634 | 1795.513 | 2190.0891 | 2672.7913 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 43.9591 | 55.4157 | 69.2711 | 86.0448 | 106.3716 | 131.0268 | 160.9579 | 197.3236 | 241.5406 | 295.3424 | 360.8506 | 440.6621 | 537.957 | 656.6302 | 801.4533 | 978.2733 | 1194.2564 | 1455.2971 | 1772.2277 | 2158.9535 | 2630.8311 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 8.2611 | 9.8752 | 11.8272 | 14.1905 | 17.0543 | 20.5279 | 24.7449 | 29.8684 | 36.0981 | 43.6782 | 52.9076 | 64.1522 | 77.86 | 94.5797 | 114.9837 | 139.8958 | 170.3254 | 207.5104 | 252.9682 | 308.5597 | 376.5672 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 6.1934 | 7.8075 | 9.7595 | 12.1228 | 14.9866 | 18.4602 | 22.6772 | 27.8007 | 34.0304 | 41.6105 | 50.8399 | 62.0845 | 75.7923 | 92.512 | 112.916 | 137.8281 | 168.2577 | 205.0355 | 249.6876 | 304.173 | 370.6555 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.25539 | 0.3053 | 0.36564 | 0.43871 | 0.52724 | 0.63463 | 0.765 | 0.9234 | 1.116 | 1.3503 | 1.6357 | 1.9833 | 2.4071 | 2.924 | 3.5548 | 4.3249 | 5.2657 | 6.4153 | 7.8206 | 9.5393 | 11.6417 | 11.649 | 11.649 | 11.649 | 11.649 | 11.649 | 11.649 | 11.649 | 11.649 | 11.649 |  | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.076513 | 0.10142 | 0.13562 | 0.18276 | 0.24804 | 0.33875 | 0.46523 | 0.64209 | 0.89008 | 1.2386 | 1.7296 | 2.4224 | 3.4019 |  | 0.19147 | 0.24137 | 0.30172 | 0.37478 | 0.46332 | 0.57071 | 0.70108 | 0.85947 | 1.0521 | 1.2864 | 1.5717 | 1.9194 | 2.3432 | 2.8601 | 3.4909 | 4.261 | 5.2018 | 6.3388 | 7.7192 | 9.4037 | 11.459 | 11.4009 | 11.3102 | 11.1837 | 11.0069 | 10.7589 | 10.4103 | 9.9194 | 9.2265 | 8.2471 |  | 159.2625 | 199.0017 | 247.0612 | 305.2436 | 375.7504 | 461.271 | 565.0921 | 691.2323 | 844.6062 | 1031.2268 | 1258.4527 | 1535.2921 | 1872.7754 | 2284.4128 | 2786.7556 | 3400.0849 | 4149.2579 | 5056.0561 | 6158.0253 | 7503.0757 | 9144.8638 | 9105.5437 | 9042.9307 | 8955.6325 | 8833.5531 | 8662.3776 | 8421.7859 | 8082.9036 | 7604.6637 | 6928.61
| FALSE | 360 | 22004908 | BAN | BAN-BATS No.2 | 66 | BATS No.2 LINE | DIR OC & DIR EF | Y | Schweitzer | SEL_351A | SEL 351 | SEL 300s | Digital |  | 0.016937 | 1 |  | 6.6 | 0.017308 | 4.0157e-07 | 0.017307 | 113.5831 | 0.066259 | 113.6493 | 49.1326 | 6.9249 | 0.023091 |  | 14.9721 | 0.15742 | 3.6523e-06 | 0.15741 | 1033.0517 | 0.60263 | 1033.6544 | 446.8673 | 62.9826 | 0.21002 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 33.9147 | 0.019784 | 33.9344 | 14.6705 | 2.0677 | 0.0068949 |  | 169.7299 | 1543.7143 | 50.6795 | 1493.0348 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021358 | 0.026432 | 0.032797 | 0.040794 | 0.050854 | 0.063527 | 0.079507 | 0.099681 | 0.12517 | 0.15742 | 0.19823 | 0.24994 | 0.31549 | 0.39864 | 0.5042 | 0.63826 | 0.80862 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.9554e-07 | 6.1325e-07 | 7.6093e-07 | 9.4647e-07 | 1.1799e-06 | 1.4739e-06 | 1.8447e-06 | 2.3128e-06 | 2.9042e-06 | 3.6523e-06 | 4.5993e-06 | 5.7989e-06 | 7.3198e-06 | 9.2491e-06 | 1.1698e-05 | 1.4809e-05 | 1.8761e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 209.4485 | 259.2016 | 321.6207 | 400.0428 | 498.7023 | 622.9751 | 779.6904 | 977.5277 | 1227.5229 | 1543.7143 | 1943.9662 | 2451.0202 | 3093.836 | 3909.3035 | 4944.4274 | 6259.1166 | 7929.7458 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 |  | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 52.5416 | 69.6471 | 93.1276 | 125.5043 | 170.3303 | 232.6216 | 319.4713 | 440.9236 | 611.2198 | 850.5757 | 1187.7172 | 1663.5004 | 2336.0813 |  | 140.1627 | 173.4574 | 215.2282 | 267.7082 | 333.731 | 416.8942 | 521.7679 | 654.1604 | 821.4569 | 1033.0517 | 1300.8999 | 1640.2198 | 2070.3914 | 2616.1012 | 3308.8049 | 4188.5934 | 5306.5764 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 113.031 | 146.3257 | 188.0965 | 240.5765 | 306.5992 | 389.7625 | 494.6362 | 627.0287 | 794.3251 | 1005.92 | 1273.7681 | 1613.088 | 2043.2596 | 2588.9695 | 3281.6732 | 4161.4617 | 5279.4447 | 6147.8398 | 6137.2673 | 6122.7545 | 6102.743 | 6075.037 | 6036.5359 | 5982.8557 | 5907.7884 | 5802.5316 | 5654.5904 | 5446.2097 | 5152.1373 | 4736.428 |  | 0.081764 | 0.10119 | 0.12555 | 0.15617 | 0.19468 | 0.2432 | 0.30437 | 0.3816 | 0.4792 | 0.60263 | 0.75888 | 0.95682 | 1.2078 | 1.5261 | 1.9302 | 2.4434 | 3.0956 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 |  | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.02368 | 0.03139 | 0.041972 | 0.056564 | 0.076767 | 0.10484 | 0.14398 | 0.19872 | 0.27547 | 0.38335 | 0.5353 | 0.74973 | 1.0529 |  | 0.06198 | 0.081402 | 0.10577 | 0.13638 | 0.1749 | 0.22341 | 0.28459 | 0.36182 | 0.45941 | 0.58285 | 0.7391 | 0.93704 | 1.188 | 1.5063 | 1.9104 | 2.4236 | 3.0758 | 3.5816 | 3.5739 | 3.5633 | 3.5487 | 3.5285 | 3.5004 | 3.4613 | 3.4066 | 3.3298 | 3.2219 | 3.07 | 2.8556 | 2.5524 |  | 113.0929 | 146.4071 | 188.2022 | 240.7128 | 306.7741 | 389.9859 | 494.9208 | 627.3905 | 794.7845 | 1006.5029 | 1274.5072 | 1614.0251 | 2044.4476 | 2590.4758 | 3283.5836 | 4163.8853 | 5282.5205 | 6151.4214 | 6140.8412 | 6126.3178 | 6106.2917 | 6078.5655 | 6040.0363 | 5986.317 | 5911.195 | 5805.8615 | 5657.8123 | 5449.2797 | 5154.9928 | 4738.9804 |  | 60.6302 | 75.0325 | 93.1013 | 115.8025 | 144.362 | 180.336 | 225.7012 | 282.9702 | 355.3377 | 446.8673 | 562.7304 | 709.51 | 895.5894 | 1131.6471 | 1431.29 | 1811.8602 | 2295.4662 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 45.9597 | 60.362 | 78.4308 | 101.1321 | 129.6916 | 165.6655 | 211.0307 | 268.2997 | 340.6672 | 432.1968 | 548.0599 | 694.8395 | 880.9189 | 1116.9766 | 1416.6195 | 1797.1897 | 2280.7957 | 2655.8596 | 2650.1429 | 2642.2957 | 2631.4752 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 8.5454 | 10.5753 | 13.1219 | 16.3215 | 20.3467 | 25.417 | 31.8109 | 39.8825 | 50.0822 | 62.9826 | 79.3126 | 100.0001 | 126.2266 | 159.4972 | 201.7296 | 255.3681 | 323.5288 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 6.4777 | 8.5076 | 11.0542 | 14.2538 | 18.2791 | 23.3493 | 29.7432 | 37.8148 | 48.0145 | 60.9149 | 77.2449 | 97.9324 | 124.1589 | 157.4295 | 199.6619 | 253.3004 | 321.4611 | 374.3235 | 373.5178 | 372.4118 | 370.8867 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.028495 | 0.035264 | 0.043756 | 0.054425 | 0.067848 | 0.084755 | 0.10608 | 0.13299 | 0.167 | 0.21002 | 0.26447 | 0.33346 | 0.42091 | 0.53185 | 0.67268 | 0.85154 | 1.0788 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 |  | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0082527 | 0.010939 | 0.014628 | 0.019713 | 0.026754 | 0.036538 | 0.050179 | 0.069256 | 0.096004 | 0.1336 | 0.18655 | 0.26129 | 0.36693 |  | 0.0216 | 0.028369 | 0.036861 | 0.04753 | 0.060953 | 0.07786 | 0.099181 | 0.1261 | 0.16011 | 0.20312 | 0.25758 | 0.32656 | 0.41402 | 0.52496 | 0.66579 | 0.84465 | 1.0719 | 1.2482 | 1.2455 | 1.2418 | 1.2367 | 1.2297 | 1.2199 | 1.2063 | 1.1872 | 1.1605 | 1.1229 | 1.0699 | 0.99517 | 0.88953 |  | 165.5519 | 215.305 | 277.7241 | 356.1463 | 454.8057 | 579.0785 | 735.7939 | 933.6312 | 1183.6263 | 1499.8177 | 1900.0696 | 2407.1236 | 3049.9394 | 3865.4069 | 4900.5308 | 6215.2201 | 7885.8492 | 9182.8528 | 9165.7475 | 9142.267 | 9109.8904 | 9065.0646 | 9002.7735 | 8915.9241 | 8794.4724 | 8624.1769 | 8384.8219 | 8047.6817 | 7571.9004 | 6899.3222
| FALSE | 361 | 22015670 | BAN | BAN-BATS No.2 | 66 | BATS No.2 LINE | REM TRIP SEND/RCVE | Y | Schweitzer | SEL_2505 | SEL 2505 | SEL 2000s | Digital |  | 0.016937 | 1 |  | 5.5 | 0.010964 | 2.5438e-07 | 0.010964 | 71.9504 | 0.041972 | 71.9924 | 31.1236 | 4.3866 | 0.014628 |  | 11.7751 | 0.080727 | 1.873e-06 | 0.080725 | 529.7716 | 0.30904 | 530.0806 | 229.1633 | 32.2989 | 0.1077 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 33.9147 | 0.019784 | 33.9344 | 14.6705 | 2.0677 | 0.0068949 |  | 107.5173 | 791.6505 | 50.6795 | 740.971 |  | 0.076124 |  | 5.935 | 6.4045 | 6.911 | 7.4577 | 8.0475 | 8.6841 | 9.3709 | 10.1121 | 10.912 | 11.7751 | 12.7064 | 13.7115 | 14.796 | 15.9663 | 17.2292 | 18.5919 | 20.0625 | 21.6493 | 23.3617 | 25.2095 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.013239 | 0.016034 | 0.019473 | 0.023709 | 0.028935 | 0.035391 | 0.043377 | 0.053265 | 0.065521 | 0.080727 | 0.099611 | 0.12308 | 0.15228 | 0.18862 | 0.23389 | 0.29032 | 0.36069 | 0.44851 | 0.55815 | 0.6951 | 0.86622 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 3.0717e-07 | 3.7202e-07 | 4.5179e-07 | 5.5008e-07 | 6.7134e-07 | 8.2113e-07 | 1.0064e-06 | 1.2358e-06 | 1.5202e-06 | 1.873e-06 | 2.3111e-06 | 2.8557e-06 | 3.5331e-06 | 4.3763e-06 | 5.4266e-06 | 6.7358e-06 | 8.3686e-06 | 1.0406e-05 | 1.295e-05 | 1.6127e-05 | 2.0098e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 129.8314 | 157.2396 | 190.958 | 232.5004 | 283.7532 | 347.0676 | 425.3766 | 522.3404 | 642.5289 | 791.6505 | 976.8388 | 1207.0117 | 1493.3222 | 1849.7226 | 2293.6731 | 2847.0304 | 3537.1617 | 4398.3426 | 5473.512 | 6816.4726 | 8494.6537 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 |  | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 52.5416 | 69.6471 | 93.1276 | 125.5043 | 170.3303 | 232.6216 | 319.4713 | 440.9236 | 611.2198 | 850.5757 | 1187.7172 | 1663.5004 | 2336.0813 |  | 86.883 | 105.2245 | 127.7888 | 155.589 | 189.8873 | 232.2572 | 284.6615 | 349.5496 | 429.9796 | 529.7716 | 653.6993 | 807.7308 | 999.3294 | 1237.8321 | 1534.9233 | 1905.2294 | 2367.0644 | 2943.3656 | 3662.8677 | 4561.5753 | 5684.6121 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 59.7513 | 78.0928 | 100.6571 | 128.4573 | 162.7555 | 205.1255 | 257.5298 | 322.4179 | 402.8478 | 502.6398 | 626.5676 | 780.5991 | 972.1977 | 1210.7004 | 1507.7916 | 1878.0976 | 2339.9326 | 2910.8907 | 3619.8202 | 4504.015 | 5607.0404 | 6075.037 | 6036.5359 | 5982.8557 | 5907.7884 | 5802.5316 | 5654.5904 | 5446.2097 | 5152.1373 | 4736.428 |  | 0.050683 | 0.061383 | 0.074546 | 0.090763 | 0.11077 | 0.13549 | 0.16606 | 0.20391 | 0.25083 | 0.30904 | 0.38134 | 0.47119 | 0.58296 | 0.72209 | 0.8954 | 1.1114 | 1.3808 | 1.717 | 2.1367 | 2.661 | 3.3161 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 |  | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.02368 | 0.03139 | 0.041972 | 0.056564 | 0.076767 | 0.10484 | 0.14398 | 0.19872 | 0.27547 | 0.38335 | 0.5353 | 0.74973 | 1.0529 |  | 0.030899 | 0.041599 | 0.054761 | 0.070979 | 0.090987 | 0.1157 | 0.14627 | 0.18413 | 0.23104 | 0.28926 | 0.36155 | 0.45141 | 0.56317 | 0.7023 | 0.87561 | 1.0916 | 1.361 | 1.6933 | 2.1053 | 2.619 | 3.2596 | 3.5285 | 3.5004 | 3.4613 | 3.4066 | 3.3298 | 3.2219 | 3.07 | 2.8556 | 2.5524 |  | 59.7822 | 78.1344 | 100.7119 | 128.5282 | 162.8465 | 205.2412 | 257.6761 | 322.602 | 403.0789 | 502.9291 | 626.9292 | 781.0505 | 972.7609 | 1211.4027 | 1508.6672 | 1879.1893 | 2341.2937 | 2912.584 | 3621.9255 | 4506.634 | 5610.2999 | 6078.5655 | 6040.0363 | 5986.317 | 5911.195 | 5805.8615 | 5657.8123 | 5449.2797 | 5154.9928 | 4738.9804 |  | 37.583 | 45.517 | 55.2776 | 67.3031 | 82.1396 | 100.4675 | 123.1361 | 151.2047 | 185.9963 | 229.1633 | 282.7708 | 349.4002 | 432.28 | 535.4491 | 663.9619 | 824.1452 | 1023.9212 | 1273.2119 | 1584.447 | 1973.201 | 2458.9931 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 22.9125 | 30.8465 | 40.6072 | 52.6327 | 67.4691 | 85.7971 | 108.4656 | 136.5342 | 171.3258 | 214.4929 | 268.1003 | 334.7297 | 417.6095 | 520.7787 | 649.2914 | 809.4748 | 1009.2508 | 1255.6523 | 1561.1707 | 1942.0774 | 2417.0491 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 5.297 | 6.4153 | 7.791 | 9.4859 | 11.577 | 14.1601 | 17.3551 | 21.3112 | 26.2148 | 32.2989 | 39.8544 | 49.2453 | 60.9266 | 75.4675 | 93.5805 | 116.1571 | 144.314 | 179.4497 | 223.3159 | 278.1079 | 346.5767 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 3.2293 | 4.3476 | 5.7233 | 7.4182 | 9.5093 | 12.0925 | 15.2874 | 19.2435 | 24.1471 | 30.2312 | 37.7867 | 47.1776 | 58.8589 | 73.3999 | 91.5128 | 114.0894 | 142.2463 | 176.9748 | 220.0353 | 273.7213 | 340.665 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.017663 | 0.021392 | 0.025979 | 0.031631 | 0.038604 | 0.047218 | 0.057872 | 0.071063 | 0.087415 | 0.1077 | 0.1329 | 0.16421 | 0.20316 | 0.25165 | 0.31205 | 0.38733 | 0.48122 | 0.59839 | 0.74466 | 0.92737 | 1.1557 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 |  | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0082527 | 0.010939 | 0.014628 | 0.019713 | 0.026754 | 0.036538 | 0.050179 | 0.069256 | 0.096004 | 0.1336 | 0.18655 | 0.26129 | 0.36693 |  | 0.010768 | 0.014497 | 0.019085 | 0.024736 | 0.031709 | 0.040323 | 0.050977 | 0.064169 | 0.08052 | 0.10081 | 0.126 | 0.15732 | 0.19627 | 0.24476 | 0.30516 | 0.38044 | 0.47433 | 0.59013 | 0.73372 | 0.91274 | 1.136 | 1.2297 | 1.2199 | 1.2063 | 1.1872 | 1.1605 | 1.1229 | 1.0699 | 0.99517 | 0.88953 |  | 85.9348 | 113.343 | 147.0614 | 188.6038 | 239.8566 | 303.171 | 381.4801 | 478.4438 | 598.6323 | 747.7539 | 932.9422 | 1163.1152 | 1449.4256 | 1805.826 | 2249.7766 | 2803.1339 | 3493.2651 | 4345.8012 | 5403.8652 | 6723.3454 | 8369.15 | 9065.0646 | 9002.7735 | 8915.9241 | 8794.4724 | 8624.1769 | 8384.8219 | 8047.6817 | 7571.9004 | 6899.3222
| FALSE | 362 | 22004409 | BAN | BAN-BATS No.2 | 66 | BATS No.2 LINE | DIRECTIONAL OC | X | GE | SR760 | SR760 | SR760 | Digital |  | 0.15703 | 1 |  | 6.6 | 0.017308 | 3.723e-06 | 0.017304 | 113.5853 | 0.6143 | 114.1996 | 49.1515 | 6.9249 | 0.21409 |  | 13.133 | 0.10917 | 2.3483e-05 | 0.10914 | 716.4285 | 3.8746 | 720.3031 | 310.0185 | 43.6782 | 1.3503 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 33.9153 | 0.18342 | 34.0987 | 14.6761 | 2.0677 | 0.063924 |  | 170.49 | 1075.3502 | 50.9065 | 1024.4437 |  | 0.068806 |  | 7.0701 | 7.5737 | 8.1132 | 8.691 | 9.3101 | 9.9732 | 10.6836 | 11.4446 | 12.2598 | 13.133 | 14.0684 | 15.0705 | 16.1439 | 17.2938 | 18.5257 | 19.8452 | 21.2587 | 22.773 | 24.395 | 26.1326 | 27.994 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.020647 | 0.024682 | 0.029561 | 0.035467 | 0.042625 | 0.051307 | 0.061847 | 0.074652 | 0.090222 | 0.10917 | 0.13224 | 0.16034 | 0.1946 | 0.23639 | 0.28739 | 0.34965 | 0.4257 | 0.51864 | 0.63226 | 0.7712 | 0.94118 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.4414e-06 | 5.3092e-06 | 6.3587e-06 | 7.6292e-06 | 9.1689e-06 | 1.1036e-05 | 1.3304e-05 | 1.6058e-05 | 1.9407e-05 | 2.3483e-05 | 2.8445e-05 | 3.449e-05 | 4.186e-05 | 5.0849e-05 | 6.1819e-05 | 7.5212e-05 | 9.1572e-05 | 0.00011156 | 0.000136 | 0.00016589 | 0.00020245 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 203.3859 | 243.1251 | 291.1846 | 349.367 | 419.8738 | 505.3944 | 609.2155 | 735.3557 | 888.7296 | 1075.3502 | 1302.5761 | 1579.4155 | 1916.8988 | 2328.5362 | 2830.879 | 3444.2083 | 4193.3812 | 5108.8691 | 6228.032 | 7596.6842 | 9271.0161 | 9276.7534 | 9276.7534 | 9276.7534 | 9276.7534 | 9276.7534 | 9276.7534 | 9276.7534 | 9276.7534 | 9276.7534 |  | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 44.125 | 52.8149 | 70.0092 | 93.6118 | 126.1569 | 171.216 | 233.8312 | 321.1326 | 443.2164 | 614.3981 | 854.9986 | 1193.8933 | 1672.1505 | 2348.2288 |  | 135.5014 | 161.9767 | 193.9953 | 232.7581 | 279.7317 | 336.7079 | 405.8765 | 489.9146 | 592.0966 | 716.4285 | 867.8127 | 1052.2509 | 1277.0918 | 1551.3362 | 1886.011 | 2294.6282 | 2793.7482 | 3403.6719 | 4149.2896 | 5061.1241 | 6176.6111 | 6180.4334 | 6180.4334 | 6180.4334 | 6180.4334 | 6180.4334 | 6180.4334 | 6180.4334 | 6180.4334 | 6180.4334 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 108.3691 | 134.8445 | 166.8631 | 205.6259 | 252.5995 | 309.5757 | 378.7442 | 462.7823 | 564.9643 | 689.2962 | 840.6805 | 1025.1187 | 1249.9595 | 1524.2039 | 1858.8788 | 2267.496 | 2766.616 | 3371.1963 | 4106.2413 | 5003.5627 | 6099.0378 | 6075.1535 | 6036.6517 | 5982.9705 | 5907.9018 | 5802.643 | 5654.6989 | 5446.3142 | 5152.2362 | 4736.5189 |  | 0.73283 | 0.87602 | 1.0492 | 1.2588 | 1.5129 | 1.821 | 2.1951 | 2.6496 | 3.2022 | 3.8746 | 4.6934 | 5.6909 | 6.9069 | 8.3901 | 10.2001 | 12.41 | 15.1094 | 18.408 | 22.4405 | 27.372 | 33.4048 | 33.4255 | 33.4255 | 33.4255 | 33.4255 | 33.4255 | 33.4255 | 33.4255 | 33.4255 | 33.4255 |  | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.18342 | 0.21955 | 0.29102 | 0.38914 | 0.52442 | 0.71173 | 0.97201 | 1.3349 | 1.8424 | 2.554 | 3.5541 | 4.9629 | 6.951 | 9.7614 |  | 0.54941 | 0.69259 | 0.86576 | 1.0754 | 1.3294 | 1.6376 | 2.0117 | 2.4662 | 3.0188 | 3.6912 | 4.5099 | 5.5074 | 6.7234 | 8.2066 | 10.0167 | 12.2266 | 14.9259 | 18.1885 | 22.1495 | 26.9828 | 32.8804 | 32.7138 | 32.4535 | 32.0906 | 31.5831 | 30.8715 | 29.8714 | 28.4626 | 26.4745 | 23.6641 |  | 108.9185 | 135.5371 | 167.7288 | 206.7013 | 253.9289 | 311.2133 | 380.7559 | 465.2485 | 567.9831 | 692.9874 | 845.1904 | 1030.6261 | 1256.683 | 1532.4106 | 1868.8954 | 2279.7225 | 2781.5419 | 3389.3848 | 4128.3908 | 5030.5455 | 6131.9182 | 6107.8673 | 6069.1052 | 6015.0611 | 5939.4849 | 5833.5145 | 5684.5703 | 5474.7768 | 5178.7107 | 4760.1831 |  | 58.6352 | 70.0918 | 83.9472 | 100.7209 | 121.0477 | 145.7029 | 175.634 | 211.9997 | 256.2166 | 310.0185 | 375.5267 | 455.3382 | 552.6331 | 671.3063 | 816.1294 | 992.9494 | 1208.9325 | 1472.8634 | 1795.513 | 2190.0891 | 2672.7913 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 43.9591 | 55.4157 | 69.2711 | 86.0448 | 106.3716 | 131.0268 | 160.9579 | 197.3236 | 241.5406 | 295.3424 | 360.8506 | 440.6621 | 537.957 | 656.6302 | 801.4533 | 978.2733 | 1194.2564 | 1455.2971 | 1772.2277 | 2158.9535 | 2630.8311 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 8.2611 | 9.8752 | 11.8272 | 14.1905 | 17.0543 | 20.5279 | 24.7449 | 29.8684 | 36.0981 | 43.6782 | 52.9076 | 64.1522 | 77.86 | 94.5797 | 114.9837 | 139.8958 | 170.3254 | 207.5104 | 252.9682 | 308.5597 | 376.5672 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 6.1934 | 7.8075 | 9.7595 | 12.1228 | 14.9866 | 18.4602 | 22.6772 | 27.8007 | 34.0304 | 41.6105 | 50.8399 | 62.0845 | 75.7923 | 92.512 | 112.916 | 137.8281 | 168.2577 | 205.0355 | 249.6876 | 304.173 | 370.6555 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.25539 | 0.3053 | 0.36564 | 0.43871 | 0.52724 | 0.63463 | 0.765 | 0.9234 | 1.116 | 1.3503 | 1.6357 | 1.9833 | 2.4071 | 2.924 | 3.5548 | 4.3249 | 5.2657 | 6.4153 | 7.8206 | 9.5393 | 11.6417 | 11.649 | 11.649 | 11.649 | 11.649 | 11.649 | 11.649 | 11.649 | 11.649 | 11.649 |  | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.076513 | 0.10142 | 0.13562 | 0.18276 | 0.24804 | 0.33875 | 0.46523 | 0.64209 | 0.89008 | 1.2386 | 1.7296 | 2.4224 | 3.4019 |  | 0.19147 | 0.24137 | 0.30172 | 0.37478 | 0.46332 | 0.57071 | 0.70108 | 0.85947 | 1.0521 | 1.2864 | 1.5717 | 1.9194 | 2.3432 | 2.8601 | 3.4909 | 4.261 | 5.2018 | 6.3388 | 7.7192 | 9.4037 | 11.459 | 11.4009 | 11.3102 | 11.1837 | 11.0069 | 10.7589 | 10.4103 | 9.9194 | 9.2265 | 8.2471 |  | 159.2625 | 199.0017 | 247.0612 | 305.2436 | 375.7504 | 461.271 | 565.0921 | 691.2323 | 844.6062 | 1031.2268 | 1258.4527 | 1535.2921 | 1872.7754 | 2284.4128 | 2786.7556 | 3400.0849 | 4149.2579 | 5056.0561 | 6158.0253 | 7503.0757 | 9144.8638 | 9105.5437 | 9042.9307 | 8955.6325 | 8833.5531 | 8662.3776 | 8421.7859 | 8082.9036 | 7604.6637 | 6928.61
| FALSE | 363 | 22004414 | BAN | BAN-BGR | 66 | BGR LINE | DISTANCE | X | ASEA | RAZOG_2167 | RAZOG 2167 | RAZOG | Electronic |  | 0.15703 | 2190 |  | 6.6 | 0.014726 | 0.0051892 | 0.0095369 | 160.0721 | 2283.2371 | 2443.3092 | 71.2617 | 5.9438 | 298.3947 |  | 9.8464 | 0.042169 | 0.014859 | 0.027309 | 458.3733 | 6538.1452 | 6996.5184 | 204.061 | 17.0203 | 854.4659 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.063924 |  | 2818.9095 | 8072.0656 | 71.5613 | 8000.5042 |  | 0.040003 |  | 6.8694 | 7.1497 | 7.4416 | 7.7453 | 8.0614 | 8.3904 | 8.7329 | 9.0893 | 9.4603 | 9.8464 | 10.2482 | 10.6665 | 11.1019 | 11.555 | 12.0266 | 12.5174 | 13.0283 | 13.5601 | 14.1135 | 14.6896 | 15.2891 | 15.9131 | 16.5626 | 17.2386 | 17.9422 | 18.6745 | 19.4366 | 20.2299 | 21.0556 | 21.915 |  | 0.016313 | 0.018083 | 0.020059 | 0.022266 | 0.024731 | 0.027485 | 0.030564 | 0.034008 | 0.037859 | 0.042169 | 0.046992 | 0.052392 | 0.058439 | 0.065213 | 0.072802 | 0.081308 | 0.090842 | 0.10153 | 0.11352 | 0.12697 | 0.14205 | 0.15898 | 0.17798 | 0.19931 | 0.22326 | 0.25015 | 0.28035 | 0.31427 | 0.35238 | 0.3952 |  | 0.0057482 | 0.006372 | 0.0070684 | 0.007846 | 0.0087146 | 0.0096853 | 0.01077 | 0.011984 | 0.013341 | 0.014859 | 0.016559 | 0.018462 | 0.020593 | 0.02298 | 0.025654 | 0.028651 | 0.032011 | 0.035778 | 0.040002 | 0.044741 | 0.050057 | 0.056023 | 0.062718 | 0.070234 | 0.078672 | 0.088147 | 0.098789 | 0.11074 | 0.12417 | 0.13926 | 3122.6068 | 3461.4793 | 3839.7485 | 4262.1534 | 4734.0149 | 5261.3082 | 5850.7444 | 6509.862 | 7247.1303 | 8072.0656 | 8995.3617 | 10029.0376 | 11186.6031 | 12483.2456 | 13936.0401 | 15564.1861 | 17389.2744 | 19435.5867 | 21730.4343 | 24304.5386 | 27192.4602 | 30433.0819 | 34070.1528 | 38152.9016 | 42736.7266 | 47883.9744 | 53664.8155 | 60158.2323 | 67453.1308 | 75649.5947 |  | 44.4355 | 44.4355 | 44.4355 | 44.4355 | 44.4355 | 44.4355 | 44.4355 | 44.4355 | 44.4355 | 44.4355 | 44.4355 | 44.4355 | 44.4355 | 44.4355 | 44.4355 | 44.4355 | 44.4355 | 53.1865 | 70.5019 | 94.2706 | 127.0447 | 172.4209 | 235.4768 | 323.3925 | 446.3354 | 618.7218 | 861.0155 | 1202.295 | 1683.918 | 2364.754 |  | 177.3176 | 196.5605 | 218.0406 | 242.0269 | 268.8216 | 298.7641 | 332.2353 | 369.6633 | 411.5292 | 458.3733 | 510.8028 | 569.5002 | 635.2327 | 708.8627 | 791.3598 | 883.8143 | 987.4522 | 1103.6523 | 1233.9655 | 1380.1363 | 1544.1273 | 1728.1464 | 1934.678 | 2166.5174 | 2426.8104 | 2719.0976 | 3047.3634 | 3416.0929 | 3830.3346 | 4295.7718 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 150.1854 | 169.4283 | 190.9084 | 214.8947 | 241.6894 | 271.6318 | 305.103 | 342.5311 | 384.397 | 431.241 | 483.6705 | 542.3679 | 608.1004 | 681.7304 | 764.2276 | 856.682 | 960.3199 | 1071.1767 | 1190.9171 | 1322.5749 | 1466.554 | 1622.8665 | 1790.8963 | 1969.0545 | 2154.2788 | 2341.3072 | 2521.6289 | 2681.9737 | 2802.1374 | 2851.8573 |  | 2529.2233 | 2803.7005 | 3110.0879 | 3452.2239 | 3834.4184 | 4261.5111 | 4738.9377 | 5272.8044 | 5869.9709 | 6538.1452 | 7285.9889 | 8123.2372 | 9060.8326 | 10111.0764 | 11287.7989 | 12606.5512 | 14084.8212 | 15742.2763 | 17601.0381 | 19685.9899 | 22025.1249 | 24649.9369 | 27595.8617 | 30902.7728 | 34615.5417 | 38784.667 | 43466.9851 | 48726.4693 | 54635.1311 | 61274.0354 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 2528.7342 | 2803.2114 | 3109.5987 | 3451.7348 | 3833.9292 | 4261.0219 | 4738.4486 | 5272.3153 | 5869.4818 | 6537.656 | 7285.4998 | 8122.7481 | 9060.3435 | 10110.5873 | 11287.3098 | 12606.0621 | 14084.3321 | 15741.6909 | 17600.262 | 19684.9522 | 22023.7264 | 24648.039 | 27593.2696 | 30899.2131 | 34610.6286 | 38777.8564 | 43457.5074 | 48713.2349 | 54616.5952 | 61248.0051 |  | 2678.9195 | 2972.6397 | 3300.5071 | 3666.6294 | 4075.6186 | 4532.6537 | 5043.5516 | 5614.8464 | 6253.8788 | 6968.8971 | 7769.1703 | 8665.116 | 9668.4439 | 10792.3177 | 12051.5373 | 13462.7442 | 15044.652 | 16812.8675 | 18791.1792 | 21007.5271 | 23490.2804 | 26270.9055 | 29384.1659 | 32868.2675 | 36764.9074 | 41119.1635 | 45979.1362 | 51395.2086 | 57418.7325 | 64099.8624 |  | 78.9392 | 87.5058 | 97.0685 | 107.7468 | 119.6754 | 133.0053 | 147.9062 | 164.5687 | 183.2067 | 204.061 | 227.4018 | 253.5331 | 282.7962 | 315.5752 | 352.3017 | 393.461 | 439.5991 | 491.3297 | 549.3432 | 614.4163 | 687.4226 | 769.3452 | 861.29 | 964.5015 | 1080.3801 | 1210.502 | 1356.6411 | 1520.794 | 1705.2083 | 1912.4141 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 64.2631 | 72.8297 | 82.3924 | 93.0707 | 104.9993 | 118.3292 | 133.2301 | 149.8926 | 168.5306 | 189.3849 | 212.7257 | 238.857 | 268.1201 | 300.8991 | 337.6256 | 378.785 | 424.923 | 473.7633 | 526.0579 | 583.2807 | 645.4625 | 712.3983 | 783.5171 | 857.6919 | 932.9651 | 1006.1515 | 1072.2662 | 1123.7018 | 1149.0464 | 1131.3867 |  | 6.5841 | 7.2987 | 8.0963 | 8.9869 | 9.9819 | 11.0937 | 12.3365 | 13.7263 | 15.2809 | 17.0203 | 18.9671 | 21.1466 | 23.5874 | 26.3214 | 29.3847 | 32.8177 | 36.666 | 40.9807 | 45.8195 | 51.2471 | 57.3364 | 64.1694 | 71.8383 | 80.4469 | 90.1121 | 100.9653 | 113.1544 | 126.846 | 142.2276 | 159.5102 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 4.5164 | 5.231 | 6.0286 | 6.9192 | 7.9142 | 9.026 | 10.2688 | 11.6586 | 13.2132 | 14.9526 | 16.8994 | 19.0789 | 21.5197 | 24.2537 | 27.317 | 30.75 | 34.5983 | 38.5058 | 42.5388 | 46.8604 | 51.4247 | 56.1462 | 60.8809 | 65.3986 | 69.3429 | 72.1745 | 73.0891 | 70.9001 | 63.8705 | 49.4719 |  | 330.5425 | 366.4138 | 406.4553 | 451.1689 | 501.1176 | 556.9341 | 619.3286 | 689.0993 | 767.1426 | 854.4659 | 952.2011 | 1061.6205 | 1184.1542 | 1321.4099 | 1475.195 | 1647.5419 | 1840.736 | 2057.3477 | 2300.268 | 2572.749 | 2878.449 | 3221.484 | 3606.4849 | 4038.663 | 4523.8823 | 5068.7425 | 5680.6716 | 6368.0301 | 7140.2292 | 8007.8632 |  | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.063924 | 0.076513 | 0.10142 | 0.13562 | 0.18276 | 0.24804 | 0.33875 | 0.46523 | 0.64209 | 0.89008 | 1.2386 | 1.7296 | 2.4224 | 3.4019 |  | 330.4786 | 366.3498 | 406.3914 | 451.1049 | 501.0537 | 556.8701 | 619.2647 | 689.0354 | 767.0787 | 854.4019 | 952.1372 | 1061.5566 | 1184.0903 | 1321.346 | 1475.1311 | 1647.4779 | 1840.672 | 2057.2712 | 2300.1666 | 2572.6134 | 2878.2663 | 3221.2359 | 3606.1462 | 4038.1977 | 4523.2402 | 5067.8524 | 5679.4329 | 6366.3005 | 7137.8067 | 8004.4613 |  | 3078.1777 | 3417.0502 | 3795.3194 | 4217.7243 | 4689.5858 | 5216.8791 | 5806.3153 | 6465.4329 | 7202.7012 | 8027.6365 | 8950.9326 | 9984.6085 | 11142.174 | 12438.8165 | 13891.611 | 15519.757 | 17344.8453 | 19382.4078 | 21659.9425 | 24210.2816 | 27065.4339 | 30260.6859 | 33834.7101 | 37829.5558 | 42290.4557 | 47265.342 | 52803.9244 | 58956.1109 | 65769.4562 | 73285.1823
| FALSE | 364 | 22004894 | BAN | BAN-BGR | 66 | BGR LINE | DISTANCE & DIR EF | Y | Schweitzer | SEL_311C | SEL 311C | SEL 300s | Digital |  | 0.016937 | 1 |  | 6.6 | 0.017308 | 4.0157e-07 | 0.017307 | 113.5831 | 0.066259 | 113.6493 | 49.1326 | 6.9249 | 0.023091 |  | 14.4249 | 0.14182 | 3.2904e-06 | 0.14181 | 930.6842 | 0.54291 | 931.2271 | 402.5861 | 56.7415 | 0.18921 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 33.9147 | 0.019784 | 33.9344 | 14.6705 | 2.0677 | 0.0068949 |  | 169.7299 | 1390.744 | 50.6795 | 1340.0645 |  | 0.078188 |  | 7.1368 | 7.7172 | 8.3448 | 9.0234 | 9.7573 | 10.5508 | 11.4088 | 12.3367 | 13.34 | 14.4249 | 15.598 | 16.8665 | 18.2382 | 19.7215 | 21.3253 | 23.0596 | 24.935 | 26.9629 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021154 | 0.025921 | 0.031841 | 0.0392 | 0.04836 | 0.059775 | 0.074014 | 0.091795 | 0.11402 | 0.14182 | 0.17662 | 0.22022 | 0.27489 | 0.34346 | 0.42954 | 0.53764 | 0.67347 | 0.84423 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.9079e-07 | 6.0142e-07 | 7.3876e-07 | 9.095e-07 | 1.122e-06 | 1.3869e-06 | 1.7172e-06 | 2.1298e-06 | 2.6454e-06 | 3.2904e-06 | 4.0979e-06 | 5.1095e-06 | 6.3778e-06 | 7.9688e-06 | 9.9659e-06 | 1.2474e-05 | 1.5626e-05 | 1.9587e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 207.443 | 254.1993 | 312.2495 | 384.4167 | 474.2444 | 586.1824 | 725.8216 | 900.1898 | 1118.1246 | 1390.744 | 1732.0397 | 2159.6266 | 2695.6871 | 3368.1643 | 4212.2675 | 5272.3727 | 6604.4228 | 8278.9571 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 | 9235.3942 |  | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 43.8967 | 52.5416 | 69.6471 | 93.1276 | 125.5043 | 170.3303 | 232.6216 | 319.4713 | 440.9236 | 611.2198 | 850.5757 | 1187.7172 | 1663.5004 | 2336.0813 |  | 138.8206 | 170.1099 | 208.957 | 257.2512 | 317.3638 | 392.2725 | 485.719 | 602.406 | 748.2477 | 930.6842 | 1159.0789 | 1445.2196 | 1803.9506 | 2253.9715 | 2818.8444 | 3528.2655 | 4419.6718 | 5540.2682 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 111.6889 | 142.9781 | 181.8253 | 230.1195 | 290.232 | 365.1408 | 458.5872 | 575.2742 | 721.1159 | 903.5525 | 1131.9472 | 1418.0878 | 1776.8189 | 2226.8398 | 2791.7126 | 3501.1338 | 4392.5401 | 5507.7932 | 6137.2673 | 6122.7545 | 6102.743 | 6075.037 | 6036.5359 | 5982.8557 | 5907.7884 | 5802.5316 | 5654.5904 | 5446.2097 | 5152.1373 | 4736.428 |  | 0.080981 | 0.099234 | 0.12189 | 0.15007 | 0.18513 | 0.22883 | 0.28334 | 0.35141 | 0.43649 | 0.54291 | 0.67615 | 0.84307 | 1.0523 | 1.3149 | 1.6444 | 2.0582 | 2.5782 | 3.2319 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 |  | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.02368 | 0.03139 | 0.041972 | 0.056564 | 0.076767 | 0.10484 | 0.14398 | 0.19872 | 0.27547 | 0.38335 | 0.5353 | 0.74973 | 1.0529 |  | 0.061197 | 0.079449 | 0.10211 | 0.13028 | 0.16535 | 0.20905 | 0.26356 | 0.33163 | 0.41671 | 0.52313 | 0.65636 | 0.82328 | 1.0325 | 1.2951 | 1.6246 | 2.0384 | 2.5584 | 3.2082 | 3.5739 | 3.5633 | 3.5487 | 3.5285 | 3.5004 | 3.4613 | 3.4066 | 3.3298 | 3.2219 | 3.07 | 2.8556 | 2.5524 |  | 111.7501 | 143.0576 | 181.9274 | 230.2497 | 290.3974 | 365.3499 | 458.8508 | 575.6059 | 721.5326 | 904.0756 | 1132.6036 | 1418.9111 | 1777.8514 | 2228.1349 | 2793.3372 | 3503.1722 | 4395.0985 | 5511.0015 | 6140.8412 | 6126.3178 | 6106.2917 | 6078.5655 | 6040.0363 | 5986.317 | 5911.195 | 5805.8615 | 5657.8123 | 5449.2797 | 5154.9928 | 4738.9804 |  | 60.0496 | 73.5844 | 90.3885 | 111.2792 | 137.2821 | 169.6854 | 210.1075 | 260.5828 | 323.6695 | 402.5861 | 501.3829 | 625.1587 | 780.3351 | 975.0006 | 1219.3477 | 1526.2221 | 1911.8178 | 2396.5543 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 45.3792 | 58.914 | 75.7181 | 96.6087 | 122.6116 | 155.0149 | 195.437 | 245.9123 | 308.9991 | 387.9157 | 486.7124 | 610.4883 | 765.6646 | 960.3302 | 1204.6773 | 1511.5516 | 1897.1473 | 2378.9946 | 2650.1429 | 2642.2957 | 2631.4752 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 8.4635 | 10.3712 | 12.7396 | 15.684 | 19.3489 | 23.9159 | 29.6131 | 36.7272 | 45.6188 | 56.7415 | 70.6662 | 88.1114 | 109.9824 | 137.419 | 171.8579 | 215.1096 | 269.4564 | 337.7764 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 6.3959 | 8.3035 | 10.6719 | 13.6163 | 17.2812 | 21.8482 | 27.5454 | 34.6595 | 43.5511 | 54.6738 | 68.5985 | 86.0437 | 107.9147 | 135.3513 | 169.7902 | 213.0419 | 267.3887 | 335.3015 | 373.5178 | 372.4118 | 370.8867 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.028222 | 0.034583 | 0.042481 | 0.052299 | 0.06452 | 0.079749 | 0.098747 | 0.12247 | 0.15212 | 0.18921 | 0.23564 | 0.29381 | 0.36674 | 0.45823 | 0.57307 | 0.7173 | 0.89852 | 1.1263 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 | 1.2565 |  | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0068949 | 0.0082527 | 0.010939 | 0.014628 | 0.019713 | 0.026754 | 0.036538 | 0.050179 | 0.069256 | 0.096004 | 0.1336 | 0.18655 | 0.26129 | 0.36693 |  | 0.021327 | 0.027689 | 0.035586 | 0.045404 | 0.057625 | 0.072854 | 0.091852 | 0.11557 | 0.14522 | 0.18231 | 0.22875 | 0.28692 | 0.35985 | 0.45134 | 0.56618 | 0.7104 | 0.89163 | 1.1181 | 1.2455 | 1.2418 | 1.2367 | 1.2297 | 1.2199 | 1.2063 | 1.1872 | 1.1605 | 1.1229 | 1.0699 | 0.99517 | 0.88953 |  | 163.5464 | 210.3027 | 268.3529 | 340.5201 | 430.3478 | 542.2858 | 681.925 | 856.2933 | 1074.228 | 1346.8474 | 1688.1432 | 2115.7301 | 2651.7905 | 3324.2677 | 4168.3709 | 5228.4761 | 6560.5262 | 8226.4157 | 9165.7475 | 9142.267 | 9109.8904 | 9065.0646 | 9002.7735 | 8915.9241 | 8794.4724 | 8624.1769 | 8384.8219 | 8047.6817 | 7571.9004 | 6899.3222
| TRUE | 1297 | 22001452 | DDL | Blank | 22 | BUS ALL | OV-UV SUPERVISION | C | RPL | GROUP_2506 | GROUP 2506 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 12.7412 | 0.085397 | 0 | 0.085397 | 469.682 | 0 | 469.682 | 242.4085 | 34.1672 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 746.2577 | 45.1611 | 701.0966 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.7321 | 289.3759 | 325.1134 | 365.4886 | 411.1193 | 462.7066 | 521.0468 | 587.0442 | 661.7256 | 746.2577 | 841.9657 | 950.3555 | 1073.138 | 1212.2577 | 1369.9246 | 1548.6508 | 1751.292 | 1981.0945 | 2241.7497 | 2537.4547 | 2872.9824 | 3253.7609 | 3685.9636 | 4176.6123 | 4733.6945 | 5366.2962 | 6084.7541 | 6900.8287 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 162.2122 | 182.1283 | 204.6209 | 230.0323 | 258.7515 | 291.2197 | 327.938 | 369.4757 | 416.4789 | 469.682 | 529.919 | 598.1377 | 675.4149 | 762.9745 | 862.2074 | 974.6946 | 1102.2335 | 1246.8674 | 1410.9193 | 1597.031 | 1808.2065 | 2047.862 | 2319.8831 | 2628.6891 | 2979.3072 | 3377.456 | 3829.6413 | 4343.2648 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.0004 | 167.9165 | 190.409 | 215.8205 | 244.5397 | 277.0079 | 313.7262 | 355.2638 | 402.2671 | 455.4701 | 515.7072 | 583.9258 | 661.2031 | 748.7626 | 847.9956 | 960.4828 | 1088.0217 | 1229.8567 | 1388.3707 | 1566.8804 | 1767.5738 | 1992.7166 | 2244.5705 | 2525.2584 | 2836.5556 | 3179.57 | 3554.2625 | 3958.7345 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.0004 | 167.9165 | 190.409 | 215.8205 | 244.5397 | 277.0079 | 313.7262 | 355.2638 | 402.2671 | 455.4701 | 515.7072 | 583.9258 | 661.2031 | 748.7626 | 847.9956 | 960.4828 | 1088.0217 | 1229.8567 | 1388.3707 | 1566.8804 | 1767.5738 | 1992.7166 | 2244.5705 | 2525.2584 | 2836.5556 | 3179.57 | 3554.2625 | 3958.7345 | 3868.4608 | 3650.7088 |  | 83.7197 | 93.9986 | 105.6073 | 118.7225 | 133.5448 | 150.302 | 169.2528 | 190.6908 | 214.9498 | 242.4085 | 273.4975 | 308.706 | 348.5897 | 393.7803 | 444.9956 | 503.0516 | 568.876 | 643.5232 | 728.1924 | 824.2469 | 933.2371 | 1056.9262 | 1197.3195 | 1356.698 | 1537.6562 | 1743.1456 | 1976.5238 | 2241.6111 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.0499 | 79.3288 | 90.9375 | 104.0527 | 118.875 | 135.6322 | 154.583 | 176.021 | 200.28 | 227.7387 | 258.8278 | 294.0362 | 333.9199 | 379.1105 | 430.3258 | 488.3818 | 554.2062 | 625.9644 | 704.9171 | 793.1247 | 891.295 | 1000.0038 | 1119.58 | 1249.9344 | 1390.3046 | 1538.8829 | 1692.2712 | 1844.6897 | 1718.5977 | 1493.8289 |  | 11.8002 | 13.249 | 14.8852 | 16.7338 | 18.823 | 21.1849 | 23.856 | 26.8777 | 30.2969 | 34.1672 | 38.5492 | 43.5118 | 49.1334 | 55.5029 | 62.7217 | 70.9046 | 80.1825 | 90.7039 | 102.638 | 116.1767 | 131.5388 | 148.9727 | 168.761 | 191.2252 | 216.7311 | 245.6946 | 278.589 | 315.9528 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7325 | 11.1813 | 12.8175 | 14.6661 | 16.7553 | 19.1172 | 21.7883 | 24.81 | 28.2293 | 32.0995 | 36.4815 | 41.4441 | 47.0657 | 53.4352 | 60.654 | 68.8369 | 78.1148 | 88.229 | 99.3573 | 111.7901 | 125.6271 | 140.9495 | 157.8037 | 176.177 | 195.962 | 216.904 | 238.5239 | 260.0071 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 226.7828 | 258.4266 | 294.1641 | 334.5393 | 380.17 | 431.7573 | 490.0975 | 556.0949 | 630.7763 | 715.3084 | 811.0164 | 919.4062 | 1042.1887 | 1181.3084 | 1338.9753 | 1517.7015 | 1720.3427 | 1944.0501 | 2192.6452 | 2471.7953 | 2784.4959 | 3133.6699 | 3521.9542 | 3951.3698 | 4422.8222 | 4935.357 | 5485.0576 | 6063.4312 | 5829.293 | 5355.0913
| TRUE | 1298 | 22001453 | DDL | Blank | 22 | BUS ALL | BATTERY UV & BUS NV | C | EMAIL | GROUP_2655 | GROUP 2655 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 12.7412 | 0.085397 | 0 | 0.085397 | 469.682 | 0 | 469.682 | 242.4085 | 34.1672 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 746.2577 | 45.1611 | 701.0966 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.7321 | 289.3759 | 325.1134 | 365.4886 | 411.1193 | 462.7066 | 521.0468 | 587.0442 | 661.7256 | 746.2577 | 841.9657 | 950.3555 | 1073.138 | 1212.2577 | 1369.9246 | 1548.6508 | 1751.292 | 1981.0945 | 2241.7497 | 2537.4547 | 2872.9824 | 3253.7609 | 3685.9636 | 4176.6123 | 4733.6945 | 5366.2962 | 6084.7541 | 6900.8287 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 162.2122 | 182.1283 | 204.6209 | 230.0323 | 258.7515 | 291.2197 | 327.938 | 369.4757 | 416.4789 | 469.682 | 529.919 | 598.1377 | 675.4149 | 762.9745 | 862.2074 | 974.6946 | 1102.2335 | 1246.8674 | 1410.9193 | 1597.031 | 1808.2065 | 2047.862 | 2319.8831 | 2628.6891 | 2979.3072 | 3377.456 | 3829.6413 | 4343.2648 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.0004 | 167.9165 | 190.409 | 215.8205 | 244.5397 | 277.0079 | 313.7262 | 355.2638 | 402.2671 | 455.4701 | 515.7072 | 583.9258 | 661.2031 | 748.7626 | 847.9956 | 960.4828 | 1088.0217 | 1229.8567 | 1388.3707 | 1566.8804 | 1767.5738 | 1992.7166 | 2244.5705 | 2525.2584 | 2836.5556 | 3179.57 | 3554.2625 | 3958.7345 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.0004 | 167.9165 | 190.409 | 215.8205 | 244.5397 | 277.0079 | 313.7262 | 355.2638 | 402.2671 | 455.4701 | 515.7072 | 583.9258 | 661.2031 | 748.7626 | 847.9956 | 960.4828 | 1088.0217 | 1229.8567 | 1388.3707 | 1566.8804 | 1767.5738 | 1992.7166 | 2244.5705 | 2525.2584 | 2836.5556 | 3179.57 | 3554.2625 | 3958.7345 | 3868.4608 | 3650.7088 |  | 83.7197 | 93.9986 | 105.6073 | 118.7225 | 133.5448 | 150.302 | 169.2528 | 190.6908 | 214.9498 | 242.4085 | 273.4975 | 308.706 | 348.5897 | 393.7803 | 444.9956 | 503.0516 | 568.876 | 643.5232 | 728.1924 | 824.2469 | 933.2371 | 1056.9262 | 1197.3195 | 1356.698 | 1537.6562 | 1743.1456 | 1976.5238 | 2241.6111 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.0499 | 79.3288 | 90.9375 | 104.0527 | 118.875 | 135.6322 | 154.583 | 176.021 | 200.28 | 227.7387 | 258.8278 | 294.0362 | 333.9199 | 379.1105 | 430.3258 | 488.3818 | 554.2062 | 625.9644 | 704.9171 | 793.1247 | 891.295 | 1000.0038 | 1119.58 | 1249.9344 | 1390.3046 | 1538.8829 | 1692.2712 | 1844.6897 | 1718.5977 | 1493.8289 |  | 11.8002 | 13.249 | 14.8852 | 16.7338 | 18.823 | 21.1849 | 23.856 | 26.8777 | 30.2969 | 34.1672 | 38.5492 | 43.5118 | 49.1334 | 55.5029 | 62.7217 | 70.9046 | 80.1825 | 90.7039 | 102.638 | 116.1767 | 131.5388 | 148.9727 | 168.761 | 191.2252 | 216.7311 | 245.6946 | 278.589 | 315.9528 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7325 | 11.1813 | 12.8175 | 14.6661 | 16.7553 | 19.1172 | 21.7883 | 24.81 | 28.2293 | 32.0995 | 36.4815 | 41.4441 | 47.0657 | 53.4352 | 60.654 | 68.8369 | 78.1148 | 88.229 | 99.3573 | 111.7901 | 125.6271 | 140.9495 | 157.8037 | 176.177 | 195.962 | 216.904 | 238.5239 | 260.0071 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 226.7828 | 258.4266 | 294.1641 | 334.5393 | 380.17 | 431.7573 | 490.0975 | 556.0949 | 630.7763 | 715.3084 | 811.0164 | 919.4062 | 1042.1887 | 1181.3084 | 1338.9753 | 1517.7015 | 1720.3427 | 1944.0501 | 2192.6452 | 2471.7953 | 2784.4959 | 3133.6699 | 3521.9542 | 3951.3698 | 4422.8222 | 4935.357 | 5485.0576 | 6063.4312 | 5829.293 | 5355.0913
| TRUE | 1299 | 22001439 | DDL | Blank | 22 | BUS NO.1 | HIBP | X | ABB | RADHA_2524 | RADHA 2524 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 81.7572 | 388.9293 | 470.6866 | 49.6875 | 5.9058 | 2146.7004 |  | 9.8464 | 0.042169 | 0.0039776 | 0.038191 | 234.1153 | 1113.7154 | 1347.8307 | 142.2821 | 16.9115 | 6147.1666 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.36747 |  | 2672.9802 | 7654.1909 | 45.5967 | 7608.5943 |  | 0.040003 |  | 6.8694 | 7.1497 | 7.4416 | 7.7453 | 8.0614 | 8.3904 | 8.7329 | 9.0893 | 9.4603 | 9.8464 | 10.2482 | 10.6665 | 11.1019 | 11.555 | 12.0266 | 12.5174 | 13.0283 | 13.5601 | 14.1135 | 14.6896 | 15.2891 | 15.9131 | 16.5626 | 17.2386 | 17.9422 | 18.6745 | 19.4366 | 20.2299 | 21.0556 | 21.915 |  | 0.016313 | 0.018083 | 0.020059 | 0.022266 | 0.024731 | 0.027485 | 0.030564 | 0.034008 | 0.037859 | 0.042169 | 0.046992 | 0.052392 | 0.058439 | 0.065213 | 0.072802 | 0.081308 | 0.090842 | 0.10153 | 0.11352 | 0.12697 | 0.14205 | 0.15898 | 0.17798 | 0.19931 | 0.22326 | 0.25015 | 0.28035 | 0.31427 | 0.35238 | 0.3952 |  | 0.0015387 | 0.0017057 | 0.0018921 | 0.0021002 | 0.0023327 | 0.0025925 | 0.002883 | 0.0032078 | 0.0035711 | 0.0039776 | 0.0044325 | 0.0049419 | 0.0055123 | 0.0061512 | 0.0068671 | 0.0076693 | 0.0085687 | 0.009577 | 0.010708 | 0.011976 | 0.013399 | 0.014996 | 0.016788 | 0.0188 | 0.021059 | 0.023595 | 0.026444 | 0.029643 | 0.033238 | 0.037277 | 2960.9557 | 3282.2855 | 3640.9724 | 4041.5103 | 4488.9444 | 4988.9408 | 5547.8631 | 6172.8595 | 6871.9609 | 7654.1909 | 8529.6898 | 9509.8544 | 10607.4951 | 11837.013 | 13214.5992 | 14758.4594 | 16489.0665 | 18429.4453 | 20605.4932 | 23046.3414 | 25784.7611 | 28857.6223 | 32306.4093 | 36177.8023 | 40524.332 | 45405.1171 | 50886.6956 | 57043.9612 | 63961.2175 | 71733.3668 |  | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 37.5665 | 49.7966 | 66.5848 | 89.7336 | 121.7835 | 166.3209 | 228.4171 | 315.2536 | 437.0127 | 608.1485 | 849.1995 | 1189.3771 | 1670.2621 |  | 90.5654 | 100.3938 | 111.3648 | 123.6158 | 137.3013 | 152.5945 | 169.69 | 188.8064 | 210.1895 | 234.1153 | 260.8937 | 290.8736 | 324.4466 | 362.0533 | 404.1889 | 451.4103 | 504.3436 | 563.6931 | 630.2509 | 704.908 | 788.6668 | 882.655 | 988.1415 | 1106.554 | 1239.4993 | 1388.7857 | 1556.4482 | 1744.7777 | 1956.3527 | 2194.0759 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 76.3535 | 86.1819 | 97.1529 | 109.4039 | 123.0894 | 138.3826 | 155.4781 | 174.5946 | 195.9777 | 219.9034 | 246.6819 | 276.6617 | 310.2347 | 347.8414 | 389.977 | 437.1984 | 490.1317 | 546.6823 | 607.7021 | 674.7572 | 748.0338 | 827.5093 | 912.8285 | 1003.1228 | 1096.7471 | 1190.8988 | 1281.0681 | 1360.2456 | 1417.7823 | 1437.7525 |  | 430.8309 | 477.5857 | 529.7761 | 588.0559 | 653.1594 | 725.9109 | 807.2363 | 898.1758 | 999.8978 | 1113.7154 | 1241.104 | 1383.7219 | 1543.433 | 1722.3328 | 1922.7771 | 2147.415 | 2399.2252 | 2681.5581 | 2998.1818 | 3353.335 | 3751.786 | 4198.8996 | 4700.712 | 5264.0152 | 5896.4526 | 6606.6264 | 7404.2181 | 8300.1249 | 9306.6134 | 10437.4922 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 430.7643 | 477.5191 | 529.7095 | 587.9894 | 653.0928 | 725.8443 | 807.1697 | 898.1092 | 999.8313 | 1113.6489 | 1241.0375 | 1383.6553 | 1543.3664 | 1722.2662 | 1922.7105 | 2147.3484 | 2399.1587 | 2681.4784 | 2998.0762 | 3353.1937 | 3751.5957 | 4198.6413 | 4700.3592 | 5263.5306 | 5895.7839 | 6605.6994 | 7402.928 | 8298.3235 | 9304.0904 | 10433.9491 |  | 507.1179 | 563.701 | 626.8624 | 697.3933 | 776.1822 | 864.2269 | 962.6478 | 1072.7038 | 1195.8089 | 1333.5522 | 1487.7193 | 1660.317 | 1853.6012 | 2070.1077 | 2312.6876 | 2584.5468 | 2889.2903 | 3228.1608 | 3605.7783 | 4027.951 | 4499.6295 | 5026.1506 | 5613.1877 | 6266.6534 | 6992.531 | 7796.5982 | 8683.9961 | 9658.5691 | 10721.8726 | 11871.7016 |  | 55.0406 | 61.0137 | 67.6813 | 75.1268 | 83.444 | 92.7384 | 103.128 | 114.746 | 127.7414 | 142.2821 | 158.5566 | 176.7767 | 197.1805 | 220.0357 | 245.6434 | 274.3419 | 306.5117 | 342.581 | 383.0311 | 428.4035 | 479.3074 | 536.4282 | 600.537 | 672.5015 | 753.2982 | 844.026 | 945.9219 | 1060.378 | 1188.9614 | 1333.4363 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 40.3694 | 46.3426 | 53.0101 | 60.4556 | 68.7729 | 78.0672 | 88.4569 | 100.0748 | 113.0703 | 127.611 | 143.8854 | 162.1055 | 182.5093 | 205.3646 | 230.9722 | 259.6707 | 291.8406 | 325.0206 | 359.7537 | 397.2785 | 437.3615 | 479.5005 | 522.7903 | 565.728 | 605.933 | 639.7446 | 661.6432 | 663.4201 | 632.9875 | 552.6729 |  | 6.542 | 7.252 | 8.0445 | 8.9295 | 9.918 | 11.0228 | 12.2577 | 13.6385 | 15.1832 | 16.9115 | 18.8458 | 21.0114 | 23.4366 | 26.1531 | 29.1968 | 32.6079 | 36.4316 | 40.7187 | 45.5265 | 50.9194 | 56.9698 | 63.7591 | 71.379 | 79.9326 | 89.536 | 100.3198 | 112.431 | 126.0351 | 141.3183 | 158.4904 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 4.4744 | 5.1843 | 5.9768 | 6.8618 | 7.8503 | 8.9551 | 10.19 | 11.5709 | 13.1155 | 14.8438 | 16.7781 | 18.9437 | 21.3689 | 24.0854 | 27.1291 | 30.5402 | 34.3639 | 38.2438 | 42.2459 | 46.5328 | 51.0581 | 55.7359 | 60.4217 | 64.8843 | 68.7669 | 71.5291 | 72.3658 | 70.0893 | 62.9615 | 48.4526 |  | 2377.9767 | 2636.0403 | 2924.1058 | 3245.7823 | 3605.1217 | 4006.6744 | 4455.5511 | 4957.4928 | 5518.949 | 6147.1666 | 6850.2896 | 7637.4708 | 8518.9984 | 9506.438 | 10612.793 | 11852.6844 | 13242.5544 | 14800.8944 | 16548.5029 | 18508.7754 | 20708.031 | 23175.8804 | 25945.64 | 29054.7992 | 32545.5459 | 36465.3592 | 40867.6765 | 45812.6456 | 51367.9717 | 57609.8721 |  | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.43984 | 0.58304 | 0.7796 | 1.0506 | 1.4259 | 1.9474 | 2.6744 | 3.6911 | 5.1167 | 7.1205 | 9.9428 | 13.9257 | 19.5561 |  | 2377.6093 | 2635.6728 | 2923.7384 | 3245.4148 | 3604.7542 | 4006.3069 | 4455.1837 | 4957.1253 | 5518.5815 | 6146.7992 | 6849.9222 | 7637.1033 | 8518.6309 | 9506.0705 | 10612.4255 | 11852.317 | 13242.1869 | 14800.4546 | 16547.9199 | 18507.9958 | 20706.9804 | 23174.4545 | 25943.6926 | 29052.1247 | 32541.8548 | 36460.2424 | 40860.556 | 45802.7028 | 51354.046 | 57590.316 |  | 2929.5709 | 3250.9007 | 3609.5877 | 4010.1255 | 4457.5597 | 4957.5561 | 5516.4783 | 6141.4748 | 6840.5762 | 7622.8062 | 8498.305 | 9478.4696 | 10576.1103 | 11805.6282 | 13183.2145 | 14727.0747 | 16457.6817 | 18391.8797 | 20555.6978 | 22979.7581 | 25695.0295 | 28735.8416 | 32140.0923 | 35949.3905 | 40209.0856 | 44968.1144 | 50278.5611 | 56194.7812 | 62771.8676 | 70063.143
| TRUE | 1300 | 22001441 | DDL | Blank | 22 | BUS NO.1 | OVERCURRENT | Y | GE | SR760 | SR760 | SR760 | Digital |  | 0.0034106 | 1 |  | 6.6 | 0.017308 | 8.0863e-08 | 0.017308 | 71.3949 | 0.011321 | 71.4063 | 49.1308 | 6.9249 | 0.12497 |  | 12.4804 | 0.094782 | 4.4283e-07 | 0.094782 | 390.978 | 0.061996 | 391.04 | 269.0536 | 37.9225 | 0.68438 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 21.3177 | 0.0033803 | 21.3211 | 14.6699 | 2.0677 | 0.037315 |  | 127.5869 | 698.7004 | 38.0961 | 660.6044 |  | 0.063709 |  | 7.0342 | 7.4969 | 7.99 | 8.5157 | 9.0758 | 9.6729 | 10.3092 | 10.9873 | 11.7101 | 12.4804 | 13.3014 | 14.1764 | 15.109 | 16.1029 | 17.1621 | 18.2911 | 19.4943 | 20.7767 | 22.1435 | 23.6001 | 25.1526 | 26.8072 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.020378 | 0.024035 | 0.028395 | 0.033598 | 0.039812 | 0.04724 | 0.056126 | 0.066764 | 0.079507 | 0.094782 | 0.1131 | 0.13509 | 0.16149 | 0.19321 | 0.23132 | 0.27716 | 0.33229 | 0.39864 | 0.47852 | 0.5747 | 0.69057 | 0.8302 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 9.5206e-08 | 1.1229e-07 | 1.3266e-07 | 1.5697e-07 | 1.86e-07 | 2.2071e-07 | 2.6223e-07 | 3.1193e-07 | 3.7146e-07 | 4.4283e-07 | 5.2843e-07 | 6.3115e-07 | 7.5449e-07 | 9.0267e-07 | 1.0808e-06 | 1.2949e-06 | 1.5525e-06 | 1.8625e-06 | 2.2357e-06 | 2.685e-06 | 3.2264e-06 | 3.8787e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 150.2177 | 177.1742 | 209.3139 | 247.6682 | 293.478 | 348.2365 | 413.7418 | 492.1593 | 586.0976 | 698.7004 | 833.7573 | 995.8372 | 1190.4505 | 1424.2442 | 1705.2383 | 2043.1115 | 2449.5459 | 2938.6449 | 3527.4375 | 4236.4888 | 5090.6375 | 6119.8886 | 6942.2965 | 6942.2965 | 6942.2965 | 6942.2965 | 6942.2965 | 6942.2965 | 6942.2965 | 6942.2965 |  | 30.9902 | 30.9902 | 30.9902 | 30.9902 | 30.9902 | 30.9902 | 30.9902 | 30.9902 | 30.9902 | 30.9902 | 30.9902 | 30.9902 | 30.9902 | 30.9902 | 30.9902 | 30.9902 | 30.9902 | 37.0933 | 49.1694 | 65.7461 | 88.6034 | 120.2496 | 164.226 | 225.5401 | 311.2828 | 431.5084 | 600.4886 | 838.5034 | 1174.3964 | 1649.2244 |  | 84.0586 | 99.1429 | 117.1276 | 138.5899 | 164.2241 | 194.8658 | 231.5212 | 275.4019 | 327.9678 | 390.978 | 466.5529 | 557.2494 | 666.1509 | 796.9769 | 954.2152 | 1143.2819 | 1370.714 | 1644.4034 | 1973.8793 | 2370.6494 | 2848.6129 | 3424.5601 | 3884.7621 | 3884.7621 | 3884.7621 | 3884.7621 | 3884.7621 | 3884.7621 | 3884.7621 | 3884.7621 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 69.8468 | 84.9311 | 102.9158 | 124.3781 | 150.0122 | 180.654 | 217.3093 | 261.1901 | 313.756 | 376.7661 | 452.3411 | 543.0376 | 651.939 | 782.765 | 940.0034 | 1129.0701 | 1356.5022 | 1627.3928 | 1951.3307 | 2340.4988 | 2807.9802 | 3369.4146 | 3809.4495 | 3781.3314 | 3742.0105 | 3686.8761 | 3609.3832 | 3500.2316 | 3346.1939 | 3128.4419 |  | 0.013329 | 0.015721 | 0.018573 | 0.021976 | 0.02604 | 0.030899 | 0.036712 | 0.04367 | 0.052005 | 0.061996 | 0.07398 | 0.088361 | 0.10563 | 0.12637 | 0.15131 | 0.18129 | 0.21735 | 0.26075 | 0.31299 | 0.37591 | 0.45169 | 0.54302 | 0.61599 | 0.61599 | 0.61599 | 0.61599 | 0.61599 | 0.61599 | 0.61599 | 0.61599 |  | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.004046 | 0.0053632 | 0.0071713 | 0.0096645 | 0.013116 | 0.017913 | 0.024601 | 0.033953 | 0.047067 | 0.065499 | 0.09146 | 0.1281 | 0.17989 |  | 0.0099486 | 0.01234 | 0.015192 | 0.018595 | 0.02266 | 0.027519 | 0.033331 | 0.040289 | 0.048624 | 0.058616 | 0.070599 | 0.084981 | 0.10225 | 0.12299 | 0.14793 | 0.17791 | 0.21397 | 0.2567 | 0.30763 | 0.36873 | 0.44203 | 0.5299 | 0.59808 | 0.59139 | 0.58204 | 0.56893 | 0.55049 | 0.52453 | 0.48789 | 0.4361 |  | 69.8568 | 84.9434 | 102.931 | 124.3967 | 150.0349 | 180.6815 | 217.3427 | 261.2304 | 313.8046 | 376.8247 | 452.4117 | 543.1226 | 652.0413 | 782.888 | 940.1513 | 1129.248 | 1356.7161 | 1627.6495 | 1951.6383 | 2340.8676 | 2808.4222 | 3369.9445 | 3810.0476 | 3781.9227 | 3742.5925 | 3687.445 | 3609.9337 | 3500.7561 | 3346.6818 | 3128.878 |  | 57.8454 | 68.2257 | 80.602 | 95.3714 | 113.0117 | 134.098 | 159.3226 | 189.5193 | 225.6928 | 269.0536 | 321.0609 | 383.4742 | 458.4154 | 548.444 | 656.6484 | 786.7557 | 943.2643 | 1131.6052 | 1358.3358 | 1631.3753 | 1960.2885 | 2356.6297 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 43.1755 | 53.5558 | 65.9321 | 80.7015 | 98.3418 | 119.428 | 144.6526 | 174.8494 | 211.0229 | 254.3837 | 306.391 | 368.8043 | 443.7454 | 533.7741 | 641.9785 | 772.0857 | 928.5944 | 1114.0462 | 1335.0604 | 1600.2529 | 1918.346 | 2299.7067 | 2595.58 | 2566.5555 | 2525.9672 | 2469.0557 | 2389.0649 | 2276.395 | 2117.3923 | 1892.6214 |  | 8.1532 | 9.6163 | 11.3607 | 13.4424 | 15.9287 | 18.9008 | 22.4561 | 26.7123 | 31.8109 | 37.9225 | 45.2528 | 54.0498 | 64.6126 | 77.3019 | 92.5531 | 110.8914 | 132.9509 | 159.4971 | 191.4543 | 229.9385 | 276.2981 | 332.1615 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 6.0855 | 7.5486 | 9.293 | 11.3747 | 13.861 | 16.8331 | 20.3885 | 24.6446 | 29.7432 | 35.8548 | 43.1851 | 51.9821 | 62.5449 | 75.2342 | 90.4854 | 108.8237 | 130.8832 | 157.0222 | 188.1736 | 225.5519 | 270.3864 | 324.1383 | 365.8409 | 361.75 | 356.0292 | 348.0076 | 336.7331 | 320.8526 | 298.4415 | 266.7606 |  | 0.14714 | 0.17354 | 0.20502 | 0.24259 | 0.28746 | 0.3411 | 0.40526 | 0.48207 | 0.57408 | 0.68438 | 0.81666 | 0.97542 | 1.166 | 1.395 | 1.6703 | 2.0012 | 2.3993 | 2.8784 | 3.4551 | 4.1496 | 4.9863 | 5.9944 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 |  | 0.037315 | 0.037315 | 0.037315 | 0.037315 | 0.037315 | 0.037315 | 0.037315 | 0.037315 | 0.037315 | 0.037315 | 0.037315 | 0.037315 | 0.037315 | 0.037315 | 0.037315 | 0.037315 | 0.037315 | 0.044664 | 0.059204 | 0.079164 | 0.10669 | 0.14479 | 0.19774 | 0.27157 | 0.37481 | 0.51958 | 0.72304 | 1.0096 | 1.4141 | 1.9858 |  | 0.10982 | 0.13623 | 0.16771 | 0.20528 | 0.25015 | 0.30378 | 0.36794 | 0.44475 | 0.53677 | 0.64706 | 0.77935 | 0.93811 | 1.1287 | 1.3577 | 1.633 | 1.9639 | 2.362 | 2.8337 | 3.3959 | 4.0705 | 4.8796 | 5.8496 | 6.6022 | 6.5284 | 6.4252 | 6.2804 | 6.0769 | 5.7903 | 5.3859 | 4.8141 |  | 119.2276 | 146.184 | 178.3238 | 216.6781 | 262.4878 | 317.2464 | 382.7517 | 461.1691 | 555.1074 | 667.7103 | 802.7672 | 964.8471 | 1159.4603 | 1393.254 | 1674.2482 | 2012.1213 | 2418.5557 | 2901.5516 | 3478.2682 | 4170.7428 | 5002.0342 | 5999.6392 | 6778.0707 | 6716.7567 | 6631.0141 | 6510.7887 | 6341.8086 | 6103.7941 | 5767.9015 | 5293.074
| TRUE | 1301 | 22001440 | DDL | Blank | 22 | BUS NO.2 | HIBP | X | ABB | RADHA_2524 | RADHA 2524 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 81.7572 | 388.9293 | 470.6866 | 49.6875 | 5.9058 | 2146.7004 |  | 9.8464 | 0.042169 | 0.0039776 | 0.038191 | 234.1153 | 1113.7154 | 1347.8307 | 142.2821 | 16.9115 | 6147.1666 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.36747 |  | 2672.9802 | 7654.1909 | 45.5967 | 7608.5943 |  | 0.040003 |  | 6.8694 | 7.1497 | 7.4416 | 7.7453 | 8.0614 | 8.3904 | 8.7329 | 9.0893 | 9.4603 | 9.8464 | 10.2482 | 10.6665 | 11.1019 | 11.555 | 12.0266 | 12.5174 | 13.0283 | 13.5601 | 14.1135 | 14.6896 | 15.2891 | 15.9131 | 16.5626 | 17.2386 | 17.9422 | 18.6745 | 19.4366 | 20.2299 | 21.0556 | 21.915 |  | 0.016313 | 0.018083 | 0.020059 | 0.022266 | 0.024731 | 0.027485 | 0.030564 | 0.034008 | 0.037859 | 0.042169 | 0.046992 | 0.052392 | 0.058439 | 0.065213 | 0.072802 | 0.081308 | 0.090842 | 0.10153 | 0.11352 | 0.12697 | 0.14205 | 0.15898 | 0.17798 | 0.19931 | 0.22326 | 0.25015 | 0.28035 | 0.31427 | 0.35238 | 0.3952 |  | 0.0015387 | 0.0017057 | 0.0018921 | 0.0021002 | 0.0023327 | 0.0025925 | 0.002883 | 0.0032078 | 0.0035711 | 0.0039776 | 0.0044325 | 0.0049419 | 0.0055123 | 0.0061512 | 0.0068671 | 0.0076693 | 0.0085687 | 0.009577 | 0.010708 | 0.011976 | 0.013399 | 0.014996 | 0.016788 | 0.0188 | 0.021059 | 0.023595 | 0.026444 | 0.029643 | 0.033238 | 0.037277 | 2960.9557 | 3282.2855 | 3640.9724 | 4041.5103 | 4488.9444 | 4988.9408 | 5547.8631 | 6172.8595 | 6871.9609 | 7654.1909 | 8529.6898 | 9509.8544 | 10607.4951 | 11837.013 | 13214.5992 | 14758.4594 | 16489.0665 | 18429.4453 | 20605.4932 | 23046.3414 | 25784.7611 | 28857.6223 | 32306.4093 | 36177.8023 | 40524.332 | 45405.1171 | 50886.6956 | 57043.9612 | 63961.2175 | 71733.3668 |  | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 31.3855 | 37.5665 | 49.7966 | 66.5848 | 89.7336 | 121.7835 | 166.3209 | 228.4171 | 315.2536 | 437.0127 | 608.1485 | 849.1995 | 1189.3771 | 1670.2621 |  | 90.5654 | 100.3938 | 111.3648 | 123.6158 | 137.3013 | 152.5945 | 169.69 | 188.8064 | 210.1895 | 234.1153 | 260.8937 | 290.8736 | 324.4466 | 362.0533 | 404.1889 | 451.4103 | 504.3436 | 563.6931 | 630.2509 | 704.908 | 788.6668 | 882.655 | 988.1415 | 1106.554 | 1239.4993 | 1388.7857 | 1556.4482 | 1744.7777 | 1956.3527 | 2194.0759 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 76.3535 | 86.1819 | 97.1529 | 109.4039 | 123.0894 | 138.3826 | 155.4781 | 174.5946 | 195.9777 | 219.9034 | 246.6819 | 276.6617 | 310.2347 | 347.8414 | 389.977 | 437.1984 | 490.1317 | 546.6823 | 607.7021 | 674.7572 | 748.0338 | 827.5093 | 912.8285 | 1003.1228 | 1096.7471 | 1190.8988 | 1281.0681 | 1360.2456 | 1417.7823 | 1437.7525 |  | 430.8309 | 477.5857 | 529.7761 | 588.0559 | 653.1594 | 725.9109 | 807.2363 | 898.1758 | 999.8978 | 1113.7154 | 1241.104 | 1383.7219 | 1543.433 | 1722.3328 | 1922.7771 | 2147.415 | 2399.2252 | 2681.5581 | 2998.1818 | 3353.335 | 3751.786 | 4198.8996 | 4700.712 | 5264.0152 | 5896.4526 | 6606.6264 | 7404.2181 | 8300.1249 | 9306.6134 | 10437.4922 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 430.7643 | 477.5191 | 529.7095 | 587.9894 | 653.0928 | 725.8443 | 807.1697 | 898.1092 | 999.8313 | 1113.6489 | 1241.0375 | 1383.6553 | 1543.3664 | 1722.2662 | 1922.7105 | 2147.3484 | 2399.1587 | 2681.4784 | 2998.0762 | 3353.1937 | 3751.5957 | 4198.6413 | 4700.3592 | 5263.5306 | 5895.7839 | 6605.6994 | 7402.928 | 8298.3235 | 9304.0904 | 10433.9491 |  | 507.1179 | 563.701 | 626.8624 | 697.3933 | 776.1822 | 864.2269 | 962.6478 | 1072.7038 | 1195.8089 | 1333.5522 | 1487.7193 | 1660.317 | 1853.6012 | 2070.1077 | 2312.6876 | 2584.5468 | 2889.2903 | 3228.1608 | 3605.7783 | 4027.951 | 4499.6295 | 5026.1506 | 5613.1877 | 6266.6534 | 6992.531 | 7796.5982 | 8683.9961 | 9658.5691 | 10721.8726 | 11871.7016 |  | 55.0406 | 61.0137 | 67.6813 | 75.1268 | 83.444 | 92.7384 | 103.128 | 114.746 | 127.7414 | 142.2821 | 158.5566 | 176.7767 | 197.1805 | 220.0357 | 245.6434 | 274.3419 | 306.5117 | 342.581 | 383.0311 | 428.4035 | 479.3074 | 536.4282 | 600.537 | 672.5015 | 753.2982 | 844.026 | 945.9219 | 1060.378 | 1188.9614 | 1333.4363 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 40.3694 | 46.3426 | 53.0101 | 60.4556 | 68.7729 | 78.0672 | 88.4569 | 100.0748 | 113.0703 | 127.611 | 143.8854 | 162.1055 | 182.5093 | 205.3646 | 230.9722 | 259.6707 | 291.8406 | 325.0206 | 359.7537 | 397.2785 | 437.3615 | 479.5005 | 522.7903 | 565.728 | 605.933 | 639.7446 | 661.6432 | 663.4201 | 632.9875 | 552.6729 |  | 6.542 | 7.252 | 8.0445 | 8.9295 | 9.918 | 11.0228 | 12.2577 | 13.6385 | 15.1832 | 16.9115 | 18.8458 | 21.0114 | 23.4366 | 26.1531 | 29.1968 | 32.6079 | 36.4316 | 40.7187 | 45.5265 | 50.9194 | 56.9698 | 63.7591 | 71.379 | 79.9326 | 89.536 | 100.3198 | 112.431 | 126.0351 | 141.3183 | 158.4904 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 4.4744 | 5.1843 | 5.9768 | 6.8618 | 7.8503 | 8.9551 | 10.19 | 11.5709 | 13.1155 | 14.8438 | 16.7781 | 18.9437 | 21.3689 | 24.0854 | 27.1291 | 30.5402 | 34.3639 | 38.2438 | 42.2459 | 46.5328 | 51.0581 | 55.7359 | 60.4217 | 64.8843 | 68.7669 | 71.5291 | 72.3658 | 70.0893 | 62.9615 | 48.4526 |  | 2377.9767 | 2636.0403 | 2924.1058 | 3245.7823 | 3605.1217 | 4006.6744 | 4455.5511 | 4957.4928 | 5518.949 | 6147.1666 | 6850.2896 | 7637.4708 | 8518.9984 | 9506.438 | 10612.793 | 11852.6844 | 13242.5544 | 14800.8944 | 16548.5029 | 18508.7754 | 20708.031 | 23175.8804 | 25945.64 | 29054.7992 | 32545.5459 | 36465.3592 | 40867.6765 | 45812.6456 | 51367.9717 | 57609.8721 |  | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.43984 | 0.58304 | 0.7796 | 1.0506 | 1.4259 | 1.9474 | 2.6744 | 3.6911 | 5.1167 | 7.1205 | 9.9428 | 13.9257 | 19.5561 |  | 2377.6093 | 2635.6728 | 2923.7384 | 3245.4148 | 3604.7542 | 4006.3069 | 4455.1837 | 4957.1253 | 5518.5815 | 6146.7992 | 6849.9222 | 7637.1033 | 8518.6309 | 9506.0705 | 10612.4255 | 11852.317 | 13242.1869 | 14800.4546 | 16547.9199 | 18507.9958 | 20706.9804 | 23174.4545 | 25943.6926 | 29052.1247 | 32541.8548 | 36460.2424 | 40860.556 | 45802.7028 | 51354.046 | 57590.316 |  | 2929.5709 | 3250.9007 | 3609.5877 | 4010.1255 | 4457.5597 | 4957.5561 | 5516.4783 | 6141.4748 | 6840.5762 | 7622.8062 | 8498.305 | 9478.4696 | 10576.1103 | 11805.6282 | 13183.2145 | 14727.0747 | 16457.6817 | 18391.8797 | 20555.6978 | 22979.7581 | 25695.0295 | 28735.8416 | 32140.0923 | 35949.3905 | 40209.0856 | 44968.1144 | 50278.5611 | 56194.7812 | 62771.8676 | 70063.143
| TRUE | 1302 | 22001442 | DDL | Blank | 22 | BUS NO.2 | OVERCURRENT | X | GE | SR760 | SR760 | SR760 | Digital |  | 0.033587 | 1 |  | 6.6 | 0.017308 | 7.9633e-07 | 0.017307 | 71.3952 | 0.11149 | 71.5067 | 49.1349 | 6.9249 | 1.2307 |  | 12.4804 | 0.094782 | 4.3609e-06 | 0.094778 | 390.9796 | 0.61053 | 391.5901 | 269.0759 | 37.9225 | 6.7397 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 21.3178 | 0.033289 | 21.3511 | 14.6711 | 2.0677 | 0.36747 |  | 128.7972 | 705.3282 | 38.4574 | 666.8707 |  | 0.063709 |  | 7.0342 | 7.4969 | 7.99 | 8.5157 | 9.0758 | 9.6729 | 10.3092 | 10.9873 | 11.7101 | 12.4804 | 13.3014 | 14.1764 | 15.109 | 16.1029 | 17.1621 | 18.2911 | 19.4943 | 20.7767 | 22.1435 | 23.6001 | 25.1526 | 26.8072 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.020378 | 0.024035 | 0.028395 | 0.033598 | 0.039812 | 0.04724 | 0.056126 | 0.066764 | 0.079507 | 0.094782 | 0.1131 | 0.13509 | 0.16149 | 0.19321 | 0.23132 | 0.27716 | 0.33229 | 0.39864 | 0.47852 | 0.5747 | 0.69057 | 0.8302 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 9.3758e-07 | 1.1058e-06 | 1.3064e-06 | 1.5458e-06 | 1.8317e-06 | 2.1735e-06 | 2.5824e-06 | 3.0718e-06 | 3.6581e-06 | 4.3609e-06 | 5.2039e-06 | 6.2155e-06 | 7.4302e-06 | 8.8894e-06 | 1.0643e-05 | 1.2752e-05 | 1.5289e-05 | 1.8342e-05 | 2.2016e-05 | 2.6442e-05 | 3.1773e-05 | 3.8197e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 151.6426 | 178.8548 | 211.2994 | 250.0176 | 296.2619 | 351.5398 | 417.6665 | 496.8278 | 591.6572 | 705.3282 | 841.6661 | 1005.2835 | 1201.7428 | 1437.7543 | 1721.4139 | 2062.492 | 2472.7818 | 2966.5202 | 3560.8981 | 4276.6753 | 5138.9263 | 6177.9406 | 7008.1497 | 7008.1497 | 7008.1497 | 7008.1497 | 7008.1497 | 7008.1497 | 7008.1497 | 7008.1497 |  | 31.3518 | 31.3518 | 31.3518 | 31.3518 | 31.3518 | 31.3518 | 31.3518 | 31.3518 | 31.3518 | 31.3518 | 31.3518 | 31.3518 | 31.3518 | 31.3518 | 31.3518 | 31.3518 | 31.3518 | 37.5262 | 49.7432 | 66.5134 | 89.6374 | 121.6529 | 166.1426 | 228.1722 | 314.9156 | 436.5442 | 607.4965 | 848.289 | 1188.102 | 1668.4714 |  | 84.059 | 99.1433 | 117.1281 | 138.5905 | 164.2247 | 194.8666 | 231.5221 | 275.4031 | 327.9691 | 390.9796 | 466.5549 | 557.2517 | 666.1536 | 796.9802 | 954.2192 | 1143.2866 | 1370.7197 | 1644.4102 | 1973.8875 | 2370.6592 | 2848.6247 | 3424.5742 | 3884.7782 | 3884.7782 | 3884.7782 | 3884.7782 | 3884.7782 | 3884.7782 | 3884.7782 | 3884.7782 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 69.8471 | 84.9314 | 102.9162 | 124.3786 | 150.0129 | 180.6547 | 217.3102 | 261.1912 | 313.7573 | 376.7677 | 452.343 | 543.0398 | 651.9417 | 782.7683 | 940.0073 | 1129.0747 | 1356.5078 | 1627.3995 | 1951.3388 | 2340.5085 | 2807.9918 | 3369.4286 | 3809.4652 | 3781.347 | 3742.0259 | 3686.8913 | 3609.3981 | 3500.2461 | 3346.2078 | 3128.4548 |  | 0.13126 | 0.15482 | 0.1829 | 0.21641 | 0.25644 | 0.30429 | 0.36153 | 0.43005 | 0.51214 | 0.61053 | 0.72855 | 0.87017 | 1.0402 | 1.2445 | 1.4901 | 1.7853 | 2.1404 | 2.5678 | 3.0823 | 3.7019 | 4.4482 | 5.3476 | 6.0662 | 6.0662 | 6.0662 | 6.0662 | 6.0662 | 6.0662 | 6.0662 | 6.0662 |  | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.039844 | 0.052816 | 0.070622 | 0.095175 | 0.12917 | 0.17641 | 0.24227 | 0.33437 | 0.46351 | 0.64503 | 0.90069 | 1.2615 | 1.7715 |  | 0.097973 | 0.12153 | 0.14961 | 0.18313 | 0.22316 | 0.271 | 0.32824 | 0.39676 | 0.47885 | 0.57724 | 0.69526 | 0.83688 | 1.0069 | 1.2112 | 1.4568 | 1.752 | 2.1071 | 2.528 | 3.0295 | 3.6313 | 4.3531 | 5.2184 | 5.8898 | 5.824 | 5.7319 | 5.6027 | 5.4212 | 5.1656 | 4.8047 | 4.2947 |  | 69.9451 | 85.053 | 103.0658 | 124.5617 | 150.236 | 180.9257 | 217.6385 | 261.5879 | 314.2361 | 377.3449 | 453.0382 | 543.8767 | 652.9487 | 783.9795 | 941.4641 | 1130.8267 | 1358.6149 | 1629.9275 | 1954.3682 | 2344.1398 | 2812.3449 | 3374.647 | 3815.3551 | 3787.171 | 3747.7578 | 3692.494 | 3614.8193 | 3505.4116 | 3351.0125 | 3132.7495 |  | 57.8502 | 68.2314 | 80.6087 | 95.3793 | 113.021 | 134.109 | 159.3357 | 189.535 | 225.7115 | 269.0759 | 321.0875 | 383.5059 | 458.4533 | 548.4893 | 656.7027 | 786.8207 | 943.3423 | 1131.6987 | 1358.4481 | 1631.5102 | 1960.4506 | 2356.8245 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 43.1791 | 53.5602 | 65.9375 | 80.7081 | 98.3499 | 119.4379 | 144.6646 | 174.8639 | 211.0403 | 254.4047 | 306.4163 | 368.8348 | 443.7821 | 533.8182 | 642.0316 | 772.1496 | 928.6711 | 1114.1383 | 1335.1707 | 1600.3852 | 1918.5046 | 2299.8968 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 8.1532 | 9.6163 | 11.3607 | 13.4424 | 15.9288 | 18.9008 | 22.4562 | 26.7123 | 31.8109 | 37.9225 | 45.2528 | 54.0499 | 64.6126 | 77.302 | 92.5532 | 110.8915 | 132.951 | 159.4973 | 191.4545 | 229.9388 | 276.2984 | 332.1618 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 6.0855 | 7.5486 | 9.293 | 11.3747 | 13.8611 | 16.8331 | 20.3885 | 24.6446 | 29.7432 | 35.8548 | 43.1851 | 51.9822 | 62.5449 | 75.2343 | 90.4855 | 108.8238 | 130.8833 | 157.0224 | 188.1738 | 225.5521 | 270.3867 | 324.1386 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 1.449 | 1.709 | 2.019 | 2.389 | 2.8309 | 3.3591 | 3.991 | 4.7474 | 5.6535 | 6.7397 | 8.0424 | 9.6059 | 11.4831 | 13.7383 | 16.4487 | 19.7079 | 23.6283 | 28.3462 | 34.0257 | 40.8652 | 49.1043 | 59.0325 | 66.9654 | 66.9654 | 66.9654 | 66.9654 | 66.9654 | 66.9654 | 66.9654 | 66.9654 |  | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.36747 | 0.43984 | 0.58304 | 0.7796 | 1.0506 | 1.4259 | 1.9474 | 2.6744 | 3.6911 | 5.1167 | 7.1205 | 9.9428 | 13.9257 | 19.5561 |  | 1.0815 | 1.3415 | 1.6516 | 2.0215 | 2.4634 | 2.9916 | 3.6235 | 4.3799 | 5.286 | 6.3722 | 7.675 | 9.2384 | 11.1156 | 13.3708 | 16.0813 | 19.3404 | 23.2609 | 27.9063 | 33.4427 | 40.0856 | 48.0537 | 57.6066 | 65.0181 | 64.291 | 63.2743 | 61.8487 | 59.845 | 57.0227 | 53.0397 | 47.4093 |  | 120.2912 | 147.5033 | 179.9479 | 218.6661 | 264.9104 | 320.1884 | 386.315 | 465.4763 | 560.3057 | 673.9767 | 810.3147 | 973.932 | 1170.3914 | 1406.4028 | 1690.0624 | 2031.1405 | 2441.4303 | 2928.9945 | 3511.1555 | 4210.1627 | 5049.2899 | 6056.2891 | 6842.0091 | 6779.9801 | 6693.2377 | 6571.6105 | 6400.6602 | 6159.8704 | 5820.0614 | 5339.6975
| FALSE | 1303 | 22014602 | DDL | Blank | 22 | BUS VRR 1 | VOLTAGE REGULATION | C | RMS | 2V164S | 2V164 S | 2V164S | Digital |  | 0 | 1 |  | 1.1573 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 3.8384 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 30.9493 | 30.9493 | 0 |  | 0.11989 |  | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 125.7409 | 175.3373 | 245.2282 | 343.8976 | 483.4225 | 681.0073 | 961.1761 | 1358.9071 | 1924.1147 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 125.7409 | 175.3373 | 245.2282 | 343.8976 | 483.4225 | 681.0073 | 961.1761 | 1358.9071 | 1924.1147 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 129.7928 | 180.9874 | 253.1305 | 354.9794 | 499.0003 | 702.9521 | 992.149 | 1402.6966 | 1986.1174 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.2942 | 25.51 | 35.6785 | 50.034 | 70.3336 | 99.0804 | 139.8424 | 197.7086 | 279.9412 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 133.0601 | 194.2933 | 273.8279 | 381.8347 | 534.0372 | 748.9109 | 1052.7564 | 1483.0397 | 2093.1675 | 2959.3123 | 4190.1734 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 1304 | 22001450 | DDL | Blank | 22 | BUS VRR 2 | VOLTAGE REGULATION | C | RMS | 2V161 | RMS - 2V161 | 2V161 | Electronic |  | 0 | 2190 |  | 5.1928 | 0.0081074 | 0 | 0.0081074 | 27.8691 | 0 | 27.8691 | 23.0137 | 3.2438 | 0 |  | 12.6825 | 0.084312 | 0 | 0.084312 | 289.8209 | 0 | 289.8209 | 239.3281 | 33.7331 | 0 |  | 0.0051679 | 0 | 0.0051679 | 17.7648 | 0 | 17.7648 | 14.6698 | 2.0677 | 0 |  | 54.1266 | 562.8821 | 34.5023 | 528.3798 |  | 0.089295 |  | 5.6779 | 6.2082 | 6.7881 | 7.4221 | 8.1153 | 8.8733 | 9.7021 | 10.6083 | 11.5992 | 12.6825 | 13.8671 | 15.1624 | 16.5786 | 18.1271 | 19.8202 | 21.6714 | 23.6956 | 25.9088 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.01009 | 0.01261 | 0.015822 | 0.019923 | 0.025169 | 0.031892 | 0.040522 | 0.051617 | 0.0659 | 0.084312 | 0.10807 | 0.13877 | 0.17847 | 0.22985 | 0.29642 | 0.38273 | 0.49469 | 0.64005 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.3623 | 84.1897 | 105.631 | 133.0082 | 168.0316 | 212.9161 | 270.5326 | 344.6041 | 439.9624 | 562.8821 | 721.5153 | 926.4593 | 1191.4963 | 1534.558 | 1978.9844 | 2555.1656 | 3302.6847 | 4273.1139 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 34.684 | 43.3482 | 54.3881 | 68.4843 | 86.5174 | 109.6279 | 139.2938 | 177.4323 | 226.5311 | 289.8209 | 371.4992 | 477.0223 | 613.4865 | 790.1247 | 1018.9543 | 1315.6228 | 1700.511 | 2200.1728 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 20.4722 | 29.1364 | 40.1763 | 54.2724 | 72.3055 | 95.416 | 125.082 | 163.2205 | 212.3193 | 275.6091 | 357.2874 | 462.8105 | 599.2747 | 775.9129 | 1004.7424 | 1301.4109 | 1686.2991 | 2183.1622 | 2731.8443 | 2724.2423 | 2713.7602 | 2699.2475 | 2679.0803 | 2650.9622 | 2611.6413 | 2556.507 | 2479.0141 | 2369.8626 | 2215.825 | 1998.073 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.4722 | 29.1364 | 40.1763 | 54.2724 | 72.3055 | 95.416 | 125.082 | 163.2205 | 212.3193 | 275.6091 | 357.2874 | 462.8105 | 599.2747 | 775.9129 | 1004.7424 | 1301.4109 | 1686.2991 | 2183.1622 | 2731.8443 | 2724.2423 | 2713.7602 | 2699.2475 | 2679.0803 | 2650.9622 | 2611.6413 | 2556.507 | 2479.0141 | 2369.8626 | 2215.825 | 1998.073 |  | 28.6413 | 35.796 | 44.9126 | 56.5529 | 71.4442 | 90.5284 | 115.026 | 146.5199 | 187.0647 | 239.3281 | 306.7763 | 393.9151 | 506.6044 | 652.4685 | 841.4312 | 1086.4139 | 1404.2466 | 1816.857 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 13.9716 | 21.1263 | 30.2428 | 41.8831 | 56.7744 | 75.8586 | 100.3562 | 131.8501 | 172.3949 | 224.6583 | 292.1065 | 379.2453 | 491.9346 | 637.7988 | 826.7615 | 1071.7441 | 1389.5768 | 1799.2982 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 4.037 | 5.0454 | 6.3304 | 7.9711 | 10.07 | 12.7599 | 16.2128 | 20.6518 | 26.3666 | 33.7331 | 43.2398 | 55.5219 | 71.4054 | 91.9648 | 118.5989 | 153.1289 | 197.9271 | 256.0841 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 1.9693 | 2.9777 | 4.2627 | 5.9034 | 8.0023 | 10.6922 | 14.1451 | 18.5841 | 24.2989 | 31.6654 | 41.1721 | 53.4542 | 69.3377 | 89.8971 | 116.5312 | 151.0612 | 195.8594 | 253.6092 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 36.413 | 53.2404 | 74.6817 | 102.0589 | 137.0823 | 181.9668 | 239.5833 | 313.6548 | 409.0131 | 531.9328 | 690.566 | 895.51 | 1160.547 | 1503.6087 | 1948.0351 | 2524.2163 | 3271.7354 | 4236.0695 | 5300.4001 | 5283.8453 | 5261.0181 | 5229.4137 | 5185.4953 | 5124.262 | 5038.6324 | 4918.5654 | 4749.8081 | 4512.1072 | 4176.6572 | 3702.4555
| TRUE | 1305 | 22001445 | DDL | Blank | 22 | CAP NO.1 | CAP CONTROL | C | Siemens | DED_760 | DED 760 | DED | Electronic |  | 0 | 2190 |  | 6.6 | 0.014726 | 0 | 0.014726 | 80.9933 | 0 | 80.9933 | 41.8016 | 5.8919 | 0 |  | 9.8464 | 0.042169 | 0 | 0.042169 | 231.9276 | 0 | 231.9276 | 119.7006 | 16.8717 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 128.6867 | 368.4999 | 45.1611 | 323.3388 |  | 0.040003 |  | 6.8694 | 7.1497 | 7.4416 | 7.7453 | 8.0614 | 8.3904 | 8.7329 | 9.0893 | 9.4603 | 9.8464 | 10.2482 | 10.6665 | 11.1019 | 11.555 | 12.0266 | 12.5174 | 13.0283 | 13.5601 | 14.1135 | 14.6896 | 15.2891 | 15.9131 | 16.5626 | 17.2386 | 17.9422 | 18.6745 | 19.4366 | 20.2299 | 21.0556 | 21.915 |  | 0.016313 | 0.018083 | 0.020059 | 0.022266 | 0.024731 | 0.027485 | 0.030564 | 0.034008 | 0.037859 | 0.042169 | 0.046992 | 0.052392 | 0.058439 | 0.065213 | 0.072802 | 0.081308 | 0.090842 | 0.10153 | 0.11352 | 0.12697 | 0.14205 | 0.15898 | 0.17798 | 0.19931 | 0.22326 | 0.25015 | 0.28035 | 0.31427 | 0.35238 | 0.3952 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142.5509 | 158.0209 | 175.2893 | 194.5726 | 216.1137 | 240.1853 | 267.0938 | 297.1834 | 330.8406 | 368.4999 | 410.6495 | 457.8381 | 510.6824 | 569.8758 | 636.1977 | 710.5246 | 793.8421 | 887.2589 | 992.0215 | 1109.5326 | 1241.3699 | 1389.3083 | 1555.3451 | 1741.7277 | 1950.9851 | 2185.9634 | 2449.866 | 2746.2986 | 3079.3199 | 3453.4987 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 89.7191 | 99.4557 | 110.3241 | 122.4607 | 136.0183 | 151.1686 | 168.1043 | 187.0422 | 208.2255 | 231.9276 | 258.4559 | 288.1556 | 321.4149 | 358.6702 | 400.4121 | 447.1922 | 499.6308 | 558.4257 | 624.3616 | 698.3211 | 781.2972 | 874.4071 | 978.9079 | 1096.214 | 1227.917 | 1375.8084 | 1541.9042 | 1728.4739 | 1938.0718 | 2173.5737 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 75.5073 | 85.2438 | 96.1123 | 108.2489 | 121.8065 | 136.9567 | 153.8925 | 172.8303 | 194.0136 | 217.7158 | 244.244 | 273.9437 | 307.2031 | 344.4584 | 386.2002 | 432.9803 | 485.419 | 541.4151 | 601.8129 | 668.1705 | 740.6644 | 819.2617 | 903.5953 | 992.7833 | 1085.1654 | 1177.9224 | 1266.5254 | 1343.9435 | 1399.5039 | 1417.2538 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 75.5073 | 85.2438 | 96.1123 | 108.2489 | 121.8065 | 136.9567 | 153.8925 | 172.8303 | 194.0136 | 217.7158 | 244.244 | 273.9437 | 307.2031 | 344.4584 | 386.2002 | 432.9803 | 485.419 | 541.4151 | 601.8129 | 668.1705 | 740.6644 | 819.2617 | 903.5953 | 992.7833 | 1085.1654 | 1177.9224 | 1266.5254 | 1343.9435 | 1399.5039 | 1417.2538 |  | 46.3051 | 51.3303 | 56.9396 | 63.2035 | 70.2007 | 78.0199 | 86.7607 | 96.5347 | 107.4677 | 119.7006 | 133.3922 | 148.7205 | 165.8861 | 185.114 | 206.6575 | 230.8012 | 257.8655 | 288.2102 | 322.2405 | 360.4119 | 403.2369 | 451.292 | 505.2261 | 565.7692 | 633.7427 | 710.0712 | 795.7953 | 892.0861 | 1000.2621 | 1121.8075 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 31.6353 | 36.6605 | 42.2698 | 48.5337 | 55.5309 | 63.3501 | 72.0909 | 81.8649 | 92.7979 | 105.0308 | 118.7224 | 134.0508 | 151.2163 | 170.4442 | 191.9877 | 216.1315 | 243.1957 | 270.6514 | 298.9653 | 329.2897 | 361.2948 | 394.3696 | 427.4866 | 459.0055 | 486.3911 | 505.8086 | 511.5427 | 495.1647 | 444.3394 | 341.1159 |  | 6.5267 | 7.2349 | 8.0256 | 8.9085 | 9.8947 | 10.9968 | 12.2288 | 13.6065 | 15.1475 | 16.8717 | 18.8015 | 20.962 | 23.3815 | 26.0916 | 29.1282 | 32.5312 | 36.3459 | 40.6229 | 45.4195 | 50.7997 | 56.8358 | 63.6091 | 71.2111 | 79.7446 | 89.3254 | 100.0838 | 112.1665 | 125.7386 | 140.9859 | 158.1176 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 4.459 | 5.1673 | 5.9579 | 6.8408 | 7.827 | 8.9291 | 10.1611 | 11.5388 | 13.0798 | 14.804 | 16.7338 | 18.8943 | 21.3138 | 24.0239 | 27.0605 | 30.4635 | 34.2782 | 38.148 | 42.1388 | 46.413 | 50.9241 | 55.586 | 60.2538 | 64.6964 | 68.5563 | 71.2932 | 72.1014 | 69.7929 | 62.6292 | 48.0799 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 111.6016 | 127.0716 | 144.34 | 163.6233 | 185.1644 | 209.236 | 236.1445 | 266.2341 | 299.8913 | 337.5506 | 379.7002 | 426.8888 | 479.7331 | 538.9265 | 605.2484 | 679.5753 | 762.8928 | 850.2145 | 942.917 | 1043.8732 | 1152.8833 | 1269.2173 | 1391.3358 | 1516.4851 | 1640.1128 | 1755.0242 | 1850.1695 | 1908.9012 | 1906.4725 | 1806.4496
| TRUE | 1306 | 22001443 | DDL | Blank | 22 | CAP NO.1 | OVERCURRENT | X | ASEA | GROUP_2603 | GROUP 2603 | GROUP 2000s | Electronic |  | 0.2894 | 2190 |  | 8.25 | 0.026286 | 0.013817 | 0.012468 | 152.1704 | 3868.8382 | 4021.0086 | 153.0587 | 10.655 | 21354.1023 |  | 12.7412 | 0.085397 | 0.04489 | 0.040507 | 494.3712 | 12569.0828 | 13063.454 | 497.2571 | 34.6161 | 69375.2136 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.57365 | 28.9984 | 14.6814 | 2.0677 | 3.1663 |  | 25538.8247 | 82970.5409 | 48.9138 | 82921.627 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0.015503 | 0.017407 | 0.019557 | 0.021985 | 0.02473 | 0.027833 | 0.031342 | 0.035312 | 0.039805 | 0.04489 | 0.050647 | 0.057167 | 0.064552 | 0.072921 | 0.082405 | 0.093156 | 0.10535 | 0.11917 | 0.13485 | 0.15264 | 0.17282 | 0.19572 | 0.22172 | 0.25124 | 0.28475 | 0.3228 | 0.36602 | 0.41511 | 0.4212 | 0.4212 | 28655.2143 | 32173.4403 | 36146.8066 | 40635.8108 | 45709.126 | 51444.7168 | 57931.1095 | 65268.8365 | 73572.0799 | 82970.5409 | 93611.5671 | 105662.5735 | 119313.7958 | 134781.4256 | 152311.1762 | 172182.3423 | 194712.4193 | 220262.3615 | 249242.5665 | 282119.6869 | 319424.3848 | 361760.1577 | 409813.3867 | 464364.775 | 526302.3699 | 596636.3885 | 676516.0965 | 767249.0257 | 778513.0821 | 778513.0821 |  | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 41.5429 | 55.0675 | 73.6328 | 99.2319 | 134.6743 | 183.9259 | 252.595 | 348.6231 | 483.2704 | 672.5209 | 939.0871 | 1315.2725 | 1847.059 |  | 170.7391 | 191.7021 | 215.3769 | 242.1242 | 272.353 | 306.5279 | 345.1764 | 388.8975 | 438.3715 | 494.3712 | 557.7747 | 629.5793 | 710.9187 | 803.0809 | 907.5301 | 1025.9304 | 1160.1735 | 1312.4101 | 1485.0856 | 1680.9805 | 1903.2566 | 2155.5098 | 2441.8299 | 2766.8686 | 3135.9173 | 3554.9951 | 4030.9499 | 4571.5726 | 4638.6883 | 4638.6883 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 156.5267 | 177.4897 | 201.1646 | 227.9118 | 258.1406 | 292.3155 | 330.964 | 374.6851 | 424.1591 | 480.1588 | 543.5623 | 615.3669 | 696.7063 | 788.8685 | 893.3177 | 1011.718 | 1145.9611 | 1295.3988 | 1462.5361 | 1650.8287 | 1862.6222 | 2100.3622 | 2366.5143 | 2663.4338 | 2993.16 | 3357.1013 | 3755.5602 | 4187.027 | 4100.099 | 3882.3384 |  | 4340.9354 | 4873.9062 | 5475.8255 | 6155.858 | 6924.4069 | 7793.283 | 8775.8969 | 9887.4782 | 11145.3241 | 12569.0828 | 14181.0759 | 16006.6648 | 18074.668 | 20417.836 | 23073.3917 | 26083.6448 | 29496.6924 | 33367.2148 | 37757.3826 | 42737.8883 | 48389.121 | 54802.5038 | 62082.0154 | 70345.9234 | 79728.7567 | 90383.5517 | 102484.4089 | 116229.4043 | 117935.7793 | 117935.7793 |  | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.68662 | 0.91016 | 1.217 | 1.6401 | 2.2259 | 3.0399 | 4.1749 | 5.7621 | 7.9875 | 11.1155 | 15.5213 | 21.7389 | 30.5284 |  | 4340.3618 | 4873.3326 | 5475.2519 | 6155.2844 | 6923.8333 | 7792.7093 | 8775.3232 | 9886.9045 | 11144.7504 | 12568.5092 | 14180.5023 | 16006.0911 | 18074.0944 | 20417.2624 | 23072.818 | 26083.0712 | 29496.1188 | 33366.5282 | 37756.4725 | 42736.6713 | 48387.4809 | 54800.2779 | 62078.9754 | 70341.7485 | 79722.9947 | 90375.5642 | 102473.2934 | 116213.883 | 117914.0404 | 117905.251 |  | 4496.8885 | 5050.8222 | 5676.4164 | 6383.1962 | 7181.9739 | 8085.0249 | 9106.2873 | 10261.5896 | 11568.9095 | 13048.668 | 14724.0646 | 16621.4581 | 18770.8007 | 21206.1309 | 23966.1357 | 27094.7891 | 30642.0798 | 34661.927 | 39219.0085 | 44387.5 | 50250.1031 | 56900.6401 | 64445.4898 | 73005.1823 | 82716.1547 | 93732.6655 | 106228.8537 | 120400.91 | 122014.1394 | 121787.5893 |  | 171.7357 | 192.8211 | 216.6342 | 243.5376 | 273.9428 | 308.3173 | 347.1913 | 391.1676 | 440.9304 | 497.2571 | 561.0306 | 633.2544 | 715.0686 | 807.7688 | 912.8277 | 1031.9191 | 1166.9458 | 1320.0711 | 1493.7546 | 1690.793 | 1914.3666 | 2168.0924 | 2456.0838 | 2783.0199 | 3154.2228 | 3575.747 | 4054.4802 | 4598.2586 | 4665.7661 | 4665.7661 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 157.0543 | 178.1397 | 201.9528 | 228.8562 | 259.2614 | 293.6358 | 332.5099 | 376.4862 | 426.249 | 482.5757 | 546.3492 | 618.573 | 700.3872 | 793.0874 | 898.1463 | 1017.2377 | 1152.2644 | 1302.4984 | 1470.4609 | 1659.6462 | 1872.3913 | 2111.1248 | 2378.2827 | 2676.1716 | 3006.7544 | 3371.3224 | 3770.0022 | 4201.0224 | 4109.4026 | 3884.4555 |  | 11.9552 | 13.4231 | 15.0808 | 16.9537 | 19.0703 | 21.4632 | 24.1694 | 27.2308 | 30.695 | 34.6161 | 39.0557 | 44.0835 | 49.7789 | 56.2321 | 63.5457 | 71.8362 | 81.2359 | 91.8956 | 103.9864 | 117.7031 | 133.267 | 150.9299 | 170.9782 | 193.7375 | 219.5785 | 248.9226 | 282.2492 | 320.1038 | 324.8033 | 324.8033 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 9.8875 | 11.3554 | 13.0131 | 14.8859 | 17.0026 | 19.3955 | 22.1017 | 25.1631 | 28.6273 | 32.5484 | 36.988 | 42.0158 | 47.7112 | 54.1644 | 61.478 | 69.7685 | 79.1682 | 89.4207 | 100.7058 | 113.3164 | 127.3552 | 142.9067 | 160.0208 | 178.6892 | 198.8093 | 220.1317 | 242.1836 | 264.1576 | 246.4458 | 214.7645 |  | 23959.8488 | 26901.5879 | 30223.8892 | 33977.3373 | 38219.3529 | 43015.1254 | 48438.6754 | 54574.0624 | 61516.7589 | 69375.2136 | 78272.6303 | 88348.9915 | 99763.3616 | 112696.5077 | 127353.881 | 143969.0118 | 162807.3717 | 184170.7698 | 208402.3572 | 235892.3221 | 267084.3736 | 302483.1219 | 342662.4794 | 388275.2255 | 440063.8945 | 498873.1721 | 565664.0083 | 641529.6864 | 650948.0452 | 650948.0452 |  | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.7898 | 5.0236 | 6.7173 | 9.0526 | 12.2859 | 16.779 | 23.0435 | 31.8038 | 44.0873 | 61.3521 | 85.6701 | 119.9884 | 168.5017 |  | 23956.6826 | 26898.4216 | 30220.7229 | 33974.1711 | 38216.1866 | 43011.9591 | 48435.5091 | 54570.8962 | 61513.5927 | 69372.0474 | 78269.464 | 88345.8252 | 99760.1954 | 112693.3414 | 127350.7147 | 143965.8456 | 162804.2054 | 184166.98 | 208397.3335 | 235885.6048 | 267075.321 | 302470.8359 | 342645.7004 | 388252.182 | 440032.0907 | 498829.0848 | 565602.6562 | 641444.0163 | 650828.0568 | 650779.5435 |  | 28620.5129 | 32138.7389 | 36112.1052 | 40601.1094 | 45674.4245 | 51410.0153 | 57896.408 | 65234.1351 | 73537.3785 | 82935.8394 | 93576.8657 | 105627.872 | 119279.0944 | 134746.7242 | 152276.4748 | 172147.6408 | 194677.7179 | 220220.8261 | 249187.5088 | 282046.0673 | 319325.1706 | 361625.5075 | 409629.4937 | 464112.2251 | 525953.809 | 596153.2044 | 675843.6957 | 766310.1063 | 777198.0445 | 776666.3529
| TRUE | 1307 | 22001444 | DDL | Blank | 22 | CAP NO.1 | NEUTRAL BALANCE | X | ASEA | GROUP_2749 | GROUP 2749 | GROUP 2000s | Electronic |  | 0.2894 | 2190 |  | 8.25 | 0.026286 | 0.013817 | 0.012468 | 152.1704 | 3868.8382 | 4021.0086 | 153.0587 | 10.655 | 21354.1023 |  | 12.7412 | 0.085397 | 0.04489 | 0.040507 | 494.3712 | 12569.0828 | 13063.454 | 497.2571 | 34.6161 | 69375.2136 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.57365 | 28.9984 | 14.6814 | 2.0677 | 3.1663 |  | 25538.8247 | 82970.5409 | 48.9138 | 82921.627 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0.015503 | 0.017407 | 0.019557 | 0.021985 | 0.02473 | 0.027833 | 0.031342 | 0.035312 | 0.039805 | 0.04489 | 0.050647 | 0.057167 | 0.064552 | 0.072921 | 0.082405 | 0.093156 | 0.10535 | 0.11917 | 0.13485 | 0.15264 | 0.17282 | 0.19572 | 0.22172 | 0.25124 | 0.28475 | 0.3228 | 0.36602 | 0.41511 | 0.4212 | 0.4212 | 28655.2143 | 32173.4403 | 36146.8066 | 40635.8108 | 45709.126 | 51444.7168 | 57931.1095 | 65268.8365 | 73572.0799 | 82970.5409 | 93611.5671 | 105662.5735 | 119313.7958 | 134781.4256 | 152311.1762 | 172182.3423 | 194712.4193 | 220262.3615 | 249242.5665 | 282119.6869 | 319424.3848 | 361760.1577 | 409813.3867 | 464364.775 | 526302.3699 | 596636.3885 | 676516.0965 | 767249.0257 | 778513.0821 | 778513.0821 |  | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 34.7076 | 41.5429 | 55.0675 | 73.6328 | 99.2319 | 134.6743 | 183.9259 | 252.595 | 348.6231 | 483.2704 | 672.5209 | 939.0871 | 1315.2725 | 1847.059 |  | 170.7391 | 191.7021 | 215.3769 | 242.1242 | 272.353 | 306.5279 | 345.1764 | 388.8975 | 438.3715 | 494.3712 | 557.7747 | 629.5793 | 710.9187 | 803.0809 | 907.5301 | 1025.9304 | 1160.1735 | 1312.4101 | 1485.0856 | 1680.9805 | 1903.2566 | 2155.5098 | 2441.8299 | 2766.8686 | 3135.9173 | 3554.9951 | 4030.9499 | 4571.5726 | 4638.6883 | 4638.6883 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 156.5267 | 177.4897 | 201.1646 | 227.9118 | 258.1406 | 292.3155 | 330.964 | 374.6851 | 424.1591 | 480.1588 | 543.5623 | 615.3669 | 696.7063 | 788.8685 | 893.3177 | 1011.718 | 1145.9611 | 1295.3988 | 1462.5361 | 1650.8287 | 1862.6222 | 2100.3622 | 2366.5143 | 2663.4338 | 2993.16 | 3357.1013 | 3755.5602 | 4187.027 | 4100.099 | 3882.3384 |  | 4340.9354 | 4873.9062 | 5475.8255 | 6155.858 | 6924.4069 | 7793.283 | 8775.8969 | 9887.4782 | 11145.3241 | 12569.0828 | 14181.0759 | 16006.6648 | 18074.668 | 20417.836 | 23073.3917 | 26083.6448 | 29496.6924 | 33367.2148 | 37757.3826 | 42737.8883 | 48389.121 | 54802.5038 | 62082.0154 | 70345.9234 | 79728.7567 | 90383.5517 | 102484.4089 | 116229.4043 | 117935.7793 | 117935.7793 |  | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.68662 | 0.91016 | 1.217 | 1.6401 | 2.2259 | 3.0399 | 4.1749 | 5.7621 | 7.9875 | 11.1155 | 15.5213 | 21.7389 | 30.5284 |  | 4340.3618 | 4873.3326 | 5475.2519 | 6155.2844 | 6923.8333 | 7792.7093 | 8775.3232 | 9886.9045 | 11144.7504 | 12568.5092 | 14180.5023 | 16006.0911 | 18074.0944 | 20417.2624 | 23072.818 | 26083.0712 | 29496.1188 | 33366.5282 | 37756.4725 | 42736.6713 | 48387.4809 | 54800.2779 | 62078.9754 | 70341.7485 | 79722.9947 | 90375.5642 | 102473.2934 | 116213.883 | 117914.0404 | 117905.251 |  | 4496.8885 | 5050.8222 | 5676.4164 | 6383.1962 | 7181.9739 | 8085.0249 | 9106.2873 | 10261.5896 | 11568.9095 | 13048.668 | 14724.0646 | 16621.4581 | 18770.8007 | 21206.1309 | 23966.1357 | 27094.7891 | 30642.0798 | 34661.927 | 39219.0085 | 44387.5 | 50250.1031 | 56900.6401 | 64445.4898 | 73005.1823 | 82716.1547 | 93732.6655 | 106228.8537 | 120400.91 | 122014.1394 | 121787.5893 |  | 171.7357 | 192.8211 | 216.6342 | 243.5376 | 273.9428 | 308.3173 | 347.1913 | 391.1676 | 440.9304 | 497.2571 | 561.0306 | 633.2544 | 715.0686 | 807.7688 | 912.8277 | 1031.9191 | 1166.9458 | 1320.0711 | 1493.7546 | 1690.793 | 1914.3666 | 2168.0924 | 2456.0838 | 2783.0199 | 3154.2228 | 3575.747 | 4054.4802 | 4598.2586 | 4665.7661 | 4665.7661 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 157.0543 | 178.1397 | 201.9528 | 228.8562 | 259.2614 | 293.6358 | 332.5099 | 376.4862 | 426.249 | 482.5757 | 546.3492 | 618.573 | 700.3872 | 793.0874 | 898.1463 | 1017.2377 | 1152.2644 | 1302.4984 | 1470.4609 | 1659.6462 | 1872.3913 | 2111.1248 | 2378.2827 | 2676.1716 | 3006.7544 | 3371.3224 | 3770.0022 | 4201.0224 | 4109.4026 | 3884.4555 |  | 11.9552 | 13.4231 | 15.0808 | 16.9537 | 19.0703 | 21.4632 | 24.1694 | 27.2308 | 30.695 | 34.6161 | 39.0557 | 44.0835 | 49.7789 | 56.2321 | 63.5457 | 71.8362 | 81.2359 | 91.8956 | 103.9864 | 117.7031 | 133.267 | 150.9299 | 170.9782 | 193.7375 | 219.5785 | 248.9226 | 282.2492 | 320.1038 | 324.8033 | 324.8033 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 9.8875 | 11.3554 | 13.0131 | 14.8859 | 17.0026 | 19.3955 | 22.1017 | 25.1631 | 28.6273 | 32.5484 | 36.988 | 42.0158 | 47.7112 | 54.1644 | 61.478 | 69.7685 | 79.1682 | 89.4207 | 100.7058 | 113.3164 | 127.3552 | 142.9067 | 160.0208 | 178.6892 | 198.8093 | 220.1317 | 242.1836 | 264.1576 | 246.4458 | 214.7645 |  | 23959.8488 | 26901.5879 | 30223.8892 | 33977.3373 | 38219.3529 | 43015.1254 | 48438.6754 | 54574.0624 | 61516.7589 | 69375.2136 | 78272.6303 | 88348.9915 | 99763.3616 | 112696.5077 | 127353.881 | 143969.0118 | 162807.3717 | 184170.7698 | 208402.3572 | 235892.3221 | 267084.3736 | 302483.1219 | 342662.4794 | 388275.2255 | 440063.8945 | 498873.1721 | 565664.0083 | 641529.6864 | 650948.0452 | 650948.0452 |  | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.1663 | 3.7898 | 5.0236 | 6.7173 | 9.0526 | 12.2859 | 16.779 | 23.0435 | 31.8038 | 44.0873 | 61.3521 | 85.6701 | 119.9884 | 168.5017 |  | 23956.6826 | 26898.4216 | 30220.7229 | 33974.1711 | 38216.1866 | 43011.9591 | 48435.5091 | 54570.8962 | 61513.5927 | 69372.0474 | 78269.464 | 88345.8252 | 99760.1954 | 112693.3414 | 127350.7147 | 143965.8456 | 162804.2054 | 184166.98 | 208397.3335 | 235885.6048 | 267075.321 | 302470.8359 | 342645.7004 | 388252.182 | 440032.0907 | 498829.0848 | 565602.6562 | 641444.0163 | 650828.0568 | 650779.5435 |  | 28620.5129 | 32138.7389 | 36112.1052 | 40601.1094 | 45674.4245 | 51410.0153 | 57896.408 | 65234.1351 | 73537.3785 | 82935.8394 | 93576.8657 | 105627.872 | 119279.0944 | 134746.7242 | 152276.4748 | 172147.6408 | 194677.7179 | 220220.8261 | 249187.5088 | 282046.0673 | 319325.1706 | 361625.5075 | 409629.4937 | 464112.2251 | 525953.809 | 596153.2044 | 675843.6957 | 766310.1063 | 777198.0445 | 776666.3529
| TRUE | 1308 | 22001436 | DDL | Blank | 22 | CB BT 1-2 | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 12.7412 | 0.085397 | 0 | 0.085397 | 469.682 | 0 | 469.682 | 242.4085 | 34.1672 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 746.2577 | 45.1611 | 701.0966 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.7321 | 289.3759 | 325.1134 | 365.4886 | 411.1193 | 462.7066 | 521.0468 | 587.0442 | 661.7256 | 746.2577 | 841.9657 | 950.3555 | 1073.138 | 1212.2577 | 1369.9246 | 1548.6508 | 1751.292 | 1981.0945 | 2241.7497 | 2537.4547 | 2872.9824 | 3253.7609 | 3685.9636 | 4176.6123 | 4733.6945 | 5366.2962 | 6084.7541 | 6900.8287 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 162.2122 | 182.1283 | 204.6209 | 230.0323 | 258.7515 | 291.2197 | 327.938 | 369.4757 | 416.4789 | 469.682 | 529.919 | 598.1377 | 675.4149 | 762.9745 | 862.2074 | 974.6946 | 1102.2335 | 1246.8674 | 1410.9193 | 1597.031 | 1808.2065 | 2047.862 | 2319.8831 | 2628.6891 | 2979.3072 | 3377.456 | 3829.6413 | 4343.2648 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.0004 | 167.9165 | 190.409 | 215.8205 | 244.5397 | 277.0079 | 313.7262 | 355.2638 | 402.2671 | 455.4701 | 515.7072 | 583.9258 | 661.2031 | 748.7626 | 847.9956 | 960.4828 | 1088.0217 | 1229.8567 | 1388.3707 | 1566.8804 | 1767.5738 | 1992.7166 | 2244.5705 | 2525.2584 | 2836.5556 | 3179.57 | 3554.2625 | 3958.7345 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.0004 | 167.9165 | 190.409 | 215.8205 | 244.5397 | 277.0079 | 313.7262 | 355.2638 | 402.2671 | 455.4701 | 515.7072 | 583.9258 | 661.2031 | 748.7626 | 847.9956 | 960.4828 | 1088.0217 | 1229.8567 | 1388.3707 | 1566.8804 | 1767.5738 | 1992.7166 | 2244.5705 | 2525.2584 | 2836.5556 | 3179.57 | 3554.2625 | 3958.7345 | 3868.4608 | 3650.7088 |  | 83.7197 | 93.9986 | 105.6073 | 118.7225 | 133.5448 | 150.302 | 169.2528 | 190.6908 | 214.9498 | 242.4085 | 273.4975 | 308.706 | 348.5897 | 393.7803 | 444.9956 | 503.0516 | 568.876 | 643.5232 | 728.1924 | 824.2469 | 933.2371 | 1056.9262 | 1197.3195 | 1356.698 | 1537.6562 | 1743.1456 | 1976.5238 | 2241.6111 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.0499 | 79.3288 | 90.9375 | 104.0527 | 118.875 | 135.6322 | 154.583 | 176.021 | 200.28 | 227.7387 | 258.8278 | 294.0362 | 333.9199 | 379.1105 | 430.3258 | 488.3818 | 554.2062 | 625.9644 | 704.9171 | 793.1247 | 891.295 | 1000.0038 | 1119.58 | 1249.9344 | 1390.3046 | 1538.8829 | 1692.2712 | 1844.6897 | 1718.5977 | 1493.8289 |  | 11.8002 | 13.249 | 14.8852 | 16.7338 | 18.823 | 21.1849 | 23.856 | 26.8777 | 30.2969 | 34.1672 | 38.5492 | 43.5118 | 49.1334 | 55.5029 | 62.7217 | 70.9046 | 80.1825 | 90.7039 | 102.638 | 116.1767 | 131.5388 | 148.9727 | 168.761 | 191.2252 | 216.7311 | 245.6946 | 278.589 | 315.9528 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7325 | 11.1813 | 12.8175 | 14.6661 | 16.7553 | 19.1172 | 21.7883 | 24.81 | 28.2293 | 32.0995 | 36.4815 | 41.4441 | 47.0657 | 53.4352 | 60.654 | 68.8369 | 78.1148 | 88.229 | 99.3573 | 111.7901 | 125.6271 | 140.9495 | 157.8037 | 176.177 | 195.962 | 216.904 | 238.5239 | 260.0071 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 226.7828 | 258.4266 | 294.1641 | 334.5393 | 380.17 | 431.7573 | 490.0975 | 556.0949 | 630.7763 | 715.3084 | 811.0164 | 919.4062 | 1042.1887 | 1181.3084 | 1338.9753 | 1517.7015 | 1720.3427 | 1944.0501 | 2192.6452 | 2471.7953 | 2784.4959 | 3133.6699 | 3521.9542 | 3951.3698 | 4422.8222 | 4935.357 | 5485.0576 | 6063.4312 | 5829.293 | 5355.0913
| TRUE | 1309 | 22001434 | DDL | Blank | 22 | CB TR NO.1 | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 12.7412 | 0.085397 | 0 | 0.085397 | 469.682 | 0 | 469.682 | 242.4085 | 34.1672 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 746.2577 | 45.1611 | 701.0966 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.7321 | 289.3759 | 325.1134 | 365.4886 | 411.1193 | 462.7066 | 521.0468 | 587.0442 | 661.7256 | 746.2577 | 841.9657 | 950.3555 | 1073.138 | 1212.2577 | 1369.9246 | 1548.6508 | 1751.292 | 1981.0945 | 2241.7497 | 2537.4547 | 2872.9824 | 3253.7609 | 3685.9636 | 4176.6123 | 4733.6945 | 5366.2962 | 6084.7541 | 6900.8287 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 162.2122 | 182.1283 | 204.6209 | 230.0323 | 258.7515 | 291.2197 | 327.938 | 369.4757 | 416.4789 | 469.682 | 529.919 | 598.1377 | 675.4149 | 762.9745 | 862.2074 | 974.6946 | 1102.2335 | 1246.8674 | 1410.9193 | 1597.031 | 1808.2065 | 2047.862 | 2319.8831 | 2628.6891 | 2979.3072 | 3377.456 | 3829.6413 | 4343.2648 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.0004 | 167.9165 | 190.409 | 215.8205 | 244.5397 | 277.0079 | 313.7262 | 355.2638 | 402.2671 | 455.4701 | 515.7072 | 583.9258 | 661.2031 | 748.7626 | 847.9956 | 960.4828 | 1088.0217 | 1229.8567 | 1388.3707 | 1566.8804 | 1767.5738 | 1992.7166 | 2244.5705 | 2525.2584 | 2836.5556 | 3179.57 | 3554.2625 | 3958.7345 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.0004 | 167.9165 | 190.409 | 215.8205 | 244.5397 | 277.0079 | 313.7262 | 355.2638 | 402.2671 | 455.4701 | 515.7072 | 583.9258 | 661.2031 | 748.7626 | 847.9956 | 960.4828 | 1088.0217 | 1229.8567 | 1388.3707 | 1566.8804 | 1767.5738 | 1992.7166 | 2244.5705 | 2525.2584 | 2836.5556 | 3179.57 | 3554.2625 | 3958.7345 | 3868.4608 | 3650.7088 |  | 83.7197 | 93.9986 | 105.6073 | 118.7225 | 133.5448 | 150.302 | 169.2528 | 190.6908 | 214.9498 | 242.4085 | 273.4975 | 308.706 | 348.5897 | 393.7803 | 444.9956 | 503.0516 | 568.876 | 643.5232 | 728.1924 | 824.2469 | 933.2371 | 1056.9262 | 1197.3195 | 1356.698 | 1537.6562 | 1743.1456 | 1976.5238 | 2241.6111 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.0499 | 79.3288 | 90.9375 | 104.0527 | 118.875 | 135.6322 | 154.583 | 176.021 | 200.28 | 227.7387 | 258.8278 | 294.0362 | 333.9199 | 379.1105 | 430.3258 | 488.3818 | 554.2062 | 625.9644 | 704.9171 | 793.1247 | 891.295 | 1000.0038 | 1119.58 | 1249.9344 | 1390.3046 | 1538.8829 | 1692.2712 | 1844.6897 | 1718.5977 | 1493.8289 |  | 11.8002 | 13.249 | 14.8852 | 16.7338 | 18.823 | 21.1849 | 23.856 | 26.8777 | 30.2969 | 34.1672 | 38.5492 | 43.5118 | 49.1334 | 55.5029 | 62.7217 | 70.9046 | 80.1825 | 90.7039 | 102.638 | 116.1767 | 131.5388 | 148.9727 | 168.761 | 191.2252 | 216.7311 | 245.6946 | 278.589 | 315.9528 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7325 | 11.1813 | 12.8175 | 14.6661 | 16.7553 | 19.1172 | 21.7883 | 24.81 | 28.2293 | 32.0995 | 36.4815 | 41.4441 | 47.0657 | 53.4352 | 60.654 | 68.8369 | 78.1148 | 88.229 | 99.3573 | 111.7901 | 125.6271 | 140.9495 | 157.8037 | 176.177 | 195.962 | 216.904 | 238.5239 | 260.0071 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 226.7828 | 258.4266 | 294.1641 | 334.5393 | 380.17 | 431.7573 | 490.0975 | 556.0949 | 630.7763 | 715.3084 | 811.0164 | 919.4062 | 1042.1887 | 1181.3084 | 1338.9753 | 1517.7015 | 1720.3427 | 1944.0501 | 2192.6452 | 2471.7953 | 2784.4959 | 3133.6699 | 3521.9542 | 3951.3698 | 4422.8222 | 4935.357 | 5485.0576 | 6063.4312 | 5829.293 | 5355.0913
| TRUE | 1310 | 22001437 | DDL | Blank | 22 | CB TR NO.1 | CB FAIL | Y | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 12.7412 | 0.085397 | 0 | 0.085397 | 469.682 | 0 | 469.682 | 242.4085 | 34.1672 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 746.2577 | 45.1611 | 701.0966 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.7321 | 289.3759 | 325.1134 | 365.4886 | 411.1193 | 462.7066 | 521.0468 | 587.0442 | 661.7256 | 746.2577 | 841.9657 | 950.3555 | 1073.138 | 1212.2577 | 1369.9246 | 1548.6508 | 1751.292 | 1981.0945 | 2241.7497 | 2537.4547 | 2872.9824 | 3253.7609 | 3685.9636 | 4176.6123 | 4733.6945 | 5366.2962 | 6084.7541 | 6900.8287 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 162.2122 | 182.1283 | 204.6209 | 230.0323 | 258.7515 | 291.2197 | 327.938 | 369.4757 | 416.4789 | 469.682 | 529.919 | 598.1377 | 675.4149 | 762.9745 | 862.2074 | 974.6946 | 1102.2335 | 1246.8674 | 1410.9193 | 1597.031 | 1808.2065 | 2047.862 | 2319.8831 | 2628.6891 | 2979.3072 | 3377.456 | 3829.6413 | 4343.2648 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.0004 | 167.9165 | 190.409 | 215.8205 | 244.5397 | 277.0079 | 313.7262 | 355.2638 | 402.2671 | 455.4701 | 515.7072 | 583.9258 | 661.2031 | 748.7626 | 847.9956 | 960.4828 | 1088.0217 | 1229.8567 | 1388.3707 | 1566.8804 | 1767.5738 | 1992.7166 | 2244.5705 | 2525.2584 | 2836.5556 | 3179.57 | 3554.2625 | 3958.7345 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.0004 | 167.9165 | 190.409 | 215.8205 | 244.5397 | 277.0079 | 313.7262 | 355.2638 | 402.2671 | 455.4701 | 515.7072 | 583.9258 | 661.2031 | 748.7626 | 847.9956 | 960.4828 | 1088.0217 | 1229.8567 | 1388.3707 | 1566.8804 | 1767.5738 | 1992.7166 | 2244.5705 | 2525.2584 | 2836.5556 | 3179.57 | 3554.2625 | 3958.7345 | 3868.4608 | 3650.7088 |  | 83.7197 | 93.9986 | 105.6073 | 118.7225 | 133.5448 | 150.302 | 169.2528 | 190.6908 | 214.9498 | 242.4085 | 273.4975 | 308.706 | 348.5897 | 393.7803 | 444.9956 | 503.0516 | 568.876 | 643.5232 | 728.1924 | 824.2469 | 933.2371 | 1056.9262 | 1197.3195 | 1356.698 | 1537.6562 | 1743.1456 | 1976.5238 | 2241.6111 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.0499 | 79.3288 | 90.9375 | 104.0527 | 118.875 | 135.6322 | 154.583 | 176.021 | 200.28 | 227.7387 | 258.8278 | 294.0362 | 333.9199 | 379.1105 | 430.3258 | 488.3818 | 554.2062 | 625.9644 | 704.9171 | 793.1247 | 891.295 | 1000.0038 | 1119.58 | 1249.9344 | 1390.3046 | 1538.8829 | 1692.2712 | 1844.6897 | 1718.5977 | 1493.8289 |  | 11.8002 | 13.249 | 14.8852 | 16.7338 | 18.823 | 21.1849 | 23.856 | 26.8777 | 30.2969 | 34.1672 | 38.5492 | 43.5118 | 49.1334 | 55.5029 | 62.7217 | 70.9046 | 80.1825 | 90.7039 | 102.638 | 116.1767 | 131.5388 | 148.9727 | 168.761 | 191.2252 | 216.7311 | 245.6946 | 278.589 | 315.9528 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7325 | 11.1813 | 12.8175 | 14.6661 | 16.7553 | 19.1172 | 21.7883 | 24.81 | 28.2293 | 32.0995 | 36.4815 | 41.4441 | 47.0657 | 53.4352 | 60.654 | 68.8369 | 78.1148 | 88.229 | 99.3573 | 111.7901 | 125.6271 | 140.9495 | 157.8037 | 176.177 | 195.962 | 216.904 | 238.5239 | 260.0071 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 226.7828 | 258.4266 | 294.1641 | 334.5393 | 380.17 | 431.7573 | 490.0975 | 556.0949 | 630.7763 | 715.3084 | 811.0164 | 919.4062 | 1042.1887 | 1181.3084 | 1338.9753 | 1517.7015 | 1720.3427 | 1944.0501 | 2192.6452 | 2471.7953 | 2784.4959 | 3133.6699 | 3521.9542 | 3951.3698 | 4422.8222 | 4935.357 | 5485.0576 | 6063.4312 | 5829.293 | 5355.0913
| TRUE | 1311 | 22001438 | DDL | Blank | 22 | CB TR NO.2 | CB FAIL | Y | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 12.7412 | 0.085397 | 0 | 0.085397 | 469.682 | 0 | 469.682 | 242.4085 | 34.1672 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 746.2577 | 45.1611 | 701.0966 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.7321 | 289.3759 | 325.1134 | 365.4886 | 411.1193 | 462.7066 | 521.0468 | 587.0442 | 661.7256 | 746.2577 | 841.9657 | 950.3555 | 1073.138 | 1212.2577 | 1369.9246 | 1548.6508 | 1751.292 | 1981.0945 | 2241.7497 | 2537.4547 | 2872.9824 | 3253.7609 | 3685.9636 | 4176.6123 | 4733.6945 | 5366.2962 | 6084.7541 | 6900.8287 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 162.2122 | 182.1283 | 204.6209 | 230.0323 | 258.7515 | 291.2197 | 327.938 | 369.4757 | 416.4789 | 469.682 | 529.919 | 598.1377 | 675.4149 | 762.9745 | 862.2074 | 974.6946 | 1102.2335 | 1246.8674 | 1410.9193 | 1597.031 | 1808.2065 | 2047.862 | 2319.8831 | 2628.6891 | 2979.3072 | 3377.456 | 3829.6413 | 4343.2648 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.0004 | 167.9165 | 190.409 | 215.8205 | 244.5397 | 277.0079 | 313.7262 | 355.2638 | 402.2671 | 455.4701 | 515.7072 | 583.9258 | 661.2031 | 748.7626 | 847.9956 | 960.4828 | 1088.0217 | 1229.8567 | 1388.3707 | 1566.8804 | 1767.5738 | 1992.7166 | 2244.5705 | 2525.2584 | 2836.5556 | 3179.57 | 3554.2625 | 3958.7345 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.0004 | 167.9165 | 190.409 | 215.8205 | 244.5397 | 277.0079 | 313.7262 | 355.2638 | 402.2671 | 455.4701 | 515.7072 | 583.9258 | 661.2031 | 748.7626 | 847.9956 | 960.4828 | 1088.0217 | 1229.8567 | 1388.3707 | 1566.8804 | 1767.5738 | 1992.7166 | 2244.5705 | 2525.2584 | 2836.5556 | 3179.57 | 3554.2625 | 3958.7345 | 3868.4608 | 3650.7088 |  | 83.7197 | 93.9986 | 105.6073 | 118.7225 | 133.5448 | 150.302 | 169.2528 | 190.6908 | 214.9498 | 242.4085 | 273.4975 | 308.706 | 348.5897 | 393.7803 | 444.9956 | 503.0516 | 568.876 | 643.5232 | 728.1924 | 824.2469 | 933.2371 | 1056.9262 | 1197.3195 | 1356.698 | 1537.6562 | 1743.1456 | 1976.5238 | 2241.6111 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.0499 | 79.3288 | 90.9375 | 104.0527 | 118.875 | 135.6322 | 154.583 | 176.021 | 200.28 | 227.7387 | 258.8278 | 294.0362 | 333.9199 | 379.1105 | 430.3258 | 488.3818 | 554.2062 | 625.9644 | 704.9171 | 793.1247 | 891.295 | 1000.0038 | 1119.58 | 1249.9344 | 1390.3046 | 1538.8829 | 1692.2712 | 1844.6897 | 1718.5977 | 1493.8289 |  | 11.8002 | 13.249 | 14.8852 | 16.7338 | 18.823 | 21.1849 | 23.856 | 26.8777 | 30.2969 | 34.1672 | 38.5492 | 43.5118 | 49.1334 | 55.5029 | 62.7217 | 70.9046 | 80.1825 | 90.7039 | 102.638 | 116.1767 | 131.5388 | 148.9727 | 168.761 | 191.2252 | 216.7311 | 245.6946 | 278.589 | 315.9528 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7325 | 11.1813 | 12.8175 | 14.6661 | 16.7553 | 19.1172 | 21.7883 | 24.81 | 28.2293 | 32.0995 | 36.4815 | 41.4441 | 47.0657 | 53.4352 | 60.654 | 68.8369 | 78.1148 | 88.229 | 99.3573 | 111.7901 | 125.6271 | 140.9495 | 157.8037 | 176.177 | 195.962 | 216.904 | 238.5239 | 260.0071 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 226.7828 | 258.4266 | 294.1641 | 334.5393 | 380.17 | 431.7573 | 490.0975 | 556.0949 | 630.7763 | 715.3084 | 811.0164 | 919.4062 | 1042.1887 | 1181.3084 | 1338.9753 | 1517.7015 | 1720.3427 | 1944.0501 | 2192.6452 | 2471.7953 | 2784.4959 | 3133.6699 | 3521.9542 | 3951.3698 | 4422.8222 | 4935.357 | 5485.0576 | 6063.4312 | 5829.293 | 5355.0913
| TRUE | 1312 | 22001435 | DDL | Blank | 22 | CB TR NO.2 | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 12.7412 | 0.085397 | 0 | 0.085397 | 469.682 | 0 | 469.682 | 242.4085 | 34.1672 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 746.2577 | 45.1611 | 701.0966 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.7321 | 289.3759 | 325.1134 | 365.4886 | 411.1193 | 462.7066 | 521.0468 | 587.0442 | 661.7256 | 746.2577 | 841.9657 | 950.3555 | 1073.138 | 1212.2577 | 1369.9246 | 1548.6508 | 1751.292 | 1981.0945 | 2241.7497 | 2537.4547 | 2872.9824 | 3253.7609 | 3685.9636 | 4176.6123 | 4733.6945 | 5366.2962 | 6084.7541 | 6900.8287 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 162.2122 | 182.1283 | 204.6209 | 230.0323 | 258.7515 | 291.2197 | 327.938 | 369.4757 | 416.4789 | 469.682 | 529.919 | 598.1377 | 675.4149 | 762.9745 | 862.2074 | 974.6946 | 1102.2335 | 1246.8674 | 1410.9193 | 1597.031 | 1808.2065 | 2047.862 | 2319.8831 | 2628.6891 | 2979.3072 | 3377.456 | 3829.6413 | 4343.2648 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.0004 | 167.9165 | 190.409 | 215.8205 | 244.5397 | 277.0079 | 313.7262 | 355.2638 | 402.2671 | 455.4701 | 515.7072 | 583.9258 | 661.2031 | 748.7626 | 847.9956 | 960.4828 | 1088.0217 | 1229.8567 | 1388.3707 | 1566.8804 | 1767.5738 | 1992.7166 | 2244.5705 | 2525.2584 | 2836.5556 | 3179.57 | 3554.2625 | 3958.7345 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.0004 | 167.9165 | 190.409 | 215.8205 | 244.5397 | 277.0079 | 313.7262 | 355.2638 | 402.2671 | 455.4701 | 515.7072 | 583.9258 | 661.2031 | 748.7626 | 847.9956 | 960.4828 | 1088.0217 | 1229.8567 | 1388.3707 | 1566.8804 | 1767.5738 | 1992.7166 | 2244.5705 | 2525.2584 | 2836.5556 | 3179.57 | 3554.2625 | 3958.7345 | 3868.4608 | 3650.7088 |  | 83.7197 | 93.9986 | 105.6073 | 118.7225 | 133.5448 | 150.302 | 169.2528 | 190.6908 | 214.9498 | 242.4085 | 273.4975 | 308.706 | 348.5897 | 393.7803 | 444.9956 | 503.0516 | 568.876 | 643.5232 | 728.1924 | 824.2469 | 933.2371 | 1056.9262 | 1197.3195 | 1356.698 | 1537.6562 | 1743.1456 | 1976.5238 | 2241.6111 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.0499 | 79.3288 | 90.9375 | 104.0527 | 118.875 | 135.6322 | 154.583 | 176.021 | 200.28 | 227.7387 | 258.8278 | 294.0362 | 333.9199 | 379.1105 | 430.3258 | 488.3818 | 554.2062 | 625.9644 | 704.9171 | 793.1247 | 891.295 | 1000.0038 | 1119.58 | 1249.9344 | 1390.3046 | 1538.8829 | 1692.2712 | 1844.6897 | 1718.5977 | 1493.8289 |  | 11.8002 | 13.249 | 14.8852 | 16.7338 | 18.823 | 21.1849 | 23.856 | 26.8777 | 30.2969 | 34.1672 | 38.5492 | 43.5118 | 49.1334 | 55.5029 | 62.7217 | 70.9046 | 80.1825 | 90.7039 | 102.638 | 116.1767 | 131.5388 | 148.9727 | 168.761 | 191.2252 | 216.7311 | 245.6946 | 278.589 | 315.9528 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7325 | 11.1813 | 12.8175 | 14.6661 | 16.7553 | 19.1172 | 21.7883 | 24.81 | 28.2293 | 32.0995 | 36.4815 | 41.4441 | 47.0657 | 53.4352 | 60.654 | 68.8369 | 78.1148 | 88.229 | 99.3573 | 111.7901 | 125.6271 | 140.9495 | 157.8037 | 176.177 | 195.962 | 216.904 | 238.5239 | 260.0071 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 226.7828 | 258.4266 | 294.1641 | 334.5393 | 380.17 | 431.7573 | 490.0975 | 556.0949 | 630.7763 | 715.3084 | 811.0164 | 919.4062 | 1042.1887 | 1181.3084 | 1338.9753 | 1517.7015 | 1720.3427 | 1944.0501 | 2192.6452 | 2471.7953 | 2784.4959 | 3133.6699 | 3521.9542 | 3951.3698 | 4422.8222 | 4935.357 | 5485.0576 | 6063.4312 | 5829.293 | 5355.0913
| TRUE | 1313 | 22001448 | DDL | Blank | 22 | ALL FEEDERS | MASTER EARTH FAULT | X | ASEA | GROUP_2650 | GROUP 2650 | GROUP 2000s | Electronic |  | 0.81881 | 2190 |  | 8.25 | 0.026286 | 0.02098 | 0.0053053 | 156.1101 | 5874.4876 | 6030.5977 | 193.7249 | 10.7267 | 32424.3097 |  | 12.7412 | 0.085397 | 0.068161 | 0.017236 | 507.1704 | 19085.0371 | 19592.2075 | 629.3734 | 34.8488 | 105340.1068 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 28.4268 | 1.6231 | 30.0499 | 14.7027 | 2.0677 | 8.9585 |  | 38659.359 | 125596.5366 | 55.7789 | 125540.7577 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0.02354 | 0.026431 | 0.029695 | 0.033383 | 0.03755 | 0.042262 | 0.047591 | 0.053619 | 0.06044 | 0.068161 | 0.076903 | 0.086803 | 0.098017 | 0.11072 | 0.12512 | 0.14145 | 0.15996 | 0.18095 | 0.20475 | 0.23176 | 0.26241 | 0.29719 | 0.33666 | 0.38148 | 0.43236 | 0.49014 | 0.55576 | 0.6303 | 0.63955 | 0.63955 | 43376.7894 | 48702.4989 | 54717.1764 | 61512.4 | 69192.1235 | 77874.3658 | 87693.1334 | 98800.6072 | 111369.6299 | 125596.5366 | 141704.3747 | 159946.5682 | 180611.0863 | 204025.1886 | 230560.8233 | 260640.7723 | 294745.6439 | 333421.8321 | 377290.5755 | 427058.2692 | 483528.2018 | 547613.917 | 620354.4231 | 702931.5084 | 796689.4533 | 903157.4726 | 1024075.2653 | 1161422.106 | 1178473.0552 | 1178473.0552 |  | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 49.7722 | 65.976 | 88.2189 | 118.8891 | 161.3523 | 220.3604 | 302.6324 | 417.683 | 579.0031 | 805.7427 | 1125.1139 | 1575.8191 | 2212.949 |  | 175.1595 | 196.6652 | 220.953 | 248.3928 | 279.4042 | 314.4639 | 354.113 | 398.966 | 449.7209 | 507.1704 | 572.2154 | 645.879 | 729.3243 | 823.8726 | 931.0259 | 1052.4915 | 1190.2102 | 1346.3882 | 1523.5342 | 1724.5008 | 1952.5316 | 2211.3156 | 2505.0485 | 2838.5024 | 3217.1057 | 3647.0334 | 4135.3106 | 4689.9299 | 4758.7832 | 4758.7832 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 160.9461 | 182.4518 | 206.7396 | 234.1793 | 265.1908 | 300.2505 | 339.8996 | 384.7526 | 435.5074 | 492.957 | 558.002 | 631.6656 | 715.1109 | 809.6592 | 916.8125 | 1038.2781 | 1175.9968 | 1329.3756 | 1500.9831 | 1694.3468 | 1911.8943 | 2156.164 | 2429.7275 | 2735.0601 | 3074.3381 | 3449.1252 | 3859.9009 | 4305.3564 | 4220.1549 | 4002.3785 |  | 6591.3253 | 7400.5942 | 8314.5552 | 9347.1243 | 10514.0976 | 11833.4088 | 13325.4208 | 15013.2584 | 16923.1857 | 19085.0371 | 21532.7056 | 24304.7003 | 27444.7797 | 31002.6725 | 35034.8981 | 39605.7005 | 44788.1104 | 50665.1553 | 57331.2356 | 64893.6916 | 73474.5871 | 83212.7398 | 94266.0323 | 106814.0434 | 121061.0434 | 137239.4043 | 155613.4823 | 176484.0383 | 179075.0174 | 179075.0174 |  | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.9427 | 2.5752 | 3.4434 | 4.6405 | 6.2979 | 8.6011 | 11.8123 | 16.303 | 22.5996 | 31.4497 | 43.9154 | 61.5073 | 86.3757 |  | 6589.7023 | 7398.9711 | 8312.9322 | 9345.5012 | 10512.4745 | 11831.7857 | 13323.7978 | 15011.6353 | 16921.5627 | 19083.414 | 21531.0825 | 24303.0773 | 27443.1567 | 31001.0494 | 35033.2751 | 39604.0774 | 44786.4873 | 50663.2126 | 57328.6604 | 64890.2482 | 73469.9466 | 83206.4419 | 94257.4312 | 106802.2311 | 121044.7404 | 137216.8047 | 155582.0326 | 176440.1229 | 179013.5101 | 178988.6417 |  | 6750.6483 | 7581.4229 | 8519.6718 | 9579.6806 | 10777.6653 | 12132.0362 | 13663.6973 | 15396.3879 | 17357.0701 | 19576.371 | 22089.0845 | 24934.7429 | 28158.2675 | 31810.7086 | 35950.0876 | 40642.3555 | 45962.4841 | 51992.5882 | 58829.6435 | 66584.595 | 75381.8409 | 85362.6059 | 96687.1587 | 109537.2912 | 124119.0785 | 140665.9299 | 159441.9335 | 180745.4793 | 183233.6649 | 182991.0201 |  | 217.3643 | 244.0518 | 274.1918 | 308.2431 | 346.7268 | 390.2342 | 439.4367 | 495.0971 | 558.0814 | 629.3734 | 710.091 | 801.504 | 905.0554 | 1022.3852 | 1155.3572 | 1306.09 | 1476.992 | 1670.8012 | 1890.6307 | 2140.0203 | 2422.9952 | 2744.1334 | 3108.6414 | 3522.4413 | 3992.2692 | 4525.7882 | 5131.7162 | 5819.9712 | 5905.4148 | 5905.4148 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 202.6616 | 229.3491 | 259.4891 | 293.5404 | 332.0241 | 375.5315 | 424.734 | 480.3944 | 543.3787 | 614.6707 | 695.3883 | 786.8013 | 890.3527 | 1007.6825 | 1140.6545 | 1291.3873 | 1462.2893 | 1653.203 | 1867.3032 | 2108.8283 | 2380.9591 | 2687.0833 | 3030.7276 | 3415.4381 | 3844.587 | 4321.0674 | 4846.8259 | 5422.1594 | 5348.2449 | 5122.9719 |  | 12.0356 | 13.5133 | 15.1822 | 17.0676 | 19.1985 | 21.6075 | 24.3319 | 27.4139 | 30.9013 | 34.8488 | 39.3182 | 44.3798 | 50.1135 | 56.6102 | 63.9729 | 72.3191 | 81.7821 | 92.5134 | 104.6855 | 118.4944 | 134.1629 | 151.9445 | 172.1276 | 195.04 | 221.0547 | 250.596 | 284.1466 | 322.2558 | 326.9868 | 326.9868 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 9.9679 | 11.4456 | 13.1144 | 14.9999 | 17.1307 | 19.5398 | 22.2642 | 25.3461 | 28.8336 | 32.7811 | 37.2505 | 42.3121 | 48.0458 | 54.5424 | 61.9052 | 70.2513 | 79.7143 | 90.0384 | 101.4048 | 114.1076 | 128.251 | 143.9212 | 161.17 | 179.9913 | 200.285 | 221.8046 | 244.0804 | 266.3085 | 248.6279 | 216.9461 |  | 36380.9047 | 40847.6744 | 45892.2942 | 51591.5722 | 58032.6964 | 65314.6514 | 73549.831 | 82865.8719 | 93407.7405 | 105340.1068 | 118850.0445 | 134150.105 | 151481.8134 | 171119.6482 | 193375.5692 | 218604.1712 | 247208.5493 | 279646.974 | 316440.4895 | 358181.5622 | 405543.925 | 459293.7836 | 520302.5732 | 589561.4813 | 668197.9804 | 757494.6506 | 858910.6096 | 974105.9108 | 988406.853 | 988406.853 |  | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 10.7228 | 14.2137 | 19.0056 | 25.6131 | 34.7613 | 47.4738 | 65.1983 | 89.9845 | 124.7389 | 173.587 | 242.3915 | 339.4902 | 476.7518 |  | 36371.9461 | 40838.7159 | 45883.3356 | 51582.6137 | 58023.7379 | 65305.6929 | 73540.8725 | 82856.9133 | 93398.782 | 105331.1482 | 118841.086 | 134141.1465 | 151472.8549 | 171110.6897 | 193366.6106 | 218595.2127 | 247199.5907 | 279636.2512 | 316426.2758 | 358162.5565 | 405518.3118 | 459259.0222 | 520255.0993 | 589496.283 | 668107.9959 | 757369.9118 | 858737.0226 | 973863.5193 | 988067.3628 | 987930.1013 |  | 43335.2239 | 48660.9335 | 54675.6109 | 61470.8346 | 69150.5581 | 77832.8004 | 87651.568 | 98759.0417 | 111328.0644 | 125554.9711 | 141662.8093 | 159905.0027 | 180569.5209 | 203983.6231 | 230519.2578 | 260599.2068 | 294704.0785 | 333372.0808 | 377224.6273 | 426970.0875 | 483409.3629 | 547452.6327 | 620134.1556 | 702629.0036 | 796271.9465 | 902578.7137 | 1023269.8624 | 1160297.4666 | 1176897.9006 | 1176261.0394
| TRUE | 1314 | 22001447 | DDL | Blank | 22 | ALL FEEDERS | BACKUP EARTH FAULT | X | ASEA | GROUP_2651 | GROUP 2651 | GROUP 2000s | Electronic |  | 0.81881 | 2190 |  | 8.25 | 0.026286 | 0.02098 | 0.0053053 | 156.1101 | 5874.4876 | 6030.5977 | 193.7249 | 10.7267 | 32424.3097 |  | 12.7412 | 0.085397 | 0.068161 | 0.017236 | 507.1704 | 19085.0371 | 19592.2075 | 629.3734 | 34.8488 | 105340.1068 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 28.4268 | 1.6231 | 30.0499 | 14.7027 | 2.0677 | 8.9585 |  | 38659.359 | 125596.5366 | 55.7789 | 125540.7577 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0.02354 | 0.026431 | 0.029695 | 0.033383 | 0.03755 | 0.042262 | 0.047591 | 0.053619 | 0.06044 | 0.068161 | 0.076903 | 0.086803 | 0.098017 | 0.11072 | 0.12512 | 0.14145 | 0.15996 | 0.18095 | 0.20475 | 0.23176 | 0.26241 | 0.29719 | 0.33666 | 0.38148 | 0.43236 | 0.49014 | 0.55576 | 0.6303 | 0.63955 | 0.63955 | 43376.7894 | 48702.4989 | 54717.1764 | 61512.4 | 69192.1235 | 77874.3658 | 87693.1334 | 98800.6072 | 111369.6299 | 125596.5366 | 141704.3747 | 159946.5682 | 180611.0863 | 204025.1886 | 230560.8233 | 260640.7723 | 294745.6439 | 333421.8321 | 377290.5755 | 427058.2692 | 483528.2018 | 547613.917 | 620354.4231 | 702931.5084 | 796689.4533 | 903157.4726 | 1024075.2653 | 1161422.106 | 1178473.0552 | 1178473.0552 |  | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 41.583 | 49.7722 | 65.976 | 88.2189 | 118.8891 | 161.3523 | 220.3604 | 302.6324 | 417.683 | 579.0031 | 805.7427 | 1125.1139 | 1575.8191 | 2212.949 |  | 175.1595 | 196.6652 | 220.953 | 248.3928 | 279.4042 | 314.4639 | 354.113 | 398.966 | 449.7209 | 507.1704 | 572.2154 | 645.879 | 729.3243 | 823.8726 | 931.0259 | 1052.4915 | 1190.2102 | 1346.3882 | 1523.5342 | 1724.5008 | 1952.5316 | 2211.3156 | 2505.0485 | 2838.5024 | 3217.1057 | 3647.0334 | 4135.3106 | 4689.9299 | 4758.7832 | 4758.7832 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 160.9461 | 182.4518 | 206.7396 | 234.1793 | 265.1908 | 300.2505 | 339.8996 | 384.7526 | 435.5074 | 492.957 | 558.002 | 631.6656 | 715.1109 | 809.6592 | 916.8125 | 1038.2781 | 1175.9968 | 1329.3756 | 1500.9831 | 1694.3468 | 1911.8943 | 2156.164 | 2429.7275 | 2735.0601 | 3074.3381 | 3449.1252 | 3859.9009 | 4305.3564 | 4220.1549 | 4002.3785 |  | 6591.3253 | 7400.5942 | 8314.5552 | 9347.1243 | 10514.0976 | 11833.4088 | 13325.4208 | 15013.2584 | 16923.1857 | 19085.0371 | 21532.7056 | 24304.7003 | 27444.7797 | 31002.6725 | 35034.8981 | 39605.7005 | 44788.1104 | 50665.1553 | 57331.2356 | 64893.6916 | 73474.5871 | 83212.7398 | 94266.0323 | 106814.0434 | 121061.0434 | 137239.4043 | 155613.4823 | 176484.0383 | 179075.0174 | 179075.0174 |  | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.9427 | 2.5752 | 3.4434 | 4.6405 | 6.2979 | 8.6011 | 11.8123 | 16.303 | 22.5996 | 31.4497 | 43.9154 | 61.5073 | 86.3757 |  | 6589.7023 | 7398.9711 | 8312.9322 | 9345.5012 | 10512.4745 | 11831.7857 | 13323.7978 | 15011.6353 | 16921.5627 | 19083.414 | 21531.0825 | 24303.0773 | 27443.1567 | 31001.0494 | 35033.2751 | 39604.0774 | 44786.4873 | 50663.2126 | 57328.6604 | 64890.2482 | 73469.9466 | 83206.4419 | 94257.4312 | 106802.2311 | 121044.7404 | 137216.8047 | 155582.0326 | 176440.1229 | 179013.5101 | 178988.6417 |  | 6750.6483 | 7581.4229 | 8519.6718 | 9579.6806 | 10777.6653 | 12132.0362 | 13663.6973 | 15396.3879 | 17357.0701 | 19576.371 | 22089.0845 | 24934.7429 | 28158.2675 | 31810.7086 | 35950.0876 | 40642.3555 | 45962.4841 | 51992.5882 | 58829.6435 | 66584.595 | 75381.8409 | 85362.6059 | 96687.1587 | 109537.2912 | 124119.0785 | 140665.9299 | 159441.9335 | 180745.4793 | 183233.6649 | 182991.0201 |  | 217.3643 | 244.0518 | 274.1918 | 308.2431 | 346.7268 | 390.2342 | 439.4367 | 495.0971 | 558.0814 | 629.3734 | 710.091 | 801.504 | 905.0554 | 1022.3852 | 1155.3572 | 1306.09 | 1476.992 | 1670.8012 | 1890.6307 | 2140.0203 | 2422.9952 | 2744.1334 | 3108.6414 | 3522.4413 | 3992.2692 | 4525.7882 | 5131.7162 | 5819.9712 | 5905.4148 | 5905.4148 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 202.6616 | 229.3491 | 259.4891 | 293.5404 | 332.0241 | 375.5315 | 424.734 | 480.3944 | 543.3787 | 614.6707 | 695.3883 | 786.8013 | 890.3527 | 1007.6825 | 1140.6545 | 1291.3873 | 1462.2893 | 1653.203 | 1867.3032 | 2108.8283 | 2380.9591 | 2687.0833 | 3030.7276 | 3415.4381 | 3844.587 | 4321.0674 | 4846.8259 | 5422.1594 | 5348.2449 | 5122.9719 |  | 12.0356 | 13.5133 | 15.1822 | 17.0676 | 19.1985 | 21.6075 | 24.3319 | 27.4139 | 30.9013 | 34.8488 | 39.3182 | 44.3798 | 50.1135 | 56.6102 | 63.9729 | 72.3191 | 81.7821 | 92.5134 | 104.6855 | 118.4944 | 134.1629 | 151.9445 | 172.1276 | 195.04 | 221.0547 | 250.596 | 284.1466 | 322.2558 | 326.9868 | 326.9868 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 9.9679 | 11.4456 | 13.1144 | 14.9999 | 17.1307 | 19.5398 | 22.2642 | 25.3461 | 28.8336 | 32.7811 | 37.2505 | 42.3121 | 48.0458 | 54.5424 | 61.9052 | 70.2513 | 79.7143 | 90.0384 | 101.4048 | 114.1076 | 128.251 | 143.9212 | 161.17 | 179.9913 | 200.285 | 221.8046 | 244.0804 | 266.3085 | 248.6279 | 216.9461 |  | 36380.9047 | 40847.6744 | 45892.2942 | 51591.5722 | 58032.6964 | 65314.6514 | 73549.831 | 82865.8719 | 93407.7405 | 105340.1068 | 118850.0445 | 134150.105 | 151481.8134 | 171119.6482 | 193375.5692 | 218604.1712 | 247208.5493 | 279646.974 | 316440.4895 | 358181.5622 | 405543.925 | 459293.7836 | 520302.5732 | 589561.4813 | 668197.9804 | 757494.6506 | 858910.6096 | 974105.9108 | 988406.853 | 988406.853 |  | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 8.9585 | 10.7228 | 14.2137 | 19.0056 | 25.6131 | 34.7613 | 47.4738 | 65.1983 | 89.9845 | 124.7389 | 173.587 | 242.3915 | 339.4902 | 476.7518 |  | 36371.9461 | 40838.7159 | 45883.3356 | 51582.6137 | 58023.7379 | 65305.6929 | 73540.8725 | 82856.9133 | 93398.782 | 105331.1482 | 118841.086 | 134141.1465 | 151472.8549 | 171110.6897 | 193366.6106 | 218595.2127 | 247199.5907 | 279636.2512 | 316426.2758 | 358162.5565 | 405518.3118 | 459259.0222 | 520255.0993 | 589496.283 | 668107.9959 | 757369.9118 | 858737.0226 | 973863.5193 | 988067.3628 | 987930.1013 |  | 43335.2239 | 48660.9335 | 54675.6109 | 61470.8346 | 69150.5581 | 77832.8004 | 87651.568 | 98759.0417 | 111328.0644 | 125554.9711 | 141662.8093 | 159905.0027 | 180569.5209 | 203983.6231 | 230519.2578 | 260599.2068 | 294704.0785 | 333372.0808 | 377224.6273 | 426970.0875 | 483409.3629 | 547452.6327 | 620134.1556 | 702629.0036 | 796271.9465 | 902578.7137 | 1023269.8624 | 1160297.4666 | 1176897.9006 | 1176261.0394
| TRUE | 1315 | 22008403 | DDL | DDL011 | 22 | DDL11 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 16.5779 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 165.0028 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 6.696 |  | 93.9665 | 935.2648 | 37.9542 | 897.3106 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 116.7199 | 145.4979 | 181.9647 | 228.2558 | 287.1136 | 362.0623 | 457.634 | 579.6597 | 735.6467 | 935.2648 | 1190.9751 | 1518.8428 | 1939.588 | 2479.9441 | 3174.4146 | 4067.5454 | 5216.8643 | 6696.6837 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 |  | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 45.4288 | 60.2185 | 80.5203 | 108.514 | 147.2716 | 201.1302 | 276.2226 | 381.2331 | 528.4753 | 735.4281 | 1026.9287 | 1438.3023 | 2019.8319 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 20.5922 | 25.6693 | 32.1029 | 40.2697 | 50.6536 | 63.8764 | 80.7374 | 102.2657 | 129.7855 | 165.0028 | 210.1161 | 267.9598 | 342.1891 | 437.5207 | 560.0417 | 717.6111 | 920.3781 | 1181.4532 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 |  | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 8.0147 | 10.624 | 14.2057 | 19.1444 | 25.9822 | 35.4841 | 48.7322 | 67.2585 | 93.2355 | 129.7469 | 181.1745 | 253.7505 | 356.3461 |  | 13.8961 | 18.9733 | 25.4069 | 33.5737 | 43.9576 | 57.1803 | 74.0414 | 95.5697 | 123.0894 | 158.3068 | 203.4201 | 261.2637 | 335.4931 | 430.8247 | 553.3457 | 710.9151 | 913.6821 | 1173.4385 | 1209.5996 | 1206.0179 | 1201.0791 | 1194.2413 | 1184.7394 | 1171.4914 | 1152.965 | 1126.988 | 1090.4767 | 1039.0491 | 966.473 | 863.8775 |  | 78.7657 | 107.5437 | 144.0106 | 190.3016 | 249.1594 | 324.1082 | 419.6798 | 541.7055 | 697.6925 | 897.3106 | 1153.0209 | 1480.8886 | 1901.6338 | 2441.9899 | 3136.4604 | 4029.5912 | 5178.9101 | 6651.255 | 6856.2222 | 6835.9204 | 6807.9267 | 6769.1691 | 6715.3105 | 6640.2182 | 6535.2076 | 6387.9655 | 6181.0126 | 5889.512 | 5478.1384 | 4896.6089
| TRUE | 1316 | 22008404 | DDL | DDL012 | 22 | DDL12 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 16.5779 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 165.0028 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 6.696 |  | 93.9665 | 935.2648 | 37.9542 | 897.3106 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 116.7199 | 145.4979 | 181.9647 | 228.2558 | 287.1136 | 362.0623 | 457.634 | 579.6597 | 735.6467 | 935.2648 | 1190.9751 | 1518.8428 | 1939.588 | 2479.9441 | 3174.4146 | 4067.5454 | 5216.8643 | 6696.6837 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 |  | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 45.4288 | 60.2185 | 80.5203 | 108.514 | 147.2716 | 201.1302 | 276.2226 | 381.2331 | 528.4753 | 735.4281 | 1026.9287 | 1438.3023 | 2019.8319 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 20.5922 | 25.6693 | 32.1029 | 40.2697 | 50.6536 | 63.8764 | 80.7374 | 102.2657 | 129.7855 | 165.0028 | 210.1161 | 267.9598 | 342.1891 | 437.5207 | 560.0417 | 717.6111 | 920.3781 | 1181.4532 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 |  | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 8.0147 | 10.624 | 14.2057 | 19.1444 | 25.9822 | 35.4841 | 48.7322 | 67.2585 | 93.2355 | 129.7469 | 181.1745 | 253.7505 | 356.3461 |  | 13.8961 | 18.9733 | 25.4069 | 33.5737 | 43.9576 | 57.1803 | 74.0414 | 95.5697 | 123.0894 | 158.3068 | 203.4201 | 261.2637 | 335.4931 | 430.8247 | 553.3457 | 710.9151 | 913.6821 | 1173.4385 | 1209.5996 | 1206.0179 | 1201.0791 | 1194.2413 | 1184.7394 | 1171.4914 | 1152.965 | 1126.988 | 1090.4767 | 1039.0491 | 966.473 | 863.8775 |  | 78.7657 | 107.5437 | 144.0106 | 190.3016 | 249.1594 | 324.1082 | 419.6798 | 541.7055 | 697.6925 | 897.3106 | 1153.0209 | 1480.8886 | 1901.6338 | 2441.9899 | 3136.4604 | 4029.5912 | 5178.9101 | 6651.255 | 6856.2222 | 6835.9204 | 6807.9267 | 6769.1691 | 6715.3105 | 6640.2182 | 6535.2076 | 6387.9655 | 6181.0126 | 5889.512 | 5478.1384 | 4896.6089
| TRUE | 1317 | 22008405 | DDL | DDL013 | 22 | DDL13 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 16.5779 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 165.0028 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 6.696 |  | 93.9665 | 935.2648 | 37.9542 | 897.3106 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 116.7199 | 145.4979 | 181.9647 | 228.2558 | 287.1136 | 362.0623 | 457.634 | 579.6597 | 735.6467 | 935.2648 | 1190.9751 | 1518.8428 | 1939.588 | 2479.9441 | 3174.4146 | 4067.5454 | 5216.8643 | 6696.6837 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 |  | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 45.4288 | 60.2185 | 80.5203 | 108.514 | 147.2716 | 201.1302 | 276.2226 | 381.2331 | 528.4753 | 735.4281 | 1026.9287 | 1438.3023 | 2019.8319 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 20.5922 | 25.6693 | 32.1029 | 40.2697 | 50.6536 | 63.8764 | 80.7374 | 102.2657 | 129.7855 | 165.0028 | 210.1161 | 267.9598 | 342.1891 | 437.5207 | 560.0417 | 717.6111 | 920.3781 | 1181.4532 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 |  | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 8.0147 | 10.624 | 14.2057 | 19.1444 | 25.9822 | 35.4841 | 48.7322 | 67.2585 | 93.2355 | 129.7469 | 181.1745 | 253.7505 | 356.3461 |  | 13.8961 | 18.9733 | 25.4069 | 33.5737 | 43.9576 | 57.1803 | 74.0414 | 95.5697 | 123.0894 | 158.3068 | 203.4201 | 261.2637 | 335.4931 | 430.8247 | 553.3457 | 710.9151 | 913.6821 | 1173.4385 | 1209.5996 | 1206.0179 | 1201.0791 | 1194.2413 | 1184.7394 | 1171.4914 | 1152.965 | 1126.988 | 1090.4767 | 1039.0491 | 966.473 | 863.8775 |  | 78.7657 | 107.5437 | 144.0106 | 190.3016 | 249.1594 | 324.1082 | 419.6798 | 541.7055 | 697.6925 | 897.3106 | 1153.0209 | 1480.8886 | 1901.6338 | 2441.9899 | 3136.4604 | 4029.5912 | 5178.9101 | 6651.255 | 6856.2222 | 6835.9204 | 6807.9267 | 6769.1691 | 6715.3105 | 6640.2182 | 6535.2076 | 6387.9655 | 6181.0126 | 5889.512 | 5478.1384 | 4896.6089
| TRUE | 1318 | 22008406 | DDL | DDL014 | 22 | DDL14 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 16.5779 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 165.0028 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 6.696 |  | 93.9665 | 935.2648 | 37.9542 | 897.3106 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 116.7199 | 145.4979 | 181.9647 | 228.2558 | 287.1136 | 362.0623 | 457.634 | 579.6597 | 735.6467 | 935.2648 | 1190.9751 | 1518.8428 | 1939.588 | 2479.9441 | 3174.4146 | 4067.5454 | 5216.8643 | 6696.6837 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 | 6916.4407 |  | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 37.9542 | 45.4288 | 60.2185 | 80.5203 | 108.514 | 147.2716 | 201.1302 | 276.2226 | 381.2331 | 528.4753 | 735.4281 | 1026.9287 | 1438.3023 | 2019.8319 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 20.5922 | 25.6693 | 32.1029 | 40.2697 | 50.6536 | 63.8764 | 80.7374 | 102.2657 | 129.7855 | 165.0028 | 210.1161 | 267.9598 | 342.1891 | 437.5207 | 560.0417 | 717.6111 | 920.3781 | 1181.4532 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 | 1220.2235 |  | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 6.696 | 8.0147 | 10.624 | 14.2057 | 19.1444 | 25.9822 | 35.4841 | 48.7322 | 67.2585 | 93.2355 | 129.7469 | 181.1745 | 253.7505 | 356.3461 |  | 13.8961 | 18.9733 | 25.4069 | 33.5737 | 43.9576 | 57.1803 | 74.0414 | 95.5697 | 123.0894 | 158.3068 | 203.4201 | 261.2637 | 335.4931 | 430.8247 | 553.3457 | 710.9151 | 913.6821 | 1173.4385 | 1209.5996 | 1206.0179 | 1201.0791 | 1194.2413 | 1184.7394 | 1171.4914 | 1152.965 | 1126.988 | 1090.4767 | 1039.0491 | 966.473 | 863.8775 |  | 78.7657 | 107.5437 | 144.0106 | 190.3016 | 249.1594 | 324.1082 | 419.6798 | 541.7055 | 697.6925 | 897.3106 | 1153.0209 | 1480.8886 | 1901.6338 | 2441.9899 | 3136.4604 | 4029.5912 | 5178.9101 | 6651.255 | 6856.2222 | 6835.9204 | 6807.9267 | 6769.1691 | 6715.3105 | 6640.2182 | 6535.2076 | 6387.9655 | 6181.0126 | 5889.512 | 5478.1384 | 4896.6089
| TRUE | 1319 | 22010566 | DDL | DDL021 | 22 | DDL21 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 2.5292 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.8715 |  | 8.8804 | 0.037562 | 2.9553e-05 | 0.037533 | 103.305 | 2.0687 | 105.3737 | 106.7933 | 15.029 | 42.6763 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.8715 |  | 37.1297 | 269.8723 | 37.1297 | 232.7426 |  | 0.12559 |  | 2.8677 | 3.2514 | 3.6865 | 4.1799 | 4.7392 | 5.3734 | 6.0925 | 6.9078 | 7.8322 | 8.8804 | 10.0687 | 11.4161 | 12.9438 | 14.676 | 16.64 | 18.8667 | 21.3915 | 24.2541 | 27.4998 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0057115 | 0.0076532 | 0.010356 | 0.014137 | 0.019449 | 0.026946 | 0.037562 | 0.052647 | 0.074144 | 0.10486 | 0.14884 | 0.21196 | 0.3027 | 0.43337 | 0.62179 | 0.89383 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.4936e-06 | 6.0213e-06 | 8.1476e-06 | 1.1122e-05 | 1.5302e-05 | 2.12e-05 | 2.9553e-05 | 4.1421e-05 | 5.8334e-05 | 8.2498e-05 | 0.0001171 | 0.00016676 | 0.00023816 | 0.00034096 | 0.0004892 | 0.00070323 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 37.1297 | 37.1297 | 37.1297 | 41.0347 | 54.9856 | 74.4032 | 101.5659 | 139.7363 | 193.5958 | 269.8723 | 378.2517 | 532.6972 | 753.3633 | 1069.3745 | 1522.8579 | 2174.8034 | 3113.5779 | 4467.3032 | 6421.8555 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 |  | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 44.4419 | 58.9104 | 78.7711 | 106.1567 | 144.0723 | 196.7609 | 270.222 | 372.9513 | 516.9949 | 719.4519 | 1004.6201 | 1407.0571 | 1975.9537 |  | 14.2129 | 14.2129 | 14.2129 | 15.7078 | 21.0481 | 28.4809 | 38.8786 | 53.49 | 74.1069 | 103.305 | 144.7918 | 203.9122 | 288.3815 | 409.3481 | 582.9379 | 832.4975 | 1191.8529 | 1710.0482 | 2458.2353 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 1.4948 | 6.8351 | 14.268 | 24.6657 | 39.277 | 59.894 | 89.092 | 130.5788 | 189.6993 | 274.1686 | 395.1351 | 568.725 | 818.2845 | 1177.64 | 1693.0362 | 2435.6849 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.31455 | 0.42149 | 0.57033 | 0.77855 | 1.0711 | 1.484 | 2.0687 | 2.8995 | 4.0834 | 5.7749 | 8.1972 | 11.6734 | 16.6709 | 23.867 | 34.2439 | 49.2264 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0.029934 | 0.13687 | 0.28572 | 0.49393 | 0.78653 | 1.1994 | 1.7841 | 2.6149 | 3.7987 | 5.4903 | 7.9126 | 11.3888 | 16.3862 | 23.5824 | 33.9032 | 48.7749 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 1.5248 | 6.972 | 14.5537 | 25.1596 | 40.0635 | 61.0934 | 90.8761 | 133.1937 | 193.4981 | 279.6588 | 403.0477 | 580.1137 | 834.6708 | 1201.2223 | 1726.9394 | 2484.4597 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 16.2382 | 21.7588 | 29.4427 | 40.1914 | 55.2962 | 76.6093 | 106.7933 | 149.6809 | 210.7977 | 298.1193 | 423.1705 | 602.6219 | 860.6083 | 1232.0981 | 1767.7912 | 2541.2423 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 1.5453 | 7.0659 | 14.7498 | 25.4985 | 40.6033 | 61.9164 | 92.1004 | 134.9881 | 196.1049 | 283.4264 | 408.4776 | 587.9291 | 845.9155 | 1217.4052 | 1750.2048 | 2517.9304 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.2852 | 3.0621 | 4.1435 | 5.6561 | 7.7818 | 10.7812 | 15.029 | 21.0646 | 29.6656 | 41.9544 | 59.5529 | 84.8072 | 121.1137 | 173.3935 | 248.7818 | 357.6298 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0.21747 | 0.99439 | 2.0757 | 3.5884 | 5.7141 | 8.7135 | 12.9613 | 18.9969 | 27.5979 | 39.8867 | 57.4852 | 82.7394 | 119.0459 | 171.3258 | 246.3068 | 354.3491 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 5.8715 | 5.8715 | 5.8715 | 6.489 | 8.6952 | 11.7658 | 16.0611 | 22.0972 | 30.6143 | 42.6763 | 59.8149 | 84.2382 | 119.1333 | 169.1058 | 240.8175 | 343.9131 | 492.3664 | 706.4381 | 1015.5217 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 |  | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 7.0278 | 9.3158 | 12.4565 | 16.7871 | 22.7829 | 31.1148 | 42.7316 | 58.9768 | 81.7551 | 113.7707 | 158.8658 | 222.5053 | 312.4679 |  | 0 | 0 | 0 | 0.61753 | 2.8237 | 5.8943 | 10.1896 | 16.2257 | 24.7428 | 36.8048 | 53.9434 | 78.3667 | 113.2618 | 163.2343 | 234.946 | 338.0416 | 486.4949 | 699.4103 | 1006.2059 | 1057.5167 | 1053.1861 | 1047.1903 | 1038.8583 | 1027.2416 | 1010.9964 | 988.2181 | 956.2025 | 911.1073 | 847.4679 | 757.5053 |  | 0 | 0 | 0 | 3.9051 | 17.856 | 37.2735 | 64.4362 | 102.6067 | 156.4661 | 232.7426 | 341.122 | 495.5675 | 716.2337 | 1032.2448 | 1485.7282 | 2137.6737 | 3076.4482 | 4422.8613 | 6362.9452 | 6687.4193 | 6660.0337 | 6622.118 | 6569.4294 | 6495.9684 | 6393.239 | 6249.1955 | 6046.7385 | 5761.5703 | 5359.1333 | 4790.2367
| TRUE | 1320 | 22008407 | DDL | DDL022 | 22 | DDL22 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 14.5366 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 144.6854 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.8715 |  | 91.9252 | 914.9474 | 37.1297 | 877.8178 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 114.1843 | 142.3372 | 178.0118 | 223.2973 | 280.8765 | 354.197 | 447.6925 | 567.0674 | 719.6658 | 914.9474 | 1165.1027 | 1485.848 | 1897.4531 | 2426.0706 | 3105.4547 | 3979.1834 | 5103.535 | 6551.2073 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 |  | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 44.4419 | 58.9104 | 78.7711 | 106.1567 | 144.0723 | 196.7609 | 270.222 | 372.9513 | 516.9949 | 719.4519 | 1004.6201 | 1407.0571 | 1975.9537 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 18.0566 | 22.5085 | 28.1499 | 35.3112 | 44.4165 | 56.011 | 70.796 | 89.6733 | 113.8045 | 144.6854 | 184.2438 | 234.9649 | 300.0542 | 383.6473 | 491.0818 | 629.2491 | 807.0488 | 1035.9768 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 |  | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 7.0278 | 9.3158 | 12.4565 | 16.7871 | 22.7829 | 31.1148 | 42.7316 | 58.9768 | 81.7551 | 113.7707 | 158.8658 | 222.5053 | 312.4679 |  | 12.1851 | 16.637 | 22.2784 | 29.4397 | 38.545 | 50.1395 | 64.9245 | 83.8018 | 107.933 | 138.8139 | 178.3723 | 229.0934 | 294.1827 | 377.7758 | 485.2103 | 623.3776 | 801.1772 | 1028.949 | 1060.6574 | 1057.5167 | 1053.1861 | 1047.1903 | 1038.8583 | 1027.2416 | 1010.9964 | 988.2181 | 956.2025 | 911.1073 | 847.4679 | 757.5053 |  | 77.0547 | 105.2075 | 140.8821 | 186.1676 | 243.7468 | 317.0674 | 410.5628 | 529.9377 | 682.5361 | 877.8178 | 1127.9731 | 1448.7183 | 1860.3234 | 2388.941 | 3068.325 | 3942.0538 | 5066.4053 | 6506.7654 | 6707.28 | 6687.4193 | 6660.0337 | 6622.118 | 6569.4294 | 6495.9684 | 6393.239 | 6249.1955 | 6046.7385 | 5761.5703 | 5359.1333 | 4790.2367
| TRUE | 1321 | 22008408 | DDL | DDL023 | 22 | DDL23 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.99892 | 1 |  | 5.8543 | 0.012795 | 1.7508e-05 | 0.012777 | 35.1903 | 1.2256 | 36.4159 | 36.4187 | 5.1193 | 25.283 |  | 13.88 | 0.12735 | 0.00017426 | 0.12717 | 350.255 | 12.1983 | 362.4533 | 362.4815 | 50.9537 | 251.6459 |  | 0.0051679 | 7.0717e-06 | 0.0051609 | 14.2138 | 0.49502 | 14.7088 | 14.7099 | 2.0678 | 10.2121 |  | 103.2369 | 1027.5343 | 41.6986 | 985.8358 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.1748e-05 | 2.711e-05 | 3.3904e-05 | 4.2529e-05 | 5.3496e-05 | 6.7461e-05 | 8.5268e-05 | 0.000108 | 0.00013707 | 0.00017426 | 0.00022191 | 0.000283 | 0.00036139 | 0.00046207 | 0.00059147 | 0.00075788 | 0.00097202 | 0.0012477 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 128.235 | 159.8522 | 199.9166 | 250.7746 | 315.4391 | 397.782 | 502.7823 | 636.8466 | 808.2227 | 1027.5343 | 1308.472 | 1668.6858 | 2130.9401 | 2724.6056 | 3487.5898 | 4468.8334 | 5731.5395 | 7357.3521 | 7598.7895 | 7598.7895 | 7598.7895 | 7598.7895 | 7598.7895 | 7598.7895 | 7598.7895 | 7598.7895 | 7598.7895 | 7598.7895 | 7598.7895 | 7598.7895 |  | 41.6986 | 41.6986 | 41.6986 | 41.6986 | 41.6986 | 41.6986 | 41.6986 | 41.6986 | 41.6986 | 41.6986 | 41.6986 | 41.6986 | 41.6986 | 41.6986 | 41.6986 | 41.6986 | 41.6986 | 49.9106 | 66.1594 | 88.4641 | 119.2196 | 161.8009 | 220.9729 | 303.4736 | 418.8441 | 580.6126 | 807.9825 | 1128.2415 | 1580.1995 | 2219.1005 |  | 43.7114 | 54.4887 | 68.1455 | 85.4814 | 107.5235 | 135.5917 | 171.3831 | 217.0815 | 275.4984 | 350.255 | 446.018 | 568.8039 | 726.3722 | 928.7346 | 1188.8125 | 1523.2884 | 1953.7063 | 2507.896 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 |  | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 17.013 | 22.5517 | 30.1547 | 40.6383 | 55.153 | 75.3229 | 103.4449 | 142.7711 | 197.913 | 275.4165 | 384.583 | 538.6416 | 756.4234 |  | 29.4976 | 40.2749 | 53.9317 | 71.2676 | 93.3098 | 121.3779 | 157.1693 | 202.8677 | 261.2846 | 336.0412 | 431.8042 | 554.5901 | 712.1584 | 914.5208 | 1174.5988 | 1509.0746 | 1939.4925 | 2490.883 | 2567.6429 | 2560.0399 | 2549.5563 | 2535.0416 | 2514.8717 | 2486.7497 | 2447.4235 | 2392.2815 | 2314.7781 | 2205.6116 | 2051.553 | 1833.7712 |  | 1.5223 | 1.8977 | 2.3733 | 2.9771 | 3.7447 | 4.7222 | 5.9687 | 7.5603 | 9.5948 | 12.1983 | 15.5334 | 19.8097 | 25.2973 | 32.3449 | 41.4026 | 53.0514 | 68.0415 | 87.3422 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 |  | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.59251 | 0.78541 | 1.0502 | 1.4153 | 1.9208 | 2.6233 | 3.6027 | 4.9723 | 6.8927 | 9.5919 | 13.3938 | 18.7592 | 26.3439 |  | 1.0273 | 1.4027 | 1.8783 | 2.482 | 3.2497 | 4.2272 | 5.4737 | 7.0653 | 9.0997 | 11.7033 | 15.0384 | 19.3147 | 24.8023 | 31.8499 | 40.9076 | 52.5564 | 67.5465 | 86.7497 | 89.423 | 89.1582 | 88.7931 | 88.2876 | 87.5852 | 86.6058 | 85.2362 | 83.3157 | 80.6165 | 76.8146 | 71.4492 | 63.8646 |  | 30.5249 | 41.6776 | 55.81 | 73.7497 | 96.5595 | 125.6051 | 162.643 | 209.933 | 270.3843 | 347.7445 | 446.8427 | 573.9048 | 736.9607 | 946.3707 | 1215.5064 | 1561.631 | 2007.039 | 2577.6327 | 2657.0659 | 2649.1981 | 2638.3494 | 2623.3293 | 2602.4568 | 2573.3555 | 2532.6596 | 2475.5973 | 2395.3946 | 2282.4262 | 2123.0022 | 1897.6358 |  | 45.2372 | 56.3908 | 70.5242 | 88.4653 | 111.2769 | 140.3248 | 177.3656 | 224.6592 | 285.1153 | 362.4815 | 461.5873 | 588.6593 | 751.7279 | 961.1543 | 1230.3108 | 1576.4624 | 2021.905 | 2595.44 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 |  | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 17.6069 | 23.3389 | 31.2073 | 42.0569 | 57.0782 | 77.9522 | 107.0558 | 147.7549 | 204.8217 | 285.0306 | 398.0077 | 557.4442 | 782.8281 |  | 30.5273 | 41.6808 | 55.8143 | 73.7554 | 96.567 | 125.6149 | 162.6557 | 209.9493 | 270.4054 | 347.7715 | 446.8774 | 573.9494 | 737.018 | 946.4443 | 1215.6009 | 1561.7524 | 2007.1951 | 2577.8331 | 2657.2725 | 2649.4041 | 2638.5545 | 2623.5332 | 2602.6592 | 2573.5556 | 2532.8566 | 2475.7898 | 2395.5809 | 2282.6037 | 2123.1673 | 1897.7833 |  | 6.359 | 7.9268 | 9.9135 | 12.4355 | 15.6421 | 19.7253 | 24.9321 | 31.5801 | 40.0784 | 50.9537 | 64.8849 | 82.7473 | 105.6697 | 135.1086 | 172.9437 | 221.6019 | 284.2173 | 364.8386 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 |  | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9577 | 15.0487 | 20.7698 | 28.7916 | 40.0665 | 55.9476 | 78.3594 | 110.0414 |  | 4.2912 | 5.859 | 7.8458 | 10.3677 | 13.5743 | 17.6576 | 22.8644 | 29.5124 | 38.0106 | 48.8859 | 62.8171 | 80.6795 | 103.6019 | 133.0408 | 170.8759 | 219.5341 | 282.1496 | 362.3636 | 373.5304 | 372.4243 | 370.8992 | 368.7877 | 365.8534 | 361.7623 | 356.0413 | 348.0195 | 336.7446 | 320.8635 | 298.4517 | 266.7697 |  | 31.4051 | 39.1482 | 48.9601 | 61.4154 | 77.2519 | 97.4179 | 123.1327 | 155.9654 | 197.9359 | 251.6459 | 320.4483 | 408.6656 | 521.873 | 667.2632 | 854.1201 | 1094.4293 | 1403.6694 | 1801.8353 | 1860.964 | 1860.964 | 1860.964 | 1860.964 | 1860.964 | 1860.964 | 1860.964 | 1860.964 | 1860.964 | 1860.964 | 1860.964 | 1860.964 |  | 10.2121 | 10.2121 | 10.2121 | 10.2121 | 10.2121 | 10.2121 | 10.2121 | 10.2121 | 10.2121 | 10.2121 | 10.2121 | 10.2121 | 10.2121 | 10.2121 | 10.2121 | 10.2121 | 10.2121 | 12.2232 | 16.2026 | 21.6651 | 29.1972 | 39.6255 | 54.1169 | 74.3215 | 102.576 | 142.1936 | 197.8771 | 276.3094 | 386.9951 | 543.4637 |  | 21.193 | 28.9361 | 38.748 | 51.2033 | 67.0398 | 87.2058 | 112.9206 | 145.7534 | 187.7238 | 241.4338 | 310.2362 | 398.4535 | 511.6609 | 657.0511 | 843.908 | 1084.2172 | 1393.4573 | 1789.6121 | 1844.7613 | 1839.2989 | 1831.7668 | 1821.3385 | 1806.8471 | 1786.6425 | 1758.3879 | 1718.7704 | 1663.0869 | 1584.6546 | 1473.9689 | 1317.5003 |  | 86.5365 | 118.1536 | 158.2181 | 209.0761 | 273.7405 | 356.0834 | 461.0837 | 595.148 | 766.5241 | 985.8358 | 1266.7734 | 1626.9873 | 2089.2415 | 2682.907 | 3445.8912 | 4427.1348 | 5689.841 | 7307.4416 | 7532.6301 | 7510.3254 | 7479.5699 | 7436.9886 | 7377.8166 | 7295.3159 | 7179.9454 | 7018.1769 | 6790.807 | 6470.548 | 6018.59 | 5379.689
| TRUE | 1322 | 22008409 | DDL | DDL024 | 22 | DDL24 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 14.5366 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 144.6854 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.8715 |  | 91.9252 | 914.9474 | 37.1297 | 877.8178 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 114.1843 | 142.3372 | 178.0118 | 223.2973 | 280.8765 | 354.197 | 447.6925 | 567.0674 | 719.6658 | 914.9474 | 1165.1027 | 1485.848 | 1897.4531 | 2426.0706 | 3105.4547 | 3979.1834 | 5103.535 | 6551.2073 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 | 6766.1904 |  | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 37.1297 | 44.4419 | 58.9104 | 78.7711 | 106.1567 | 144.0723 | 196.7609 | 270.222 | 372.9513 | 516.9949 | 719.4519 | 1004.6201 | 1407.0571 | 1975.9537 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 18.0566 | 22.5085 | 28.1499 | 35.3112 | 44.4165 | 56.011 | 70.796 | 89.6733 | 113.8045 | 144.6854 | 184.2438 | 234.9649 | 300.0542 | 383.6473 | 491.0818 | 629.2491 | 807.0488 | 1035.9768 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 | 1069.9732 |  | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 5.8715 | 7.0278 | 9.3158 | 12.4565 | 16.7871 | 22.7829 | 31.1148 | 42.7316 | 58.9768 | 81.7551 | 113.7707 | 158.8658 | 222.5053 | 312.4679 |  | 12.1851 | 16.637 | 22.2784 | 29.4397 | 38.545 | 50.1395 | 64.9245 | 83.8018 | 107.933 | 138.8139 | 178.3723 | 229.0934 | 294.1827 | 377.7758 | 485.2103 | 623.3776 | 801.1772 | 1028.949 | 1060.6574 | 1057.5167 | 1053.1861 | 1047.1903 | 1038.8583 | 1027.2416 | 1010.9964 | 988.2181 | 956.2025 | 911.1073 | 847.4679 | 757.5053 |  | 77.0547 | 105.2075 | 140.8821 | 186.1676 | 243.7468 | 317.0674 | 410.5628 | 529.9377 | 682.5361 | 877.8178 | 1127.9731 | 1448.7183 | 1860.3234 | 2388.941 | 3068.325 | 3942.0538 | 5066.4053 | 6506.7654 | 6707.28 | 6687.4193 | 6660.0337 | 6622.118 | 6569.4294 | 6495.9684 | 6393.239 | 6249.1955 | 6046.7385 | 5761.5703 | 5359.1333 | 4790.2367
| TRUE | 1323 | 22001430 | DDL | Blank | 22 | TRANS NO.1 | DIFFERENTIAL | X | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.066046 | 2190 |  | 8.25 | 0.026286 | 0.0045837 | 0.021702 | 280.8119 | 2016.8282 | 2297.64 | 100.6375 | 10.5627 | 1720.2027 |  | 12.7412 | 0.085397 | 0.014892 | 0.070505 | 912.3017 | 6552.2719 | 7464.5736 | 326.9512 | 34.3161 | 5588.5951 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.17547 |  | 4129.043 | 13414.436 | 71.3852 | 13343.0509 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0.005143 | 0.0057745 | 0.0064876 | 0.0072933 | 0.0082039 | 0.0092333 | 0.010397 | 0.011714 | 0.013205 | 0.014892 | 0.016801 | 0.018964 | 0.021414 | 0.024191 | 0.027337 | 0.030903 | 0.034947 | 0.039533 | 0.044734 | 0.050635 | 0.05733 | 0.064929 | 0.073553 | 0.083344 | 0.094461 | 0.10708 | 0.12142 | 0.13771 | 0.13973 | 0.13973 | 4632.8918 | 5201.7084 | 5844.1107 | 6569.8799 | 7390.1187 | 8317.4324 | 9366.1335 | 10552.4759 | 11894.9202 | 13414.436 | 15134.8462 | 17083.2179 | 19290.3079 | 21791.0694 | 24625.2285 | 27837.9409 | 31480.5383 | 35611.3788 | 40296.8141 | 45612.2915 | 51643.6067 | 58488.3314 | 66257.4379 | 75077.1479 | 85091.0383 | 96462.4382 | 109377.1573 | 124046.5937 | 125867.7337 | 125867.7337 |  | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 52.9716 | 70.217 | 93.8896 | 126.5313 | 171.7241 | 234.5252 | 322.0856 | 444.5317 | 616.2214 | 857.536 | 1197.4363 | 1677.1129 | 2355.1975 |  | 315.0781 | 353.7627 | 397.4518 | 446.8106 | 502.5942 | 565.6598 | 636.9809 | 717.6628 | 808.961 | 912.3017 | 1029.305 | 1161.8117 | 1311.9135 | 1481.9877 | 1674.7359 | 1893.2291 | 2140.9583 | 2421.8924 | 2740.5439 | 3102.0439 | 3512.2273 | 3977.7298 | 4506.0986 | 5105.9178 | 5786.9519 | 6560.3089 | 7438.6253 | 8436.2782 | 8560.1321 | 8560.1321 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 287.9462 | 326.6308 | 370.3199 | 419.6787 | 475.4623 | 538.5279 | 609.849 | 690.5309 | 781.8291 | 885.1698 | 1002.173 | 1134.6798 | 1284.7816 | 1454.8558 | 1647.604 | 1866.0971 | 2113.8264 | 2389.4172 | 2697.4961 | 3044.4832 | 3434.655 | 3872.4513 | 4362.3187 | 4908.4574 | 5514.4237 | 6182.5232 | 6912.8974 | 7702.1682 | 7531.9476 | 7116.2356 |  | 2262.9328 | 2540.7708 | 2854.5518 | 3209.0532 | 3609.6983 | 4062.644 | 4574.8814 | 5154.3495 | 5810.0654 | 6552.2719 | 7392.6051 | 8344.2859 | 9422.3374 | 10643.8326 | 12028.1757 | 13597.4228 | 15376.647 | 17394.3531 | 19682.9507 | 22279.2919 | 25225.2836 | 28568.5847 | 32363.3993 | 36671.3805 | 41562.6583 | 47117.0106 | 53425.1961 | 60590.4721 | 61480.0066 | 61480.0066 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 2262.727 | 2540.5651 | 2854.3461 | 3208.8475 | 3609.4926 | 4062.4383 | 4574.6756 | 5154.1438 | 5809.8597 | 6552.0662 | 7392.3994 | 8344.0801 | 9422.1317 | 10643.6269 | 12027.97 | 13597.2171 | 15376.4412 | 17394.1069 | 19682.6243 | 22278.8555 | 25224.6954 | 28567.7864 | 32362.3091 | 36669.8832 | 41560.5918 | 47114.146 | 53421.2098 | 60584.9057 | 61472.2104 | 61469.0582 |  | 2550.6732 | 2867.1959 | 3224.666 | 3628.5262 | 4084.9549 | 4600.9662 | 5184.5246 | 5844.6746 | 6591.6888 | 7437.2359 | 8394.5724 | 9478.7599 | 10706.9133 | 12098.4827 | 13675.5739 | 15463.3142 | 17490.2676 | 19783.524 | 22380.1204 | 25323.3387 | 28659.3504 | 32440.2377 | 36724.6278 | 41578.3406 | 47075.0155 | 53296.6691 | 60334.1071 | 68287.0739 | 69004.158 | 68585.2938 |  | 112.9179 | 126.7817 | 142.439 | 160.1282 | 180.12 | 202.7215 | 228.2815 | 257.1964 | 289.9159 | 326.9512 | 368.8829 | 416.3707 | 470.1643 | 531.1155 | 600.1927 | 678.4964 | 767.2778 | 867.9591 | 982.1576 | 1111.7121 | 1258.7139 | 1425.5409 | 1614.898 | 1829.8615 | 2073.9309 | 2351.087 | 2665.8585 | 3023.3978 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 98.2454 | 112.1092 | 127.7666 | 145.4558 | 165.4475 | 188.049 | 213.6091 | 242.5239 | 275.2434 | 312.2787 | 354.2104 | 401.6982 | 455.4918 | 516.4431 | 585.5203 | 663.824 | 752.6053 | 850.3971 | 958.8781 | 1080.5843 | 1216.7642 | 1368.6082 | 1537.1445 | 1723.0785 | 1926.5526 | 2146.7874 | 2381.5544 | 2626.4046 | 2511.7613 | 2286.9518 |  | 11.8516 | 13.3068 | 14.9501 | 16.8067 | 18.905 | 21.2772 | 23.96 | 26.9948 | 30.429 | 34.3161 | 38.7172 | 43.7014 | 49.3475 | 55.7448 | 62.995 | 71.2136 | 80.5319 | 91.0993 | 103.0853 | 116.6831 | 132.1121 | 149.6219 | 169.4965 | 192.0586 | 217.6757 | 246.7654 | 279.8032 | 317.3298 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 9.7839 | 11.2391 | 12.8824 | 14.739 | 16.8373 | 19.2095 | 21.8923 | 24.9271 | 28.3613 | 32.2484 | 36.6495 | 41.6337 | 47.2798 | 53.6771 | 60.9273 | 69.1459 | 78.4643 | 88.6244 | 99.8047 | 112.2964 | 126.2004 | 141.5988 | 158.5392 | 177.0104 | 196.9066 | 217.9747 | 239.738 | 261.384 | 243.6317 | 211.9507 |  | 1930.1115 | 2167.0864 | 2434.718 | 2737.0811 | 3078.8012 | 3465.1298 | 3902.0297 | 4396.2725 | 4955.5489 | 5588.5951 | 6305.3361 | 7117.0483 | 8036.5452 | 9078.3887 | 10259.1292 | 11597.579 | 13115.1234 | 14836.075 | 16788.0766 | 19002.5604 | 21515.2697 | 24366.8541 | 27603.5456 | 31277.9295 | 35449.8216 | 40187.2664 | 45567.6742 | 51679.1157 | 52437.8218 | 52437.8218 |  | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.21003 | 0.27841 | 0.37227 | 0.50169 | 0.68087 | 0.92988 | 1.277 | 1.7625 | 2.4433 | 3.4001 | 4.7477 | 6.6496 | 9.3382 |  | 1929.936 | 2166.911 | 2434.5425 | 2736.9056 | 3078.6257 | 3464.9543 | 3901.8543 | 4396.097 | 4955.3734 | 5588.4197 | 6305.1607 | 7116.8728 | 8036.3697 | 9078.2132 | 10258.9537 | 11597.4035 | 13114.9479 | 14835.8649 | 16787.7982 | 19002.1881 | 21514.7681 | 24366.1732 | 27602.6157 | 31276.6525 | 35448.059 | 40184.8231 | 45564.2741 | 51674.368 | 52431.1721 | 52428.4836 |  | 4588.6386 | 5157.4551 | 5799.8574 | 6525.6266 | 7345.8655 | 8273.1791 | 9321.8803 | 10508.2226 | 11850.6669 | 13370.1828 | 15090.593 | 17038.9647 | 19246.0547 | 21746.8161 | 24580.9753 | 27793.6877 | 31436.2851 | 35558.4104 | 40226.6014 | 45518.4076 | 51517.0831 | 58316.6178 | 66022.9271 | 74755.082 | 84646.5338 | 95846.2543 | 108519.6737 | 122849.2305 | 124190.7231 | 123512.6798
| TRUE | 1324 | 22001432 | DDL | Blank | 22 | TRANS NO.1 | DIFFERENTIAL | Y | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.0068096 | 2190 |  | 8.25 | 0.026286 | 0.00052975 | 0.025756 | 276.5552 | 233.0884 | 509.6437 | 77.6223 | 10.5222 | 198.8069 |  | 12.7412 | 0.085397 | 0.001721 | 0.083676 | 898.4727 | 757.2578 | 1655.7304 | 252.1792 | 34.1844 | 645.8839 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.018092 |  | 796.595 | 2587.9781 | 71.0404 | 2516.9376 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0.00059439 | 0.00066737 | 0.00074979 | 0.0008429 | 0.00094813 | 0.0010671 | 0.0012017 | 0.0013539 | 0.0015261 | 0.001721 | 0.0019418 | 0.0021917 | 0.0024749 | 0.0027957 | 0.0031594 | 0.0035715 | 0.0040389 | 0.0045689 | 0.00517 | 0.0058519 | 0.0066258 | 0.0075039 | 0.0085007 | 0.0096322 | 0.010917 | 0.012376 | 0.014033 | 0.015915 | 0.016149 | 0.016149 | 893.8 | 1003.5388 | 1127.4742 | 1267.4931 | 1425.7375 | 1604.6394 | 1806.9599 | 2035.8348 | 2294.8257 | 2587.9781 | 2919.888 | 3295.7773 | 3721.5798 | 4204.0388 | 4750.8185 | 5370.6306 | 6073.3782 | 6870.3199 | 7774.2568 | 8799.7445 | 9963.3351 | 11283.8526 | 12782.7063 | 14484.2475 | 16416.1759 | 18610.0015 | 21101.5717 | 23931.6706 | 24283.0137 | 24283.0137 |  | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 52.5563 | 69.6666 | 93.1536 | 125.5394 | 170.3779 | 232.6867 | 319.5607 | 441.047 | 611.3908 | 850.8137 | 1188.0495 | 1663.9659 | 2336.735 |  | 310.302 | 348.4002 | 391.4271 | 440.0377 | 494.9757 | 557.0853 | 627.3253 | 706.7842 | 796.6985 | 898.4727 | 1013.7024 | 1144.2005 | 1292.0271 | 1459.5232 | 1649.3496 | 1864.5308 | 2108.5048 | 2385.1804 | 2699.0017 | 3055.022 | 3458.9877 | 3917.4339 | 4437.7935 | 5028.5204 | 5699.2311 | 6460.8652 | 7325.8678 | 8308.398 | 8430.3744 | 8430.3744 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 283.1703 | 321.2686 | 364.2954 | 412.906 | 467.844 | 529.9536 | 600.1936 | 679.6525 | 769.5668 | 871.341 | 986.5707 | 1117.0688 | 1264.8954 | 1432.3915 | 1622.2179 | 1837.3991 | 2081.3731 | 2352.7055 | 2655.9543 | 2997.4617 | 3381.416 | 3812.1562 | 4294.0147 | 4831.0616 | 5426.7051 | 6083.0826 | 6800.1442 | 7574.2939 | 7402.1983 | 6986.4896 |  | 261.5312 | 293.6414 | 329.9057 | 370.876 | 417.1793 | 469.527 | 528.7272 | 595.6974 | 671.4797 | 757.2578 | 854.3766 | 964.364 | 1088.9564 | 1230.1268 | 1390.1178 | 1571.4785 | 1777.1066 | 2010.2965 | 2274.7938 | 2574.8576 | 2915.3311 | 3301.7224 | 3740.2959 | 4238.177 | 4803.4708 | 5445.3972 | 6174.4455 | 7002.5492 | 7105.3543 | 7105.3543 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 261.51 | 293.6202 | 329.8844 | 370.8548 | 417.1581 | 469.5058 | 528.706 | 595.6762 | 671.4584 | 757.2366 | 854.3554 | 964.3428 | 1088.9352 | 1230.1056 | 1390.0966 | 1571.4573 | 1777.0854 | 2010.2711 | 2274.7602 | 2574.8126 | 2915.2705 | 3301.6401 | 3740.1835 | 4238.0227 | 4803.2577 | 5445.1018 | 6174.0345 | 7001.9753 | 7104.5505 | 7104.2255 |  | 544.6803 | 614.8888 | 694.1798 | 783.7608 | 885.0021 | 999.4595 | 1128.8996 | 1275.3287 | 1441.0252 | 1628.5775 | 1840.9261 | 2081.4116 | 2353.8305 | 2662.497 | 3012.3145 | 3408.8564 | 3858.4585 | 4362.9766 | 4930.7144 | 5572.2743 | 6296.6865 | 7113.7963 | 8034.1983 | 9069.0842 | 10229.9628 | 11528.1844 | 12974.1786 | 14576.2692 | 14506.7488 | 14090.7151 |  | 87.0942 | 97.7874 | 109.864 | 123.5078 | 138.9275 | 156.3602 | 176.0748 | 198.377 | 223.6137 | 252.1792 | 284.5214 | 321.149 | 362.6403 | 409.6524 | 462.932 | 523.3281 | 591.8056 | 669.4617 | 757.5436 | 857.4698 | 970.853 | 1099.5276 | 1245.5798 | 1411.3824 | 1599.6344 | 1813.4065 | 2056.1915 | 2331.9636 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 72.4241 | 83.1173 | 95.1939 | 108.8377 | 124.2575 | 141.6901 | 161.4048 | 183.7069 | 208.9437 | 237.5092 | 269.8513 | 306.479 | 347.9703 | 394.9823 | 448.2619 | 508.658 | 577.1355 | 651.9025 | 734.2679 | 826.347 | 928.9101 | 1042.6042 | 1167.8389 | 1304.6167 | 1452.2801 | 1609.14 | 1771.9335 | 1935.0347 | 1810.2663 | 1585.4933 |  | 11.8061 | 13.2557 | 14.8927 | 16.7422 | 18.8325 | 21.1956 | 23.868 | 26.8912 | 30.3122 | 34.1844 | 38.5686 | 43.5337 | 49.1581 | 55.5309 | 62.7533 | 70.9403 | 80.2229 | 90.7496 | 102.6897 | 116.2353 | 131.6051 | 149.0477 | 168.846 | 191.3215 | 216.8402 | 245.8183 | 278.7293 | 316.1119 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 9.7385 | 11.188 | 12.825 | 14.6745 | 16.7648 | 19.1279 | 21.8003 | 24.8235 | 28.2445 | 32.1167 | 36.5009 | 41.466 | 47.0904 | 53.4632 | 60.6856 | 68.8726 | 78.1552 | 88.2747 | 99.409 | 111.8486 | 125.6934 | 141.0245 | 157.8887 | 176.2733 | 196.0712 | 217.0277 | 238.6642 | 260.1662 | 242.396 | 210.7151 |  | 223.0664 | 250.4541 | 281.3847 | 316.3294 | 355.8226 | 400.4713 | 450.9646 | 508.0851 | 572.7216 | 645.8839 | 728.719 | 822.53 | 928.7979 | 1049.2056 | 1185.6659 | 1340.353 | 1515.7383 | 1714.6317 | 1940.228 | 2196.1599 | 2486.5582 | 2816.1209 | 3190.1911 | 3614.8463 | 4096.9993 | 4644.5143 | 5266.3376 | 5972.6478 | 6060.3329 | 6060.3329 |  | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.021655 | 0.028704 | 0.038382 | 0.051725 | 0.0702 | 0.095873 | 0.13167 | 0.18172 | 0.25191 | 0.35056 | 0.48951 | 0.68559 | 0.96279 |  | 223.0483 | 250.436 | 281.3666 | 316.3113 | 355.8045 | 400.4532 | 450.9465 | 508.067 | 572.7036 | 645.8658 | 728.7009 | 822.5119 | 928.7798 | 1049.1875 | 1185.6478 | 1340.3349 | 1515.7202 | 1714.6101 | 1940.1993 | 2196.1215 | 2486.5065 | 2816.0507 | 3190.0953 | 3614.7146 | 4096.8176 | 4644.2623 | 5265.9871 | 5972.1583 | 6059.6473 | 6059.3701 |  | 849.8912 | 959.6301 | 1083.5654 | 1223.5843 | 1381.8288 | 1560.7307 | 1763.0512 | 1991.9261 | 2250.917 | 2544.0693 | 2875.9792 | 3251.8685 | 3677.671 | 4160.1301 | 4706.9098 | 5326.7219 | 6029.4694 | 6817.7639 | 7704.5907 | 8706.5915 | 9837.7965 | 11113.4758 | 12550.0211 | 14164.6888 | 15975.1317 | 17998.6145 | 20250.7634 | 22743.6286 | 22619.0584 | 21946.2935
| TRUE | 1325 | 22001431 | DDL | Blank | 22 | TRANS NO.2 | DIFFERENTIAL | X | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.066046 | 2190 |  | 8.25 | 0.026286 | 0.0045837 | 0.021702 | 280.8119 | 2016.8282 | 2297.64 | 100.6375 | 10.5627 | 1720.2027 |  | 12.7412 | 0.085397 | 0.014892 | 0.070505 | 912.3017 | 6552.2719 | 7464.5736 | 326.9512 | 34.3161 | 5588.5951 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.17547 |  | 4129.043 | 13414.436 | 71.3852 | 13343.0509 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0.005143 | 0.0057745 | 0.0064876 | 0.0072933 | 0.0082039 | 0.0092333 | 0.010397 | 0.011714 | 0.013205 | 0.014892 | 0.016801 | 0.018964 | 0.021414 | 0.024191 | 0.027337 | 0.030903 | 0.034947 | 0.039533 | 0.044734 | 0.050635 | 0.05733 | 0.064929 | 0.073553 | 0.083344 | 0.094461 | 0.10708 | 0.12142 | 0.13771 | 0.13973 | 0.13973 | 4632.8918 | 5201.7084 | 5844.1107 | 6569.8799 | 7390.1187 | 8317.4324 | 9366.1335 | 10552.4759 | 11894.9202 | 13414.436 | 15134.8462 | 17083.2179 | 19290.3079 | 21791.0694 | 24625.2285 | 27837.9409 | 31480.5383 | 35611.3788 | 40296.8141 | 45612.2915 | 51643.6067 | 58488.3314 | 66257.4379 | 75077.1479 | 85091.0383 | 96462.4382 | 109377.1573 | 124046.5937 | 125867.7337 | 125867.7337 |  | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 44.2559 | 52.9716 | 70.217 | 93.8896 | 126.5313 | 171.7241 | 234.5252 | 322.0856 | 444.5317 | 616.2214 | 857.536 | 1197.4363 | 1677.1129 | 2355.1975 |  | 315.0781 | 353.7627 | 397.4518 | 446.8106 | 502.5942 | 565.6598 | 636.9809 | 717.6628 | 808.961 | 912.3017 | 1029.305 | 1161.8117 | 1311.9135 | 1481.9877 | 1674.7359 | 1893.2291 | 2140.9583 | 2421.8924 | 2740.5439 | 3102.0439 | 3512.2273 | 3977.7298 | 4506.0986 | 5105.9178 | 5786.9519 | 6560.3089 | 7438.6253 | 8436.2782 | 8560.1321 | 8560.1321 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 287.9462 | 326.6308 | 370.3199 | 419.6787 | 475.4623 | 538.5279 | 609.849 | 690.5309 | 781.8291 | 885.1698 | 1002.173 | 1134.6798 | 1284.7816 | 1454.8558 | 1647.604 | 1866.0971 | 2113.8264 | 2389.4172 | 2697.4961 | 3044.4832 | 3434.655 | 3872.4513 | 4362.3187 | 4908.4574 | 5514.4237 | 6182.5232 | 6912.8974 | 7702.1682 | 7531.9476 | 7116.2356 |  | 2262.9328 | 2540.7708 | 2854.5518 | 3209.0532 | 3609.6983 | 4062.644 | 4574.8814 | 5154.3495 | 5810.0654 | 6552.2719 | 7392.6051 | 8344.2859 | 9422.3374 | 10643.8326 | 12028.1757 | 13597.4228 | 15376.647 | 17394.3531 | 19682.9507 | 22279.2919 | 25225.2836 | 28568.5847 | 32363.3993 | 36671.3805 | 41562.6583 | 47117.0106 | 53425.1961 | 60590.4721 | 61480.0066 | 61480.0066 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 2262.727 | 2540.5651 | 2854.3461 | 3208.8475 | 3609.4926 | 4062.4383 | 4574.6756 | 5154.1438 | 5809.8597 | 6552.0662 | 7392.3994 | 8344.0801 | 9422.1317 | 10643.6269 | 12027.97 | 13597.2171 | 15376.4412 | 17394.1069 | 19682.6243 | 22278.8555 | 25224.6954 | 28567.7864 | 32362.3091 | 36669.8832 | 41560.5918 | 47114.146 | 53421.2098 | 60584.9057 | 61472.2104 | 61469.0582 |  | 2550.6732 | 2867.1959 | 3224.666 | 3628.5262 | 4084.9549 | 4600.9662 | 5184.5246 | 5844.6746 | 6591.6888 | 7437.2359 | 8394.5724 | 9478.7599 | 10706.9133 | 12098.4827 | 13675.5739 | 15463.3142 | 17490.2676 | 19783.524 | 22380.1204 | 25323.3387 | 28659.3504 | 32440.2377 | 36724.6278 | 41578.3406 | 47075.0155 | 53296.6691 | 60334.1071 | 68287.0739 | 69004.158 | 68585.2938 |  | 112.9179 | 126.7817 | 142.439 | 160.1282 | 180.12 | 202.7215 | 228.2815 | 257.1964 | 289.9159 | 326.9512 | 368.8829 | 416.3707 | 470.1643 | 531.1155 | 600.1927 | 678.4964 | 767.2778 | 867.9591 | 982.1576 | 1111.7121 | 1258.7139 | 1425.5409 | 1614.898 | 1829.8615 | 2073.9309 | 2351.087 | 2665.8585 | 3023.3978 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 98.2454 | 112.1092 | 127.7666 | 145.4558 | 165.4475 | 188.049 | 213.6091 | 242.5239 | 275.2434 | 312.2787 | 354.2104 | 401.6982 | 455.4918 | 516.4431 | 585.5203 | 663.824 | 752.6053 | 850.3971 | 958.8781 | 1080.5843 | 1216.7642 | 1368.6082 | 1537.1445 | 1723.0785 | 1926.5526 | 2146.7874 | 2381.5544 | 2626.4046 | 2511.7613 | 2286.9518 |  | 11.8516 | 13.3068 | 14.9501 | 16.8067 | 18.905 | 21.2772 | 23.96 | 26.9948 | 30.429 | 34.3161 | 38.7172 | 43.7014 | 49.3475 | 55.7448 | 62.995 | 71.2136 | 80.5319 | 91.0993 | 103.0853 | 116.6831 | 132.1121 | 149.6219 | 169.4965 | 192.0586 | 217.6757 | 246.7654 | 279.8032 | 317.3298 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 9.7839 | 11.2391 | 12.8824 | 14.739 | 16.8373 | 19.2095 | 21.8923 | 24.9271 | 28.3613 | 32.2484 | 36.6495 | 41.6337 | 47.2798 | 53.6771 | 60.9273 | 69.1459 | 78.4643 | 88.6244 | 99.8047 | 112.2964 | 126.2004 | 141.5988 | 158.5392 | 177.0104 | 196.9066 | 217.9747 | 239.738 | 261.384 | 243.6317 | 211.9507 |  | 1930.1115 | 2167.0864 | 2434.718 | 2737.0811 | 3078.8012 | 3465.1298 | 3902.0297 | 4396.2725 | 4955.5489 | 5588.5951 | 6305.3361 | 7117.0483 | 8036.5452 | 9078.3887 | 10259.1292 | 11597.579 | 13115.1234 | 14836.075 | 16788.0766 | 19002.5604 | 21515.2697 | 24366.8541 | 27603.5456 | 31277.9295 | 35449.8216 | 40187.2664 | 45567.6742 | 51679.1157 | 52437.8218 | 52437.8218 |  | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.17547 | 0.21003 | 0.27841 | 0.37227 | 0.50169 | 0.68087 | 0.92988 | 1.277 | 1.7625 | 2.4433 | 3.4001 | 4.7477 | 6.6496 | 9.3382 |  | 1929.936 | 2166.911 | 2434.5425 | 2736.9056 | 3078.6257 | 3464.9543 | 3901.8543 | 4396.097 | 4955.3734 | 5588.4197 | 6305.1607 | 7116.8728 | 8036.3697 | 9078.2132 | 10258.9537 | 11597.4035 | 13114.9479 | 14835.8649 | 16787.7982 | 19002.1881 | 21514.7681 | 24366.1732 | 27602.6157 | 31276.6525 | 35448.059 | 40184.8231 | 45564.2741 | 51674.368 | 52431.1721 | 52428.4836 |  | 4588.6386 | 5157.4551 | 5799.8574 | 6525.6266 | 7345.8655 | 8273.1791 | 9321.8803 | 10508.2226 | 11850.6669 | 13370.1828 | 15090.593 | 17038.9647 | 19246.0547 | 21746.8161 | 24580.9753 | 27793.6877 | 31436.2851 | 35558.4104 | 40226.6014 | 45518.4076 | 51517.0831 | 58316.6178 | 66022.9271 | 74755.082 | 84646.5338 | 95846.2543 | 108519.6737 | 122849.2305 | 124190.7231 | 123512.6798
| TRUE | 1326 | 22001433 | DDL | Blank | 22 | TRANS NO.2 | DIFFERENTIAL | Y | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.0068096 | 2190 |  | 8.25 | 0.026286 | 0.00052975 | 0.025756 | 276.5552 | 233.0884 | 509.6437 | 77.6223 | 10.5222 | 198.8069 |  | 12.7412 | 0.085397 | 0.001721 | 0.083676 | 898.4727 | 757.2578 | 1655.7304 | 252.1792 | 34.1844 | 645.8839 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.018092 |  | 796.595 | 2587.9781 | 71.0404 | 2516.9376 |  | 0.043463 |  | 8.6165 | 8.9992 | 9.399 | 9.8165 | 10.2526 | 10.708 | 11.1837 | 11.6805 | 12.1993 | 12.7412 | 13.3072 | 13.8983 | 14.5157 | 15.1605 | 15.834 | 16.5373 | 17.2719 | 18.0392 | 18.8405 | 19.6774 | 20.5515 | 21.4645 | 22.4179 | 23.4138 | 24.4538 | 25.5401 | 26.6746 | 27.8596 | 28 | 28 |  | 0.029493 | 0.033114 | 0.037204 | 0.041824 | 0.047046 | 0.052949 | 0.059625 | 0.067177 | 0.075723 | 0.085397 | 0.096349 | 0.10875 | 0.1228 | 0.13872 | 0.15676 | 0.17722 | 0.20041 | 0.2267 | 0.25653 | 0.29037 | 0.32876 | 0.37234 | 0.4218 | 0.47794 | 0.54169 | 0.61408 | 0.6963 | 0.78968 | 0.80128 | 0.80128 |  | 0.00059439 | 0.00066737 | 0.00074979 | 0.0008429 | 0.00094813 | 0.0010671 | 0.0012017 | 0.0013539 | 0.0015261 | 0.001721 | 0.0019418 | 0.0021917 | 0.0024749 | 0.0027957 | 0.0031594 | 0.0035715 | 0.0040389 | 0.0045689 | 0.00517 | 0.0058519 | 0.0066258 | 0.0075039 | 0.0085007 | 0.0096322 | 0.010917 | 0.012376 | 0.014033 | 0.015915 | 0.016149 | 0.016149 | 893.8 | 1003.5388 | 1127.4742 | 1267.4931 | 1425.7375 | 1604.6394 | 1806.9599 | 2035.8348 | 2294.8257 | 2587.9781 | 2919.888 | 3295.7773 | 3721.5798 | 4204.0388 | 4750.8185 | 5370.6306 | 6073.3782 | 6870.3199 | 7774.2568 | 8799.7445 | 9963.3351 | 11283.8526 | 12782.7063 | 14484.2475 | 16416.1759 | 18610.0015 | 21101.5717 | 23931.6706 | 24283.0137 | 24283.0137 |  | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 43.909 | 52.5563 | 69.6666 | 93.1536 | 125.5394 | 170.3779 | 232.6867 | 319.5607 | 441.047 | 611.3908 | 850.8137 | 1188.0495 | 1663.9659 | 2336.735 |  | 310.302 | 348.4002 | 391.4271 | 440.0377 | 494.9757 | 557.0853 | 627.3253 | 706.7842 | 796.6985 | 898.4727 | 1013.7024 | 1144.2005 | 1292.0271 | 1459.5232 | 1649.3496 | 1864.5308 | 2108.5048 | 2385.1804 | 2699.0017 | 3055.022 | 3458.9877 | 3917.4339 | 4437.7935 | 5028.5204 | 5699.2311 | 6460.8652 | 7325.8678 | 8308.398 | 8430.3744 | 8430.3744 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 283.1703 | 321.2686 | 364.2954 | 412.906 | 467.844 | 529.9536 | 600.1936 | 679.6525 | 769.5668 | 871.341 | 986.5707 | 1117.0688 | 1264.8954 | 1432.3915 | 1622.2179 | 1837.3991 | 2081.3731 | 2352.7055 | 2655.9543 | 2997.4617 | 3381.416 | 3812.1562 | 4294.0147 | 4831.0616 | 5426.7051 | 6083.0826 | 6800.1442 | 7574.2939 | 7402.1983 | 6986.4896 |  | 261.5312 | 293.6414 | 329.9057 | 370.876 | 417.1793 | 469.527 | 528.7272 | 595.6974 | 671.4797 | 757.2578 | 854.3766 | 964.364 | 1088.9564 | 1230.1268 | 1390.1178 | 1571.4785 | 1777.1066 | 2010.2965 | 2274.7938 | 2574.8576 | 2915.3311 | 3301.7224 | 3740.2959 | 4238.177 | 4803.4708 | 5445.3972 | 6174.4455 | 7002.5492 | 7105.3543 | 7105.3543 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 261.51 | 293.6202 | 329.8844 | 370.8548 | 417.1581 | 469.5058 | 528.706 | 595.6762 | 671.4584 | 757.2366 | 854.3554 | 964.3428 | 1088.9352 | 1230.1056 | 1390.0966 | 1571.4573 | 1777.0854 | 2010.2711 | 2274.7602 | 2574.8126 | 2915.2705 | 3301.6401 | 3740.1835 | 4238.0227 | 4803.2577 | 5445.1018 | 6174.0345 | 7001.9753 | 7104.5505 | 7104.2255 |  | 544.6803 | 614.8888 | 694.1798 | 783.7608 | 885.0021 | 999.4595 | 1128.8996 | 1275.3287 | 1441.0252 | 1628.5775 | 1840.9261 | 2081.4116 | 2353.8305 | 2662.497 | 3012.3145 | 3408.8564 | 3858.4585 | 4362.9766 | 4930.7144 | 5572.2743 | 6296.6865 | 7113.7963 | 8034.1983 | 9069.0842 | 10229.9628 | 11528.1844 | 12974.1786 | 14576.2692 | 14506.7488 | 14090.7151 |  | 87.0942 | 97.7874 | 109.864 | 123.5078 | 138.9275 | 156.3602 | 176.0748 | 198.377 | 223.6137 | 252.1792 | 284.5214 | 321.149 | 362.6403 | 409.6524 | 462.932 | 523.3281 | 591.8056 | 669.4617 | 757.5436 | 857.4698 | 970.853 | 1099.5276 | 1245.5798 | 1411.3824 | 1599.6344 | 1813.4065 | 2056.1915 | 2331.9636 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 72.4241 | 83.1173 | 95.1939 | 108.8377 | 124.2575 | 141.6901 | 161.4048 | 183.7069 | 208.9437 | 237.5092 | 269.8513 | 306.479 | 347.9703 | 394.9823 | 448.2619 | 508.658 | 577.1355 | 651.9025 | 734.2679 | 826.347 | 928.9101 | 1042.6042 | 1167.8389 | 1304.6167 | 1452.2801 | 1609.14 | 1771.9335 | 1935.0347 | 1810.2663 | 1585.4933 |  | 11.8061 | 13.2557 | 14.8927 | 16.7422 | 18.8325 | 21.1956 | 23.868 | 26.8912 | 30.3122 | 34.1844 | 38.5686 | 43.5337 | 49.1581 | 55.5309 | 62.7533 | 70.9403 | 80.2229 | 90.7496 | 102.6897 | 116.2353 | 131.6051 | 149.0477 | 168.846 | 191.3215 | 216.8402 | 245.8183 | 278.7293 | 316.1119 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 9.7385 | 11.188 | 12.825 | 14.6745 | 16.7648 | 19.1279 | 21.8003 | 24.8235 | 28.2445 | 32.1167 | 36.5009 | 41.466 | 47.0904 | 53.4632 | 60.6856 | 68.8726 | 78.1552 | 88.2747 | 99.409 | 111.8486 | 125.6934 | 141.0245 | 157.8887 | 176.2733 | 196.0712 | 217.0277 | 238.6642 | 260.1662 | 242.396 | 210.7151 |  | 223.0664 | 250.4541 | 281.3847 | 316.3294 | 355.8226 | 400.4713 | 450.9646 | 508.0851 | 572.7216 | 645.8839 | 728.719 | 822.53 | 928.7979 | 1049.2056 | 1185.6659 | 1340.353 | 1515.7383 | 1714.6317 | 1940.228 | 2196.1599 | 2486.5582 | 2816.1209 | 3190.1911 | 3614.8463 | 4096.9993 | 4644.5143 | 5266.3376 | 5972.6478 | 6060.3329 | 6060.3329 |  | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.018092 | 0.021655 | 0.028704 | 0.038382 | 0.051725 | 0.0702 | 0.095873 | 0.13167 | 0.18172 | 0.25191 | 0.35056 | 0.48951 | 0.68559 | 0.96279 |  | 223.0483 | 250.436 | 281.3666 | 316.3113 | 355.8045 | 400.4532 | 450.9465 | 508.067 | 572.7036 | 645.8658 | 728.7009 | 822.5119 | 928.7798 | 1049.1875 | 1185.6478 | 1340.3349 | 1515.7202 | 1714.6101 | 1940.1993 | 2196.1215 | 2486.5065 | 2816.0507 | 3190.0953 | 3614.7146 | 4096.8176 | 4644.2623 | 5265.9871 | 5972.1583 | 6059.6473 | 6059.3701 |  | 849.8912 | 959.6301 | 1083.5654 | 1223.5843 | 1381.8288 | 1560.7307 | 1763.0512 | 1991.9261 | 2250.917 | 2544.0693 | 2875.9792 | 3251.8685 | 3677.671 | 4160.1301 | 4706.9098 | 5326.7219 | 6029.4694 | 6817.7639 | 7704.5907 | 8706.5915 | 9837.7965 | 11113.4758 | 12550.0211 | 14164.6888 | 15975.1317 | 17998.6145 | 20250.7634 | 22743.6286 | 22619.0584 | 21946.2935
| FALSE | 1327 | 22015531 | DDL | DDL-GLE NO.1 | 66 | GLE NO.1 LINE | DISTANCE & DIR EF | Y | GE | GE_D30 | GE D30 | GE RELAYS | Digital |  | 0.016937 | 1 |  | 0.96924 | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.0089997 |  | 5.0708 | 0.0089964 | 2.0873e-07 | 0.0089962 | 47.2313 | 0.02296 | 47.2543 | 25.5386 | 3.5995 | 0.015667 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.0089997 |  | 43.8921 | 76.408 | 43.8921 | 32.5159 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.4124e-07 | 2.0873e-07 | 3.1346e-07 | 4.773e-07 | 7.3543e-07 | 1.1446e-06 | 1.7968e-06 | 2.8408e-06 | 4.5187e-06 | 7.2241e-06 | 1.1599e-05 | 1.869e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 51.702 | 76.408 | 114.7451 | 174.7203 | 269.214 | 419.0101 | 657.7331 | 1039.9053 | 1654.1051 | 2644.4781 | 4245.9291 | 6841.7289 | 7998.5131 | 7998.5131 | 7998.5131 | 7998.5131 | 7998.5131 | 7998.5131 | 7998.5131 | 7998.5131 | 7998.5131 | 7998.5131 |  | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 52.5361 | 69.6397 | 93.1177 | 125.491 | 170.3122 | 232.5969 | 319.4374 | 440.8768 | 611.1549 | 850.4853 | 1187.591 | 1663.3237 | 2335.8331 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 31.9594 | 47.2313 | 70.9293 | 108.0027 | 166.4137 | 259.0096 | 406.5754 | 642.8137 | 1022.479 | 1634.6746 | 2624.6057 | 4229.1899 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8277 | 20.0996 | 43.7976 | 80.871 | 139.2819 | 231.8778 | 379.4436 | 615.682 | 995.3473 | 1602.1996 | 2581.5582 | 4171.6296 | 4866.6801 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015536 | 0.02296 | 0.03448 | 0.052503 | 0.080898 | 0.12591 | 0.19765 | 0.31249 | 0.49705 | 0.79466 | 1.2759 | 2.0559 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015787 | 0.020926 | 0.027982 | 0.03771 | 0.051178 | 0.069894 | 0.09599 | 0.13248 | 0.18365 | 0.25557 | 0.35687 | 0.49982 | 0.70191 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0023469 | 0.0097709 | 0.021291 | 0.039313 | 0.067708 | 0.11272 | 0.18446 | 0.2993 | 0.48386 | 0.77887 | 1.255 | 2.0279 | 2.3658 | 2.3523 | 2.3336 | 2.3075 | 2.271 | 2.2199 | 2.148 | 2.0467 | 1.9037 | 1.7016 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.83 | 20.1094 | 43.8188 | 80.9103 | 139.3497 | 231.9905 | 379.6281 | 615.9813 | 995.8312 | 1602.9784 | 2582.8131 | 4173.6575 | 4869.0459 | 4841.3263 | 4802.8065 | 4749.1003 | 4673.9965 | 4568.6886 | 4420.6754 | 4212.1934 | 3917.978 | 3502.0667 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.2809 | 25.5386 | 38.3524 | 58.3984 | 89.982 | 140.0497 | 219.8404 | 347.5775 | 552.8673 | 883.8891 | 1419.1574 | 2286.7763 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6104 | 10.8681 | 23.6819 | 43.728 | 75.3115 | 125.3793 | 205.1699 | 332.907 | 538.1968 | 866.3295 | 1395.881 | 2255.6527 | 2631.4752 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2308 | 12.6823 | 19.739 | 30.9849 | 48.9884 | 77.9225 | 124.5776 | 200.0196 | 322.304 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36791 | 1.5318 | 3.3378 | 6.1631 | 10.6146 | 17.6713 | 28.9172 | 46.9207 | 75.8548 | 122.1027 | 196.739 | 317.9173 | 370.8867 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.010601 | 0.015667 | 0.023527 | 0.035825 | 0.0552 | 0.085914 | 0.13486 | 0.21322 | 0.33916 | 0.54223 | 0.87059 | 1.4028 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 |  | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.010772 | 0.014279 | 0.019093 | 0.025731 | 0.034921 | 0.047692 | 0.065498 | 0.090398 | 0.12531 | 0.17438 | 0.2435 | 0.34105 | 0.47894 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016014 | 0.0066671 | 0.014528 | 0.026825 | 0.0462 | 0.076914 | 0.12586 | 0.20422 | 0.33016 | 0.53145 | 0.85631 | 1.3837 | 1.6143 | 1.6051 | 1.5923 | 1.5745 | 1.5496 | 1.5147 | 1.4656 | 1.3965 | 1.299 | 1.1611 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8099 | 32.5159 | 70.853 | 130.8282 | 225.3219 | 375.118 | 613.8411 | 996.0133 | 1610.213 | 2591.9421 | 4176.2894 | 6748.6112 | 7873.0221 | 7828.2009 | 7765.9162 | 7679.0757 | 7557.6363 | 7387.3582 | 7148.0278 | 6810.9221 | 6335.1894 | 5662.6799
| FALSE | 1328 | 22008410 | DDL | DDL-GLE NO.1 | 66 | GLE NO.1 LINE | DISTANCE & DIR EF | X | Schweitzer | SEL_311C | SEL 311C | SEL 300s | Digital |  | 0.15703 | 1 |  | 5.8543 | 0.012795 | 2.7522e-06 | 0.012792 | 67.1737 | 0.30275 | 67.4765 | 36.3349 | 5.1192 | 0.20658 |  | 13.88 | 0.12735 | 2.7393e-05 | 0.12732 | 668.5915 | 3.0133 | 671.6048 | 361.6477 | 50.9522 | 2.0561 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.083438 |  | 109.1372 | 1086.2607 | 44.0818 | 1042.1789 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 3.4187e-06 | 4.2616e-06 | 5.3296e-06 | 6.6855e-06 | 8.4094e-06 | 1.0605e-05 | 1.3404e-05 | 1.6978e-05 | 2.1547e-05 | 2.7393e-05 | 3.4883e-05 | 4.4486e-05 | 5.6809e-05 | 7.2636e-05 | 9.2977e-05 | 0.00011914 | 0.0001528 | 0.00019614 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 135.564 | 168.9882 | 211.3424 | 265.1071 | 333.4673 | 420.5163 | 531.5177 | 673.2441 | 854.4148 | 1086.2607 | 1383.2547 | 1764.0558 | 2252.7291 | 2880.3242 | 3686.915 | 4724.2393 | 6059.1126 | 7777.8448 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 |  | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 52.7631 | 69.9406 | 93.5201 | 126.0333 | 171.0482 | 233.6021 | 320.818 | 442.7821 | 613.7961 | 854.1609 | 1192.7235 | 1670.5122 | 2345.9281 |  | 83.4394 | 104.0119 | 130.0809 | 163.1729 | 205.2485 | 258.827 | 327.1482 | 414.3805 | 525.8908 | 668.5915 | 851.3908 | 1085.7731 | 1386.5507 | 1772.8343 | 2269.2895 | 2907.7607 | 3729.3728 | 4787.2493 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 56.3072 | 76.8797 | 102.9486 | 136.0407 | 178.1163 | 231.6948 | 300.0159 | 387.2483 | 498.7585 | 641.4592 | 824.2585 | 1058.6409 | 1359.4184 | 1745.7021 | 2242.1572 | 2880.6285 | 3702.2405 | 4754.7737 | 4901.2984 | 4886.7853 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.37605 | 0.46877 | 0.58626 | 0.7354 | 0.92503 | 1.1665 | 1.4744 | 1.8676 | 2.3701 | 3.0133 | 3.8371 | 4.8935 | 6.249 | 7.99 | 10.2275 | 13.105 | 16.8079 | 21.5756 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0.25377 | 0.34649 | 0.46398 | 0.61312 | 0.80275 | 1.0442 | 1.3521 | 1.7453 | 2.2479 | 2.891 | 3.7148 | 4.7712 | 6.1268 | 7.8677 | 10.1052 | 12.9827 | 16.6856 | 21.4293 | 22.0897 | 22.0242 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 56.5609 | 77.2261 | 103.4126 | 136.6538 | 178.919 | 232.739 | 301.3681 | 388.9936 | 501.0064 | 644.3502 | 827.9734 | 1063.4121 | 1365.5452 | 1753.5698 | 2252.2624 | 2893.6112 | 3718.9262 | 4776.203 | 4923.388 | 4908.8095 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 45.1332 | 56.2611 | 70.362 | 88.2618 | 111.0209 | 140.0021 | 176.9576 | 224.1425 | 284.4594 | 361.6477 | 460.5256 | 587.3053 | 749.9988 | 958.9434 | 1227.4808 | 1572.8361 | 2017.2541 | 2589.4698 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 30.4571 | 41.585 | 55.6859 | 73.5857 | 96.3448 | 125.326 | 162.2815 | 209.4664 | 269.7834 | 346.9716 | 445.8495 | 572.6292 | 735.3227 | 944.2673 | 1212.8047 | 1558.16 | 2002.578 | 2571.9034 | 2651.16 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 6.3588 | 7.9266 | 9.9132 | 12.4351 | 15.6416 | 19.7248 | 24.9314 | 31.5792 | 40.0772 | 50.9522 | 64.883 | 82.7449 | 105.6667 | 135.1047 | 172.9387 | 221.5955 | 284.2091 | 364.8281 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 4.2911 | 5.8589 | 7.8455 | 10.3674 | 13.5739 | 17.6571 | 22.8637 | 29.5115 | 38.0095 | 48.8845 | 62.8153 | 80.6772 | 103.599 | 133.037 | 170.871 | 219.5278 | 282.1414 | 362.3532 | 373.5196 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.2566 | 0.31986 | 0.40003 | 0.5018 | 0.63119 | 0.79595 | 1.0061 | 1.2743 | 1.6172 | 2.0561 | 2.6182 | 3.339 | 4.264 | 5.4519 | 6.9786 | 8.9421 | 11.4687 | 14.7219 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 |  | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.09987 | 0.13238 | 0.17702 | 0.23856 | 0.32376 | 0.44216 | 0.60725 | 0.8381 | 1.1618 | 1.6168 | 2.2576 | 3.1619 | 4.4404 |  | 0.17316 | 0.23642 | 0.31659 | 0.41836 | 0.54775 | 0.71252 | 0.92262 | 1.1909 | 1.5338 | 1.9726 | 2.5348 | 3.2556 | 4.1805 | 5.3684 | 6.8952 | 8.8586 | 11.3853 | 14.6221 | 15.0727 | 15.028 | 14.9665 | 14.8813 | 14.7629 | 14.5978 | 14.3669 | 14.0432 | 13.5883 | 12.9474 | 12.0431 | 10.7647 |  | 91.4823 | 124.9064 | 167.2607 | 221.0253 | 289.3855 | 376.4345 | 487.4359 | 629.1624 | 810.3331 | 1042.1789 | 1339.1729 | 1719.974 | 2208.6474 | 2836.2424 | 3642.8332 | 4680.1576 | 6015.0308 | 7725.0817 | 7963.1403 | 7939.5609 | 7907.0477 | 7862.0328 | 7799.4788 | 7712.263 | 7590.2988 | 7419.2848 | 7178.92 | 6840.3574 | 6362.5687 | 5687.1529
| FALSE | 1329 | 22015532 | DDL | DDL-GLE NO.2 | 66 | GLE NO.2 LINE | DISTANCE & DIR EF | Y | GE | GE_D30 | GE D30 | GE RELAYS | Digital |  | 0.016937 | 1 |  | 0.96924 | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.0089997 |  | 5.0708 | 0.0089964 | 2.0873e-07 | 0.0089962 | 47.2313 | 0.02296 | 47.2543 | 25.5386 | 3.5995 | 0.015667 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.0089997 |  | 43.8921 | 76.408 | 43.8921 | 32.5159 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.4124e-07 | 2.0873e-07 | 3.1346e-07 | 4.773e-07 | 7.3543e-07 | 1.1446e-06 | 1.7968e-06 | 2.8408e-06 | 4.5187e-06 | 7.2241e-06 | 1.1599e-05 | 1.869e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 51.702 | 76.408 | 114.7451 | 174.7203 | 269.214 | 419.0101 | 657.7331 | 1039.9053 | 1654.1051 | 2644.4781 | 4245.9291 | 6841.7289 | 7998.5131 | 7998.5131 | 7998.5131 | 7998.5131 | 7998.5131 | 7998.5131 | 7998.5131 | 7998.5131 | 7998.5131 | 7998.5131 |  | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 43.8921 | 52.5361 | 69.6397 | 93.1177 | 125.491 | 170.3122 | 232.5969 | 319.4374 | 440.8768 | 611.1549 | 850.4853 | 1187.591 | 1663.3237 | 2335.8331 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 31.9594 | 47.2313 | 70.9293 | 108.0027 | 166.4137 | 259.0096 | 406.5754 | 642.8137 | 1022.479 | 1634.6746 | 2624.6057 | 4229.1899 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8277 | 20.0996 | 43.7976 | 80.871 | 139.2819 | 231.8778 | 379.4436 | 615.682 | 995.3473 | 1602.1996 | 2581.5582 | 4171.6296 | 4866.6801 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015536 | 0.02296 | 0.03448 | 0.052503 | 0.080898 | 0.12591 | 0.19765 | 0.31249 | 0.49705 | 0.79466 | 1.2759 | 2.0559 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015787 | 0.020926 | 0.027982 | 0.03771 | 0.051178 | 0.069894 | 0.09599 | 0.13248 | 0.18365 | 0.25557 | 0.35687 | 0.49982 | 0.70191 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0023469 | 0.0097709 | 0.021291 | 0.039313 | 0.067708 | 0.11272 | 0.18446 | 0.2993 | 0.48386 | 0.77887 | 1.255 | 2.0279 | 2.3658 | 2.3523 | 2.3336 | 2.3075 | 2.271 | 2.2199 | 2.148 | 2.0467 | 1.9037 | 1.7016 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.83 | 20.1094 | 43.8188 | 80.9103 | 139.3497 | 231.9905 | 379.6281 | 615.9813 | 995.8312 | 1602.9784 | 2582.8131 | 4173.6575 | 4869.0459 | 4841.3263 | 4802.8065 | 4749.1003 | 4673.9965 | 4568.6886 | 4420.6754 | 4212.1934 | 3917.978 | 3502.0667 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.2809 | 25.5386 | 38.3524 | 58.3984 | 89.982 | 140.0497 | 219.8404 | 347.5775 | 552.8673 | 883.8891 | 1419.1574 | 2286.7763 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6104 | 10.8681 | 23.6819 | 43.728 | 75.3115 | 125.3793 | 205.1699 | 332.907 | 538.1968 | 866.3295 | 1395.881 | 2255.6527 | 2631.4752 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4356 | 3.5995 | 5.4055 | 8.2308 | 12.6823 | 19.739 | 30.9849 | 48.9884 | 77.9225 | 124.5776 | 200.0196 | 322.304 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36791 | 1.5318 | 3.3378 | 6.1631 | 10.6146 | 17.6713 | 28.9172 | 46.9207 | 75.8548 | 122.1027 | 196.739 | 317.9173 | 370.8867 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.010601 | 0.015667 | 0.023527 | 0.035825 | 0.0552 | 0.085914 | 0.13486 | 0.21322 | 0.33916 | 0.54223 | 0.87059 | 1.4028 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 |  | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.0089997 | 0.010772 | 0.014279 | 0.019093 | 0.025731 | 0.034921 | 0.047692 | 0.065498 | 0.090398 | 0.12531 | 0.17438 | 0.2435 | 0.34105 | 0.47894 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016014 | 0.0066671 | 0.014528 | 0.026825 | 0.0462 | 0.076914 | 0.12586 | 0.20422 | 0.33016 | 0.53145 | 0.85631 | 1.3837 | 1.6143 | 1.6051 | 1.5923 | 1.5745 | 1.5496 | 1.5147 | 1.4656 | 1.3965 | 1.299 | 1.1611 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8099 | 32.5159 | 70.853 | 130.8282 | 225.3219 | 375.118 | 613.8411 | 996.0133 | 1610.213 | 2591.9421 | 4176.2894 | 6748.6112 | 7873.0221 | 7828.2009 | 7765.9162 | 7679.0757 | 7557.6363 | 7387.3582 | 7148.0278 | 6810.9221 | 6335.1894 | 5662.6799
| FALSE | 1330 | 22008411 | DDL | DDL-GLE NO.2 | 66 | GLE NO.2 LINE | DISTANCE & DIR EF | X | Schweitzer | SEL_311C | SEL 311C | SEL 300s | Digital |  | 0.15703 | 1 |  | 5.8543 | 0.012795 | 2.7522e-06 | 0.012792 | 67.1737 | 0.30275 | 67.4765 | 36.3349 | 5.1192 | 0.20658 |  | 13.88 | 0.12735 | 2.7393e-05 | 0.12732 | 668.5915 | 3.0133 | 671.6048 | 361.6477 | 50.9522 | 2.0561 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.083438 |  | 109.1372 | 1086.2607 | 44.0818 | 1042.1789 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 3.4187e-06 | 4.2616e-06 | 5.3296e-06 | 6.6855e-06 | 8.4094e-06 | 1.0605e-05 | 1.3404e-05 | 1.6978e-05 | 2.1547e-05 | 2.7393e-05 | 3.4883e-05 | 4.4486e-05 | 5.6809e-05 | 7.2636e-05 | 9.2977e-05 | 0.00011914 | 0.0001528 | 0.00019614 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 135.564 | 168.9882 | 211.3424 | 265.1071 | 333.4673 | 420.5163 | 531.5177 | 673.2441 | 854.4148 | 1086.2607 | 1383.2547 | 1764.0558 | 2252.7291 | 2880.3242 | 3686.915 | 4724.2393 | 6059.1126 | 7777.8448 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 | 8033.081 |  | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 44.0818 | 52.7631 | 69.9406 | 93.5201 | 126.0333 | 171.0482 | 233.6021 | 320.818 | 442.7821 | 613.7961 | 854.1609 | 1192.7235 | 1670.5122 | 2345.9281 |  | 83.4394 | 104.0119 | 130.0809 | 163.1729 | 205.2485 | 258.827 | 327.1482 | 414.3805 | 525.8908 | 668.5915 | 851.3908 | 1085.7731 | 1386.5507 | 1772.8343 | 2269.2895 | 2907.7607 | 3729.3728 | 4787.2493 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 56.3072 | 76.8797 | 102.9486 | 136.0407 | 178.1163 | 231.6948 | 300.0159 | 387.2483 | 498.7585 | 641.4592 | 824.2585 | 1058.6409 | 1359.4184 | 1745.7021 | 2242.1572 | 2880.6285 | 3702.2405 | 4754.7737 | 4901.2984 | 4886.7853 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.37605 | 0.46877 | 0.58626 | 0.7354 | 0.92503 | 1.1665 | 1.4744 | 1.8676 | 2.3701 | 3.0133 | 3.8371 | 4.8935 | 6.249 | 7.99 | 10.2275 | 13.105 | 16.8079 | 21.5756 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0.25377 | 0.34649 | 0.46398 | 0.61312 | 0.80275 | 1.0442 | 1.3521 | 1.7453 | 2.2479 | 2.891 | 3.7148 | 4.7712 | 6.1268 | 7.8677 | 10.1052 | 12.9827 | 16.6856 | 21.4293 | 22.0897 | 22.0242 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 56.5609 | 77.2261 | 103.4126 | 136.6538 | 178.919 | 232.739 | 301.3681 | 388.9936 | 501.0064 | 644.3502 | 827.9734 | 1063.4121 | 1365.5452 | 1753.5698 | 2252.2624 | 2893.6112 | 3718.9262 | 4776.203 | 4923.388 | 4908.8095 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 45.1332 | 56.2611 | 70.362 | 88.2618 | 111.0209 | 140.0021 | 176.9576 | 224.1425 | 284.4594 | 361.6477 | 460.5256 | 587.3053 | 749.9988 | 958.9434 | 1227.4808 | 1572.8361 | 2017.2541 | 2589.4698 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 30.4571 | 41.585 | 55.6859 | 73.5857 | 96.3448 | 125.326 | 162.2815 | 209.4664 | 269.7834 | 346.9716 | 445.8495 | 572.6292 | 735.3227 | 944.2673 | 1212.8047 | 1558.16 | 2002.578 | 2571.9034 | 2651.16 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 6.3588 | 7.9266 | 9.9132 | 12.4351 | 15.6416 | 19.7248 | 24.9314 | 31.5792 | 40.0772 | 50.9522 | 64.883 | 82.7449 | 105.6667 | 135.1047 | 172.9387 | 221.5955 | 284.2091 | 364.8281 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 4.2911 | 5.8589 | 7.8455 | 10.3674 | 13.5739 | 17.6571 | 22.8637 | 29.5115 | 38.0095 | 48.8845 | 62.8153 | 80.6772 | 103.599 | 133.037 | 170.871 | 219.5278 | 282.1414 | 362.3532 | 373.5196 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.2566 | 0.31986 | 0.40003 | 0.5018 | 0.63119 | 0.79595 | 1.0061 | 1.2743 | 1.6172 | 2.0561 | 2.6182 | 3.339 | 4.264 | 5.4519 | 6.9786 | 8.9421 | 11.4687 | 14.7219 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 | 15.205 |  | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.083438 | 0.09987 | 0.13238 | 0.17702 | 0.23856 | 0.32376 | 0.44216 | 0.60725 | 0.8381 | 1.1618 | 1.6168 | 2.2576 | 3.1619 | 4.4404 |  | 0.17316 | 0.23642 | 0.31659 | 0.41836 | 0.54775 | 0.71252 | 0.92262 | 1.1909 | 1.5338 | 1.9726 | 2.5348 | 3.2556 | 4.1805 | 5.3684 | 6.8952 | 8.8586 | 11.3853 | 14.6221 | 15.0727 | 15.028 | 14.9665 | 14.8813 | 14.7629 | 14.5978 | 14.3669 | 14.0432 | 13.5883 | 12.9474 | 12.0431 | 10.7647 |  | 91.4823 | 124.9064 | 167.2607 | 221.0253 | 289.3855 | 376.4345 | 487.4359 | 629.1624 | 810.3331 | 1042.1789 | 1339.1729 | 1719.974 | 2208.6474 | 2836.2424 | 3642.8332 | 4680.1576 | 6015.0308 | 7725.0817 | 7963.1403 | 7939.5609 | 7907.0477 | 7862.0328 | 7799.4788 | 7712.263 | 7590.2988 | 7419.2848 | 7178.92 | 6840.3574 | 6362.5687 | 5687.1529
| TRUE | 1442 | 22008362 | ECA | Blank | 22 | BUS ALL | OV-UV SUPERVISION | C | RMS | 2V67 | 2V67 | 2V6X | Digital |  | 0 | 1 |  | 5.5 | 0.010964 | 0 | 0.010964 | 45.2259 | 0 | 45.2259 | 31.1222 | 4.3866 | 0 |  | 11.7751 | 0.080727 | 0 | 0.080727 | 332.9985 | 0 | 332.9985 | 229.1527 | 32.2988 | 0 |  | 0.0051679 | 0 | 0.0051679 | 21.3177 | 0 | 21.3177 | 14.6698 | 2.0677 | 0 |  | 80.7347 | 594.45 | 38.0552 | 556.3948 |  | 0.076124 |  | 5.935 | 6.4045 | 6.911 | 7.4577 | 8.0475 | 8.6841 | 9.3709 | 10.1121 | 10.912 | 11.7751 | 12.7064 | 13.7115 | 14.796 | 15.9663 | 17.2292 | 18.5919 | 20.0625 | 21.6493 | 23.3617 | 25.2095 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.013239 | 0.016034 | 0.019473 | 0.023709 | 0.028935 | 0.035391 | 0.043377 | 0.053265 | 0.065521 | 0.080727 | 0.099611 | 0.12308 | 0.15228 | 0.18862 | 0.23389 | 0.29032 | 0.36069 | 0.44851 | 0.55815 | 0.6951 | 0.86622 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4903 | 118.0711 | 143.3902 | 174.5845 | 213.0701 | 260.6129 | 319.4151 | 392.2252 | 482.4747 | 594.45 | 733.5078 | 906.3446 | 1121.335 | 1388.9559 | 1722.3182 | 2137.834 | 2656.0532 | 3302.7137 | 4110.0579 | 5118.4865 | 6378.632 | 6934.8537 | 6934.8537 | 6934.8537 | 6934.8537 | 6934.8537 | 6934.8537 | 6934.8537 | 6934.8537 | 6934.8537 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 54.612 | 66.141 | 80.3242 | 97.7986 | 119.3574 | 145.9899 | 178.9297 | 219.7164 | 270.2722 | 332.9985 | 410.8958 | 507.7153 | 628.1485 | 778.0641 | 964.8067 | 1197.57 | 1487.8656 | 1850.1112 | 2302.3686 | 2867.2693 | 3573.1765 | 3884.7603 | 3884.7603 | 3884.7603 | 3884.7603 | 3884.7603 | 3884.7603 | 3884.7603 | 3884.7603 | 3884.7603 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 40.4002 | 51.9292 | 66.1124 | 83.5867 | 105.1456 | 131.7781 | 164.7179 | 205.5045 | 256.0604 | 318.7867 | 396.6839 | 493.5035 | 613.9366 | 763.8523 | 950.5949 | 1183.3581 | 1473.6538 | 1833.1006 | 2279.82 | 2837.1187 | 3532.5437 | 3829.6149 | 3809.4477 | 3781.3296 | 3742.0087 | 3686.8743 | 3609.3815 | 3500.23 | 3346.1924 | 3128.4404 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40.4002 | 51.9292 | 66.1124 | 83.5867 | 105.1456 | 131.7781 | 164.7179 | 205.5045 | 256.0604 | 318.7867 | 396.6839 | 493.5035 | 613.9366 | 763.8523 | 950.5949 | 1183.3581 | 1473.6538 | 1833.1006 | 2279.82 | 2837.1187 | 3532.5437 | 3829.6149 | 3809.4477 | 3781.3296 | 3742.0087 | 3686.8743 | 3609.3815 | 3500.23 | 3346.1924 | 3128.4404 |  | 37.5812 | 45.5149 | 55.2751 | 67.3 | 82.1357 | 100.4629 | 123.1303 | 151.1977 | 185.9877 | 229.1527 | 282.7577 | 349.384 | 432.26 | 535.4243 | 663.9311 | 824.107 | 1023.8737 | 1273.1528 | 1584.3735 | 1973.1095 | 2458.879 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 22.9115 | 30.8451 | 40.6053 | 52.6302 | 67.466 | 85.7931 | 108.4606 | 136.5279 | 171.3179 | 214.4829 | 268.0879 | 334.7142 | 417.5902 | 520.7545 | 649.2613 | 809.4372 | 1009.2039 | 1255.594 | 1561.0982 | 1941.9873 | 2416.9369 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 5.297 | 6.4153 | 7.791 | 9.4859 | 11.5769 | 14.1601 | 17.3551 | 21.3112 | 26.2148 | 32.2988 | 39.8544 | 49.2453 | 60.9266 | 75.4675 | 93.5804 | 116.157 | 144.3139 | 179.4496 | 223.3158 | 278.1077 | 346.5765 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 3.2293 | 4.3476 | 5.7233 | 7.4182 | 9.5093 | 12.0924 | 15.2874 | 19.2435 | 24.1471 | 30.2311 | 37.7867 | 47.1776 | 58.8589 | 73.3998 | 91.5127 | 114.0893 | 142.2463 | 176.9747 | 220.0352 | 273.7211 | 340.6648 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 66.541 | 87.1218 | 112.4409 | 143.6352 | 182.1208 | 229.6636 | 288.4658 | 361.2759 | 451.5254 | 563.5007 | 702.5585 | 875.3953 | 1090.3857 | 1358.0066 | 1691.3689 | 2106.8847 | 2625.1039 | 3265.6693 | 4060.9534 | 5052.8271 | 6290.1455 | 6814.7627 | 6770.8443 | 6709.6111 | 6623.9815 | 6503.9145 | 6335.1572 | 6097.4563 | 5762.0063 | 5287.8046
| FALSE | 1443 | 22014611 | ECA | Blank | 22 | BUS ALL | VOLTAGE REGULATION | C | RMS | 2V164S | 2V164 S | 2V164S | Digital |  | 0 | 1 |  | 1.1573 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 3.8384 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 30.9493 | 30.9493 | 0 |  | 0.11989 |  | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 125.7409 | 175.3373 | 245.2282 | 343.8976 | 483.4225 | 681.0073 | 961.1761 | 1358.9071 | 1924.1147 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 125.7409 | 175.3373 | 245.2282 | 343.8976 | 483.4225 | 681.0073 | 961.1761 | 1358.9071 | 1924.1147 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 129.7928 | 180.9874 | 253.1305 | 354.9794 | 499.0003 | 702.9521 | 992.149 | 1402.6966 | 1986.1174 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.2942 | 25.51 | 35.6785 | 50.034 | 70.3336 | 99.0804 | 139.8424 | 197.7086 | 279.9412 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 133.0601 | 194.2933 | 273.8279 | 381.8347 | 534.0372 | 748.9109 | 1052.7564 | 1483.0397 | 2093.1675 | 2959.3123 | 4190.1734 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 1444 | 22015762 | ECA | Blank | 22 | CAP NO.1 | NEUTRAL BALANCE | X | Siemens | 7SR11 | 7SR11 | SIEMENS 7SR11 | Digital |  | 0.2894 | 1 |  | 1.0266 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 1.8365 |  | 3.4047 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 1.8365 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 1.8365 |  | 32.9414 | 32.9414 | 32.9414 | 0 |  | 0.11989 |  | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 |  | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.4522e-06 | 3.2506e-06 | 4.3465e-06 | 5.8575e-06 | 7.9497e-06 | 1.0857e-05 | 1.491e-05 | 2.0579e-05 | 2.8527e-05 | 3.9698e-05 | 5.5433e-05 | 7.7639e-05 | 0.00010903 | 0.00015347 | 0.00021648 | 0.0003059 | 0.00037335 | 0.00037335 | 0.00037335 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 39.4288 | 52.2652 | 69.8856 | 94.182 | 127.8208 | 174.566 | 239.7406 | 330.8818 | 458.677 | 638.2966 | 891.2974 | 1248.3389 | 1753.063 | 2467.6368 | 3480.6732 | 4918.555 | 6002.9535 | 6002.9535 | 6002.9535 |  | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 39.4288 | 52.2652 | 69.8856 | 94.182 | 127.8208 | 174.566 | 239.7406 | 330.8818 | 458.677 | 638.2966 | 891.2974 | 1248.3389 | 1753.063 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 | 1064.649 | 1501.7182 | 2122.0848 | 2589.9429 | 2589.9429 | 2589.9429 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7989 | 8.3371 | 15.9394 | 26.422 | 40.9352 | 61.1032 | 86.4235 | 120.2077 | 167.742 | 234.7554 | 329.398 | 463.2737 | 652.9151 | 921.8917 | 1303.8244 | 1846.6951 | 2205.3973 | 2051.3536 | 1833.593 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 | 10.743 | 15.1534 | 21.4133 | 26.1343 | 26.1343 | 26.1343 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028243 | 0.084128 | 0.16084 | 0.26662 | 0.41306 | 0.61657 | 0.87207 | 1.213 | 1.6926 | 2.3688 | 3.3239 | 4.6747 | 6.5884 | 9.3025 | 13.1565 | 18.6344 | 22.254 | 20.6996 | 18.5022 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8272 | 8.4213 | 16.1002 | 26.6886 | 41.3483 | 61.7198 | 87.2955 | 121.4207 | 169.4347 | 237.1242 | 332.7218 | 467.9484 | 659.5034 | 931.1943 | 1316.9809 | 1865.3295 | 2227.6513 | 2072.0532 | 1852.0952 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 | 1099.784 | 1551.2772 | 2192.1168 | 2675.4148 | 2675.4148 | 2675.4148 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8913 | 8.6123 | 16.4654 | 27.2939 | 42.2861 | 63.1197 | 89.2756 | 124.1747 | 173.2778 | 242.5027 | 340.2686 | 478.5624 | 674.4622 | 952.3155 | 1346.8526 | 1907.6388 | 2278.1786 | 2119.0513 | 1894.1043 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 | 154.8921 | 218.4799 | 308.7349 | 376.8019 | 376.8019 | 376.8019 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.9555 | 8.8897 | 12.5735 | 17.4886 | 24.4042 | 34.1538 | 47.923 | 67.4001 | 94.9904 | 134.1229 | 189.689 | 268.6694 | 320.8557 | 298.4444 | 266.7632 |  | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 2.1981 | 2.9137 | 3.8961 | 5.2506 | 7.1259 | 9.7319 | 13.3653 | 18.4464 | 25.5709 | 35.5845 | 49.6891 | 69.5938 | 97.7318 | 137.5687 | 194.0446 | 274.2053 | 334.6596 | 334.6596 | 334.6596 |  | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 2.1981 | 2.9137 | 3.8961 | 5.2506 | 7.1259 | 9.7319 | 13.3653 | 18.4464 | 25.5709 | 35.5845 | 49.6891 | 69.5938 | 97.7318 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36167 | 1.0773 | 2.0596 | 3.4141 | 5.2894 | 7.8955 | 11.1672 | 15.5326 | 21.6748 | 30.3339 | 42.5632 | 59.8619 | 84.3664 | 119.1223 | 168.4737 | 238.6208 | 284.9705 | 265.0657 | 236.9278 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4874 | 19.3238 | 36.9442 | 61.2407 | 94.8794 | 141.6246 | 200.3118 | 278.6167 | 388.7914 | 544.1146 | 763.4766 | 1073.7729 | 1513.3225 | 2136.755 | 3021.9962 | 4280.2584 | 5111.6561 | 4754.6146 | 4249.8904
| FALSE | 1445 | 22015763 | ECA | Blank | 22 | CAP NO.1 | OC & EF | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0.2894 | 1 |  | 1.0266 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 1.8365 |  | 3.4047 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 1.8365 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 1.8365 |  | 32.9414 | 32.9414 | 32.9414 | 0 |  | 0.11989 |  | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 |  | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.4522e-06 | 3.2506e-06 | 4.3465e-06 | 5.8575e-06 | 7.9497e-06 | 1.0857e-05 | 1.491e-05 | 2.0579e-05 | 2.8527e-05 | 3.9698e-05 | 5.5433e-05 | 7.7639e-05 | 0.00010903 | 0.00015347 | 0.00021648 | 0.0003059 | 0.00037335 | 0.00037335 | 0.00037335 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 39.4288 | 52.2652 | 69.8856 | 94.182 | 127.8208 | 174.566 | 239.7406 | 330.8818 | 458.677 | 638.2966 | 891.2974 | 1248.3389 | 1753.063 | 2467.6368 | 3480.6732 | 4918.555 | 6002.9535 | 6002.9535 | 6002.9535 |  | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 39.4288 | 52.2652 | 69.8856 | 94.182 | 127.8208 | 174.566 | 239.7406 | 330.8818 | 458.677 | 638.2966 | 891.2974 | 1248.3389 | 1753.063 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 | 1064.649 | 1501.7182 | 2122.0848 | 2589.9429 | 2589.9429 | 2589.9429 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7989 | 8.3371 | 15.9394 | 26.422 | 40.9352 | 61.1032 | 86.4235 | 120.2077 | 167.742 | 234.7554 | 329.398 | 463.2737 | 652.9151 | 921.8917 | 1303.8244 | 1846.6951 | 2205.3973 | 2051.3536 | 1833.593 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 | 10.743 | 15.1534 | 21.4133 | 26.1343 | 26.1343 | 26.1343 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028243 | 0.084128 | 0.16084 | 0.26662 | 0.41306 | 0.61657 | 0.87207 | 1.213 | 1.6926 | 2.3688 | 3.3239 | 4.6747 | 6.5884 | 9.3025 | 13.1565 | 18.6344 | 22.254 | 20.6996 | 18.5022 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8272 | 8.4213 | 16.1002 | 26.6886 | 41.3483 | 61.7198 | 87.2955 | 121.4207 | 169.4347 | 237.1242 | 332.7218 | 467.9484 | 659.5034 | 931.1943 | 1316.9809 | 1865.3295 | 2227.6513 | 2072.0532 | 1852.0952 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 | 1099.784 | 1551.2772 | 2192.1168 | 2675.4148 | 2675.4148 | 2675.4148 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8913 | 8.6123 | 16.4654 | 27.2939 | 42.2861 | 63.1197 | 89.2756 | 124.1747 | 173.2778 | 242.5027 | 340.2686 | 478.5624 | 674.4622 | 952.3155 | 1346.8526 | 1907.6388 | 2278.1786 | 2119.0513 | 1894.1043 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 | 154.8921 | 218.4799 | 308.7349 | 376.8019 | 376.8019 | 376.8019 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.9555 | 8.8897 | 12.5735 | 17.4886 | 24.4042 | 34.1538 | 47.923 | 67.4001 | 94.9904 | 134.1229 | 189.689 | 268.6694 | 320.8557 | 298.4444 | 266.7632 |  | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 2.1981 | 2.9137 | 3.8961 | 5.2506 | 7.1259 | 9.7319 | 13.3653 | 18.4464 | 25.5709 | 35.5845 | 49.6891 | 69.5938 | 97.7318 | 137.5687 | 194.0446 | 274.2053 | 334.6596 | 334.6596 | 334.6596 |  | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 2.1981 | 2.9137 | 3.8961 | 5.2506 | 7.1259 | 9.7319 | 13.3653 | 18.4464 | 25.5709 | 35.5845 | 49.6891 | 69.5938 | 97.7318 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36167 | 1.0773 | 2.0596 | 3.4141 | 5.2894 | 7.8955 | 11.1672 | 15.5326 | 21.6748 | 30.3339 | 42.5632 | 59.8619 | 84.3664 | 119.1223 | 168.4737 | 238.6208 | 284.9705 | 265.0657 | 236.9278 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4874 | 19.3238 | 36.9442 | 61.2407 | 94.8794 | 141.6246 | 200.3118 | 278.6167 | 388.7914 | 544.1146 | 763.4766 | 1073.7729 | 1513.3225 | 2136.755 | 3021.9962 | 4280.2584 | 5111.6561 | 4754.6146 | 4249.8904
| TRUE | 1446 | 22002634 | ECA | Blank | 22 | CAP NO.1&3 | CAP CONTROL | C | Siemens | DED_760 | DED 760 | DED | Electronic |  | 0 | 2190 |  | 6.6 | 0.014726 | 0 | 0.014726 | 80.9933 | 0 | 80.9933 | 41.8016 | 5.8919 | 0 |  | 10.9462 | 0.056226 | 0 | 0.056226 | 309.2436 | 0 | 309.2436 | 159.6043 | 22.4961 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 128.6867 | 491.344 | 45.1611 | 446.1828 |  | 0.050592 |  | 6.9425 | 7.3028 | 7.6817 | 8.0804 | 8.4997 | 8.9408 | 9.4048 | 9.8928 | 10.4062 | 10.9462 | 11.5143 | 12.1118 | 12.7403 | 13.4015 | 14.0969 | 14.8285 | 15.598 | 16.4074 | 17.2589 | 18.1545 | 19.0966 | 20.0876 | 21.1301 | 22.2266 | 23.38 | 24.5933 | 25.8696 | 27.212 | 28 | 28 |  | 0.016762 | 0.019102 | 0.021791 | 0.024884 | 0.028444 | 0.032543 | 0.037265 | 0.042708 | 0.048985 | 0.056226 | 0.064584 | 0.074234 | 0.08538 | 0.09826 | 0.11315 | 0.13036 | 0.15027 | 0.17331 | 0.19998 | 0.23085 | 0.26659 | 0.30799 | 0.35596 | 0.41154 | 0.47596 | 0.55065 | 0.63725 | 0.73768 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.4821 | 166.9258 | 190.4264 | 217.4568 | 248.5648 | 284.3845 | 325.651 | 373.2156 | 428.0652 | 491.344 | 564.3781 | 648.7059 | 746.1114 | 858.6642 | 988.7656 | 1139.2019 | 1313.2071 | 1514.5348 | 1747.5427 | 2017.2901 | 2329.6518 | 2691.4502 | 3110.6093 | 3596.3327 | 4159.3126 | 4811.9703 | 5568.7383 | 6446.3865 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 92.1934 | 105.0603 | 119.8511 | 136.8636 | 156.4424 | 178.9868 | 204.9592 | 234.8956 | 269.417 | 309.2436 | 355.21 | 408.2845 | 469.5899 | 540.4287 | 622.3123 | 716.9944 | 826.5103 | 953.2226 | 1099.8738 | 1269.6483 | 1466.2434 | 1693.9532 | 1957.7648 | 2263.471 | 2617.801 | 3028.5727 | 3504.8697 | 4057.2466 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 77.9815 | 90.8485 | 105.6393 | 122.6518 | 142.2306 | 164.775 | 190.7474 | 220.6838 | 255.2052 | 295.0317 | 340.9982 | 394.0727 | 455.3781 | 526.2169 | 608.1005 | 702.7826 | 812.2985 | 936.2119 | 1077.3252 | 1239.4977 | 1425.6107 | 1638.8078 | 1882.4522 | 2160.0403 | 2475.0494 | 2830.6867 | 3229.4908 | 3672.7162 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 77.9815 | 90.8485 | 105.6393 | 122.6518 | 142.2306 | 164.775 | 190.7474 | 220.6838 | 255.2052 | 295.0317 | 340.9982 | 394.0727 | 455.3781 | 526.2169 | 608.1005 | 702.7826 | 812.2985 | 936.2119 | 1077.3252 | 1239.4977 | 1425.6107 | 1638.8078 | 1882.4522 | 2160.0403 | 2475.0494 | 2830.6867 | 3229.4908 | 3672.7162 | 3868.4608 | 3650.7088 |  | 47.5821 | 54.2229 | 61.8566 | 70.637 | 80.7418 | 92.3772 | 105.7819 | 121.2324 | 139.0494 | 159.6043 | 183.3282 | 210.7205 | 242.361 | 278.9218 | 321.1829 | 370.0494 | 426.5719 | 491.9696 | 567.6581 | 655.2807 | 756.7458 | 874.2696 | 1010.4259 | 1168.2045 | 1351.0785 | 1563.0827 | 1808.9053 | 2093.9937 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 32.9123 | 39.5531 | 47.1868 | 55.9672 | 66.072 | 77.7075 | 91.1121 | 106.5626 | 124.3796 | 144.9345 | 168.6584 | 196.0508 | 227.6912 | 264.252 | 306.5131 | 355.3796 | 411.9021 | 474.4108 | 544.3828 | 624.1585 | 714.8037 | 817.3472 | 932.6865 | 1061.4409 | 1203.7269 | 1358.8201 | 1524.6527 | 1697.0722 | 1718.5977 | 1493.8289 |  | 6.7066 | 7.6427 | 8.7186 | 9.9562 | 11.3805 | 13.0205 | 14.9099 | 17.0876 | 19.5989 | 22.4961 | 25.8399 | 29.7008 | 34.1605 | 39.3137 | 45.2704 | 52.1581 | 60.1249 | 69.3426 | 80.0108 | 92.3611 | 106.6625 | 123.2274 | 142.4185 | 164.6572 | 190.4331 | 220.3149 | 254.9633 | 295.1462 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 4.639 | 5.575 | 6.6509 | 7.8885 | 9.3128 | 10.9528 | 12.8422 | 15.0199 | 17.5312 | 20.4284 | 23.7722 | 27.6332 | 32.0928 | 37.246 | 43.2027 | 50.0904 | 58.0572 | 66.8677 | 76.7302 | 87.9745 | 100.7508 | 115.2042 | 131.4612 | 149.609 | 169.6641 | 191.5243 | 214.8982 | 239.2006 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 115.5328 | 135.9765 | 159.4771 | 186.5075 | 217.6155 | 253.4352 | 294.7017 | 342.2663 | 397.1159 | 460.3947 | 533.4288 | 617.7566 | 715.1621 | 827.7149 | 957.8163 | 1108.2526 | 1282.2578 | 1477.4905 | 1698.4382 | 1951.6307 | 2241.1653 | 2571.3593 | 2946.5999 | 3371.0902 | 3848.4403 | 4381.0311 | 4969.0417 | 5608.989 | 5829.293 | 5355.0913
| FALSE | 1447 | 22015546 | ECA | Blank | 22 | CAP NO.3 | OC & EF | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0.2894 | 1 |  | 0.8077 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 1.8365 |  | 2.6788 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 1.8365 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 1.8365 |  | 32.9414 | 32.9414 | 32.9414 | 0 |  | 0.11989 |  | 0.91058 | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 |  | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.4522e-06 | 3.2506e-06 | 4.3465e-06 | 5.8575e-06 | 7.9497e-06 | 1.0857e-05 | 1.491e-05 | 2.0579e-05 | 2.8527e-05 | 3.9698e-05 | 5.5433e-05 | 7.7639e-05 | 0.00010903 | 0.00015347 | 0.00021648 | 0.0003059 | 0.00037335 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 39.4288 | 52.2652 | 69.8856 | 94.182 | 127.8208 | 174.566 | 239.7406 | 330.8818 | 458.677 | 638.2966 | 891.2974 | 1248.3389 | 1753.063 | 2467.6368 | 3480.6732 | 4918.555 | 6002.9535 |  | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 32.9414 | 39.4288 | 52.2652 | 69.8856 | 94.182 | 127.8208 | 174.566 | 239.7406 | 330.8818 | 458.677 | 638.2966 | 891.2974 | 1248.3389 | 1753.063 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 | 1064.649 | 1501.7182 | 2122.0848 | 2589.9429 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7989 | 8.3371 | 15.9394 | 26.422 | 38.1363 | 52.7661 | 73.283 | 102.1229 | 142.7462 | 200.0741 | 281.1108 | 395.832 | 558.4561 | 789.2593 | 1117.1726 | 1583.4955 | 1833.593 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 | 10.743 | 15.1534 | 21.4133 | 26.1343 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028243 | 0.084128 | 0.16084 | 0.26662 | 0.38482 | 0.53245 | 0.73948 | 1.0305 | 1.4404 | 2.0189 | 2.8366 | 3.9942 | 5.6352 | 7.9642 | 11.273 | 15.9786 | 18.5022 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8272 | 8.4213 | 16.1002 | 26.6886 | 38.5211 | 53.2985 | 74.0225 | 103.1534 | 144.1866 | 202.093 | 283.9474 | 399.8262 | 564.0913 | 797.2234 | 1128.4457 | 1599.4741 | 1852.0952 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 | 1099.784 | 1551.2772 | 2192.1168 | 2675.4148 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8913 | 8.6123 | 16.4654 | 27.2939 | 39.3948 | 54.5074 | 75.7015 | 105.4931 | 147.457 | 206.6769 | 290.3878 | 408.8951 | 576.8859 | 815.306 | 1154.041 | 1635.7532 | 1894.1043 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 | 154.8921 | 218.4799 | 308.7349 | 376.8019 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.5483 | 7.6768 | 10.6617 | 14.8575 | 20.7677 | 29.1081 | 40.8978 | 57.5882 | 81.2479 | 114.8266 | 162.5336 | 230.3774 | 266.7632 |  | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 2.1981 | 2.9137 | 3.8961 | 5.2506 | 7.1259 | 9.7319 | 13.3653 | 18.4464 | 25.5709 | 35.5845 | 49.6891 | 69.5938 | 97.7318 | 137.5687 | 194.0446 | 274.2053 | 334.6596 |  | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 1.8365 | 2.1981 | 2.9137 | 3.8961 | 5.2506 | 7.1259 | 9.7319 | 13.3653 | 18.4464 | 25.5709 | 35.5845 | 49.6891 | 69.5938 | 97.7318 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36167 | 1.0773 | 2.0596 | 3.4141 | 4.9278 | 6.8182 | 9.4693 | 13.1958 | 18.445 | 25.8526 | 36.3237 | 51.1475 | 72.1609 | 101.9842 | 144.3555 | 204.6114 | 236.9278 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4874 | 19.3238 | 36.9442 | 61.2407 | 88.392 | 122.3008 | 169.8549 | 236.6998 | 330.8563 | 463.7306 | 651.5568 | 917.457 | 1294.386 | 1829.3402 | 2589.3758 | 3670.2161 | 4249.8904
| TRUE | 1448 | 22008261 | ECA | Blank | 22 | ALL FEEDERS | MASTER EARTH FAULT | X | RMS | 2C137 | RMS - 2C137 | RMS 2C13X | Electronic |  | 0.81881 | 2190 |  | 6.6 | 0.014726 | 0.011754 | 0.0029722 | 65.5934 | 1645.5384 | 1711.1318 | 108.5309 | 6.0094 | 10535.8695 |  | 14.9721 | 0.13394 | 0.1069 | 0.027033 | 596.58 | 14966.3702 | 15562.9501 | 987.1017 | 54.6565 | 95825.0039 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 21.3201 | 0.81153 | 22.1317 | 14.7027 | 2.0677 | 5.196 |  | 12361.5416 | 112429.7122 | 44.0981 | 112385.6141 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.018172 | 0.022489 | 0.027904 | 0.034708 | 0.043268 | 0.05405 | 0.067647 | 0.084812 | 0.1065 | 0.13394 | 0.16866 | 0.21265 | 0.26843 | 0.33918 | 0.42899 | 0.54305 | 0.688 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.014504 | 0.01795 | 0.022272 | 0.027703 | 0.034535 | 0.043141 | 0.053994 | 0.067694 | 0.085006 | 0.1069 | 0.13462 | 0.16973 | 0.21425 | 0.27072 | 0.3424 | 0.43345 | 0.54914 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 15254.2696 | 18877.82 | 23423.8443 | 29135.3785 | 36320.8111 | 45371.6809 | 56785.3611 | 71193.9786 | 89401.2898 | 112429.7122 | 141580.32 | 178509.3906 | 225326.0846 | 284717.1109 | 360105.8559 | 455855.5299 | 577528.5365 | 672619.7608 | 672619.7608 | 672619.7608 | 672619.7608 | 672619.7608 | 672619.7608 | 672619.7608 | 672619.7608 | 672619.7608 | 672619.7608 | 672619.7608 | 672619.7608 | 672619.7608 |  | 37.0002 | 37.0002 | 37.0002 | 37.0002 | 37.0002 | 37.0002 | 37.0002 | 37.0002 | 37.0002 | 37.0002 | 37.0002 | 37.0002 | 37.0002 | 37.0002 | 37.0002 | 37.0002 | 37.0002 | 44.2869 | 58.7049 | 78.4964 | 105.7864 | 143.5698 | 196.0746 | 269.2794 | 371.6504 | 515.1915 | 716.9423 | 1001.1157 | 1402.149 | 1969.0611 |  | 80.9429 | 100.1704 | 124.2927 | 154.5995 | 192.7272 | 240.7534 | 301.3172 | 377.7729 | 474.3854 | 596.58 | 751.2603 | 947.2151 | 1195.6361 | 1510.7797 | 1910.811 | 2418.8826 | 3064.5098 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 66.7295 | 85.957 | 110.0793 | 140.3861 | 178.5138 | 226.54 | 287.1038 | 363.5595 | 460.172 | 582.3665 | 737.0469 | 933.0017 | 1181.4227 | 1496.5662 | 1896.5976 | 2404.6692 | 3050.2963 | 3552.0748 | 3546.5362 | 3538.9334 | 3528.4501 | 3513.9358 | 3493.7663 | 3465.6451 | 3426.3198 | 3371.1792 | 3293.6777 | 3184.5139 | 3030.4591 | 2812.6827 |  | 2030.6113 | 2512.9695 | 3118.1253 | 3878.4308 | 4834.9382 | 6039.7679 | 7559.1293 | 9477.1695 | 11900.8825 | 14966.3702 | 18846.8283 | 23762.7365 | 29994.861 | 37900.8502 | 47936.4168 | 60682.3808 | 76879.1959 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 |  | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.97135 | 1.2876 | 1.7217 | 2.3202 | 3.1489 | 4.3005 | 5.9062 | 8.1515 | 11.2998 | 15.7249 | 21.9577 | 30.7536 | 43.1878 |  | 2029.7998 | 2512.158 | 3117.3137 | 3877.6193 | 4834.1266 | 6038.9564 | 7558.3178 | 9476.358 | 11900.071 | 14965.5586 | 18846.0167 | 23761.9249 | 29994.0495 | 37900.0387 | 47935.6053 | 60681.5693 | 76878.3844 | 89536.5373 | 89536.2211 | 89535.787 | 89535.1884 | 89534.3597 | 89533.2081 | 89531.6025 | 89529.3572 | 89526.2089 | 89521.7838 | 89515.551 | 89506.755 | 89494.3208 |  | 2096.5293 | 2598.115 | 3227.393 | 4018.0054 | 5012.6404 | 6265.4964 | 7845.4216 | 9839.9175 | 12360.243 | 15547.9252 | 19583.0636 | 24694.9266 | 31175.4722 | 39396.6049 | 49832.2029 | 63086.2384 | 79928.6807 | 93088.6121 | 93082.7573 | 93074.7204 | 93063.6385 | 93048.2955 | 93026.9745 | 92997.2476 | 92955.677 | 92897.3881 | 92815.4615 | 92700.0649 | 92537.2141 | 92307.0035 |  | 133.9283 | 165.742 | 205.6549 | 255.8005 | 318.8866 | 398.3508 | 498.5597 | 625.0634 | 784.9185 | 987.1017 | 1243.0359 | 1567.2629 | 1978.3005 | 2499.7372 | 3161.6295 | 4002.285 | 5070.5402 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 119.2256 | 151.0393 | 190.9522 | 241.0978 | 304.1839 | 383.6481 | 483.857 | 610.3607 | 770.2158 | 972.399 | 1228.3332 | 1552.5602 | 1963.5978 | 2485.0345 | 3146.9268 | 3987.5823 | 5055.8375 | 5887.8166 | 5882.0873 | 5874.2228 | 5863.3786 | 5848.3647 | 5827.5009 | 5798.4116 | 5757.7326 | 5700.6939 | 5620.5245 | 5507.6029 | 5348.2449 | 5122.9719 |  | 7.4157 | 9.1772 | 11.3872 | 14.1638 | 17.657 | 22.057 | 27.6056 | 34.6102 | 43.4615 | 54.6565 | 68.8277 | 86.7804 | 109.5398 | 138.4122 | 175.0616 | 221.6092 | 280.7593 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 5.3479 | 7.1095 | 9.3195 | 12.0961 | 15.5892 | 19.9892 | 25.5378 | 32.5424 | 41.3937 | 52.5887 | 66.76 | 84.7127 | 107.4721 | 136.3444 | 172.9938 | 219.5415 | 278.6915 | 324.5119 | 323.7061 | 322.6001 | 321.075 | 318.9635 | 316.0292 | 311.9382 | 306.2172 | 298.1954 | 286.9206 | 271.0396 | 248.6279 | 216.9461 |  | 13001.3714 | 16089.7608 | 19964.3842 | 24832.3838 | 30956.6021 | 38670.7518 | 48398.7492 | 60679.3626 | 76197.6418 | 95825.0039 | 120670.3677 | 152145.3957 | 192047.7472 | 242667.3317 | 306921.937 | 388530.3723 | 492233.5313 | 573280.7631 | 573280.7631 | 573280.7631 | 573280.7631 | 573280.7631 | 573280.7631 | 573280.7631 | 573280.7631 | 573280.7631 | 573280.7631 | 573280.7631 | 573280.7631 | 573280.7631 |  | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 6.2193 | 8.244 | 11.0234 | 14.8557 | 20.1617 | 27.5351 | 37.8153 | 52.1914 | 72.3491 | 100.6813 | 140.5882 | 196.906 | 276.5183 |  | 12996.1754 | 16084.5648 | 19959.1882 | 24827.1878 | 30951.4061 | 38665.5558 | 48393.5532 | 60674.1666 | 76192.4459 | 95819.8079 | 120665.1717 | 152140.1997 | 192042.5512 | 242662.1357 | 306916.7411 | 388525.1763 | 492228.3354 | 573274.5438 | 573272.5191 | 573269.7397 | 573265.9073 | 573260.6013 | 573253.228 | 573242.9477 | 573228.5716 | 573208.4139 | 573180.0817 | 573140.1748 | 573083.8571 | 573004.2447 |  | 15217.2782 | 18840.8287 | 23386.8529 | 29098.3871 | 36283.8197 | 45334.6895 | 56748.3697 | 71156.9872 | 89364.2984 | 112392.7208 | 141543.3286 | 178472.3993 | 225289.0933 | 284680.1195 | 360068.8645 | 455818.5385 | 577491.5451 | 672575.4844 | 672561.0698 | 672541.283 | 672513.9994 | 672476.225 | 672423.7326 | 672350.5452 | 672248.1984 | 672104.6914 | 671902.9884 | 671618.8823 | 671217.944 | 670651.1662
| TRUE | 1449 | 22010233 | ECA | Blank | 22 | ALL FEEDERS | BUEF & Y MEF | BU | Schweitzer | SEL_351A | SEL 351 | SEL 300s | Digital |  | 0.15703 | 1 |  | 6.6 | 0.017308 | 3.723e-06 | 0.017304 | 59.497 | 0.39092 | 59.888 | 49.1515 | 6.9249 | 3.3372 |  | 14.9721 | 0.15742 | 3.3861e-05 | 0.15738 | 541.1327 | 3.5555 | 544.6882 | 447.0388 | 62.9829 | 30.3526 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 17.7652 | 0.11672 | 17.8819 | 14.6761 | 2.0677 | 0.99646 |  | 119.3016 | 1085.0625 | 35.6221 | 1049.4403 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021358 | 0.026432 | 0.032797 | 0.040794 | 0.050854 | 0.063527 | 0.079507 | 0.099681 | 0.12517 | 0.15742 | 0.19823 | 0.24994 | 0.31549 | 0.39864 | 0.5042 | 0.63826 | 0.80862 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.5943e-06 | 5.6856e-06 | 7.0548e-06 | 8.775e-06 | 1.0939e-05 | 1.3665e-05 | 1.7103e-05 | 2.1442e-05 | 2.6926e-05 | 3.3861e-05 | 4.2641e-05 | 5.3763e-05 | 6.7863e-05 | 8.5751e-05 | 0.00010846 | 0.00013729 | 0.00017394 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 147.2194 | 182.1904 | 226.0642 | 281.1864 | 350.5332 | 437.8834 | 548.0372 | 687.0952 | 862.8145 | 1085.0625 | 1366.3958 | 1722.7994 | 2174.6287 | 2747.8132 | 3475.3922 | 4399.4751 | 5573.7449 | 6491.4731 | 6491.4731 | 6491.4731 | 6491.4731 | 6491.4731 | 6491.4731 | 6491.4731 | 6491.4731 | 6491.4731 | 6491.4731 | 6491.4731 | 6491.4731 | 6491.4731 |  | 32.07 | 32.07 | 32.07 | 32.07 | 32.07 | 32.07 | 32.07 | 32.07 | 32.07 | 32.07 | 32.07 | 32.07 | 32.07 | 32.07 | 32.07 | 32.07 | 32.07 | 38.3857 | 50.8826 | 68.0369 | 91.6906 | 124.4394 | 169.9481 | 233.3985 | 322.1287 | 446.5433 | 621.4112 | 867.7191 | 1215.3155 | 1706.6878 |  | 73.42 | 90.8604 | 112.7407 | 140.2308 | 174.8148 | 218.3773 | 273.3122 | 342.662 | 430.2952 | 541.1327 | 681.4368 | 859.1792 | 1084.5115 | 1370.365 | 1733.2168 | 2194.0672 | 2779.6886 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 59.2078 | 76.6482 | 98.5286 | 126.0187 | 160.6027 | 204.1652 | 259.1001 | 328.4499 | 416.0831 | 526.9206 | 667.2247 | 844.9671 | 1070.2994 | 1356.1529 | 1719.0046 | 2179.8551 | 2765.4765 | 3220.3589 | 3214.8208 | 3207.2186 | 3196.7363 | 3182.2233 | 3162.0557 | 3133.9369 | 3094.6152 | 3039.4797 | 2961.9851 | 2852.8313 | 2698.7904 | 2481.0337 |  | 0.4824 | 0.59699 | 0.74075 | 0.92137 | 1.1486 | 1.4348 | 1.7958 | 2.2514 | 2.8272 | 3.5555 | 4.4773 | 5.6451 | 7.1257 | 9.0038 | 11.3879 | 14.4159 | 18.2636 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 |  | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.13971 | 0.1852 | 0.24763 | 0.33372 | 0.45292 | 0.61855 | 0.84949 | 1.1724 | 1.6253 | 2.2617 | 3.1582 | 4.4233 | 6.2118 |  | 0.36567 | 0.48026 | 0.62403 | 0.80465 | 1.0319 | 1.3181 | 1.679 | 2.1347 | 2.7105 | 3.4387 | 4.3606 | 5.5284 | 7.0089 | 8.8871 | 11.2712 | 14.2991 | 18.1469 | 21.1311 | 21.0856 | 21.0231 | 20.9371 | 20.8179 | 20.6522 | 20.4213 | 20.0983 | 19.6455 | 19.009 | 18.1126 | 16.8474 | 15.059 |  | 59.5735 | 77.1285 | 99.1526 | 126.8233 | 161.6346 | 205.4833 | 260.7792 | 330.5846 | 418.7935 | 530.3593 | 671.5853 | 850.4955 | 1077.3083 | 1365.04 | 1730.2758 | 2194.1542 | 2783.6234 | 3241.4899 | 3235.9063 | 3228.2418 | 3217.6733 | 3203.0411 | 3182.7079 | 3154.3582 | 3114.7136 | 3059.1252 | 2980.9942 | 2870.9438 | 2715.6378 | 2496.0927 |  | 60.6535 | 75.0613 | 93.137 | 115.847 | 144.4174 | 180.4052 | 225.7878 | 283.0788 | 355.474 | 447.0388 | 562.9463 | 709.7823 | 895.9331 | 1132.0814 | 1431.8393 | 1812.5556 | 2296.3472 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 45.9774 | 60.3852 | 78.4609 | 101.1709 | 129.7413 | 165.7291 | 211.1117 | 268.4027 | 340.7979 | 432.3627 | 548.2702 | 695.1062 | 881.257 | 1117.4053 | 1417.1632 | 1797.8795 | 2281.6711 | 2656.8789 | 2651.16 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 8.5454 | 10.5753 | 13.122 | 16.3216 | 20.3468 | 25.4171 | 31.811 | 39.8827 | 50.0824 | 62.9829 | 79.313 | 100.0006 | 126.2272 | 159.4979 | 201.7306 | 255.3693 | 323.5303 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 6.4777 | 8.5076 | 11.0543 | 14.2539 | 18.2791 | 23.3494 | 29.7433 | 37.815 | 48.0147 | 60.9152 | 77.2453 | 97.9329 | 124.1595 | 157.4302 | 199.6629 | 253.3016 | 321.4626 | 374.3253 | 373.5196 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 4.1182 | 5.0964 | 6.3237 | 7.8657 | 9.8055 | 12.249 | 15.3303 | 19.2202 | 24.1356 | 30.3526 | 38.2224 | 48.1921 | 60.8312 | 76.865 | 97.2176 | 123.0671 | 155.9151 | 181.5869 | 181.5869 | 181.5869 | 181.5869 | 181.5869 | 181.5869 | 181.5869 | 181.5869 | 181.5869 | 181.5869 | 181.5869 | 181.5869 | 181.5869 |  | 0.99646 | 0.99646 | 0.99646 | 0.99646 | 0.99646 | 0.99646 | 0.99646 | 0.99646 | 0.99646 | 0.99646 | 0.99646 | 0.99646 | 0.99646 | 0.99646 | 0.99646 | 0.99646 | 0.99646 | 1.1927 | 1.581 | 2.114 | 2.849 | 3.8665 | 5.2805 | 7.2521 | 10.009 | 13.8748 | 19.3082 | 26.9614 | 37.7617 | 53.0294 |  | 3.1217 | 4.1 | 5.3273 | 6.8692 | 8.8091 | 11.2525 | 14.3339 | 18.2237 | 23.1392 | 29.3561 | 37.2259 | 47.1956 | 59.8347 | 75.8685 | 96.2212 | 122.0707 | 154.9187 | 180.3942 | 180.0059 | 179.4729 | 178.7379 | 177.7204 | 176.3063 | 174.3348 | 171.5778 | 167.7121 | 162.2787 | 154.6255 | 143.8251 | 128.5574 |  | 115.1503 | 150.1213 | 193.9951 | 249.1173 | 318.4641 | 405.8143 | 515.9681 | 655.0261 | 830.7454 | 1052.9933 | 1334.3267 | 1690.7303 | 2142.5595 | 2715.7441 | 3443.3231 | 4367.406 | 5541.6758 | 6453.0884 | 6440.5919 | 6423.438 | 6399.7849 | 6367.0369 | 6321.5295 | 6258.0807 | 6169.3528 | 6044.9415 | 5870.0782 | 5623.7767 | 5276.1894 | 4784.83
| FALSE | 1450 | 22016141 | ECA | ECA001 | 22 | ECA1 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 0.96924 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 3.571 |  | 5.0708 | 0.0089964 | 7.078e-06 | 0.0089893 | 24.7421 | 0.49546 | 25.2376 | 25.5776 | 3.5995 | 6.2164 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 3.571 |  | 34.8291 | 60.6311 | 34.8291 | 25.8019 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.7894e-06 | 7.078e-06 | 1.0629e-05 | 1.6185e-05 | 2.4939e-05 | 3.8815e-05 | 6.0929e-05 | 9.6332e-05 | 0.00015323 | 0.00024497 | 0.00039332 | 0.00063378 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 41.0264 | 60.6311 | 91.0522 | 138.6436 | 213.6259 | 332.4917 | 521.9225 | 825.1827 | 1312.5608 | 2098.4388 | 3369.2176 | 5429.0293 | 6346.9574 | 6346.9574 | 6346.9574 | 6346.9574 | 6346.9574 | 6346.9574 | 6346.9574 | 6346.9574 | 6346.9574 | 6346.9574 |  | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 34.8291 | 41.6883 | 55.2603 | 73.8905 | 99.5792 | 135.1456 | 184.5696 | 253.4791 | 349.8433 | 484.9619 | 674.8747 | 942.3739 | 1319.8759 | 1853.5237 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.7419 | 24.7421 | 37.1563 | 56.5772 | 87.1757 | 135.682 | 212.9843 | 336.7377 | 535.6252 | 856.3235 | 1374.8984 | 2215.4591 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.529 | 10.5292 | 22.9433 | 42.3642 | 72.9628 | 121.4691 | 198.7714 | 322.5247 | 521.4122 | 839.3115 | 1352.348 | 2185.3061 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.33526 | 0.49546 | 0.74406 | 1.133 | 1.7457 | 2.717 | 4.265 | 6.7432 | 10.726 | 17.148 | 27.5325 | 44.3648 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050643 | 0.21085 | 0.45944 | 0.84835 | 1.4611 | 2.4324 | 3.9804 | 6.4586 | 10.4413 | 16.8073 | 27.0809 | 43.761 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5796 | 10.74 | 23.4028 | 43.2126 | 74.4239 | 123.9015 | 202.7518 | 328.9833 | 531.8536 | 856.1188 | 1379.4289 | 2229.0671 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.3072 | 25.5776 | 38.4109 | 58.4876 | 90.1194 | 140.2636 | 220.1761 | 348.1082 | 553.7116 | 885.2389 | 1421.3245 | 2290.2683 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6144 | 10.8847 | 23.7181 | 43.7947 | 75.4265 | 125.5707 | 205.4833 | 333.4154 | 539.0187 | 867.6524 | 1398.0126 | 2259.0972 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5995 | 5.4056 | 8.231 | 12.6825 | 19.7393 | 30.9855 | 48.9894 | 77.924 | 124.5799 | 200.0234 | 322.3101 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6148 | 17.6716 | 28.9177 | 46.9216 | 75.8563 | 122.105 | 196.7427 | 317.9234 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 4.2064 | 6.2164 | 9.3354 | 14.2148 | 21.9026 | 34.0897 | 53.5116 | 84.6043 | 134.5741 | 215.1485 | 345.4388 | 556.627 | 650.7402 | 650.7402 | 650.7402 | 650.7402 | 650.7402 | 650.7402 | 650.7402 | 650.7402 | 650.7402 | 650.7402 |  | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 4.2742 | 5.6657 | 7.5758 | 10.2096 | 13.8562 | 18.9235 | 25.9887 | 35.8687 | 49.7221 | 69.1935 | 96.6196 | 135.3241 | 190.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6354 | 2.6454 | 5.7644 | 10.6439 | 18.3317 | 30.5187 | 49.9407 | 81.0333 | 131.0031 | 210.8743 | 339.7731 | 549.0511 | 640.5306 | 636.884 | 631.8167 | 624.7515 | 614.8715 | 601.0181 | 581.5467 | 554.1206 | 515.4161 | 460.7023 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1973 | 25.8019 | 56.2231 | 103.8144 | 178.7968 | 297.6626 | 487.0934 | 790.3536 | 1277.7316 | 2056.7505 | 3313.9574 | 5355.1389 | 6247.3782 | 6211.8118 | 6162.3878 | 6093.4783 | 5997.1141 | 5861.9955 | 5672.0827 | 5404.5836 | 5027.0815 | 4493.4337
| FALSE | 1451 | 22016145 | ECA | ECA010 | 22 | ECA10 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 0.96924 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 1.5241 |  | 5.0708 | 0.0089964 | 7.078e-06 | 0.0089893 | 24.7421 | 0.49546 | 25.2376 | 25.5776 | 3.5995 | 2.6533 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 1.5241 |  | 32.7823 | 57.0679 | 32.7823 | 24.2856 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.7894e-06 | 7.078e-06 | 1.0629e-05 | 1.6185e-05 | 2.4939e-05 | 3.8815e-05 | 6.0929e-05 | 9.6332e-05 | 0.00015323 | 0.00024497 | 0.00039332 | 0.00063378 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 38.6154 | 57.0679 | 85.7013 | 130.4959 | 201.0717 | 312.9521 | 491.2506 | 776.689 | 1235.4252 | 1975.1193 | 3171.218 | 5109.9803 | 5973.9643 | 5973.9643 | 5973.9643 | 5973.9643 | 5973.9643 | 5973.9643 | 5973.9643 | 5973.9643 | 5973.9643 | 5973.9643 |  | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 32.7823 | 39.2384 | 52.0128 | 69.5481 | 93.7272 | 127.2035 | 173.723 | 238.5828 | 329.284 | 456.462 | 635.2142 | 886.9931 | 1242.3104 | 1744.5972 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.7419 | 24.7421 | 37.1563 | 56.5772 | 87.1757 | 135.682 | 212.9843 | 336.7377 | 535.6252 | 856.3235 | 1374.8984 | 2215.4591 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.529 | 10.5292 | 22.9433 | 42.3642 | 72.9628 | 121.4691 | 198.7714 | 322.5247 | 521.4122 | 839.3115 | 1352.348 | 2185.3061 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.33526 | 0.49546 | 0.74406 | 1.133 | 1.7457 | 2.717 | 4.265 | 6.7432 | 10.726 | 17.148 | 27.5325 | 44.3648 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050643 | 0.21085 | 0.45944 | 0.84835 | 1.4611 | 2.4324 | 3.9804 | 6.4586 | 10.4413 | 16.8073 | 27.0809 | 43.761 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5796 | 10.74 | 23.4028 | 43.2126 | 74.4239 | 123.9015 | 202.7518 | 328.9833 | 531.8536 | 856.1188 | 1379.4289 | 2229.0671 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.3072 | 25.5776 | 38.4109 | 58.4876 | 90.1194 | 140.2636 | 220.1761 | 348.1082 | 553.7116 | 885.2389 | 1421.3245 | 2290.2683 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6144 | 10.8847 | 23.7181 | 43.7947 | 75.4265 | 125.5707 | 205.4833 | 333.4154 | 539.0187 | 867.6524 | 1398.0126 | 2259.0972 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5995 | 5.4056 | 8.231 | 12.6825 | 19.7393 | 30.9855 | 48.9894 | 77.924 | 124.5799 | 200.0234 | 322.3101 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6148 | 17.6716 | 28.9177 | 46.9216 | 75.8563 | 122.105 | 196.7427 | 317.9234 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.7953 | 2.6533 | 3.9845 | 6.0671 | 9.3484 | 14.5501 | 22.8397 | 36.1105 | 57.4385 | 91.8291 | 147.4392 | 237.5779 | 277.7471 | 277.7471 | 277.7471 | 277.7471 | 277.7471 | 277.7471 | 277.7471 | 277.7471 | 277.7471 | 277.7471 |  | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.5241 | 1.8243 | 2.4182 | 3.2335 | 4.3577 | 5.9141 | 8.0769 | 11.0924 | 15.3094 | 21.2223 | 29.533 | 41.2389 | 57.7586 | 81.1114 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2712 | 1.1291 | 2.4604 | 4.543 | 7.8243 | 13.0259 | 21.3155 | 34.5864 | 55.9144 | 90.0048 | 145.021 | 234.3444 | 273.3894 | 271.833 | 269.6702 | 266.6546 | 262.4377 | 256.5248 | 248.2141 | 236.5082 | 219.9884 | 196.6356 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8331 | 24.2856 | 52.919 | 97.7136 | 168.2894 | 280.1698 | 458.4683 | 743.9067 | 1202.6429 | 1935.881 | 3119.2052 | 5040.4321 | 5880.237 | 5846.7608 | 5800.2413 | 5735.3815 | 5644.6803 | 5517.5023 | 5338.7501 | 5086.9711 | 4731.6538 | 4229.367
| FALSE | 1452 | 22016146 | ECA | ECA012 | 22 | ECA12 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 1 | 1 |  | 0.96924 | 0.0051679 | 7.0794e-06 | 0.0051609 | 14.2138 | 0.49555 | 14.7093 | 14.71 | 2.0678 | 2.6537 |  | 5.0708 | 0.0089964 | 1.2324e-05 | 0.0089841 | 24.7435 | 0.86267 | 25.6062 | 25.6074 | 3.5996 | 4.6197 |  | 0.0051679 | 7.0794e-06 | 0.0051609 | 14.2138 | 0.49555 | 14.7093 | 14.71 | 2.0678 | 2.6537 |  | 34.1408 | 59.4328 | 34.1408 | 25.292 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 7.0794e-06 | 7.0794e-06 | 7.0794e-06 | 7.0794e-06 | 7.0794e-06 | 7.0794e-06 | 7.0794e-06 | 7.0794e-06 | 8.339e-06 | 1.2324e-05 | 1.8507e-05 | 2.8181e-05 | 4.3422e-05 | 6.7582e-05 | 0.00010609 | 0.00016773 | 0.00026679 | 0.00042653 | 0.00068483 | 0.0011035 | 0.0012901 | 0.0012901 | 0.0012901 | 0.0012901 | 0.0012901 | 0.0012901 | 0.0012901 | 0.0012901 | 0.0012901 | 0.0012901 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 40.2157 | 59.4328 | 89.2528 | 135.9036 | 209.4042 | 325.9209 | 511.6081 | 808.8752 | 1286.6215 | 2056.9687 | 3302.634 | 5321.739 | 6221.5267 | 6221.5267 | 6221.5267 | 6221.5267 | 6221.5267 | 6221.5267 | 6221.5267 | 6221.5267 | 6221.5267 | 6221.5267 |  | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 34.1408 | 40.8644 | 54.1682 | 72.4302 | 97.6113 | 132.4748 | 180.9221 | 248.4697 | 342.9296 | 475.3779 | 661.5376 | 923.7503 | 1293.7921 | 1816.8937 |  | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 16.7429 | 24.7435 | 37.1584 | 56.5805 | 87.1808 | 135.6899 | 212.9967 | 336.7573 | 535.6564 | 856.3734 | 1374.9786 | 2215.5883 | 2590.195 | 2590.195 | 2590.195 | 2590.195 | 2590.195 | 2590.195 | 2590.195 | 2590.195 | 2590.195 | 2590.195 |  | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 17.013 | 22.5517 | 30.1547 | 40.6383 | 55.153 | 75.3229 | 103.4449 | 142.7711 | 197.9131 | 275.4165 | 384.583 | 538.6417 | 756.4235 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5291 | 10.5298 | 22.9447 | 42.3667 | 72.967 | 121.4762 | 198.7829 | 322.5435 | 521.4426 | 839.3604 | 1352.4269 | 2185.4336 | 2549.5567 | 2535.042 | 2514.872 | 2486.7501 | 2447.4238 | 2392.2819 | 2314.7784 | 2205.612 | 2051.5533 | 1833.7715 |  | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.58373 | 0.86267 | 1.2955 | 1.9726 | 3.0395 | 4.7308 | 7.426 | 11.7408 | 18.6754 | 29.857 | 47.9378 | 77.2452 | 90.3057 | 90.3057 | 90.3057 | 90.3057 | 90.3057 | 90.3057 | 90.3057 | 90.3057 | 90.3057 | 90.3057 |  | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.49555 | 0.59315 | 0.78625 | 1.0513 | 1.4168 | 1.9229 | 2.6261 | 3.6065 | 4.9776 | 6.9001 | 9.6022 | 13.4083 | 18.7794 | 26.3723 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.088177 | 0.36711 | 0.79995 | 1.4771 | 2.544 | 4.2352 | 6.9305 | 11.2453 | 18.1798 | 29.2638 | 47.1516 | 76.1939 | 88.8888 | 88.3828 | 87.6796 | 86.6991 | 85.328 | 83.4055 | 80.7034 | 76.8974 | 71.5262 | 63.9334 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6173 | 10.8969 | 23.7446 | 43.8438 | 75.511 | 125.7114 | 205.7134 | 333.7888 | 539.6224 | 868.6242 | 1399.5784 | 2261.6274 | 2638.4455 | 2623.4248 | 2602.5516 | 2573.4492 | 2532.7519 | 2475.6874 | 2395.4818 | 2282.5093 | 2123.0795 | 1897.7049 |  | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 17.3274 | 25.6074 | 38.4556 | 58.5557 | 90.2243 | 140.4269 | 220.4325 | 348.5136 | 554.3563 | 886.2696 | 1422.9794 | 2292.935 | 2680.6193 | 2680.6193 | 2680.6193 | 2680.6193 | 2680.6193 | 2680.6193 | 2680.6193 | 2680.6193 | 2680.6193 | 2680.6193 |  | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 14.71 | 17.6069 | 23.339 | 31.2074 | 42.057 | 57.0784 | 77.9525 | 107.0562 | 147.7553 | 204.8223 | 285.0314 | 398.0089 | 557.4458 | 782.8304 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6174 | 10.8974 | 23.7457 | 43.8457 | 75.5143 | 125.7169 | 205.7225 | 333.8036 | 539.6463 | 868.6627 | 1399.6404 | 2261.7276 | 2638.5623 | 2623.5409 | 2602.6669 | 2573.5632 | 2532.864 | 2475.7971 | 2395.5879 | 2282.6104 | 2123.1735 | 1897.7889 |  | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.4357 | 3.5996 | 5.4057 | 8.2311 | 12.6827 | 19.7396 | 30.9859 | 48.9901 | 77.9251 | 124.5817 | 200.0263 | 322.3148 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 |  | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9577 | 15.0487 | 20.7698 | 28.7916 | 40.0665 | 55.9476 | 78.3594 | 110.0414 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36793 | 1.5318 | 3.3379 | 6.1633 | 10.6149 | 17.6719 | 28.9181 | 46.9223 | 75.8574 | 122.1068 | 196.7456 | 317.928 | 370.8992 | 368.7877 | 365.8534 | 361.7624 | 356.0413 | 348.0195 | 336.7446 | 320.8635 | 298.4517 | 266.7697 |  | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 3.1259 | 4.6197 | 6.9376 | 10.5637 | 16.2769 | 25.3336 | 39.767 | 62.8734 | 100.0083 | 159.887 | 256.7118 | 413.6557 | 483.5956 | 483.5956 | 483.5956 | 483.5956 | 483.5956 | 483.5956 | 483.5956 | 483.5956 | 483.5956 | 483.5956 |  | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 2.6537 | 3.1764 | 4.2105 | 5.63 | 7.5873 | 10.2972 | 14.063 | 19.3134 | 26.6557 | 36.9508 | 51.4209 | 71.8026 | 100.5657 | 141.2261 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47219 | 1.9659 | 4.2838 | 7.91 | 13.6231 | 22.6799 | 37.1133 | 60.2196 | 97.3546 | 156.7106 | 252.5013 | 408.0257 | 476.0083 | 473.2984 | 469.5326 | 464.2822 | 456.9399 | 446.6448 | 432.1747 | 411.793 | 383.0299 | 342.3695 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0748 | 25.292 | 55.112 | 101.7628 | 175.2634 | 291.7801 | 477.4673 | 774.7344 | 1252.4807 | 2016.1043 | 3248.4658 | 5249.3088 | 6123.9154 | 6089.0518 | 6040.6045 | 5973.0569 | 5878.5971 | 5746.1488 | 5559.9891 | 5297.7763 | 4927.7346 | 4404.6329
| FALSE | 1453 | 22016142 | ECA | ECA003 | 22 | ECA3 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 0.96924 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 1.7855 |  | 5.0708 | 0.0089964 | 7.078e-06 | 0.0089893 | 24.7421 | 0.49546 | 25.2376 | 25.5776 | 3.5995 | 3.1082 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 1.7855 |  | 33.0436 | 57.5229 | 33.0436 | 24.4792 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.7894e-06 | 7.078e-06 | 1.0629e-05 | 1.6185e-05 | 2.4939e-05 | 3.8815e-05 | 6.0929e-05 | 9.6332e-05 | 0.00015323 | 0.00024497 | 0.00039332 | 0.00063378 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 38.9233 | 57.5229 | 86.3845 | 131.5361 | 202.6746 | 315.4468 | 495.1667 | 782.8806 | 1245.2737 | 1990.8645 | 3196.4982 | 5150.7158 | 6021.5873 | 6021.5873 | 6021.5873 | 6021.5873 | 6021.5873 | 6021.5873 | 6021.5873 | 6021.5873 | 6021.5873 | 6021.5873 |  | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 33.0436 | 39.5512 | 52.4274 | 70.1026 | 94.4744 | 128.2175 | 175.1079 | 240.4847 | 331.9089 | 460.1008 | 640.278 | 894.064 | 1252.2138 | 1758.5047 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.7419 | 24.7421 | 37.1563 | 56.5772 | 87.1757 | 135.682 | 212.9843 | 336.7377 | 535.6252 | 856.3235 | 1374.8984 | 2215.4591 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.529 | 10.5292 | 22.9433 | 42.3642 | 72.9628 | 121.4691 | 198.7714 | 322.5247 | 521.4122 | 839.3115 | 1352.348 | 2185.3061 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.33526 | 0.49546 | 0.74406 | 1.133 | 1.7457 | 2.717 | 4.265 | 6.7432 | 10.726 | 17.148 | 27.5325 | 44.3648 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050643 | 0.21085 | 0.45944 | 0.84835 | 1.4611 | 2.4324 | 3.9804 | 6.4586 | 10.4413 | 16.8073 | 27.0809 | 43.761 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5796 | 10.74 | 23.4028 | 43.2126 | 74.4239 | 123.9015 | 202.7518 | 328.9833 | 531.8536 | 856.1188 | 1379.4289 | 2229.0671 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.3072 | 25.5776 | 38.4109 | 58.4876 | 90.1194 | 140.2636 | 220.1761 | 348.1082 | 553.7116 | 885.2389 | 1421.3245 | 2290.2683 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6144 | 10.8847 | 23.7181 | 43.7947 | 75.4265 | 125.5707 | 205.4833 | 333.4154 | 539.0187 | 867.6524 | 1398.0126 | 2259.0972 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5995 | 5.4056 | 8.231 | 12.6825 | 19.7393 | 30.9855 | 48.9894 | 77.924 | 124.5799 | 200.0234 | 322.3101 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6148 | 17.6716 | 28.9177 | 46.9216 | 75.8563 | 122.105 | 196.7427 | 317.9234 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 2.1032 | 3.1082 | 4.6677 | 7.1074 | 10.9513 | 17.0448 | 26.7558 | 42.3021 | 67.287 | 107.5743 | 172.7194 | 278.3135 | 325.3701 | 325.3701 | 325.3701 | 325.3701 | 325.3701 | 325.3701 | 325.3701 | 325.3701 | 325.3701 | 325.3701 |  | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 1.7855 | 2.1371 | 2.8329 | 3.7879 | 5.1048 | 6.9281 | 9.4618 | 12.9943 | 17.9343 | 24.8611 | 34.5967 | 48.3098 | 67.6621 | 95.0189 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3177 | 1.3227 | 2.8822 | 5.3219 | 9.1658 | 15.2594 | 24.9703 | 40.5166 | 65.5016 | 105.4372 | 169.8865 | 274.5256 | 320.2653 | 318.442 | 315.9083 | 312.3758 | 307.4358 | 300.509 | 290.7734 | 277.0603 | 257.7081 | 230.3512 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8796 | 24.4792 | 53.3409 | 98.4925 | 169.631 | 282.4032 | 462.1231 | 749.837 | 1212.2301 | 1951.3134 | 3144.0708 | 5080.6133 | 5927.1129 | 5893.3698 | 5846.4794 | 5781.1026 | 5689.6784 | 5561.4865 | 5381.3094 | 5127.5233 | 4769.3735 | 4263.0826
| FALSE | 1454 | 22016143 | ECA | ECA005 | 22 | ECA5 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 0.96924 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 0.66998 |  | 5.0708 | 0.0089964 | 7.078e-06 | 0.0089893 | 24.7421 | 0.49546 | 25.2376 | 25.5776 | 3.5995 | 1.1663 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 0.66998 |  | 31.9281 | 55.581 | 31.9281 | 23.6529 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.7894e-06 | 7.078e-06 | 1.0629e-05 | 1.6185e-05 | 2.4939e-05 | 3.8815e-05 | 6.0929e-05 | 9.6332e-05 | 0.00015323 | 0.00024497 | 0.00039332 | 0.00063378 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 37.6093 | 55.581 | 83.4683 | 127.0957 | 195.8327 | 304.7979 | 478.4507 | 756.4518 | 1203.2352 | 1923.6561 | 3088.5895 | 4976.8358 | 5818.3081 | 5818.3081 | 5818.3081 | 5818.3081 | 5818.3081 | 5818.3081 | 5818.3081 | 5818.3081 | 5818.3081 | 5818.3081 |  | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 38.216 | 50.6575 | 67.736 | 91.2851 | 123.8891 | 169.1965 | 232.3663 | 320.7042 | 444.5685 | 618.6632 | 863.8819 | 1209.9411 | 1699.1404 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.7419 | 24.7421 | 37.1563 | 56.5772 | 87.1757 | 135.682 | 212.9843 | 336.7377 | 535.6252 | 856.3235 | 1374.8984 | 2215.4591 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.529 | 10.5292 | 22.9433 | 42.3642 | 72.9628 | 121.4691 | 198.7714 | 322.5247 | 521.4122 | 839.3115 | 1352.348 | 2185.3061 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.33526 | 0.49546 | 0.74406 | 1.133 | 1.7457 | 2.717 | 4.265 | 6.7432 | 10.726 | 17.148 | 27.5325 | 44.3648 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050643 | 0.21085 | 0.45944 | 0.84835 | 1.4611 | 2.4324 | 3.9804 | 6.4586 | 10.4413 | 16.8073 | 27.0809 | 43.761 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5796 | 10.74 | 23.4028 | 43.2126 | 74.4239 | 123.9015 | 202.7518 | 328.9833 | 531.8536 | 856.1188 | 1379.4289 | 2229.0671 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.3072 | 25.5776 | 38.4109 | 58.4876 | 90.1194 | 140.2636 | 220.1761 | 348.1082 | 553.7116 | 885.2389 | 1421.3245 | 2290.2683 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6144 | 10.8847 | 23.7181 | 43.7947 | 75.4265 | 125.5707 | 205.4833 | 333.4154 | 539.0187 | 867.6524 | 1398.0126 | 2259.0972 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5995 | 5.4056 | 8.231 | 12.6825 | 19.7393 | 30.9855 | 48.9894 | 77.924 | 124.5799 | 200.0234 | 322.3101 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6148 | 17.6716 | 28.9177 | 46.9216 | 75.8563 | 122.105 | 196.7427 | 317.9234 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.78919 | 1.1663 | 1.7515 | 2.667 | 4.1093 | 6.3959 | 10.0398 | 15.8733 | 25.2486 | 40.3658 | 64.8107 | 104.4335 | 122.0909 | 122.0909 | 122.0909 | 122.0909 | 122.0909 | 122.0909 | 122.0909 | 122.0909 | 122.0909 | 122.0909 |  | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.80192 | 1.063 | 1.4214 | 1.9155 | 2.5997 | 3.5504 | 4.876 | 6.7296 | 9.3288 | 12.982 | 18.1276 | 25.3893 | 35.6546 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11921 | 0.49633 | 1.0815 | 1.997 | 3.4394 | 5.7259 | 9.3698 | 15.2033 | 24.5786 | 39.5639 | 63.7477 | 103.0121 | 120.1753 | 119.4912 | 118.5405 | 117.2149 | 115.3612 | 112.7621 | 109.1089 | 103.9632 | 96.7016 | 86.4363 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6811 | 23.6529 | 51.5402 | 95.1676 | 163.9045 | 272.8697 | 446.5225 | 724.5237 | 1171.3071 | 1885.4401 | 3037.932 | 4909.0998 | 5727.023 | 5694.419 | 5649.1116 | 5585.9417 | 5497.6039 | 5373.7395 | 5199.6449 | 4954.4262 | 4608.367 | 4119.1677
| FALSE | 1455 | 22016144 | ECA | ECA007 | 22 | ECA7 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 0.96924 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 0.66998 |  | 5.0708 | 0.0089964 | 7.078e-06 | 0.0089893 | 24.7421 | 0.49546 | 25.2376 | 25.5776 | 3.5995 | 1.1663 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 0.66998 |  | 31.9281 | 55.581 | 31.9281 | 23.6529 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.7894e-06 | 7.078e-06 | 1.0629e-05 | 1.6185e-05 | 2.4939e-05 | 3.8815e-05 | 6.0929e-05 | 9.6332e-05 | 0.00015323 | 0.00024497 | 0.00039332 | 0.00063378 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 37.6093 | 55.581 | 83.4683 | 127.0957 | 195.8327 | 304.7979 | 478.4507 | 756.4518 | 1203.2352 | 1923.6561 | 3088.5895 | 4976.8358 | 5818.3081 | 5818.3081 | 5818.3081 | 5818.3081 | 5818.3081 | 5818.3081 | 5818.3081 | 5818.3081 | 5818.3081 | 5818.3081 |  | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 31.9281 | 38.216 | 50.6575 | 67.736 | 91.2851 | 123.8891 | 169.1965 | 232.3663 | 320.7042 | 444.5685 | 618.6632 | 863.8819 | 1209.9411 | 1699.1404 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.7419 | 24.7421 | 37.1563 | 56.5772 | 87.1757 | 135.682 | 212.9843 | 336.7377 | 535.6252 | 856.3235 | 1374.8984 | 2215.4591 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.529 | 10.5292 | 22.9433 | 42.3642 | 72.9628 | 121.4691 | 198.7714 | 322.5247 | 521.4122 | 839.3115 | 1352.348 | 2185.3061 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.33526 | 0.49546 | 0.74406 | 1.133 | 1.7457 | 2.717 | 4.265 | 6.7432 | 10.726 | 17.148 | 27.5325 | 44.3648 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050643 | 0.21085 | 0.45944 | 0.84835 | 1.4611 | 2.4324 | 3.9804 | 6.4586 | 10.4413 | 16.8073 | 27.0809 | 43.761 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5796 | 10.74 | 23.4028 | 43.2126 | 74.4239 | 123.9015 | 202.7518 | 328.9833 | 531.8536 | 856.1188 | 1379.4289 | 2229.0671 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.3072 | 25.5776 | 38.4109 | 58.4876 | 90.1194 | 140.2636 | 220.1761 | 348.1082 | 553.7116 | 885.2389 | 1421.3245 | 2290.2683 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6144 | 10.8847 | 23.7181 | 43.7947 | 75.4265 | 125.5707 | 205.4833 | 333.4154 | 539.0187 | 867.6524 | 1398.0126 | 2259.0972 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5995 | 5.4056 | 8.231 | 12.6825 | 19.7393 | 30.9855 | 48.9894 | 77.924 | 124.5799 | 200.0234 | 322.3101 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6148 | 17.6716 | 28.9177 | 46.9216 | 75.8563 | 122.105 | 196.7427 | 317.9234 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.78919 | 1.1663 | 1.7515 | 2.667 | 4.1093 | 6.3959 | 10.0398 | 15.8733 | 25.2486 | 40.3658 | 64.8107 | 104.4335 | 122.0909 | 122.0909 | 122.0909 | 122.0909 | 122.0909 | 122.0909 | 122.0909 | 122.0909 | 122.0909 | 122.0909 |  | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.66998 | 0.80192 | 1.063 | 1.4214 | 1.9155 | 2.5997 | 3.5504 | 4.876 | 6.7296 | 9.3288 | 12.982 | 18.1276 | 25.3893 | 35.6546 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11921 | 0.49633 | 1.0815 | 1.997 | 3.4394 | 5.7259 | 9.3698 | 15.2033 | 24.5786 | 39.5639 | 63.7477 | 103.0121 | 120.1753 | 119.4912 | 118.5405 | 117.2149 | 115.3612 | 112.7621 | 109.1089 | 103.9632 | 96.7016 | 86.4363 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6811 | 23.6529 | 51.5402 | 95.1676 | 163.9045 | 272.8697 | 446.5225 | 724.5237 | 1171.3071 | 1885.4401 | 3037.932 | 4909.0998 | 5727.023 | 5694.419 | 5649.1116 | 5585.9417 | 5497.6039 | 5373.7395 | 5199.6449 | 4954.4262 | 4608.367 | 4119.1677
| TRUE | 1456 | 22008359 | ECA | Blank | 66 | BUS ALL | DISTANCE & DIR EF | X | Schweitzer | SEL_311B | SEL 311B | SEL 300s | Digital |  | 0.033587 | 1 |  | 6.6 | 0.017308 | 7.9633e-07 | 0.017307 | 113.5833 | 0.1314 | 113.7147 | 49.1349 | 6.9249 | 0.7561 |  | 14.9721 | 0.15742 | 7.2427e-06 | 0.15741 | 1033.0541 | 1.1951 | 1034.2492 | 446.8877 | 62.9826 | 6.8769 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 33.9147 | 0.039233 | 33.954 | 14.6711 | 2.0677 | 0.22576 |  | 170.5306 | 1550.9963 | 50.9186 | 1500.0777 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021358 | 0.026432 | 0.032797 | 0.040794 | 0.050854 | 0.063527 | 0.079507 | 0.099681 | 0.12517 | 0.15742 | 0.19823 | 0.24994 | 0.31549 | 0.39864 | 0.5042 | 0.63826 | 0.80862 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 9.8268e-07 | 1.2161e-06 | 1.509e-06 | 1.8769e-06 | 2.3398e-06 | 2.9229e-06 | 3.6581e-06 | 4.5863e-06 | 5.7593e-06 | 7.2427e-06 | 9.1206e-06 | 1.15e-05 | 1.4516e-05 | 1.8342e-05 | 2.3198e-05 | 2.9366e-05 | 3.7205e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 210.4365 | 260.4243 | 323.1379 | 401.9299 | 501.0548 | 625.9138 | 783.3684 | 982.1389 | 1233.3134 | 1550.9963 | 1953.1363 | 2462.5822 | 3108.4303 | 3927.7445 | 4967.7513 | 6288.6422 | 7967.1521 | 9278.9596 | 9278.9596 | 9278.9596 | 9278.9596 | 9278.9596 | 9278.9596 | 9278.9596 | 9278.9596 | 9278.9596 | 9278.9596 | 9278.9596 | 9278.9596 | 9278.9596 |  | 44.136 | 44.136 | 44.136 | 44.136 | 44.136 | 44.136 | 44.136 | 44.136 | 44.136 | 44.136 | 44.136 | 44.136 | 44.136 | 44.136 | 44.136 | 44.136 | 44.136 | 52.828 | 70.0266 | 93.6351 | 126.1882 | 171.2585 | 233.8893 | 321.2123 | 443.3265 | 614.5507 | 855.211 | 1194.1898 | 1672.5659 | 2348.8121 |  | 140.163 | 173.4578 | 215.2287 | 267.7088 | 333.7317 | 416.8951 | 521.7691 | 654.1619 | 821.4587 | 1033.0541 | 1300.9028 | 1640.2235 | 2070.3961 | 2616.1072 | 3308.8124 | 4188.6029 | 5306.5885 | 6180.3289 | 6180.3289 | 6180.3289 | 6180.3289 | 6180.3289 | 6180.3289 | 6180.3289 | 6180.3289 | 6180.3289 | 6180.3289 | 6180.3289 | 6180.3289 | 6180.3289 |  | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 32.4751 | 43.0476 | 57.5605 | 77.572 | 105.2781 | 143.7793 | 197.4595 | 272.527 | 377.784 | 525.7256 | 734.1068 | 1028.1799 | 1443.8901 |  | 113.0312 | 146.326 | 188.0969 | 240.577 | 306.5999 | 389.7634 | 494.6373 | 627.0301 | 794.3269 | 1005.9223 | 1273.771 | 1613.0917 | 2043.2643 | 2588.9754 | 3281.6806 | 4161.4711 | 5279.4567 | 6147.8538 | 6137.2813 | 6122.7684 | 6102.7569 | 6075.0508 | 6036.5496 | 5982.8694 | 5907.8019 | 5802.5449 | 5654.6033 | 5446.2221 | 5152.149 | 4736.4388 |  | 0.16214 | 0.20066 | 0.24898 | 0.30969 | 0.38607 | 0.48227 | 0.60359 | 0.75675 | 0.95028 | 1.1951 | 1.5049 | 1.8974 | 2.3951 | 3.0264 | 3.8277 | 4.8454 | 6.1387 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 | 7.1495 |  | 0.039233 | 0.039233 | 0.039233 | 0.039233 | 0.039233 | 0.039233 | 0.039233 | 0.039233 | 0.039233 | 0.039233 | 0.039233 | 0.039233 | 0.039233 | 0.039233 | 0.039233 | 0.039233 | 0.039233 | 0.04696 | 0.062248 | 0.083234 | 0.11217 | 0.15223 | 0.20791 | 0.28553 | 0.39408 | 0.54628 | 0.76021 | 1.0615 | 1.4868 | 2.0879 |  | 0.12291 | 0.16143 | 0.20975 | 0.27046 | 0.34683 | 0.44304 | 0.56436 | 0.71751 | 0.91104 | 1.1558 | 1.4657 | 1.8582 | 2.3558 | 2.9871 | 3.7885 | 4.8062 | 6.0995 | 7.1025 | 7.0873 | 7.0663 | 7.0373 | 6.9973 | 6.9416 | 6.864 | 6.7554 | 6.6032 | 6.3893 | 6.088 | 5.6627 | 5.0616 |  | 113.1541 | 146.4874 | 188.3066 | 240.8475 | 306.9468 | 390.2064 | 495.2017 | 627.7476 | 795.238 | 1007.0781 | 1275.2367 | 1614.9499 | 2045.6201 | 2591.9625 | 3285.4691 | 4166.2774 | 5285.5562 | 6154.9564 | 6144.3686 | 6129.8347 | 6109.7943 | 6082.0481 | 6043.4912 | 5989.7333 | 5914.5573 | 5809.1481 | 5660.9926 | 5452.3101 | 5157.8118 | 4741.5004 |  | 60.6329 | 75.0359 | 93.1055 | 115.8078 | 144.3686 | 180.3442 | 225.7115 | 282.9831 | 355.3539 | 446.8877 | 562.756 | 709.5424 | 895.6302 | 1131.6987 | 1431.3553 | 1811.9428 | 2295.5709 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 45.9618 | 60.3648 | 78.4344 | 101.1367 | 129.6975 | 165.673 | 211.0403 | 268.312 | 340.6827 | 432.2165 | 548.0849 | 694.8712 | 880.9591 | 1117.0276 | 1416.6841 | 1797.2717 | 2280.8998 | 2655.9808 | 2650.2638 | 2642.4162 | 2631.5953 | 2616.6136 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 8.5454 | 10.5753 | 13.1219 | 16.3215 | 20.3468 | 25.417 | 31.8109 | 39.8826 | 50.0822 | 62.9826 | 79.3127 | 100.0002 | 126.2267 | 159.4973 | 201.7297 | 255.3683 | 323.529 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 6.4777 | 8.5076 | 11.0542 | 14.2538 | 18.2791 | 23.3493 | 29.7432 | 37.8149 | 48.0145 | 60.9149 | 77.245 | 97.9325 | 124.159 | 157.4296 | 199.662 | 253.3006 | 321.4613 | 374.3237 | 373.518 | 372.412 | 370.8869 | 368.7755 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 0.93304 | 1.1547 | 1.4327 | 1.7821 | 2.2216 | 2.7752 | 3.4733 | 4.3546 | 5.4683 | 6.8769 | 8.6599 | 10.9187 | 13.7823 | 17.4149 | 22.0262 | 27.8828 | 35.325 | 41.1413 | 41.1413 | 41.1413 | 41.1413 | 41.1413 | 41.1413 | 41.1413 | 41.1413 | 41.1413 | 41.1413 | 41.1413 | 41.1413 | 41.1413 |  | 0.22576 | 0.22576 | 0.22576 | 0.22576 | 0.22576 | 0.22576 | 0.22576 | 0.22576 | 0.22576 | 0.22576 | 0.22576 | 0.22576 | 0.22576 | 0.22576 | 0.22576 | 0.22576 | 0.22576 | 0.27023 | 0.3582 | 0.47896 | 0.64548 | 0.87602 | 1.1964 | 1.6431 | 2.2677 | 3.1435 | 4.3746 | 6.1085 | 8.5555 | 12.0146 |  | 0.70728 | 0.92891 | 1.207 | 1.5563 | 1.9958 | 2.5494 | 3.2476 | 4.1289 | 5.2425 | 6.6511 | 8.4341 | 10.6929 | 13.5565 | 17.1892 | 21.8004 | 27.657 | 35.0992 | 40.8711 | 40.7831 | 40.6624 | 40.4958 | 40.2653 | 39.9449 | 39.4983 | 38.8736 | 37.9978 | 36.7668 | 35.0328 | 32.5858 | 29.1267 |  | 166.3009 | 216.2887 | 279.0022 | 357.7943 | 456.9192 | 581.7782 | 739.2328 | 938.0033 | 1189.1778 | 1506.8607 | 1909.0007 | 2418.4465 | 3064.2947 | 3883.6089 | 4923.6157 | 6244.5066 | 7923.0165 | 9226.132 | 9208.9335 | 9185.3252 | 9152.7723 | 9107.7024 | 9045.0721 | 8957.7497 | 8835.6366 | 8664.4137 | 8423.7553 | 8084.7791 | 7606.4067 | 6930.1658
| FALSE | 1457 | 22016060 | ECA | Blank | 66 | CB A | CB MGMT & CB FAIL | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0 | 1 |  | 1.2319 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 5.5365 | 0.011144 | 0 | 0.011144 | 58.5036 | 0 | 58.5036 | 31.6323 | 4.4585 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 94.5944 | 43.8691 | 50.7253 |  | 0.15028 |  | 1.4316 | 1.6638 | 1.9336 | 2.2472 | 2.6116 | 3.0351 | 3.5272 | 4.0992 | 4.764 | 5.5365 | 6.4343 | 7.4777 | 8.6903 | 10.0995 | 11.7373 | 13.6406 | 15.8526 | 18.4232 | 21.4108 | 24.8828 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054631 | 0.0077483 | 0.011144 | 0.016224 | 0.023875 | 0.035459 | 0.053084 | 0.080016 | 0.12132 | 0.18486 | 0.28289 | 0.43449 | 0.66941 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 46.3744 | 65.7727 | 94.5944 | 137.7226 | 202.6656 | 301.0001 | 450.6184 | 679.2303 | 1029.8289 | 1569.224 | 2401.3776 | 3688.2559 | 5682.4502 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 28.6811 | 40.6783 | 58.5036 | 85.177 | 125.3422 | 186.159 | 278.6931 | 420.0823 | 636.9163 | 970.515 | 1485.1754 | 2281.0686 | 3514.4142 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5494 | 13.5467 | 31.372 | 58.0454 | 98.2105 | 159.0273 | 251.5614 | 392.9506 | 609.7847 | 943.3833 | 1452.7005 | 2238.0212 | 3456.8539 | 4866.6688 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5494 | 13.5467 | 31.372 | 58.0454 | 98.2105 | 159.0273 | 251.5614 | 392.9506 | 609.7847 | 943.3833 | 1452.7005 | 2238.0212 | 3456.8539 | 4866.6688 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 15.5075 | 21.9943 | 31.6323 | 46.0543 | 67.7711 | 100.6541 | 150.6862 | 227.1338 | 344.3735 | 524.7465 | 803.0177 | 1233.3482 | 1900.2043 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83774 | 7.3245 | 16.9625 | 31.3845 | 53.1013 | 85.9843 | 136.0164 | 212.464 | 329.7037 | 510.0767 | 785.4588 | 1210.0729 | 1869.0821 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1858 | 3.1001 | 4.4585 | 6.4913 | 9.5523 | 14.1871 | 21.2391 | 32.0143 | 48.5391 | 73.9625 | 113.1845 | 173.8392 | 267.8318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11808 | 1.0324 | 2.3908 | 4.4236 | 7.4846 | 12.1194 | 19.1714 | 29.9466 | 46.4714 | 71.8948 | 110.7096 | 170.5585 | 263.4452 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5052 | 21.9036 | 50.7253 | 93.8535 | 158.7964 | 257.131 | 406.7492 | 635.3612 | 985.9598 | 1525.3548 | 2348.8689 | 3618.6526 | 5589.3812 | 7868.9084 | 7824.1106 | 7761.8584 | 7675.0633 | 7553.6874 | 7383.4983 | 7144.2929 | 6807.3633 | 6331.8792 | 5659.7211
| FALSE | 1458 | 22016059 | ECA | Blank | 66 | CB B | CB MGMT & CB FAIL | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0 | 1 |  | 1.2319 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 5.5365 | 0.011144 | 0 | 0.011144 | 58.5036 | 0 | 58.5036 | 31.6323 | 4.4585 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 94.5944 | 43.8691 | 50.7253 |  | 0.15028 |  | 1.4316 | 1.6638 | 1.9336 | 2.2472 | 2.6116 | 3.0351 | 3.5272 | 4.0992 | 4.764 | 5.5365 | 6.4343 | 7.4777 | 8.6903 | 10.0995 | 11.7373 | 13.6406 | 15.8526 | 18.4232 | 21.4108 | 24.8828 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054631 | 0.0077483 | 0.011144 | 0.016224 | 0.023875 | 0.035459 | 0.053084 | 0.080016 | 0.12132 | 0.18486 | 0.28289 | 0.43449 | 0.66941 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 46.3744 | 65.7727 | 94.5944 | 137.7226 | 202.6656 | 301.0001 | 450.6184 | 679.2303 | 1029.8289 | 1569.224 | 2401.3776 | 3688.2559 | 5682.4502 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 28.6811 | 40.6783 | 58.5036 | 85.177 | 125.3422 | 186.159 | 278.6931 | 420.0823 | 636.9163 | 970.515 | 1485.1754 | 2281.0686 | 3514.4142 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5494 | 13.5467 | 31.372 | 58.0454 | 98.2105 | 159.0273 | 251.5614 | 392.9506 | 609.7847 | 943.3833 | 1452.7005 | 2238.0212 | 3456.8539 | 4866.6688 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5494 | 13.5467 | 31.372 | 58.0454 | 98.2105 | 159.0273 | 251.5614 | 392.9506 | 609.7847 | 943.3833 | 1452.7005 | 2238.0212 | 3456.8539 | 4866.6688 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 15.5075 | 21.9943 | 31.6323 | 46.0543 | 67.7711 | 100.6541 | 150.6862 | 227.1338 | 344.3735 | 524.7465 | 803.0177 | 1233.3482 | 1900.2043 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83774 | 7.3245 | 16.9625 | 31.3845 | 53.1013 | 85.9843 | 136.0164 | 212.464 | 329.7037 | 510.0767 | 785.4588 | 1210.0729 | 1869.0821 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1858 | 3.1001 | 4.4585 | 6.4913 | 9.5523 | 14.1871 | 21.2391 | 32.0143 | 48.5391 | 73.9625 | 113.1845 | 173.8392 | 267.8318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11808 | 1.0324 | 2.3908 | 4.4236 | 7.4846 | 12.1194 | 19.1714 | 29.9466 | 46.4714 | 71.8948 | 110.7096 | 170.5585 | 263.4452 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5052 | 21.9036 | 50.7253 | 93.8535 | 158.7964 | 257.131 | 406.7492 | 635.3612 | 985.9598 | 1525.3548 | 2348.8689 | 3618.6526 | 5589.3812 | 7868.9084 | 7824.1106 | 7761.8584 | 7675.0633 | 7553.6874 | 7383.4983 | 7144.2929 | 6807.3633 | 6331.8792 | 5659.7211
| FALSE | 1459 | 22015548 | ECA | ECA-KYM NO.1 | 66 | KYM NO.1 LINE | DISTANCE & DIR EF | Y | GE | GE_D30 | GE D30 | GE RELAYS | Digital |  | 0.016937 | 1 |  | 1.0927 | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.11385 |  | 5.2187 | 0.0096441 | 2.2376e-07 | 0.0096439 | 50.6318 | 0.024613 | 50.6564 | 27.3772 | 3.8586 | 0.21245 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.11385 |  | 43.9969 | 82.1047 | 43.9969 | 38.1077 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.542e-07 | 2.2376e-07 | 3.2926e-07 | 4.9041e-07 | 7.3813e-07 | 1.121e-06 | 1.7156e-06 | 2.6427e-06 | 4.0934e-06 | 6.3704e-06 | 9.9538e-06 | 1.5606e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 56.582 | 82.1047 | 120.8156 | 179.9497 | 270.848 | 411.3372 | 629.5034 | 969.6859 | 1502.0065 | 2337.5284 | 3652.3902 | 5726.249 | 8017.6194 | 8017.6194 | 8017.6194 | 8017.6194 | 8017.6194 | 8017.6194 | 8017.6194 | 8017.6194 | 8017.6194 | 8017.6194 |  | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 52.6616 | 69.806 | 93.3401 | 125.7907 | 170.719 | 233.1525 | 320.2005 | 441.9299 | 612.6147 | 852.5169 | 1190.4279 | 1667.2969 | 2341.4128 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 34.8926 | 50.6318 | 74.5038 | 110.9702 | 167.0247 | 253.6607 | 388.1979 | 597.9794 | 926.2473 | 1441.4914 | 2252.3315 | 3531.2249 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7609 | 23.5 | 47.3721 | 83.8384 | 139.893 | 226.529 | 361.0662 | 570.8477 | 899.1156 | 1409.0164 | 2209.284 | 3473.6645 | 4866.6801 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.016962 | 0.024613 | 0.036218 | 0.053945 | 0.081195 | 0.12331 | 0.18871 | 0.29069 | 0.45027 | 0.70074 | 1.0949 | 1.7166 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015787 | 0.020926 | 0.027982 | 0.03771 | 0.051178 | 0.069894 | 0.09599 | 0.13248 | 0.18365 | 0.25557 | 0.35687 | 0.49982 | 0.70191 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0037728 | 0.011424 | 0.023029 | 0.040756 | 0.068005 | 0.11012 | 0.17552 | 0.2775 | 0.43708 | 0.68496 | 1.074 | 1.6886 | 2.3658 | 2.3523 | 2.3336 | 2.3075 | 2.271 | 2.2199 | 2.148 | 2.0467 | 1.9037 | 1.7016 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7647 | 23.5115 | 47.3951 | 83.8792 | 139.961 | 226.6391 | 361.2417 | 571.1252 | 899.5527 | 1409.7014 | 2210.358 | 3475.3532 | 4869.0459 | 4841.3263 | 4802.8065 | 4749.1003 | 4673.9965 | 4568.6886 | 4420.6754 | 4212.1934 | 3917.978 | 3502.0667 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 18.8669 | 27.3772 | 40.2851 | 60.003 | 90.3124 | 137.1575 | 209.9035 | 323.335 | 500.8336 | 779.4325 | 1217.864 | 1909.3778 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1964 | 12.7068 | 25.6147 | 45.3325 | 75.6419 | 122.4871 | 195.233 | 308.6645 | 486.1631 | 761.8729 | 1194.5877 | 1878.2542 | 2631.4752 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6591 | 3.8586 | 5.6779 | 8.457 | 12.7289 | 19.3313 | 29.5843 | 45.5716 | 70.5887 | 109.8552 | 171.6488 | 269.1125 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59145 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2636 | 27.5166 | 43.504 | 68.5211 | 107.3803 | 168.3682 | 264.7259 | 370.8867 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.14641 | 0.21245 | 0.31262 | 0.46564 | 0.70085 | 1.0644 | 1.6289 | 2.5092 | 3.8866 | 6.0486 | 9.4509 | 14.8172 | 20.7464 | 20.7464 | 20.7464 | 20.7464 | 20.7464 | 20.7464 | 20.7464 | 20.7464 | 20.7464 | 20.7464 |  | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.13627 | 0.18063 | 0.24153 | 0.3255 | 0.44175 | 0.6033 | 0.82855 | 1.1435 | 1.5852 | 2.206 | 3.0803 | 4.3143 | 6.0586 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032565 | 0.098607 | 0.19878 | 0.35179 | 0.587 | 0.95053 | 1.5151 | 2.3953 | 3.7727 | 5.9123 | 9.2703 | 14.5757 | 20.4209 | 20.3046 | 20.143 | 19.9178 | 19.6028 | 19.1612 | 18.5404 | 17.666 | 16.4321 | 14.6877 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5851 | 38.1077 | 76.8187 | 135.9528 | 226.8511 | 367.3403 | 585.5064 | 925.689 | 1458.0096 | 2284.8669 | 3582.5842 | 5632.9089 | 7891.8287 | 7846.9004 | 7784.4669 | 7697.4189 | 7575.6895 | 7405.0047 | 7165.1025 | 6827.1916 | 6350.3225 | 5676.2066
| FALSE | 1460 | 22015547 | ECA | ECA-KYM NO.1 | 66 | KYM NO.1 LINE | DISTANCE & DIR EF | X | Schweitzer | SEL_311C_1 | SEL 311C | SEL 300s | Digital |  | 0.15703 | 1 |  | 1.0927 | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 1.0555 |  | 5.2187 | 0.0096441 | 2.0745e-06 | 0.009642 | 50.6327 | 0.2282 | 50.8609 | 27.3877 | 3.8586 | 1.9697 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 1.0555 |  | 45.0538 | 84.077 | 45.0538 | 39.0232 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.4296e-06 | 2.0745e-06 | 3.0526e-06 | 4.5467e-06 | 6.8434e-06 | 1.0393e-05 | 1.5905e-05 | 2.4501e-05 | 3.7951e-05 | 5.9062e-05 | 9.2284e-05 | 0.00014468 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 57.9412 | 84.077 | 123.7179 | 184.2725 | 277.3544 | 421.2185 | 644.6254 | 992.9799 | 1538.0881 | 2393.6811 | 3740.1288 | 5863.8064 | 8210.2207 | 8210.2207 | 8210.2207 | 8210.2207 | 8210.2207 | 8210.2207 | 8210.2207 | 8210.2207 | 8210.2207 | 8210.2207 |  | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 53.9266 | 71.4829 | 95.5823 | 128.8125 | 174.8201 | 238.7534 | 327.8924 | 452.5461 | 627.3311 | 872.9963 | 1219.0246 | 1707.3492 | 2397.6588 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 34.8933 | 50.6327 | 74.5052 | 110.9723 | 167.0279 | 253.6656 | 388.2054 | 597.9909 | 926.2651 | 1441.519 | 2252.3748 | 3531.2926 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.761 | 23.5005 | 47.373 | 83.84 | 139.8957 | 226.5333 | 361.0731 | 570.8586 | 899.1328 | 1409.0434 | 2209.3264 | 3473.7312 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.15726 | 0.2282 | 0.33579 | 0.50014 | 0.75278 | 1.1432 | 1.7496 | 2.6951 | 4.1746 | 6.4968 | 10.1512 | 15.9152 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034978 | 0.10591 | 0.21351 | 0.37786 | 0.6305 | 1.021 | 1.6273 | 2.5728 | 4.0523 | 6.3504 | 9.9572 | 15.6558 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.796 | 23.6064 | 47.5865 | 84.2179 | 140.5262 | 227.5543 | 362.7004 | 573.4314 | 903.1851 | 1415.3939 | 2219.2836 | 3489.387 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 18.8741 | 27.3877 | 40.3006 | 60.026 | 90.347 | 137.2102 | 209.9841 | 323.4591 | 501.0258 | 779.7317 | 1218.3314 | 1910.1106 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.198 | 12.7116 | 25.6245 | 45.3499 | 75.6709 | 122.5341 | 195.308 | 308.783 | 486.3497 | 762.1653 | 1195.0462 | 1878.975 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6592 | 3.8586 | 5.6779 | 8.457 | 12.7289 | 19.3314 | 29.5845 | 45.5719 | 70.5891 | 109.8557 | 171.6496 | 269.1138 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59146 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2637 | 27.5168 | 43.5042 | 68.5214 | 107.3808 | 168.369 | 264.7271 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.3574 | 1.9697 | 2.8984 | 4.317 | 6.4977 | 9.8681 | 15.1019 | 23.263 | 36.0335 | 56.0779 | 87.6218 | 137.3742 | 192.3448 | 192.3448 | 192.3448 | 192.3448 | 192.3448 | 192.3448 | 192.3448 | 192.3448 | 192.3448 | 192.3448 |  | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.2634 | 1.6747 | 2.2393 | 3.0178 | 4.0956 | 5.5934 | 7.6817 | 10.602 | 14.6968 | 20.4521 | 28.5587 | 39.9989 | 56.1711 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30192 | 0.91421 | 1.8429 | 3.2615 | 5.4422 | 8.8126 | 14.0465 | 22.2075 | 34.978 | 54.8145 | 85.9471 | 135.1349 | 189.327 | 188.2492 | 186.7514 | 184.6631 | 181.7427 | 177.648 | 171.8927 | 163.7861 | 152.3459 | 136.1737 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.8874 | 39.0232 | 78.6641 | 139.2186 | 232.3006 | 376.1647 | 599.5716 | 947.9261 | 1493.0342 | 2339.7545 | 3668.6459 | 5768.2241 | 8081.4082 | 8035.4006 | 7971.4673 | 7882.3283 | 7757.6746 | 7582.8896 | 7337.2244 | 6991.1961 | 6502.8715 | 5812.5619
| FALSE | 1461 | 22015550 | ECA | ECA-KYM NO.2 | 66 | KYM NO.2 LINE | DISTANCE & DIR EF | Y | GE | GE_D30 | GE D30 | GE RELAYS | Digital |  | 0.016937 | 1 |  | 1.0927 | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.11385 |  | 5.2187 | 0.0096441 | 2.2376e-07 | 0.0096439 | 50.6318 | 0.024613 | 50.6564 | 27.3772 | 3.8586 | 0.21245 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.11385 |  | 43.9969 | 82.1047 | 43.9969 | 38.1077 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.542e-07 | 2.2376e-07 | 3.2926e-07 | 4.9041e-07 | 7.3813e-07 | 1.121e-06 | 1.7156e-06 | 2.6427e-06 | 4.0934e-06 | 6.3704e-06 | 9.9538e-06 | 1.5606e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 56.582 | 82.1047 | 120.8156 | 179.9497 | 270.848 | 411.3372 | 629.5034 | 969.6859 | 1502.0065 | 2337.5284 | 3652.3902 | 5726.249 | 8017.6194 | 8017.6194 | 8017.6194 | 8017.6194 | 8017.6194 | 8017.6194 | 8017.6194 | 8017.6194 | 8017.6194 | 8017.6194 |  | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 43.9969 | 52.6616 | 69.806 | 93.3401 | 125.7907 | 170.719 | 233.1525 | 320.2005 | 441.9299 | 612.6147 | 852.5169 | 1190.4279 | 1667.2969 | 2341.4128 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 34.8926 | 50.6318 | 74.5038 | 110.9702 | 167.0247 | 253.6607 | 388.1979 | 597.9794 | 926.2473 | 1441.4914 | 2252.3315 | 3531.2249 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7609 | 23.5 | 47.3721 | 83.8384 | 139.893 | 226.529 | 361.0662 | 570.8477 | 899.1156 | 1409.0164 | 2209.284 | 3473.6645 | 4866.6801 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.016962 | 0.024613 | 0.036218 | 0.053945 | 0.081195 | 0.12331 | 0.18871 | 0.29069 | 0.45027 | 0.70074 | 1.0949 | 1.7166 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015787 | 0.020926 | 0.027982 | 0.03771 | 0.051178 | 0.069894 | 0.09599 | 0.13248 | 0.18365 | 0.25557 | 0.35687 | 0.49982 | 0.70191 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0037728 | 0.011424 | 0.023029 | 0.040756 | 0.068005 | 0.11012 | 0.17552 | 0.2775 | 0.43708 | 0.68496 | 1.074 | 1.6886 | 2.3658 | 2.3523 | 2.3336 | 2.3075 | 2.271 | 2.2199 | 2.148 | 2.0467 | 1.9037 | 1.7016 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7647 | 23.5115 | 47.3951 | 83.8792 | 139.961 | 226.6391 | 361.2417 | 571.1252 | 899.5527 | 1409.7014 | 2210.358 | 3475.3532 | 4869.0459 | 4841.3263 | 4802.8065 | 4749.1003 | 4673.9965 | 4568.6886 | 4420.6754 | 4212.1934 | 3917.978 | 3502.0667 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 18.8669 | 27.3772 | 40.2851 | 60.003 | 90.3124 | 137.1575 | 209.9035 | 323.335 | 500.8336 | 779.4325 | 1217.864 | 1909.3778 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1964 | 12.7068 | 25.6147 | 45.3325 | 75.6419 | 122.4871 | 195.233 | 308.6645 | 486.1631 | 761.8729 | 1194.5877 | 1878.2542 | 2631.4752 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6591 | 3.8586 | 5.6779 | 8.457 | 12.7289 | 19.3313 | 29.5843 | 45.5716 | 70.5887 | 109.8552 | 171.6488 | 269.1125 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59145 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2636 | 27.5166 | 43.504 | 68.5211 | 107.3803 | 168.3682 | 264.7259 | 370.8867 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.14641 | 0.21245 | 0.31262 | 0.46564 | 0.70085 | 1.0644 | 1.6289 | 2.5092 | 3.8866 | 6.0486 | 9.4509 | 14.8172 | 20.7464 | 20.7464 | 20.7464 | 20.7464 | 20.7464 | 20.7464 | 20.7464 | 20.7464 | 20.7464 | 20.7464 |  | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.11385 | 0.13627 | 0.18063 | 0.24153 | 0.3255 | 0.44175 | 0.6033 | 0.82855 | 1.1435 | 1.5852 | 2.206 | 3.0803 | 4.3143 | 6.0586 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032565 | 0.098607 | 0.19878 | 0.35179 | 0.587 | 0.95053 | 1.5151 | 2.3953 | 3.7727 | 5.9123 | 9.2703 | 14.5757 | 20.4209 | 20.3046 | 20.143 | 19.9178 | 19.6028 | 19.1612 | 18.5404 | 17.666 | 16.4321 | 14.6877 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5851 | 38.1077 | 76.8187 | 135.9528 | 226.8511 | 367.3403 | 585.5064 | 925.689 | 1458.0096 | 2284.8669 | 3582.5842 | 5632.9089 | 7891.8287 | 7846.9004 | 7784.4669 | 7697.4189 | 7575.6895 | 7405.0047 | 7165.1025 | 6827.1916 | 6350.3225 | 5676.2066
| FALSE | 1462 | 22015549 | ECA | ECA-KYM NO.2 | 66 | KYM NO.2 LINE | DISTANCE & DIR EF | X | Schweitzer | SEL_311C_1 | SEL 311C | SEL 300s | Digital |  | 0.15703 | 1 |  | 1.0927 | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 1.0555 |  | 5.2187 | 0.0096441 | 2.0745e-06 | 0.009642 | 50.6327 | 0.2282 | 50.8609 | 27.3877 | 3.8586 | 1.9697 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 1.0555 |  | 45.0538 | 84.077 | 45.0538 | 39.0232 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.4296e-06 | 2.0745e-06 | 3.0526e-06 | 4.5467e-06 | 6.8434e-06 | 1.0393e-05 | 1.5905e-05 | 2.4501e-05 | 3.7951e-05 | 5.9062e-05 | 9.2284e-05 | 0.00014468 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 57.9412 | 84.077 | 123.7179 | 184.2725 | 277.3544 | 421.2185 | 644.6254 | 992.9799 | 1538.0881 | 2393.6811 | 3740.1288 | 5863.8064 | 8210.2207 | 8210.2207 | 8210.2207 | 8210.2207 | 8210.2207 | 8210.2207 | 8210.2207 | 8210.2207 | 8210.2207 | 8210.2207 |  | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 45.0538 | 53.9266 | 71.4829 | 95.5823 | 128.8125 | 174.8201 | 238.7534 | 327.8924 | 452.5461 | 627.3311 | 872.9963 | 1219.0246 | 1707.3492 | 2397.6588 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 34.8933 | 50.6327 | 74.5052 | 110.9723 | 167.0279 | 253.6656 | 388.2054 | 597.9909 | 926.2651 | 1441.519 | 2252.3748 | 3531.2926 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.761 | 23.5005 | 47.373 | 83.84 | 139.8957 | 226.5333 | 361.0731 | 570.8586 | 899.1328 | 1409.0434 | 2209.3264 | 3473.7312 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.15726 | 0.2282 | 0.33579 | 0.50014 | 0.75278 | 1.1432 | 1.7496 | 2.6951 | 4.1746 | 6.4968 | 10.1512 | 15.9152 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034978 | 0.10591 | 0.21351 | 0.37786 | 0.6305 | 1.021 | 1.6273 | 2.5728 | 4.0523 | 6.3504 | 9.9572 | 15.6558 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.796 | 23.6064 | 47.5865 | 84.2179 | 140.5262 | 227.5543 | 362.7004 | 573.4314 | 903.1851 | 1415.3939 | 2219.2836 | 3489.387 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 18.8741 | 27.3877 | 40.3006 | 60.026 | 90.347 | 137.2102 | 209.9841 | 323.4591 | 501.0258 | 779.7317 | 1218.3314 | 1910.1106 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.198 | 12.7116 | 25.6245 | 45.3499 | 75.6709 | 122.5341 | 195.308 | 308.783 | 486.3497 | 762.1653 | 1195.0462 | 1878.975 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6592 | 3.8586 | 5.6779 | 8.457 | 12.7289 | 19.3314 | 29.5845 | 45.5719 | 70.5891 | 109.8557 | 171.6496 | 269.1138 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59146 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2637 | 27.5168 | 43.5042 | 68.5214 | 107.3808 | 168.369 | 264.7271 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.3574 | 1.9697 | 2.8984 | 4.317 | 6.4977 | 9.8681 | 15.1019 | 23.263 | 36.0335 | 56.0779 | 87.6218 | 137.3742 | 192.3448 | 192.3448 | 192.3448 | 192.3448 | 192.3448 | 192.3448 | 192.3448 | 192.3448 | 192.3448 | 192.3448 |  | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 1.2634 | 1.6747 | 2.2393 | 3.0178 | 4.0956 | 5.5934 | 7.6817 | 10.602 | 14.6968 | 20.4521 | 28.5587 | 39.9989 | 56.1711 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30192 | 0.91421 | 1.8429 | 3.2615 | 5.4422 | 8.8126 | 14.0465 | 22.2075 | 34.978 | 54.8145 | 85.9471 | 135.1349 | 189.327 | 188.2492 | 186.7514 | 184.6631 | 181.7427 | 177.648 | 171.8927 | 163.7861 | 152.3459 | 136.1737 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.8874 | 39.0232 | 78.6641 | 139.2186 | 232.3006 | 376.1647 | 599.5716 | 947.9261 | 1493.0342 | 2339.7545 | 3668.6459 | 5768.2241 | 8081.4082 | 8035.4006 | 7971.4673 | 7882.3283 | 7757.6746 | 7582.8896 | 7337.2244 | 6991.1961 | 6502.8715 | 5812.5619
| TRUE | 1463 | 22002627 | ECA | Blank | 66 | TRANS ALL | DIFFERENTIAL | Blank | AEI | PBD3_236 | PBD3 236 | PBD3 | Electromechanical |  | 0.066046 | 2190 |  | 6.6 | 0.003029 | 0.0005282 | 0.0025008 | 32.359 | 232.4065 | 264.7655 | 11.5968 | 1.2172 | 501.5127 |  | 8.6352 | 0.0061014 | 0.001064 | 0.0050375 | 65.1822 | 468.1476 | 533.3298 | 23.36 | 2.4518 | 1010.221 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.44395 |  | 779.0922 | 1569.3627 | 71.6536 | 1497.7091 |  | 0.026877 |  | 6.7798 | 6.9645 | 7.1542 | 7.3491 | 7.5493 | 7.755 | 7.9662 | 8.1832 | 8.4062 | 8.6352 | 8.8704 | 9.112 | 9.3603 | 9.6153 | 9.8772 | 10.1463 | 10.4227 | 10.7066 | 10.9983 | 11.2979 | 11.6057 | 11.9218 | 12.2466 | 12.5802 | 12.9229 | 13.2749 | 13.6366 | 14.0081 | 14.3897 | 14.7817 |  | 0.0032443 | 0.003476 | 0.0037255 | 0.003994 | 0.0042833 | 0.0045948 | 0.0049304 | 0.0052919 | 0.0056815 | 0.0061014 | 0.006554 | 0.007042 | 0.007568 | 0.0081353 | 0.0087472 | 0.0094071 | 0.010119 | 0.010887 | 0.011716 | 0.01261 | 0.013576 | 0.014618 | 0.015743 | 0.016957 | 0.018269 | 0.019685 | 0.021214 | 0.022866 | 0.02465 | 0.026577 |  | 0.00056574 | 0.00060615 | 0.00064965 | 0.00069648 | 0.00074692 | 0.00080124 | 0.00085976 | 0.00092281 | 0.00099075 | 0.001064 | 0.0011429 | 0.001228 | 0.0013197 | 0.0014186 | 0.0015253 | 0.0016404 | 0.0017646 | 0.0018985 | 0.002043 | 0.002199 | 0.0023674 | 0.0025491 | 0.0027452 | 0.002957 | 0.0031857 | 0.0034326 | 0.0036993 | 0.0039873 | 0.0042985 | 0.0046346 | 834.4683 | 894.0705 | 958.2327 | 1027.3159 | 1101.7102 | 1181.8374 | 1268.1531 | 1361.1502 | 1461.3614 | 1569.3627 | 1685.7768 | 1811.2771 | 1946.592 | 2092.5089 | 2249.8797 | 2419.6255 | 2602.743 | 2800.3098 | 3013.4922 | 3243.5516 | 3491.8526 | 3759.8719 | 4049.2069 | 4361.5864 | 4698.8808 | 5063.1144 | 5456.4777 | 5881.3414 | 6340.271 | 6836.0434 |  | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 53.2929 | 70.643 | 94.4592 | 127.2989 | 172.7658 | 235.9479 | 324.0395 | 447.2284 | 619.9597 | 862.7381 | 1204.7004 | 1687.2869 | 2369.4851 |  | 34.659 | 37.1345 | 39.7994 | 42.6688 | 45.7587 | 49.0867 | 52.6717 | 56.5343 | 60.6965 | 65.1822 | 70.0174 | 75.23 | 80.8502 | 86.9107 | 93.447 | 100.4972 | 108.1029 | 116.3087 | 125.163 | 134.7184 | 145.0314 | 156.1633 | 168.1806 | 181.1551 | 195.1643 | 210.2925 | 226.6305 | 244.2769 | 263.3382 | 283.9297 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 7.5271 | 10.0026 | 12.6675 | 15.5369 | 18.6268 | 21.9548 | 25.5398 | 29.4024 | 33.5646 | 38.0503 | 42.8855 | 48.0981 | 53.7183 | 59.7788 | 66.3151 | 73.3653 | 80.971 | 83.8335 | 82.1152 | 77.1576 | 67.4591 | 50.8848 | 24.4007 | -16.3053 | -77.3639 | -167.4932 | -299.0974 | -489.8331 | -764.8462 | -1159.9668 |  | 248.9254 | 266.705 | 285.8449 | 306.4527 | 328.6449 | 352.5471 | 378.2955 | 406.0369 | 435.9303 | 468.1476 | 502.8744 | 540.3117 | 580.6767 | 624.2043 | 671.1487 | 721.7846 | 776.4093 | 835.3444 | 898.9376 | 967.5653 | 1041.6345 | 1121.5858 | 1207.8957 | 1301.0798 | 1401.6962 | 1510.3486 | 1627.6906 | 1754.4292 | 1891.3298 | 2039.2209 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 248.7197 | 266.4993 | 285.6392 | 306.247 | 328.4391 | 352.3414 | 378.0898 | 405.8312 | 435.7246 | 467.9418 | 502.6687 | 540.106 | 580.471 | 623.9986 | 670.943 | 721.5789 | 776.2036 | 835.0981 | 898.6112 | 967.1288 | 1041.0463 | 1120.7875 | 1206.8054 | 1299.5825 | 1399.6297 | 1507.484 | 1623.7042 | 1748.8627 | 1883.5336 | 2028.2724 |  | 256.2468 | 276.5019 | 298.3067 | 321.7838 | 347.0659 | 374.2962 | 403.6296 | 435.2336 | 469.2892 | 505.9922 | 545.5542 | 588.204 | 634.1892 | 683.7774 | 737.258 | 794.9442 | 857.1746 | 918.9316 | 980.7264 | 1044.2864 | 1108.5054 | 1171.6723 | 1231.2062 | 1283.2772 | 1322.2658 | 1339.9908 | 1324.6068 | 1259.0296 | 1118.6873 | 868.3056 |  | 12.4211 | 13.3083 | 14.2633 | 15.2917 | 16.399 | 17.5917 | 18.8765 | 20.2608 | 21.7524 | 23.36 | 25.0929 | 26.961 | 28.9751 | 31.1471 | 33.4896 | 36.0163 | 38.742 | 41.6828 | 44.856 | 48.2804 | 51.9764 | 55.9659 | 60.2727 | 64.9224 | 69.9431 | 75.3647 | 81.22 | 87.5441 | 94.3753 | 101.7549 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | -2.2513 | -1.3642 | -0.40909 | 0.61921 | 1.7266 | 2.9193 | 4.2041 | 5.5884 | 7.08 | 8.6876 | 10.4204 | 12.2885 | 14.3027 | 16.4747 | 18.8171 | 21.3438 | 24.0695 | 24.1208 | 21.5765 | 17.1526 | 10.0267 | -0.96682 | -17.4809 | -41.8605 | -77.4352 | -128.9349 | -203.0841 | -309.4492 | -461.6481 | -679.0779 |  | 1.3037 | 1.3968 | 1.4971 | 1.605 | 1.7212 | 1.8464 | 1.9812 | 2.1265 | 2.2831 | 2.4518 | 2.6337 | 2.8298 | 3.0412 | 3.2691 | 3.515 | 3.7802 | 4.0663 | 4.3749 | 4.708 | 5.0674 | 5.4553 | 5.8741 | 6.3261 | 6.8141 | 7.3411 | 7.9101 | 8.5247 | 9.1885 | 9.9054 | 10.68 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | -0.764 | -0.67088 | -0.57064 | -0.46271 | -0.34649 | -0.2213 | -0.086453 | 0.058837 | 0.2154 | 0.38413 | 0.566 | 0.76207 | 0.97348 | 1.2014 | 1.4473 | 1.7125 | 1.9986 | 1.9 | 1.4274 | 0.68077 | -0.45637 | -2.1491 | -4.6312 | -8.2341 | -13.428 | -20.8805 | -31.5405 | -46.7573 | -68.4515 | -99.3579 |  | 537.1591 | 575.5258 | 616.828 | 661.2978 | 709.1865 | 760.7655 | 816.3281 | 876.1917 | 940.6991 | 1010.221 | 1085.1584 | 1165.9447 | 1253.0488 | 1346.9776 | 1448.2794 | 1557.5472 | 1675.4225 | 1802.5991 | 1939.8276 | 2087.9201 | 2247.755 | 2420.2828 | 2606.5318 | 2807.6149 | 3024.7361 | 3259.1985 | 3512.412 | 3785.9027 | 4081.3222 | 4400.458 |  | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.53138 | 0.70437 | 0.94184 | 1.2693 | 1.7226 | 2.3526 | 3.2309 | 4.4592 | 6.1815 | 8.6022 | 12.0119 | 16.8237 | 23.6257 |  | 536.7151 | 575.0819 | 616.384 | 660.8539 | 708.7425 | 760.3215 | 815.8842 | 875.7477 | 940.2551 | 1009.777 | 1084.7144 | 1165.5008 | 1252.6049 | 1346.5337 | 1447.8355 | 1557.1033 | 1674.9786 | 1802.0677 | 1939.1233 | 2086.9783 | 2246.4857 | 2418.5602 | 2604.1792 | 2804.384 | 3020.2769 | 3253.017 | 3503.8098 | 3773.8909 | 4064.4986 | 4376.8322 |  | 789.9466 | 849.5487 | 913.711 | 982.7942 | 1057.1885 | 1137.3157 | 1223.6314 | 1316.6285 | 1416.8397 | 1524.841 | 1641.2551 | 1766.7554 | 1902.0703 | 2047.9872 | 2205.358 | 2375.1038 | 2558.2212 | 2747.0201 | 2942.8536 | 3149.0981 | 3364.5615 | 3587.1165 | 3813.2733 | 4037.5665 | 4251.6795 | 4443.1924 | 4593.7919 | 4676.714 | 4653.0864 | 4466.702
| TRUE | 1464 | 22002628 | ECA | Blank | 66 | TRANS ALL | DIFFERENTIAL | Blank | AEI | PBD3_236 | PBD3 236 | PBD3 | Electromechanical |  | 0.066046 | 2190 |  | 6.6 | 0.003029 | 0.0005282 | 0.0025008 | 32.359 | 232.4065 | 264.7655 | 11.5968 | 1.2172 | 501.5127 |  | 8.6352 | 0.0061014 | 0.001064 | 0.0050375 | 65.1822 | 468.1476 | 533.3298 | 23.36 | 2.4518 | 1010.221 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.44395 |  | 779.0922 | 1569.3627 | 71.6536 | 1497.7091 |  | 0.026877 |  | 6.7798 | 6.9645 | 7.1542 | 7.3491 | 7.5493 | 7.755 | 7.9662 | 8.1832 | 8.4062 | 8.6352 | 8.8704 | 9.112 | 9.3603 | 9.6153 | 9.8772 | 10.1463 | 10.4227 | 10.7066 | 10.9983 | 11.2979 | 11.6057 | 11.9218 | 12.2466 | 12.5802 | 12.9229 | 13.2749 | 13.6366 | 14.0081 | 14.3897 | 14.7817 |  | 0.0032443 | 0.003476 | 0.0037255 | 0.003994 | 0.0042833 | 0.0045948 | 0.0049304 | 0.0052919 | 0.0056815 | 0.0061014 | 0.006554 | 0.007042 | 0.007568 | 0.0081353 | 0.0087472 | 0.0094071 | 0.010119 | 0.010887 | 0.011716 | 0.01261 | 0.013576 | 0.014618 | 0.015743 | 0.016957 | 0.018269 | 0.019685 | 0.021214 | 0.022866 | 0.02465 | 0.026577 |  | 0.00056574 | 0.00060615 | 0.00064965 | 0.00069648 | 0.00074692 | 0.00080124 | 0.00085976 | 0.00092281 | 0.00099075 | 0.001064 | 0.0011429 | 0.001228 | 0.0013197 | 0.0014186 | 0.0015253 | 0.0016404 | 0.0017646 | 0.0018985 | 0.002043 | 0.002199 | 0.0023674 | 0.0025491 | 0.0027452 | 0.002957 | 0.0031857 | 0.0034326 | 0.0036993 | 0.0039873 | 0.0042985 | 0.0046346 | 834.4683 | 894.0705 | 958.2327 | 1027.3159 | 1101.7102 | 1181.8374 | 1268.1531 | 1361.1502 | 1461.3614 | 1569.3627 | 1685.7768 | 1811.2771 | 1946.592 | 2092.5089 | 2249.8797 | 2419.6255 | 2602.743 | 2800.3098 | 3013.4922 | 3243.5516 | 3491.8526 | 3759.8719 | 4049.2069 | 4361.5864 | 4698.8808 | 5063.1144 | 5456.4777 | 5881.3414 | 6340.271 | 6836.0434 |  | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 53.2929 | 70.643 | 94.4592 | 127.2989 | 172.7658 | 235.9479 | 324.0395 | 447.2284 | 619.9597 | 862.7381 | 1204.7004 | 1687.2869 | 2369.4851 |  | 34.659 | 37.1345 | 39.7994 | 42.6688 | 45.7587 | 49.0867 | 52.6717 | 56.5343 | 60.6965 | 65.1822 | 70.0174 | 75.23 | 80.8502 | 86.9107 | 93.447 | 100.4972 | 108.1029 | 116.3087 | 125.163 | 134.7184 | 145.0314 | 156.1633 | 168.1806 | 181.1551 | 195.1643 | 210.2925 | 226.6305 | 244.2769 | 263.3382 | 283.9297 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 7.5271 | 10.0026 | 12.6675 | 15.5369 | 18.6268 | 21.9548 | 25.5398 | 29.4024 | 33.5646 | 38.0503 | 42.8855 | 48.0981 | 53.7183 | 59.7788 | 66.3151 | 73.3653 | 80.971 | 83.8335 | 82.1152 | 77.1576 | 67.4591 | 50.8848 | 24.4007 | -16.3053 | -77.3639 | -167.4932 | -299.0974 | -489.8331 | -764.8462 | -1159.9668 |  | 248.9254 | 266.705 | 285.8449 | 306.4527 | 328.6449 | 352.5471 | 378.2955 | 406.0369 | 435.9303 | 468.1476 | 502.8744 | 540.3117 | 580.6767 | 624.2043 | 671.1487 | 721.7846 | 776.4093 | 835.3444 | 898.9376 | 967.5653 | 1041.6345 | 1121.5858 | 1207.8957 | 1301.0798 | 1401.6962 | 1510.3486 | 1627.6906 | 1754.4292 | 1891.3298 | 2039.2209 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 248.7197 | 266.4993 | 285.6392 | 306.247 | 328.4391 | 352.3414 | 378.0898 | 405.8312 | 435.7246 | 467.9418 | 502.6687 | 540.106 | 580.471 | 623.9986 | 670.943 | 721.5789 | 776.2036 | 835.0981 | 898.6112 | 967.1288 | 1041.0463 | 1120.7875 | 1206.8054 | 1299.5825 | 1399.6297 | 1507.484 | 1623.7042 | 1748.8627 | 1883.5336 | 2028.2724 |  | 256.2468 | 276.5019 | 298.3067 | 321.7838 | 347.0659 | 374.2962 | 403.6296 | 435.2336 | 469.2892 | 505.9922 | 545.5542 | 588.204 | 634.1892 | 683.7774 | 737.258 | 794.9442 | 857.1746 | 918.9316 | 980.7264 | 1044.2864 | 1108.5054 | 1171.6723 | 1231.2062 | 1283.2772 | 1322.2658 | 1339.9908 | 1324.6068 | 1259.0296 | 1118.6873 | 868.3056 |  | 12.4211 | 13.3083 | 14.2633 | 15.2917 | 16.399 | 17.5917 | 18.8765 | 20.2608 | 21.7524 | 23.36 | 25.0929 | 26.961 | 28.9751 | 31.1471 | 33.4896 | 36.0163 | 38.742 | 41.6828 | 44.856 | 48.2804 | 51.9764 | 55.9659 | 60.2727 | 64.9224 | 69.9431 | 75.3647 | 81.22 | 87.5441 | 94.3753 | 101.7549 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | -2.2513 | -1.3642 | -0.40909 | 0.61921 | 1.7266 | 2.9193 | 4.2041 | 5.5884 | 7.08 | 8.6876 | 10.4204 | 12.2885 | 14.3027 | 16.4747 | 18.8171 | 21.3438 | 24.0695 | 24.1208 | 21.5765 | 17.1526 | 10.0267 | -0.96682 | -17.4809 | -41.8605 | -77.4352 | -128.9349 | -203.0841 | -309.4492 | -461.6481 | -679.0779 |  | 1.3037 | 1.3968 | 1.4971 | 1.605 | 1.7212 | 1.8464 | 1.9812 | 2.1265 | 2.2831 | 2.4518 | 2.6337 | 2.8298 | 3.0412 | 3.2691 | 3.515 | 3.7802 | 4.0663 | 4.3749 | 4.708 | 5.0674 | 5.4553 | 5.8741 | 6.3261 | 6.8141 | 7.3411 | 7.9101 | 8.5247 | 9.1885 | 9.9054 | 10.68 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | -0.764 | -0.67088 | -0.57064 | -0.46271 | -0.34649 | -0.2213 | -0.086453 | 0.058837 | 0.2154 | 0.38413 | 0.566 | 0.76207 | 0.97348 | 1.2014 | 1.4473 | 1.7125 | 1.9986 | 1.9 | 1.4274 | 0.68077 | -0.45637 | -2.1491 | -4.6312 | -8.2341 | -13.428 | -20.8805 | -31.5405 | -46.7573 | -68.4515 | -99.3579 |  | 537.1591 | 575.5258 | 616.828 | 661.2978 | 709.1865 | 760.7655 | 816.3281 | 876.1917 | 940.6991 | 1010.221 | 1085.1584 | 1165.9447 | 1253.0488 | 1346.9776 | 1448.2794 | 1557.5472 | 1675.4225 | 1802.5991 | 1939.8276 | 2087.9201 | 2247.755 | 2420.2828 | 2606.5318 | 2807.6149 | 3024.7361 | 3259.1985 | 3512.412 | 3785.9027 | 4081.3222 | 4400.458 |  | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.53138 | 0.70437 | 0.94184 | 1.2693 | 1.7226 | 2.3526 | 3.2309 | 4.4592 | 6.1815 | 8.6022 | 12.0119 | 16.8237 | 23.6257 |  | 536.7151 | 575.0819 | 616.384 | 660.8539 | 708.7425 | 760.3215 | 815.8842 | 875.7477 | 940.2551 | 1009.777 | 1084.7144 | 1165.5008 | 1252.6049 | 1346.5337 | 1447.8355 | 1557.1033 | 1674.9786 | 1802.0677 | 1939.1233 | 2086.9783 | 2246.4857 | 2418.5602 | 2604.1792 | 2804.384 | 3020.2769 | 3253.017 | 3503.8098 | 3773.8909 | 4064.4986 | 4376.8322 |  | 789.9466 | 849.5487 | 913.711 | 982.7942 | 1057.1885 | 1137.3157 | 1223.6314 | 1316.6285 | 1416.8397 | 1524.841 | 1641.2551 | 1766.7554 | 1902.0703 | 2047.9872 | 2205.358 | 2375.1038 | 2558.2212 | 2747.0201 | 2942.8536 | 3149.0981 | 3364.5615 | 3587.1165 | 3813.2733 | 4037.5665 | 4251.6795 | 4443.1924 | 4593.7919 | 4676.714 | 4653.0864 | 4466.702
| TRUE | 1465 | 22002626 | ECA | Blank | 66 | TRANS ALL | DIFFERENTIAL | Blank | AEI | PBD3_236 | PBD3 236 | PBD3 | Electromechanical |  | 0.066046 | 2190 |  | 6.6 | 0.003029 | 0.0005282 | 0.0025008 | 32.359 | 232.4065 | 264.7655 | 11.5968 | 1.2172 | 501.5127 |  | 8.6352 | 0.0061014 | 0.001064 | 0.0050375 | 65.1822 | 468.1476 | 533.3298 | 23.36 | 2.4518 | 1010.221 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.44395 |  | 779.0922 | 1569.3627 | 71.6536 | 1497.7091 |  | 0.026877 |  | 6.7798 | 6.9645 | 7.1542 | 7.3491 | 7.5493 | 7.755 | 7.9662 | 8.1832 | 8.4062 | 8.6352 | 8.8704 | 9.112 | 9.3603 | 9.6153 | 9.8772 | 10.1463 | 10.4227 | 10.7066 | 10.9983 | 11.2979 | 11.6057 | 11.9218 | 12.2466 | 12.5802 | 12.9229 | 13.2749 | 13.6366 | 14.0081 | 14.3897 | 14.7817 |  | 0.0032443 | 0.003476 | 0.0037255 | 0.003994 | 0.0042833 | 0.0045948 | 0.0049304 | 0.0052919 | 0.0056815 | 0.0061014 | 0.006554 | 0.007042 | 0.007568 | 0.0081353 | 0.0087472 | 0.0094071 | 0.010119 | 0.010887 | 0.011716 | 0.01261 | 0.013576 | 0.014618 | 0.015743 | 0.016957 | 0.018269 | 0.019685 | 0.021214 | 0.022866 | 0.02465 | 0.026577 |  | 0.00056574 | 0.00060615 | 0.00064965 | 0.00069648 | 0.00074692 | 0.00080124 | 0.00085976 | 0.00092281 | 0.00099075 | 0.001064 | 0.0011429 | 0.001228 | 0.0013197 | 0.0014186 | 0.0015253 | 0.0016404 | 0.0017646 | 0.0018985 | 0.002043 | 0.002199 | 0.0023674 | 0.0025491 | 0.0027452 | 0.002957 | 0.0031857 | 0.0034326 | 0.0036993 | 0.0039873 | 0.0042985 | 0.0046346 | 834.4683 | 894.0705 | 958.2327 | 1027.3159 | 1101.7102 | 1181.8374 | 1268.1531 | 1361.1502 | 1461.3614 | 1569.3627 | 1685.7768 | 1811.2771 | 1946.592 | 2092.5089 | 2249.8797 | 2419.6255 | 2602.743 | 2800.3098 | 3013.4922 | 3243.5516 | 3491.8526 | 3759.8719 | 4049.2069 | 4361.5864 | 4698.8808 | 5063.1144 | 5456.4777 | 5881.3414 | 6340.271 | 6836.0434 |  | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 44.5244 | 53.2929 | 70.643 | 94.4592 | 127.2989 | 172.7658 | 235.9479 | 324.0395 | 447.2284 | 619.9597 | 862.7381 | 1204.7004 | 1687.2869 | 2369.4851 |  | 34.659 | 37.1345 | 39.7994 | 42.6688 | 45.7587 | 49.0867 | 52.6717 | 56.5343 | 60.6965 | 65.1822 | 70.0174 | 75.23 | 80.8502 | 86.9107 | 93.447 | 100.4972 | 108.1029 | 116.3087 | 125.163 | 134.7184 | 145.0314 | 156.1633 | 168.1806 | 181.1551 | 195.1643 | 210.2925 | 226.6305 | 244.2769 | 263.3382 | 283.9297 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 7.5271 | 10.0026 | 12.6675 | 15.5369 | 18.6268 | 21.9548 | 25.5398 | 29.4024 | 33.5646 | 38.0503 | 42.8855 | 48.0981 | 53.7183 | 59.7788 | 66.3151 | 73.3653 | 80.971 | 83.8335 | 82.1152 | 77.1576 | 67.4591 | 50.8848 | 24.4007 | -16.3053 | -77.3639 | -167.4932 | -299.0974 | -489.8331 | -764.8462 | -1159.9668 |  | 248.9254 | 266.705 | 285.8449 | 306.4527 | 328.6449 | 352.5471 | 378.2955 | 406.0369 | 435.9303 | 468.1476 | 502.8744 | 540.3117 | 580.6767 | 624.2043 | 671.1487 | 721.7846 | 776.4093 | 835.3444 | 898.9376 | 967.5653 | 1041.6345 | 1121.5858 | 1207.8957 | 1301.0798 | 1401.6962 | 1510.3486 | 1627.6906 | 1754.4292 | 1891.3298 | 2039.2209 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 248.7197 | 266.4993 | 285.6392 | 306.247 | 328.4391 | 352.3414 | 378.0898 | 405.8312 | 435.7246 | 467.9418 | 502.6687 | 540.106 | 580.471 | 623.9986 | 670.943 | 721.5789 | 776.2036 | 835.0981 | 898.6112 | 967.1288 | 1041.0463 | 1120.7875 | 1206.8054 | 1299.5825 | 1399.6297 | 1507.484 | 1623.7042 | 1748.8627 | 1883.5336 | 2028.2724 |  | 256.2468 | 276.5019 | 298.3067 | 321.7838 | 347.0659 | 374.2962 | 403.6296 | 435.2336 | 469.2892 | 505.9922 | 545.5542 | 588.204 | 634.1892 | 683.7774 | 737.258 | 794.9442 | 857.1746 | 918.9316 | 980.7264 | 1044.2864 | 1108.5054 | 1171.6723 | 1231.2062 | 1283.2772 | 1322.2658 | 1339.9908 | 1324.6068 | 1259.0296 | 1118.6873 | 868.3056 |  | 12.4211 | 13.3083 | 14.2633 | 15.2917 | 16.399 | 17.5917 | 18.8765 | 20.2608 | 21.7524 | 23.36 | 25.0929 | 26.961 | 28.9751 | 31.1471 | 33.4896 | 36.0163 | 38.742 | 41.6828 | 44.856 | 48.2804 | 51.9764 | 55.9659 | 60.2727 | 64.9224 | 69.9431 | 75.3647 | 81.22 | 87.5441 | 94.3753 | 101.7549 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | -2.2513 | -1.3642 | -0.40909 | 0.61921 | 1.7266 | 2.9193 | 4.2041 | 5.5884 | 7.08 | 8.6876 | 10.4204 | 12.2885 | 14.3027 | 16.4747 | 18.8171 | 21.3438 | 24.0695 | 24.1208 | 21.5765 | 17.1526 | 10.0267 | -0.96682 | -17.4809 | -41.8605 | -77.4352 | -128.9349 | -203.0841 | -309.4492 | -461.6481 | -679.0779 |  | 1.3037 | 1.3968 | 1.4971 | 1.605 | 1.7212 | 1.8464 | 1.9812 | 2.1265 | 2.2831 | 2.4518 | 2.6337 | 2.8298 | 3.0412 | 3.2691 | 3.515 | 3.7802 | 4.0663 | 4.3749 | 4.708 | 5.0674 | 5.4553 | 5.8741 | 6.3261 | 6.8141 | 7.3411 | 7.9101 | 8.5247 | 9.1885 | 9.9054 | 10.68 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | -0.764 | -0.67088 | -0.57064 | -0.46271 | -0.34649 | -0.2213 | -0.086453 | 0.058837 | 0.2154 | 0.38413 | 0.566 | 0.76207 | 0.97348 | 1.2014 | 1.4473 | 1.7125 | 1.9986 | 1.9 | 1.4274 | 0.68077 | -0.45637 | -2.1491 | -4.6312 | -8.2341 | -13.428 | -20.8805 | -31.5405 | -46.7573 | -68.4515 | -99.3579 |  | 537.1591 | 575.5258 | 616.828 | 661.2978 | 709.1865 | 760.7655 | 816.3281 | 876.1917 | 940.6991 | 1010.221 | 1085.1584 | 1165.9447 | 1253.0488 | 1346.9776 | 1448.2794 | 1557.5472 | 1675.4225 | 1802.5991 | 1939.8276 | 2087.9201 | 2247.755 | 2420.2828 | 2606.5318 | 2807.6149 | 3024.7361 | 3259.1985 | 3512.412 | 3785.9027 | 4081.3222 | 4400.458 |  | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.53138 | 0.70437 | 0.94184 | 1.2693 | 1.7226 | 2.3526 | 3.2309 | 4.4592 | 6.1815 | 8.6022 | 12.0119 | 16.8237 | 23.6257 |  | 536.7151 | 575.0819 | 616.384 | 660.8539 | 708.7425 | 760.3215 | 815.8842 | 875.7477 | 940.2551 | 1009.777 | 1084.7144 | 1165.5008 | 1252.6049 | 1346.5337 | 1447.8355 | 1557.1033 | 1674.9786 | 1802.0677 | 1939.1233 | 2086.9783 | 2246.4857 | 2418.5602 | 2604.1792 | 2804.384 | 3020.2769 | 3253.017 | 3503.8098 | 3773.8909 | 4064.4986 | 4376.8322 |  | 789.9466 | 849.5487 | 913.711 | 982.7942 | 1057.1885 | 1137.3157 | 1223.6314 | 1316.6285 | 1416.8397 | 1524.841 | 1641.2551 | 1766.7554 | 1902.0703 | 2047.9872 | 2205.358 | 2375.1038 | 2558.2212 | 2747.0201 | 2942.8536 | 3149.0981 | 3364.5615 | 3587.1165 | 3813.2733 | 4037.5665 | 4251.6795 | 4443.1924 | 4593.7919 | 4676.714 | 4653.0864 | 4466.702
| FALSE | 1466 | 22010598 | ECA | Blank | 66 | TRANS TR NO.1 | WTI | C | Schweitzer | SEL_2414 | SEL 2414 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 2.1077 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.44395 |  | 6.8646 | 0.019138 | 1.7315e-06 | 0.019136 | 100.476 | 0.19047 | 100.6665 | 54.3356 | 7.6572 | 1.644 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.44395 |  | 44.3674 | 164.3033 | 44.3674 | 119.9359 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.006032 | 0.0079547 | 0.01058 | 0.01418 | 0.019138 | 0.02599 | 0.035489 | 0.0487 | 0.06712 | 0.092864 | 0.12892 | 0.17952 | 0.25064 | 0.35077 | 0.49191 | 0.69112 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.4574e-07 | 7.1969e-07 | 9.5721e-07 | 1.283e-06 | 1.7315e-06 | 2.3514e-06 | 3.2109e-06 | 4.4061e-06 | 6.0726e-06 | 8.4018e-06 | 1.1664e-05 | 1.6242e-05 | 2.2677e-05 | 3.1735e-05 | 4.4505e-05 | 6.2529e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 51.7857 | 68.2918 | 90.8299 | 121.7403 | 164.3033 | 223.1248 | 304.682 | 418.0971 | 576.2327 | 797.2472 | 1106.8006 | 1541.1871 | 2151.7835 | 3011.3709 | 4223.1187 | 5933.3579 | 8085.1365 | 8085.1365 | 8085.1365 | 8085.1365 | 8085.1365 | 8085.1365 | 8085.1365 | 8085.1365 | 8085.1365 |  | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 53.105 | 70.3939 | 94.1261 | 126.85 | 172.1566 | 235.1159 | 322.8969 | 445.6514 | 617.7736 | 859.696 | 1200.4526 | 1681.3374 | 2361.1301 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 31.6684 | 41.7623 | 55.545 | 74.4476 | 100.476 | 136.447 | 186.3215 | 255.678 | 352.3823 | 487.5388 | 676.8393 | 942.4786 | 1315.8752 | 1841.5368 | 2582.5542 | 3628.4128 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 4.5365 | 14.6304 | 28.4131 | 47.3157 | 73.3441 | 109.3151 | 159.1896 | 228.546 | 325.2504 | 460.4068 | 649.7073 | 915.3467 | 1283.4 | 1798.489 | 2524.9934 | 3550.8405 | 4839.0065 | 4800.5052 | 4746.8247 | 4671.7569 | 4566.4994 | 4418.5572 | 4210.1751 | 3916.1007 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.060032 | 0.079166 | 0.10529 | 0.14113 | 0.19047 | 0.25865 | 0.3532 | 0.48467 | 0.66799 | 0.9242 | 1.283 | 1.7866 | 2.4944 | 3.4909 | 4.8956 | 6.8782 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0.0085995 | 0.027734 | 0.053861 | 0.089693 | 0.13903 | 0.20722 | 0.30177 | 0.43324 | 0.61656 | 0.87277 | 1.2316 | 1.7352 | 2.4329 | 3.4093 | 4.7865 | 6.7311 | 9.173 | 9.1 | 8.9983 | 8.856 | 8.6564 | 8.376 | 7.981 | 7.4235 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 4.5451 | 14.6581 | 28.4669 | 47.4053 | 73.4832 | 109.5223 | 159.4914 | 228.9793 | 325.8669 | 461.2796 | 650.939 | 917.0819 | 1285.8329 | 1801.8983 | 2529.7799 | 3557.5717 | 4848.1796 | 4809.6052 | 4755.823 | 4680.6129 | 4575.1558 | 4426.9331 | 4218.1561 | 3923.5242 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.1257 | 22.5843 | 30.0377 | 40.2599 | 54.3356 | 73.788 | 100.7593 | 138.266 | 190.5619 | 263.652 | 366.0223 | 509.6752 | 711.6013 | 995.8694 | 1396.5981 | 1962.1793 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 2.4532 | 7.9119 | 15.3653 | 25.5874 | 39.6632 | 59.1156 | 86.0868 | 123.5935 | 175.8894 | 248.9796 | 351.3499 | 495.0028 | 694.0393 | 972.59 | 1365.4703 | 1920.2296 | 2616.8462 | 2596.0254 | 2566.996 | 2526.4007 | 2469.4794 | 2389.4749 | 2276.7857 | 2117.7556 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4134 | 3.1827 | 4.233 | 5.6736 | 7.6572 | 10.3985 | 14.1994 | 19.485 | 26.8547 | 37.1548 | 51.5812 | 71.8254 | 100.2815 | 140.3417 | 196.8139 | 276.5177 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0.34572 | 1.115 | 2.1653 | 3.6059 | 5.5895 | 8.3308 | 12.1317 | 17.4173 | 24.787 | 35.0871 | 49.5136 | 69.7577 | 97.8066 | 137.0611 | 192.4272 | 270.606 | 368.7759 | 365.8417 | 361.7508 | 356.03 | 348.0084 | 336.7339 | 320.8533 | 298.4421 | 266.7611 |  | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.51817 | 0.68334 | 0.90885 | 1.2181 | 1.644 | 2.2326 | 3.0487 | 4.1835 | 5.7659 | 7.9773 | 11.0748 | 15.4213 | 21.531 | 30.1321 | 42.257 | 59.3699 | 80.9008 | 80.9008 | 80.9008 | 80.9008 | 80.9008 | 80.9008 | 80.9008 | 80.9008 | 80.9008 |  | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.53138 | 0.70437 | 0.94184 | 1.2693 | 1.7226 | 2.3526 | 3.2309 | 4.4592 | 6.1815 | 8.6022 | 12.0119 | 16.8237 | 23.6257 |  | 0 | 0 | 0 | 0 | 0 | 0.074228 | 0.23939 | 0.46491 | 0.7742 | 1.2001 | 1.7887 | 2.6047 | 3.7396 | 5.3219 | 7.5334 | 10.6308 | 14.9774 | 20.9996 | 29.4278 | 41.3152 | 58.1006 | 79.1782 | 78.5482 | 77.6699 | 76.4416 | 74.7193 | 72.2986 | 68.889 | 64.0772 | 57.2751 |  | 0 | 0 | 0 | 0 | 0 | 7.4183 | 23.9243 | 46.4625 | 77.3729 | 119.9359 | 178.7574 | 260.3146 | 373.7297 | 531.8653 | 752.8798 | 1062.4332 | 1496.8196 | 2098.6785 | 2940.9771 | 4128.9926 | 5806.5079 | 7912.9799 | 7850.0206 | 7762.2396 | 7639.4851 | 7467.3629 | 7225.4405 | 6884.684 | 6403.7991 | 5724.0064
| FALSE | 1467 | 22010599 | ECA | Blank | 66 | TRANS TR NO.2 | WTI | C | Schweitzer | SEL_2414 | SEL 2414 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 2.1077 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.44395 |  | 6.8646 | 0.019138 | 1.7315e-06 | 0.019136 | 100.476 | 0.19047 | 100.6665 | 54.3356 | 7.6572 | 1.644 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.44395 |  | 44.3674 | 164.3033 | 44.3674 | 119.9359 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.006032 | 0.0079547 | 0.01058 | 0.01418 | 0.019138 | 0.02599 | 0.035489 | 0.0487 | 0.06712 | 0.092864 | 0.12892 | 0.17952 | 0.25064 | 0.35077 | 0.49191 | 0.69112 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.4574e-07 | 7.1969e-07 | 9.5721e-07 | 1.283e-06 | 1.7315e-06 | 2.3514e-06 | 3.2109e-06 | 4.4061e-06 | 6.0726e-06 | 8.4018e-06 | 1.1664e-05 | 1.6242e-05 | 2.2677e-05 | 3.1735e-05 | 4.4505e-05 | 6.2529e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 51.7857 | 68.2918 | 90.8299 | 121.7403 | 164.3033 | 223.1248 | 304.682 | 418.0971 | 576.2327 | 797.2472 | 1106.8006 | 1541.1871 | 2151.7835 | 3011.3709 | 4223.1187 | 5933.3579 | 8085.1365 | 8085.1365 | 8085.1365 | 8085.1365 | 8085.1365 | 8085.1365 | 8085.1365 | 8085.1365 | 8085.1365 |  | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 44.3674 | 53.105 | 70.3939 | 94.1261 | 126.85 | 172.1566 | 235.1159 | 322.8969 | 445.6514 | 617.7736 | 859.696 | 1200.4526 | 1681.3374 | 2361.1301 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 31.6684 | 41.7623 | 55.545 | 74.4476 | 100.476 | 136.447 | 186.3215 | 255.678 | 352.3823 | 487.5388 | 676.8393 | 942.4786 | 1315.8752 | 1841.5368 | 2582.5542 | 3628.4128 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 4.5365 | 14.6304 | 28.4131 | 47.3157 | 73.3441 | 109.3151 | 159.1896 | 228.546 | 325.2504 | 460.4068 | 649.7073 | 915.3467 | 1283.4 | 1798.489 | 2524.9934 | 3550.8405 | 4839.0065 | 4800.5052 | 4746.8247 | 4671.7569 | 4566.4994 | 4418.5572 | 4210.1751 | 3916.1007 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.060032 | 0.079166 | 0.10529 | 0.14113 | 0.19047 | 0.25865 | 0.3532 | 0.48467 | 0.66799 | 0.9242 | 1.283 | 1.7866 | 2.4944 | 3.4909 | 4.8956 | 6.8782 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0.0085995 | 0.027734 | 0.053861 | 0.089693 | 0.13903 | 0.20722 | 0.30177 | 0.43324 | 0.61656 | 0.87277 | 1.2316 | 1.7352 | 2.4329 | 3.4093 | 4.7865 | 6.7311 | 9.173 | 9.1 | 8.9983 | 8.856 | 8.6564 | 8.376 | 7.981 | 7.4235 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 4.5451 | 14.6581 | 28.4669 | 47.4053 | 73.4832 | 109.5223 | 159.4914 | 228.9793 | 325.8669 | 461.2796 | 650.939 | 917.0819 | 1285.8329 | 1801.8983 | 2529.7799 | 3557.5717 | 4848.1796 | 4809.6052 | 4755.823 | 4680.6129 | 4575.1558 | 4426.9331 | 4218.1561 | 3923.5242 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.1257 | 22.5843 | 30.0377 | 40.2599 | 54.3356 | 73.788 | 100.7593 | 138.266 | 190.5619 | 263.652 | 366.0223 | 509.6752 | 711.6013 | 995.8694 | 1396.5981 | 1962.1793 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 2.4532 | 7.9119 | 15.3653 | 25.5874 | 39.6632 | 59.1156 | 86.0868 | 123.5935 | 175.8894 | 248.9796 | 351.3499 | 495.0028 | 694.0393 | 972.59 | 1365.4703 | 1920.2296 | 2616.8462 | 2596.0254 | 2566.996 | 2526.4007 | 2469.4794 | 2389.4749 | 2276.7857 | 2117.7556 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4134 | 3.1827 | 4.233 | 5.6736 | 7.6572 | 10.3985 | 14.1994 | 19.485 | 26.8547 | 37.1548 | 51.5812 | 71.8254 | 100.2815 | 140.3417 | 196.8139 | 276.5177 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0.34572 | 1.115 | 2.1653 | 3.6059 | 5.5895 | 8.3308 | 12.1317 | 17.4173 | 24.787 | 35.0871 | 49.5136 | 69.7577 | 97.8066 | 137.0611 | 192.4272 | 270.606 | 368.7759 | 365.8417 | 361.7508 | 356.03 | 348.0084 | 336.7339 | 320.8533 | 298.4421 | 266.7611 |  | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.51817 | 0.68334 | 0.90885 | 1.2181 | 1.644 | 2.2326 | 3.0487 | 4.1835 | 5.7659 | 7.9773 | 11.0748 | 15.4213 | 21.531 | 30.1321 | 42.257 | 59.3699 | 80.9008 | 80.9008 | 80.9008 | 80.9008 | 80.9008 | 80.9008 | 80.9008 | 80.9008 | 80.9008 |  | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.44395 | 0.53138 | 0.70437 | 0.94184 | 1.2693 | 1.7226 | 2.3526 | 3.2309 | 4.4592 | 6.1815 | 8.6022 | 12.0119 | 16.8237 | 23.6257 |  | 0 | 0 | 0 | 0 | 0 | 0.074228 | 0.23939 | 0.46491 | 0.7742 | 1.2001 | 1.7887 | 2.6047 | 3.7396 | 5.3219 | 7.5334 | 10.6308 | 14.9774 | 20.9996 | 29.4278 | 41.3152 | 58.1006 | 79.1782 | 78.5482 | 77.6699 | 76.4416 | 74.7193 | 72.2986 | 68.889 | 64.0772 | 57.2751 |  | 0 | 0 | 0 | 0 | 0 | 7.4183 | 23.9243 | 46.4625 | 77.3729 | 119.9359 | 178.7574 | 260.3146 | 373.7297 | 531.8653 | 752.8798 | 1062.4332 | 1496.8196 | 2098.6785 | 2940.9771 | 4128.9926 | 5806.5079 | 7912.9799 | 7850.0206 | 7762.2396 | 7639.4851 | 7467.3629 | 7225.4405 | 6884.684 | 6403.7991 | 5724.0064
| TRUE | 1657 | 22001511 | FDN | Blank | 66 | CB A | CB FAIL | X | ASEA | GROUP_3095 | GROUP 3095 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 449.3168 | 0 | 449.3168 | 121.4703 | 17.1211 | 0 |  | 17.4831 | 0.20743 | 0 | 0.20743 | 2178.0029 | 0 | 2178.0029 | 588.8108 | 82.9923 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 587.9082 | 2849.806 | 71.0008 | 2778.8052 |  | 0.05687 |  | 10.4793 | 11.0926 | 11.7417 | 12.4288 | 13.1561 | 13.926 | 14.7409 | 15.6035 | 16.5166 | 17.4831 | 18.5062 | 19.5892 | 20.7355 | 21.9489 | 23.2333 | 24.5929 | 26.032 | 27.5554 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049927 | 0.058305 | 0.06815 | 0.079725 | 0.093338 | 0.10936 | 0.12822 | 0.15042 | 0.17659 | 0.20743 | 0.24379 | 0.28667 | 0.33726 | 0.39695 | 0.46742 | 0.55062 | 0.64888 | 0.76496 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 685.926 | 801.0384 | 936.2986 | 1095.3134 | 1282.3441 | 1502.4263 | 1761.512 | 2066.6376 | 2426.1227 | 2849.806 | 3349.3244 | 3938.4439 | 4633.4509 | 5453.617 | 6421.7484 | 7564.8378 | 8914.8363 | 10509.5685 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 524.2283 | 612.2044 | 715.5789 | 837.1081 | 980.0488 | 1148.2496 | 1346.2594 | 1579.4558 | 1854.1972 | 2178.0029 | 2559.7666 | 3010.0091 | 3541.1777 | 4168.0007 | 4907.9083 | 5781.5299 | 6813.2845 | 8032.0802 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 497.0966 | 585.0728 | 688.4472 | 809.9764 | 952.9172 | 1121.118 | 1319.1278 | 1552.3241 | 1827.0655 | 2150.8712 | 2532.6349 | 2982.8775 | 3514.046 | 4140.8691 | 4880.7766 | 5754.3982 | 6786.1529 | 7999.6053 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 497.0966 | 585.0728 | 688.4472 | 809.9764 | 952.9172 | 1121.118 | 1319.1278 | 1552.3241 | 1827.0655 | 2150.8712 | 2532.6349 | 2982.8775 | 3514.046 | 4140.8691 | 4880.7766 | 5754.3982 | 6786.1529 | 7999.6053 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 141.7222 | 165.506 | 193.4527 | 226.3075 | 264.9507 | 310.4228 | 363.9537 | 426.997 | 501.2718 | 588.8108 | 692.0185 | 813.7391 | 957.3375 | 1126.7956 | 1326.8254 | 1563.0041 | 1841.9332 | 2171.4278 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 127.0524 | 150.8362 | 178.7829 | 211.6377 | 250.2809 | 295.7531 | 349.2839 | 412.3272 | 486.602 | 574.1411 | 677.3487 | 799.0693 | 942.6677 | 1112.1258 | 1312.1557 | 1548.3343 | 1827.2634 | 2153.869 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 19.9756 | 23.3279 | 27.267 | 31.8978 | 37.3445 | 43.7538 | 51.2989 | 60.1848 | 70.6537 | 82.9923 | 97.5393 | 114.6957 | 134.9357 | 158.8207 | 187.0147 | 220.3038 | 259.6186 | 306.0605 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 17.9079 | 21.2602 | 25.1993 | 29.8301 | 35.2768 | 41.6861 | 49.2312 | 58.1171 | 68.5861 | 80.9246 | 95.4716 | 112.628 | 132.868 | 156.753 | 184.947 | 218.2361 | 257.5509 | 303.5856 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 642.0569 | 757.1692 | 892.4294 | 1051.4442 | 1238.4749 | 1458.5571 | 1717.6429 | 2022.7685 | 2382.2535 | 2805.9368 | 3305.4553 | 3894.5747 | 4589.5818 | 5409.7479 | 6377.8793 | 7520.9687 | 8870.9672 | 10457.0599 | 10938.9268 | 10915.4611 | 10883.1047 | 10838.3069 | 10776.0547 | 10689.2596 | 10567.8837 | 10397.6946 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| TRUE | 1658 | 22001514 | FDN | Blank | 66 | CB A | CB FAIL | Y | ASEA | GROUP_3095 | GROUP 3095 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 449.3168 | 0 | 449.3168 | 121.4703 | 17.1211 | 0 |  | 17.4831 | 0.20743 | 0 | 0.20743 | 2178.0029 | 0 | 2178.0029 | 588.8108 | 82.9923 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 587.9082 | 2849.806 | 71.0008 | 2778.8052 |  | 0.05687 |  | 10.4793 | 11.0926 | 11.7417 | 12.4288 | 13.1561 | 13.926 | 14.7409 | 15.6035 | 16.5166 | 17.4831 | 18.5062 | 19.5892 | 20.7355 | 21.9489 | 23.2333 | 24.5929 | 26.032 | 27.5554 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049927 | 0.058305 | 0.06815 | 0.079725 | 0.093338 | 0.10936 | 0.12822 | 0.15042 | 0.17659 | 0.20743 | 0.24379 | 0.28667 | 0.33726 | 0.39695 | 0.46742 | 0.55062 | 0.64888 | 0.76496 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 685.926 | 801.0384 | 936.2986 | 1095.3134 | 1282.3441 | 1502.4263 | 1761.512 | 2066.6376 | 2426.1227 | 2849.806 | 3349.3244 | 3938.4439 | 4633.4509 | 5453.617 | 6421.7484 | 7564.8378 | 8914.8363 | 10509.5685 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 524.2283 | 612.2044 | 715.5789 | 837.1081 | 980.0488 | 1148.2496 | 1346.2594 | 1579.4558 | 1854.1972 | 2178.0029 | 2559.7666 | 3010.0091 | 3541.1777 | 4168.0007 | 4907.9083 | 5781.5299 | 6813.2845 | 8032.0802 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 497.0966 | 585.0728 | 688.4472 | 809.9764 | 952.9172 | 1121.118 | 1319.1278 | 1552.3241 | 1827.0655 | 2150.8712 | 2532.6349 | 2982.8775 | 3514.046 | 4140.8691 | 4880.7766 | 5754.3982 | 6786.1529 | 7999.6053 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 497.0966 | 585.0728 | 688.4472 | 809.9764 | 952.9172 | 1121.118 | 1319.1278 | 1552.3241 | 1827.0655 | 2150.8712 | 2532.6349 | 2982.8775 | 3514.046 | 4140.8691 | 4880.7766 | 5754.3982 | 6786.1529 | 7999.6053 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 141.7222 | 165.506 | 193.4527 | 226.3075 | 264.9507 | 310.4228 | 363.9537 | 426.997 | 501.2718 | 588.8108 | 692.0185 | 813.7391 | 957.3375 | 1126.7956 | 1326.8254 | 1563.0041 | 1841.9332 | 2171.4278 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 127.0524 | 150.8362 | 178.7829 | 211.6377 | 250.2809 | 295.7531 | 349.2839 | 412.3272 | 486.602 | 574.1411 | 677.3487 | 799.0693 | 942.6677 | 1112.1258 | 1312.1557 | 1548.3343 | 1827.2634 | 2153.869 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 19.9756 | 23.3279 | 27.267 | 31.8978 | 37.3445 | 43.7538 | 51.2989 | 60.1848 | 70.6537 | 82.9923 | 97.5393 | 114.6957 | 134.9357 | 158.8207 | 187.0147 | 220.3038 | 259.6186 | 306.0605 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 17.9079 | 21.2602 | 25.1993 | 29.8301 | 35.2768 | 41.6861 | 49.2312 | 58.1171 | 68.5861 | 80.9246 | 95.4716 | 112.628 | 132.868 | 156.753 | 184.947 | 218.2361 | 257.5509 | 303.5856 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 642.0569 | 757.1692 | 892.4294 | 1051.4442 | 1238.4749 | 1458.5571 | 1717.6429 | 2022.7685 | 2382.2535 | 2805.9368 | 3305.4553 | 3894.5747 | 4589.5818 | 5409.7479 | 6377.8793 | 7520.9687 | 8870.9672 | 10457.0599 | 10938.9268 | 10915.4611 | 10883.1047 | 10838.3069 | 10776.0547 | 10689.2596 | 10567.8837 | 10397.6946 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| TRUE | 1659 | 22001512 | FDN | Blank | 66 | CB TR NO.1 | CB FAIL | X | ASEA | GROUP_3095 | GROUP 3095 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 449.3168 | 0 | 449.3168 | 121.4703 | 17.1211 | 0 |  | 17.4831 | 0.20743 | 0 | 0.20743 | 2178.0029 | 0 | 2178.0029 | 588.8108 | 82.9923 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 587.9082 | 2849.806 | 71.0008 | 2778.8052 |  | 0.05687 |  | 10.4793 | 11.0926 | 11.7417 | 12.4288 | 13.1561 | 13.926 | 14.7409 | 15.6035 | 16.5166 | 17.4831 | 18.5062 | 19.5892 | 20.7355 | 21.9489 | 23.2333 | 24.5929 | 26.032 | 27.5554 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049927 | 0.058305 | 0.06815 | 0.079725 | 0.093338 | 0.10936 | 0.12822 | 0.15042 | 0.17659 | 0.20743 | 0.24379 | 0.28667 | 0.33726 | 0.39695 | 0.46742 | 0.55062 | 0.64888 | 0.76496 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 685.926 | 801.0384 | 936.2986 | 1095.3134 | 1282.3441 | 1502.4263 | 1761.512 | 2066.6376 | 2426.1227 | 2849.806 | 3349.3244 | 3938.4439 | 4633.4509 | 5453.617 | 6421.7484 | 7564.8378 | 8914.8363 | 10509.5685 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 524.2283 | 612.2044 | 715.5789 | 837.1081 | 980.0488 | 1148.2496 | 1346.2594 | 1579.4558 | 1854.1972 | 2178.0029 | 2559.7666 | 3010.0091 | 3541.1777 | 4168.0007 | 4907.9083 | 5781.5299 | 6813.2845 | 8032.0802 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 497.0966 | 585.0728 | 688.4472 | 809.9764 | 952.9172 | 1121.118 | 1319.1278 | 1552.3241 | 1827.0655 | 2150.8712 | 2532.6349 | 2982.8775 | 3514.046 | 4140.8691 | 4880.7766 | 5754.3982 | 6786.1529 | 7999.6053 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 497.0966 | 585.0728 | 688.4472 | 809.9764 | 952.9172 | 1121.118 | 1319.1278 | 1552.3241 | 1827.0655 | 2150.8712 | 2532.6349 | 2982.8775 | 3514.046 | 4140.8691 | 4880.7766 | 5754.3982 | 6786.1529 | 7999.6053 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 141.7222 | 165.506 | 193.4527 | 226.3075 | 264.9507 | 310.4228 | 363.9537 | 426.997 | 501.2718 | 588.8108 | 692.0185 | 813.7391 | 957.3375 | 1126.7956 | 1326.8254 | 1563.0041 | 1841.9332 | 2171.4278 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 127.0524 | 150.8362 | 178.7829 | 211.6377 | 250.2809 | 295.7531 | 349.2839 | 412.3272 | 486.602 | 574.1411 | 677.3487 | 799.0693 | 942.6677 | 1112.1258 | 1312.1557 | 1548.3343 | 1827.2634 | 2153.869 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 19.9756 | 23.3279 | 27.267 | 31.8978 | 37.3445 | 43.7538 | 51.2989 | 60.1848 | 70.6537 | 82.9923 | 97.5393 | 114.6957 | 134.9357 | 158.8207 | 187.0147 | 220.3038 | 259.6186 | 306.0605 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 17.9079 | 21.2602 | 25.1993 | 29.8301 | 35.2768 | 41.6861 | 49.2312 | 58.1171 | 68.5861 | 80.9246 | 95.4716 | 112.628 | 132.868 | 156.753 | 184.947 | 218.2361 | 257.5509 | 303.5856 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 642.0569 | 757.1692 | 892.4294 | 1051.4442 | 1238.4749 | 1458.5571 | 1717.6429 | 2022.7685 | 2382.2535 | 2805.9368 | 3305.4553 | 3894.5747 | 4589.5818 | 5409.7479 | 6377.8793 | 7520.9687 | 8870.9672 | 10457.0599 | 10938.9268 | 10915.4611 | 10883.1047 | 10838.3069 | 10776.0547 | 10689.2596 | 10567.8837 | 10397.6946 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| TRUE | 1660 | 22001515 | FDN | Blank | 66 | CB TR NO.1 | CB FAIL | Y | ASEA | GROUP_3095 | GROUP 3095 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 449.3168 | 0 | 449.3168 | 121.4703 | 17.1211 | 0 |  | 17.4831 | 0.20743 | 0 | 0.20743 | 2178.0029 | 0 | 2178.0029 | 588.8108 | 82.9923 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 587.9082 | 2849.806 | 71.0008 | 2778.8052 |  | 0.05687 |  | 10.4793 | 11.0926 | 11.7417 | 12.4288 | 13.1561 | 13.926 | 14.7409 | 15.6035 | 16.5166 | 17.4831 | 18.5062 | 19.5892 | 20.7355 | 21.9489 | 23.2333 | 24.5929 | 26.032 | 27.5554 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049927 | 0.058305 | 0.06815 | 0.079725 | 0.093338 | 0.10936 | 0.12822 | 0.15042 | 0.17659 | 0.20743 | 0.24379 | 0.28667 | 0.33726 | 0.39695 | 0.46742 | 0.55062 | 0.64888 | 0.76496 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 685.926 | 801.0384 | 936.2986 | 1095.3134 | 1282.3441 | 1502.4263 | 1761.512 | 2066.6376 | 2426.1227 | 2849.806 | 3349.3244 | 3938.4439 | 4633.4509 | 5453.617 | 6421.7484 | 7564.8378 | 8914.8363 | 10509.5685 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 524.2283 | 612.2044 | 715.5789 | 837.1081 | 980.0488 | 1148.2496 | 1346.2594 | 1579.4558 | 1854.1972 | 2178.0029 | 2559.7666 | 3010.0091 | 3541.1777 | 4168.0007 | 4907.9083 | 5781.5299 | 6813.2845 | 8032.0802 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 497.0966 | 585.0728 | 688.4472 | 809.9764 | 952.9172 | 1121.118 | 1319.1278 | 1552.3241 | 1827.0655 | 2150.8712 | 2532.6349 | 2982.8775 | 3514.046 | 4140.8691 | 4880.7766 | 5754.3982 | 6786.1529 | 7999.6053 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 497.0966 | 585.0728 | 688.4472 | 809.9764 | 952.9172 | 1121.118 | 1319.1278 | 1552.3241 | 1827.0655 | 2150.8712 | 2532.6349 | 2982.8775 | 3514.046 | 4140.8691 | 4880.7766 | 5754.3982 | 6786.1529 | 7999.6053 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 141.7222 | 165.506 | 193.4527 | 226.3075 | 264.9507 | 310.4228 | 363.9537 | 426.997 | 501.2718 | 588.8108 | 692.0185 | 813.7391 | 957.3375 | 1126.7956 | 1326.8254 | 1563.0041 | 1841.9332 | 2171.4278 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 127.0524 | 150.8362 | 178.7829 | 211.6377 | 250.2809 | 295.7531 | 349.2839 | 412.3272 | 486.602 | 574.1411 | 677.3487 | 799.0693 | 942.6677 | 1112.1258 | 1312.1557 | 1548.3343 | 1827.2634 | 2153.869 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 19.9756 | 23.3279 | 27.267 | 31.8978 | 37.3445 | 43.7538 | 51.2989 | 60.1848 | 70.6537 | 82.9923 | 97.5393 | 114.6957 | 134.9357 | 158.8207 | 187.0147 | 220.3038 | 259.6186 | 306.0605 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 17.9079 | 21.2602 | 25.1993 | 29.8301 | 35.2768 | 41.6861 | 49.2312 | 58.1171 | 68.5861 | 80.9246 | 95.4716 | 112.628 | 132.868 | 156.753 | 184.947 | 218.2361 | 257.5509 | 303.5856 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 642.0569 | 757.1692 | 892.4294 | 1051.4442 | 1238.4749 | 1458.5571 | 1717.6429 | 2022.7685 | 2382.2535 | 2805.9368 | 3305.4553 | 3894.5747 | 4589.5818 | 5409.7479 | 6377.8793 | 7520.9687 | 8870.9672 | 10457.0599 | 10938.9268 | 10915.4611 | 10883.1047 | 10838.3069 | 10776.0547 | 10689.2596 | 10567.8837 | 10397.6946 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| TRUE | 1661 | 22001516 | FDN | Blank | 66 | CB TR NO.2 | CB FAIL | Y | ASEA | GROUP_3095 | GROUP 3095 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 449.3168 | 0 | 449.3168 | 121.4703 | 17.1211 | 0 |  | 17.4831 | 0.20743 | 0 | 0.20743 | 2178.0029 | 0 | 2178.0029 | 588.8108 | 82.9923 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 587.9082 | 2849.806 | 71.0008 | 2778.8052 |  | 0.05687 |  | 10.4793 | 11.0926 | 11.7417 | 12.4288 | 13.1561 | 13.926 | 14.7409 | 15.6035 | 16.5166 | 17.4831 | 18.5062 | 19.5892 | 20.7355 | 21.9489 | 23.2333 | 24.5929 | 26.032 | 27.5554 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049927 | 0.058305 | 0.06815 | 0.079725 | 0.093338 | 0.10936 | 0.12822 | 0.15042 | 0.17659 | 0.20743 | 0.24379 | 0.28667 | 0.33726 | 0.39695 | 0.46742 | 0.55062 | 0.64888 | 0.76496 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 685.926 | 801.0384 | 936.2986 | 1095.3134 | 1282.3441 | 1502.4263 | 1761.512 | 2066.6376 | 2426.1227 | 2849.806 | 3349.3244 | 3938.4439 | 4633.4509 | 5453.617 | 6421.7484 | 7564.8378 | 8914.8363 | 10509.5685 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 524.2283 | 612.2044 | 715.5789 | 837.1081 | 980.0488 | 1148.2496 | 1346.2594 | 1579.4558 | 1854.1972 | 2178.0029 | 2559.7666 | 3010.0091 | 3541.1777 | 4168.0007 | 4907.9083 | 5781.5299 | 6813.2845 | 8032.0802 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 497.0966 | 585.0728 | 688.4472 | 809.9764 | 952.9172 | 1121.118 | 1319.1278 | 1552.3241 | 1827.0655 | 2150.8712 | 2532.6349 | 2982.8775 | 3514.046 | 4140.8691 | 4880.7766 | 5754.3982 | 6786.1529 | 7999.6053 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 497.0966 | 585.0728 | 688.4472 | 809.9764 | 952.9172 | 1121.118 | 1319.1278 | 1552.3241 | 1827.0655 | 2150.8712 | 2532.6349 | 2982.8775 | 3514.046 | 4140.8691 | 4880.7766 | 5754.3982 | 6786.1529 | 7999.6053 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 141.7222 | 165.506 | 193.4527 | 226.3075 | 264.9507 | 310.4228 | 363.9537 | 426.997 | 501.2718 | 588.8108 | 692.0185 | 813.7391 | 957.3375 | 1126.7956 | 1326.8254 | 1563.0041 | 1841.9332 | 2171.4278 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 127.0524 | 150.8362 | 178.7829 | 211.6377 | 250.2809 | 295.7531 | 349.2839 | 412.3272 | 486.602 | 574.1411 | 677.3487 | 799.0693 | 942.6677 | 1112.1258 | 1312.1557 | 1548.3343 | 1827.2634 | 2153.869 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 19.9756 | 23.3279 | 27.267 | 31.8978 | 37.3445 | 43.7538 | 51.2989 | 60.1848 | 70.6537 | 82.9923 | 97.5393 | 114.6957 | 134.9357 | 158.8207 | 187.0147 | 220.3038 | 259.6186 | 306.0605 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 17.9079 | 21.2602 | 25.1993 | 29.8301 | 35.2768 | 41.6861 | 49.2312 | 58.1171 | 68.5861 | 80.9246 | 95.4716 | 112.628 | 132.868 | 156.753 | 184.947 | 218.2361 | 257.5509 | 303.5856 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 642.0569 | 757.1692 | 892.4294 | 1051.4442 | 1238.4749 | 1458.5571 | 1717.6429 | 2022.7685 | 2382.2535 | 2805.9368 | 3305.4553 | 3894.5747 | 4589.5818 | 5409.7479 | 6377.8793 | 7520.9687 | 8870.9672 | 10457.0599 | 10938.9268 | 10915.4611 | 10883.1047 | 10838.3069 | 10776.0547 | 10689.2596 | 10567.8837 | 10397.6946 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| TRUE | 1662 | 22001513 | FDN | Blank | 66 | CB TR NO.2 | CB FAIL | X | ASEA | GROUP_3095 | GROUP 3095 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 449.3168 | 0 | 449.3168 | 121.4703 | 17.1211 | 0 |  | 17.4831 | 0.20743 | 0 | 0.20743 | 2178.0029 | 0 | 2178.0029 | 588.8108 | 82.9923 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 587.9082 | 2849.806 | 71.0008 | 2778.8052 |  | 0.05687 |  | 10.4793 | 11.0926 | 11.7417 | 12.4288 | 13.1561 | 13.926 | 14.7409 | 15.6035 | 16.5166 | 17.4831 | 18.5062 | 19.5892 | 20.7355 | 21.9489 | 23.2333 | 24.5929 | 26.032 | 27.5554 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049927 | 0.058305 | 0.06815 | 0.079725 | 0.093338 | 0.10936 | 0.12822 | 0.15042 | 0.17659 | 0.20743 | 0.24379 | 0.28667 | 0.33726 | 0.39695 | 0.46742 | 0.55062 | 0.64888 | 0.76496 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 685.926 | 801.0384 | 936.2986 | 1095.3134 | 1282.3441 | 1502.4263 | 1761.512 | 2066.6376 | 2426.1227 | 2849.806 | 3349.3244 | 3938.4439 | 4633.4509 | 5453.617 | 6421.7484 | 7564.8378 | 8914.8363 | 10509.5685 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 524.2283 | 612.2044 | 715.5789 | 837.1081 | 980.0488 | 1148.2496 | 1346.2594 | 1579.4558 | 1854.1972 | 2178.0029 | 2559.7666 | 3010.0091 | 3541.1777 | 4168.0007 | 4907.9083 | 5781.5299 | 6813.2845 | 8032.0802 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 497.0966 | 585.0728 | 688.4472 | 809.9764 | 952.9172 | 1121.118 | 1319.1278 | 1552.3241 | 1827.0655 | 2150.8712 | 2532.6349 | 2982.8775 | 3514.046 | 4140.8691 | 4880.7766 | 5754.3982 | 6786.1529 | 7999.6053 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 497.0966 | 585.0728 | 688.4472 | 809.9764 | 952.9172 | 1121.118 | 1319.1278 | 1552.3241 | 1827.0655 | 2150.8712 | 2532.6349 | 2982.8775 | 3514.046 | 4140.8691 | 4880.7766 | 5754.3982 | 6786.1529 | 7999.6053 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 141.7222 | 165.506 | 193.4527 | 226.3075 | 264.9507 | 310.4228 | 363.9537 | 426.997 | 501.2718 | 588.8108 | 692.0185 | 813.7391 | 957.3375 | 1126.7956 | 1326.8254 | 1563.0041 | 1841.9332 | 2171.4278 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 127.0524 | 150.8362 | 178.7829 | 211.6377 | 250.2809 | 295.7531 | 349.2839 | 412.3272 | 486.602 | 574.1411 | 677.3487 | 799.0693 | 942.6677 | 1112.1258 | 1312.1557 | 1548.3343 | 1827.2634 | 2153.869 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 19.9756 | 23.3279 | 27.267 | 31.8978 | 37.3445 | 43.7538 | 51.2989 | 60.1848 | 70.6537 | 82.9923 | 97.5393 | 114.6957 | 134.9357 | 158.8207 | 187.0147 | 220.3038 | 259.6186 | 306.0605 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 17.9079 | 21.2602 | 25.1993 | 29.8301 | 35.2768 | 41.6861 | 49.2312 | 58.1171 | 68.5861 | 80.9246 | 95.4716 | 112.628 | 132.868 | 156.753 | 184.947 | 218.2361 | 257.5509 | 303.5856 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 642.0569 | 757.1692 | 892.4294 | 1051.4442 | 1238.4749 | 1458.5571 | 1717.6429 | 2022.7685 | 2382.2535 | 2805.9368 | 3305.4553 | 3894.5747 | 4589.5818 | 5409.7479 | 6377.8793 | 7520.9687 | 8870.9672 | 10457.0599 | 10938.9268 | 10915.4611 | 10883.1047 | 10838.3069 | 10776.0547 | 10689.2596 | 10567.8837 | 10397.6946 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| TRUE | 1663 | 22009683 | FDN | FDN-CRO | 66 | CRO LINE | CURRENT DIFF & DEF | Y | Siemens | 7SD522 | 7SD522 | SIEMENS 7SD522 | Digital |  | 0.016937 | 1 |  | 3.4047 | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.00034542 |  | 9.2417 | 0.041791 | 9.696e-07 | 0.04179 | 219.401 | 0.10666 | 219.5076 | 118.6329 | 16.7204 | 0.0027933 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.00034542 |  | 43.8834 | 354.8637 | 43.8834 | 310.9803 |  | 0.099856 |  | 3.7623 | 4.1574 | 4.5939 | 5.0764 | 5.6094 | 6.1985 | 6.8494 | 7.5687 | 8.3635 | 9.2417 | 10.2122 | 11.2846 | 12.4696 | 13.7791 | 15.2261 | 16.825 | 18.5918 | 20.5441 | 22.7015 | 25.0854 | 27.7197 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0056413 | 0.0071108 | 0.0090201 | 0.011509 | 0.014763 | 0.01903 | 0.024639 | 0.03203 | 0.041791 | 0.054706 | 0.071825 | 0.094556 | 0.12478 | 0.16503 | 0.21869 | 0.29031 | 0.38601 | 0.51398 | 0.68527 | 0.9147 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.199e-07 | 1.3089e-07 | 1.6498e-07 | 2.0928e-07 | 2.6702e-07 | 3.4252e-07 | 4.4152e-07 | 5.7166e-07 | 7.4314e-07 | 9.696e-07 | 1.2692e-06 | 1.6665e-06 | 2.1938e-06 | 2.8951e-06 | 3.829e-06 | 5.074e-06 | 6.7357e-06 | 8.9559e-06 | 1.1925e-05 | 1.5899e-05 | 2.1222e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 43.8834 | 47.9033 | 60.3814 | 76.5936 | 97.727 | 125.3594 | 161.591 | 209.2207 | 271.9825 | 354.8637 | 464.5307 | 609.9027 | 802.9223 | 1059.5911 | 1401.3635 | 1857.0218 | 2465.1994 | 3277.7773 | 4364.4585 | 5818.9266 | 7767.1425 | 7996.936 | 7996.936 | 7996.936 | 7996.936 | 7996.936 | 7996.936 | 7996.936 | 7996.936 | 7996.936 |  | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 52.5257 | 69.6259 | 93.0993 | 125.4662 | 170.2786 | 232.551 | 319.3744 | 440.7898 | 611.0344 | 850.3176 | 1187.3569 | 1662.9957 | 2335.3726 |  | 27.1317 | 29.6171 | 37.3319 | 47.3554 | 60.4215 | 77.5057 | 99.9066 | 129.3545 | 168.1582 | 219.401 | 287.2046 | 377.0835 | 496.4214 | 655.1115 | 866.4186 | 1148.1377 | 1524.1546 | 2026.5457 | 2698.4062 | 3597.6577 | 4802.1778 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 0 | 2.4854 | 10.2002 | 20.2237 | 33.2898 | 50.374 | 72.7748 | 102.2228 | 141.0265 | 192.2692 | 260.0728 | 349.9518 | 469.2896 | 627.9798 | 839.2869 | 1121.006 | 1497.0228 | 1994.0707 | 2655.3587 | 3540.0974 | 4724.606 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.013189 | 0.014398 | 0.018148 | 0.023021 | 0.029372 | 0.037677 | 0.048567 | 0.062882 | 0.081746 | 0.10666 | 0.13962 | 0.18331 | 0.24132 | 0.31847 | 0.42119 | 0.55814 | 0.74093 | 0.98515 | 1.3118 | 1.7489 | 2.3345 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015787 | 0.020926 | 0.027982 | 0.03771 | 0.051178 | 0.069894 | 0.09599 | 0.13248 | 0.18365 | 0.25557 | 0.35687 | 0.49982 | 0.70191 |  | 0 | 0.0012082 | 0.0049585 | 0.0098312 | 0.016183 | 0.024488 | 0.035378 | 0.049693 | 0.068556 | 0.093467 | 0.12643 | 0.17012 | 0.22813 | 0.30528 | 0.408 | 0.54495 | 0.72774 | 0.96937 | 1.2908 | 1.7209 | 2.2967 | 2.3523 | 2.3336 | 2.3075 | 2.271 | 2.2199 | 2.148 | 2.0467 | 1.9037 | 1.7016 |  | 0 | 2.4866 | 10.2051 | 20.2335 | 33.3059 | 50.3985 | 72.8102 | 102.2725 | 141.095 | 192.3627 | 260.1993 | 350.1219 | 469.5178 | 628.2851 | 839.6949 | 1121.5509 | 1497.7506 | 1995.0401 | 2656.6495 | 3541.8183 | 4726.9028 | 4841.3263 | 4802.8065 | 4749.1003 | 4673.9965 | 4568.6886 | 4420.6754 | 4212.1934 | 3917.978 | 3502.0667 |  | 14.6705 | 16.0143 | 20.1858 | 25.6057 | 32.6707 | 41.9083 | 54.0207 | 69.9436 | 90.9252 | 118.6329 | 155.2951 | 203.8938 | 268.4213 | 354.2271 | 468.4835 | 620.8125 | 824.1296 | 1095.7788 | 1459.0622 | 1945.2989 | 2596.598 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 0 | 1.3439 | 5.5154 | 10.9352 | 18.0002 | 27.2379 | 39.3503 | 55.2731 | 76.2548 | 103.9624 | 140.6247 | 189.2233 | 253.7508 | 339.5566 | 453.813 | 606.1421 | 809.4591 | 1078.2192 | 1435.7859 | 1914.1753 | 2554.654 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 2.0677 | 2.2571 | 2.845 | 3.6089 | 4.6047 | 5.9067 | 7.6138 | 9.858 | 12.8152 | 16.7204 | 21.8877 | 28.7373 | 37.832 | 49.9257 | 66.0292 | 87.4989 | 116.1549 | 154.4418 | 205.6439 | 274.1753 | 365.971 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0.18941 | 0.77735 | 1.5412 | 2.537 | 3.839 | 5.5461 | 7.7903 | 10.7475 | 14.6527 | 19.82 | 26.6696 | 35.7643 | 47.858 | 63.9615 | 85.4312 | 114.0872 | 151.9669 | 202.3633 | 269.7887 | 360.0593 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.00034542 | 0.00037707 | 0.00047529 | 0.0006029 | 0.00076925 | 0.00098676 | 0.001272 | 0.0016469 | 0.0021409 | 0.0027933 | 0.0036565 | 0.0048008 | 0.0063201 | 0.0083405 | 0.011031 | 0.014617 | 0.019405 | 0.025801 | 0.034354 | 0.045803 | 0.061138 | 0.062947 | 0.062947 | 0.062947 | 0.062947 | 0.062947 | 0.062947 | 0.062947 | 0.062947 | 0.062947 |  | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00041345 | 0.00054805 | 0.00073282 | 0.0009876 | 0.0013403 | 0.0018305 | 0.0025139 | 0.0034696 | 0.0048097 | 0.0066932 | 0.0093462 | 0.01309 | 0.018383 |  | 0 | 3.1642e-05 | 0.00012986 | 0.00025748 | 0.00042383 | 0.00064133 | 0.00092653 | 0.0013014 | 0.0017955 | 0.0024479 | 0.0033111 | 0.0044554 | 0.0059747 | 0.0079951 | 0.010685 | 0.014272 | 0.019059 | 0.025387 | 0.033806 | 0.04507 | 0.060151 | 0.061607 | 0.061117 | 0.060433 | 0.059478 | 0.058138 | 0.056254 | 0.053601 | 0.049857 | 0.044565 |  | 0 | 4.0199 | 16.498 | 32.7102 | 53.8436 | 81.476 | 117.7076 | 165.3372 | 228.0991 | 310.9803 | 420.6472 | 566.0193 | 759.0389 | 1015.7076 | 1357.4801 | 1813.1384 | 2421.3159 | 3225.2516 | 4294.8325 | 5725.8273 | 7641.6763 | 7826.6574 | 7764.385 | 7677.5616 | 7556.1462 | 7385.9016 | 7146.6184 | 6809.5791 | 6333.9403 | 5661.5634
| TRUE | 1664 | 22015779 | FDN | FDN-CRO | 66 | CRO LINE | NEUTRAL DISPLACEMENT | X | EMAIL | GROUP_3242 | GROUP 3242 | GROUP 3000s | Electronic |  | 0.15703 | 2190 |  | 9.9 | 0.042792 | 0.015079 | 0.027713 | 465.1499 | 6634.8055 | 7099.9554 | 207.0778 | 17.2719 | 43.4407 |  | 17.4831 | 0.20743 | 0.073094 | 0.13433 | 2254.7515 | 32161.3269 | 34416.0783 | 1003.782 | 83.7232 | 210.5728 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.0032025 |  | 7367.7458 | 35714.1564 | 71.5006 | 35642.6558 |  | 0.05687 |  | 10.4793 | 11.0926 | 11.7417 | 12.4288 | 13.1561 | 13.926 | 14.7409 | 15.6035 | 16.5166 | 17.4831 | 18.5062 | 19.5892 | 20.7355 | 21.9489 | 23.2333 | 24.5929 | 26.032 | 27.5554 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049927 | 0.058305 | 0.06815 | 0.079725 | 0.093338 | 0.10936 | 0.12822 | 0.15042 | 0.17659 | 0.20743 | 0.24379 | 0.28667 | 0.33726 | 0.39695 | 0.46742 | 0.55062 | 0.64888 | 0.76496 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.017593 | 0.020546 | 0.024015 | 0.028093 | 0.032891 | 0.038535 | 0.045181 | 0.053007 | 0.062227 | 0.073094 | 0.085906 | 0.10102 | 0.11884 | 0.13988 | 0.16471 | 0.19403 | 0.22865 | 0.26956 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 8596.1181 | 10038.7216 | 11733.8212 | 13726.6164 | 16070.5102 | 18828.6105 | 22075.5082 | 25899.3836 | 30404.4996 | 35714.1564 | 41974.1894 | 49357.1145 | 58067.0373 | 68345.4705 | 80478.2252 | 94803.5772 | 111721.9422 | 131707.3424 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 |  | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 53.1139 | 70.4056 | 94.1418 | 126.8711 | 172.1853 | 235.155 | 322.9506 | 445.7255 | 617.8763 | 859.8389 | 1200.6521 | 1681.6169 | 2361.5226 |  | 542.701 | 633.7773 | 740.7945 | 866.6062 | 1014.5839 | 1188.7118 | 1393.699 | 1635.1128 | 1919.5355 | 2254.7515 | 2649.9678 | 3116.076 | 3665.962 | 4314.873 | 5080.8535 | 5985.2598 | 7053.3716 | 8315.1152 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 515.5688 | 606.6451 | 713.6623 | 839.4739 | 987.4516 | 1161.5795 | 1366.5668 | 1607.9805 | 1892.4032 | 2227.6192 | 2622.8356 | 3088.9438 | 3638.8297 | 4287.7408 | 5053.7213 | 5958.1276 | 7026.2393 | 8282.6396 | 8666.8427 | 8652.3296 | 8632.3178 | 8604.6112 | 8566.1093 | 8512.4282 | 8437.3594 | 8332.1006 | 8184.1565 | 7975.7719 | 7681.6938 | 7265.9765 |  | 7740.9799 | 9040.0737 | 10566.5455 | 12361.0983 | 14471.8225 | 16955.5481 | 19879.4458 | 23322.9236 | 27379.8726 | 32161.3269 | 37798.6144 | 44447.0891 | 52290.5524 | 61546.4913 | 72472.2846 | 85372.5564 | 100607.8895 | 118605.1503 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 7740.4907 | 9039.5846 | 10566.0563 | 12360.6091 | 14471.3334 | 16955.059 | 19878.9566 | 23322.4344 | 27379.3834 | 32160.8377 | 37798.1253 | 44446.6 | 52290.0632 | 61546.0021 | 72471.7954 | 85372.0673 | 100607.4003 | 118604.5648 | 124235.378 | 124235.1163 | 124234.7556 | 124234.2561 | 124233.562 | 124232.5942 | 124231.2409 | 124229.3434 | 124226.6763 | 124222.9196 | 124217.6181 | 124210.1237 |  | 8256.0595 | 9646.2297 | 11279.7186 | 13200.0831 | 15458.785 | 18116.6385 | 21245.5234 | 24930.415 | 29271.7867 | 34388.457 | 40420.9609 | 47535.5438 | 55928.893 | 65833.7429 | 77525.5167 | 91330.1949 | 107633.6397 | 126887.2044 | 132902.2207 | 132887.4459 | 132867.0733 | 132838.8672 | 132799.6713 | 132745.0224 | 132668.6004 | 132561.444 | 132410.8328 | 132198.6915 | 131899.3119 | 131476.1003 |  | 241.6025 | 282.1483 | 329.7908 | 385.8003 | 451.6777 | 529.1969 | 620.4542 | 727.928 | 854.5488 | 1003.782 | 1179.7265 | 1387.231 | 1632.032 | 1920.9177 | 2261.9208 | 2664.5492 | 3140.0567 | 3701.7663 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 226.9264 | 267.4722 | 315.1147 | 371.1242 | 437.0016 | 514.5208 | 605.7781 | 713.2519 | 839.8727 | 989.1059 | 1165.0504 | 1372.5549 | 1617.3559 | 1906.2416 | 2247.2447 | 2649.8731 | 3125.3806 | 3684.1999 | 3854.2294 | 3846.3791 | 3835.5545 | 3820.5678 | 3799.7417 | 3770.7051 | 3730.0997 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 20.1515 | 23.5334 | 27.5071 | 32.1787 | 37.6734 | 44.1391 | 51.7507 | 60.7149 | 71.276 | 83.7232 | 98.3984 | 115.7058 | 136.1242 | 160.2195 | 188.6618 | 222.2441 | 261.9051 | 308.7561 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 18.0838 | 21.4657 | 25.4394 | 30.111 | 35.6057 | 42.0714 | 49.683 | 58.6472 | 69.2083 | 81.6555 | 96.3307 | 113.6381 | 134.0565 | 158.1518 | 186.5941 | 220.1764 | 259.8374 | 306.2812 | 320.1342 | 319.0282 | 317.5031 | 315.3917 | 312.4575 | 308.3665 | 302.6457 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 50.6832 | 59.1889 | 69.1833 | 80.933 | 94.7527 | 111.0146 | 130.1585 | 152.7043 | 179.2668 | 210.5728 | 247.4824 | 291.0125 | 342.3668 | 402.969 | 474.5045 | 558.9676 | 658.7194 | 776.5545 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 |  | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0038332 | 0.0050812 | 0.0067942 | 0.0091563 | 0.012427 | 0.016971 | 0.023307 | 0.032168 | 0.044592 | 0.062054 | 0.086651 | 0.12136 | 0.17043 |  | 50.68 | 59.1857 | 69.1801 | 80.9298 | 94.7495 | 111.0114 | 130.1553 | 152.7011 | 179.2636 | 210.5696 | 247.4792 | 291.0093 | 342.3636 | 402.9658 | 474.5013 | 558.9644 | 658.7161 | 776.5507 | 813.4178 | 813.4161 | 813.4137 | 813.4105 | 813.4059 | 813.3996 | 813.3907 | 813.3783 | 813.3608 | 813.3362 | 813.3015 | 813.2524 |  | 8551.7498 | 9994.3533 | 11689.4528 | 13682.248 | 16026.1419 | 18784.2421 | 22031.1399 | 25855.0152 | 30360.1313 | 35669.788 | 41929.8211 | 49312.7461 | 58022.6689 | 68301.1021 | 80433.8569 | 94759.2088 | 111677.5738 | 131654.2362 | 137890.0021 | 137866.2693 | 137833.5447 | 137788.2371 | 137725.2765 | 137637.4936 | 137514.7364 | 137342.6105 | 137100.6829 | 136759.9191 | 136279.0239 | 135599.2166
| FALSE | 1665 | 22009681 | FDN | FDN-CRO | 66 | CRO LINE | CURRENT DIFF, DIST & DEF | X | Schweitzer | SEL_311L | SEL 311L | SEL 300s | Digital |  | 0.15703 | 1 |  | 4.0857 | 0.0054221 | 1.1663e-06 | 0.005421 | 28.4669 | 0.1283 | 28.5952 | 15.398 | 2.1694 | 0.0033601 |  | 11.2347 | 0.070957 | 1.5263e-05 | 0.070942 | 372.5341 | 1.679 | 374.213 | 201.5073 | 28.3902 | 0.043972 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.0032025 |  | 46.166 | 604.1545 | 44.0015 | 560.153 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0068474 | 0.0087043 | 0.011132 | 0.014316 | 0.018505 | 0.024029 | 0.031333 | 0.041011 | 0.053862 | 0.070957 | 0.093738 | 0.12414 | 0.16478 | 0.21915 | 0.292 | 0.38971 | 0.52087 | 0.69709 | 0.93404 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.4729e-06 | 1.8724e-06 | 2.3946e-06 | 3.0796e-06 | 3.9805e-06 | 5.1688e-06 | 6.7399e-06 | 8.8217e-06 | 1.1586e-05 | 1.5263e-05 | 2.0164e-05 | 2.6704e-05 | 3.5444e-05 | 4.7141e-05 | 6.2812e-05 | 8.3829e-05 | 0.00011204 | 0.00014995 | 0.00020092 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 58.3007 | 74.1116 | 94.783 | 121.8946 | 157.5566 | 204.5912 | 266.7774 | 349.1807 | 458.5974 | 604.1545 | 798.1182 | 1056.986 | 1402.9613 | 1865.9441 | 2486.2218 | 3318.1045 | 4434.8388 | 5935.2511 | 7952.7303 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 |  | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 52.6671 | 69.8133 | 93.3499 | 125.8039 | 170.7369 | 233.1769 | 320.234 | 441.9762 | 612.6789 | 852.6062 | 1190.5526 | 1667.4716 | 2341.6582 |  | 35.9494 | 45.6987 | 58.4451 | 75.1627 | 97.1526 | 126.1551 | 164.5004 | 215.312 | 282.7806 | 372.5341 | 492.1361 | 651.7593 | 865.0947 | 1150.5794 | 1533.0554 | 2046.0113 | 2734.6126 | 3659.7977 | 4903.8167 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 8.8171 | 18.5665 | 31.3129 | 48.0304 | 70.0204 | 99.0229 | 137.3682 | 188.1797 | 255.6483 | 345.4018 | 465.0038 | 624.627 | 837.9625 | 1123.4472 | 1505.9232 | 2018.8791 | 2707.4804 | 3627.3221 | 4860.7684 | 4886.7853 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.16202 | 0.20596 | 0.26341 | 0.33875 | 0.43786 | 0.56857 | 0.74139 | 0.97039 | 1.2745 | 1.679 | 2.218 | 2.9374 | 3.8989 | 5.1855 | 6.9093 | 9.2212 | 12.3246 | 16.4943 | 22.101 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0.039738 | 0.083677 | 0.14112 | 0.21647 | 0.31557 | 0.44629 | 0.6191 | 0.84811 | 1.1522 | 1.5567 | 2.0957 | 2.8151 | 3.7766 | 5.0633 | 6.787 | 9.0989 | 12.2023 | 16.348 | 21.907 | 22.0242 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 8.8569 | 18.6502 | 31.454 | 48.2469 | 70.3359 | 99.4691 | 137.9873 | 189.0278 | 256.8005 | 346.9585 | 467.0995 | 627.4422 | 841.7391 | 1128.5105 | 1512.7102 | 2027.978 | 2719.6827 | 3643.67 | 4882.6754 | 4908.8095 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 19.4454 | 24.7189 | 31.6135 | 40.6562 | 52.5508 | 68.2385 | 88.9799 | 116.4643 | 152.9588 | 201.5073 | 266.2012 | 352.543 | 467.9382 | 622.3596 | 829.2446 | 1106.7075 | 1479.1786 | 1979.6202 | 2652.5222 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 4.7693 | 10.0428 | 16.9374 | 25.9801 | 37.8747 | 53.5624 | 74.3038 | 101.7882 | 138.2827 | 186.8312 | 251.5251 | 337.8669 | 453.2621 | 607.6835 | 814.5685 | 1092.0314 | 1464.5025 | 1962.0538 | 2629.237 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.7396 | 3.4826 | 4.454 | 5.728 | 7.4038 | 9.6141 | 12.5363 | 16.4086 | 21.5502 | 28.3902 | 37.5048 | 49.6695 | 65.9274 | 87.6837 | 116.8315 | 155.923 | 208.4002 | 278.9069 | 373.7115 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0.67194 | 1.4149 | 2.3863 | 3.6603 | 5.3361 | 7.5464 | 10.4686 | 14.3409 | 19.4825 | 26.3225 | 35.4371 | 47.6018 | 63.8597 | 85.616 | 114.7638 | 153.8553 | 206.3325 | 276.432 | 370.4309 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.0042432 | 0.005394 | 0.0068985 | 0.0088717 | 0.011467 | 0.014891 | 0.019417 | 0.025414 | 0.033378 | 0.043972 | 0.058089 | 0.07693 | 0.10211 | 0.13581 | 0.18095 | 0.2415 | 0.32278 | 0.43198 | 0.57882 | 0.5836 | 0.5836 | 0.5836 | 0.5836 | 0.5836 | 0.5836 | 0.5836 | 0.5836 | 0.5836 | 0.5836 | 0.5836 |  | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0038332 | 0.0050812 | 0.0067942 | 0.0091563 | 0.012427 | 0.016971 | 0.023307 | 0.032168 | 0.044592 | 0.062054 | 0.086651 | 0.12136 | 0.17043 |  | 0.0010407 | 0.0021915 | 0.003696 | 0.0056692 | 0.0082648 | 0.011688 | 0.016214 | 0.022212 | 0.030175 | 0.040769 | 0.054886 | 0.073727 | 0.098908 | 0.1326 | 0.17775 | 0.2383 | 0.31957 | 0.42815 | 0.57373 | 0.57681 | 0.57444 | 0.57117 | 0.56663 | 0.56029 | 0.55143 | 0.53901 | 0.52155 | 0.49695 | 0.46224 | 0.41317 |  | 14.2991 | 30.1101 | 50.7814 | 77.893 | 113.555 | 160.5896 | 222.7759 | 305.1791 | 414.5959 | 560.153 | 754.1167 | 1012.9845 | 1358.9598 | 1821.9426 | 2442.2203 | 3274.103 | 4390.8373 | 5882.584 | 7882.917 | 7925.1097 | 7892.6556 | 7847.7226 | 7785.2826 | 7698.2255 | 7576.4833 | 7405.7806 | 7165.8533 | 6827.9069 | 6350.9879 | 5676.8014
| TRUE | 1666 | 22009682 | FDN | FDN-GTS | 66 | GTS LINE | CURRENT DIFF & DEF | Y | Siemens | 7SD522 | 7SD522 | SIEMENS 7SD522 | Digital |  | 0.016937 | 1 |  | 3.4047 | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.00034542 |  | 9.2417 | 0.041791 | 9.696e-07 | 0.04179 | 219.401 | 0.10666 | 219.5076 | 118.6329 | 16.7204 | 0.0027933 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.00034542 |  | 43.8834 | 354.8637 | 43.8834 | 310.9803 |  | 0.099856 |  | 3.7623 | 4.1574 | 4.5939 | 5.0764 | 5.6094 | 6.1985 | 6.8494 | 7.5687 | 8.3635 | 9.2417 | 10.2122 | 11.2846 | 12.4696 | 13.7791 | 15.2261 | 16.825 | 18.5918 | 20.5441 | 22.7015 | 25.0854 | 27.7197 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0056413 | 0.0071108 | 0.0090201 | 0.011509 | 0.014763 | 0.01903 | 0.024639 | 0.03203 | 0.041791 | 0.054706 | 0.071825 | 0.094556 | 0.12478 | 0.16503 | 0.21869 | 0.29031 | 0.38601 | 0.51398 | 0.68527 | 0.9147 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.199e-07 | 1.3089e-07 | 1.6498e-07 | 2.0928e-07 | 2.6702e-07 | 3.4252e-07 | 4.4152e-07 | 5.7166e-07 | 7.4314e-07 | 9.696e-07 | 1.2692e-06 | 1.6665e-06 | 2.1938e-06 | 2.8951e-06 | 3.829e-06 | 5.074e-06 | 6.7357e-06 | 8.9559e-06 | 1.1925e-05 | 1.5899e-05 | 2.1222e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 43.8834 | 47.9033 | 60.3814 | 76.5936 | 97.727 | 125.3594 | 161.591 | 209.2207 | 271.9825 | 354.8637 | 464.5307 | 609.9027 | 802.9223 | 1059.5911 | 1401.3635 | 1857.0218 | 2465.1994 | 3277.7773 | 4364.4585 | 5818.9266 | 7767.1425 | 7996.936 | 7996.936 | 7996.936 | 7996.936 | 7996.936 | 7996.936 | 7996.936 | 7996.936 | 7996.936 |  | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 52.5257 | 69.6259 | 93.0993 | 125.4662 | 170.2786 | 232.551 | 319.3744 | 440.7898 | 611.0344 | 850.3176 | 1187.3569 | 1662.9957 | 2335.3726 |  | 27.1317 | 29.6171 | 37.3319 | 47.3554 | 60.4215 | 77.5057 | 99.9066 | 129.3545 | 168.1582 | 219.401 | 287.2046 | 377.0835 | 496.4214 | 655.1115 | 866.4186 | 1148.1377 | 1524.1546 | 2026.5457 | 2698.4062 | 3597.6577 | 4802.1778 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 0 | 2.4854 | 10.2002 | 20.2237 | 33.2898 | 50.374 | 72.7748 | 102.2228 | 141.0265 | 192.2692 | 260.0728 | 349.9518 | 469.2896 | 627.9798 | 839.2869 | 1121.006 | 1497.0228 | 1994.0707 | 2655.3587 | 3540.0974 | 4724.606 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.013189 | 0.014398 | 0.018148 | 0.023021 | 0.029372 | 0.037677 | 0.048567 | 0.062882 | 0.081746 | 0.10666 | 0.13962 | 0.18331 | 0.24132 | 0.31847 | 0.42119 | 0.55814 | 0.74093 | 0.98515 | 1.3118 | 1.7489 | 2.3345 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015787 | 0.020926 | 0.027982 | 0.03771 | 0.051178 | 0.069894 | 0.09599 | 0.13248 | 0.18365 | 0.25557 | 0.35687 | 0.49982 | 0.70191 |  | 0 | 0.0012082 | 0.0049585 | 0.0098312 | 0.016183 | 0.024488 | 0.035378 | 0.049693 | 0.068556 | 0.093467 | 0.12643 | 0.17012 | 0.22813 | 0.30528 | 0.408 | 0.54495 | 0.72774 | 0.96937 | 1.2908 | 1.7209 | 2.2967 | 2.3523 | 2.3336 | 2.3075 | 2.271 | 2.2199 | 2.148 | 2.0467 | 1.9037 | 1.7016 |  | 0 | 2.4866 | 10.2051 | 20.2335 | 33.3059 | 50.3985 | 72.8102 | 102.2725 | 141.095 | 192.3627 | 260.1993 | 350.1219 | 469.5178 | 628.2851 | 839.6949 | 1121.5509 | 1497.7506 | 1995.0401 | 2656.6495 | 3541.8183 | 4726.9028 | 4841.3263 | 4802.8065 | 4749.1003 | 4673.9965 | 4568.6886 | 4420.6754 | 4212.1934 | 3917.978 | 3502.0667 |  | 14.6705 | 16.0143 | 20.1858 | 25.6057 | 32.6707 | 41.9083 | 54.0207 | 69.9436 | 90.9252 | 118.6329 | 155.2951 | 203.8938 | 268.4213 | 354.2271 | 468.4835 | 620.8125 | 824.1296 | 1095.7788 | 1459.0622 | 1945.2989 | 2596.598 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 0 | 1.3439 | 5.5154 | 10.9352 | 18.0002 | 27.2379 | 39.3503 | 55.2731 | 76.2548 | 103.9624 | 140.6247 | 189.2233 | 253.7508 | 339.5566 | 453.813 | 606.1421 | 809.4591 | 1078.2192 | 1435.7859 | 1914.1753 | 2554.654 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 2.0677 | 2.2571 | 2.845 | 3.6089 | 4.6047 | 5.9067 | 7.6138 | 9.858 | 12.8152 | 16.7204 | 21.8877 | 28.7373 | 37.832 | 49.9257 | 66.0292 | 87.4989 | 116.1549 | 154.4418 | 205.6439 | 274.1753 | 365.971 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0.18941 | 0.77735 | 1.5412 | 2.537 | 3.839 | 5.5461 | 7.7903 | 10.7475 | 14.6527 | 19.82 | 26.6696 | 35.7643 | 47.858 | 63.9615 | 85.4312 | 114.0872 | 151.9669 | 202.3633 | 269.7887 | 360.0593 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.00034542 | 0.00037707 | 0.00047529 | 0.0006029 | 0.00076925 | 0.00098676 | 0.001272 | 0.0016469 | 0.0021409 | 0.0027933 | 0.0036565 | 0.0048008 | 0.0063201 | 0.0083405 | 0.011031 | 0.014617 | 0.019405 | 0.025801 | 0.034354 | 0.045803 | 0.061138 | 0.062947 | 0.062947 | 0.062947 | 0.062947 | 0.062947 | 0.062947 | 0.062947 | 0.062947 | 0.062947 |  | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00034542 | 0.00041345 | 0.00054805 | 0.00073282 | 0.0009876 | 0.0013403 | 0.0018305 | 0.0025139 | 0.0034696 | 0.0048097 | 0.0066932 | 0.0093462 | 0.01309 | 0.018383 |  | 0 | 3.1642e-05 | 0.00012986 | 0.00025748 | 0.00042383 | 0.00064133 | 0.00092653 | 0.0013014 | 0.0017955 | 0.0024479 | 0.0033111 | 0.0044554 | 0.0059747 | 0.0079951 | 0.010685 | 0.014272 | 0.019059 | 0.025387 | 0.033806 | 0.04507 | 0.060151 | 0.061607 | 0.061117 | 0.060433 | 0.059478 | 0.058138 | 0.056254 | 0.053601 | 0.049857 | 0.044565 |  | 0 | 4.0199 | 16.498 | 32.7102 | 53.8436 | 81.476 | 117.7076 | 165.3372 | 228.0991 | 310.9803 | 420.6472 | 566.0193 | 759.0389 | 1015.7076 | 1357.4801 | 1813.1384 | 2421.3159 | 3225.2516 | 4294.8325 | 5725.8273 | 7641.6763 | 7826.6574 | 7764.385 | 7677.5616 | 7556.1462 | 7385.9016 | 7146.6184 | 6809.5791 | 6333.9403 | 5661.5634
| TRUE | 1667 | 22015778 | FDN | FDN-GTS | 66 | GTS LINE | NEUTRAL DISPLACEMENT | X | EMAIL | GROUP_3242 | GROUP 3242 | GROUP 3000s | Electronic |  | 0.15703 | 2190 |  | 9.9 | 0.042792 | 0.015079 | 0.027713 | 465.1499 | 6634.8055 | 7099.9554 | 207.0778 | 17.2719 | 43.4407 |  | 17.4831 | 0.20743 | 0.073094 | 0.13433 | 2254.7515 | 32161.3269 | 34416.0783 | 1003.782 | 83.7232 | 210.5728 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.0032025 |  | 7367.7458 | 35714.1564 | 71.5006 | 35642.6558 |  | 0.05687 |  | 10.4793 | 11.0926 | 11.7417 | 12.4288 | 13.1561 | 13.926 | 14.7409 | 15.6035 | 16.5166 | 17.4831 | 18.5062 | 19.5892 | 20.7355 | 21.9489 | 23.2333 | 24.5929 | 26.032 | 27.5554 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.049927 | 0.058305 | 0.06815 | 0.079725 | 0.093338 | 0.10936 | 0.12822 | 0.15042 | 0.17659 | 0.20743 | 0.24379 | 0.28667 | 0.33726 | 0.39695 | 0.46742 | 0.55062 | 0.64888 | 0.76496 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.017593 | 0.020546 | 0.024015 | 0.028093 | 0.032891 | 0.038535 | 0.045181 | 0.053007 | 0.062227 | 0.073094 | 0.085906 | 0.10102 | 0.11884 | 0.13988 | 0.16471 | 0.19403 | 0.22865 | 0.26956 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 8596.1181 | 10038.7216 | 11733.8212 | 13726.6164 | 16070.5102 | 18828.6105 | 22075.5082 | 25899.3836 | 30404.4996 | 35714.1564 | 41974.1894 | 49357.1145 | 58067.0373 | 68345.4705 | 80478.2252 | 94803.5772 | 111721.9422 | 131707.3424 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 | 137960.3975 |  | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 44.3748 | 53.1139 | 70.4056 | 94.1418 | 126.8711 | 172.1853 | 235.155 | 322.9506 | 445.7255 | 617.8763 | 859.8389 | 1200.6521 | 1681.6169 | 2361.5226 |  | 542.701 | 633.7773 | 740.7945 | 866.6062 | 1014.5839 | 1188.7118 | 1393.699 | 1635.1128 | 1919.5355 | 2254.7515 | 2649.9678 | 3116.076 | 3665.962 | 4314.873 | 5080.8535 | 5985.2598 | 7053.3716 | 8315.1152 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 515.5688 | 606.6451 | 713.6623 | 839.4739 | 987.4516 | 1161.5795 | 1366.5668 | 1607.9805 | 1892.4032 | 2227.6192 | 2622.8356 | 3088.9438 | 3638.8297 | 4287.7408 | 5053.7213 | 5958.1276 | 7026.2393 | 8282.6396 | 8666.8427 | 8652.3296 | 8632.3178 | 8604.6112 | 8566.1093 | 8512.4282 | 8437.3594 | 8332.1006 | 8184.1565 | 7975.7719 | 7681.6938 | 7265.9765 |  | 7740.9799 | 9040.0737 | 10566.5455 | 12361.0983 | 14471.8225 | 16955.5481 | 19879.4458 | 23322.9236 | 27379.8726 | 32161.3269 | 37798.6144 | 44447.0891 | 52290.5524 | 61546.4913 | 72472.2846 | 85372.5564 | 100607.8895 | 118605.1503 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 7740.4907 | 9039.5846 | 10566.0563 | 12360.6091 | 14471.3334 | 16955.059 | 19878.9566 | 23322.4344 | 27379.3834 | 32160.8377 | 37798.1253 | 44446.6 | 52290.0632 | 61546.0021 | 72471.7954 | 85372.0673 | 100607.4003 | 118604.5648 | 124235.378 | 124235.1163 | 124234.7556 | 124234.2561 | 124233.562 | 124232.5942 | 124231.2409 | 124229.3434 | 124226.6763 | 124222.9196 | 124217.6181 | 124210.1237 |  | 8256.0595 | 9646.2297 | 11279.7186 | 13200.0831 | 15458.785 | 18116.6385 | 21245.5234 | 24930.415 | 29271.7867 | 34388.457 | 40420.9609 | 47535.5438 | 55928.893 | 65833.7429 | 77525.5167 | 91330.1949 | 107633.6397 | 126887.2044 | 132902.2207 | 132887.4459 | 132867.0733 | 132838.8672 | 132799.6713 | 132745.0224 | 132668.6004 | 132561.444 | 132410.8328 | 132198.6915 | 131899.3119 | 131476.1003 |  | 241.6025 | 282.1483 | 329.7908 | 385.8003 | 451.6777 | 529.1969 | 620.4542 | 727.928 | 854.5488 | 1003.782 | 1179.7265 | 1387.231 | 1632.032 | 1920.9177 | 2261.9208 | 2664.5492 | 3140.0567 | 3701.7663 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 226.9264 | 267.4722 | 315.1147 | 371.1242 | 437.0016 | 514.5208 | 605.7781 | 713.2519 | 839.8727 | 989.1059 | 1165.0504 | 1372.5549 | 1617.3559 | 1906.2416 | 2247.2447 | 2649.8731 | 3125.3806 | 3684.1999 | 3854.2294 | 3846.3791 | 3835.5545 | 3820.5678 | 3799.7417 | 3770.7051 | 3730.0997 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 20.1515 | 23.5334 | 27.5071 | 32.1787 | 37.6734 | 44.1391 | 51.7507 | 60.7149 | 71.276 | 83.7232 | 98.3984 | 115.7058 | 136.1242 | 160.2195 | 188.6618 | 222.2441 | 261.9051 | 308.7561 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 18.0838 | 21.4657 | 25.4394 | 30.111 | 35.6057 | 42.0714 | 49.683 | 58.6472 | 69.2083 | 81.6555 | 96.3307 | 113.6381 | 134.0565 | 158.1518 | 186.5941 | 220.1764 | 259.8374 | 306.2812 | 320.1342 | 319.0282 | 317.5031 | 315.3917 | 312.4575 | 308.3665 | 302.6457 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 50.6832 | 59.1889 | 69.1833 | 80.933 | 94.7527 | 111.0146 | 130.1585 | 152.7043 | 179.2668 | 210.5728 | 247.4824 | 291.0125 | 342.3668 | 402.969 | 474.5045 | 558.9676 | 658.7194 | 776.5545 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 | 813.4229 |  | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0038332 | 0.0050812 | 0.0067942 | 0.0091563 | 0.012427 | 0.016971 | 0.023307 | 0.032168 | 0.044592 | 0.062054 | 0.086651 | 0.12136 | 0.17043 |  | 50.68 | 59.1857 | 69.1801 | 80.9298 | 94.7495 | 111.0114 | 130.1553 | 152.7011 | 179.2636 | 210.5696 | 247.4792 | 291.0093 | 342.3636 | 402.9658 | 474.5013 | 558.9644 | 658.7161 | 776.5507 | 813.4178 | 813.4161 | 813.4137 | 813.4105 | 813.4059 | 813.3996 | 813.3907 | 813.3783 | 813.3608 | 813.3362 | 813.3015 | 813.2524 |  | 8551.7498 | 9994.3533 | 11689.4528 | 13682.248 | 16026.1419 | 18784.2421 | 22031.1399 | 25855.0152 | 30360.1313 | 35669.788 | 41929.8211 | 49312.7461 | 58022.6689 | 68301.1021 | 80433.8569 | 94759.2088 | 111677.5738 | 131654.2362 | 137890.0021 | 137866.2693 | 137833.5447 | 137788.2371 | 137725.2765 | 137637.4936 | 137514.7364 | 137342.6105 | 137100.6829 | 136759.9191 | 136279.0239 | 135599.2166
| FALSE | 1668 | 22009680 | FDN | FDN-GTS | 66 | GTS LINE | CURRENT DIFF & DEF | X | Schweitzer | SEL_311L | SEL 311L | SEL 300s | Digital |  | 0.15703 | 1 |  | 4.0857 | 0.0054221 | 1.1663e-06 | 0.005421 | 28.4669 | 0.1283 | 28.5952 | 15.398 | 2.1694 | 0.0033601 |  | 11.2347 | 0.070957 | 1.5263e-05 | 0.070942 | 372.5341 | 1.679 | 374.213 | 201.5073 | 28.3902 | 0.043972 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.0032025 |  | 46.166 | 604.1545 | 44.0015 | 560.153 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0068474 | 0.0087043 | 0.011132 | 0.014316 | 0.018505 | 0.024029 | 0.031333 | 0.041011 | 0.053862 | 0.070957 | 0.093738 | 0.12414 | 0.16478 | 0.21915 | 0.292 | 0.38971 | 0.52087 | 0.69709 | 0.93404 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.4729e-06 | 1.8724e-06 | 2.3946e-06 | 3.0796e-06 | 3.9805e-06 | 5.1688e-06 | 6.7399e-06 | 8.8217e-06 | 1.1586e-05 | 1.5263e-05 | 2.0164e-05 | 2.6704e-05 | 3.5444e-05 | 4.7141e-05 | 6.2812e-05 | 8.3829e-05 | 0.00011204 | 0.00014995 | 0.00020092 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 58.3007 | 74.1116 | 94.783 | 121.8946 | 157.5566 | 204.5912 | 266.7774 | 349.1807 | 458.5974 | 604.1545 | 798.1182 | 1056.986 | 1402.9613 | 1865.9441 | 2486.2218 | 3318.1045 | 4434.8388 | 5935.2511 | 7952.7303 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 | 8018.4595 |  | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 44.0015 | 52.6671 | 69.8133 | 93.3499 | 125.8039 | 170.7369 | 233.1769 | 320.234 | 441.9762 | 612.6789 | 852.6062 | 1190.5526 | 1667.4716 | 2341.6582 |  | 35.9494 | 45.6987 | 58.4451 | 75.1627 | 97.1526 | 126.1551 | 164.5004 | 215.312 | 282.7806 | 372.5341 | 492.1361 | 651.7593 | 865.0947 | 1150.5794 | 1533.0554 | 2046.0113 | 2734.6126 | 3659.7977 | 4903.8167 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 8.8171 | 18.5665 | 31.3129 | 48.0304 | 70.0204 | 99.0229 | 137.3682 | 188.1797 | 255.6483 | 345.4018 | 465.0038 | 624.627 | 837.9625 | 1123.4472 | 1505.9232 | 2018.8791 | 2707.4804 | 3627.3221 | 4860.7684 | 4886.7853 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.16202 | 0.20596 | 0.26341 | 0.33875 | 0.43786 | 0.56857 | 0.74139 | 0.97039 | 1.2745 | 1.679 | 2.218 | 2.9374 | 3.8989 | 5.1855 | 6.9093 | 9.2212 | 12.3246 | 16.4943 | 22.101 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0.039738 | 0.083677 | 0.14112 | 0.21647 | 0.31557 | 0.44629 | 0.6191 | 0.84811 | 1.1522 | 1.5567 | 2.0957 | 2.8151 | 3.7766 | 5.0633 | 6.787 | 9.0989 | 12.2023 | 16.348 | 21.907 | 22.0242 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 8.8569 | 18.6502 | 31.454 | 48.2469 | 70.3359 | 99.4691 | 137.9873 | 189.0278 | 256.8005 | 346.9585 | 467.0995 | 627.4422 | 841.7391 | 1128.5105 | 1512.7102 | 2027.978 | 2719.6827 | 3643.67 | 4882.6754 | 4908.8095 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 19.4454 | 24.7189 | 31.6135 | 40.6562 | 52.5508 | 68.2385 | 88.9799 | 116.4643 | 152.9588 | 201.5073 | 266.2012 | 352.543 | 467.9382 | 622.3596 | 829.2446 | 1106.7075 | 1479.1786 | 1979.6202 | 2652.5222 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 4.7693 | 10.0428 | 16.9374 | 25.9801 | 37.8747 | 53.5624 | 74.3038 | 101.7882 | 138.2827 | 186.8312 | 251.5251 | 337.8669 | 453.2621 | 607.6835 | 814.5685 | 1092.0314 | 1464.5025 | 1962.0538 | 2629.237 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.7396 | 3.4826 | 4.454 | 5.728 | 7.4038 | 9.6141 | 12.5363 | 16.4086 | 21.5502 | 28.3902 | 37.5048 | 49.6695 | 65.9274 | 87.6837 | 116.8315 | 155.923 | 208.4002 | 278.9069 | 373.7115 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0.67194 | 1.4149 | 2.3863 | 3.6603 | 5.3361 | 7.5464 | 10.4686 | 14.3409 | 19.4825 | 26.3225 | 35.4371 | 47.6018 | 63.8597 | 85.616 | 114.7638 | 153.8553 | 206.3325 | 276.432 | 370.4309 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.0042432 | 0.005394 | 0.0068985 | 0.0088717 | 0.011467 | 0.014891 | 0.019417 | 0.025414 | 0.033378 | 0.043972 | 0.058089 | 0.07693 | 0.10211 | 0.13581 | 0.18095 | 0.2415 | 0.32278 | 0.43198 | 0.57882 | 0.5836 | 0.5836 | 0.5836 | 0.5836 | 0.5836 | 0.5836 | 0.5836 | 0.5836 | 0.5836 | 0.5836 | 0.5836 |  | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0032025 | 0.0038332 | 0.0050812 | 0.0067942 | 0.0091563 | 0.012427 | 0.016971 | 0.023307 | 0.032168 | 0.044592 | 0.062054 | 0.086651 | 0.12136 | 0.17043 |  | 0.0010407 | 0.0021915 | 0.003696 | 0.0056692 | 0.0082648 | 0.011688 | 0.016214 | 0.022212 | 0.030175 | 0.040769 | 0.054886 | 0.073727 | 0.098908 | 0.1326 | 0.17775 | 0.2383 | 0.31957 | 0.42815 | 0.57373 | 0.57681 | 0.57444 | 0.57117 | 0.56663 | 0.56029 | 0.55143 | 0.53901 | 0.52155 | 0.49695 | 0.46224 | 0.41317 |  | 14.2991 | 30.1101 | 50.7814 | 77.893 | 113.555 | 160.5896 | 222.7759 | 305.1791 | 414.5959 | 560.153 | 754.1167 | 1012.9845 | 1358.9598 | 1821.9426 | 2442.2203 | 3274.103 | 4390.8373 | 5882.584 | 7882.917 | 7925.1097 | 7892.6556 | 7847.7226 | 7785.2826 | 7698.2255 | 7576.4833 | 7405.7806 | 7165.8533 | 6827.9069 | 6350.9879 | 5676.8014
| TRUE | 1669 | 22001509 | FDN | Blank | 66 | TRANS NO.1 | OVERCURRENT | Y | ASEA | GROUP_2602 | GROUP 2602 | GROUP 2000s | Electronic |  | 0.0068096 | 2190 |  | 8.25 | 0.026286 | 0.00052975 | 0.025756 | 276.5552 | 233.0884 | 509.6437 | 77.6223 | 10.5222 | 1.5261 |  | 14.072 | 0.11259 | 0.0022691 | 0.11032 | 1184.5716 | 998.39 | 2182.9616 | 332.4802 | 45.0697 | 6.5369 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.00013888 |  | 599.3142 | 2567.0484 | 71.0225 | 2496.0259 |  | 0.053397 |  | 8.7025 | 9.1798 | 9.6833 | 10.2144 | 10.7747 | 11.3657 | 11.9891 | 12.6466 | 13.3403 | 14.072 | 14.8438 | 15.658 | 16.5168 | 17.4227 | 18.3783 | 19.3864 | 20.4497 | 21.5713 | 22.7545 | 24.0025 | 25.3191 | 26.7078 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.030282 | 0.034922 | 0.040311 | 0.046573 | 0.053853 | 0.062322 | 0.072178 | 0.083652 | 0.097017 | 0.11259 | 0.13074 | 0.15191 | 0.1766 | 0.2054 | 0.23903 | 0.27828 | 0.32413 | 0.37768 | 0.44025 | 0.51338 | 0.59886 | 0.6988 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0006103 | 0.0007038 | 0.0008124 | 0.0009386 | 0.0010853 | 0.001256 | 0.0014546 | 0.0016859 | 0.0019552 | 0.0022691 | 0.0026349 | 0.0030615 | 0.003559 | 0.0041396 | 0.0048172 | 0.0056084 | 0.0065323 | 0.0076115 | 0.0088726 | 0.010346 | 0.012069 | 0.014083 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 690.4431 | 796.2257 | 919.087 | 1061.8603 | 1227.8568 | 1420.9468 | 1645.6553 | 1907.274 | 2211.9917 | 2567.0484 | 2980.9148 | 3463.5034 | 4026.4153 | 4683.2305 | 5449.8468 | 6344.8787 | 7390.1236 | 8611.1098 | 10037.738 | 11705.0337 | 13654.0306 | 15932.8051 | 18269.2024 | 18269.2024 | 18269.2024 | 18269.2024 | 18269.2024 | 18269.2024 | 18269.2024 | 18269.2024 |  | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 52.5349 | 69.6381 | 93.1155 | 125.4881 | 170.3083 | 232.5916 | 319.4301 | 440.8667 | 611.1409 | 850.4658 | 1187.5638 | 1663.2856 | 2335.7796 |  | 318.6069 | 367.4205 | 424.1153 | 489.9984 | 566.5979 | 655.6998 | 759.3922 | 880.1169 | 1020.7297 | 1184.5716 | 1375.5515 | 1598.2433 | 1858.0006 | 2161.0898 | 2514.847 | 2927.8619 | 3410.1931 | 3973.6206 | 4631.9422 | 5401.3204 | 6300.6905 | 7352.2373 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 291.4752 | 340.2889 | 396.9836 | 462.8667 | 539.4662 | 628.5682 | 732.2605 | 852.9852 | 993.598 | 1157.44 | 1348.4198 | 1571.1116 | 1830.8689 | 2133.9581 | 2487.7153 | 2900.7303 | 3383.0615 | 3941.1457 | 4588.8947 | 5343.7601 | 6223.1188 | 7246.9596 | 8286.5956 | 8232.9156 | 8157.8484 | 8052.5917 | 7904.6507 | 7696.2703 | 7402.1983 | 6986.4896 |  | 268.5307 | 309.6723 | 357.4561 | 412.9843 | 477.5445 | 552.6421 | 640.0369 | 741.787 | 860.2995 | 998.39 | 1159.3531 | 1347.044 | 1565.9746 | 1821.4266 | 2119.5831 | 2467.6836 | 2874.2058 | 3349.0782 | 3903.9299 | 4552.3833 | 5310.3974 | 6196.6704 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 268.5095 | 309.6511 | 357.4349 | 412.9631 | 477.5233 | 552.6209 | 640.0157 | 741.7658 | 860.2782 | 998.3688 | 1159.3319 | 1347.0228 | 1565.9534 | 1821.4054 | 2119.5619 | 2467.6624 | 2874.1846 | 3349.0528 | 3903.8962 | 4552.3383 | 5310.3368 | 6196.5881 | 7105.2419 | 7105.2 | 7105.1413 | 7105.059 | 7104.9433 | 7104.7804 | 7104.5505 | 7104.2255 |  | 559.9847 | 649.9399 | 754.4185 | 875.8298 | 1016.9896 | 1181.189 | 1372.2763 | 1594.751 | 1853.8763 | 2155.8087 | 2507.7516 | 2918.1343 | 3396.8223 | 3955.3635 | 4607.2772 | 5368.3926 | 6257.246 | 7290.1985 | 8492.7909 | 9896.0984 | 11533.4556 | 13443.5477 | 15391.8376 | 15338.1155 | 15262.9896 | 15157.6507 | 15009.594 | 14801.0507 | 14506.7488 | 14090.7151 |  | 89.4251 | 103.1259 | 119.0388 | 137.5305 | 159.0301 | 184.0389 | 213.1428 | 247.0272 | 286.4938 | 332.4802 | 386.0836 | 448.5877 | 521.4952 | 606.5649 | 705.8559 | 821.7791 | 957.1576 | 1115.2979 | 1300.0726 | 1516.0182 | 1768.4493 | 2063.5927 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 74.7551 | 88.4559 | 104.3687 | 122.8605 | 144.3601 | 169.3688 | 198.4727 | 232.3572 | 271.8237 | 317.8102 | 371.4135 | 433.9176 | 506.8251 | 591.8948 | 691.1858 | 807.109 | 942.4875 | 1097.7387 | 1276.7969 | 1484.8955 | 1726.5064 | 2006.6693 | 2288.4584 | 2259.4337 | 2218.845 | 2161.9329 | 2081.9414 | 1969.2705 | 1810.2663 | 1585.4933 |  | 12.1221 | 13.9794 | 16.1364 | 18.6431 | 21.5575 | 24.9476 | 28.8928 | 33.4861 | 38.836 | 45.0697 | 52.336 | 60.8088 | 70.6919 | 82.2236 | 95.6831 | 111.3972 | 129.7486 | 151.1854 | 176.2328 | 205.5055 | 239.7241 | 279.7326 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 10.0544 | 11.9117 | 14.0687 | 16.5754 | 19.4898 | 22.8799 | 26.8251 | 31.4184 | 36.7683 | 43.002 | 50.2683 | 58.7411 | 68.6242 | 80.1559 | 93.6154 | 109.3295 | 127.6809 | 148.7105 | 172.9522 | 201.1189 | 233.8124 | 271.7095 | 309.7955 | 305.7046 | 299.9837 | 291.9622 | 280.6877 | 264.8071 | 242.396 | 210.7151 |  | 1.7582 | 2.0275 | 2.3404 | 2.704 | 3.1267 | 3.6184 | 4.1906 | 4.8568 | 5.6327 | 6.5369 | 7.5907 | 8.8196 | 10.2531 | 11.9256 | 13.8777 | 16.1569 | 18.8186 | 21.9277 | 25.5606 | 29.8062 | 34.7693 | 40.572 | 46.5215 | 46.5215 | 46.5215 | 46.5215 | 46.5215 | 46.5215 | 46.5215 | 46.5215 |  | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00016623 | 0.00022035 | 0.00029463 | 0.00039706 | 0.00053888 | 0.00073596 | 0.0010107 | 0.001395 | 0.0019337 | 0.002691 | 0.0037576 | 0.0052629 | 0.0073908 |  | 1.758 | 2.0274 | 2.3403 | 2.7038 | 3.1265 | 3.6182 | 4.1904 | 4.8566 | 5.6326 | 6.5367 | 7.5906 | 8.8195 | 10.2529 | 11.9255 | 13.8776 | 16.1568 | 18.8184 | 21.9276 | 25.5603 | 29.8059 | 34.7689 | 40.5715 | 46.5208 | 46.5205 | 46.5201 | 46.5196 | 46.5189 | 46.5178 | 46.5163 | 46.5142 |  | 646.5523 | 752.3349 | 875.1962 | 1017.9695 | 1183.966 | 1377.056 | 1601.7645 | 1863.3832 | 2168.1009 | 2523.1576 | 2937.024 | 3419.6126 | 3982.5245 | 4639.3397 | 5405.956 | 6300.9879 | 7346.2328 | 8558.5753 | 9968.1003 | 11611.9188 | 13528.5433 | 15762.4979 | 18036.6123 | 17949.7743 | 17828.3385 | 17658.0654 | 17418.742 | 17081.6461 | 16605.9274 | 15933.4376
| TRUE | 1670 | 22001510 | FDN | Blank | 66 | TRANS NO.2 | OVERCURRENT | Y | ASEA | GROUP_2602 | GROUP 2602 | GROUP 2000s | Electronic |  | 0.0068096 | 2190 |  | 8.25 | 0.026286 | 0.00052975 | 0.025756 | 276.5552 | 233.0884 | 509.6437 | 77.6223 | 10.5222 | 1.5261 |  | 14.072 | 0.11259 | 0.0022691 | 0.11032 | 1184.5716 | 998.39 | 2182.9616 | 332.4802 | 45.0697 | 6.5369 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.00013888 |  | 599.3142 | 2567.0484 | 71.0225 | 2496.0259 |  | 0.053397 |  | 8.7025 | 9.1798 | 9.6833 | 10.2144 | 10.7747 | 11.3657 | 11.9891 | 12.6466 | 13.3403 | 14.072 | 14.8438 | 15.658 | 16.5168 | 17.4227 | 18.3783 | 19.3864 | 20.4497 | 21.5713 | 22.7545 | 24.0025 | 25.3191 | 26.7078 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.030282 | 0.034922 | 0.040311 | 0.046573 | 0.053853 | 0.062322 | 0.072178 | 0.083652 | 0.097017 | 0.11259 | 0.13074 | 0.15191 | 0.1766 | 0.2054 | 0.23903 | 0.27828 | 0.32413 | 0.37768 | 0.44025 | 0.51338 | 0.59886 | 0.6988 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0006103 | 0.0007038 | 0.0008124 | 0.0009386 | 0.0010853 | 0.001256 | 0.0014546 | 0.0016859 | 0.0019552 | 0.0022691 | 0.0026349 | 0.0030615 | 0.003559 | 0.0041396 | 0.0048172 | 0.0056084 | 0.0065323 | 0.0076115 | 0.0088726 | 0.010346 | 0.012069 | 0.014083 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 690.4431 | 796.2257 | 919.087 | 1061.8603 | 1227.8568 | 1420.9468 | 1645.6553 | 1907.274 | 2211.9917 | 2567.0484 | 2980.9148 | 3463.5034 | 4026.4153 | 4683.2305 | 5449.8468 | 6344.8787 | 7390.1236 | 8611.1098 | 10037.738 | 11705.0337 | 13654.0306 | 15932.8051 | 18269.2024 | 18269.2024 | 18269.2024 | 18269.2024 | 18269.2024 | 18269.2024 | 18269.2024 | 18269.2024 |  | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 43.8911 | 52.5349 | 69.6381 | 93.1155 | 125.4881 | 170.3083 | 232.5916 | 319.4301 | 440.8667 | 611.1409 | 850.4658 | 1187.5638 | 1663.2856 | 2335.7796 |  | 318.6069 | 367.4205 | 424.1153 | 489.9984 | 566.5979 | 655.6998 | 759.3922 | 880.1169 | 1020.7297 | 1184.5716 | 1375.5515 | 1598.2433 | 1858.0006 | 2161.0898 | 2514.847 | 2927.8619 | 3410.1931 | 3973.6206 | 4631.9422 | 5401.3204 | 6300.6905 | 7352.2373 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 291.4752 | 340.2889 | 396.9836 | 462.8667 | 539.4662 | 628.5682 | 732.2605 | 852.9852 | 993.598 | 1157.44 | 1348.4198 | 1571.1116 | 1830.8689 | 2133.9581 | 2487.7153 | 2900.7303 | 3383.0615 | 3941.1457 | 4588.8947 | 5343.7601 | 6223.1188 | 7246.9596 | 8286.5956 | 8232.9156 | 8157.8484 | 8052.5917 | 7904.6507 | 7696.2703 | 7402.1983 | 6986.4896 |  | 268.5307 | 309.6723 | 357.4561 | 412.9843 | 477.5445 | 552.6421 | 640.0369 | 741.787 | 860.2995 | 998.39 | 1159.3531 | 1347.044 | 1565.9746 | 1821.4266 | 2119.5831 | 2467.6836 | 2874.2058 | 3349.0782 | 3903.9299 | 4552.3833 | 5310.3974 | 6196.6704 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 268.5095 | 309.6511 | 357.4349 | 412.9631 | 477.5233 | 552.6209 | 640.0157 | 741.7658 | 860.2782 | 998.3688 | 1159.3319 | 1347.0228 | 1565.9534 | 1821.4054 | 2119.5619 | 2467.6624 | 2874.1846 | 3349.0528 | 3903.8962 | 4552.3383 | 5310.3368 | 6196.5881 | 7105.2419 | 7105.2 | 7105.1413 | 7105.059 | 7104.9433 | 7104.7804 | 7104.5505 | 7104.2255 |  | 559.9847 | 649.9399 | 754.4185 | 875.8298 | 1016.9896 | 1181.189 | 1372.2763 | 1594.751 | 1853.8763 | 2155.8087 | 2507.7516 | 2918.1343 | 3396.8223 | 3955.3635 | 4607.2772 | 5368.3926 | 6257.246 | 7290.1985 | 8492.7909 | 9896.0984 | 11533.4556 | 13443.5477 | 15391.8376 | 15338.1155 | 15262.9896 | 15157.6507 | 15009.594 | 14801.0507 | 14506.7488 | 14090.7151 |  | 89.4251 | 103.1259 | 119.0388 | 137.5305 | 159.0301 | 184.0389 | 213.1428 | 247.0272 | 286.4938 | 332.4802 | 386.0836 | 448.5877 | 521.4952 | 606.5649 | 705.8559 | 821.7791 | 957.1576 | 1115.2979 | 1300.0726 | 1516.0182 | 1768.4493 | 2063.5927 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 74.7551 | 88.4559 | 104.3687 | 122.8605 | 144.3601 | 169.3688 | 198.4727 | 232.3572 | 271.8237 | 317.8102 | 371.4135 | 433.9176 | 506.8251 | 591.8948 | 691.1858 | 807.109 | 942.4875 | 1097.7387 | 1276.7969 | 1484.8955 | 1726.5064 | 2006.6693 | 2288.4584 | 2259.4337 | 2218.845 | 2161.9329 | 2081.9414 | 1969.2705 | 1810.2663 | 1585.4933 |  | 12.1221 | 13.9794 | 16.1364 | 18.6431 | 21.5575 | 24.9476 | 28.8928 | 33.4861 | 38.836 | 45.0697 | 52.336 | 60.8088 | 70.6919 | 82.2236 | 95.6831 | 111.3972 | 129.7486 | 151.1854 | 176.2328 | 205.5055 | 239.7241 | 279.7326 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 10.0544 | 11.9117 | 14.0687 | 16.5754 | 19.4898 | 22.8799 | 26.8251 | 31.4184 | 36.7683 | 43.002 | 50.2683 | 58.7411 | 68.6242 | 80.1559 | 93.6154 | 109.3295 | 127.6809 | 148.7105 | 172.9522 | 201.1189 | 233.8124 | 271.7095 | 309.7955 | 305.7046 | 299.9837 | 291.9622 | 280.6877 | 264.8071 | 242.396 | 210.7151 |  | 1.7582 | 2.0275 | 2.3404 | 2.704 | 3.1267 | 3.6184 | 4.1906 | 4.8568 | 5.6327 | 6.5369 | 7.5907 | 8.8196 | 10.2531 | 11.9256 | 13.8777 | 16.1569 | 18.8186 | 21.9277 | 25.5606 | 29.8062 | 34.7693 | 40.572 | 46.5215 | 46.5215 | 46.5215 | 46.5215 | 46.5215 | 46.5215 | 46.5215 | 46.5215 |  | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00013888 | 0.00016623 | 0.00022035 | 0.00029463 | 0.00039706 | 0.00053888 | 0.00073596 | 0.0010107 | 0.001395 | 0.0019337 | 0.002691 | 0.0037576 | 0.0052629 | 0.0073908 |  | 1.758 | 2.0274 | 2.3403 | 2.7038 | 3.1265 | 3.6182 | 4.1904 | 4.8566 | 5.6326 | 6.5367 | 7.5906 | 8.8195 | 10.2529 | 11.9255 | 13.8776 | 16.1568 | 18.8184 | 21.9276 | 25.5603 | 29.8059 | 34.7689 | 40.5715 | 46.5208 | 46.5205 | 46.5201 | 46.5196 | 46.5189 | 46.5178 | 46.5163 | 46.5142 |  | 646.5523 | 752.3349 | 875.1962 | 1017.9695 | 1183.966 | 1377.056 | 1601.7645 | 1863.3832 | 2168.1009 | 2523.1576 | 2937.024 | 3419.6126 | 3982.5245 | 4639.3397 | 5405.956 | 6300.9879 | 7346.2328 | 8558.5753 | 9968.1003 | 11611.9188 | 13528.5433 | 15762.4979 | 18036.6123 | 17949.7743 | 17828.3385 | 17658.0654 | 17418.742 | 17081.6461 | 16605.9274 | 15933.4376
| TRUE | 1865 | 22001655 | GCY | Blank | 22 | BUS ALL | OV-UV SUPERVISION | C | RPL | GROUP_2506 | GROUP 2506 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 498.1313 | 0 | 498.1313 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 791.4596 | 45.1611 | 746.2985 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.1882 | 292.6741 | 330.7184 | 373.9588 | 423.1235 | 479.0446 | 542.6727 | 615.0939 | 697.5498 | 791.4596 | 898.4455 | 1020.3625 | 1159.3315 | 1317.7785 | 1498.4776 | 1704.6026 | 1939.7838 | 2208.1751 | 2514.5289 | 2864.2839 | 3263.6638 | 3719.792 | 4240.8213 | 4836.0847 | 5516.2655 | 6293.5949 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 163.1287 | 184.2041 | 208.1485 | 235.3633 | 266.3068 | 301.5026 | 341.549 | 387.1297 | 439.0261 | 498.1313 | 565.4664 | 642.1989 | 729.6637 | 829.3875 | 943.1165 | 1072.848 | 1220.8671 | 1389.788 | 1582.602 | 1802.7318 | 2054.0948 | 2341.1741 | 2669.1012 | 3043.7499 | 3471.8442 | 3961.0821 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 228.2389 | 261.7248 | 299.7691 | 343.0095 | 392.1742 | 448.0953 | 511.7234 | 584.1446 | 666.6005 | 760.5103 | 867.4962 | 989.4132 | 1128.3822 | 1286.8292 | 1467.5283 | 1673.6533 | 1908.8345 | 2171.1307 | 2465.4244 | 2798.6245 | 3175.1773 | 3599.701 | 4076.812 | 4610.8421 | 5205.3933 | 5862.6557 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 1866 | 22001656 | GCY | Blank | 22 | BUS ALL | BATTERY UV & BUS NV | C | EMAIL | GROUP_2655 | GROUP 2655 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 498.1313 | 0 | 498.1313 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 791.4596 | 45.1611 | 746.2985 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.1882 | 292.6741 | 330.7184 | 373.9588 | 423.1235 | 479.0446 | 542.6727 | 615.0939 | 697.5498 | 791.4596 | 898.4455 | 1020.3625 | 1159.3315 | 1317.7785 | 1498.4776 | 1704.6026 | 1939.7838 | 2208.1751 | 2514.5289 | 2864.2839 | 3263.6638 | 3719.792 | 4240.8213 | 4836.0847 | 5516.2655 | 6293.5949 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 163.1287 | 184.2041 | 208.1485 | 235.3633 | 266.3068 | 301.5026 | 341.549 | 387.1297 | 439.0261 | 498.1313 | 565.4664 | 642.1989 | 729.6637 | 829.3875 | 943.1165 | 1072.848 | 1220.8671 | 1389.788 | 1582.602 | 1802.7318 | 2054.0948 | 2341.1741 | 2669.1012 | 3043.7499 | 3471.8442 | 3961.0821 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 228.2389 | 261.7248 | 299.7691 | 343.0095 | 392.1742 | 448.0953 | 511.7234 | 584.1446 | 666.6005 | 760.5103 | 867.4962 | 989.4132 | 1128.3822 | 1286.8292 | 1467.5283 | 1673.6533 | 1908.8345 | 2171.1307 | 2465.4244 | 2798.6245 | 3175.1773 | 3599.701 | 4076.812 | 4610.8421 | 5205.3933 | 5862.6557 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 1867 | 22001697 | GCY | Blank | 22 | BUS NO.1 | HIBP | X | ABB | RADHA_2524 | RADHA 2524 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 81.7572 | 388.9293 | 470.6866 | 49.6875 | 5.9058 | 1149.2299 |  | 10.0404 | 0.044454 | 0.0041931 | 0.040261 | 246.8009 | 1174.0627 | 1420.8636 | 149.9917 | 17.8278 | 3469.1854 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.19673 |  | 1675.5097 | 5057.8685 | 45.4259 | 5012.4426 |  | 0.041955 |  | 6.8828 | 7.1777 | 7.4852 | 7.806 | 8.1404 | 8.4892 | 8.853 | 9.2323 | 9.6279 | 10.0404 | 10.4706 | 10.9192 | 11.3871 | 11.875 | 12.3838 | 12.9144 | 13.4678 | 14.0448 | 14.6466 | 15.2742 | 15.9286 | 16.6111 | 17.3229 | 18.0651 | 18.8392 | 19.6464 | 20.4882 | 21.366 | 22.2815 | 23.2362 |  | 0.016394 | 0.018266 | 0.020367 | 0.022725 | 0.025374 | 0.028351 | 0.031697 | 0.03546 | 0.039692 | 0.044454 | 0.049814 | 0.055848 | 0.062645 | 0.070302 | 0.07893 | 0.088655 | 0.099619 | 0.11198 | 0.12593 | 0.14167 | 0.15942 | 0.17946 | 0.20209 | 0.22763 | 0.25648 | 0.28906 | 0.32587 | 0.36747 | 0.41447 | 0.46759 |  | 0.0015464 | 0.001723 | 0.0019211 | 0.0021436 | 0.0023934 | 0.0026742 | 0.0029898 | 0.0033447 | 0.0037439 | 0.0041931 | 0.0046987 | 0.0052679 | 0.005909 | 0.0066312 | 0.007445 | 0.0083623 | 0.0093966 | 0.010563 | 0.011878 | 0.013363 | 0.015037 | 0.016928 | 0.019062 | 0.021471 | 0.024192 | 0.027266 | 0.030738 | 0.034661 | 0.039095 | 0.044105 | 1865.3431 | 2078.3034 | 2317.3102 | 2585.6597 | 2887.074 | 3225.7564 | 3606.4553 | 4034.5348 | 4516.056 | 5057.8685 | 5667.7139 | 6354.3435 | 7127.6507 | 7998.8221 | 8980.5076 | 10087.014 | 11334.5231 | 12741.3399 | 14328.1733 | 16118.454 | 18138.6948 | 20418.8987 | 22993.0215 | 25899.4958 | 29181.8244 | 32889.2536 | 37077.5355 | 41809.7915 | 47157.4921 | 53201.5661 |  | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 37.3621 | 49.5257 | 66.2225 | 89.2454 | 121.121 | 165.416 | 227.1744 | 313.5385 | 434.6352 | 604.8399 | 844.5795 | 1182.9065 | 1661.1753 |  | 91.0202 | 101.4117 | 113.0742 | 126.1684 | 140.876 | 157.4022 | 175.9786 | 196.8669 | 220.3629 | 246.8009 | 276.5586 | 310.063 | 347.7968 | 390.306 | 438.2078 | 492.2003 | 553.073 | 621.7192 | 699.1495 | 786.507 | 885.0855 | 996.3491 | 1121.9545 | 1263.7772 | 1423.9399 | 1604.8455 | 1809.2146 | 2040.1271 | 2301.0704 | 2595.9937 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 76.8083 | 87.1998 | 98.8623 | 111.9565 | 126.6641 | 143.1903 | 161.7667 | 182.655 | 206.151 | 232.589 | 262.3467 | 295.8511 | 333.5849 | 376.0941 | 423.9959 | 477.9884 | 538.8611 | 604.7085 | 676.6007 | 756.3563 | 844.4526 | 941.2034 | 1046.6416 | 1160.346 | 1281.1876 | 1406.9586 | 1533.8345 | 1655.5949 | 1762.5 | 1839.6703 |  | 432.9946 | 482.4282 | 537.9079 | 600.1988 | 670.1649 | 748.7819 | 837.152 | 936.5203 | 1048.2939 | 1174.0627 | 1315.6236 | 1475.0082 | 1654.5128 | 1856.7344 | 2084.6091 | 2341.4579 | 2631.0372 | 2957.5959 | 3325.9412 | 3741.5118 | 4210.4622 | 4739.7567 | 5337.2775 | 6011.9457 | 6773.8594 | 7634.45 | 8606.659 | 9705.1385 | 10946.4787 | 12349.4653 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 432.928 | 482.3616 | 537.8413 | 600.1322 | 670.0983 | 748.7153 | 837.0854 | 936.4537 | 1048.2273 | 1173.9961 | 1315.557 | 1474.9416 | 1654.4463 | 1856.6678 | 2084.5425 | 2341.3914 | 2630.9706 | 2957.5162 | 3325.8355 | 3741.3706 | 4210.2718 | 4739.4984 | 5336.9247 | 6011.4611 | 6773.1906 | 7633.523 | 8605.3689 | 9703.3371 | 10943.9557 | 12345.9222 |  | 509.7363 | 569.5614 | 636.7036 | 712.0887 | 796.7624 | 891.9056 | 998.852 | 1119.1087 | 1254.3784 | 1406.5851 | 1577.9037 | 1770.7927 | 1988.0312 | 2232.7619 | 2508.5384 | 2819.3797 | 3169.8317 | 3562.2247 | 4002.4363 | 4497.7269 | 5054.7244 | 5680.7018 | 6383.5663 | 7171.8072 | 8054.3783 | 9040.4816 | 10139.2034 | 11358.9321 | 12706.4558 | 14185.5925 |  | 55.317 | 61.6324 | 68.7201 | 76.6781 | 85.6166 | 95.6602 | 106.9499 | 119.6447 | 133.9242 | 149.9917 | 168.0768 | 188.4389 | 211.3714 | 237.2061 | 266.3181 | 299.1317 | 336.1268 | 377.8461 | 424.9038 | 477.9948 | 537.9054 | 605.5251 | 681.861 | 768.0529 | 865.3908 | 975.3351 | 1099.5391 | 1239.8748 | 1398.4616 | 1577.6994 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 40.6459 | 46.9612 | 54.049 | 62.0069 | 70.9454 | 80.9891 | 92.2788 | 104.9735 | 119.2531 | 135.3206 | 153.4057 | 173.7677 | 196.7003 | 222.535 | 251.647 | 284.4606 | 321.4556 | 360.2857 | 401.6265 | 446.8698 | 495.9594 | 548.5974 | 604.1144 | 661.2794 | 718.0256 | 771.0537 | 815.2604 | 842.9168 | 842.4877 | 796.936 |  | 6.5749 | 7.3255 | 8.168 | 9.1138 | 10.1763 | 11.37 | 12.7119 | 14.2208 | 15.918 | 17.8278 | 19.9774 | 22.3976 | 25.1233 | 28.194 | 31.6542 | 35.5544 | 39.9516 | 44.9103 | 50.5035 | 56.8138 | 63.9347 | 71.9719 | 81.0451 | 91.2897 | 102.8591 | 115.927 | 130.6897 | 147.3698 | 166.2192 | 187.5231 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 4.5072 | 5.2578 | 6.1003 | 7.0462 | 8.1086 | 9.3023 | 10.6442 | 12.1531 | 13.8504 | 15.7601 | 17.9097 | 20.3299 | 23.0556 | 26.1263 | 29.5865 | 33.4867 | 37.8839 | 42.4354 | 47.2229 | 52.4272 | 58.023 | 63.9487 | 70.0877 | 76.2415 | 82.0901 | 87.1363 | 90.6245 | 91.4241 | 87.8624 | 77.4853 |  | 1279.4364 | 1425.5056 | 1589.44 | 1773.5006 | 1980.2403 | 2212.5421 | 2473.663 | 2767.2822 | 3097.5569 | 3469.1854 | 3887.4776 | 4358.4359 | 4888.8463 | 5486.3816 | 6159.7185 | 6918.6697 | 7774.3345 | 8739.2684 | 9827.6753 | 11055.6265 | 12441.307 | 14005.2959 | 15770.8834 | 17764.4303 | 20015.7752 | 22558.6961 | 25431.4331 | 28677.2813 | 32345.2622 | 36490.8846 |  | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.23547 | 0.31213 | 0.41736 | 0.56246 | 0.76335 | 1.0425 | 1.4317 | 1.976 | 2.7392 | 3.8119 | 5.3228 | 7.4551 | 10.4693 |  | 1279.2396 | 1425.3088 | 1589.2433 | 1773.3039 | 1980.0435 | 2212.3454 | 2473.4663 | 2767.0854 | 3097.3602 | 3468.9887 | 3887.2809 | 4358.2392 | 4888.6495 | 5486.1849 | 6159.5217 | 6918.473 | 7774.1378 | 8739.0329 | 9827.3632 | 11055.2091 | 12440.7446 | 14004.5326 | 15769.8409 | 17762.9985 | 20013.7992 | 22555.9568 | 25427.6212 | 28671.9585 | 32337.8071 | 36480.4153 |  | 1834.129 | 2047.0893 | 2286.0962 | 2554.4457 | 2855.8599 | 3194.5424 | 3575.2413 | 4003.3208 | 4484.842 | 5026.6545 | 5636.4999 | 6323.1295 | 7096.4366 | 7967.608 | 8949.2936 | 10055.8 | 11303.309 | 12703.9786 | 14278.6487 | 16052.233 | 18049.4514 | 20297.7805 | 22827.6093 | 25672.3266 | 28868.2931 | 32454.6284 | 36472.7095 | 40965.2314 | 45974.6129 | 51540.4291
| TRUE | 1868 | 22001698 | GCY | Blank | 22 | BUS NO.1 | OVERCURRENT | X | GE | SR760 | SR760 | SR760 | Digital |  | 0.033587 | 1 |  | 6.6 | 0.017308 | 7.9633e-07 | 0.017307 | 71.3952 | 0.11149 | 71.5067 | 49.1349 | 6.9249 | 0.65885 |  | 12.4804 | 0.094782 | 4.3609e-06 | 0.094778 | 390.9796 | 0.61053 | 391.5901 | 269.0759 | 37.9225 | 3.6081 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 21.3178 | 0.033289 | 21.3511 | 14.6711 | 2.0677 | 0.19673 |  | 128.2253 | 702.1966 | 38.2867 | 663.9099 |  | 0.063709 |  | 7.0342 | 7.4969 | 7.99 | 8.5157 | 9.0758 | 9.6729 | 10.3092 | 10.9873 | 11.7101 | 12.4804 | 13.3014 | 14.1764 | 15.109 | 16.1029 | 17.1621 | 18.2911 | 19.4943 | 20.7767 | 22.1435 | 23.6001 | 25.1526 | 26.8072 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.020378 | 0.024035 | 0.028395 | 0.033598 | 0.039812 | 0.04724 | 0.056126 | 0.066764 | 0.079507 | 0.094782 | 0.1131 | 0.13509 | 0.16149 | 0.19321 | 0.23132 | 0.27716 | 0.33229 | 0.39864 | 0.47852 | 0.5747 | 0.69057 | 0.8302 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 9.3758e-07 | 1.1058e-06 | 1.3064e-06 | 1.5458e-06 | 1.8317e-06 | 2.1735e-06 | 2.5824e-06 | 3.0718e-06 | 3.6581e-06 | 4.3609e-06 | 5.2039e-06 | 6.2155e-06 | 7.4302e-06 | 8.8894e-06 | 1.0643e-05 | 1.2752e-05 | 1.5289e-05 | 1.8342e-05 | 2.2016e-05 | 2.6442e-05 | 3.1773e-05 | 3.8197e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 150.9693 | 178.0607 | 210.3612 | 248.9075 | 294.9465 | 349.979 | 415.8121 | 494.6219 | 589.0303 | 702.1966 | 837.9292 | 1000.8201 | 1196.4072 | 1431.3707 | 1713.7709 | 2053.3347 | 2461.8028 | 2953.3491 | 3545.0879 | 4257.6871 | 5116.1098 | 6150.511 | 6977.034 | 6977.034 | 6977.034 | 6977.034 | 6977.034 | 6977.034 | 6977.034 | 6977.034 |  | 31.1811 | 31.1811 | 31.1811 | 31.1811 | 31.1811 | 31.1811 | 31.1811 | 31.1811 | 31.1811 | 31.1811 | 31.1811 | 31.1811 | 31.1811 | 31.1811 | 31.1811 | 31.1811 | 31.1811 | 37.3218 | 49.4723 | 66.1511 | 89.1492 | 120.9904 | 165.2377 | 226.9295 | 313.2005 | 434.1667 | 604.1879 | 843.6691 | 1181.6314 | 1659.3846 |  | 84.059 | 99.1433 | 117.1281 | 138.5905 | 164.2247 | 194.8666 | 231.5221 | 275.4031 | 327.9691 | 390.9796 | 466.5549 | 557.2517 | 666.1536 | 796.9802 | 954.2192 | 1143.2866 | 1370.7197 | 1644.4102 | 1973.8875 | 2370.6592 | 2848.6247 | 3424.5742 | 3884.7782 | 3884.7782 | 3884.7782 | 3884.7782 | 3884.7782 | 3884.7782 | 3884.7782 | 3884.7782 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 69.8471 | 84.9314 | 102.9162 | 124.3786 | 150.0129 | 180.6547 | 217.3102 | 261.1912 | 313.7573 | 376.7677 | 452.343 | 543.0398 | 651.9417 | 782.7683 | 940.0073 | 1129.0747 | 1356.5078 | 1627.3995 | 1951.3388 | 2340.5085 | 2807.9918 | 3369.4286 | 3809.4652 | 3781.347 | 3742.0259 | 3686.8913 | 3609.3981 | 3500.2461 | 3346.2078 | 3128.4548 |  | 0.13126 | 0.15482 | 0.1829 | 0.21641 | 0.25644 | 0.30429 | 0.36153 | 0.43005 | 0.51214 | 0.61053 | 0.72855 | 0.87017 | 1.0402 | 1.2445 | 1.4901 | 1.7853 | 2.1404 | 2.5678 | 3.0823 | 3.7019 | 4.4482 | 5.3476 | 6.0662 | 6.0662 | 6.0662 | 6.0662 | 6.0662 | 6.0662 | 6.0662 | 6.0662 |  | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.039844 | 0.052816 | 0.070622 | 0.095175 | 0.12917 | 0.17641 | 0.24227 | 0.33437 | 0.46351 | 0.64503 | 0.90069 | 1.2615 | 1.7715 |  | 0.097973 | 0.12153 | 0.14961 | 0.18313 | 0.22316 | 0.271 | 0.32824 | 0.39676 | 0.47885 | 0.57724 | 0.69526 | 0.83688 | 1.0069 | 1.2112 | 1.4568 | 1.752 | 2.1071 | 2.528 | 3.0295 | 3.6313 | 4.3531 | 5.2184 | 5.8898 | 5.824 | 5.7319 | 5.6027 | 5.4212 | 5.1656 | 4.8047 | 4.2947 |  | 69.9451 | 85.053 | 103.0658 | 124.5617 | 150.236 | 180.9257 | 217.6385 | 261.5879 | 314.2361 | 377.3449 | 453.0382 | 543.8767 | 652.9487 | 783.9795 | 941.4641 | 1130.8267 | 1358.6149 | 1629.9275 | 1954.3682 | 2344.1398 | 2812.3449 | 3374.647 | 3815.3551 | 3787.171 | 3747.7578 | 3692.494 | 3614.8193 | 3505.4116 | 3351.0125 | 3132.7495 |  | 57.8502 | 68.2314 | 80.6087 | 95.3793 | 113.021 | 134.109 | 159.3357 | 189.535 | 225.7115 | 269.0759 | 321.0875 | 383.5059 | 458.4533 | 548.4893 | 656.7027 | 786.8207 | 943.3423 | 1131.6987 | 1358.4481 | 1631.5102 | 1960.4506 | 2356.8245 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 43.1791 | 53.5602 | 65.9375 | 80.7081 | 98.3499 | 119.4379 | 144.6646 | 174.8639 | 211.0403 | 254.4047 | 306.4163 | 368.8348 | 443.7821 | 533.8182 | 642.0316 | 772.1496 | 928.6711 | 1114.1383 | 1335.1707 | 1600.3852 | 1918.5046 | 2299.8968 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 8.1532 | 9.6163 | 11.3607 | 13.4424 | 15.9288 | 18.9008 | 22.4562 | 26.7123 | 31.8109 | 37.9225 | 45.2528 | 54.0499 | 64.6126 | 77.302 | 92.5532 | 110.8915 | 132.951 | 159.4973 | 191.4545 | 229.9388 | 276.2984 | 332.1618 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 6.0855 | 7.5486 | 9.293 | 11.3747 | 13.8611 | 16.8331 | 20.3885 | 24.6446 | 29.7432 | 35.8548 | 43.1851 | 51.9822 | 62.5449 | 75.2343 | 90.4855 | 108.8238 | 130.8833 | 157.0224 | 188.1738 | 225.5521 | 270.3867 | 324.1386 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 0.77572 | 0.91492 | 1.0809 | 1.2789 | 1.5155 | 1.7983 | 2.1365 | 2.5415 | 3.0266 | 3.6081 | 4.3055 | 5.1425 | 6.1474 | 7.3547 | 8.8058 | 10.5506 | 12.6494 | 15.1751 | 18.2156 | 21.8771 | 26.2879 | 31.6029 | 35.8498 | 35.8498 | 35.8498 | 35.8498 | 35.8498 | 35.8498 | 35.8498 | 35.8498 |  | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.23547 | 0.31213 | 0.41736 | 0.56246 | 0.76335 | 1.0425 | 1.4317 | 1.976 | 2.7392 | 3.8119 | 5.3228 | 7.4551 | 10.4693 |  | 0.57899 | 0.71819 | 0.88416 | 1.0822 | 1.3188 | 1.6016 | 1.9398 | 2.3448 | 2.8299 | 3.4113 | 4.1088 | 4.9457 | 5.9507 | 7.158 | 8.6091 | 10.3538 | 12.4526 | 14.9396 | 17.9034 | 21.4597 | 25.7254 | 30.8395 | 34.8072 | 34.418 | 33.8737 | 33.1105 | 32.0378 | 30.5269 | 28.3947 | 25.3804 |  | 119.7886 | 146.88 | 179.1805 | 217.7268 | 263.7657 | 318.7983 | 384.6314 | 463.4412 | 557.8495 | 671.0158 | 806.7485 | 969.6394 | 1165.2265 | 1400.19 | 1682.5902 | 2022.1539 | 2430.622 | 2916.0277 | 3495.6162 | 4191.5368 | 5026.9616 | 6029.522 | 6811.7982 | 6750.1071 | 6663.8371 | 6542.8723 | 6372.8531 | 6133.3747 | 5795.4163 | 5317.6686
| TRUE | 1869 | 22001644 | GCY | Blank | 22 | BUS NO.2 | HIBP | X | ABB | RADHA_2524 | RADHA 2524 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 81.7572 | 388.9293 | 470.6866 | 49.6875 | 5.9058 | 1149.2299 |  | 10.0404 | 0.044454 | 0.0041931 | 0.040261 | 246.8009 | 1174.0627 | 1420.8636 | 149.9917 | 17.8278 | 3469.1854 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.19673 |  | 1675.5097 | 5057.8685 | 45.4259 | 5012.4426 |  | 0.041955 |  | 6.8828 | 7.1777 | 7.4852 | 7.806 | 8.1404 | 8.4892 | 8.853 | 9.2323 | 9.6279 | 10.0404 | 10.4706 | 10.9192 | 11.3871 | 11.875 | 12.3838 | 12.9144 | 13.4678 | 14.0448 | 14.6466 | 15.2742 | 15.9286 | 16.6111 | 17.3229 | 18.0651 | 18.8392 | 19.6464 | 20.4882 | 21.366 | 22.2815 | 23.2362 |  | 0.016394 | 0.018266 | 0.020367 | 0.022725 | 0.025374 | 0.028351 | 0.031697 | 0.03546 | 0.039692 | 0.044454 | 0.049814 | 0.055848 | 0.062645 | 0.070302 | 0.07893 | 0.088655 | 0.099619 | 0.11198 | 0.12593 | 0.14167 | 0.15942 | 0.17946 | 0.20209 | 0.22763 | 0.25648 | 0.28906 | 0.32587 | 0.36747 | 0.41447 | 0.46759 |  | 0.0015464 | 0.001723 | 0.0019211 | 0.0021436 | 0.0023934 | 0.0026742 | 0.0029898 | 0.0033447 | 0.0037439 | 0.0041931 | 0.0046987 | 0.0052679 | 0.005909 | 0.0066312 | 0.007445 | 0.0083623 | 0.0093966 | 0.010563 | 0.011878 | 0.013363 | 0.015037 | 0.016928 | 0.019062 | 0.021471 | 0.024192 | 0.027266 | 0.030738 | 0.034661 | 0.039095 | 0.044105 | 1865.3431 | 2078.3034 | 2317.3102 | 2585.6597 | 2887.074 | 3225.7564 | 3606.4553 | 4034.5348 | 4516.056 | 5057.8685 | 5667.7139 | 6354.3435 | 7127.6507 | 7998.8221 | 8980.5076 | 10087.014 | 11334.5231 | 12741.3399 | 14328.1733 | 16118.454 | 18138.6948 | 20418.8987 | 22993.0215 | 25899.4958 | 29181.8244 | 32889.2536 | 37077.5355 | 41809.7915 | 47157.4921 | 53201.5661 |  | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 31.2147 | 37.3621 | 49.5257 | 66.2225 | 89.2454 | 121.121 | 165.416 | 227.1744 | 313.5385 | 434.6352 | 604.8399 | 844.5795 | 1182.9065 | 1661.1753 |  | 91.0202 | 101.4117 | 113.0742 | 126.1684 | 140.876 | 157.4022 | 175.9786 | 196.8669 | 220.3629 | 246.8009 | 276.5586 | 310.063 | 347.7968 | 390.306 | 438.2078 | 492.2003 | 553.073 | 621.7192 | 699.1495 | 786.507 | 885.0855 | 996.3491 | 1121.9545 | 1263.7772 | 1423.9399 | 1604.8455 | 1809.2146 | 2040.1271 | 2301.0704 | 2595.9937 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 76.8083 | 87.1998 | 98.8623 | 111.9565 | 126.6641 | 143.1903 | 161.7667 | 182.655 | 206.151 | 232.589 | 262.3467 | 295.8511 | 333.5849 | 376.0941 | 423.9959 | 477.9884 | 538.8611 | 604.7085 | 676.6007 | 756.3563 | 844.4526 | 941.2034 | 1046.6416 | 1160.346 | 1281.1876 | 1406.9586 | 1533.8345 | 1655.5949 | 1762.5 | 1839.6703 |  | 432.9946 | 482.4282 | 537.9079 | 600.1988 | 670.1649 | 748.7819 | 837.152 | 936.5203 | 1048.2939 | 1174.0627 | 1315.6236 | 1475.0082 | 1654.5128 | 1856.7344 | 2084.6091 | 2341.4579 | 2631.0372 | 2957.5959 | 3325.9412 | 3741.5118 | 4210.4622 | 4739.7567 | 5337.2775 | 6011.9457 | 6773.8594 | 7634.45 | 8606.659 | 9705.1385 | 10946.4787 | 12349.4653 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 432.928 | 482.3616 | 537.8413 | 600.1322 | 670.0983 | 748.7153 | 837.0854 | 936.4537 | 1048.2273 | 1173.9961 | 1315.557 | 1474.9416 | 1654.4463 | 1856.6678 | 2084.5425 | 2341.3914 | 2630.9706 | 2957.5162 | 3325.8355 | 3741.3706 | 4210.2718 | 4739.4984 | 5336.9247 | 6011.4611 | 6773.1906 | 7633.523 | 8605.3689 | 9703.3371 | 10943.9557 | 12345.9222 |  | 509.7363 | 569.5614 | 636.7036 | 712.0887 | 796.7624 | 891.9056 | 998.852 | 1119.1087 | 1254.3784 | 1406.5851 | 1577.9037 | 1770.7927 | 1988.0312 | 2232.7619 | 2508.5384 | 2819.3797 | 3169.8317 | 3562.2247 | 4002.4363 | 4497.7269 | 5054.7244 | 5680.7018 | 6383.5663 | 7171.8072 | 8054.3783 | 9040.4816 | 10139.2034 | 11358.9321 | 12706.4558 | 14185.5925 |  | 55.317 | 61.6324 | 68.7201 | 76.6781 | 85.6166 | 95.6602 | 106.9499 | 119.6447 | 133.9242 | 149.9917 | 168.0768 | 188.4389 | 211.3714 | 237.2061 | 266.3181 | 299.1317 | 336.1268 | 377.8461 | 424.9038 | 477.9948 | 537.9054 | 605.5251 | 681.861 | 768.0529 | 865.3908 | 975.3351 | 1099.5391 | 1239.8748 | 1398.4616 | 1577.6994 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 40.6459 | 46.9612 | 54.049 | 62.0069 | 70.9454 | 80.9891 | 92.2788 | 104.9735 | 119.2531 | 135.3206 | 153.4057 | 173.7677 | 196.7003 | 222.535 | 251.647 | 284.4606 | 321.4556 | 360.2857 | 401.6265 | 446.8698 | 495.9594 | 548.5974 | 604.1144 | 661.2794 | 718.0256 | 771.0537 | 815.2604 | 842.9168 | 842.4877 | 796.936 |  | 6.5749 | 7.3255 | 8.168 | 9.1138 | 10.1763 | 11.37 | 12.7119 | 14.2208 | 15.918 | 17.8278 | 19.9774 | 22.3976 | 25.1233 | 28.194 | 31.6542 | 35.5544 | 39.9516 | 44.9103 | 50.5035 | 56.8138 | 63.9347 | 71.9719 | 81.0451 | 91.2897 | 102.8591 | 115.927 | 130.6897 | 147.3698 | 166.2192 | 187.5231 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 4.5072 | 5.2578 | 6.1003 | 7.0462 | 8.1086 | 9.3023 | 10.6442 | 12.1531 | 13.8504 | 15.7601 | 17.9097 | 20.3299 | 23.0556 | 26.1263 | 29.5865 | 33.4867 | 37.8839 | 42.4354 | 47.2229 | 52.4272 | 58.023 | 63.9487 | 70.0877 | 76.2415 | 82.0901 | 87.1363 | 90.6245 | 91.4241 | 87.8624 | 77.4853 |  | 1279.4364 | 1425.5056 | 1589.44 | 1773.5006 | 1980.2403 | 2212.5421 | 2473.663 | 2767.2822 | 3097.5569 | 3469.1854 | 3887.4776 | 4358.4359 | 4888.8463 | 5486.3816 | 6159.7185 | 6918.6697 | 7774.3345 | 8739.2684 | 9827.6753 | 11055.6265 | 12441.307 | 14005.2959 | 15770.8834 | 17764.4303 | 20015.7752 | 22558.6961 | 25431.4331 | 28677.2813 | 32345.2622 | 36490.8846 |  | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.19673 | 0.23547 | 0.31213 | 0.41736 | 0.56246 | 0.76335 | 1.0425 | 1.4317 | 1.976 | 2.7392 | 3.8119 | 5.3228 | 7.4551 | 10.4693 |  | 1279.2396 | 1425.3088 | 1589.2433 | 1773.3039 | 1980.0435 | 2212.3454 | 2473.4663 | 2767.0854 | 3097.3602 | 3468.9887 | 3887.2809 | 4358.2392 | 4888.6495 | 5486.1849 | 6159.5217 | 6918.473 | 7774.1378 | 8739.0329 | 9827.3632 | 11055.2091 | 12440.7446 | 14004.5326 | 15769.8409 | 17762.9985 | 20013.7992 | 22555.9568 | 25427.6212 | 28671.9585 | 32337.8071 | 36480.4153 |  | 1834.129 | 2047.0893 | 2286.0962 | 2554.4457 | 2855.8599 | 3194.5424 | 3575.2413 | 4003.3208 | 4484.842 | 5026.6545 | 5636.4999 | 6323.1295 | 7096.4366 | 7967.608 | 8949.2936 | 10055.8 | 11303.309 | 12703.9786 | 14278.6487 | 16052.233 | 18049.4514 | 20297.7805 | 22827.6093 | 25672.3266 | 28868.2931 | 32454.6284 | 36472.7095 | 40965.2314 | 45974.6129 | 51540.4291
| TRUE | 1870 | 22016377 | GCY | Blank | 22 | BUS NO.2 | OVERCURRENT | Y | GE | SR760 | SR760 | SR760 | Digital |  | 0.0034106 | 1 |  | 0.85973 | 0.0051679 | 2.4145e-08 | 0.0051679 | 14.2118 | 0.0016901 | 14.2135 | 14.6699 | 2.0677 | 0.019976 |  | 5.2359 | 0.0097219 | 4.5421e-08 | 0.0097218 | 26.7351 | 0.0031795 | 26.7383 | 27.5969 | 3.8897 | 0.03758 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 14.2118 | 0.0016901 | 14.2135 | 14.6699 | 2.0677 | 0.019976 |  | 30.9711 | 58.2625 | 30.9711 | 27.2914 |  | 0.18067 |  | 1.03 | 1.2339 | 1.4783 | 1.771 | 2.1217 | 2.5418 | 3.0451 | 3.6481 | 4.3705 | 5.2359 | 6.2727 | 7.5149 | 9.0029 | 10.7857 | 12.9214 | 15.4801 | 18.5455 | 22.2178 | 26.6173 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0063294 | 0.0097219 | 0.015213 | 0.024185 | 0.038963 | 0.063471 | 0.10435 | 0.17289 | 0.28826 | 0.48314 | 0.8133 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.9571e-08 | 4.5421e-08 | 7.1076e-08 | 1.1299e-07 | 1.8204e-07 | 2.9654e-07 | 4.8755e-07 | 8.0776e-07 | 1.3468e-06 | 2.2573e-06 | 3.7998e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 37.9315 | 58.2625 | 91.1707 | 144.939 | 233.5012 | 380.3783 | 625.3917 | 1036.1266 | 1727.5303 | 2895.4476 | 4874.0502 | 5643.9082 | 5643.9082 | 5643.9082 | 5643.9082 | 5643.9082 | 5643.9082 | 5643.9082 | 5643.9082 | 5643.9082 | 5643.9082 | 5643.9082 |  | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 30.9711 | 37.0705 | 49.1391 | 65.7057 | 88.5489 | 120.1756 | 164.125 | 225.4013 | 311.0913 | 431.2429 | 600.1192 | 837.9876 | 1173.6739 | 1648.2098 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.4058 | 26.7351 | 41.8358 | 66.5087 | 107.1476 | 174.5456 | 286.9758 | 475.4513 | 792.7184 | 1328.6449 | 2236.5738 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.194 | 12.5233 | 27.624 | 52.2969 | 92.9357 | 160.3338 | 272.764 | 461.2395 | 778.5065 | 1311.6343 | 2214.0251 | 2559.6908 | 2549.2086 | 2534.696 | 2514.5288 | 2486.4106 | 2447.0898 | 2391.9554 | 2314.4625 | 2205.3109 | 2051.2732 | 1833.5212 |  | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.00207 | 0.0031795 | 0.0049753 | 0.0079095 | 0.012743 | 0.020758 | 0.034129 | 0.056543 | 0.094274 | 0.15801 | 0.26598 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 |  | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.002023 | 0.0026816 | 0.0035857 | 0.0048322 | 0.0065582 | 0.0089565 | 0.0123 | 0.016977 | 0.023534 | 0.032749 | 0.04573 | 0.064049 | 0.089945 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00037984 | 0.0014893 | 0.0032852 | 0.0062194 | 0.011052 | 0.019068 | 0.032438 | 0.054853 | 0.092584 | 0.15599 | 0.2633 | 0.30441 | 0.30316 | 0.30144 | 0.29904 | 0.2957 | 0.29102 | 0.28446 | 0.27525 | 0.26227 | 0.24395 | 0.21805 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1943 | 12.5248 | 27.6273 | 52.3031 | 92.9468 | 160.3529 | 272.7964 | 461.2943 | 778.5991 | 1311.7902 | 2214.2884 | 2559.9952 | 2549.5118 | 2534.9974 | 2514.8278 | 2486.7063 | 2447.3808 | 2392.2398 | 2314.7377 | 2205.5732 | 2051.5172 | 1833.7392 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.9668 | 27.5969 | 43.1844 | 68.6525 | 110.6013 | 180.1718 | 296.226 | 490.7766 | 818.2702 | 1371.4714 | 2308.6656 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2969 | 12.927 | 28.5144 | 53.9826 | 95.9314 | 165.5019 | 281.5561 | 476.1067 | 803.6003 | 1353.9124 | 2285.3902 | 2642.1978 | 2631.3777 | 2616.3973 | 2595.58 | 2566.5555 | 2525.9672 | 2469.0557 | 2389.0649 | 2276.395 | 2117.3923 | 1892.6214 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.5324 | 3.8897 | 6.0867 | 9.6764 | 15.589 | 25.3948 | 41.7524 | 69.1738 | 115.3333 | 193.3057 | 325.401 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46469 | 1.822 | 4.019 | 7.6087 | 13.5213 | 23.3271 | 39.6847 | 67.1061 | 113.2656 | 190.8308 | 322.1204 | 372.4116 | 370.8866 | 368.7751 | 365.8409 | 361.75 | 356.0292 | 348.0076 | 336.7331 | 320.8526 | 298.4415 | 266.7606 |  | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.024466 | 0.03758 | 0.058805 | 0.093486 | 0.15061 | 0.24535 | 0.40338 | 0.66831 | 1.1143 | 1.8676 | 3.1438 | 3.6403 | 3.6403 | 3.6403 | 3.6403 | 3.6403 | 3.6403 | 3.6403 | 3.6403 | 3.6403 | 3.6403 | 3.6403 |  | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.019976 | 0.023911 | 0.031695 | 0.04238 | 0.057114 | 0.077514 | 0.10586 | 0.14538 | 0.20066 | 0.27815 | 0.38708 | 0.54051 | 0.75702 | 1.0631 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044895 | 0.017603 | 0.038829 | 0.07351 | 0.13063 | 0.22537 | 0.3834 | 0.64833 | 1.0943 | 1.8437 | 3.1121 | 3.598 | 3.5832 | 3.5628 | 3.5345 | 3.495 | 3.4397 | 3.3622 | 3.2533 | 3.0998 | 2.8833 | 2.5772 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9604 | 27.2914 | 60.1996 | 113.9679 | 202.5301 | 349.4072 | 594.4206 | 1005.1555 | 1696.5592 | 2858.3771 | 4824.9111 | 5578.2025 | 5555.3593 | 5523.7326 | 5479.7832 | 5418.5069 | 5332.8169 | 5212.6653 | 5043.789 | 4805.9206 | 4470.2343 | 3995.6984
| FALSE | 1871 | 22014605 | GCY | Blank | 22 | BUS VRR 1 | VOLTAGE REGULATION | C | RMS | 2V164S | 2V164 S | 2V164S | Digital |  | 0 | 1 |  | 1.0266 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 3.4047 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 30.9493 | 30.9493 | 0 |  | 0.11989 |  | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 86.42 | 120.2029 | 167.7354 | 234.7461 | 329.3849 | 463.2553 | 652.8892 | 921.8552 | 1303.7727 | 1846.6219 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 86.42 | 120.2029 | 167.7354 | 234.7461 | 329.3849 | 463.2553 | 652.8892 | 921.8552 | 1303.7727 | 1846.6219 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 89.2048 | 124.0764 | 173.1405 | 242.3105 | 339.999 | 478.1833 | 673.9279 | 951.5611 | 1345.7855 | 1906.1274 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.5733 | 17.4884 | 24.404 | 34.1534 | 47.9225 | 67.3994 | 94.9894 | 134.1216 | 189.6871 | 268.6667 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 133.0601 | 188.1982 | 261.7677 | 365.2798 | 511.21 | 717.3065 | 1008.838 | 1421.8065 | 2007.5378 | 2839.2454 | 4021.416 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 1872 | 22008071 | GCY | Blank | 22 | BUS VRR 2 | VOLTAGE REGULATION | C | RMS | 2V162 | 2V162 | 2V162 | Electronic |  | 0 | 2190 |  | 4.0857 | 0.0046133 | 0 | 0.0046133 | 15.8583 | 0 | 15.8583 | 13.0955 | 1.8458 | 0 |  | 11.2347 | 0.060373 | 0 | 0.060373 | 207.531 | 0 | 207.531 | 171.3748 | 24.1551 | 0 |  | 0.0051679 | 0 | 0.0051679 | 17.7648 | 0 | 17.7648 | 14.6698 | 2.0677 | 0 |  | 30.7996 | 403.0609 | 34.5023 | 368.5586 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0058259 | 0.0074059 | 0.0094716 | 0.012181 | 0.015744 | 0.020445 | 0.026659 | 0.034893 | 0.045827 | 0.060373 | 0.079755 | 0.10562 | 0.1402 | 0.18646 | 0.24845 | 0.33158 | 0.44317 | 0.5931 | 0.79471 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.8952 | 49.4434 | 63.2343 | 81.3218 | 105.1136 | 136.4927 | 177.9802 | 232.9554 | 305.9527 | 403.0609 | 532.4635 | 705.1668 | 935.9838 | 1244.8621 | 1658.6796 | 2213.669 | 2958.6968 | 3959.6949 | 5305.6535 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 | 5349.5046 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 20.0267 | 25.4578 | 32.5586 | 41.8716 | 54.1217 | 70.2784 | 91.6398 | 119.9458 | 157.5312 | 207.531 | 274.1588 | 363.0816 | 481.9263 | 640.9639 | 854.0333 | 1139.7905 | 1523.3959 | 2038.7973 | 2731.8145 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 | 2754.3929 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 5.8148 | 11.246 | 18.3467 | 27.6598 | 39.9099 | 56.0666 | 77.4279 | 105.734 | 143.3194 | 193.3192 | 259.947 | 348.8697 | 467.7145 | 626.7521 | 839.8215 | 1125.5786 | 1509.1841 | 2021.7866 | 2709.2659 | 2724.2423 | 2713.7602 | 2699.2475 | 2679.0803 | 2650.9622 | 2611.6413 | 2556.507 | 2479.0141 | 2369.8626 | 2215.825 | 1998.073 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.8148 | 11.246 | 18.3467 | 27.6598 | 39.9099 | 56.0666 | 77.4279 | 105.734 | 143.3194 | 193.3192 | 259.947 | 348.8697 | 467.7145 | 626.7521 | 839.8215 | 1125.5786 | 1509.1841 | 2021.7866 | 2709.2659 | 2724.2423 | 2713.7602 | 2699.2475 | 2679.0803 | 2650.9622 | 2611.6413 | 2556.507 | 2479.0141 | 2369.8626 | 2215.825 | 1998.073 |  | 16.5376 | 21.0225 | 26.8862 | 34.5767 | 44.6926 | 58.0344 | 75.6742 | 99.0488 | 130.086 | 171.3748 | 226.3946 | 299.8252 | 397.9647 | 529.2947 | 705.243 | 941.2153 | 1257.9887 | 1683.5964 | 2255.8756 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 1.8678 | 6.3527 | 12.2164 | 19.9069 | 30.0228 | 43.3647 | 61.0044 | 84.379 | 115.4162 | 156.705 | 211.7248 | 285.1554 | 383.2949 | 514.6249 | 690.5732 | 926.5455 | 1243.3189 | 1666.0376 | 2232.6004 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 2.331 | 2.9631 | 3.7896 | 4.8735 | 6.2994 | 8.1799 | 10.6662 | 13.9608 | 18.3355 | 24.1551 | 31.9101 | 42.2601 | 56.0927 | 74.6035 | 99.4033 | 132.6633 | 177.3122 | 237.3012 | 317.9633 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0.26327 | 0.89541 | 1.7219 | 2.8059 | 4.2317 | 6.1122 | 8.5985 | 11.8931 | 16.2678 | 22.0874 | 29.8424 | 40.1924 | 54.025 | 72.5358 | 97.3356 | 130.5956 | 175.2445 | 234.8263 | 314.6827 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.9459 | 18.4941 | 32.285 | 50.3725 | 74.1643 | 105.5434 | 147.0309 | 202.0061 | 275.0034 | 372.1116 | 501.5142 | 674.2175 | 905.0345 | 1213.9128 | 1627.7303 | 2182.7197 | 2927.7475 | 3922.6505 | 5256.549 | 5283.8453 | 5261.0181 | 5229.4137 | 5185.4953 | 5124.262 | 5038.6324 | 4918.5654 | 4749.8081 | 4512.1072 | 4176.6572 | 3702.4555
| TRUE | 1873 | 22001645 | GCY | Blank | 22 | CAP NO.1 | OVERCURRENT | X | ASEA | GROUP_2603 | GROUP 2603 | GROUP 2000s | Electronic |  | 0.2894 | 2190 |  | 8.25 | 0.026286 | 0.013817 | 0.012468 | 152.1704 | 3868.8382 | 4021.0086 | 153.0587 | 10.655 | 11431.8577 |  | 13.0142 | 0.090569 | 0.047609 | 0.042961 | 524.316 | 13330.4101 | 13854.7262 | 527.3766 | 36.7129 | 39389.4348 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.57365 | 28.9984 | 14.6814 | 2.0677 | 1.6951 |  | 15616.5801 | 53808.2505 | 47.4426 | 53760.8079 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.015591 | 0.017605 | 0.019894 | 0.022495 | 0.025452 | 0.028816 | 0.032643 | 0.037 | 0.04196 | 0.047609 | 0.054044 | 0.061378 | 0.069737 | 0.079268 | 0.090138 | 0.10254 | 0.11668 | 0.13283 | 0.15126 | 0.1723 | 0.19632 | 0.22376 | 0.2551 | 0.2909 | 0.33182 | 0.37858 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 17621.1966 | 19897.7678 | 22484.2521 | 25423.998 | 28766.5183 | 32568.376 | 36894.1978 | 41817.835 | 47423.6927 | 53808.2505 | 61081.8049 | 69370.4637 | 78818.4302 | 89590.6184 | 101875.6492 | 115889.2804 | 131878.3366 | 150125.2095 | 170953.0133 | 194731.4904 | 221883.7758 | 252894.147 | 288316.9027 | 328786.5339 | 375029.3777 | 427876.9699 | 476048.2151 | 476048.2151 | 476048.2151 | 476048.2151 |  | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 39.7819 | 52.7333 | 70.5115 | 95.0256 | 128.9656 | 176.1295 | 241.8878 | 333.8454 | 462.7851 | 644.0135 | 899.2802 | 1259.5195 | 1768.7642 |  | 171.7037 | 193.887 | 219.0901 | 247.7354 | 280.3055 | 317.3513 | 359.5028 | 407.4795 | 462.1039 | 524.316 | 595.1907 | 675.9566 | 768.0191 | 872.985 | 992.6923 | 1129.2433 | 1285.0431 | 1462.8435 | 1665.7929 | 1897.4941 | 2162.0702 | 2464.2401 | 2809.405 | 3203.7474 | 3654.3449 | 4169.3001 | 4638.6883 | 4638.6883 | 4638.6883 | 4638.6883 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 157.4913 | 179.6746 | 204.8777 | 233.523 | 266.0931 | 303.139 | 345.2904 | 393.2671 | 447.8915 | 510.1036 | 580.9783 | 661.7443 | 753.8067 | 858.7726 | 978.4799 | 1115.0309 | 1270.8307 | 1445.8322 | 1643.2434 | 1867.3423 | 2121.4359 | 2409.0925 | 2734.0894 | 3100.3126 | 3511.5877 | 3971.4063 | 4363.2985 | 4254.1427 | 4100.099 | 3882.3384 |  | 4365.4602 | 4929.456 | 5570.2295 | 6298.5196 | 7126.5928 | 8068.4617 | 9140.1371 | 10359.9148 | 11748.7052 | 13330.4101 | 15132.3543 | 17185.7796 | 19526.4107 | 22195.1035 | 25238.5866 | 28710.3116 | 32671.4268 | 37191.8915 | 42351.7539 | 48242.6136 | 54969.2976 | 62651.7806 | 71427.3839 | 81453.2958 | 92909.4586 | 106001.8761 | 117935.7793 | 117935.7793 | 117935.7793 | 117935.7793 |  | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.68662 | 0.91016 | 1.217 | 1.6401 | 2.2259 | 3.0399 | 4.1749 | 5.7621 | 7.9875 | 11.1155 | 15.5213 | 21.7389 | 30.5284 |  | 4364.8866 | 4928.8824 | 5569.6558 | 6297.946 | 7126.0191 | 8067.8881 | 9139.5635 | 10359.3412 | 11748.1316 | 13329.8365 | 15131.7807 | 17185.2059 | 19525.8371 | 22194.5298 | 25238.0129 | 28709.738 | 32670.8531 | 37191.2049 | 42350.8437 | 48241.3966 | 54967.6575 | 62649.5547 | 71424.344 | 81449.1209 | 92903.6965 | 105993.8885 | 117924.6638 | 117920.258 | 117914.0404 | 117905.251 |  | 4522.3779 | 5108.557 | 5774.5335 | 6531.469 | 7392.1122 | 8371.027 | 9484.8539 | 10752.6083 | 12196.0231 | 13839.9401 | 15712.7589 | 17846.9502 | 20279.6438 | 23053.3025 | 26216.4928 | 29824.7689 | 33941.6839 | 38637.0371 | 43994.0871 | 50108.7389 | 57089.0934 | 65058.6472 | 74158.4334 | 84549.4335 | 96415.2842 | 109965.2948 | 122287.9623 | 122174.4007 | 122014.1394 | 121787.5893 |  | 172.706 | 195.0188 | 220.369 | 249.1815 | 281.9417 | 319.2039 | 361.6014 | 409.8581 | 464.8014 | 527.3766 | 598.665 | 679.9025 | 772.5023 | 878.0809 | 998.487 | 1135.8351 | 1292.5444 | 1471.3827 | 1675.5168 | 1908.5705 | 2174.691 | 2478.6248 | 2825.8046 | 3222.4489 | 3675.6767 | 4193.6379 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 158.0246 | 180.3373 | 205.6876 | 234.5001 | 267.2603 | 304.5224 | 346.92 | 395.1767 | 450.1199 | 512.6952 | 583.9836 | 665.221 | 757.8209 | 863.3995 | 983.8056 | 1121.1537 | 1277.863 | 1453.81 | 1652.2231 | 1877.4237 | 2132.7157 | 2421.6573 | 2748.0035 | 3115.6006 | 3528.2083 | 3989.2133 | 4381.2881 | 4268.5299 | 4109.4026 | 3884.4555 |  | 12.0228 | 13.5761 | 15.3408 | 17.3466 | 19.6271 | 22.2211 | 25.1726 | 28.5319 | 32.3567 | 36.7129 | 41.6756 | 47.3308 | 53.7771 | 61.1269 | 69.5088 | 79.0702 | 89.9794 | 102.429 | 116.6397 | 132.8635 | 151.3892 | 172.5473 | 196.716 | 224.328 | 255.8791 | 291.9365 | 324.8033 | 324.8033 | 324.8033 | 324.8033 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 9.9551 | 11.5084 | 13.2731 | 15.2788 | 17.5594 | 20.1534 | 23.1049 | 26.4642 | 30.289 | 34.6452 | 39.6078 | 45.2631 | 51.7094 | 59.0591 | 67.4411 | 77.0025 | 87.9117 | 99.9541 | 113.359 | 128.4768 | 145.4775 | 164.5241 | 185.7586 | 209.2796 | 235.1098 | 263.1456 | 284.7378 | 268.8571 | 246.4458 | 214.7645 |  | 12899.3039 | 14565.83 | 16459.2228 | 18611.2149 | 21058.0513 | 23841.138 | 27007.7838 | 30612.0506 | 34715.7255 | 39389.4348 | 44713.9194 | 50781.4942 | 57697.7209 | 65583.3221 | 74576.3746 | 84834.8203 | 96539.3429 | 109896.6627 | 125143.3101 | 142549.9487 | 162426.3277 | 185126.9542 | 211057.5933 | 240682.7137 | 274534.0184 | 313220.2193 | 348483.1781 | 348483.1781 | 348483.1781 | 348483.1781 |  | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 2.0289 | 2.6894 | 3.5961 | 4.8463 | 6.5772 | 8.9826 | 12.3363 | 17.0261 | 23.602 | 32.8447 | 45.8632 | 64.2354 | 90.2069 |  | 12897.6088 | 14564.1349 | 16457.5277 | 18609.5198 | 21056.3563 | 23839.4429 | 27006.0888 | 30610.3556 | 34714.0304 | 39387.7398 | 44712.2243 | 50779.7991 | 57696.0258 | 65581.6271 | 74574.6795 | 84833.1252 | 96537.6478 | 109894.6338 | 125140.6207 | 142546.3527 | 162421.4814 | 185120.3769 | 211048.6107 | 240670.3774 | 274516.9923 | 313196.6173 | 348450.3335 | 348437.3149 | 348418.9427 | 348392.9713 |  | 17587.9663 | 19864.5376 | 22451.0219 | 25390.7678 | 28733.2881 | 32535.1458 | 36860.9675 | 41784.6048 | 47390.4625 | 53775.0203 | 61048.5747 | 69337.2335 | 78785.1999 | 89557.3882 | 101842.419 | 115856.0502 | 131845.1064 | 150085.435 | 170900.2899 | 194660.992 | 221788.7679 | 252765.2055 | 288140.8061 | 328544.6912 | 374695.5946 | 427414.271 | 475404.3217 | 475149.1026 | 474788.9304 | 474279.7807
| TRUE | 1874 | 22001646 | GCY | Blank | 22 | CAP NO.1 | NEUTRAL BALANCE | X | ASEA | GROUP_2945 | GROUP 2945 | GROUP 2000s | Electronic |  | 0.2894 | 2190 |  | 8.25 | 0.026286 | 0.013817 | 0.012468 | 152.1704 | 3868.8382 | 4021.0086 | 153.0587 | 10.655 | 11431.8577 |  | 13.0142 | 0.090569 | 0.047609 | 0.042961 | 524.316 | 13330.4101 | 13854.7262 | 527.3766 | 36.7129 | 39389.4348 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.57365 | 28.9984 | 14.6814 | 2.0677 | 1.6951 |  | 15616.5801 | 53808.2505 | 47.4426 | 53760.8079 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.015591 | 0.017605 | 0.019894 | 0.022495 | 0.025452 | 0.028816 | 0.032643 | 0.037 | 0.04196 | 0.047609 | 0.054044 | 0.061378 | 0.069737 | 0.079268 | 0.090138 | 0.10254 | 0.11668 | 0.13283 | 0.15126 | 0.1723 | 0.19632 | 0.22376 | 0.2551 | 0.2909 | 0.33182 | 0.37858 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 17621.1966 | 19897.7678 | 22484.2521 | 25423.998 | 28766.5183 | 32568.376 | 36894.1978 | 41817.835 | 47423.6927 | 53808.2505 | 61081.8049 | 69370.4637 | 78818.4302 | 89590.6184 | 101875.6492 | 115889.2804 | 131878.3366 | 150125.2095 | 170953.0133 | 194731.4904 | 221883.7758 | 252894.147 | 288316.9027 | 328786.5339 | 375029.3777 | 427876.9699 | 476048.2151 | 476048.2151 | 476048.2151 | 476048.2151 |  | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 33.2364 | 39.7819 | 52.7333 | 70.5115 | 95.0256 | 128.9656 | 176.1295 | 241.8878 | 333.8454 | 462.7851 | 644.0135 | 899.2802 | 1259.5195 | 1768.7642 |  | 171.7037 | 193.887 | 219.0901 | 247.7354 | 280.3055 | 317.3513 | 359.5028 | 407.4795 | 462.1039 | 524.316 | 595.1907 | 675.9566 | 768.0191 | 872.985 | 992.6923 | 1129.2433 | 1285.0431 | 1462.8435 | 1665.7929 | 1897.4941 | 2162.0702 | 2464.2401 | 2809.405 | 3203.7474 | 3654.3449 | 4169.3001 | 4638.6883 | 4638.6883 | 4638.6883 | 4638.6883 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 157.4913 | 179.6746 | 204.8777 | 233.523 | 266.0931 | 303.139 | 345.2904 | 393.2671 | 447.8915 | 510.1036 | 580.9783 | 661.7443 | 753.8067 | 858.7726 | 978.4799 | 1115.0309 | 1270.8307 | 1445.8322 | 1643.2434 | 1867.3423 | 2121.4359 | 2409.0925 | 2734.0894 | 3100.3126 | 3511.5877 | 3971.4063 | 4363.2985 | 4254.1427 | 4100.099 | 3882.3384 |  | 4365.4602 | 4929.456 | 5570.2295 | 6298.5196 | 7126.5928 | 8068.4617 | 9140.1371 | 10359.9148 | 11748.7052 | 13330.4101 | 15132.3543 | 17185.7796 | 19526.4107 | 22195.1035 | 25238.5866 | 28710.3116 | 32671.4268 | 37191.8915 | 42351.7539 | 48242.6136 | 54969.2976 | 62651.7806 | 71427.3839 | 81453.2958 | 92909.4586 | 106001.8761 | 117935.7793 | 117935.7793 | 117935.7793 | 117935.7793 |  | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.68662 | 0.91016 | 1.217 | 1.6401 | 2.2259 | 3.0399 | 4.1749 | 5.7621 | 7.9875 | 11.1155 | 15.5213 | 21.7389 | 30.5284 |  | 4364.8866 | 4928.8824 | 5569.6558 | 6297.946 | 7126.0191 | 8067.8881 | 9139.5635 | 10359.3412 | 11748.1316 | 13329.8365 | 15131.7807 | 17185.2059 | 19525.8371 | 22194.5298 | 25238.0129 | 28709.738 | 32670.8531 | 37191.2049 | 42350.8437 | 48241.3966 | 54967.6575 | 62649.5547 | 71424.344 | 81449.1209 | 92903.6965 | 105993.8885 | 117924.6638 | 117920.258 | 117914.0404 | 117905.251 |  | 4522.3779 | 5108.557 | 5774.5335 | 6531.469 | 7392.1122 | 8371.027 | 9484.8539 | 10752.6083 | 12196.0231 | 13839.9401 | 15712.7589 | 17846.9502 | 20279.6438 | 23053.3025 | 26216.4928 | 29824.7689 | 33941.6839 | 38637.0371 | 43994.0871 | 50108.7389 | 57089.0934 | 65058.6472 | 74158.4334 | 84549.4335 | 96415.2842 | 109965.2948 | 122287.9623 | 122174.4007 | 122014.1394 | 121787.5893 |  | 172.706 | 195.0188 | 220.369 | 249.1815 | 281.9417 | 319.2039 | 361.6014 | 409.8581 | 464.8014 | 527.3766 | 598.665 | 679.9025 | 772.5023 | 878.0809 | 998.487 | 1135.8351 | 1292.5444 | 1471.3827 | 1675.5168 | 1908.5705 | 2174.691 | 2478.6248 | 2825.8046 | 3222.4489 | 3675.6767 | 4193.6379 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 158.0246 | 180.3373 | 205.6876 | 234.5001 | 267.2603 | 304.5224 | 346.92 | 395.1767 | 450.1199 | 512.6952 | 583.9836 | 665.221 | 757.8209 | 863.3995 | 983.8056 | 1121.1537 | 1277.863 | 1453.81 | 1652.2231 | 1877.4237 | 2132.7157 | 2421.6573 | 2748.0035 | 3115.6006 | 3528.2083 | 3989.2133 | 4381.2881 | 4268.5299 | 4109.4026 | 3884.4555 |  | 12.0228 | 13.5761 | 15.3408 | 17.3466 | 19.6271 | 22.2211 | 25.1726 | 28.5319 | 32.3567 | 36.7129 | 41.6756 | 47.3308 | 53.7771 | 61.1269 | 69.5088 | 79.0702 | 89.9794 | 102.429 | 116.6397 | 132.8635 | 151.3892 | 172.5473 | 196.716 | 224.328 | 255.8791 | 291.9365 | 324.8033 | 324.8033 | 324.8033 | 324.8033 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 9.9551 | 11.5084 | 13.2731 | 15.2788 | 17.5594 | 20.1534 | 23.1049 | 26.4642 | 30.289 | 34.6452 | 39.6078 | 45.2631 | 51.7094 | 59.0591 | 67.4411 | 77.0025 | 87.9117 | 99.9541 | 113.359 | 128.4768 | 145.4775 | 164.5241 | 185.7586 | 209.2796 | 235.1098 | 263.1456 | 284.7378 | 268.8571 | 246.4458 | 214.7645 |  | 12899.3039 | 14565.83 | 16459.2228 | 18611.2149 | 21058.0513 | 23841.138 | 27007.7838 | 30612.0506 | 34715.7255 | 39389.4348 | 44713.9194 | 50781.4942 | 57697.7209 | 65583.3221 | 74576.3746 | 84834.8203 | 96539.3429 | 109896.6627 | 125143.3101 | 142549.9487 | 162426.3277 | 185126.9542 | 211057.5933 | 240682.7137 | 274534.0184 | 313220.2193 | 348483.1781 | 348483.1781 | 348483.1781 | 348483.1781 |  | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 1.6951 | 2.0289 | 2.6894 | 3.5961 | 4.8463 | 6.5772 | 8.9826 | 12.3363 | 17.0261 | 23.602 | 32.8447 | 45.8632 | 64.2354 | 90.2069 |  | 12897.6088 | 14564.1349 | 16457.5277 | 18609.5198 | 21056.3563 | 23839.4429 | 27006.0888 | 30610.3556 | 34714.0304 | 39387.7398 | 44712.2243 | 50779.7991 | 57696.0258 | 65581.6271 | 74574.6795 | 84833.1252 | 96537.6478 | 109894.6338 | 125140.6207 | 142546.3527 | 162421.4814 | 185120.3769 | 211048.6107 | 240670.3774 | 274516.9923 | 313196.6173 | 348450.3335 | 348437.3149 | 348418.9427 | 348392.9713 |  | 17587.9663 | 19864.5376 | 22451.0219 | 25390.7678 | 28733.2881 | 32535.1458 | 36860.9675 | 41784.6048 | 47390.4625 | 53775.0203 | 61048.5747 | 69337.2335 | 78785.1999 | 89557.3882 | 101842.419 | 115856.0502 | 131845.1064 | 150085.435 | 170900.2899 | 194660.992 | 221788.7679 | 252765.2055 | 288140.8061 | 328544.6912 | 374695.5946 | 427414.271 | 475404.3217 | 475149.1026 | 474788.9304 | 474279.7807
| TRUE | 1875 | 22001694 | GCY | Blank | 22 | CB BT1-2 | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 498.1313 | 0 | 498.1313 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 791.4596 | 45.1611 | 746.2985 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.1882 | 292.6741 | 330.7184 | 373.9588 | 423.1235 | 479.0446 | 542.6727 | 615.0939 | 697.5498 | 791.4596 | 898.4455 | 1020.3625 | 1159.3315 | 1317.7785 | 1498.4776 | 1704.6026 | 1939.7838 | 2208.1751 | 2514.5289 | 2864.2839 | 3263.6638 | 3719.792 | 4240.8213 | 4836.0847 | 5516.2655 | 6293.5949 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 163.1287 | 184.2041 | 208.1485 | 235.3633 | 266.3068 | 301.5026 | 341.549 | 387.1297 | 439.0261 | 498.1313 | 565.4664 | 642.1989 | 729.6637 | 829.3875 | 943.1165 | 1072.848 | 1220.8671 | 1389.788 | 1582.602 | 1802.7318 | 2054.0948 | 2341.1741 | 2669.1012 | 3043.7499 | 3471.8442 | 3961.0821 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 228.2389 | 261.7248 | 299.7691 | 343.0095 | 392.1742 | 448.0953 | 511.7234 | 584.1446 | 666.6005 | 760.5103 | 867.4962 | 989.4132 | 1128.3822 | 1286.8292 | 1467.5283 | 1673.6533 | 1908.8345 | 2171.1307 | 2465.4244 | 2798.6245 | 3175.1773 | 3599.701 | 4076.812 | 4610.8421 | 5205.3933 | 5862.6557 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 1876 | 22001692 | GCY | Blank | 22 | CB TR NO.1 | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 498.1313 | 0 | 498.1313 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 791.4596 | 45.1611 | 746.2985 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.1882 | 292.6741 | 330.7184 | 373.9588 | 423.1235 | 479.0446 | 542.6727 | 615.0939 | 697.5498 | 791.4596 | 898.4455 | 1020.3625 | 1159.3315 | 1317.7785 | 1498.4776 | 1704.6026 | 1939.7838 | 2208.1751 | 2514.5289 | 2864.2839 | 3263.6638 | 3719.792 | 4240.8213 | 4836.0847 | 5516.2655 | 6293.5949 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 163.1287 | 184.2041 | 208.1485 | 235.3633 | 266.3068 | 301.5026 | 341.549 | 387.1297 | 439.0261 | 498.1313 | 565.4664 | 642.1989 | 729.6637 | 829.3875 | 943.1165 | 1072.848 | 1220.8671 | 1389.788 | 1582.602 | 1802.7318 | 2054.0948 | 2341.1741 | 2669.1012 | 3043.7499 | 3471.8442 | 3961.0821 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 228.2389 | 261.7248 | 299.7691 | 343.0095 | 392.1742 | 448.0953 | 511.7234 | 584.1446 | 666.6005 | 760.5103 | 867.4962 | 989.4132 | 1128.3822 | 1286.8292 | 1467.5283 | 1673.6533 | 1908.8345 | 2171.1307 | 2465.4244 | 2798.6245 | 3175.1773 | 3599.701 | 4076.812 | 4610.8421 | 5205.3933 | 5862.6557 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 1877 | 22001695 | GCY | Blank | 22 | CB TR NO.1 | CB FAIL | Y | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 498.1313 | 0 | 498.1313 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 791.4596 | 45.1611 | 746.2985 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.1882 | 292.6741 | 330.7184 | 373.9588 | 423.1235 | 479.0446 | 542.6727 | 615.0939 | 697.5498 | 791.4596 | 898.4455 | 1020.3625 | 1159.3315 | 1317.7785 | 1498.4776 | 1704.6026 | 1939.7838 | 2208.1751 | 2514.5289 | 2864.2839 | 3263.6638 | 3719.792 | 4240.8213 | 4836.0847 | 5516.2655 | 6293.5949 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 163.1287 | 184.2041 | 208.1485 | 235.3633 | 266.3068 | 301.5026 | 341.549 | 387.1297 | 439.0261 | 498.1313 | 565.4664 | 642.1989 | 729.6637 | 829.3875 | 943.1165 | 1072.848 | 1220.8671 | 1389.788 | 1582.602 | 1802.7318 | 2054.0948 | 2341.1741 | 2669.1012 | 3043.7499 | 3471.8442 | 3961.0821 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 228.2389 | 261.7248 | 299.7691 | 343.0095 | 392.1742 | 448.0953 | 511.7234 | 584.1446 | 666.6005 | 760.5103 | 867.4962 | 989.4132 | 1128.3822 | 1286.8292 | 1467.5283 | 1673.6533 | 1908.8345 | 2171.1307 | 2465.4244 | 2798.6245 | 3175.1773 | 3599.701 | 4076.812 | 4610.8421 | 5205.3933 | 5862.6557 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 1878 | 22001693 | GCY | Blank | 22 | CB TR NO.2 | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 498.1313 | 0 | 498.1313 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 791.4596 | 45.1611 | 746.2985 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.1882 | 292.6741 | 330.7184 | 373.9588 | 423.1235 | 479.0446 | 542.6727 | 615.0939 | 697.5498 | 791.4596 | 898.4455 | 1020.3625 | 1159.3315 | 1317.7785 | 1498.4776 | 1704.6026 | 1939.7838 | 2208.1751 | 2514.5289 | 2864.2839 | 3263.6638 | 3719.792 | 4240.8213 | 4836.0847 | 5516.2655 | 6293.5949 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 163.1287 | 184.2041 | 208.1485 | 235.3633 | 266.3068 | 301.5026 | 341.549 | 387.1297 | 439.0261 | 498.1313 | 565.4664 | 642.1989 | 729.6637 | 829.3875 | 943.1165 | 1072.848 | 1220.8671 | 1389.788 | 1582.602 | 1802.7318 | 2054.0948 | 2341.1741 | 2669.1012 | 3043.7499 | 3471.8442 | 3961.0821 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 228.2389 | 261.7248 | 299.7691 | 343.0095 | 392.1742 | 448.0953 | 511.7234 | 584.1446 | 666.6005 | 760.5103 | 867.4962 | 989.4132 | 1128.3822 | 1286.8292 | 1467.5283 | 1673.6533 | 1908.8345 | 2171.1307 | 2465.4244 | 2798.6245 | 3175.1773 | 3599.701 | 4076.812 | 4610.8421 | 5205.3933 | 5862.6557 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 1879 | 22001696 | GCY | Blank | 22 | CB TR NO.2 | CB FAIL | Y | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 498.1313 | 0 | 498.1313 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 791.4596 | 45.1611 | 746.2985 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.1882 | 292.6741 | 330.7184 | 373.9588 | 423.1235 | 479.0446 | 542.6727 | 615.0939 | 697.5498 | 791.4596 | 898.4455 | 1020.3625 | 1159.3315 | 1317.7785 | 1498.4776 | 1704.6026 | 1939.7838 | 2208.1751 | 2514.5289 | 2864.2839 | 3263.6638 | 3719.792 | 4240.8213 | 4836.0847 | 5516.2655 | 6293.5949 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 163.1287 | 184.2041 | 208.1485 | 235.3633 | 266.3068 | 301.5026 | 341.549 | 387.1297 | 439.0261 | 498.1313 | 565.4664 | 642.1989 | 729.6637 | 829.3875 | 943.1165 | 1072.848 | 1220.8671 | 1389.788 | 1582.602 | 1802.7318 | 2054.0948 | 2341.1741 | 2669.1012 | 3043.7499 | 3471.8442 | 3961.0821 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 228.2389 | 261.7248 | 299.7691 | 343.0095 | 392.1742 | 448.0953 | 511.7234 | 584.1446 | 666.6005 | 760.5103 | 867.4962 | 989.4132 | 1128.3822 | 1286.8292 | 1467.5283 | 1673.6533 | 1908.8345 | 2171.1307 | 2465.4244 | 2798.6245 | 3175.1773 | 3599.701 | 4076.812 | 4610.8421 | 5205.3933 | 5862.6557 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 1880 | 22001651 | GCY | Blank | 22 | ALL FEEDERS | MASTER EARTH FAULT | X | ASEA | GROUP_2650 | GROUP 2650 | GROUP 2000s | Electronic |  | 0.81881 | 2190 |  | 8.25 | 0.026286 | 0.02098 | 0.0053053 | 156.1101 | 5874.4876 | 6030.5977 | 193.7249 | 10.7267 | 17358.2617 |  | 13.0142 | 0.090569 | 0.072289 | 0.01828 | 537.8905 | 20241.0451 | 20778.9356 | 667.4955 | 36.9597 | 59809.3621 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 28.4268 | 1.6231 | 30.0499 | 14.7027 | 2.0677 | 4.7959 |  | 23593.3109 | 81292.7528 | 51.6163 | 81241.1366 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.023673 | 0.026732 | 0.030207 | 0.034156 | 0.038647 | 0.043754 | 0.049566 | 0.056181 | 0.063712 | 0.072289 | 0.082061 | 0.093197 | 0.10589 | 0.12036 | 0.13687 | 0.15569 | 0.17717 | 0.20169 | 0.22967 | 0.26161 | 0.29809 | 0.33975 | 0.38734 | 0.44171 | 0.50384 | 0.57484 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 26621.8575 | 30061.2695 | 33968.8938 | 38410.2208 | 43460.0539 | 49203.8473 | 55739.2383 | 63177.8007 | 71647.0521 | 81292.7528 | 92281.5372 | 104803.9271 | 119077.7827 | 135352.2542 | 153912.307 | 175083.9052 | 199239.9478 | 226807.0683 | 258273.4233 | 294197.6141 | 335218.9073 | 382068.9429 | 435585.1471 | 496726.1002 | 566589.1423 | 646430.546 | 719206.99 | 719206.99 | 719206.99 | 719206.99 |  | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 44.7899 | 59.3716 | 79.3879 | 106.9879 | 145.2004 | 198.3015 | 272.3378 | 375.8715 | 521.0428 | 725.085 | 1012.486 | 1418.074 | 1991.4249 |  | 176.1491 | 198.9067 | 224.7623 | 254.1492 | 287.5625 | 325.5675 | 368.8103 | 418.0291 | 474.0677 | 537.8905 | 610.6001 | 693.4571 | 787.903 | 895.5864 | 1018.3929 | 1158.4792 | 1318.3127 | 1500.7163 | 1708.92 | 1946.6199 | 2218.0459 | 2528.0389 | 2882.1401 | 3286.6919 | 3748.9553 | 4277.2426 | 4758.7832 | 4758.7832 | 4758.7832 | 4758.7832 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 161.9357 | 184.6932 | 210.5489 | 239.9358 | 273.3491 | 311.3541 | 354.5969 | 403.8157 | 459.8543 | 523.6771 | 596.3866 | 679.2436 | 773.6896 | 881.373 | 1004.1795 | 1144.2658 | 1304.0993 | 1483.7037 | 1686.3688 | 1916.466 | 2177.4086 | 2472.8873 | 2806.819 | 3183.2496 | 3606.1877 | 4079.3345 | 4483.3735 | 4374.2097 | 4220.1549 | 4002.3785 |  | 6628.564 | 7484.9417 | 8457.8992 | 9563.7432 | 10821.0988 | 12251.2433 | 13878.4873 | 15730.6115 | 17839.3665 | 20241.0451 | 22977.1375 | 26095.0816 | 29649.1223 | 33701.2955 | 38322.5545 | 43594.061 | 49608.6629 | 56472.5875 | 64307.3808 | 73252.1285 | 83466.0014 | 95131.1702 | 108456.1453 | 123679.603 | 141074.7697 | 160954.4441 | 179075.0174 | 179075.0174 | 179075.0174 | 179075.0174 |  | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.9427 | 2.5752 | 3.4434 | 4.6405 | 6.2979 | 8.6011 | 11.8123 | 16.303 | 22.5996 | 31.4497 | 43.9154 | 61.5073 | 86.3757 |  | 6626.941 | 7483.3186 | 8456.2762 | 9562.1201 | 10819.4757 | 12249.6202 | 13876.8642 | 15728.9885 | 17837.7435 | 20239.422 | 22975.5144 | 26093.4585 | 29647.4992 | 33699.6724 | 38320.9314 | 43592.4379 | 49607.0398 | 56470.6448 | 64304.8056 | 73248.6851 | 83461.361 | 95124.8723 | 108447.5442 | 123667.7907 | 141058.4668 | 160931.8445 | 179043.5677 | 179031.102 | 179013.5101 | 178988.6417 |  | 6788.8766 | 7668.0118 | 8666.825 | 9802.056 | 11092.8248 | 12560.9743 | 14231.4611 | 16132.8041 | 18297.5977 | 20763.0991 | 23571.901 | 26772.7021 | 30421.1888 | 34581.0454 | 39325.1109 | 44736.7037 | 50911.1391 | 57954.3486 | 65991.1744 | 75165.1511 | 85638.7695 | 97597.7596 | 111254.3632 | 126851.0403 | 144664.6545 | 165011.179 | 183526.9411 | 183405.3117 | 183233.6649 | 182991.0201 |  | 218.5923 | 246.8333 | 278.9189 | 315.3867 | 356.8509 | 404.0132 | 457.6754 | 518.7535 | 588.2946 | 667.4955 | 757.7245 | 860.5459 | 977.7487 | 1111.3785 | 1263.7753 | 1437.6155 | 1635.9609 | 1862.3148 | 2120.6853 | 2415.6591 | 2752.4853 | 3137.1714 | 3576.5934 | 4078.6223 | 4652.2683 | 5307.8468 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 203.8896 | 232.1306 | 264.2162 | 300.684 | 342.1482 | 389.3105 | 442.9727 | 504.0508 | 573.5919 | 652.7928 | 743.0218 | 845.8433 | 963.046 | 1096.6758 | 1249.0726 | 1422.9128 | 1621.2582 | 1844.7166 | 2097.3578 | 2384.4672 | 2710.4492 | 3080.1213 | 3498.6795 | 3971.6191 | 4504.5862 | 5103.1259 | 5620.5245 | 5507.6029 | 5348.2449 | 5122.9719 |  | 12.1036 | 13.6673 | 15.4439 | 17.4632 | 19.7591 | 22.3705 | 25.3418 | 28.7237 | 32.5743 | 36.9597 | 41.9557 | 47.649 | 54.1386 | 61.5378 | 69.9761 | 79.6017 | 90.5843 | 103.1176 | 117.4238 | 133.7567 | 152.407 | 173.7073 | 198.0384 | 225.8361 | 257.5993 | 293.8991 | 326.9868 | 326.9868 | 326.9868 | 326.9868 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 10.0359 | 11.5996 | 13.3762 | 15.3954 | 17.6913 | 20.3027 | 23.274 | 26.656 | 30.5065 | 34.8919 | 39.888 | 45.5813 | 52.0709 | 59.47 | 67.9083 | 77.534 | 88.5165 | 100.6427 | 114.1431 | 129.3699 | 146.4951 | 165.6839 | 187.0808 | 210.7874 | 236.8296 | 265.1077 | 286.9206 | 271.0396 | 248.6279 | 216.9461 |  | 19586.4485 | 22116.9205 | 24991.8695 | 28259.4785 | 31974.7826 | 36200.6528 | 41008.9236 | 46481.6829 | 52712.7491 | 59809.3621 | 67894.1194 | 77107.1935 | 87608.8701 | 99582.4559 | 113237.6082 | 128814.1478 | 146586.427 | 166868.332 | 190019.0134 | 216449.4498 | 246629.9677 | 281098.855 | 320472.23 | 365455.3468 | 416855.5497 | 475597.1134 | 529140.7878 | 529140.7878 | 529140.7878 | 529140.7878 |  | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 5.7404 | 7.6093 | 10.1746 | 13.7119 | 18.6094 | 25.415 | 34.9037 | 48.1729 | 66.7786 | 92.9293 | 129.7636 | 181.7451 | 255.2277 |  | 19581.6525 | 22112.1246 | 24987.0736 | 28254.6826 | 31969.9867 | 36195.8569 | 41004.1277 | 46476.887 | 52707.9532 | 59804.5662 | 67889.3235 | 77102.3976 | 87604.0742 | 99577.66 | 113232.8123 | 128809.3519 | 146581.6311 | 166862.5916 | 190011.4041 | 216439.2752 | 246616.2558 | 281080.2457 | 320446.815 | 365420.4431 | 416807.3767 | 475530.3348 | 529047.8585 | 529011.0242 | 528959.0427 | 528885.5601 |  | 26584.4546 | 30023.8666 | 33931.4909 | 38372.818 | 43422.651 | 49166.4444 | 55701.8355 | 63140.3979 | 71609.6493 | 81255.35 | 92244.1343 | 104766.5242 | 119040.3798 | 135314.8513 | 153874.9041 | 175046.5023 | 199202.545 | 226762.2994 | 258214.0795 | 294118.2634 | 335111.9696 | 381923.8105 | 435386.9385 | 496453.89 | 566213.447 | 645909.7473 | 718482.2447 | 718194.9784 | 717789.5805 | 717216.4982
| TRUE | 1881 | 22001650 | GCY | Blank | 22 | ALL FEEDERS | BACKUP EARTH FAULT | X | ASEA | GROUP_2651 | GROUP 2651 | GROUP 2000s | Electronic |  | 0.81881 | 2190 |  | 8.25 | 0.026286 | 0.02098 | 0.0053053 | 156.1101 | 5874.4876 | 6030.5977 | 193.7249 | 10.7267 | 17358.2617 |  | 13.0142 | 0.090569 | 0.072289 | 0.01828 | 537.8905 | 20241.0451 | 20778.9356 | 667.4955 | 36.9597 | 59809.3621 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 28.4268 | 1.6231 | 30.0499 | 14.7027 | 2.0677 | 4.7959 |  | 23593.3109 | 81292.7528 | 51.6163 | 81241.1366 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.023673 | 0.026732 | 0.030207 | 0.034156 | 0.038647 | 0.043754 | 0.049566 | 0.056181 | 0.063712 | 0.072289 | 0.082061 | 0.093197 | 0.10589 | 0.12036 | 0.13687 | 0.15569 | 0.17717 | 0.20169 | 0.22967 | 0.26161 | 0.29809 | 0.33975 | 0.38734 | 0.44171 | 0.50384 | 0.57484 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 26621.8575 | 30061.2695 | 33968.8938 | 38410.2208 | 43460.0539 | 49203.8473 | 55739.2383 | 63177.8007 | 71647.0521 | 81292.7528 | 92281.5372 | 104803.9271 | 119077.7827 | 135352.2542 | 153912.307 | 175083.9052 | 199239.9478 | 226807.0683 | 258273.4233 | 294197.6141 | 335218.9073 | 382068.9429 | 435585.1471 | 496726.1002 | 566589.1423 | 646430.546 | 719206.99 | 719206.99 | 719206.99 | 719206.99 |  | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 37.4204 | 44.7899 | 59.3716 | 79.3879 | 106.9879 | 145.2004 | 198.3015 | 272.3378 | 375.8715 | 521.0428 | 725.085 | 1012.486 | 1418.074 | 1991.4249 |  | 176.1491 | 198.9067 | 224.7623 | 254.1492 | 287.5625 | 325.5675 | 368.8103 | 418.0291 | 474.0677 | 537.8905 | 610.6001 | 693.4571 | 787.903 | 895.5864 | 1018.3929 | 1158.4792 | 1318.3127 | 1500.7163 | 1708.92 | 1946.6199 | 2218.0459 | 2528.0389 | 2882.1401 | 3286.6919 | 3748.9553 | 4277.2426 | 4758.7832 | 4758.7832 | 4758.7832 | 4758.7832 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 161.9357 | 184.6932 | 210.5489 | 239.9358 | 273.3491 | 311.3541 | 354.5969 | 403.8157 | 459.8543 | 523.6771 | 596.3866 | 679.2436 | 773.6896 | 881.373 | 1004.1795 | 1144.2658 | 1304.0993 | 1483.7037 | 1686.3688 | 1916.466 | 2177.4086 | 2472.8873 | 2806.819 | 3183.2496 | 3606.1877 | 4079.3345 | 4483.3735 | 4374.2097 | 4220.1549 | 4002.3785 |  | 6628.564 | 7484.9417 | 8457.8992 | 9563.7432 | 10821.0988 | 12251.2433 | 13878.4873 | 15730.6115 | 17839.3665 | 20241.0451 | 22977.1375 | 26095.0816 | 29649.1223 | 33701.2955 | 38322.5545 | 43594.061 | 49608.6629 | 56472.5875 | 64307.3808 | 73252.1285 | 83466.0014 | 95131.1702 | 108456.1453 | 123679.603 | 141074.7697 | 160954.4441 | 179075.0174 | 179075.0174 | 179075.0174 | 179075.0174 |  | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.9427 | 2.5752 | 3.4434 | 4.6405 | 6.2979 | 8.6011 | 11.8123 | 16.303 | 22.5996 | 31.4497 | 43.9154 | 61.5073 | 86.3757 |  | 6626.941 | 7483.3186 | 8456.2762 | 9562.1201 | 10819.4757 | 12249.6202 | 13876.8642 | 15728.9885 | 17837.7435 | 20239.422 | 22975.5144 | 26093.4585 | 29647.4992 | 33699.6724 | 38320.9314 | 43592.4379 | 49607.0398 | 56470.6448 | 64304.8056 | 73248.6851 | 83461.361 | 95124.8723 | 108447.5442 | 123667.7907 | 141058.4668 | 160931.8445 | 179043.5677 | 179031.102 | 179013.5101 | 178988.6417 |  | 6788.8766 | 7668.0118 | 8666.825 | 9802.056 | 11092.8248 | 12560.9743 | 14231.4611 | 16132.8041 | 18297.5977 | 20763.0991 | 23571.901 | 26772.7021 | 30421.1888 | 34581.0454 | 39325.1109 | 44736.7037 | 50911.1391 | 57954.3486 | 65991.1744 | 75165.1511 | 85638.7695 | 97597.7596 | 111254.3632 | 126851.0403 | 144664.6545 | 165011.179 | 183526.9411 | 183405.3117 | 183233.6649 | 182991.0201 |  | 218.5923 | 246.8333 | 278.9189 | 315.3867 | 356.8509 | 404.0132 | 457.6754 | 518.7535 | 588.2946 | 667.4955 | 757.7245 | 860.5459 | 977.7487 | 1111.3785 | 1263.7753 | 1437.6155 | 1635.9609 | 1862.3148 | 2120.6853 | 2415.6591 | 2752.4853 | 3137.1714 | 3576.5934 | 4078.6223 | 4652.2683 | 5307.8468 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 203.8896 | 232.1306 | 264.2162 | 300.684 | 342.1482 | 389.3105 | 442.9727 | 504.0508 | 573.5919 | 652.7928 | 743.0218 | 845.8433 | 963.046 | 1096.6758 | 1249.0726 | 1422.9128 | 1621.2582 | 1844.7166 | 2097.3578 | 2384.4672 | 2710.4492 | 3080.1213 | 3498.6795 | 3971.6191 | 4504.5862 | 5103.1259 | 5620.5245 | 5507.6029 | 5348.2449 | 5122.9719 |  | 12.1036 | 13.6673 | 15.4439 | 17.4632 | 19.7591 | 22.3705 | 25.3418 | 28.7237 | 32.5743 | 36.9597 | 41.9557 | 47.649 | 54.1386 | 61.5378 | 69.9761 | 79.6017 | 90.5843 | 103.1176 | 117.4238 | 133.7567 | 152.407 | 173.7073 | 198.0384 | 225.8361 | 257.5993 | 293.8991 | 326.9868 | 326.9868 | 326.9868 | 326.9868 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 10.0359 | 11.5996 | 13.3762 | 15.3954 | 17.6913 | 20.3027 | 23.274 | 26.656 | 30.5065 | 34.8919 | 39.888 | 45.5813 | 52.0709 | 59.47 | 67.9083 | 77.534 | 88.5165 | 100.6427 | 114.1431 | 129.3699 | 146.4951 | 165.6839 | 187.0808 | 210.7874 | 236.8296 | 265.1077 | 286.9206 | 271.0396 | 248.6279 | 216.9461 |  | 19586.4485 | 22116.9205 | 24991.8695 | 28259.4785 | 31974.7826 | 36200.6528 | 41008.9236 | 46481.6829 | 52712.7491 | 59809.3621 | 67894.1194 | 77107.1935 | 87608.8701 | 99582.4559 | 113237.6082 | 128814.1478 | 146586.427 | 166868.332 | 190019.0134 | 216449.4498 | 246629.9677 | 281098.855 | 320472.23 | 365455.3468 | 416855.5497 | 475597.1134 | 529140.7878 | 529140.7878 | 529140.7878 | 529140.7878 |  | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 4.7959 | 5.7404 | 7.6093 | 10.1746 | 13.7119 | 18.6094 | 25.415 | 34.9037 | 48.1729 | 66.7786 | 92.9293 | 129.7636 | 181.7451 | 255.2277 |  | 19581.6525 | 22112.1246 | 24987.0736 | 28254.6826 | 31969.9867 | 36195.8569 | 41004.1277 | 46476.887 | 52707.9532 | 59804.5662 | 67889.3235 | 77102.3976 | 87604.0742 | 99577.66 | 113232.8123 | 128809.3519 | 146581.6311 | 166862.5916 | 190011.4041 | 216439.2752 | 246616.2558 | 281080.2457 | 320446.815 | 365420.4431 | 416807.3767 | 475530.3348 | 529047.8585 | 529011.0242 | 528959.0427 | 528885.5601 |  | 26584.4546 | 30023.8666 | 33931.4909 | 38372.818 | 43422.651 | 49166.4444 | 55701.8355 | 63140.3979 | 71609.6493 | 81255.35 | 92244.1343 | 104766.5242 | 119040.3798 | 135314.8513 | 153874.9041 | 175046.5023 | 199202.545 | 226762.2994 | 258214.0795 | 294118.2634 | 335111.9696 | 381923.8105 | 435386.9385 | 496453.89 | 566213.447 | 645909.7473 | 718482.2447 | 718194.9784 | 717789.5805 | 717216.4982
| TRUE | 1882 | 22009712 | GCY | GCY011 | 22 | GCY11 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.81881 | 1 |  | 4.0857 | 0.0054221 | 6.0818e-06 | 0.0054161 | 14.9126 | 0.42573 | 15.3383 | 15.4259 | 2.1695 | 4.2095 |  | 11.2347 | 0.070957 | 7.959e-05 | 0.070878 | 195.1546 | 5.5713 | 200.7259 | 201.8725 | 28.3908 | 55.0875 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 4.0121 |  | 37.1431 | 486.0767 | 35.4017 | 450.6749 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0068474 | 0.0087043 | 0.011132 | 0.014316 | 0.018505 | 0.024029 | 0.031333 | 0.041011 | 0.053862 | 0.070957 | 0.093738 | 0.12414 | 0.16478 | 0.21915 | 0.292 | 0.38971 | 0.52087 | 0.69709 | 0.93404 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 7.6804e-06 | 9.7633e-06 | 1.2486e-05 | 1.6058e-05 | 2.0756e-05 | 2.6952e-05 | 3.5145e-05 | 4.6e-05 | 6.0415e-05 | 7.959e-05 | 0.00010514 | 0.00013924 | 0.00018482 | 0.00024582 | 0.00032753 | 0.00043712 | 0.00058424 | 0.0007819 | 0.0010477 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 46.9062 | 59.627 | 76.2583 | 98.0711 | 126.7632 | 164.6052 | 214.6376 | 280.9357 | 368.9677 | 486.0767 | 642.1315 | 850.4054 | 1128.7622 | 1501.2582 | 2000.3069 | 2669.6039 | 3568.0802 | 4775.2473 | 6398.4241 | 6451.307 | 6451.307 | 6451.307 | 6451.307 | 6451.307 | 6451.307 | 6451.307 | 6451.307 | 6451.307 | 6451.307 | 6451.307 |  | 35.4017 | 35.4017 | 35.4017 | 35.4017 | 35.4017 | 35.4017 | 35.4017 | 35.4017 | 35.4017 | 35.4017 | 35.4017 | 35.4017 | 35.4017 | 35.4017 | 35.4017 | 35.4017 | 35.4017 | 42.3737 | 56.1688 | 75.1053 | 101.2164 | 137.3675 | 187.6041 | 257.6465 | 355.595 | 492.9351 | 685.9702 | 957.8673 | 1341.5758 | 1883.9973 |  | 18.8323 | 23.9396 | 30.6169 | 39.3745 | 50.8941 | 66.0872 | 86.1747 | 112.7927 | 148.1366 | 195.1546 | 257.8089 | 341.4287 | 453.1859 | 602.7391 | 803.1018 | 1071.8174 | 1432.546 | 1917.2107 | 2568.8988 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 4.6189 | 9.7262 | 16.4035 | 25.1611 | 36.6807 | 51.8738 | 71.9613 | 98.5793 | 133.9232 | 180.9412 | 243.5955 | 327.2153 | 438.9725 | 588.5257 | 788.8884 | 1057.604 | 1418.3326 | 1900.1981 | 2546.3476 | 2559.9767 | 2549.4934 | 2534.9791 | 2514.8096 | 2486.6884 | 2447.3631 | 2392.2225 | 2314.721 | 2205.5572 | 2051.5024 | 1833.726 |  | 0.53763 | 0.68343 | 0.87405 | 1.1241 | 1.4529 | 1.8867 | 2.4601 | 3.22 | 4.229 | 5.5713 | 7.36 | 9.7471 | 12.9376 | 17.2071 | 22.927 | 30.5984 | 40.8965 | 54.7327 | 73.3372 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 |  | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.48568 | 0.64379 | 0.86084 | 1.1601 | 1.5745 | 2.1503 | 2.9531 | 4.0757 | 5.6499 | 7.8624 | 10.9788 | 15.3768 | 21.5939 |  | 0.13186 | 0.27766 | 0.46829 | 0.7183 | 1.0472 | 1.4809 | 2.0544 | 2.8143 | 3.8233 | 5.1655 | 6.9542 | 9.3414 | 12.5318 | 16.8013 | 22.5213 | 30.1926 | 40.4907 | 54.2471 | 72.6934 | 73.0825 | 72.7832 | 72.3689 | 71.7931 | 70.9902 | 69.8676 | 68.2934 | 66.0809 | 62.9645 | 58.5665 | 52.3494 |  | 4.7508 | 10.0038 | 16.8718 | 25.8794 | 37.7278 | 53.3547 | 74.0156 | 101.3935 | 137.7464 | 186.1067 | 250.5497 | 336.5566 | 451.5044 | 605.327 | 811.4097 | 1087.7966 | 1458.8233 | 1954.4451 | 2619.041 | 2633.0592 | 2622.2766 | 2607.3479 | 2586.6027 | 2557.6786 | 2517.2307 | 2460.516 | 2380.8019 | 2268.5217 | 2110.0689 | 1886.0754 |  | 19.4806 | 24.7637 | 31.6708 | 40.7299 | 52.646 | 68.3622 | 89.1411 | 116.6754 | 153.236 | 201.8725 | 266.6836 | 353.1819 | 468.7862 | 623.4875 | 830.7475 | 1108.7132 | 1481.8594 | 1983.2079 | 2657.3295 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 4.7779 | 10.061 | 16.9681 | 26.0272 | 37.9433 | 53.6595 | 74.4384 | 101.9727 | 138.5333 | 187.1698 | 251.9809 | 338.4792 | 454.0835 | 608.7848 | 816.0448 | 1094.0105 | 1467.1567 | 1965.6097 | 2634.002 | 2648.1003 | 2637.2561 | 2622.2422 | 2601.3784 | 2572.2891 | 2531.6101 | 2474.5714 | 2394.402 | 2281.4804 | 2122.1224 | 1896.8494 |  | 2.7397 | 3.4827 | 4.4541 | 5.7282 | 7.404 | 9.6143 | 12.5366 | 16.4089 | 21.5507 | 28.3908 | 37.5057 | 49.6706 | 65.9289 | 87.6857 | 116.8342 | 155.9266 | 208.4049 | 278.9133 | 373.72 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 0.67196 | 1.415 | 2.3864 | 3.6604 | 5.3363 | 7.5465 | 10.4688 | 14.3412 | 19.483 | 26.3231 | 35.4379 | 47.6028 | 63.8611 | 85.6179 | 114.7664 | 153.8588 | 206.3371 | 276.4383 | 370.4393 | 372.422 | 370.8969 | 368.7854 | 365.8512 | 361.7601 | 356.0391 | 348.0174 | 336.7425 | 320.8615 | 298.4498 | 266.768 |  | 5.3159 | 6.7576 | 8.6424 | 11.1145 | 14.3662 | 18.6548 | 24.3251 | 31.8387 | 41.8154 | 55.0875 | 72.7733 | 96.3771 | 127.9235 | 170.1388 | 226.6964 | 302.5484 | 404.3735 | 541.1827 | 725.1387 | 731.1319 | 731.1319 | 731.1319 | 731.1319 | 731.1319 | 731.1319 | 731.1319 | 731.1319 | 731.1319 | 731.1319 | 731.1319 |  | 4.0121 | 4.0121 | 4.0121 | 4.0121 | 4.0121 | 4.0121 | 4.0121 | 4.0121 | 4.0121 | 4.0121 | 4.0121 | 4.0121 | 4.0121 | 4.0121 | 4.0121 | 4.0121 | 4.0121 | 4.8022 | 6.3657 | 8.5117 | 11.4709 | 15.568 | 21.2613 | 29.1993 | 40.2999 | 55.8647 | 77.7416 | 108.5559 | 152.0419 | 213.515 |  | 1.3038 | 2.7455 | 4.6303 | 7.1024 | 10.3541 | 14.6427 | 20.3129 | 27.8266 | 37.8033 | 51.0754 | 68.7612 | 92.365 | 123.9114 | 166.1267 | 222.6843 | 298.5363 | 400.3614 | 536.3805 | 718.773 | 722.6202 | 719.661 | 715.5639 | 709.8706 | 701.9326 | 690.832 | 675.2672 | 653.3904 | 622.576 | 579.09 | 517.617 |  | 11.5045 | 24.2253 | 40.8566 | 62.6694 | 91.3615 | 129.2035 | 179.2359 | 245.534 | 333.566 | 450.6749 | 606.7298 | 815.0037 | 1093.3605 | 1465.8565 | 1964.9052 | 2634.2022 | 3532.6784 | 4732.8736 | 6342.2553 | 6376.2017 | 6350.0906 | 6313.9394 | 6263.7029 | 6193.6605 | 6095.712 | 5958.3719 | 5765.3368 | 5493.4397 | 5109.7312 | 4567.3097
| TRUE | 1883 | 22009713 | GCY | GCY012 | 22 | GCY12 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 4.0857 | 0.0054221 | 4.2659e-06 | 0.0054179 | 14.9121 | 0.29862 | 15.2107 | 15.4156 | 2.1694 | 5.9053 |  | 11.2347 | 0.070957 | 5.5827e-05 | 0.070902 | 195.148 | 3.9079 | 199.0559 | 201.7376 | 28.3906 | 77.2798 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.6284 |  | 38.701 | 506.4639 | 36.8866 | 469.5773 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0068474 | 0.0087043 | 0.011132 | 0.014316 | 0.018505 | 0.024029 | 0.031333 | 0.041011 | 0.053862 | 0.070957 | 0.093738 | 0.12414 | 0.16478 | 0.21915 | 0.292 | 0.38971 | 0.52087 | 0.69709 | 0.93404 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 5.3872e-06 | 6.8482e-06 | 8.7584e-06 | 1.1264e-05 | 1.4559e-05 | 1.8905e-05 | 2.4651e-05 | 3.2266e-05 | 4.2376e-05 | 5.5827e-05 | 7.375e-05 | 9.767e-05 | 0.00012964 | 0.00017242 | 0.00022974 | 0.00030661 | 0.0004098 | 0.00054844 | 0.00073487 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 48.8736 | 62.1279 | 79.4567 | 102.1845 | 132.08 | 171.5092 | 223.64 | 292.7188 | 384.4431 | 506.4639 | 669.064 | 886.0734 | 1176.1051 | 1564.2245 | 2084.2045 | 2781.5733 | 3717.7338 | 4975.5323 | 6666.7889 | 6721.8899 | 6721.8899 | 6721.8899 | 6721.8899 | 6721.8899 | 6721.8899 | 6721.8899 | 6721.8899 | 6721.8899 | 6721.8899 | 6721.8899 |  | 36.8866 | 36.8866 | 36.8866 | 36.8866 | 36.8866 | 36.8866 | 36.8866 | 36.8866 | 36.8866 | 36.8866 | 36.8866 | 36.8866 | 36.8866 | 36.8866 | 36.8866 | 36.8866 | 36.8866 | 44.1509 | 58.5246 | 78.2554 | 105.4616 | 143.1291 | 195.4727 | 268.4528 | 370.5095 | 513.6099 | 714.7414 | 998.0425 | 1397.8446 | 1963.0165 |  | 18.8317 | 23.9388 | 30.6159 | 39.3732 | 50.8924 | 66.085 | 86.1718 | 112.7889 | 148.1316 | 195.148 | 257.8003 | 341.4172 | 453.1708 | 602.7189 | 803.0749 | 1071.7815 | 1432.498 | 1917.1465 | 2568.8127 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 4.6188 | 9.7259 | 16.4029 | 25.1602 | 36.6794 | 51.8721 | 71.9589 | 98.576 | 133.9187 | 180.9351 | 243.5873 | 327.2043 | 438.9578 | 588.506 | 788.862 | 1057.5686 | 1418.2851 | 1900.1345 | 2546.2623 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.37711 | 0.47938 | 0.61309 | 0.78845 | 1.0191 | 1.3234 | 1.7256 | 2.2586 | 2.9664 | 3.9079 | 5.1625 | 6.8369 | 9.0748 | 12.0695 | 16.0817 | 21.4625 | 28.6859 | 38.3911 | 51.4408 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.092491 | 0.19476 | 0.32847 | 0.50384 | 0.73451 | 1.0387 | 1.441 | 1.974 | 2.6817 | 3.6232 | 4.8779 | 6.5523 | 8.7902 | 11.7849 | 15.797 | 21.1779 | 28.4013 | 38.0504 | 50.9892 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 4.7113 | 9.9206 | 16.7314 | 25.6641 | 37.4139 | 52.9108 | 73.3999 | 100.55 | 136.6004 | 184.5584 | 248.4652 | 333.7566 | 447.748 | 600.2909 | 804.659 | 1078.7465 | 1446.6864 | 1938.1849 | 2597.2515 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 19.4676 | 24.7471 | 31.6497 | 40.7027 | 52.6108 | 68.3165 | 89.0816 | 116.5974 | 153.1336 | 201.7376 | 266.5054 | 352.9458 | 468.4729 | 623.0709 | 830.1923 | 1107.9722 | 1480.869 | 1981.8826 | 2655.5536 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 4.7747 | 10.0543 | 16.9568 | 26.0098 | 37.918 | 53.6236 | 74.3887 | 101.9046 | 138.4407 | 187.0447 | 251.8125 | 338.253 | 453.7801 | 608.378 | 815.4994 | 1093.2794 | 1466.1762 | 1964.2961 | 2632.2417 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.7397 | 3.4827 | 4.4541 | 5.7281 | 7.4039 | 9.6142 | 12.5365 | 16.4088 | 21.5505 | 28.3906 | 37.5054 | 49.6702 | 65.9283 | 87.6849 | 116.8332 | 155.9253 | 208.4031 | 278.9109 | 373.7168 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.67195 | 1.4149 | 2.3863 | 3.6604 | 5.3362 | 7.5465 | 10.4687 | 14.3411 | 19.4828 | 26.3229 | 35.4377 | 47.6024 | 63.8606 | 85.6172 | 114.7655 | 153.8575 | 206.3354 | 276.436 | 370.4362 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 7.4575 | 9.4799 | 12.1241 | 15.592 | 20.1537 | 26.1701 | 34.1245 | 44.6651 | 58.661 | 77.2798 | 102.0904 | 135.2032 | 179.4583 | 238.6802 | 318.0224 | 424.4318 | 567.2777 | 759.2013 | 1017.265 | 1025.6727 | 1025.6727 | 1025.6727 | 1025.6727 | 1025.6727 | 1025.6727 | 1025.6727 | 1025.6727 | 1025.6727 | 1025.6727 | 1025.6727 |  | 5.6284 | 5.6284 | 5.6284 | 5.6284 | 5.6284 | 5.6284 | 5.6284 | 5.6284 | 5.6284 | 5.6284 | 5.6284 | 5.6284 | 5.6284 | 5.6284 | 5.6284 | 5.6284 | 5.6284 | 6.7369 | 8.9301 | 11.9408 | 16.0921 | 21.8396 | 29.8266 | 40.9624 | 56.5349 | 78.3702 | 109.0602 | 152.2883 | 213.2929 | 299.5307 |  | 1.8291 | 3.8515 | 6.4957 | 9.9636 | 14.5253 | 20.5417 | 28.4961 | 39.0367 | 53.0326 | 71.6514 | 96.462 | 129.5748 | 173.8299 | 233.0518 | 312.394 | 418.8034 | 561.6493 | 752.4644 | 1008.3349 | 1013.7319 | 1009.5806 | 1003.833 | 995.8461 | 984.7103 | 969.1378 | 947.3025 | 916.6125 | 873.3844 | 812.3798 | 726.142 |  | 11.987 | 25.2413 | 42.5702 | 65.2979 | 95.1934 | 134.6226 | 186.7534 | 255.8323 | 347.5565 | 469.5773 | 632.1774 | 849.1868 | 1139.2186 | 1527.3379 | 2047.3179 | 2744.6868 | 3680.8472 | 4931.3814 | 6608.2643 | 6643.6345 | 6616.4282 | 6578.7608 | 6526.4172 | 6453.4371 | 6351.3804 | 6208.28 | 6007.1485 | 5723.8474 | 5324.0452 | 4758.8734
| TRUE | 1884 | 22009714 | GCY | GCY013 | 22 | GCY13 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 4.0857 | 0.0054221 | 4.2659e-06 | 0.0054179 | 14.9121 | 0.29862 | 15.2107 | 15.4156 | 2.1694 | 2.9526 |  | 11.2347 | 0.070957 | 5.5827e-05 | 0.070902 | 195.148 | 3.9079 | 199.0559 | 201.7376 | 28.3906 | 38.6399 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 2.8142 |  | 35.7484 | 467.824 | 34.0724 | 433.7516 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0068474 | 0.0087043 | 0.011132 | 0.014316 | 0.018505 | 0.024029 | 0.031333 | 0.041011 | 0.053862 | 0.070957 | 0.093738 | 0.12414 | 0.16478 | 0.21915 | 0.292 | 0.38971 | 0.52087 | 0.69709 | 0.93404 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 5.3872e-06 | 6.8482e-06 | 8.7584e-06 | 1.1264e-05 | 1.4559e-05 | 1.8905e-05 | 2.4651e-05 | 3.2266e-05 | 4.2376e-05 | 5.5827e-05 | 7.375e-05 | 9.767e-05 | 0.00012964 | 0.00017242 | 0.00022974 | 0.00030661 | 0.0004098 | 0.00054844 | 0.00073487 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 45.1448 | 57.3879 | 73.3947 | 94.3884 | 122.0031 | 158.4241 | 206.5777 | 270.3863 | 355.1126 | 467.824 | 618.0188 | 818.4718 | 1086.376 | 1444.8844 | 1925.1933 | 2569.3574 | 3434.095 | 4595.9316 | 6158.1564 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 |  | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 40.7825 | 54.0596 | 72.285 | 97.4156 | 132.2092 | 180.5594 | 247.9716 | 342.242 | 474.4248 | 660.2113 | 921.8984 | 1291.1982 | 1813.2512 |  | 18.8317 | 23.9388 | 30.6159 | 39.3732 | 50.8924 | 66.085 | 86.1718 | 112.7889 | 148.1316 | 195.148 | 257.8003 | 341.4172 | 453.1708 | 602.7189 | 803.0749 | 1071.7815 | 1432.498 | 1917.1465 | 2568.8127 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 4.6188 | 9.7259 | 16.4029 | 25.1602 | 36.6794 | 51.8721 | 71.9589 | 98.576 | 133.9187 | 180.9351 | 243.5873 | 327.2043 | 438.9578 | 588.506 | 788.862 | 1057.5686 | 1418.2851 | 1900.1345 | 2546.2623 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.37711 | 0.47938 | 0.61309 | 0.78845 | 1.0191 | 1.3234 | 1.7256 | 2.2586 | 2.9664 | 3.9079 | 5.1625 | 6.8369 | 9.0748 | 12.0695 | 16.0817 | 21.4625 | 28.6859 | 38.3911 | 51.4408 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.092491 | 0.19476 | 0.32847 | 0.50384 | 0.73451 | 1.0387 | 1.441 | 1.974 | 2.6817 | 3.6232 | 4.8779 | 6.5523 | 8.7902 | 11.7849 | 15.797 | 21.1779 | 28.4013 | 38.0504 | 50.9892 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 4.7113 | 9.9206 | 16.7314 | 25.6641 | 37.4139 | 52.9108 | 73.3999 | 100.55 | 136.6004 | 184.5584 | 248.4652 | 333.7566 | 447.748 | 600.2909 | 804.659 | 1078.7465 | 1446.6864 | 1938.1849 | 2597.2515 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 19.4676 | 24.7471 | 31.6497 | 40.7027 | 52.6108 | 68.3165 | 89.0816 | 116.5974 | 153.1336 | 201.7376 | 266.5054 | 352.9458 | 468.4729 | 623.0709 | 830.1923 | 1107.9722 | 1480.869 | 1981.8826 | 2655.5536 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 4.7747 | 10.0543 | 16.9568 | 26.0098 | 37.918 | 53.6236 | 74.3887 | 101.9046 | 138.4407 | 187.0447 | 251.8125 | 338.253 | 453.7801 | 608.378 | 815.4994 | 1093.2794 | 1466.1762 | 1964.2961 | 2632.2417 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.7397 | 3.4827 | 4.4541 | 5.7281 | 7.4039 | 9.6142 | 12.5365 | 16.4088 | 21.5505 | 28.3906 | 37.5054 | 49.6702 | 65.9283 | 87.6849 | 116.8332 | 155.9253 | 208.4031 | 278.9109 | 373.7168 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.67195 | 1.4149 | 2.3863 | 3.6604 | 5.3362 | 7.5465 | 10.4687 | 14.3411 | 19.4828 | 26.3229 | 35.4377 | 47.6024 | 63.8606 | 85.6172 | 114.7655 | 153.8575 | 206.3354 | 276.436 | 370.4362 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 3.7287 | 4.74 | 6.062 | 7.796 | 10.0768 | 13.085 | 17.0623 | 22.3325 | 29.3305 | 38.6399 | 51.0452 | 67.6016 | 89.7291 | 119.3401 | 159.0112 | 212.2159 | 283.6388 | 379.6006 | 508.6325 | 512.8363 | 512.8363 | 512.8363 | 512.8363 | 512.8363 | 512.8363 | 512.8363 | 512.8363 | 512.8363 | 512.8363 | 512.8363 |  | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 3.3684 | 4.465 | 5.9704 | 8.046 | 10.9198 | 14.9133 | 20.4812 | 28.2675 | 39.1851 | 54.5301 | 76.1441 | 106.6464 | 149.7654 |  | 0.91453 | 1.9257 | 3.2478 | 4.9818 | 7.2626 | 10.2708 | 14.2481 | 19.5183 | 26.5163 | 35.8257 | 48.231 | 64.7874 | 86.9149 | 116.5259 | 156.197 | 209.4017 | 280.8246 | 376.2322 | 504.1674 | 506.866 | 504.7903 | 501.9165 | 497.923 | 492.3551 | 484.5689 | 473.6513 | 458.3062 | 436.6922 | 406.1899 | 363.071 |  | 11.0725 | 23.3156 | 39.3223 | 60.3161 | 87.9308 | 124.3518 | 172.5054 | 236.3139 | 321.0402 | 433.7516 | 583.9464 | 784.3994 | 1052.3036 | 1410.812 | 1891.1209 | 2535.2851 | 3400.0226 | 4555.1492 | 6104.0968 | 6136.7685 | 6111.6379 | 6076.8443 | 6028.4942 | 5961.082 | 5866.8115 | 5734.6287 | 5548.8422 | 5287.1552 | 4917.8553 | 4395.8024
| TRUE | 1885 | 22009715 | GCY | GCY014 | 22 | GCY14 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 4.0857 | 0.0054221 | 4.2659e-06 | 0.0054179 | 14.9121 | 0.29862 | 15.2107 | 15.4156 | 2.1694 | 2.9526 |  | 11.2347 | 0.070957 | 5.5827e-05 | 0.070902 | 195.148 | 3.9079 | 199.0559 | 201.7376 | 28.3906 | 38.6399 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 2.8142 |  | 35.7484 | 467.824 | 34.0724 | 433.7516 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0068474 | 0.0087043 | 0.011132 | 0.014316 | 0.018505 | 0.024029 | 0.031333 | 0.041011 | 0.053862 | 0.070957 | 0.093738 | 0.12414 | 0.16478 | 0.21915 | 0.292 | 0.38971 | 0.52087 | 0.69709 | 0.93404 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 5.3872e-06 | 6.8482e-06 | 8.7584e-06 | 1.1264e-05 | 1.4559e-05 | 1.8905e-05 | 2.4651e-05 | 3.2266e-05 | 4.2376e-05 | 5.5827e-05 | 7.375e-05 | 9.767e-05 | 0.00012964 | 0.00017242 | 0.00022974 | 0.00030661 | 0.0004098 | 0.00054844 | 0.00073487 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 45.1448 | 57.3879 | 73.3947 | 94.3884 | 122.0031 | 158.4241 | 206.5777 | 270.3863 | 355.1126 | 467.824 | 618.0188 | 818.4718 | 1086.376 | 1444.8844 | 1925.1933 | 2569.3574 | 3434.095 | 4595.9316 | 6158.1564 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 | 6209.0535 |  | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 34.0724 | 40.7825 | 54.0596 | 72.285 | 97.4156 | 132.2092 | 180.5594 | 247.9716 | 342.242 | 474.4248 | 660.2113 | 921.8984 | 1291.1982 | 1813.2512 |  | 18.8317 | 23.9388 | 30.6159 | 39.3732 | 50.8924 | 66.085 | 86.1718 | 112.7889 | 148.1316 | 195.148 | 257.8003 | 341.4172 | 453.1708 | 602.7189 | 803.0749 | 1071.7815 | 1432.498 | 1917.1465 | 2568.8127 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 4.6188 | 9.7259 | 16.4029 | 25.1602 | 36.6794 | 51.8721 | 71.9589 | 98.576 | 133.9187 | 180.9351 | 243.5873 | 327.2043 | 438.9578 | 588.506 | 788.862 | 1057.5686 | 1418.2851 | 1900.1345 | 2546.2623 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.37711 | 0.47938 | 0.61309 | 0.78845 | 1.0191 | 1.3234 | 1.7256 | 2.2586 | 2.9664 | 3.9079 | 5.1625 | 6.8369 | 9.0748 | 12.0695 | 16.0817 | 21.4625 | 28.6859 | 38.3911 | 51.4408 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.092491 | 0.19476 | 0.32847 | 0.50384 | 0.73451 | 1.0387 | 1.441 | 1.974 | 2.6817 | 3.6232 | 4.8779 | 6.5523 | 8.7902 | 11.7849 | 15.797 | 21.1779 | 28.4013 | 38.0504 | 50.9892 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 4.7113 | 9.9206 | 16.7314 | 25.6641 | 37.4139 | 52.9108 | 73.3999 | 100.55 | 136.6004 | 184.5584 | 248.4652 | 333.7566 | 447.748 | 600.2909 | 804.659 | 1078.7465 | 1446.6864 | 1938.1849 | 2597.2515 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 19.4676 | 24.7471 | 31.6497 | 40.7027 | 52.6108 | 68.3165 | 89.0816 | 116.5974 | 153.1336 | 201.7376 | 266.5054 | 352.9458 | 468.4729 | 623.0709 | 830.1923 | 1107.9722 | 1480.869 | 1981.8826 | 2655.5536 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 4.7747 | 10.0543 | 16.9568 | 26.0098 | 37.918 | 53.6236 | 74.3887 | 101.9046 | 138.4407 | 187.0447 | 251.8125 | 338.253 | 453.7801 | 608.378 | 815.4994 | 1093.2794 | 1466.1762 | 1964.2961 | 2632.2417 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.7397 | 3.4827 | 4.4541 | 5.7281 | 7.4039 | 9.6142 | 12.5365 | 16.4088 | 21.5505 | 28.3906 | 37.5054 | 49.6702 | 65.9283 | 87.6849 | 116.8332 | 155.9253 | 208.4031 | 278.9109 | 373.7168 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.67195 | 1.4149 | 2.3863 | 3.6604 | 5.3362 | 7.5465 | 10.4687 | 14.3411 | 19.4828 | 26.3229 | 35.4377 | 47.6024 | 63.8606 | 85.6172 | 114.7655 | 153.8575 | 206.3354 | 276.436 | 370.4362 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 3.7287 | 4.74 | 6.062 | 7.796 | 10.0768 | 13.085 | 17.0623 | 22.3325 | 29.3305 | 38.6399 | 51.0452 | 67.6016 | 89.7291 | 119.3401 | 159.0112 | 212.2159 | 283.6388 | 379.6006 | 508.6325 | 512.8363 | 512.8363 | 512.8363 | 512.8363 | 512.8363 | 512.8363 | 512.8363 | 512.8363 | 512.8363 | 512.8363 | 512.8363 |  | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 2.8142 | 3.3684 | 4.465 | 5.9704 | 8.046 | 10.9198 | 14.9133 | 20.4812 | 28.2675 | 39.1851 | 54.5301 | 76.1441 | 106.6464 | 149.7654 |  | 0.91453 | 1.9257 | 3.2478 | 4.9818 | 7.2626 | 10.2708 | 14.2481 | 19.5183 | 26.5163 | 35.8257 | 48.231 | 64.7874 | 86.9149 | 116.5259 | 156.197 | 209.4017 | 280.8246 | 376.2322 | 504.1674 | 506.866 | 504.7903 | 501.9165 | 497.923 | 492.3551 | 484.5689 | 473.6513 | 458.3062 | 436.6922 | 406.1899 | 363.071 |  | 11.0725 | 23.3156 | 39.3223 | 60.3161 | 87.9308 | 124.3518 | 172.5054 | 236.3139 | 321.0402 | 433.7516 | 583.9464 | 784.3994 | 1052.3036 | 1410.812 | 1891.1209 | 2535.2851 | 3400.0226 | 4555.1492 | 6104.0968 | 6136.7685 | 6111.6379 | 6076.8443 | 6028.4942 | 5961.082 | 5866.8115 | 5734.6287 | 5548.8422 | 5287.1552 | 4917.8553 | 4395.8024
| TRUE | 1886 | 22009708 | GCY | GCY021 | 22 | GCY21 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 4.0857 | 0.0054221 | 4.2659e-06 | 0.0054179 | 14.9121 | 0.29862 | 15.2107 | 15.4156 | 2.1694 | 4.1063 |  | 11.2347 | 0.070957 | 5.5827e-05 | 0.070902 | 195.148 | 3.9079 | 199.0559 | 201.7376 | 28.3906 | 53.7374 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 3.9138 |  | 36.902 | 482.9215 | 35.1719 | 447.7496 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0068474 | 0.0087043 | 0.011132 | 0.014316 | 0.018505 | 0.024029 | 0.031333 | 0.041011 | 0.053862 | 0.070957 | 0.093738 | 0.12414 | 0.16478 | 0.21915 | 0.292 | 0.38971 | 0.52087 | 0.69709 | 0.93404 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 5.3872e-06 | 6.8482e-06 | 8.7584e-06 | 1.1264e-05 | 1.4559e-05 | 1.8905e-05 | 2.4651e-05 | 3.2266e-05 | 4.2376e-05 | 5.5827e-05 | 7.375e-05 | 9.767e-05 | 0.00012964 | 0.00017242 | 0.00022974 | 0.00030661 | 0.0004098 | 0.00054844 | 0.00073487 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 46.6017 | 59.2399 | 75.7633 | 97.4345 | 125.9404 | 163.5368 | 213.2444 | 279.1122 | 366.5727 | 482.9215 | 637.9634 | 844.8854 | 1121.4353 | 1491.5135 | 1987.3228 | 2652.2753 | 3544.9196 | 4744.2508 | 6356.8915 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 |  | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 42.0986 | 55.8042 | 74.6178 | 100.5594 | 136.4759 | 186.3864 | 255.9741 | 353.2868 | 489.7354 | 681.5176 | 951.6497 | 1332.8676 | 1871.7681 |  | 18.8317 | 23.9388 | 30.6159 | 39.3732 | 50.8924 | 66.085 | 86.1718 | 112.7889 | 148.1316 | 195.148 | 257.8003 | 341.4172 | 453.1708 | 602.7189 | 803.0749 | 1071.7815 | 1432.498 | 1917.1465 | 2568.8127 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 4.6188 | 9.7259 | 16.4029 | 25.1602 | 36.6794 | 51.8721 | 71.9589 | 98.576 | 133.9187 | 180.9351 | 243.5873 | 327.2043 | 438.9578 | 588.506 | 788.862 | 1057.5686 | 1418.2851 | 1900.1345 | 2546.2623 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.37711 | 0.47938 | 0.61309 | 0.78845 | 1.0191 | 1.3234 | 1.7256 | 2.2586 | 2.9664 | 3.9079 | 5.1625 | 6.8369 | 9.0748 | 12.0695 | 16.0817 | 21.4625 | 28.6859 | 38.3911 | 51.4408 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.092491 | 0.19476 | 0.32847 | 0.50384 | 0.73451 | 1.0387 | 1.441 | 1.974 | 2.6817 | 3.6232 | 4.8779 | 6.5523 | 8.7902 | 11.7849 | 15.797 | 21.1779 | 28.4013 | 38.0504 | 50.9892 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 4.7113 | 9.9206 | 16.7314 | 25.6641 | 37.4139 | 52.9108 | 73.3999 | 100.55 | 136.6004 | 184.5584 | 248.4652 | 333.7566 | 447.748 | 600.2909 | 804.659 | 1078.7465 | 1446.6864 | 1938.1849 | 2597.2515 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 19.4676 | 24.7471 | 31.6497 | 40.7027 | 52.6108 | 68.3165 | 89.0816 | 116.5974 | 153.1336 | 201.7376 | 266.5054 | 352.9458 | 468.4729 | 623.0709 | 830.1923 | 1107.9722 | 1480.869 | 1981.8826 | 2655.5536 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 4.7747 | 10.0543 | 16.9568 | 26.0098 | 37.918 | 53.6236 | 74.3887 | 101.9046 | 138.4407 | 187.0447 | 251.8125 | 338.253 | 453.7801 | 608.378 | 815.4994 | 1093.2794 | 1466.1762 | 1964.2961 | 2632.2417 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.7397 | 3.4827 | 4.4541 | 5.7281 | 7.4039 | 9.6142 | 12.5365 | 16.4088 | 21.5505 | 28.3906 | 37.5054 | 49.6702 | 65.9283 | 87.6849 | 116.8332 | 155.9253 | 208.4031 | 278.9109 | 373.7168 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.67195 | 1.4149 | 2.3863 | 3.6604 | 5.3362 | 7.5465 | 10.4687 | 14.3411 | 19.4828 | 26.3229 | 35.4377 | 47.6024 | 63.8606 | 85.6172 | 114.7655 | 153.8575 | 206.3354 | 276.436 | 370.4362 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 5.1856 | 6.592 | 8.4306 | 10.8421 | 14.0141 | 18.1977 | 23.7289 | 31.0584 | 40.7906 | 53.7374 | 70.9898 | 94.0152 | 124.7885 | 165.9692 | 221.1407 | 295.1338 | 394.4634 | 527.9198 | 707.3676 | 713.2139 | 713.2139 | 713.2139 | 713.2139 | 713.2139 | 713.2139 | 713.2139 | 713.2139 | 713.2139 | 713.2139 | 713.2139 |  | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 4.6846 | 6.2097 | 8.3031 | 11.1898 | 15.1864 | 20.7403 | 28.4837 | 39.3122 | 54.4956 | 75.8363 | 105.8955 | 148.3158 | 208.2823 |  | 1.2719 | 2.6782 | 4.5168 | 6.9283 | 10.1003 | 14.2839 | 19.8151 | 27.1446 | 36.8769 | 49.8236 | 67.076 | 90.1014 | 120.8747 | 162.0554 | 217.227 | 291.22 | 390.5496 | 523.2353 | 701.1579 | 704.9108 | 702.0241 | 698.0275 | 692.4737 | 684.7302 | 673.9017 | 658.7183 | 637.3776 | 607.3184 | 564.8982 | 504.9316 |  | 11.4298 | 24.068 | 40.5914 | 62.2626 | 90.7684 | 128.3648 | 178.0724 | 243.9402 | 331.4008 | 447.7496 | 602.7914 | 809.7134 | 1086.2634 | 1456.3415 | 1952.1509 | 2617.1034 | 3509.7476 | 4702.1522 | 6301.0873 | 6334.8134 | 6308.8718 | 6272.9553 | 6223.0448 | 6153.4571 | 6056.1443 | 5919.6957 | 5727.9136 | 5457.7814 | 5076.5636 | 4537.663
| TRUE | 1887 | 22009709 | GCY | GCY022 | 22 | GCY22 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 4.0857 | 0.0054221 | 4.2659e-06 | 0.0054179 | 14.9121 | 0.29862 | 15.2107 | 15.4156 | 2.1694 | 4.1063 |  | 11.2347 | 0.070957 | 5.5827e-05 | 0.070902 | 195.148 | 3.9079 | 199.0559 | 201.7376 | 28.3906 | 53.7374 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 3.9138 |  | 36.902 | 482.9215 | 35.1719 | 447.7496 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0068474 | 0.0087043 | 0.011132 | 0.014316 | 0.018505 | 0.024029 | 0.031333 | 0.041011 | 0.053862 | 0.070957 | 0.093738 | 0.12414 | 0.16478 | 0.21915 | 0.292 | 0.38971 | 0.52087 | 0.69709 | 0.93404 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 5.3872e-06 | 6.8482e-06 | 8.7584e-06 | 1.1264e-05 | 1.4559e-05 | 1.8905e-05 | 2.4651e-05 | 3.2266e-05 | 4.2376e-05 | 5.5827e-05 | 7.375e-05 | 9.767e-05 | 0.00012964 | 0.00017242 | 0.00022974 | 0.00030661 | 0.0004098 | 0.00054844 | 0.00073487 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 46.6017 | 59.2399 | 75.7633 | 97.4345 | 125.9404 | 163.5368 | 213.2444 | 279.1122 | 366.5727 | 482.9215 | 637.9634 | 844.8854 | 1121.4353 | 1491.5135 | 1987.3228 | 2652.2753 | 3544.9196 | 4744.2508 | 6356.8915 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 | 6409.4311 |  | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 35.1719 | 42.0986 | 55.8042 | 74.6178 | 100.5594 | 136.4759 | 186.3864 | 255.9741 | 353.2868 | 489.7354 | 681.5176 | 951.6497 | 1332.8676 | 1871.7681 |  | 18.8317 | 23.9388 | 30.6159 | 39.3732 | 50.8924 | 66.085 | 86.1718 | 112.7889 | 148.1316 | 195.148 | 257.8003 | 341.4172 | 453.1708 | 602.7189 | 803.0749 | 1071.7815 | 1432.498 | 1917.1465 | 2568.8127 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 4.6188 | 9.7259 | 16.4029 | 25.1602 | 36.6794 | 51.8721 | 71.9589 | 98.576 | 133.9187 | 180.9351 | 243.5873 | 327.2043 | 438.9578 | 588.506 | 788.862 | 1057.5686 | 1418.2851 | 1900.1345 | 2546.2623 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.37711 | 0.47938 | 0.61309 | 0.78845 | 1.0191 | 1.3234 | 1.7256 | 2.2586 | 2.9664 | 3.9079 | 5.1625 | 6.8369 | 9.0748 | 12.0695 | 16.0817 | 21.4625 | 28.6859 | 38.3911 | 51.4408 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.092491 | 0.19476 | 0.32847 | 0.50384 | 0.73451 | 1.0387 | 1.441 | 1.974 | 2.6817 | 3.6232 | 4.8779 | 6.5523 | 8.7902 | 11.7849 | 15.797 | 21.1779 | 28.4013 | 38.0504 | 50.9892 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 4.7113 | 9.9206 | 16.7314 | 25.6641 | 37.4139 | 52.9108 | 73.3999 | 100.55 | 136.6004 | 184.5584 | 248.4652 | 333.7566 | 447.748 | 600.2909 | 804.659 | 1078.7465 | 1446.6864 | 1938.1849 | 2597.2515 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 19.4676 | 24.7471 | 31.6497 | 40.7027 | 52.6108 | 68.3165 | 89.0816 | 116.5974 | 153.1336 | 201.7376 | 266.5054 | 352.9458 | 468.4729 | 623.0709 | 830.1923 | 1107.9722 | 1480.869 | 1981.8826 | 2655.5536 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 4.7747 | 10.0543 | 16.9568 | 26.0098 | 37.918 | 53.6236 | 74.3887 | 101.9046 | 138.4407 | 187.0447 | 251.8125 | 338.253 | 453.7801 | 608.378 | 815.4994 | 1093.2794 | 1466.1762 | 1964.2961 | 2632.2417 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.7397 | 3.4827 | 4.4541 | 5.7281 | 7.4039 | 9.6142 | 12.5365 | 16.4088 | 21.5505 | 28.3906 | 37.5054 | 49.6702 | 65.9283 | 87.6849 | 116.8332 | 155.9253 | 208.4031 | 278.9109 | 373.7168 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.67195 | 1.4149 | 2.3863 | 3.6604 | 5.3362 | 7.5465 | 10.4687 | 14.3411 | 19.4828 | 26.3229 | 35.4377 | 47.6024 | 63.8606 | 85.6172 | 114.7655 | 153.8575 | 206.3354 | 276.436 | 370.4362 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 5.1856 | 6.592 | 8.4306 | 10.8421 | 14.0141 | 18.1977 | 23.7289 | 31.0584 | 40.7906 | 53.7374 | 70.9898 | 94.0152 | 124.7885 | 165.9692 | 221.1407 | 295.1338 | 394.4634 | 527.9198 | 707.3676 | 713.2139 | 713.2139 | 713.2139 | 713.2139 | 713.2139 | 713.2139 | 713.2139 | 713.2139 | 713.2139 | 713.2139 | 713.2139 |  | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 3.9138 | 4.6846 | 6.2097 | 8.3031 | 11.1898 | 15.1864 | 20.7403 | 28.4837 | 39.3122 | 54.4956 | 75.8363 | 105.8955 | 148.3158 | 208.2823 |  | 1.2719 | 2.6782 | 4.5168 | 6.9283 | 10.1003 | 14.2839 | 19.8151 | 27.1446 | 36.8769 | 49.8236 | 67.076 | 90.1014 | 120.8747 | 162.0554 | 217.227 | 291.22 | 390.5496 | 523.2353 | 701.1579 | 704.9108 | 702.0241 | 698.0275 | 692.4737 | 684.7302 | 673.9017 | 658.7183 | 637.3776 | 607.3184 | 564.8982 | 504.9316 |  | 11.4298 | 24.068 | 40.5914 | 62.2626 | 90.7684 | 128.3648 | 178.0724 | 243.9402 | 331.4008 | 447.7496 | 602.7914 | 809.7134 | 1086.2634 | 1456.3415 | 1952.1509 | 2617.1034 | 3509.7476 | 4702.1522 | 6301.0873 | 6334.8134 | 6308.8718 | 6272.9553 | 6223.0448 | 6153.4571 | 6056.1443 | 5919.6957 | 5727.9136 | 5457.7814 | 5076.5636 | 4537.663
| TRUE | 1888 | 22009710 | GCY | GCY023 | 22 | GCY23 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 4.0857 | 0.0054221 | 4.2659e-06 | 0.0054179 | 14.9121 | 0.29862 | 15.2107 | 15.4156 | 2.1694 | 8.2126 |  | 11.2347 | 0.070957 | 5.5827e-05 | 0.070902 | 195.148 | 3.9079 | 199.0559 | 201.7376 | 28.3906 | 107.4749 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 7.8276 |  | 41.0083 | 536.659 | 39.0857 | 497.5732 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0068474 | 0.0087043 | 0.011132 | 0.014316 | 0.018505 | 0.024029 | 0.031333 | 0.041011 | 0.053862 | 0.070957 | 0.093738 | 0.12414 | 0.16478 | 0.21915 | 0.292 | 0.38971 | 0.52087 | 0.69709 | 0.93404 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 5.3872e-06 | 6.8482e-06 | 8.7584e-06 | 1.1264e-05 | 1.4559e-05 | 1.8905e-05 | 2.4651e-05 | 3.2266e-05 | 4.2376e-05 | 5.5827e-05 | 7.375e-05 | 9.767e-05 | 0.00012964 | 0.00017242 | 0.00022974 | 0.00030661 | 0.0004098 | 0.00054844 | 0.00073487 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 51.7874 | 65.8319 | 84.1939 | 108.2766 | 139.9545 | 181.7344 | 236.9733 | 310.1706 | 407.3634 | 536.659 | 708.9532 | 938.9006 | 1246.2238 | 1657.4827 | 2208.4636 | 2947.4091 | 3939.383 | 5272.1707 | 7064.2591 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 |  | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 46.7832 | 62.0139 | 82.9209 | 111.7492 | 151.6623 | 207.1266 | 284.4578 | 392.5991 | 544.231 | 757.3539 | 1057.5452 | 1481.1833 | 2080.0504 |  | 18.8317 | 23.9388 | 30.6159 | 39.3732 | 50.8924 | 66.085 | 86.1718 | 112.7889 | 148.1316 | 195.148 | 257.8003 | 341.4172 | 453.1708 | 602.7189 | 803.0749 | 1071.7815 | 1432.498 | 1917.1465 | 2568.8127 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 4.6188 | 9.7259 | 16.4029 | 25.1602 | 36.6794 | 51.8721 | 71.9589 | 98.576 | 133.9187 | 180.9351 | 243.5873 | 327.2043 | 438.9578 | 588.506 | 788.862 | 1057.5686 | 1418.2851 | 1900.1345 | 2546.2623 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.37711 | 0.47938 | 0.61309 | 0.78845 | 1.0191 | 1.3234 | 1.7256 | 2.2586 | 2.9664 | 3.9079 | 5.1625 | 6.8369 | 9.0748 | 12.0695 | 16.0817 | 21.4625 | 28.6859 | 38.3911 | 51.4408 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.092491 | 0.19476 | 0.32847 | 0.50384 | 0.73451 | 1.0387 | 1.441 | 1.974 | 2.6817 | 3.6232 | 4.8779 | 6.5523 | 8.7902 | 11.7849 | 15.797 | 21.1779 | 28.4013 | 38.0504 | 50.9892 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 4.7113 | 9.9206 | 16.7314 | 25.6641 | 37.4139 | 52.9108 | 73.3999 | 100.55 | 136.6004 | 184.5584 | 248.4652 | 333.7566 | 447.748 | 600.2909 | 804.659 | 1078.7465 | 1446.6864 | 1938.1849 | 2597.2515 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 19.4676 | 24.7471 | 31.6497 | 40.7027 | 52.6108 | 68.3165 | 89.0816 | 116.5974 | 153.1336 | 201.7376 | 266.5054 | 352.9458 | 468.4729 | 623.0709 | 830.1923 | 1107.9722 | 1480.869 | 1981.8826 | 2655.5536 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 4.7747 | 10.0543 | 16.9568 | 26.0098 | 37.918 | 53.6236 | 74.3887 | 101.9046 | 138.4407 | 187.0447 | 251.8125 | 338.253 | 453.7801 | 608.378 | 815.4994 | 1093.2794 | 1466.1762 | 1964.2961 | 2632.2417 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.7397 | 3.4827 | 4.4541 | 5.7281 | 7.4039 | 9.6142 | 12.5365 | 16.4088 | 21.5505 | 28.3906 | 37.5054 | 49.6702 | 65.9283 | 87.6849 | 116.8332 | 155.9253 | 208.4031 | 278.9109 | 373.7168 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.67195 | 1.4149 | 2.3863 | 3.6604 | 5.3362 | 7.5465 | 10.4687 | 14.3411 | 19.4828 | 26.3229 | 35.4377 | 47.6024 | 63.8606 | 85.6172 | 114.7655 | 153.8575 | 206.3354 | 276.436 | 370.4362 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 10.3713 | 13.1839 | 16.8612 | 21.6842 | 28.0282 | 36.3953 | 47.4578 | 62.1168 | 81.5813 | 107.4749 | 141.9796 | 188.0304 | 249.577 | 331.9384 | 442.2815 | 590.2676 | 788.9268 | 1055.8397 | 1414.7351 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 |  | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 9.3691 | 12.4193 | 16.6063 | 22.3796 | 30.3729 | 41.4805 | 56.9674 | 78.6245 | 108.9913 | 151.6727 | 211.791 | 296.6315 | 416.5646 |  | 2.5437 | 5.3564 | 9.0337 | 13.8566 | 20.2006 | 28.5678 | 39.6303 | 54.2892 | 73.7537 | 99.6473 | 134.1521 | 180.2029 | 241.7494 | 324.1108 | 434.4539 | 582.44 | 781.0992 | 1046.4706 | 1402.3158 | 1409.8216 | 1404.0482 | 1396.055 | 1384.9473 | 1369.4605 | 1347.8034 | 1317.4366 | 1274.7552 | 1214.6369 | 1129.7963 | 1009.8633 |  | 12.7017 | 26.7462 | 45.1082 | 69.1909 | 100.8688 | 142.6487 | 197.8876 | 271.0848 | 368.2776 | 497.5732 | 669.8675 | 899.8149 | 1207.1381 | 1618.3969 | 2169.3778 | 2908.3234 | 3900.2972 | 5225.3875 | 7002.2452 | 7039.7242 | 7010.8959 | 6970.9828 | 6915.5184 | 6838.1873 | 6730.046 | 6578.414 | 6365.2912 | 6065.0999 | 5641.4617 | 5042.5947
| TRUE | 1889 | 22009711 | GCY | GCY024 | 22 | GCY24 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 4.0857 | 0.0054221 | 4.2659e-06 | 0.0054179 | 14.9121 | 0.29862 | 15.2107 | 15.4156 | 2.1694 | 8.2126 |  | 11.2347 | 0.070957 | 5.5827e-05 | 0.070902 | 195.148 | 3.9079 | 199.0559 | 201.7376 | 28.3906 | 107.4749 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 7.8276 |  | 41.0083 | 536.659 | 39.0857 | 497.5732 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0068474 | 0.0087043 | 0.011132 | 0.014316 | 0.018505 | 0.024029 | 0.031333 | 0.041011 | 0.053862 | 0.070957 | 0.093738 | 0.12414 | 0.16478 | 0.21915 | 0.292 | 0.38971 | 0.52087 | 0.69709 | 0.93404 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 5.3872e-06 | 6.8482e-06 | 8.7584e-06 | 1.1264e-05 | 1.4559e-05 | 1.8905e-05 | 2.4651e-05 | 3.2266e-05 | 4.2376e-05 | 5.5827e-05 | 7.375e-05 | 9.767e-05 | 0.00012964 | 0.00017242 | 0.00022974 | 0.00030661 | 0.0004098 | 0.00054844 | 0.00073487 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 51.7874 | 65.8319 | 84.1939 | 108.2766 | 139.9545 | 181.7344 | 236.9733 | 310.1706 | 407.3634 | 536.659 | 708.9532 | 938.9006 | 1246.2238 | 1657.4827 | 2208.4636 | 2947.4091 | 3939.383 | 5272.1707 | 7064.2591 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 | 7122.6451 |  | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 39.0857 | 46.7832 | 62.0139 | 82.9209 | 111.7492 | 151.6623 | 207.1266 | 284.4578 | 392.5991 | 544.231 | 757.3539 | 1057.5452 | 1481.1833 | 2080.0504 |  | 18.8317 | 23.9388 | 30.6159 | 39.3732 | 50.8924 | 66.085 | 86.1718 | 112.7889 | 148.1316 | 195.148 | 257.8003 | 341.4172 | 453.1708 | 602.7189 | 803.0749 | 1071.7815 | 1432.498 | 1917.1465 | 2568.8127 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 4.6188 | 9.7259 | 16.4029 | 25.1602 | 36.6794 | 51.8721 | 71.9589 | 98.576 | 133.9187 | 180.9351 | 243.5873 | 327.2043 | 438.9578 | 588.506 | 788.862 | 1057.5686 | 1418.2851 | 1900.1345 | 2546.2623 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.37711 | 0.47938 | 0.61309 | 0.78845 | 1.0191 | 1.3234 | 1.7256 | 2.2586 | 2.9664 | 3.9079 | 5.1625 | 6.8369 | 9.0748 | 12.0695 | 16.0817 | 21.4625 | 28.6859 | 38.3911 | 51.4408 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.092491 | 0.19476 | 0.32847 | 0.50384 | 0.73451 | 1.0387 | 1.441 | 1.974 | 2.6817 | 3.6232 | 4.8779 | 6.5523 | 8.7902 | 11.7849 | 15.797 | 21.1779 | 28.4013 | 38.0504 | 50.9892 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 4.7113 | 9.9206 | 16.7314 | 25.6641 | 37.4139 | 52.9108 | 73.3999 | 100.55 | 136.6004 | 184.5584 | 248.4652 | 333.7566 | 447.748 | 600.2909 | 804.659 | 1078.7465 | 1446.6864 | 1938.1849 | 2597.2515 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 19.4676 | 24.7471 | 31.6497 | 40.7027 | 52.6108 | 68.3165 | 89.0816 | 116.5974 | 153.1336 | 201.7376 | 266.5054 | 352.9458 | 468.4729 | 623.0709 | 830.1923 | 1107.9722 | 1480.869 | 1981.8826 | 2655.5536 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 4.7747 | 10.0543 | 16.9568 | 26.0098 | 37.918 | 53.6236 | 74.3887 | 101.9046 | 138.4407 | 187.0447 | 251.8125 | 338.253 | 453.7801 | 608.378 | 815.4994 | 1093.2794 | 1466.1762 | 1964.2961 | 2632.2417 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.7397 | 3.4827 | 4.4541 | 5.7281 | 7.4039 | 9.6142 | 12.5365 | 16.4088 | 21.5505 | 28.3906 | 37.5054 | 49.6702 | 65.9283 | 87.6849 | 116.8332 | 155.9253 | 208.4031 | 278.9109 | 373.7168 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.67195 | 1.4149 | 2.3863 | 3.6604 | 5.3362 | 7.5465 | 10.4687 | 14.3411 | 19.4828 | 26.3229 | 35.4377 | 47.6024 | 63.8606 | 85.6172 | 114.7655 | 153.8575 | 206.3354 | 276.436 | 370.4362 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 10.3713 | 13.1839 | 16.8612 | 21.6842 | 28.0282 | 36.3953 | 47.4578 | 62.1168 | 81.5813 | 107.4749 | 141.9796 | 188.0304 | 249.577 | 331.9384 | 442.2815 | 590.2676 | 788.9268 | 1055.8397 | 1414.7351 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 | 1426.4279 |  | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 7.8276 | 9.3691 | 12.4193 | 16.6063 | 22.3796 | 30.3729 | 41.4805 | 56.9674 | 78.6245 | 108.9913 | 151.6727 | 211.791 | 296.6315 | 416.5646 |  | 2.5437 | 5.3564 | 9.0337 | 13.8566 | 20.2006 | 28.5678 | 39.6303 | 54.2892 | 73.7537 | 99.6473 | 134.1521 | 180.2029 | 241.7494 | 324.1108 | 434.4539 | 582.44 | 781.0992 | 1046.4706 | 1402.3158 | 1409.8216 | 1404.0482 | 1396.055 | 1384.9473 | 1369.4605 | 1347.8034 | 1317.4366 | 1274.7552 | 1214.6369 | 1129.7963 | 1009.8633 |  | 12.7017 | 26.7462 | 45.1082 | 69.1909 | 100.8688 | 142.6487 | 197.8876 | 271.0848 | 368.2776 | 497.5732 | 669.8675 | 899.8149 | 1207.1381 | 1618.3969 | 2169.3778 | 2908.3234 | 3900.2972 | 5225.3875 | 7002.2452 | 7039.7242 | 7010.8959 | 6970.9828 | 6915.5184 | 6838.1873 | 6730.046 | 6578.414 | 6365.2912 | 6065.0999 | 5641.4617 | 5042.5947
| TRUE | 1890 | 22015828 | GCY | Blank | 22 | TRANS NO.1 | GAS & T/C PROT | X | ASEA | GROUP_2598 | GROUP 2598 | GROUP 2000s | Electronic |  | 0.066046 | 2190 |  | 8.25 | 0.026286 | 0.0045837 | 0.021702 | 280.8119 | 2016.8282 | 2297.64 | 100.6375 | 10.5627 | 255.4581 |  | 13.0142 | 0.090569 | 0.015794 | 0.074776 | 967.5611 | 6949.1524 | 7916.7135 | 346.7551 | 36.3947 | 880.2025 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.026058 |  | 2664.2983 | 9180.0657 | 71.2357 | 9108.83 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0051721 | 0.0058403 | 0.0065995 | 0.0074623 | 0.0084434 | 0.0095593 | 0.010829 | 0.012274 | 0.01392 | 0.015794 | 0.017928 | 0.020361 | 0.023134 | 0.026296 | 0.029902 | 0.034015 | 0.038708 | 0.044064 | 0.050177 | 0.057157 | 0.065126 | 0.074228 | 0.084625 | 0.096504 | 0.11008 | 0.12559 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 3006.3 | 3394.699 | 3835.9714 | 4337.5128 | 4907.7702 | 5556.3939 | 6294.4095 | 7134.4166 | 8090.8153 | 9180.0657 | 10420.9852 | 11835.0887 | 13446.9782 | 15284.7892 | 17380.7018 | 19771.5258 | 22499.3712 | 25612.4159 | 29165.7857 | 33222.561 | 37854.9317 | 43145.519 | 49188.8901 | 56093.2936 | 63982.6478 | 72998.8185 | 81217.1715 | 81217.1715 | 81217.1715 | 81217.1715 |  | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 52.7928 | 69.9799 | 93.5726 | 126.1041 | 171.1443 | 233.7334 | 320.9982 | 443.0309 | 614.141 | 854.6408 | 1193.3936 | 1671.4508 | 2347.2461 |  | 316.8582 | 357.7947 | 404.3039 | 457.1654 | 517.2694 | 585.6331 | 663.4185 | 751.9536 | 852.7562 | 967.5611 | 1098.3516 | 1247.3954 | 1417.2854 | 1610.9871 | 1831.8922 | 2083.8804 | 2371.39 | 2699.4989 | 3074.0171 | 3501.5934 | 3989.8362 | 4547.4539 | 5184.4134 | 5912.1241 | 6743.6467 | 7693.9336 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 289.7263 | 330.6628 | 377.172 | 430.0335 | 490.1375 | 558.5012 | 636.2866 | 724.8217 | 825.6243 | 940.4292 | 1071.2197 | 1220.2634 | 1390.1535 | 1583.8552 | 1804.7603 | 2056.7485 | 2344.2581 | 2667.0237 | 3030.9693 | 3444.0326 | 3912.2639 | 4442.1753 | 5040.6335 | 5714.6637 | 6471.1185 | 7316.1479 | 8034.4041 | 7826.022 | 7531.9476 | 7116.2356 |  | 2275.7176 | 2569.729 | 2903.7646 | 3283.4228 | 3715.0979 | 4206.0949 | 4764.7601 | 5400.6311 | 6124.6085 | 6949.1524 | 7888.5072 | 8958.9593 | 10179.132 | 11570.3234 | 13156.8933 | 14966.7061 | 17031.6383 | 19388.1598 | 22077.9998 | 25148.9092 | 28655.5344 | 32660.4183 | 37235.1466 | 42461.6617 | 48433.7676 | 55258.8543 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 2275.5118 | 2569.5233 | 2903.5589 | 3283.2171 | 3714.8922 | 4205.8892 | 4764.5543 | 5400.4253 | 6124.4028 | 6948.9467 | 7888.3015 | 8958.7535 | 10178.9262 | 11570.1177 | 13156.6876 | 14966.5004 | 17031.4326 | 19387.9136 | 22077.6734 | 25148.4727 | 28654.9462 | 32659.62 | 37234.0564 | 42460.1645 | 48431.7012 | 55255.9897 | 61476.0203 | 61474.4402 | 61472.2104 | 61469.0582 |  | 2565.2381 | 2900.186 | 3280.7309 | 3713.2506 | 4205.0297 | 4764.3904 | 5400.8409 | 6125.2471 | 6950.0271 | 7889.3759 | 8959.5212 | 10179.017 | 11569.0797 | 13153.9729 | 14961.4479 | 17023.2489 | 19375.6907 | 22054.9372 | 25108.6427 | 28592.5053 | 32567.2101 | 37101.7953 | 42274.6899 | 48174.8282 | 54902.8197 | 62572.1376 | 69510.4244 | 69300.4622 | 69004.158 | 68585.2938 |  | 113.5558 | 128.2266 | 144.8947 | 163.8392 | 185.3793 | 209.8795 | 237.7563 | 269.4855 | 305.6112 | 346.7551 | 393.6278 | 447.0422 | 507.9275 | 577.3464 | 656.5145 | 746.8222 | 849.86 | 967.4478 | 1101.6679 | 1254.9029 | 1429.8796 | 1629.7189 | 1857.9928 | 2118.7902 | 2416.7917 | 2757.356 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 98.8834 | 113.5542 | 130.2222 | 149.1667 | 170.7069 | 195.2071 | 223.0838 | 254.8131 | 290.9388 | 332.0826 | 378.9554 | 432.3698 | 493.255 | 562.674 | 641.8421 | 732.1497 | 835.1876 | 949.8858 | 1078.3884 | 1223.7751 | 1387.9299 | 1572.7862 | 1780.2393 | 2012.0072 | 2269.4134 | 2553.0564 | 2783.4806 | 2670.7914 | 2511.7613 | 2286.9518 |  | 11.9186 | 13.4584 | 15.2079 | 17.1962 | 19.457 | 22.0285 | 24.9544 | 28.2847 | 32.0763 | 36.3947 | 41.3144 | 46.9207 | 53.3111 | 60.5971 | 68.9065 | 78.385 | 89.1996 | 101.5414 | 115.6289 | 131.7121 | 150.0773 | 171.0521 | 195.0112 | 222.384 | 253.6617 | 289.4066 | 321.9886 | 321.9886 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 9.8509 | 11.3907 | 13.1402 | 15.1285 | 17.3893 | 19.9608 | 22.8867 | 26.217 | 30.0087 | 34.327 | 39.2467 | 44.853 | 51.2434 | 58.5294 | 66.8388 | 76.3173 | 87.1319 | 99.0665 | 112.3482 | 127.3255 | 144.1656 | 163.0289 | 184.0539 | 207.3357 | 232.8925 | 260.6159 | 281.9234 | 266.0428 | 243.6317 | 211.9507 |  | 288.2499 | 325.4903 | 367.8004 | 415.8891 | 470.5665 | 532.7578 | 603.5202 | 684.0617 | 775.763 | 880.2025 | 999.1842 | 1134.7712 | 1289.3223 | 1465.5352 | 1666.4953 | 1895.7322 | 2157.2833 | 2455.768 | 2796.472 | 3185.4435 | 3629.6041 | 4136.8759 | 4716.326 | 5378.3336 | 6134.7801 | 6999.268 | 7787.2596 | 7787.2596 | 7787.2596 | 7787.2596 |  | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.03119 | 0.041344 | 0.055283 | 0.074503 | 0.10111 | 0.13809 | 0.18965 | 0.26174 | 0.36284 | 0.50493 | 0.70506 | 0.9875 | 1.3868 |  | 288.2238 | 325.4643 | 367.7743 | 415.8631 | 470.5405 | 532.7317 | 603.4941 | 684.0356 | 775.737 | 880.1764 | 999.1582 | 1134.7452 | 1289.2962 | 1465.5091 | 1666.4693 | 1895.7061 | 2157.2572 | 2455.7368 | 2796.4306 | 3185.3882 | 3629.5296 | 4136.7748 | 4716.1879 | 5378.1439 | 6134.5184 | 6998.9052 | 7786.7547 | 7786.5546 | 7786.2721 | 7785.8729 |  | 2962.1962 | 3350.5952 | 3791.8676 | 4293.4089 | 4863.6664 | 5512.29 | 6250.3056 | 7090.3128 | 8046.7115 | 9135.9619 | 10376.8814 | 11790.9849 | 13402.8743 | 15240.6854 | 17336.598 | 19727.422 | 22455.2673 | 25559.6264 | 29095.81 | 33128.9941 | 37728.8353 | 42974.3852 | 48955.171 | 55772.3151 | 63539.644 | 72384.7151 | 80362.583 | 80023.8509 | 79545.8231 | 78870.0691
| TRUE | 1891 | 22015825 | GCY | Blank | 22 | TRANS NO.1 | NEUTRAL DISPLACEMENT | X | ASEA | GROUP_2605 | GROUP 2605 | GROUP 2000s | Electronic |  | 0.066046 | 2190 |  | 8.25 | 0.026286 | 0.0045837 | 0.021702 | 280.8119 | 2016.8282 | 2297.64 | 100.6375 | 10.5627 | 255.4581 |  | 13.0142 | 0.090569 | 0.015794 | 0.074776 | 967.5611 | 6949.1524 | 7916.7135 | 346.7551 | 36.3947 | 880.2025 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.026058 |  | 2664.2983 | 9180.0657 | 71.2357 | 9108.83 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0051721 | 0.0058403 | 0.0065995 | 0.0074623 | 0.0084434 | 0.0095593 | 0.010829 | 0.012274 | 0.01392 | 0.015794 | 0.017928 | 0.020361 | 0.023134 | 0.026296 | 0.029902 | 0.034015 | 0.038708 | 0.044064 | 0.050177 | 0.057157 | 0.065126 | 0.074228 | 0.084625 | 0.096504 | 0.11008 | 0.12559 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 3006.3 | 3394.699 | 3835.9714 | 4337.5128 | 4907.7702 | 5556.3939 | 6294.4095 | 7134.4166 | 8090.8153 | 9180.0657 | 10420.9852 | 11835.0887 | 13446.9782 | 15284.7892 | 17380.7018 | 19771.5258 | 22499.3712 | 25612.4159 | 29165.7857 | 33222.561 | 37854.9317 | 43145.519 | 49188.8901 | 56093.2936 | 63982.6478 | 72998.8185 | 81217.1715 | 81217.1715 | 81217.1715 | 81217.1715 |  | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 52.7928 | 69.9799 | 93.5726 | 126.1041 | 171.1443 | 233.7334 | 320.9982 | 443.0309 | 614.141 | 854.6408 | 1193.3936 | 1671.4508 | 2347.2461 |  | 316.8582 | 357.7947 | 404.3039 | 457.1654 | 517.2694 | 585.6331 | 663.4185 | 751.9536 | 852.7562 | 967.5611 | 1098.3516 | 1247.3954 | 1417.2854 | 1610.9871 | 1831.8922 | 2083.8804 | 2371.39 | 2699.4989 | 3074.0171 | 3501.5934 | 3989.8362 | 4547.4539 | 5184.4134 | 5912.1241 | 6743.6467 | 7693.9336 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 289.7263 | 330.6628 | 377.172 | 430.0335 | 490.1375 | 558.5012 | 636.2866 | 724.8217 | 825.6243 | 940.4292 | 1071.2197 | 1220.2634 | 1390.1535 | 1583.8552 | 1804.7603 | 2056.7485 | 2344.2581 | 2667.0237 | 3030.9693 | 3444.0326 | 3912.2639 | 4442.1753 | 5040.6335 | 5714.6637 | 6471.1185 | 7316.1479 | 8034.4041 | 7826.022 | 7531.9476 | 7116.2356 |  | 2275.7176 | 2569.729 | 2903.7646 | 3283.4228 | 3715.0979 | 4206.0949 | 4764.7601 | 5400.6311 | 6124.6085 | 6949.1524 | 7888.5072 | 8958.9593 | 10179.132 | 11570.3234 | 13156.8933 | 14966.7061 | 17031.6383 | 19388.1598 | 22077.9998 | 25148.9092 | 28655.5344 | 32660.4183 | 37235.1466 | 42461.6617 | 48433.7676 | 55258.8543 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 2275.5118 | 2569.5233 | 2903.5589 | 3283.2171 | 3714.8922 | 4205.8892 | 4764.5543 | 5400.4253 | 6124.4028 | 6948.9467 | 7888.3015 | 8958.7535 | 10178.9262 | 11570.1177 | 13156.6876 | 14966.5004 | 17031.4326 | 19387.9136 | 22077.6734 | 25148.4727 | 28654.9462 | 32659.62 | 37234.0564 | 42460.1645 | 48431.7012 | 55255.9897 | 61476.0203 | 61474.4402 | 61472.2104 | 61469.0582 |  | 2565.2381 | 2900.186 | 3280.7309 | 3713.2506 | 4205.0297 | 4764.3904 | 5400.8409 | 6125.2471 | 6950.0271 | 7889.3759 | 8959.5212 | 10179.017 | 11569.0797 | 13153.9729 | 14961.4479 | 17023.2489 | 19375.6907 | 22054.9372 | 25108.6427 | 28592.5053 | 32567.2101 | 37101.7953 | 42274.6899 | 48174.8282 | 54902.8197 | 62572.1376 | 69510.4244 | 69300.4622 | 69004.158 | 68585.2938 |  | 113.5558 | 128.2266 | 144.8947 | 163.8392 | 185.3793 | 209.8795 | 237.7563 | 269.4855 | 305.6112 | 346.7551 | 393.6278 | 447.0422 | 507.9275 | 577.3464 | 656.5145 | 746.8222 | 849.86 | 967.4478 | 1101.6679 | 1254.9029 | 1429.8796 | 1629.7189 | 1857.9928 | 2118.7902 | 2416.7917 | 2757.356 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 98.8834 | 113.5542 | 130.2222 | 149.1667 | 170.7069 | 195.2071 | 223.0838 | 254.8131 | 290.9388 | 332.0826 | 378.9554 | 432.3698 | 493.255 | 562.674 | 641.8421 | 732.1497 | 835.1876 | 949.8858 | 1078.3884 | 1223.7751 | 1387.9299 | 1572.7862 | 1780.2393 | 2012.0072 | 2269.4134 | 2553.0564 | 2783.4806 | 2670.7914 | 2511.7613 | 2286.9518 |  | 11.9186 | 13.4584 | 15.2079 | 17.1962 | 19.457 | 22.0285 | 24.9544 | 28.2847 | 32.0763 | 36.3947 | 41.3144 | 46.9207 | 53.3111 | 60.5971 | 68.9065 | 78.385 | 89.1996 | 101.5414 | 115.6289 | 131.7121 | 150.0773 | 171.0521 | 195.0112 | 222.384 | 253.6617 | 289.4066 | 321.9886 | 321.9886 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 9.8509 | 11.3907 | 13.1402 | 15.1285 | 17.3893 | 19.9608 | 22.8867 | 26.217 | 30.0087 | 34.327 | 39.2467 | 44.853 | 51.2434 | 58.5294 | 66.8388 | 76.3173 | 87.1319 | 99.0665 | 112.3482 | 127.3255 | 144.1656 | 163.0289 | 184.0539 | 207.3357 | 232.8925 | 260.6159 | 281.9234 | 266.0428 | 243.6317 | 211.9507 |  | 288.2499 | 325.4903 | 367.8004 | 415.8891 | 470.5665 | 532.7578 | 603.5202 | 684.0617 | 775.763 | 880.2025 | 999.1842 | 1134.7712 | 1289.3223 | 1465.5352 | 1666.4953 | 1895.7322 | 2157.2833 | 2455.768 | 2796.472 | 3185.4435 | 3629.6041 | 4136.8759 | 4716.326 | 5378.3336 | 6134.7801 | 6999.268 | 7787.2596 | 7787.2596 | 7787.2596 | 7787.2596 |  | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.03119 | 0.041344 | 0.055283 | 0.074503 | 0.10111 | 0.13809 | 0.18965 | 0.26174 | 0.36284 | 0.50493 | 0.70506 | 0.9875 | 1.3868 |  | 288.2238 | 325.4643 | 367.7743 | 415.8631 | 470.5405 | 532.7317 | 603.4941 | 684.0356 | 775.737 | 880.1764 | 999.1582 | 1134.7452 | 1289.2962 | 1465.5091 | 1666.4693 | 1895.7061 | 2157.2572 | 2455.7368 | 2796.4306 | 3185.3882 | 3629.5296 | 4136.7748 | 4716.1879 | 5378.1439 | 6134.5184 | 6998.9052 | 7786.7547 | 7786.5546 | 7786.2721 | 7785.8729 |  | 2962.1962 | 3350.5952 | 3791.8676 | 4293.4089 | 4863.6664 | 5512.29 | 6250.3056 | 7090.3128 | 8046.7115 | 9135.9619 | 10376.8814 | 11790.9849 | 13402.8743 | 15240.6854 | 17336.598 | 19727.422 | 22455.2673 | 25559.6264 | 29095.81 | 33128.9941 | 37728.8353 | 42974.3852 | 48955.171 | 55772.3151 | 63539.644 | 72384.7151 | 80362.583 | 80023.8509 | 79545.8231 | 78870.0691
| TRUE | 1892 | 22001688 | GCY | Blank | 22 | TRANS NO.1 | DIFFERENTIAL | Y | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.0068096 | 2190 |  | 8.25 | 0.026286 | 0.00052975 | 0.025756 | 276.5552 | 233.0884 | 509.6437 | 77.6223 | 10.5222 | 147.6187 |  | 13.0142 | 0.090569 | 0.0018253 | 0.088744 | 952.8944 | 803.126 | 1756.0204 | 267.4541 | 36.255 | 508.6329 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.013433 |  | 745.4068 | 2568.3624 | 71.0358 | 2497.3266 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00059775 | 0.00067497 | 0.00076271 | 0.00086243 | 0.00097582 | 0.0011048 | 0.0012515 | 0.0014185 | 0.0016087 | 0.0018253 | 0.002072 | 0.0023532 | 0.0026737 | 0.0030391 | 0.0034558 | 0.0039312 | 0.0044736 | 0.0050926 | 0.0057991 | 0.0066057 | 0.0075268 | 0.0085787 | 0.0097803 | 0.011153 | 0.012722 | 0.014514 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 841.0907 | 949.7554 | 1073.2129 | 1213.5321 | 1373.0765 | 1554.5459 | 1761.0249 | 1996.0388 | 2263.6163 | 2568.3624 | 2915.542 | 3311.1742 | 3762.1423 | 4276.3178 | 4862.7039 | 5531.5992 | 6294.7849 | 7165.7403 | 8159.888 | 9294.8765 | 10590.9028 | 12071.0824 | 13761.8728 | 15693.5595 | 17900.8117 | 20423.3202 | 22722.6185 | 22722.6185 | 22722.6185 | 22722.6185 |  | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 52.5508 | 69.6592 | 93.1437 | 125.5261 | 170.3599 | 232.662 | 319.5268 | 441.0002 | 611.326 | 850.7234 | 1187.9235 | 1663.7894 | 2336.4871 |  | 312.0551 | 352.3711 | 398.1753 | 450.2355 | 509.4285 | 576.7559 | 653.3622 | 740.5552 | 839.8298 | 952.8944 | 1081.7024 | 1228.4869 | 1395.8016 | 1586.5671 | 1804.1237 | 2052.2922 | 2335.4436 | 2658.5789 | 3027.42 | 3448.5149 | 3929.3568 | 4478.5218 | 5105.8261 | 5822.5059 | 6641.424 | 7577.3061 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 284.9234 | 325.2394 | 371.0437 | 423.1038 | 482.2968 | 549.6242 | 626.2305 | 713.4236 | 812.6981 | 925.7627 | 1054.5707 | 1201.3552 | 1368.6699 | 1559.4354 | 1776.992 | 2025.1605 | 2308.3119 | 2626.1039 | 2984.3726 | 3390.9546 | 3851.7851 | 4373.2441 | 4962.0474 | 5625.0471 | 6368.898 | 7199.5234 | 7904.6507 | 7696.2703 | 7402.1983 | 6986.4896 |  | 263.0087 | 296.9882 | 335.5933 | 379.471 | 429.3605 | 486.1059 | 550.6718 | 624.1606 | 707.832 | 803.126 | 911.6889 | 1035.4029 | 1176.4205 | 1337.203 | 1520.5657 | 1729.729 | 1968.3769 | 2240.7243 | 2551.5939 | 2906.5044 | 3311.7714 | 3774.623 | 4303.3325 | 4907.3702 | 5597.5772 | 6386.3646 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 262.9875 | 296.967 | 335.5721 | 379.4498 | 429.3393 | 486.0847 | 550.6506 | 624.1394 | 707.8107 | 803.1048 | 911.6677 | 1035.3817 | 1176.3993 | 1337.1818 | 1520.5445 | 1729.7078 | 1968.3557 | 2240.6989 | 2551.5603 | 2906.4594 | 3311.7107 | 3774.5407 | 4303.2201 | 4907.2158 | 5597.3641 | 6386.0693 | 7104.9433 | 7104.7804 | 7104.5505 | 7104.2255 |  | 547.911 | 622.2064 | 706.6157 | 802.5537 | 911.6361 | 1035.7089 | 1176.8811 | 1337.5629 | 1520.5089 | 1728.8675 | 1966.2384 | 2236.7369 | 2545.0692 | 2896.6172 | 3297.5365 | 3754.8683 | 4276.6676 | 4866.8028 | 5535.9329 | 6297.4141 | 7163.4959 | 8147.7848 | 9265.2675 | 10532.263 | 11966.2621 | 13585.5927 | 15009.594 | 14801.0507 | 14506.7488 | 14090.7151 |  | 87.5862 | 98.9019 | 111.7581 | 126.3701 | 142.9841 | 161.8812 | 183.3827 | 207.8557 | 235.7196 | 267.4541 | 303.6073 | 344.8061 | 391.7673 | 445.3105 | 506.3733 | 576.0281 | 655.5017 | 746.1979 | 849.7226 | 967.9136 | 1102.8741 | 1257.0113 | 1433.0802 | 1634.2347 | 1864.0849 | 2126.764 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 72.9162 | 84.2319 | 97.088 | 111.7 | 128.314 | 147.2112 | 168.7127 | 193.1856 | 221.0496 | 252.784 | 288.9373 | 330.1361 | 377.0972 | 430.6404 | 491.7032 | 561.358 | 640.8317 | 728.6388 | 826.4469 | 936.7908 | 1060.9312 | 1200.0878 | 1355.3393 | 1527.469 | 1716.7305 | 1922.4976 | 2081.9414 | 1969.2705 | 1810.2663 | 1585.4933 |  | 11.8728 | 13.4068 | 15.1495 | 17.1302 | 19.3824 | 21.944 | 24.8587 | 28.1761 | 31.9532 | 36.255 | 41.1558 | 46.7406 | 53.1065 | 60.3646 | 68.642 | 78.0841 | 88.8573 | 101.1517 | 115.1851 | 131.2066 | 149.5013 | 170.3956 | 194.2628 | 221.5305 | 252.6881 | 288.2959 | 320.7528 | 320.7528 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 9.8052 | 11.3391 | 13.0818 | 15.0625 | 17.3147 | 19.8763 | 22.791 | 26.1084 | 29.8855 | 34.1873 | 39.0881 | 44.6729 | 51.0388 | 58.2969 | 66.5743 | 76.0164 | 86.7896 | 98.6768 | 111.9045 | 126.82 | 143.5896 | 162.3724 | 183.3055 | 206.4823 | 231.919 | 259.5053 | 280.6877 | 264.8071 | 242.396 | 210.7151 |  | 166.5678 | 188.0875 | 212.5367 | 240.3252 | 271.9211 | 307.8589 | 348.7495 | 395.2912 | 448.2816 | 508.6329 | 577.3875 | 655.7377 | 745.0464 | 846.8726 | 962.9992 | 1095.4658 | 1246.6054 | 1419.0875 | 1615.9663 | 1840.737 | 2097.3992 | 2390.5307 | 2725.3712 | 3107.9182 | 3545.0376 | 4044.5896 | 4499.9376 | 4499.9376 | 4499.9376 | 4499.9376 |  | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.016079 | 0.021314 | 0.028499 | 0.038407 | 0.052125 | 0.071188 | 0.097766 | 0.13493 | 0.18705 | 0.2603 | 0.36347 | 0.50907 | 0.7149 |  | 166.5543 | 188.0741 | 212.5233 | 240.3118 | 271.9076 | 307.8454 | 348.7361 | 395.2777 | 448.2682 | 508.6194 | 577.3741 | 655.7243 | 745.033 | 846.8592 | 962.9858 | 1095.4524 | 1246.592 | 1419.0714 | 1615.945 | 1840.7085 | 2097.3608 | 2390.4786 | 2725.3 | 3107.8204 | 3544.9026 | 4044.4026 | 4499.6773 | 4499.5741 | 4499.4285 | 4499.2227 |  | 797.1866 | 905.8514 | 1029.3088 | 1169.628 | 1329.1724 | 1510.6418 | 1717.1209 | 1952.1347 | 2219.7122 | 2524.4583 | 2871.6379 | 3267.2701 | 3718.2382 | 4232.4137 | 4818.7998 | 5487.6951 | 6250.8808 | 7113.1898 | 8090.2292 | 9201.7333 | 10465.3775 | 11900.7236 | 13529.2122 | 15374.0346 | 17459.8143 | 19811.9981 | 21871.9004 | 21534.7025 | 21058.8396 | 20386.1462
| TRUE | 1893 | 22001686 | GCY | Blank | 22 | TRANS NO.1 | DIFFERENTIAL | X | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.066046 | 2190 |  | 8.25 | 0.026286 | 0.0045837 | 0.021702 | 280.8119 | 2016.8282 | 2297.64 | 100.6375 | 10.5627 | 1277.2904 |  | 13.0142 | 0.090569 | 0.015794 | 0.074776 | 967.5611 | 6949.1524 | 7916.7135 | 346.7551 | 36.3947 | 4401.0124 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.13029 |  | 3686.1307 | 12700.8756 | 71.34 | 12629.5357 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0051721 | 0.0058403 | 0.0065995 | 0.0074623 | 0.0084434 | 0.0095593 | 0.010829 | 0.012274 | 0.01392 | 0.015794 | 0.017928 | 0.020361 | 0.023134 | 0.026296 | 0.029902 | 0.034015 | 0.038708 | 0.044064 | 0.050177 | 0.057157 | 0.065126 | 0.074228 | 0.084625 | 0.096504 | 0.11008 | 0.12559 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 4159.2994 | 4696.6603 | 5307.1729 | 6001.0692 | 6790.0363 | 7687.4251 | 8708.4901 | 9870.6633 | 11193.8674 | 12700.8756 | 14417.7222 | 16374.1736 | 18604.2674 | 21146.9299 | 24046.6831 | 27354.4545 | 31128.5042 | 35435.488 | 40351.6736 | 45964.3348 | 52373.3482 | 59693.0225 | 68054.1941 | 77606.6279 | 88521.7683 | 100995.8906 | 112366.21 | 112366.21 | 112366.21 | 112366.21 |  | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 52.9175 | 70.1453 | 93.7938 | 126.4021 | 171.5488 | 234.2857 | 321.7568 | 444.0779 | 615.5923 | 856.6605 | 1196.2139 | 1675.4008 | 2352.7932 |  | 316.8582 | 357.7947 | 404.3039 | 457.1654 | 517.2694 | 585.6331 | 663.4185 | 751.9536 | 852.7562 | 967.5611 | 1098.3516 | 1247.3954 | 1417.2854 | 1610.9871 | 1831.8922 | 2083.8804 | 2371.39 | 2699.4989 | 3074.0171 | 3501.5934 | 3989.8362 | 4547.4539 | 5184.4134 | 5912.1241 | 6743.6467 | 7693.9336 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 289.7263 | 330.6628 | 377.172 | 430.0335 | 490.1375 | 558.5012 | 636.2866 | 724.8217 | 825.6243 | 940.4292 | 1071.2197 | 1220.2634 | 1390.1535 | 1583.8552 | 1804.7603 | 2056.7485 | 2344.2581 | 2667.0237 | 3030.9693 | 3444.0326 | 3912.2639 | 4442.1753 | 5040.6335 | 5714.6637 | 6471.1185 | 7316.1479 | 8034.4041 | 7826.022 | 7531.9476 | 7116.2356 |  | 2275.7176 | 2569.729 | 2903.7646 | 3283.4228 | 3715.0979 | 4206.0949 | 4764.7601 | 5400.6311 | 6124.6085 | 6949.1524 | 7888.5072 | 8958.9593 | 10179.132 | 11570.3234 | 13156.8933 | 14966.7061 | 17031.6383 | 19388.1598 | 22077.9998 | 25148.9092 | 28655.5344 | 32660.4183 | 37235.1466 | 42461.6617 | 48433.7676 | 55258.8543 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 2275.5118 | 2569.5233 | 2903.5589 | 3283.2171 | 3714.8922 | 4205.8892 | 4764.5543 | 5400.4253 | 6124.4028 | 6948.9467 | 7888.3015 | 8958.7535 | 10178.9262 | 11570.1177 | 13156.6876 | 14966.5004 | 17031.4326 | 19387.9136 | 22077.6734 | 25148.4727 | 28654.9462 | 32659.62 | 37234.0564 | 42460.1645 | 48431.7012 | 55255.9897 | 61476.0203 | 61474.4402 | 61472.2104 | 61469.0582 |  | 2565.2381 | 2900.186 | 3280.7309 | 3713.2506 | 4205.0297 | 4764.3904 | 5400.8409 | 6125.2471 | 6950.0271 | 7889.3759 | 8959.5212 | 10179.017 | 11569.0797 | 13153.9729 | 14961.4479 | 17023.2489 | 19375.6907 | 22054.9372 | 25108.6427 | 28592.5053 | 32567.2101 | 37101.7953 | 42274.6899 | 48174.8282 | 54902.8197 | 62572.1376 | 69510.4244 | 69300.4622 | 69004.158 | 68585.2938 |  | 113.5558 | 128.2266 | 144.8947 | 163.8392 | 185.3793 | 209.8795 | 237.7563 | 269.4855 | 305.6112 | 346.7551 | 393.6278 | 447.0422 | 507.9275 | 577.3464 | 656.5145 | 746.8222 | 849.86 | 967.4478 | 1101.6679 | 1254.9029 | 1429.8796 | 1629.7189 | 1857.9928 | 2118.7902 | 2416.7917 | 2757.356 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 98.8834 | 113.5542 | 130.2222 | 149.1667 | 170.7069 | 195.2071 | 223.0838 | 254.8131 | 290.9388 | 332.0826 | 378.9554 | 432.3698 | 493.255 | 562.674 | 641.8421 | 732.1497 | 835.1876 | 949.8858 | 1078.3884 | 1223.7751 | 1387.9299 | 1572.7862 | 1780.2393 | 2012.0072 | 2269.4134 | 2553.0564 | 2783.4806 | 2670.7914 | 2511.7613 | 2286.9518 |  | 11.9186 | 13.4584 | 15.2079 | 17.1962 | 19.457 | 22.0285 | 24.9544 | 28.2847 | 32.0763 | 36.3947 | 41.3144 | 46.9207 | 53.3111 | 60.5971 | 68.9065 | 78.385 | 89.1996 | 101.5414 | 115.6289 | 131.7121 | 150.0773 | 171.0521 | 195.0112 | 222.384 | 253.6617 | 289.4066 | 321.9886 | 321.9886 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 9.8509 | 11.3907 | 13.1402 | 15.1285 | 17.3893 | 19.9608 | 22.8867 | 26.217 | 30.0087 | 34.327 | 39.2467 | 44.853 | 51.2434 | 58.5294 | 66.8388 | 76.3173 | 87.1319 | 99.0665 | 112.3482 | 127.3255 | 144.1656 | 163.0289 | 184.0539 | 207.3357 | 232.8925 | 260.6159 | 281.9234 | 266.0428 | 243.6317 | 211.9507 |  | 1441.2493 | 1627.4516 | 1839.0018 | 2079.4456 | 2352.8325 | 2663.789 | 3017.6008 | 3420.3084 | 3878.8152 | 4401.0124 | 4995.9212 | 5673.8561 | 6446.6115 | 7327.6759 | 8332.4767 | 9478.6608 | 10786.4163 | 12278.8401 | 13982.3599 | 15927.2173 | 18148.0206 | 20684.3794 | 23581.63 | 26891.6679 | 30673.9006 | 34996.3401 | 38936.2981 | 38936.2981 | 38936.2981 | 38936.2981 |  | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.15595 | 0.20672 | 0.27642 | 0.37251 | 0.50556 | 0.69045 | 0.94824 | 1.3087 | 1.8142 | 2.5246 | 3.5253 | 4.9375 | 6.9338 |  | 1441.119 | 1627.3213 | 1838.8715 | 2079.3153 | 2352.7023 | 2663.6587 | 3017.4705 | 3420.1781 | 3878.6849 | 4400.8821 | 4995.7909 | 5673.7258 | 6446.4812 | 7327.5456 | 8332.3464 | 9478.5305 | 10786.286 | 12278.6841 | 13982.1532 | 15926.9409 | 18147.6481 | 20683.8738 | 23580.9395 | 26890.7196 | 30672.5919 | 34994.5259 | 38933.7735 | 38932.7728 | 38931.3606 | 38929.3643 |  | 4115.0914 | 4652.4522 | 5262.9648 | 5956.8612 | 6745.8282 | 7643.217 | 8664.282 | 9826.4552 | 11149.6594 | 12656.6676 | 14373.5141 | 16329.9655 | 18560.0593 | 21102.7219 | 24002.4751 | 27310.2464 | 31084.2961 | 35382.5737 | 40281.5326 | 45870.5468 | 52246.9538 | 59521.4842 | 67819.9227 | 77284.8908 | 88077.7176 | 100380.3358 | 111509.6018 | 111170.0692 | 110690.9115 | 110013.5605
| TRUE | 1894 | 22015827 | GCY | Blank | 22 | TRANS NO.2 | GAS & T/C PROT | X | ASEA | GROUP_2598 | GROUP 2598 | GROUP 2000s | Electronic |  | 0.066046 | 2190 |  | 8.25 | 0.026286 | 0.0045837 | 0.021702 | 280.8119 | 2016.8282 | 2297.64 | 100.6375 | 10.5627 | 255.4581 |  | 13.0142 | 0.090569 | 0.015794 | 0.074776 | 967.5611 | 6949.1524 | 7916.7135 | 346.7551 | 36.3947 | 880.2025 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.026058 |  | 2664.2983 | 9180.0657 | 71.2357 | 9108.83 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0051721 | 0.0058403 | 0.0065995 | 0.0074623 | 0.0084434 | 0.0095593 | 0.010829 | 0.012274 | 0.01392 | 0.015794 | 0.017928 | 0.020361 | 0.023134 | 0.026296 | 0.029902 | 0.034015 | 0.038708 | 0.044064 | 0.050177 | 0.057157 | 0.065126 | 0.074228 | 0.084625 | 0.096504 | 0.11008 | 0.12559 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 3006.3 | 3394.699 | 3835.9714 | 4337.5128 | 4907.7702 | 5556.3939 | 6294.4095 | 7134.4166 | 8090.8153 | 9180.0657 | 10420.9852 | 11835.0887 | 13446.9782 | 15284.7892 | 17380.7018 | 19771.5258 | 22499.3712 | 25612.4159 | 29165.7857 | 33222.561 | 37854.9317 | 43145.519 | 49188.8901 | 56093.2936 | 63982.6478 | 72998.8185 | 81217.1715 | 81217.1715 | 81217.1715 | 81217.1715 |  | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 52.7928 | 69.9799 | 93.5726 | 126.1041 | 171.1443 | 233.7334 | 320.9982 | 443.0309 | 614.141 | 854.6408 | 1193.3936 | 1671.4508 | 2347.2461 |  | 316.8582 | 357.7947 | 404.3039 | 457.1654 | 517.2694 | 585.6331 | 663.4185 | 751.9536 | 852.7562 | 967.5611 | 1098.3516 | 1247.3954 | 1417.2854 | 1610.9871 | 1831.8922 | 2083.8804 | 2371.39 | 2699.4989 | 3074.0171 | 3501.5934 | 3989.8362 | 4547.4539 | 5184.4134 | 5912.1241 | 6743.6467 | 7693.9336 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 289.7263 | 330.6628 | 377.172 | 430.0335 | 490.1375 | 558.5012 | 636.2866 | 724.8217 | 825.6243 | 940.4292 | 1071.2197 | 1220.2634 | 1390.1535 | 1583.8552 | 1804.7603 | 2056.7485 | 2344.2581 | 2667.0237 | 3030.9693 | 3444.0326 | 3912.2639 | 4442.1753 | 5040.6335 | 5714.6637 | 6471.1185 | 7316.1479 | 8034.4041 | 7826.022 | 7531.9476 | 7116.2356 |  | 2275.7176 | 2569.729 | 2903.7646 | 3283.4228 | 3715.0979 | 4206.0949 | 4764.7601 | 5400.6311 | 6124.6085 | 6949.1524 | 7888.5072 | 8958.9593 | 10179.132 | 11570.3234 | 13156.8933 | 14966.7061 | 17031.6383 | 19388.1598 | 22077.9998 | 25148.9092 | 28655.5344 | 32660.4183 | 37235.1466 | 42461.6617 | 48433.7676 | 55258.8543 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 2275.5118 | 2569.5233 | 2903.5589 | 3283.2171 | 3714.8922 | 4205.8892 | 4764.5543 | 5400.4253 | 6124.4028 | 6948.9467 | 7888.3015 | 8958.7535 | 10178.9262 | 11570.1177 | 13156.6876 | 14966.5004 | 17031.4326 | 19387.9136 | 22077.6734 | 25148.4727 | 28654.9462 | 32659.62 | 37234.0564 | 42460.1645 | 48431.7012 | 55255.9897 | 61476.0203 | 61474.4402 | 61472.2104 | 61469.0582 |  | 2565.2381 | 2900.186 | 3280.7309 | 3713.2506 | 4205.0297 | 4764.3904 | 5400.8409 | 6125.2471 | 6950.0271 | 7889.3759 | 8959.5212 | 10179.017 | 11569.0797 | 13153.9729 | 14961.4479 | 17023.2489 | 19375.6907 | 22054.9372 | 25108.6427 | 28592.5053 | 32567.2101 | 37101.7953 | 42274.6899 | 48174.8282 | 54902.8197 | 62572.1376 | 69510.4244 | 69300.4622 | 69004.158 | 68585.2938 |  | 113.5558 | 128.2266 | 144.8947 | 163.8392 | 185.3793 | 209.8795 | 237.7563 | 269.4855 | 305.6112 | 346.7551 | 393.6278 | 447.0422 | 507.9275 | 577.3464 | 656.5145 | 746.8222 | 849.86 | 967.4478 | 1101.6679 | 1254.9029 | 1429.8796 | 1629.7189 | 1857.9928 | 2118.7902 | 2416.7917 | 2757.356 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 98.8834 | 113.5542 | 130.2222 | 149.1667 | 170.7069 | 195.2071 | 223.0838 | 254.8131 | 290.9388 | 332.0826 | 378.9554 | 432.3698 | 493.255 | 562.674 | 641.8421 | 732.1497 | 835.1876 | 949.8858 | 1078.3884 | 1223.7751 | 1387.9299 | 1572.7862 | 1780.2393 | 2012.0072 | 2269.4134 | 2553.0564 | 2783.4806 | 2670.7914 | 2511.7613 | 2286.9518 |  | 11.9186 | 13.4584 | 15.2079 | 17.1962 | 19.457 | 22.0285 | 24.9544 | 28.2847 | 32.0763 | 36.3947 | 41.3144 | 46.9207 | 53.3111 | 60.5971 | 68.9065 | 78.385 | 89.1996 | 101.5414 | 115.6289 | 131.7121 | 150.0773 | 171.0521 | 195.0112 | 222.384 | 253.6617 | 289.4066 | 321.9886 | 321.9886 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 9.8509 | 11.3907 | 13.1402 | 15.1285 | 17.3893 | 19.9608 | 22.8867 | 26.217 | 30.0087 | 34.327 | 39.2467 | 44.853 | 51.2434 | 58.5294 | 66.8388 | 76.3173 | 87.1319 | 99.0665 | 112.3482 | 127.3255 | 144.1656 | 163.0289 | 184.0539 | 207.3357 | 232.8925 | 260.6159 | 281.9234 | 266.0428 | 243.6317 | 211.9507 |  | 288.2499 | 325.4903 | 367.8004 | 415.8891 | 470.5665 | 532.7578 | 603.5202 | 684.0617 | 775.763 | 880.2025 | 999.1842 | 1134.7712 | 1289.3223 | 1465.5352 | 1666.4953 | 1895.7322 | 2157.2833 | 2455.768 | 2796.472 | 3185.4435 | 3629.6041 | 4136.8759 | 4716.326 | 5378.3336 | 6134.7801 | 6999.268 | 7787.2596 | 7787.2596 | 7787.2596 | 7787.2596 |  | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.03119 | 0.041344 | 0.055283 | 0.074503 | 0.10111 | 0.13809 | 0.18965 | 0.26174 | 0.36284 | 0.50493 | 0.70506 | 0.9875 | 1.3868 |  | 288.2238 | 325.4643 | 367.7743 | 415.8631 | 470.5405 | 532.7317 | 603.4941 | 684.0356 | 775.737 | 880.1764 | 999.1582 | 1134.7452 | 1289.2962 | 1465.5091 | 1666.4693 | 1895.7061 | 2157.2572 | 2455.7368 | 2796.4306 | 3185.3882 | 3629.5296 | 4136.7748 | 4716.1879 | 5378.1439 | 6134.5184 | 6998.9052 | 7786.7547 | 7786.5546 | 7786.2721 | 7785.8729 |  | 2962.1962 | 3350.5952 | 3791.8676 | 4293.4089 | 4863.6664 | 5512.29 | 6250.3056 | 7090.3128 | 8046.7115 | 9135.9619 | 10376.8814 | 11790.9849 | 13402.8743 | 15240.6854 | 17336.598 | 19727.422 | 22455.2673 | 25559.6264 | 29095.81 | 33128.9941 | 37728.8353 | 42974.3852 | 48955.171 | 55772.3151 | 63539.644 | 72384.7151 | 80362.583 | 80023.8509 | 79545.8231 | 78870.0691
| TRUE | 1895 | 22015826 | GCY | Blank | 22 | TRANS NO.2 | NEUTRAL DISPLACEMENT | X | ASEA | GROUP_2605 | GROUP 2605 | GROUP 2000s | Electronic |  | 0.066046 | 2190 |  | 8.25 | 0.026286 | 0.0045837 | 0.021702 | 280.8119 | 2016.8282 | 2297.64 | 100.6375 | 10.5627 | 255.4581 |  | 13.0142 | 0.090569 | 0.015794 | 0.074776 | 967.5611 | 6949.1524 | 7916.7135 | 346.7551 | 36.3947 | 880.2025 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.026058 |  | 2664.2983 | 9180.0657 | 71.2357 | 9108.83 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0051721 | 0.0058403 | 0.0065995 | 0.0074623 | 0.0084434 | 0.0095593 | 0.010829 | 0.012274 | 0.01392 | 0.015794 | 0.017928 | 0.020361 | 0.023134 | 0.026296 | 0.029902 | 0.034015 | 0.038708 | 0.044064 | 0.050177 | 0.057157 | 0.065126 | 0.074228 | 0.084625 | 0.096504 | 0.11008 | 0.12559 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 3006.3 | 3394.699 | 3835.9714 | 4337.5128 | 4907.7702 | 5556.3939 | 6294.4095 | 7134.4166 | 8090.8153 | 9180.0657 | 10420.9852 | 11835.0887 | 13446.9782 | 15284.7892 | 17380.7018 | 19771.5258 | 22499.3712 | 25612.4159 | 29165.7857 | 33222.561 | 37854.9317 | 43145.519 | 49188.8901 | 56093.2936 | 63982.6478 | 72998.8185 | 81217.1715 | 81217.1715 | 81217.1715 | 81217.1715 |  | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 44.1065 | 52.7928 | 69.9799 | 93.5726 | 126.1041 | 171.1443 | 233.7334 | 320.9982 | 443.0309 | 614.141 | 854.6408 | 1193.3936 | 1671.4508 | 2347.2461 |  | 316.8582 | 357.7947 | 404.3039 | 457.1654 | 517.2694 | 585.6331 | 663.4185 | 751.9536 | 852.7562 | 967.5611 | 1098.3516 | 1247.3954 | 1417.2854 | 1610.9871 | 1831.8922 | 2083.8804 | 2371.39 | 2699.4989 | 3074.0171 | 3501.5934 | 3989.8362 | 4547.4539 | 5184.4134 | 5912.1241 | 6743.6467 | 7693.9336 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 289.7263 | 330.6628 | 377.172 | 430.0335 | 490.1375 | 558.5012 | 636.2866 | 724.8217 | 825.6243 | 940.4292 | 1071.2197 | 1220.2634 | 1390.1535 | 1583.8552 | 1804.7603 | 2056.7485 | 2344.2581 | 2667.0237 | 3030.9693 | 3444.0326 | 3912.2639 | 4442.1753 | 5040.6335 | 5714.6637 | 6471.1185 | 7316.1479 | 8034.4041 | 7826.022 | 7531.9476 | 7116.2356 |  | 2275.7176 | 2569.729 | 2903.7646 | 3283.4228 | 3715.0979 | 4206.0949 | 4764.7601 | 5400.6311 | 6124.6085 | 6949.1524 | 7888.5072 | 8958.9593 | 10179.132 | 11570.3234 | 13156.8933 | 14966.7061 | 17031.6383 | 19388.1598 | 22077.9998 | 25148.9092 | 28655.5344 | 32660.4183 | 37235.1466 | 42461.6617 | 48433.7676 | 55258.8543 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 2275.5118 | 2569.5233 | 2903.5589 | 3283.2171 | 3714.8922 | 4205.8892 | 4764.5543 | 5400.4253 | 6124.4028 | 6948.9467 | 7888.3015 | 8958.7535 | 10178.9262 | 11570.1177 | 13156.6876 | 14966.5004 | 17031.4326 | 19387.9136 | 22077.6734 | 25148.4727 | 28654.9462 | 32659.62 | 37234.0564 | 42460.1645 | 48431.7012 | 55255.9897 | 61476.0203 | 61474.4402 | 61472.2104 | 61469.0582 |  | 2565.2381 | 2900.186 | 3280.7309 | 3713.2506 | 4205.0297 | 4764.3904 | 5400.8409 | 6125.2471 | 6950.0271 | 7889.3759 | 8959.5212 | 10179.017 | 11569.0797 | 13153.9729 | 14961.4479 | 17023.2489 | 19375.6907 | 22054.9372 | 25108.6427 | 28592.5053 | 32567.2101 | 37101.7953 | 42274.6899 | 48174.8282 | 54902.8197 | 62572.1376 | 69510.4244 | 69300.4622 | 69004.158 | 68585.2938 |  | 113.5558 | 128.2266 | 144.8947 | 163.8392 | 185.3793 | 209.8795 | 237.7563 | 269.4855 | 305.6112 | 346.7551 | 393.6278 | 447.0422 | 507.9275 | 577.3464 | 656.5145 | 746.8222 | 849.86 | 967.4478 | 1101.6679 | 1254.9029 | 1429.8796 | 1629.7189 | 1857.9928 | 2118.7902 | 2416.7917 | 2757.356 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 98.8834 | 113.5542 | 130.2222 | 149.1667 | 170.7069 | 195.2071 | 223.0838 | 254.8131 | 290.9388 | 332.0826 | 378.9554 | 432.3698 | 493.255 | 562.674 | 641.8421 | 732.1497 | 835.1876 | 949.8858 | 1078.3884 | 1223.7751 | 1387.9299 | 1572.7862 | 1780.2393 | 2012.0072 | 2269.4134 | 2553.0564 | 2783.4806 | 2670.7914 | 2511.7613 | 2286.9518 |  | 11.9186 | 13.4584 | 15.2079 | 17.1962 | 19.457 | 22.0285 | 24.9544 | 28.2847 | 32.0763 | 36.3947 | 41.3144 | 46.9207 | 53.3111 | 60.5971 | 68.9065 | 78.385 | 89.1996 | 101.5414 | 115.6289 | 131.7121 | 150.0773 | 171.0521 | 195.0112 | 222.384 | 253.6617 | 289.4066 | 321.9886 | 321.9886 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 9.8509 | 11.3907 | 13.1402 | 15.1285 | 17.3893 | 19.9608 | 22.8867 | 26.217 | 30.0087 | 34.327 | 39.2467 | 44.853 | 51.2434 | 58.5294 | 66.8388 | 76.3173 | 87.1319 | 99.0665 | 112.3482 | 127.3255 | 144.1656 | 163.0289 | 184.0539 | 207.3357 | 232.8925 | 260.6159 | 281.9234 | 266.0428 | 243.6317 | 211.9507 |  | 288.2499 | 325.4903 | 367.8004 | 415.8891 | 470.5665 | 532.7578 | 603.5202 | 684.0617 | 775.763 | 880.2025 | 999.1842 | 1134.7712 | 1289.3223 | 1465.5352 | 1666.4953 | 1895.7322 | 2157.2833 | 2455.768 | 2796.472 | 3185.4435 | 3629.6041 | 4136.8759 | 4716.326 | 5378.3336 | 6134.7801 | 6999.268 | 7787.2596 | 7787.2596 | 7787.2596 | 7787.2596 |  | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.026058 | 0.03119 | 0.041344 | 0.055283 | 0.074503 | 0.10111 | 0.13809 | 0.18965 | 0.26174 | 0.36284 | 0.50493 | 0.70506 | 0.9875 | 1.3868 |  | 288.2238 | 325.4643 | 367.7743 | 415.8631 | 470.5405 | 532.7317 | 603.4941 | 684.0356 | 775.737 | 880.1764 | 999.1582 | 1134.7452 | 1289.2962 | 1465.5091 | 1666.4693 | 1895.7061 | 2157.2572 | 2455.7368 | 2796.4306 | 3185.3882 | 3629.5296 | 4136.7748 | 4716.1879 | 5378.1439 | 6134.5184 | 6998.9052 | 7786.7547 | 7786.5546 | 7786.2721 | 7785.8729 |  | 2962.1962 | 3350.5952 | 3791.8676 | 4293.4089 | 4863.6664 | 5512.29 | 6250.3056 | 7090.3128 | 8046.7115 | 9135.9619 | 10376.8814 | 11790.9849 | 13402.8743 | 15240.6854 | 17336.598 | 19727.422 | 22455.2673 | 25559.6264 | 29095.81 | 33128.9941 | 37728.8353 | 42974.3852 | 48955.171 | 55772.3151 | 63539.644 | 72384.7151 | 80362.583 | 80023.8509 | 79545.8231 | 78870.0691
| TRUE | 1896 | 22001689 | GCY | Blank | 22 | TRANS NO.2 | DIFFERENTIAL | Y | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.0068096 | 2190 |  | 8.25 | 0.026286 | 0.00052975 | 0.025756 | 276.5552 | 233.0884 | 509.6437 | 77.6223 | 10.5222 | 147.6187 |  | 13.0142 | 0.090569 | 0.0018253 | 0.088744 | 952.8944 | 803.126 | 1756.0204 | 267.4541 | 36.255 | 508.6329 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.013433 |  | 745.4068 | 2568.3624 | 71.0358 | 2497.3266 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00059775 | 0.00067497 | 0.00076271 | 0.00086243 | 0.00097582 | 0.0011048 | 0.0012515 | 0.0014185 | 0.0016087 | 0.0018253 | 0.002072 | 0.0023532 | 0.0026737 | 0.0030391 | 0.0034558 | 0.0039312 | 0.0044736 | 0.0050926 | 0.0057991 | 0.0066057 | 0.0075268 | 0.0085787 | 0.0097803 | 0.011153 | 0.012722 | 0.014514 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 841.0907 | 949.7554 | 1073.2129 | 1213.5321 | 1373.0765 | 1554.5459 | 1761.0249 | 1996.0388 | 2263.6163 | 2568.3624 | 2915.542 | 3311.1742 | 3762.1423 | 4276.3178 | 4862.7039 | 5531.5992 | 6294.7849 | 7165.7403 | 8159.888 | 9294.8765 | 10590.9028 | 12071.0824 | 13761.8728 | 15693.5595 | 17900.8117 | 20423.3202 | 22722.6185 | 22722.6185 | 22722.6185 | 22722.6185 |  | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 43.9044 | 52.5508 | 69.6592 | 93.1437 | 125.5261 | 170.3599 | 232.662 | 319.5268 | 441.0002 | 611.326 | 850.7234 | 1187.9235 | 1663.7894 | 2336.4871 |  | 312.0551 | 352.3711 | 398.1753 | 450.2355 | 509.4285 | 576.7559 | 653.3622 | 740.5552 | 839.8298 | 952.8944 | 1081.7024 | 1228.4869 | 1395.8016 | 1586.5671 | 1804.1237 | 2052.2922 | 2335.4436 | 2658.5789 | 3027.42 | 3448.5149 | 3929.3568 | 4478.5218 | 5105.8261 | 5822.5059 | 6641.424 | 7577.3061 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 284.9234 | 325.2394 | 371.0437 | 423.1038 | 482.2968 | 549.6242 | 626.2305 | 713.4236 | 812.6981 | 925.7627 | 1054.5707 | 1201.3552 | 1368.6699 | 1559.4354 | 1776.992 | 2025.1605 | 2308.3119 | 2626.1039 | 2984.3726 | 3390.9546 | 3851.7851 | 4373.2441 | 4962.0474 | 5625.0471 | 6368.898 | 7199.5234 | 7904.6507 | 7696.2703 | 7402.1983 | 6986.4896 |  | 263.0087 | 296.9882 | 335.5933 | 379.471 | 429.3605 | 486.1059 | 550.6718 | 624.1606 | 707.832 | 803.126 | 911.6889 | 1035.4029 | 1176.4205 | 1337.203 | 1520.5657 | 1729.729 | 1968.3769 | 2240.7243 | 2551.5939 | 2906.5044 | 3311.7714 | 3774.623 | 4303.3325 | 4907.3702 | 5597.5772 | 6386.3646 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 262.9875 | 296.967 | 335.5721 | 379.4498 | 429.3393 | 486.0847 | 550.6506 | 624.1394 | 707.8107 | 803.1048 | 911.6677 | 1035.3817 | 1176.3993 | 1337.1818 | 1520.5445 | 1729.7078 | 1968.3557 | 2240.6989 | 2551.5603 | 2906.4594 | 3311.7107 | 3774.5407 | 4303.2201 | 4907.2158 | 5597.3641 | 6386.0693 | 7104.9433 | 7104.7804 | 7104.5505 | 7104.2255 |  | 547.911 | 622.2064 | 706.6157 | 802.5537 | 911.6361 | 1035.7089 | 1176.8811 | 1337.5629 | 1520.5089 | 1728.8675 | 1966.2384 | 2236.7369 | 2545.0692 | 2896.6172 | 3297.5365 | 3754.8683 | 4276.6676 | 4866.8028 | 5535.9329 | 6297.4141 | 7163.4959 | 8147.7848 | 9265.2675 | 10532.263 | 11966.2621 | 13585.5927 | 15009.594 | 14801.0507 | 14506.7488 | 14090.7151 |  | 87.5862 | 98.9019 | 111.7581 | 126.3701 | 142.9841 | 161.8812 | 183.3827 | 207.8557 | 235.7196 | 267.4541 | 303.6073 | 344.8061 | 391.7673 | 445.3105 | 506.3733 | 576.0281 | 655.5017 | 746.1979 | 849.7226 | 967.9136 | 1102.8741 | 1257.0113 | 1433.0802 | 1634.2347 | 1864.0849 | 2126.764 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 72.9162 | 84.2319 | 97.088 | 111.7 | 128.314 | 147.2112 | 168.7127 | 193.1856 | 221.0496 | 252.784 | 288.9373 | 330.1361 | 377.0972 | 430.6404 | 491.7032 | 561.358 | 640.8317 | 728.6388 | 826.4469 | 936.7908 | 1060.9312 | 1200.0878 | 1355.3393 | 1527.469 | 1716.7305 | 1922.4976 | 2081.9414 | 1969.2705 | 1810.2663 | 1585.4933 |  | 11.8728 | 13.4068 | 15.1495 | 17.1302 | 19.3824 | 21.944 | 24.8587 | 28.1761 | 31.9532 | 36.255 | 41.1558 | 46.7406 | 53.1065 | 60.3646 | 68.642 | 78.0841 | 88.8573 | 101.1517 | 115.1851 | 131.2066 | 149.5013 | 170.3956 | 194.2628 | 221.5305 | 252.6881 | 288.2959 | 320.7528 | 320.7528 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 9.8052 | 11.3391 | 13.0818 | 15.0625 | 17.3147 | 19.8763 | 22.791 | 26.1084 | 29.8855 | 34.1873 | 39.0881 | 44.6729 | 51.0388 | 58.2969 | 66.5743 | 76.0164 | 86.7896 | 98.6768 | 111.9045 | 126.82 | 143.5896 | 162.3724 | 183.3055 | 206.4823 | 231.919 | 259.5053 | 280.6877 | 264.8071 | 242.396 | 210.7151 |  | 166.5678 | 188.0875 | 212.5367 | 240.3252 | 271.9211 | 307.8589 | 348.7495 | 395.2912 | 448.2816 | 508.6329 | 577.3875 | 655.7377 | 745.0464 | 846.8726 | 962.9992 | 1095.4658 | 1246.6054 | 1419.0875 | 1615.9663 | 1840.737 | 2097.3992 | 2390.5307 | 2725.3712 | 3107.9182 | 3545.0376 | 4044.5896 | 4499.9376 | 4499.9376 | 4499.9376 | 4499.9376 |  | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.013433 | 0.016079 | 0.021314 | 0.028499 | 0.038407 | 0.052125 | 0.071188 | 0.097766 | 0.13493 | 0.18705 | 0.2603 | 0.36347 | 0.50907 | 0.7149 |  | 166.5543 | 188.0741 | 212.5233 | 240.3118 | 271.9076 | 307.8454 | 348.7361 | 395.2777 | 448.2682 | 508.6194 | 577.3741 | 655.7243 | 745.033 | 846.8592 | 962.9858 | 1095.4524 | 1246.592 | 1419.0714 | 1615.945 | 1840.7085 | 2097.3608 | 2390.4786 | 2725.3 | 3107.8204 | 3544.9026 | 4044.4026 | 4499.6773 | 4499.5741 | 4499.4285 | 4499.2227 |  | 797.1866 | 905.8514 | 1029.3088 | 1169.628 | 1329.1724 | 1510.6418 | 1717.1209 | 1952.1347 | 2219.7122 | 2524.4583 | 2871.6379 | 3267.2701 | 3718.2382 | 4232.4137 | 4818.7998 | 5487.6951 | 6250.8808 | 7113.1898 | 8090.2292 | 9201.7333 | 10465.3775 | 11900.7236 | 13529.2122 | 15374.0346 | 17459.8143 | 19811.9981 | 21871.9004 | 21534.7025 | 21058.8396 | 20386.1462
| TRUE | 1897 | 22001687 | GCY | Blank | 22 | TRANS NO.2 | DIFFERENTIAL | X | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.066046 | 2190 |  | 8.25 | 0.026286 | 0.0045837 | 0.021702 | 280.8119 | 2016.8282 | 2297.64 | 100.6375 | 10.5627 | 1277.2904 |  | 13.0142 | 0.090569 | 0.015794 | 0.074776 | 967.5611 | 6949.1524 | 7916.7135 | 346.7551 | 36.3947 | 4401.0124 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.13029 |  | 3686.1307 | 12700.8756 | 71.34 | 12629.5357 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0051721 | 0.0058403 | 0.0065995 | 0.0074623 | 0.0084434 | 0.0095593 | 0.010829 | 0.012274 | 0.01392 | 0.015794 | 0.017928 | 0.020361 | 0.023134 | 0.026296 | 0.029902 | 0.034015 | 0.038708 | 0.044064 | 0.050177 | 0.057157 | 0.065126 | 0.074228 | 0.084625 | 0.096504 | 0.11008 | 0.12559 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 4159.2994 | 4696.6603 | 5307.1729 | 6001.0692 | 6790.0363 | 7687.4251 | 8708.4901 | 9870.6633 | 11193.8674 | 12700.8756 | 14417.7222 | 16374.1736 | 18604.2674 | 21146.9299 | 24046.6831 | 27354.4545 | 31128.5042 | 35435.488 | 40351.6736 | 45964.3348 | 52373.3482 | 59693.0225 | 68054.1941 | 77606.6279 | 88521.7683 | 100995.8906 | 112366.21 | 112366.21 | 112366.21 | 112366.21 |  | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 44.2108 | 52.9175 | 70.1453 | 93.7938 | 126.4021 | 171.5488 | 234.2857 | 321.7568 | 444.0779 | 615.5923 | 856.6605 | 1196.2139 | 1675.4008 | 2352.7932 |  | 316.8582 | 357.7947 | 404.3039 | 457.1654 | 517.2694 | 585.6331 | 663.4185 | 751.9536 | 852.7562 | 967.5611 | 1098.3516 | 1247.3954 | 1417.2854 | 1610.9871 | 1831.8922 | 2083.8804 | 2371.39 | 2699.4989 | 3074.0171 | 3501.5934 | 3989.8362 | 4547.4539 | 5184.4134 | 5912.1241 | 6743.6467 | 7693.9336 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 289.7263 | 330.6628 | 377.172 | 430.0335 | 490.1375 | 558.5012 | 636.2866 | 724.8217 | 825.6243 | 940.4292 | 1071.2197 | 1220.2634 | 1390.1535 | 1583.8552 | 1804.7603 | 2056.7485 | 2344.2581 | 2667.0237 | 3030.9693 | 3444.0326 | 3912.2639 | 4442.1753 | 5040.6335 | 5714.6637 | 6471.1185 | 7316.1479 | 8034.4041 | 7826.022 | 7531.9476 | 7116.2356 |  | 2275.7176 | 2569.729 | 2903.7646 | 3283.4228 | 3715.0979 | 4206.0949 | 4764.7601 | 5400.6311 | 6124.6085 | 6949.1524 | 7888.5072 | 8958.9593 | 10179.132 | 11570.3234 | 13156.8933 | 14966.7061 | 17031.6383 | 19388.1598 | 22077.9998 | 25148.9092 | 28655.5344 | 32660.4183 | 37235.1466 | 42461.6617 | 48433.7676 | 55258.8543 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 2275.5118 | 2569.5233 | 2903.5589 | 3283.2171 | 3714.8922 | 4205.8892 | 4764.5543 | 5400.4253 | 6124.4028 | 6948.9467 | 7888.3015 | 8958.7535 | 10178.9262 | 11570.1177 | 13156.6876 | 14966.5004 | 17031.4326 | 19387.9136 | 22077.6734 | 25148.4727 | 28654.9462 | 32659.62 | 37234.0564 | 42460.1645 | 48431.7012 | 55255.9897 | 61476.0203 | 61474.4402 | 61472.2104 | 61469.0582 |  | 2565.2381 | 2900.186 | 3280.7309 | 3713.2506 | 4205.0297 | 4764.3904 | 5400.8409 | 6125.2471 | 6950.0271 | 7889.3759 | 8959.5212 | 10179.017 | 11569.0797 | 13153.9729 | 14961.4479 | 17023.2489 | 19375.6907 | 22054.9372 | 25108.6427 | 28592.5053 | 32567.2101 | 37101.7953 | 42274.6899 | 48174.8282 | 54902.8197 | 62572.1376 | 69510.4244 | 69300.4622 | 69004.158 | 68585.2938 |  | 113.5558 | 128.2266 | 144.8947 | 163.8392 | 185.3793 | 209.8795 | 237.7563 | 269.4855 | 305.6112 | 346.7551 | 393.6278 | 447.0422 | 507.9275 | 577.3464 | 656.5145 | 746.8222 | 849.86 | 967.4478 | 1101.6679 | 1254.9029 | 1429.8796 | 1629.7189 | 1857.9928 | 2118.7902 | 2416.7917 | 2757.356 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 98.8834 | 113.5542 | 130.2222 | 149.1667 | 170.7069 | 195.2071 | 223.0838 | 254.8131 | 290.9388 | 332.0826 | 378.9554 | 432.3698 | 493.255 | 562.674 | 641.8421 | 732.1497 | 835.1876 | 949.8858 | 1078.3884 | 1223.7751 | 1387.9299 | 1572.7862 | 1780.2393 | 2012.0072 | 2269.4134 | 2553.0564 | 2783.4806 | 2670.7914 | 2511.7613 | 2286.9518 |  | 11.9186 | 13.4584 | 15.2079 | 17.1962 | 19.457 | 22.0285 | 24.9544 | 28.2847 | 32.0763 | 36.3947 | 41.3144 | 46.9207 | 53.3111 | 60.5971 | 68.9065 | 78.385 | 89.1996 | 101.5414 | 115.6289 | 131.7121 | 150.0773 | 171.0521 | 195.0112 | 222.384 | 253.6617 | 289.4066 | 321.9886 | 321.9886 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 9.8509 | 11.3907 | 13.1402 | 15.1285 | 17.3893 | 19.9608 | 22.8867 | 26.217 | 30.0087 | 34.327 | 39.2467 | 44.853 | 51.2434 | 58.5294 | 66.8388 | 76.3173 | 87.1319 | 99.0665 | 112.3482 | 127.3255 | 144.1656 | 163.0289 | 184.0539 | 207.3357 | 232.8925 | 260.6159 | 281.9234 | 266.0428 | 243.6317 | 211.9507 |  | 1441.2493 | 1627.4516 | 1839.0018 | 2079.4456 | 2352.8325 | 2663.789 | 3017.6008 | 3420.3084 | 3878.8152 | 4401.0124 | 4995.9212 | 5673.8561 | 6446.6115 | 7327.6759 | 8332.4767 | 9478.6608 | 10786.4163 | 12278.8401 | 13982.3599 | 15927.2173 | 18148.0206 | 20684.3794 | 23581.63 | 26891.6679 | 30673.9006 | 34996.3401 | 38936.2981 | 38936.2981 | 38936.2981 | 38936.2981 |  | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.13029 | 0.15595 | 0.20672 | 0.27642 | 0.37251 | 0.50556 | 0.69045 | 0.94824 | 1.3087 | 1.8142 | 2.5246 | 3.5253 | 4.9375 | 6.9338 |  | 1441.119 | 1627.3213 | 1838.8715 | 2079.3153 | 2352.7023 | 2663.6587 | 3017.4705 | 3420.1781 | 3878.6849 | 4400.8821 | 4995.7909 | 5673.7258 | 6446.4812 | 7327.5456 | 8332.3464 | 9478.5305 | 10786.286 | 12278.6841 | 13982.1532 | 15926.9409 | 18147.6481 | 20683.8738 | 23580.9395 | 26890.7196 | 30672.5919 | 34994.5259 | 38933.7735 | 38932.7728 | 38931.3606 | 38929.3643 |  | 4115.0914 | 4652.4522 | 5262.9648 | 5956.8612 | 6745.8282 | 7643.217 | 8664.282 | 9826.4552 | 11149.6594 | 12656.6676 | 14373.5141 | 16329.9655 | 18560.0593 | 21102.7219 | 24002.4751 | 27310.2464 | 31084.2961 | 35382.5737 | 40281.5326 | 45870.5468 | 52246.9538 | 59521.4842 | 67819.9227 | 77284.8908 | 88077.7176 | 100380.3358 | 111509.6018 | 111170.0692 | 110690.9115 | 110013.5605
| TRUE | 1898 | 22001690 | GCY | Blank | 66 | CB A | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 275.999 | 0 | 275.999 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 950.9779 | 0 | 950.9779 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 361.1306 | 1244.3062 | 71.0008 | 1173.3054 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407.487 | 460.1323 | 519.9443 | 587.9254 | 665.2206 | 753.1379 | 853.1717 | 967.03 | 1096.6644 | 1244.3062 | 1412.5058 | 1604.1796 | 1822.6621 | 2071.7671 | 2355.8562 | 2679.919 | 3049.663 | 3471.6187 | 3953.258 | 4503.131 | 5131.0228 | 5848.1321 | 6667.277 | 7603.13 | 8672.4875 | 9894.5787 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 311.4275 | 351.6624 | 397.3745 | 449.33 | 508.4039 | 575.5958 | 652.0481 | 739.0658 | 838.1407 | 950.9779 | 1079.5267 | 1226.016 | 1392.9943 | 1583.3761 | 1800.4951 | 2048.1644 | 2330.7463 | 2653.2317 | 3021.331 | 3441.5789 | 3921.4537 | 4469.5142 | 5095.5568 | 5810.7952 | 6628.0662 | 7562.0659 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 284.2958 | 324.5307 | 370.2428 | 422.1983 | 481.2722 | 548.4642 | 624.9164 | 711.9341 | 811.009 | 923.8462 | 1052.3951 | 1198.8844 | 1365.8626 | 1556.2444 | 1773.3634 | 2021.0327 | 2303.6147 | 2620.7568 | 2978.2836 | 3384.0187 | 3843.8821 | 4364.2366 | 4951.7782 | 5613.3366 | 6355.5404 | 7184.2836 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 284.2958 | 324.5307 | 370.2428 | 422.1983 | 481.2722 | 548.4642 | 624.9164 | 711.9341 | 811.009 | 923.8462 | 1052.3951 | 1198.8844 | 1365.8626 | 1556.2444 | 1773.3634 | 2021.0327 | 2303.6147 | 2620.7568 | 2978.2836 | 3384.0187 | 3843.8821 | 4364.2366 | 4951.7782 | 5613.3366 | 6355.5404 | 7184.2836 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 363.6179 | 416.2632 | 476.0752 | 544.0563 | 621.3515 | 709.2687 | 809.3026 | 923.1608 | 1052.7953 | 1200.4371 | 1368.6367 | 1560.3105 | 1778.793 | 2027.8979 | 2311.9871 | 2636.0498 | 3005.7939 | 3419.1101 | 3883.6547 | 4410.062 | 5005.5974 | 5677.9089 | 6434.8016 | 7283.8595 | 8231.8411 | 9283.7431 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| TRUE | 1899 | 22001691 | GCY | Blank | 66 | CB B | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 275.999 | 0 | 275.999 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 950.9779 | 0 | 950.9779 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 361.1306 | 1244.3062 | 71.0008 | 1173.3054 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407.487 | 460.1323 | 519.9443 | 587.9254 | 665.2206 | 753.1379 | 853.1717 | 967.03 | 1096.6644 | 1244.3062 | 1412.5058 | 1604.1796 | 1822.6621 | 2071.7671 | 2355.8562 | 2679.919 | 3049.663 | 3471.6187 | 3953.258 | 4503.131 | 5131.0228 | 5848.1321 | 6667.277 | 7603.13 | 8672.4875 | 9894.5787 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 311.4275 | 351.6624 | 397.3745 | 449.33 | 508.4039 | 575.5958 | 652.0481 | 739.0658 | 838.1407 | 950.9779 | 1079.5267 | 1226.016 | 1392.9943 | 1583.3761 | 1800.4951 | 2048.1644 | 2330.7463 | 2653.2317 | 3021.331 | 3441.5789 | 3921.4537 | 4469.5142 | 5095.5568 | 5810.7952 | 6628.0662 | 7562.0659 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 284.2958 | 324.5307 | 370.2428 | 422.1983 | 481.2722 | 548.4642 | 624.9164 | 711.9341 | 811.009 | 923.8462 | 1052.3951 | 1198.8844 | 1365.8626 | 1556.2444 | 1773.3634 | 2021.0327 | 2303.6147 | 2620.7568 | 2978.2836 | 3384.0187 | 3843.8821 | 4364.2366 | 4951.7782 | 5613.3366 | 6355.5404 | 7184.2836 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 284.2958 | 324.5307 | 370.2428 | 422.1983 | 481.2722 | 548.4642 | 624.9164 | 711.9341 | 811.009 | 923.8462 | 1052.3951 | 1198.8844 | 1365.8626 | 1556.2444 | 1773.3634 | 2021.0327 | 2303.6147 | 2620.7568 | 2978.2836 | 3384.0187 | 3843.8821 | 4364.2366 | 4951.7782 | 5613.3366 | 6355.5404 | 7184.2836 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 363.6179 | 416.2632 | 476.0752 | 544.0563 | 621.3515 | 709.2687 | 809.3026 | 923.1608 | 1052.7953 | 1200.4371 | 1368.6367 | 1560.3105 | 1778.793 | 2027.8979 | 2311.9871 | 2636.0498 | 3005.7939 | 3419.1101 | 3883.6547 | 4410.062 | 5005.5974 | 5677.9089 | 6434.8016 | 7283.8595 | 8231.8411 | 9283.7431 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| TRUE | 1900 | 22001678 | GCY | GCY-ALL | 66 | ALL LINE | EARTH FAULT | X | ASEA | GROUP_2890 | GROUP 2890 | GROUP 2000s | Electronic |  | 0.15703 | 2190 |  | 8.25 | 0.026286 | 0.0092625 | 0.017023 | 285.7247 | 4075.5196 | 4361.2443 | 127.2004 | 10.6095 | 516.2187 |  | 13.0142 | 0.090569 | 0.031915 | 0.058654 | 984.4885 | 14042.5484 | 15027.0369 | 438.2797 | 36.5559 | 1778.6753 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.061955 |  | 5015.2729 | 17280.5479 | 71.5594 | 17208.9885 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.010452 | 0.011802 | 0.013336 | 0.01508 | 0.017062 | 0.019317 | 0.021883 | 0.024803 | 0.028128 | 0.031915 | 0.036229 | 0.041145 | 0.046749 | 0.053138 | 0.060425 | 0.068737 | 0.07822 | 0.089043 | 0.1014 | 0.1155 | 0.1316 | 0.15 | 0.17101 | 0.19501 | 0.22244 | 0.25378 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 5659.0565 | 6390.1786 | 7220.8293 | 8164.9303 | 9238.3825 | 10459.351 | 11848.591 | 13429.8197 | 15230.1438 | 17280.5479 | 19616.4537 | 22278.3608 | 25312.5802 | 28772.0741 | 32717.4182 | 37217.9032 | 42352.797 | 48212.7898 | 54901.6499 | 62538.1203 | 71258.091 | 81217.088 | 92593.1246 | 105589.9678 | 120440.8814 | 137412.9133 | 152883.134 | 152883.134 | 152883.134 | 152883.134 |  | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 53.1842 | 70.4988 | 94.2664 | 127.0391 | 172.4132 | 235.4663 | 323.3782 | 446.3157 | 618.6944 | 860.9773 | 1202.2418 | 1683.8433 | 2364.6492 |  | 322.4016 | 364.0543 | 411.3772 | 465.1635 | 526.319 | 595.8787 | 675.025 | 765.109 | 867.6751 | 984.4885 | 1117.5672 | 1269.2185 | 1442.0807 | 1639.1712 | 1863.941 | 2120.3378 | 2412.8773 | 2746.7264 | 3127.7969 | 3562.8535 | 4059.6382 | 4627.0113 | 5275.1144 | 6015.5564 | 6861.6264 | 7828.5385 | 8709.891 | 8709.891 | 8709.891 | 8709.891 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 295.2693 | 336.922 | 384.245 | 438.0312 | 499.1868 | 568.7465 | 647.8927 | 737.9768 | 840.5429 | 957.3563 | 1090.4349 | 1242.0862 | 1414.9484 | 1612.039 | 1836.8088 | 2093.2055 | 2385.7451 | 2714.2508 | 3084.7485 | 3505.2921 | 3982.0649 | 4521.7314 | 5131.3327 | 5818.0935 | 6589.0948 | 7450.7481 | 8184.1565 | 7975.7719 | 7681.6938 | 7265.9765 |  | 4598.6722 | 5192.7978 | 5867.8027 | 6634.9996 | 7507.3102 | 8499.4957 | 9628.4223 | 10913.363 | 12376.3455 | 14042.5484 | 15940.7562 | 18103.8797 | 20569.5522 | 23380.8121 | 26586.8844 | 30244.0762 | 34416.8024 | 39178.7597 | 44614.2727 | 50819.8344 | 57905.8719 | 65998.7691 | 75243.1834 | 85804.7004 | 97872.8752 | 111664.7168 | 124236.154 | 124236.154 | 124236.154 | 124236.154 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 4598.1831 | 5192.3087 | 5867.3136 | 6634.5105 | 7506.821 | 8499.0066 | 9627.9331 | 10912.8739 | 12375.8564 | 14042.0593 | 15940.267 | 18103.3906 | 20569.0631 | 23380.323 | 26586.3952 | 30243.5871 | 34416.3132 | 39178.1743 | 44613.4967 | 50818.7967 | 57904.4734 | 65996.8711 | 75240.5913 | 85801.1406 | 97867.9621 | 111657.9062 | 124226.6763 | 124222.9196 | 124217.6181 | 124210.1237 |  | 4893.4524 | 5529.2307 | 6251.5585 | 7072.5417 | 8006.0078 | 9067.7531 | 10275.8259 | 11650.8507 | 13216.3993 | 14999.4155 | 17030.702 | 19345.4768 | 21984.0116 | 24992.3619 | 28423.204 | 32336.7926 | 36802.0583 | 41892.4251 | 47698.2452 | 54324.0887 | 61886.5383 | 70518.6025 | 80371.9241 | 91619.2341 | 104457.0569 | 119108.6543 | 132410.8328 | 132198.6915 | 131899.3119 | 131476.1003 |  | 143.5284 | 162.0716 | 183.139 | 207.0839 | 234.3095 | 265.2764 | 300.5111 | 340.6152 | 386.2761 | 438.2797 | 497.5244 | 565.0373 | 641.993 | 729.7348 | 829.799 | 943.943 | 1074.1773 | 1222.802 | 1392.4489 | 1586.1297 | 1807.2909 | 2059.877 | 2348.4029 | 2678.0367 | 3054.6946 | 3485.1496 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 128.8523 | 147.3955 | 168.463 | 192.4078 | 219.6334 | 250.6003 | 285.835 | 325.9391 | 371.6 | 423.6036 | 482.8483 | 550.3612 | 627.3169 | 715.0587 | 815.1229 | 929.2669 | 1059.5012 | 1205.2356 | 1369.1636 | 1554.9941 | 1765.3307 | 2002.9301 | 2270.63 | 2571.2271 | 2907.2796 | 3280.799 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 11.9714 | 13.518 | 15.2752 | 17.2724 | 19.5432 | 22.1261 | 25.065 | 28.41 | 32.2184 | 36.5559 | 41.4974 | 47.1285 | 53.5472 | 60.8656 | 69.2117 | 78.7322 | 89.5947 | 101.9912 | 116.1411 | 132.2955 | 150.7421 | 171.8097 | 195.8751 | 223.3691 | 254.7853 | 290.6886 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 9.9037 | 11.4503 | 13.2075 | 15.2047 | 17.4755 | 20.0584 | 22.9973 | 26.3423 | 30.1507 | 34.4882 | 39.4297 | 45.0608 | 51.4795 | 58.7978 | 67.144 | 76.6645 | 87.527 | 99.5163 | 112.8604 | 127.9089 | 144.8304 | 163.7865 | 184.9177 | 208.3208 | 234.0161 | 261.8978 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 582.4829 | 657.7368 | 743.2352 | 840.4109 | 950.9006 | 1076.5741 | 1219.5676 | 1382.3224 | 1567.6286 | 1778.6753 | 2019.1085 | 2293.0969 | 2605.4071 | 2961.4905 | 3367.5821 | 3830.8141 | 4359.3453 | 4962.5104 | 5650.9904 | 6437.0072 | 7334.548 | 8359.6209 | 9530.5488 | 10868.3052 | 12396.8999 | 14143.8199 | 15736.1594 | 15736.1594 | 15736.1594 | 15736.1594 |  | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.074156 | 0.098298 | 0.13144 | 0.17713 | 0.2404 | 0.32832 | 0.45089 | 0.62231 | 0.86266 | 1.2005 | 1.6763 | 2.3478 | 3.2971 |  | 582.421 | 657.6749 | 743.1732 | 840.3489 | 950.8386 | 1076.5121 | 1219.5056 | 1382.2605 | 1567.5666 | 1778.6134 | 2019.0466 | 2293.0349 | 2605.3451 | 2961.4285 | 3367.5202 | 3830.7521 | 4359.2833 | 4962.4363 | 5650.8921 | 6436.8757 | 7334.3708 | 8359.3805 | 9530.2205 | 10867.8543 | 12396.2776 | 14142.9572 | 15734.9589 | 15734.4831 | 15733.8116 | 15732.8623 |  | 5614.6294 | 6345.7514 | 7176.4022 | 8120.5032 | 9193.9553 | 10414.9239 | 11804.1638 | 13385.3925 | 15185.7167 | 17236.1207 | 19572.0266 | 22233.9337 | 25268.1531 | 28727.647 | 32672.9911 | 37173.4761 | 42308.3699 | 48159.6133 | 54831.1613 | 62443.8675 | 71131.0703 | 81044.6997 | 92357.6922 | 105266.6364 | 119994.6302 | 136794.3083 | 152022.281 | 151681.0659 | 151199.534 | 150518.8264
| TRUE | 1901 | 22009706 | GCY | GCY-GL | 66 | GL LINE | CURRENT DIFF & DEF | Y | Siemens | 7SD522 | 7SD522 | SIEMENS 7SD522 | Digital |  | 0.016937 | 1 |  | 3.4047 | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.0066825 |  | 9.2417 | 0.041791 | 9.696e-07 | 0.04179 | 219.401 | 0.10666 | 219.5076 | 118.6329 | 16.7204 | 0.054038 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.0066825 |  | 43.8898 | 354.9149 | 43.8898 | 311.0252 |  | 0.099856 |  | 3.7623 | 4.1574 | 4.5939 | 5.0764 | 5.6094 | 6.1985 | 6.8494 | 7.5687 | 8.3635 | 9.2417 | 10.2122 | 11.2846 | 12.4696 | 13.7791 | 15.2261 | 16.825 | 18.5918 | 20.5441 | 22.7015 | 25.0854 | 27.7197 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0056413 | 0.0071108 | 0.0090201 | 0.011509 | 0.014763 | 0.01903 | 0.024639 | 0.03203 | 0.041791 | 0.054706 | 0.071825 | 0.094556 | 0.12478 | 0.16503 | 0.21869 | 0.29031 | 0.38601 | 0.51398 | 0.68527 | 0.9147 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.199e-07 | 1.3089e-07 | 1.6498e-07 | 2.0928e-07 | 2.6702e-07 | 3.4252e-07 | 4.4152e-07 | 5.7166e-07 | 7.4314e-07 | 9.696e-07 | 1.2692e-06 | 1.6665e-06 | 2.1938e-06 | 2.8951e-06 | 3.829e-06 | 5.074e-06 | 6.7357e-06 | 8.9559e-06 | 1.1925e-05 | 1.5899e-05 | 2.1222e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 43.8898 | 47.9102 | 60.3901 | 76.6047 | 97.7411 | 125.3775 | 161.6143 | 209.2509 | 272.0218 | 354.9149 | 464.5977 | 609.9908 | 803.0382 | 1059.7441 | 1401.5659 | 1857.29 | 2465.5553 | 3278.2506 | 4365.0887 | 5819.7669 | 7768.2641 | 7998.0908 | 7998.0908 | 7998.0908 | 7998.0908 | 7998.0908 | 7998.0908 | 7998.0908 | 7998.0908 | 7998.0908 |  | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 52.5333 | 69.636 | 93.1128 | 125.4843 | 170.3032 | 232.5846 | 319.4205 | 440.8535 | 611.1226 | 850.4404 | 1187.5283 | 1663.2359 | 2335.7098 |  | 27.1317 | 29.6171 | 37.3319 | 47.3554 | 60.4215 | 77.5057 | 99.9066 | 129.3545 | 168.1582 | 219.401 | 287.2046 | 377.0835 | 496.4214 | 655.1115 | 866.4186 | 1148.1377 | 1524.1546 | 2026.5457 | 2698.4062 | 3597.6577 | 4802.1778 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 0 | 2.4854 | 10.2002 | 20.2237 | 33.2898 | 50.374 | 72.7748 | 102.2228 | 141.0265 | 192.2692 | 260.0728 | 349.9518 | 469.2896 | 627.9798 | 839.2869 | 1121.006 | 1497.0228 | 1994.0707 | 2655.3587 | 3540.0974 | 4724.606 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.013189 | 0.014398 | 0.018148 | 0.023021 | 0.029372 | 0.037677 | 0.048567 | 0.062882 | 0.081746 | 0.10666 | 0.13962 | 0.18331 | 0.24132 | 0.31847 | 0.42119 | 0.55814 | 0.74093 | 0.98515 | 1.3118 | 1.7489 | 2.3345 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015787 | 0.020926 | 0.027982 | 0.03771 | 0.051178 | 0.069894 | 0.09599 | 0.13248 | 0.18365 | 0.25557 | 0.35687 | 0.49982 | 0.70191 |  | 0 | 0.0012082 | 0.0049585 | 0.0098312 | 0.016183 | 0.024488 | 0.035378 | 0.049693 | 0.068556 | 0.093467 | 0.12643 | 0.17012 | 0.22813 | 0.30528 | 0.408 | 0.54495 | 0.72774 | 0.96937 | 1.2908 | 1.7209 | 2.2967 | 2.3523 | 2.3336 | 2.3075 | 2.271 | 2.2199 | 2.148 | 2.0467 | 1.9037 | 1.7016 |  | 0 | 2.4866 | 10.2051 | 20.2335 | 33.3059 | 50.3985 | 72.8102 | 102.2725 | 141.095 | 192.3627 | 260.1993 | 350.1219 | 469.5178 | 628.2851 | 839.6949 | 1121.5509 | 1497.7506 | 1995.0401 | 2656.6495 | 3541.8183 | 4726.9028 | 4841.3263 | 4802.8065 | 4749.1003 | 4673.9965 | 4568.6886 | 4420.6754 | 4212.1934 | 3917.978 | 3502.0667 |  | 14.6705 | 16.0143 | 20.1858 | 25.6057 | 32.6707 | 41.9083 | 54.0207 | 69.9436 | 90.9252 | 118.6329 | 155.2951 | 203.8938 | 268.4213 | 354.2271 | 468.4835 | 620.8125 | 824.1296 | 1095.7788 | 1459.0622 | 1945.2989 | 2596.598 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 0 | 1.3439 | 5.5154 | 10.9352 | 18.0002 | 27.2379 | 39.3503 | 55.2731 | 76.2548 | 103.9624 | 140.6247 | 189.2233 | 253.7508 | 339.5566 | 453.813 | 606.1421 | 809.4591 | 1078.2192 | 1435.7859 | 1914.1753 | 2554.654 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 2.0677 | 2.2571 | 2.845 | 3.6089 | 4.6047 | 5.9067 | 7.6138 | 9.858 | 12.8152 | 16.7204 | 21.8877 | 28.7373 | 37.832 | 49.9257 | 66.0292 | 87.4989 | 116.1549 | 154.4418 | 205.6439 | 274.1753 | 365.971 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0.18941 | 0.77735 | 1.5412 | 2.537 | 3.839 | 5.5461 | 7.7903 | 10.7475 | 14.6527 | 19.82 | 26.6696 | 35.7643 | 47.858 | 63.9615 | 85.4312 | 114.0872 | 151.9669 | 202.3633 | 269.7887 | 360.0593 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.0066825 | 0.0072946 | 0.0091947 | 0.011663 | 0.014882 | 0.019089 | 0.024607 | 0.03186 | 0.041417 | 0.054038 | 0.070737 | 0.092874 | 0.12227 | 0.16135 | 0.2134 | 0.28278 | 0.37539 | 0.49913 | 0.66461 | 0.88609 | 1.1828 | 1.2178 | 1.2178 | 1.2178 | 1.2178 | 1.2178 | 1.2178 | 1.2178 | 1.2178 | 1.2178 |  | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0079985 | 0.010602 | 0.014177 | 0.019106 | 0.02593 | 0.035412 | 0.048633 | 0.067122 | 0.093047 | 0.12948 | 0.18081 | 0.25324 | 0.35562 |  | 0 | 0.00061214 | 0.0025123 | 0.004981 | 0.0081992 | 0.012407 | 0.017924 | 0.025177 | 0.034734 | 0.047355 | 0.064055 | 0.086192 | 0.11558 | 0.15467 | 0.20671 | 0.2761 | 0.36871 | 0.49113 | 0.65401 | 0.87191 | 1.1637 | 1.1918 | 1.1823 | 1.1691 | 1.1506 | 1.1247 | 1.0883 | 1.0369 | 0.96452 | 0.86213 |  | 0 | 4.0205 | 16.5003 | 32.7149 | 53.8513 | 81.4877 | 117.7246 | 165.3611 | 228.1321 | 311.0252 | 420.708 | 566.101 | 759.1485 | 1015.8543 | 1357.6761 | 1813.4003 | 2421.6656 | 3225.7173 | 4295.4527 | 5726.6541 | 7642.7798 | 7827.7876 | 7765.5062 | 7678.6703 | 7557.2373 | 7386.9682 | 7147.6504 | 6810.5625 | 6334.8549 | 5662.381
| TRUE | 1902 | 22001683 | GCY | GCY-GL | 66 | GL LINE | U/G CABLE OIL PRESSURE | X | ASEA | GROUP_3001 | GROUP 3001 | GROUP 3000s | Electronic |  | 0.15703 | 2190 |  | 9.9 | 0.042792 | 0.015079 | 0.027713 | 465.1499 | 6634.8055 | 7099.9554 | 207.0778 | 17.2719 | 840.3863 |  | 16.087 | 0.16393 | 0.057766 | 0.10616 | 1781.9172 | 25416.9129 | 27198.8301 | 793.2832 | 66.166 | 3219.3897 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.061955 |  | 8164.6914 | 31277.669 | 71.5594 | 31206.1096 |  | 0.048548 |  | 10.3925 | 10.9095 | 11.4522 | 12.0218 | 12.6199 | 13.2477 | 13.9067 | 14.5985 | 15.3247 | 16.087 | 16.8873 | 17.7273 | 18.6092 | 19.5349 | 20.5067 | 21.5268 | 22.5976 | 23.7218 | 24.9018 | 26.1406 | 27.4409 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.04881 | 0.055712 | 0.063632 | 0.072723 | 0.083163 | 0.095155 | 0.10893 | 0.12477 | 0.14298 | 0.16393 | 0.18803 | 0.21575 | 0.24767 | 0.28441 | 0.32672 | 0.37545 | 0.43158 | 0.49627 | 0.57081 | 0.65674 | 0.75579 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0172 | 0.019632 | 0.022423 | 0.025626 | 0.029305 | 0.033531 | 0.038386 | 0.043968 | 0.050385 | 0.057766 | 0.066256 | 0.076027 | 0.087273 | 0.10022 | 0.11513 | 0.1323 | 0.15208 | 0.17488 | 0.20114 | 0.23142 | 0.26633 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 9312.8216 | 10629.7456 | 12140.8719 | 13875.4898 | 15867.3669 | 18155.44 | 20784.6135 | 23806.6805 | 27281.3884 | 31277.669 | 35875.0601 | 41165.3482 | 47254.4664 | 54264.6882 | 62337.1621 | 71634.8412 | 82345.8692 | 94687.4937 | 108910.589 | 125304.8855 | 144205.0123 | 152883.134 | 152883.134 | 152883.134 | 152883.134 | 152883.134 | 152883.134 | 152883.134 | 152883.134 | 152883.134 |  | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 44.4336 | 53.1842 | 70.4988 | 94.2664 | 127.0391 | 172.4132 | 235.4663 | 323.3782 | 446.3157 | 618.6944 | 860.9773 | 1202.2418 | 1683.8433 | 2364.6492 |  | 530.5599 | 605.5863 | 691.6765 | 790.4993 | 903.9783 | 1034.3319 | 1184.1183 | 1356.2882 | 1554.2455 | 1781.9172 | 2043.8348 | 2345.2273 | 2692.1299 | 3091.5086 | 3551.4048 | 4081.102 | 4691.319 | 5394.4325 | 6204.7352 | 7138.7332 | 8215.4906 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 503.4277 | 578.454 | 664.5443 | 763.367 | 876.8461 | 1007.1997 | 1156.9861 | 1329.156 | 1527.1132 | 1754.785 | 2016.7025 | 2318.095 | 2664.9976 | 3064.3763 | 3524.2725 | 4053.9697 | 4664.1867 | 5361.9569 | 6161.6869 | 7081.1717 | 8137.9173 | 8604.6112 | 8566.1093 | 8512.4282 | 8437.3594 | 8332.1006 | 8184.1565 | 7975.7719 | 7681.6938 | 7265.9765 |  | 7567.801 | 8637.962 | 9865.9361 | 11275.5243 | 12894.1669 | 14753.5048 | 16890.0282 | 19345.8254 | 22169.4485 | 25416.9129 | 29152.8528 | 33451.8557 | 38400.0054 | 44096.6638 | 50656.5313 | 58212.0273 | 66916.0412 | 76945.1132 | 88503.1093 | 101825.4705 | 117184.1239 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 7567.3119 | 8637.4729 | 9865.447 | 11275.0352 | 12893.6777 | 14753.0156 | 16889.539 | 19345.3363 | 22168.9594 | 25416.4238 | 29152.3636 | 33451.3666 | 38399.5162 | 44096.1747 | 50656.0422 | 58211.5381 | 66915.5521 | 76944.5277 | 88502.3332 | 101824.4328 | 117182.7254 | 124234.2561 | 124233.562 | 124232.5942 | 124231.2409 | 124229.3434 | 124226.6763 | 124222.9196 | 124217.6181 | 124210.1237 |  | 8070.7396 | 9215.9269 | 10529.9913 | 12038.4022 | 13770.5238 | 15760.2153 | 18046.5251 | 20674.4923 | 23696.0726 | 27171.2088 | 31169.0661 | 35769.4616 | 41064.5139 | 47160.551 | 54180.3147 | 62265.5079 | 71579.7388 | 82306.4846 | 94664.0201 | 108905.6045 | 125320.6427 | 132838.8672 | 132799.6713 | 132745.0224 | 132668.6004 | 132561.444 | 132410.8328 | 132198.6915 | 131899.3119 | 131476.1003 |  | 236.1974 | 269.598 | 307.9241 | 351.9186 | 402.4378 | 460.4693 | 527.152 | 603.7995 | 691.9271 | 793.2832 | 909.885 | 1044.0605 | 1198.4964 | 1376.2939 | 1581.0329 | 1816.8462 | 2088.5058 | 2401.5216 | 2762.2563 | 3178.0584 | 3657.4149 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 221.5213 | 254.9219 | 293.2481 | 337.2425 | 387.7617 | 445.7932 | 512.4759 | 589.1234 | 677.251 | 778.6071 | 895.2089 | 1029.3844 | 1183.8203 | 1361.6178 | 1566.3568 | 1802.1701 | 2073.8297 | 2383.9552 | 2738.9711 | 3146.9229 | 3615.4548 | 3820.5678 | 3799.7417 | 3770.7051 | 3730.0997 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 19.7007 | 22.4866 | 25.6833 | 29.3527 | 33.5664 | 38.4067 | 43.9686 | 50.3616 | 57.7121 | 66.166 | 75.8915 | 87.0828 | 99.9639 | 114.7936 | 131.8704 | 151.5391 | 174.1976 | 200.3056 | 230.3936 | 265.0748 | 305.0568 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 17.633 | 20.4189 | 23.6156 | 27.285 | 31.4987 | 36.339 | 41.9009 | 48.2939 | 55.6444 | 64.0983 | 73.8238 | 85.0151 | 97.8962 | 112.7259 | 129.8027 | 149.4714 | 172.1299 | 197.8307 | 227.113 | 260.6881 | 299.1451 | 315.3917 | 312.4575 | 308.3665 | 302.6457 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 958.5625 | 1094.1126 | 1249.6519 | 1428.195 | 1633.2175 | 1868.7274 | 2139.3465 | 2450.4058 | 2808.0552 | 3219.3897 | 3692.5961 | 4237.1219 | 4863.8708 | 5585.4283 | 6416.3227 | 7373.3266 | 8475.8056 | 9746.1208 | 11210.0946 | 12897.5486 | 14842.9261 | 15736.1594 | 15736.1594 | 15736.1594 | 15736.1594 | 15736.1594 | 15736.1594 | 15736.1594 | 15736.1594 | 15736.1594 |  | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.074156 | 0.098298 | 0.13144 | 0.17713 | 0.2404 | 0.32832 | 0.45089 | 0.62231 | 0.86266 | 1.2005 | 1.6763 | 2.3478 | 3.2971 |  | 958.5006 | 1094.0507 | 1249.5899 | 1428.133 | 1633.1556 | 1868.6654 | 2139.2845 | 2450.3438 | 2807.9932 | 3219.3277 | 3692.5342 | 4237.06 | 4863.8089 | 5585.3663 | 6416.2607 | 7373.2647 | 8475.7437 | 9746.0467 | 11209.9963 | 12897.4172 | 14842.749 | 15735.919 | 15735.8311 | 15735.7085 | 15735.5371 | 15735.2968 | 15734.9589 | 15734.4831 | 15733.8116 | 15732.8623 |  | 9268.3945 | 10585.3184 | 12096.4448 | 13831.0627 | 15822.9398 | 18111.0129 | 20740.1863 | 23762.2533 | 27236.9612 | 31233.2419 | 35830.633 | 41120.921 | 47210.0393 | 54220.261 | 62292.7349 | 71590.4141 | 82301.4421 | 94634.3172 | 108840.1004 | 125210.6327 | 144077.9916 | 152710.7457 | 152647.7017 | 152559.8026 | 152436.8828 | 152264.529 | 152022.281 | 151681.0659 | 151199.534 | 150518.8264
| TRUE | 1903 | 22009702 | GCY | GCY-GL | 66 | GL LINE | CURRENT DIFF & DEF | X | Schweitzer | SEL_311L | SEL 311L | SEL 300s | Digital |  | 0.15703 | 1 |  | 4.0857 | 0.0054221 | 1.1663e-06 | 0.005421 | 28.4669 | 0.1283 | 28.5952 | 15.398 | 2.1694 | 0.065002 |  | 11.2347 | 0.070957 | 1.5263e-05 | 0.070942 | 372.5341 | 1.679 | 374.213 | 201.5073 | 28.3902 | 0.85066 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.061955 |  | 46.2276 | 604.9612 | 44.0603 | 560.9009 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0068474 | 0.0087043 | 0.011132 | 0.014316 | 0.018505 | 0.024029 | 0.031333 | 0.041011 | 0.053862 | 0.070957 | 0.093738 | 0.12414 | 0.16478 | 0.21915 | 0.292 | 0.38971 | 0.52087 | 0.69709 | 0.93404 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.4729e-06 | 1.8724e-06 | 2.3946e-06 | 3.0796e-06 | 3.9805e-06 | 5.1688e-06 | 6.7399e-06 | 8.8217e-06 | 1.1586e-05 | 1.5263e-05 | 2.0164e-05 | 2.6704e-05 | 3.5444e-05 | 4.7141e-05 | 6.2812e-05 | 8.3829e-05 | 0.00011204 | 0.00014995 | 0.00020092 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 58.3785 | 74.2105 | 94.9095 | 122.0573 | 157.7669 | 204.8643 | 267.1336 | 349.6469 | 459.2098 | 604.9612 | 799.1839 | 1058.3974 | 1404.8346 | 1868.4356 | 2489.5415 | 3322.535 | 4440.7603 | 5943.176 | 7963.349 | 8029.166 | 8029.166 | 8029.166 | 8029.166 | 8029.166 | 8029.166 | 8029.166 | 8029.166 | 8029.166 | 8029.166 | 8029.166 |  | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 52.7374 | 69.9065 | 93.4745 | 125.9719 | 170.9649 | 233.4883 | 320.6616 | 442.5664 | 613.497 | 853.7447 | 1192.1423 | 1669.6981 | 2344.7848 |  | 35.9494 | 45.6987 | 58.4451 | 75.1627 | 97.1526 | 126.1551 | 164.5004 | 215.312 | 282.7806 | 372.5341 | 492.1361 | 651.7593 | 865.0947 | 1150.5794 | 1533.0554 | 2046.0113 | 2734.6126 | 3659.7977 | 4903.8167 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 8.8171 | 18.5665 | 31.3129 | 48.0304 | 70.0204 | 99.0229 | 137.3682 | 188.1797 | 255.6483 | 345.4018 | 465.0038 | 624.627 | 837.9625 | 1123.4472 | 1505.9232 | 2018.8791 | 2707.4804 | 3627.3221 | 4860.7684 | 4886.7853 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.16202 | 0.20596 | 0.26341 | 0.33875 | 0.43786 | 0.56857 | 0.74139 | 0.97039 | 1.2745 | 1.679 | 2.218 | 2.9374 | 3.8989 | 5.1855 | 6.9093 | 9.2212 | 12.3246 | 16.4943 | 22.101 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0.039738 | 0.083677 | 0.14112 | 0.21647 | 0.31557 | 0.44629 | 0.6191 | 0.84811 | 1.1522 | 1.5567 | 2.0957 | 2.8151 | 3.7766 | 5.0633 | 6.787 | 9.0989 | 12.2023 | 16.348 | 21.907 | 22.0242 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 8.8569 | 18.6502 | 31.454 | 48.2469 | 70.3359 | 99.4691 | 137.9873 | 189.0278 | 256.8005 | 346.9585 | 467.0995 | 627.4422 | 841.7391 | 1128.5105 | 1512.7102 | 2027.978 | 2719.6827 | 3643.67 | 4882.6754 | 4908.8095 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 19.4454 | 24.7189 | 31.6135 | 40.6562 | 52.5508 | 68.2385 | 88.9799 | 116.4643 | 152.9588 | 201.5073 | 266.2012 | 352.543 | 467.9382 | 622.3596 | 829.2446 | 1106.7075 | 1479.1786 | 1979.6202 | 2652.5222 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 4.7693 | 10.0428 | 16.9374 | 25.9801 | 37.8747 | 53.5624 | 74.3038 | 101.7882 | 138.2827 | 186.8312 | 251.5251 | 337.8669 | 453.2621 | 607.6835 | 814.5685 | 1092.0314 | 1464.5025 | 1962.0538 | 2629.237 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.7396 | 3.4826 | 4.454 | 5.728 | 7.4038 | 9.6141 | 12.5363 | 16.4086 | 21.5502 | 28.3902 | 37.5048 | 49.6695 | 65.9274 | 87.6837 | 116.8315 | 155.923 | 208.4002 | 278.9069 | 373.7115 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0.67194 | 1.4149 | 2.3863 | 3.6603 | 5.3361 | 7.5464 | 10.4686 | 14.3409 | 19.4825 | 26.3225 | 35.4371 | 47.6018 | 63.8597 | 85.616 | 114.7638 | 153.8553 | 206.3325 | 276.432 | 370.4309 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.082088 | 0.10435 | 0.13346 | 0.17163 | 0.22184 | 0.28807 | 0.37563 | 0.49165 | 0.64571 | 0.85066 | 1.1238 | 1.4882 | 1.9754 | 2.6273 | 3.5006 | 4.6719 | 6.2443 | 8.3569 | 11.1975 | 11.2901 | 11.2901 | 11.2901 | 11.2901 | 11.2901 | 11.2901 | 11.2901 | 11.2901 | 11.2901 | 11.2901 | 11.2901 |  | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.074156 | 0.098298 | 0.13144 | 0.17713 | 0.2404 | 0.32832 | 0.45089 | 0.62231 | 0.86266 | 1.2005 | 1.6763 | 2.3478 | 3.2971 |  | 0.020133 | 0.042395 | 0.071501 | 0.10967 | 0.15989 | 0.22611 | 0.31367 | 0.4297 | 0.58376 | 0.7887 | 1.0618 | 1.4263 | 1.9134 | 2.5653 | 3.4387 | 4.61 | 6.1824 | 8.2828 | 11.0992 | 11.1587 | 11.113 | 11.0497 | 10.9618 | 10.8392 | 10.6678 | 10.4274 | 10.0896 | 9.6138 | 8.9423 | 7.993 |  | 14.3182 | 30.1503 | 50.8492 | 77.997 | 113.7066 | 160.8041 | 223.0733 | 305.5866 | 415.1495 | 560.9009 | 755.1236 | 1014.3371 | 1360.7743 | 1824.3753 | 2445.4812 | 3278.4747 | 4396.7001 | 5890.4386 | 7893.4425 | 7935.6915 | 7903.1942 | 7858.2012 | 7795.6777 | 7708.5044 | 7586.5997 | 7415.669 | 7175.4214 | 6837.0238 | 6359.4679 | 5684.3812
| TRUE | 1904 | 22009705 | GCY | GCY-GTS | 66 | GTS LINE | CURRENT DIFF & DEF | Y | Siemens | 7SD522 | 7SD522 | SIEMENS 7SD522 | Digital |  | 0.016937 | 1 |  | 3.4047 | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.0066825 |  | 9.2417 | 0.041791 | 9.696e-07 | 0.04179 | 219.401 | 0.10666 | 219.5076 | 118.6329 | 16.7204 | 0.054038 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.0066825 |  | 43.8898 | 354.9149 | 43.8898 | 311.0252 |  | 0.099856 |  | 3.7623 | 4.1574 | 4.5939 | 5.0764 | 5.6094 | 6.1985 | 6.8494 | 7.5687 | 8.3635 | 9.2417 | 10.2122 | 11.2846 | 12.4696 | 13.7791 | 15.2261 | 16.825 | 18.5918 | 20.5441 | 22.7015 | 25.0854 | 27.7197 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0056413 | 0.0071108 | 0.0090201 | 0.011509 | 0.014763 | 0.01903 | 0.024639 | 0.03203 | 0.041791 | 0.054706 | 0.071825 | 0.094556 | 0.12478 | 0.16503 | 0.21869 | 0.29031 | 0.38601 | 0.51398 | 0.68527 | 0.9147 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.199e-07 | 1.3089e-07 | 1.6498e-07 | 2.0928e-07 | 2.6702e-07 | 3.4252e-07 | 4.4152e-07 | 5.7166e-07 | 7.4314e-07 | 9.696e-07 | 1.2692e-06 | 1.6665e-06 | 2.1938e-06 | 2.8951e-06 | 3.829e-06 | 5.074e-06 | 6.7357e-06 | 8.9559e-06 | 1.1925e-05 | 1.5899e-05 | 2.1222e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 43.8898 | 47.9102 | 60.3901 | 76.6047 | 97.7411 | 125.3775 | 161.6143 | 209.2509 | 272.0218 | 354.9149 | 464.5977 | 609.9908 | 803.0382 | 1059.7441 | 1401.5659 | 1857.29 | 2465.5553 | 3278.2506 | 4365.0887 | 5819.7669 | 7768.2641 | 7998.0908 | 7998.0908 | 7998.0908 | 7998.0908 | 7998.0908 | 7998.0908 | 7998.0908 | 7998.0908 | 7998.0908 |  | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 43.8898 | 52.5333 | 69.636 | 93.1128 | 125.4843 | 170.3032 | 232.5846 | 319.4205 | 440.8535 | 611.1226 | 850.4404 | 1187.5283 | 1663.2359 | 2335.7098 |  | 27.1317 | 29.6171 | 37.3319 | 47.3554 | 60.4215 | 77.5057 | 99.9066 | 129.3545 | 168.1582 | 219.401 | 287.2046 | 377.0835 | 496.4214 | 655.1115 | 866.4186 | 1148.1377 | 1524.1546 | 2026.5457 | 2698.4062 | 3597.6577 | 4802.1778 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 0 | 2.4854 | 10.2002 | 20.2237 | 33.2898 | 50.374 | 72.7748 | 102.2228 | 141.0265 | 192.2692 | 260.0728 | 349.9518 | 469.2896 | 627.9798 | 839.2869 | 1121.006 | 1497.0228 | 1994.0707 | 2655.3587 | 3540.0974 | 4724.606 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.013189 | 0.014398 | 0.018148 | 0.023021 | 0.029372 | 0.037677 | 0.048567 | 0.062882 | 0.081746 | 0.10666 | 0.13962 | 0.18331 | 0.24132 | 0.31847 | 0.42119 | 0.55814 | 0.74093 | 0.98515 | 1.3118 | 1.7489 | 2.3345 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015787 | 0.020926 | 0.027982 | 0.03771 | 0.051178 | 0.069894 | 0.09599 | 0.13248 | 0.18365 | 0.25557 | 0.35687 | 0.49982 | 0.70191 |  | 0 | 0.0012082 | 0.0049585 | 0.0098312 | 0.016183 | 0.024488 | 0.035378 | 0.049693 | 0.068556 | 0.093467 | 0.12643 | 0.17012 | 0.22813 | 0.30528 | 0.408 | 0.54495 | 0.72774 | 0.96937 | 1.2908 | 1.7209 | 2.2967 | 2.3523 | 2.3336 | 2.3075 | 2.271 | 2.2199 | 2.148 | 2.0467 | 1.9037 | 1.7016 |  | 0 | 2.4866 | 10.2051 | 20.2335 | 33.3059 | 50.3985 | 72.8102 | 102.2725 | 141.095 | 192.3627 | 260.1993 | 350.1219 | 469.5178 | 628.2851 | 839.6949 | 1121.5509 | 1497.7506 | 1995.0401 | 2656.6495 | 3541.8183 | 4726.9028 | 4841.3263 | 4802.8065 | 4749.1003 | 4673.9965 | 4568.6886 | 4420.6754 | 4212.1934 | 3917.978 | 3502.0667 |  | 14.6705 | 16.0143 | 20.1858 | 25.6057 | 32.6707 | 41.9083 | 54.0207 | 69.9436 | 90.9252 | 118.6329 | 155.2951 | 203.8938 | 268.4213 | 354.2271 | 468.4835 | 620.8125 | 824.1296 | 1095.7788 | 1459.0622 | 1945.2989 | 2596.598 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 0 | 1.3439 | 5.5154 | 10.9352 | 18.0002 | 27.2379 | 39.3503 | 55.2731 | 76.2548 | 103.9624 | 140.6247 | 189.2233 | 253.7508 | 339.5566 | 453.813 | 606.1421 | 809.4591 | 1078.2192 | 1435.7859 | 1914.1753 | 2554.654 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 2.0677 | 2.2571 | 2.845 | 3.6089 | 4.6047 | 5.9067 | 7.6138 | 9.858 | 12.8152 | 16.7204 | 21.8877 | 28.7373 | 37.832 | 49.9257 | 66.0292 | 87.4989 | 116.1549 | 154.4418 | 205.6439 | 274.1753 | 365.971 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0.18941 | 0.77735 | 1.5412 | 2.537 | 3.839 | 5.5461 | 7.7903 | 10.7475 | 14.6527 | 19.82 | 26.6696 | 35.7643 | 47.858 | 63.9615 | 85.4312 | 114.0872 | 151.9669 | 202.3633 | 269.7887 | 360.0593 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.0066825 | 0.0072946 | 0.0091947 | 0.011663 | 0.014882 | 0.019089 | 0.024607 | 0.03186 | 0.041417 | 0.054038 | 0.070737 | 0.092874 | 0.12227 | 0.16135 | 0.2134 | 0.28278 | 0.37539 | 0.49913 | 0.66461 | 0.88609 | 1.1828 | 1.2178 | 1.2178 | 1.2178 | 1.2178 | 1.2178 | 1.2178 | 1.2178 | 1.2178 | 1.2178 |  | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0066825 | 0.0079985 | 0.010602 | 0.014177 | 0.019106 | 0.02593 | 0.035412 | 0.048633 | 0.067122 | 0.093047 | 0.12948 | 0.18081 | 0.25324 | 0.35562 |  | 0 | 0.00061214 | 0.0025123 | 0.004981 | 0.0081992 | 0.012407 | 0.017924 | 0.025177 | 0.034734 | 0.047355 | 0.064055 | 0.086192 | 0.11558 | 0.15467 | 0.20671 | 0.2761 | 0.36871 | 0.49113 | 0.65401 | 0.87191 | 1.1637 | 1.1918 | 1.1823 | 1.1691 | 1.1506 | 1.1247 | 1.0883 | 1.0369 | 0.96452 | 0.86213 |  | 0 | 4.0205 | 16.5003 | 32.7149 | 53.8513 | 81.4877 | 117.7246 | 165.3611 | 228.1321 | 311.0252 | 420.708 | 566.101 | 759.1485 | 1015.8543 | 1357.6761 | 1813.4003 | 2421.6656 | 3225.7173 | 4295.4527 | 5726.6541 | 7642.7798 | 7827.7876 | 7765.5062 | 7678.6703 | 7557.2373 | 7386.9682 | 7147.6504 | 6810.5625 | 6334.8549 | 5662.381
| TRUE | 1905 | 22009700 | GCY | GCY-GTS | 66 | GTS LINE | CURRENT DIFF & DEF | X | Schweitzer | SEL_311L | SEL 311L | SEL 300s | Digital |  | 0.15703 | 1 |  | 4.0857 | 0.0054221 | 1.1663e-06 | 0.005421 | 28.4669 | 0.1283 | 28.5952 | 15.398 | 2.1694 | 0.065002 |  | 11.2347 | 0.070957 | 1.5263e-05 | 0.070942 | 372.5341 | 1.679 | 374.213 | 201.5073 | 28.3902 | 0.85066 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.061955 |  | 46.2276 | 604.9612 | 44.0603 | 560.9009 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0068474 | 0.0087043 | 0.011132 | 0.014316 | 0.018505 | 0.024029 | 0.031333 | 0.041011 | 0.053862 | 0.070957 | 0.093738 | 0.12414 | 0.16478 | 0.21915 | 0.292 | 0.38971 | 0.52087 | 0.69709 | 0.93404 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.4729e-06 | 1.8724e-06 | 2.3946e-06 | 3.0796e-06 | 3.9805e-06 | 5.1688e-06 | 6.7399e-06 | 8.8217e-06 | 1.1586e-05 | 1.5263e-05 | 2.0164e-05 | 2.6704e-05 | 3.5444e-05 | 4.7141e-05 | 6.2812e-05 | 8.3829e-05 | 0.00011204 | 0.00014995 | 0.00020092 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 58.3785 | 74.2105 | 94.9095 | 122.0573 | 157.7669 | 204.8643 | 267.1336 | 349.6469 | 459.2098 | 604.9612 | 799.1839 | 1058.3974 | 1404.8346 | 1868.4356 | 2489.5415 | 3322.535 | 4440.7603 | 5943.176 | 7963.349 | 8029.166 | 8029.166 | 8029.166 | 8029.166 | 8029.166 | 8029.166 | 8029.166 | 8029.166 | 8029.166 | 8029.166 | 8029.166 |  | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 44.0603 | 52.7374 | 69.9065 | 93.4745 | 125.9719 | 170.9649 | 233.4883 | 320.6616 | 442.5664 | 613.497 | 853.7447 | 1192.1423 | 1669.6981 | 2344.7848 |  | 35.9494 | 45.6987 | 58.4451 | 75.1627 | 97.1526 | 126.1551 | 164.5004 | 215.312 | 282.7806 | 372.5341 | 492.1361 | 651.7593 | 865.0947 | 1150.5794 | 1533.0554 | 2046.0113 | 2734.6126 | 3659.7977 | 4903.8167 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 8.8171 | 18.5665 | 31.3129 | 48.0304 | 70.0204 | 99.0229 | 137.3682 | 188.1797 | 255.6483 | 345.4018 | 465.0038 | 624.627 | 837.9625 | 1123.4472 | 1505.9232 | 2018.8791 | 2707.4804 | 3627.3221 | 4860.7684 | 4886.7853 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.16202 | 0.20596 | 0.26341 | 0.33875 | 0.43786 | 0.56857 | 0.74139 | 0.97039 | 1.2745 | 1.679 | 2.218 | 2.9374 | 3.8989 | 5.1855 | 6.9093 | 9.2212 | 12.3246 | 16.4943 | 22.101 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0.039738 | 0.083677 | 0.14112 | 0.21647 | 0.31557 | 0.44629 | 0.6191 | 0.84811 | 1.1522 | 1.5567 | 2.0957 | 2.8151 | 3.7766 | 5.0633 | 6.787 | 9.0989 | 12.2023 | 16.348 | 21.907 | 22.0242 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 8.8569 | 18.6502 | 31.454 | 48.2469 | 70.3359 | 99.4691 | 137.9873 | 189.0278 | 256.8005 | 346.9585 | 467.0995 | 627.4422 | 841.7391 | 1128.5105 | 1512.7102 | 2027.978 | 2719.6827 | 3643.67 | 4882.6754 | 4908.8095 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 19.4454 | 24.7189 | 31.6135 | 40.6562 | 52.5508 | 68.2385 | 88.9799 | 116.4643 | 152.9588 | 201.5073 | 266.2012 | 352.543 | 467.9382 | 622.3596 | 829.2446 | 1106.7075 | 1479.1786 | 1979.6202 | 2652.5222 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 4.7693 | 10.0428 | 16.9374 | 25.9801 | 37.8747 | 53.5624 | 74.3038 | 101.7882 | 138.2827 | 186.8312 | 251.5251 | 337.8669 | 453.2621 | 607.6835 | 814.5685 | 1092.0314 | 1464.5025 | 1962.0538 | 2629.237 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.7396 | 3.4826 | 4.454 | 5.728 | 7.4038 | 9.6141 | 12.5363 | 16.4086 | 21.5502 | 28.3902 | 37.5048 | 49.6695 | 65.9274 | 87.6837 | 116.8315 | 155.923 | 208.4002 | 278.9069 | 373.7115 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0.67194 | 1.4149 | 2.3863 | 3.6603 | 5.3361 | 7.5464 | 10.4686 | 14.3409 | 19.4825 | 26.3225 | 35.4371 | 47.6018 | 63.8597 | 85.616 | 114.7638 | 153.8553 | 206.3325 | 276.432 | 370.4309 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.082088 | 0.10435 | 0.13346 | 0.17163 | 0.22184 | 0.28807 | 0.37563 | 0.49165 | 0.64571 | 0.85066 | 1.1238 | 1.4882 | 1.9754 | 2.6273 | 3.5006 | 4.6719 | 6.2443 | 8.3569 | 11.1975 | 11.2901 | 11.2901 | 11.2901 | 11.2901 | 11.2901 | 11.2901 | 11.2901 | 11.2901 | 11.2901 | 11.2901 | 11.2901 |  | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.061955 | 0.074156 | 0.098298 | 0.13144 | 0.17713 | 0.2404 | 0.32832 | 0.45089 | 0.62231 | 0.86266 | 1.2005 | 1.6763 | 2.3478 | 3.2971 |  | 0.020133 | 0.042395 | 0.071501 | 0.10967 | 0.15989 | 0.22611 | 0.31367 | 0.4297 | 0.58376 | 0.7887 | 1.0618 | 1.4263 | 1.9134 | 2.5653 | 3.4387 | 4.61 | 6.1824 | 8.2828 | 11.0992 | 11.1587 | 11.113 | 11.0497 | 10.9618 | 10.8392 | 10.6678 | 10.4274 | 10.0896 | 9.6138 | 8.9423 | 7.993 |  | 14.3182 | 30.1503 | 50.8492 | 77.997 | 113.7066 | 160.8041 | 223.0733 | 305.5866 | 415.1495 | 560.9009 | 755.1236 | 1014.3371 | 1360.7743 | 1824.3753 | 2445.4812 | 3278.4747 | 4396.7001 | 5890.4386 | 7893.4425 | 7935.6915 | 7903.1942 | 7858.2012 | 7795.6777 | 7708.5044 | 7586.5997 | 7415.669 | 7175.4214 | 6837.0238 | 6359.4679 | 5684.3812
| TRUE | 2929 | 22004019 | MLN | Blank | 22 | BUS ALL | OV-UV SUPERVISION | C | RPL | GROUP_2506 | GROUP 2506 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 12.8738 | 0.087882 | 0 | 0.087882 | 483.3526 | 0 | 483.3526 | 249.4641 | 35.1617 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 767.9784 | 45.1611 | 722.8173 |  | 0.044498 |  | 8.6254 | 9.0179 | 9.4282 | 9.8572 | 10.3058 | 10.7747 | 11.265 | 11.7776 | 12.3135 | 12.8738 | 13.4595 | 14.072 | 14.7123 | 15.3818 | 16.0817 | 16.8134 | 17.5785 | 18.3783 | 19.2146 | 20.0889 | 21.003 | 21.9587 | 22.9579 | 24.0025 | 25.0947 | 26.2366 | 27.4304 | 28 | 28 | 28 |  | 0.029574 | 0.033298 | 0.037515 | 0.042294 | 0.047711 | 0.053853 | 0.06082 | 0.068725 | 0.077697 | 0.087882 | 0.09945 | 0.11259 | 0.12752 | 0.14449 | 0.16378 | 0.18571 | 0.21065 | 0.23903 | 0.27131 | 0.30805 | 0.34986 | 0.39746 | 0.45166 | 0.51338 | 0.58367 | 0.66374 | 0.75496 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258.4418 | 290.9808 | 327.8366 | 369.5976 | 416.9336 | 470.6076 | 531.4885 | 600.566 | 678.9677 | 767.9784 | 869.062 | 983.8871 | 1114.3555 | 1262.6351 | 1431.1974 | 1622.8605 | 1840.8377 | 2088.7936 | 2370.9075 | 2691.9464 | 3057.3481 | 3473.3156 | 3946.9262 | 4486.2544 | 5100.5136 | 5800.2172 | 6597.3633 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 162.6589 | 183.1384 | 206.3348 | 232.6185 | 262.411 | 296.1925 | 334.5099 | 377.9861 | 427.3308 | 483.3526 | 546.9729 | 619.2419 | 701.3565 | 794.6811 | 900.7714 | 1021.4009 | 1158.5921 | 1314.6513 | 1492.2091 | 1694.2655 | 1924.2431 | 2186.0461 | 2484.1286 | 2823.5726 | 3210.1769 | 3650.5586 | 4152.2688 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.4471 | 168.9266 | 192.123 | 218.4066 | 248.1991 | 281.9806 | 320.298 | 363.7743 | 413.119 | 469.1408 | 532.7611 | 605.0301 | 687.1447 | 780.4693 | 886.5596 | 1007.1891 | 1144.3803 | 1297.6407 | 1469.6604 | 1664.1149 | 1883.6104 | 2130.9007 | 2408.816 | 2720.1419 | 3067.4253 | 3452.6726 | 3876.89 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.4471 | 168.9266 | 192.123 | 218.4066 | 248.1991 | 281.9806 | 320.298 | 363.7743 | 413.119 | 469.1408 | 532.7611 | 605.0301 | 687.1447 | 780.4693 | 886.5596 | 1007.1891 | 1144.3803 | 1297.6407 | 1469.6604 | 1664.1149 | 1883.6104 | 2130.9007 | 2408.816 | 2720.1419 | 3067.4253 | 3452.6726 | 3876.89 | 4022.4983 | 3868.4608 | 3650.7088 |  | 83.9502 | 94.5199 | 106.4919 | 120.0572 | 135.4334 | 152.8685 | 172.6446 | 195.0832 | 220.5506 | 249.4641 | 282.2993 | 319.5982 | 361.9785 | 410.1445 | 464.8989 | 527.1573 | 597.9633 | 678.5073 | 770.147 | 874.4308 | 993.125 | 1128.2446 | 1282.0886 | 1457.2797 | 1656.8108 | 1884.0971 | 2143.0358 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.2804 | 79.8501 | 91.8221 | 105.3874 | 120.7637 | 138.1987 | 157.9748 | 180.4134 | 205.8808 | 234.7943 | 267.6295 | 304.9284 | 347.3087 | 395.4747 | 450.2292 | 512.4875 | 583.2935 | 660.9485 | 746.8718 | 843.3086 | 951.1829 | 1071.3222 | 1204.3491 | 1350.5161 | 1509.4592 | 1679.8345 | 1858.7832 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8327 | 13.3225 | 15.0099 | 16.9219 | 19.0892 | 21.5467 | 24.3341 | 27.4968 | 31.0864 | 35.1617 | 39.7898 | 45.047 | 51.0205 | 57.8094 | 65.527 | 74.3023 | 84.2823 | 95.6349 | 108.5514 | 123.2501 | 139.9799 | 159.0249 | 180.7091 | 205.4021 | 233.5258 | 265.5615 | 302.0587 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.765 | 11.2548 | 12.9422 | 14.8542 | 17.0215 | 19.479 | 22.2664 | 25.4291 | 29.0187 | 33.094 | 37.7221 | 42.9793 | 48.9528 | 55.7417 | 63.4593 | 72.2346 | 82.2146 | 93.16 | 105.2708 | 118.8635 | 134.0682 | 151.0018 | 169.7518 | 190.3538 | 212.7567 | 236.7709 | 261.9936 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 227.4925 | 260.0315 | 296.8873 | 338.6483 | 385.9843 | 439.6583 | 500.5392 | 569.6167 | 648.0184 | 737.0291 | 838.1127 | 952.9378 | 1083.4062 | 1231.6858 | 1400.2481 | 1591.9112 | 1809.8884 | 2051.7492 | 2321.803 | 2626.287 | 2968.8615 | 3353.2247 | 3782.9168 | 4261.0118 | 4789.6413 | 5369.278 | 5997.6667 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 2930 | 22004020 | MLN | Blank | 22 | BUS ALL | BATTERY UV & BUS NV | C | EMAIL | GROUP_2655 | GROUP 2655 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 12.8738 | 0.087882 | 0 | 0.087882 | 483.3526 | 0 | 483.3526 | 249.4641 | 35.1617 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 767.9784 | 45.1611 | 722.8173 |  | 0.044498 |  | 8.6254 | 9.0179 | 9.4282 | 9.8572 | 10.3058 | 10.7747 | 11.265 | 11.7776 | 12.3135 | 12.8738 | 13.4595 | 14.072 | 14.7123 | 15.3818 | 16.0817 | 16.8134 | 17.5785 | 18.3783 | 19.2146 | 20.0889 | 21.003 | 21.9587 | 22.9579 | 24.0025 | 25.0947 | 26.2366 | 27.4304 | 28 | 28 | 28 |  | 0.029574 | 0.033298 | 0.037515 | 0.042294 | 0.047711 | 0.053853 | 0.06082 | 0.068725 | 0.077697 | 0.087882 | 0.09945 | 0.11259 | 0.12752 | 0.14449 | 0.16378 | 0.18571 | 0.21065 | 0.23903 | 0.27131 | 0.30805 | 0.34986 | 0.39746 | 0.45166 | 0.51338 | 0.58367 | 0.66374 | 0.75496 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258.4418 | 290.9808 | 327.8366 | 369.5976 | 416.9336 | 470.6076 | 531.4885 | 600.566 | 678.9677 | 767.9784 | 869.062 | 983.8871 | 1114.3555 | 1262.6351 | 1431.1974 | 1622.8605 | 1840.8377 | 2088.7936 | 2370.9075 | 2691.9464 | 3057.3481 | 3473.3156 | 3946.9262 | 4486.2544 | 5100.5136 | 5800.2172 | 6597.3633 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 162.6589 | 183.1384 | 206.3348 | 232.6185 | 262.411 | 296.1925 | 334.5099 | 377.9861 | 427.3308 | 483.3526 | 546.9729 | 619.2419 | 701.3565 | 794.6811 | 900.7714 | 1021.4009 | 1158.5921 | 1314.6513 | 1492.2091 | 1694.2655 | 1924.2431 | 2186.0461 | 2484.1286 | 2823.5726 | 3210.1769 | 3650.5586 | 4152.2688 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.4471 | 168.9266 | 192.123 | 218.4066 | 248.1991 | 281.9806 | 320.298 | 363.7743 | 413.119 | 469.1408 | 532.7611 | 605.0301 | 687.1447 | 780.4693 | 886.5596 | 1007.1891 | 1144.3803 | 1297.6407 | 1469.6604 | 1664.1149 | 1883.6104 | 2130.9007 | 2408.816 | 2720.1419 | 3067.4253 | 3452.6726 | 3876.89 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.4471 | 168.9266 | 192.123 | 218.4066 | 248.1991 | 281.9806 | 320.298 | 363.7743 | 413.119 | 469.1408 | 532.7611 | 605.0301 | 687.1447 | 780.4693 | 886.5596 | 1007.1891 | 1144.3803 | 1297.6407 | 1469.6604 | 1664.1149 | 1883.6104 | 2130.9007 | 2408.816 | 2720.1419 | 3067.4253 | 3452.6726 | 3876.89 | 4022.4983 | 3868.4608 | 3650.7088 |  | 83.9502 | 94.5199 | 106.4919 | 120.0572 | 135.4334 | 152.8685 | 172.6446 | 195.0832 | 220.5506 | 249.4641 | 282.2993 | 319.5982 | 361.9785 | 410.1445 | 464.8989 | 527.1573 | 597.9633 | 678.5073 | 770.147 | 874.4308 | 993.125 | 1128.2446 | 1282.0886 | 1457.2797 | 1656.8108 | 1884.0971 | 2143.0358 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.2804 | 79.8501 | 91.8221 | 105.3874 | 120.7637 | 138.1987 | 157.9748 | 180.4134 | 205.8808 | 234.7943 | 267.6295 | 304.9284 | 347.3087 | 395.4747 | 450.2292 | 512.4875 | 583.2935 | 660.9485 | 746.8718 | 843.3086 | 951.1829 | 1071.3222 | 1204.3491 | 1350.5161 | 1509.4592 | 1679.8345 | 1858.7832 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8327 | 13.3225 | 15.0099 | 16.9219 | 19.0892 | 21.5467 | 24.3341 | 27.4968 | 31.0864 | 35.1617 | 39.7898 | 45.047 | 51.0205 | 57.8094 | 65.527 | 74.3023 | 84.2823 | 95.6349 | 108.5514 | 123.2501 | 139.9799 | 159.0249 | 180.7091 | 205.4021 | 233.5258 | 265.5615 | 302.0587 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.765 | 11.2548 | 12.9422 | 14.8542 | 17.0215 | 19.479 | 22.2664 | 25.4291 | 29.0187 | 33.094 | 37.7221 | 42.9793 | 48.9528 | 55.7417 | 63.4593 | 72.2346 | 82.2146 | 93.16 | 105.2708 | 118.8635 | 134.0682 | 151.0018 | 169.7518 | 190.3538 | 212.7567 | 236.7709 | 261.9936 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 227.4925 | 260.0315 | 296.8873 | 338.6483 | 385.9843 | 439.6583 | 500.5392 | 569.6167 | 648.0184 | 737.0291 | 838.1127 | 952.9378 | 1083.4062 | 1231.6858 | 1400.2481 | 1591.9112 | 1809.8884 | 2051.7492 | 2321.803 | 2626.287 | 2968.8615 | 3353.2247 | 3782.9168 | 4261.0118 | 4789.6413 | 5369.278 | 5997.6667 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 2931 | 22010531 | MLN | Blank | 22 | BUS NO.1 | BUS PROT | X | ABB | RADHA_3110 | RADHA 3110 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 81.7572 | 388.9293 | 470.6866 | 49.6875 | 5.9058 | 1351.1962 |  | 9.9406 | 0.043268 | 0.0040813 | 0.039187 | 240.22 | 1142.7562 | 1382.9762 | 145.9922 | 17.3524 | 3970.0988 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.2313 |  | 1877.476 | 5516.4197 | 45.4605 | 5470.9592 |  | 0.040956 |  | 6.8759 | 7.1634 | 7.4628 | 7.7748 | 8.0999 | 8.4385 | 8.7913 | 9.1588 | 9.5417 | 9.9406 | 10.3562 | 10.7891 | 11.2402 | 11.7101 | 12.1996 | 12.7097 | 13.241 | 13.7946 | 14.3713 | 14.9721 | 15.598 | 16.2501 | 16.9294 | 17.6372 | 18.3745 | 19.1427 | 19.943 | 20.7767 | 21.6453 | 22.5502 |  | 0.016353 | 0.018172 | 0.020209 | 0.022489 | 0.025043 | 0.027904 | 0.031112 | 0.034708 | 0.038742 | 0.043268 | 0.048348 | 0.05405 | 0.060454 | 0.067647 | 0.075729 | 0.084812 | 0.095022 | 0.1065 | 0.11941 | 0.13394 | 0.15027 | 0.16866 | 0.18936 | 0.21265 | 0.23889 | 0.26843 | 0.3017 | 0.33918 | 0.3814 | 0.42899 |  | 0.0015424 | 0.0017141 | 0.0019062 | 0.0021213 | 0.0023622 | 0.0026321 | 0.0029346 | 0.0032739 | 0.0036544 | 0.0040813 | 0.0045604 | 0.0050983 | 0.0057023 | 0.0063808 | 0.0071431 | 0.0079999 | 0.0089629 | 0.010046 | 0.011264 | 0.012633 | 0.014175 | 0.015909 | 0.017861 | 0.020059 | 0.022533 | 0.025319 | 0.028458 | 0.031993 | 0.035976 | 0.040464 | 2084.8382 | 2316.8247 | 2576.4654 | 2867.171 | 3192.7821 | 3557.6231 | 3966.5646 | 4425.0932 | 4939.39 | 5516.4197 | 6164.0308 | 6891.0695 | 7707.5068 | 8624.5839 | 9654.9747 | 10812.9706 | 12114.6882 | 13578.3045 | 15224.3225 | 17075.8707 | 19159.0422 | 21503.2769 | 24141.7939 | 27112.0793 | 30456.4384 | 34222.618 | 38464.511 | 43242.9513 | 48626.6129 | 54693.0248 |  | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 37.4035 | 49.5805 | 66.2959 | 89.3443 | 121.2551 | 165.5992 | 227.426 | 313.8858 | 435.1166 | 605.5098 | 845.515 | 1184.2166 | 1663.0151 |  | 90.7871 | 100.8893 | 112.1957 | 124.8548 | 139.034 | 154.9215 | 172.7294 | 192.6967 | 215.0924 | 240.22 | 268.4211 | 300.0809 | 335.6338 | 375.5692 | 420.4389 | 470.8654 | 527.5505 | 591.2856 | 662.9637 | 743.5919 | 834.3064 | 936.3893 | 1051.287 | 1180.6321 | 1326.2668 | 1490.2702 | 1674.9891 | 1883.0728 | 2117.5116 | 2381.6817 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 76.5752 | 86.6774 | 97.9838 | 110.6429 | 124.8221 | 140.7096 | 158.5175 | 178.4848 | 200.8805 | 226.0081 | 254.2092 | 285.869 | 321.4219 | 361.3573 | 406.227 | 456.6535 | 513.3386 | 574.2749 | 640.415 | 713.4411 | 793.6735 | 881.2436 | 975.9741 | 1077.201 | 1183.5145 | 1292.3833 | 1399.609 | 1498.5407 | 1578.9412 | 1625.3583 |  | 431.8855 | 479.9428 | 533.7288 | 593.95 | 661.4021 | 736.9809 | 821.6954 | 916.682 | 1023.2214 | 1142.7562 | 1276.9124 | 1427.5224 | 1596.6518 | 1786.6293 | 2000.0803 | 2239.9655 | 2509.6233 | 2812.8194 | 3153.8009 | 3537.3592 | 3968.8994 | 4454.5204 | 5001.1034 | 5616.4142 | 6309.2163 | 7089.4008 | 7968.1319 | 8958.0117 | 10073.2664 | 11329.9565 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 431.819 | 479.8762 | 533.6622 | 593.8834 | 661.3355 | 736.9143 | 821.6288 | 916.6155 | 1023.1548 | 1142.6897 | 1276.8458 | 1427.4558 | 1596.5852 | 1786.5627 | 2000.0138 | 2239.8989 | 2509.5567 | 2812.7397 | 3153.6953 | 3537.2179 | 3968.7091 | 4454.262 | 5000.7506 | 5615.9296 | 6308.5475 | 7088.4738 | 7966.8419 | 8956.2103 | 10070.7434 | 11326.4134 |  | 508.3942 | 566.5536 | 631.646 | 704.5264 | 786.1577 | 877.6239 | 980.1463 | 1095.1002 | 1224.0354 | 1368.6977 | 1531.055 | 1713.3249 | 1918.0071 | 2147.92 | 2406.2408 | 2696.5524 | 3022.8953 | 3387.0146 | 3794.1102 | 4250.6591 | 4762.3825 | 5335.5056 | 5976.7247 | 6693.1306 | 7492.0621 | 8380.857 | 9366.4509 | 10454.751 | 11649.6846 | 12951.7717 |  | 55.1753 | 61.3148 | 68.1862 | 75.8798 | 84.4971 | 94.1526 | 104.9753 | 117.1102 | 130.7211 | 145.9922 | 163.1313 | 182.3724 | 203.9794 | 228.2499 | 255.5192 | 286.1656 | 320.6156 | 359.3502 | 402.9122 | 451.9134 | 507.0446 | 569.0849 | 638.9133 | 717.522 | 806.0306 | 905.7026 | 1017.9644 | 1144.426 | 1286.9048 | 1447.4526 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 40.5042 | 46.6437 | 53.5151 | 61.2086 | 69.8259 | 79.4815 | 90.3041 | 102.4391 | 116.05 | 131.3211 | 148.4601 | 167.7012 | 189.3083 | 213.5787 | 240.8481 | 271.4945 | 305.9445 | 341.7898 | 379.6348 | 420.7884 | 465.0987 | 512.1572 | 561.1667 | 610.7485 | 658.6654 | 701.4212 | 733.6857 | 747.468 | 730.9309 | 666.6892 |  | 6.5581 | 7.2878 | 8.1045 | 9.019 | 10.0432 | 11.1908 | 12.4772 | 13.9196 | 15.5373 | 17.3524 | 19.3896 | 21.6765 | 24.2447 | 27.1295 | 30.3707 | 34.0132 | 38.1079 | 42.7119 | 47.8896 | 53.7138 | 60.2666 | 67.6406 | 75.9403 | 85.2837 | 95.8037 | 107.6505 | 120.9938 | 136.0249 | 152.9597 | 172.0422 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 4.4904 | 5.2201 | 6.0368 | 6.9513 | 7.9755 | 9.1232 | 10.4095 | 11.8519 | 13.4696 | 15.2847 | 17.3219 | 19.6088 | 22.177 | 25.0618 | 28.303 | 31.9455 | 36.0402 | 40.237 | 44.6089 | 49.3272 | 54.3549 | 59.6175 | 64.983 | 70.2354 | 75.0346 | 78.8599 | 80.9287 | 80.0791 | 74.6029 | 62.0044 |  | 1500.4322 | 1667.39 | 1854.2502 | 2063.4674 | 2297.8057 | 2560.3772 | 2854.6874 | 3184.6847 | 3554.8177 | 3970.0988 | 4436.1766 | 4959.4173 | 5546.9971 | 6207.0061 | 6948.5656 | 7781.9609 | 8718.7909 | 9772.1374 | 10956.7561 | 12289.2924 | 13788.5252 | 15475.6418 | 17374.5497 | 19512.2273 | 21919.1211 | 24629.5939 | 27682.4317 | 31121.416 | 34995.9705 | 39361.8919 |  | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.27685 | 0.36698 | 0.49071 | 0.6613 | 0.8975 | 1.2257 | 1.6833 | 2.3233 | 3.2206 | 4.4818 | 6.2583 | 8.7653 | 12.3092 |  | 1500.2009 | 1667.1587 | 1854.0189 | 2063.2361 | 2297.5744 | 2560.1459 | 2854.4561 | 3184.4534 | 3554.5864 | 3969.8675 | 4435.9453 | 4959.186 | 5546.7658 | 6206.7748 | 6948.3343 | 7781.7296 | 8718.5596 | 9771.8605 | 10956.3891 | 12288.8017 | 13787.8639 | 15474.7443 | 17373.324 | 19510.544 | 21916.7978 | 24626.3732 | 27677.9498 | 31115.1577 | 34987.2052 | 39349.5826 |  | 2053.5896 | 2285.5761 | 2545.2168 | 2835.9224 | 3161.5335 | 3526.3745 | 3935.316 | 4393.8446 | 4908.1414 | 5485.1711 | 6132.7822 | 6859.8209 | 7676.2582 | 8593.3353 | 9623.7261 | 10781.722 | 12083.4396 | 13540.9019 | 15174.7431 | 17009.5764 | 19069.7 | 21382.0246 | 23976.1985 | 26884.6585 | 30142.5598 | 33787.5114 | 37859.0151 | 42397.4559 | 47442.4236 | 53030.0479
| FALSE | 2932 | 22008112 | MLN | Blank | 22 | BUS NO.1 | DISTANCE | Y | Schweitzer | SEL_311A | SEL 311A | SEL 300s | Digital |  | 0.0034106 | 1 |  | 6.6 | 0.017308 | 8.0863e-08 | 0.017308 | 47.5966 | 0.0056604 | 47.6023 | 49.1308 | 6.9249 | 0.07866 |  | 15.598 | 0.17662 | 8.2518e-07 | 0.17662 | 485.7084 | 0.057763 | 485.7661 | 501.3643 | 70.6661 | 0.80271 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 14.2118 | 0.0016901 | 14.2135 | 14.6699 | 2.0677 | 0.023487 |  | 103.7366 | 1058.5992 | 30.9746 | 1027.6246 |  | 0.086007 |  | 7.1928 | 7.8388 | 8.5428 | 9.3101 | 10.1463 | 11.0575 | 12.0507 | 13.133 | 14.3125 | 15.598 | 16.9989 | 18.5257 | 20.1895 | 22.0028 | 23.979 | 26.1326 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021585 | 0.027005 | 0.033883 | 0.042625 | 0.053753 | 0.067937 | 0.086039 | 0.10917 | 0.13875 | 0.17662 | 0.22515 | 0.28739 | 0.36726 | 0.46984 | 0.60168 | 0.7712 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.0085e-07 | 1.2617e-07 | 1.583e-07 | 1.9915e-07 | 2.5114e-07 | 3.1741e-07 | 4.0198e-07 | 5.1004e-07 | 6.4824e-07 | 8.2518e-07 | 1.0519e-06 | 1.3427e-06 | 1.7159e-06 | 2.1951e-06 | 2.8111e-06 | 3.6031e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 129.375 | 161.8572 | 203.0799 | 255.4771 | 322.1747 | 407.1896 | 515.6864 | 654.3093 | 831.6097 | 1058.5992 | 1349.4629 | 1722.4811 | 2201.2197 | 2816.0691 | 3606.2315 | 4622.2904 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 |  | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 37.0747 | 49.1447 | 65.7131 | 88.5589 | 120.1892 | 164.1436 | 225.4269 | 311.1266 | 431.2918 | 600.1872 | 838.0826 | 1173.807 | 1648.3967 |  | 59.3601 | 74.2636 | 93.1775 | 117.2184 | 147.8208 | 186.8275 | 236.6081 | 300.2113 | 381.5606 | 485.7084 | 619.163 | 790.3118 | 1009.9675 | 1292.0738 | 1654.6175 | 2120.8074 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 45.1482 | 60.0518 | 78.9656 | 103.0066 | 133.6089 | 172.6156 | 222.3963 | 285.9995 | 367.3488 | 471.4965 | 604.9511 | 776.1 | 995.7557 | 1277.8619 | 1640.4056 | 2106.5956 | 2575.6296 | 2572.8307 | 2567.2928 | 2559.6908 | 2549.2086 | 2534.696 | 2514.5288 | 2486.4106 | 2447.0898 | 2391.9554 | 2314.4625 | 2205.3109 | 2051.2732 | 1833.5212 |  | 0.0070594 | 0.0088318 | 0.011081 | 0.01394 | 0.01758 | 0.022218 | 0.028139 | 0.035703 | 0.045377 | 0.057763 | 0.073634 | 0.093988 | 0.12011 | 0.15366 | 0.19678 | 0.25222 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 |  | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.002023 | 0.0026816 | 0.0035857 | 0.0048322 | 0.0065582 | 0.0089565 | 0.0123 | 0.016977 | 0.023534 | 0.032749 | 0.04573 | 0.064049 | 0.089945 |  | 0.0053692 | 0.0071416 | 0.009391 | 0.01225 | 0.015889 | 0.020528 | 0.026448 | 0.034012 | 0.043687 | 0.056073 | 0.071944 | 0.092298 | 0.11842 | 0.15197 | 0.19509 | 0.25053 | 0.30631 | 0.30597 | 0.30532 | 0.30441 | 0.30316 | 0.30144 | 0.29904 | 0.2957 | 0.29102 | 0.28446 | 0.27525 | 0.26227 | 0.24395 | 0.21805 |  | 45.1536 | 60.0589 | 78.975 | 103.0189 | 133.6248 | 172.6361 | 222.4228 | 286.0335 | 367.3925 | 471.5526 | 605.0231 | 776.1923 | 995.8741 | 1278.0139 | 1640.6007 | 2106.8461 | 2575.9359 | 2573.1367 | 2567.5981 | 2559.9952 | 2549.5118 | 2534.9974 | 2514.8278 | 2486.7063 | 2447.3808 | 2392.2398 | 2314.7377 | 2205.5732 | 2051.5172 | 1833.7392 |  | 61.2734 | 76.6573 | 96.1809 | 120.9968 | 152.5855 | 192.8495 | 244.2348 | 309.8881 | 393.8595 | 501.3643 | 639.1205 | 815.786 | 1042.5219 | 1333.7214 | 1707.951 | 2189.1677 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 46.6035 | 61.9874 | 81.5109 | 106.3268 | 137.9156 | 178.1796 | 229.5649 | 295.2182 | 379.1896 | 486.6944 | 624.4506 | 801.1161 | 1027.852 | 1319.0515 | 1693.2811 | 2174.4978 | 2658.6503 | 2655.7612 | 2650.0447 | 2642.1978 | 2631.3777 | 2616.3973 | 2595.58 | 2566.5555 | 2525.9672 | 2469.0557 | 2389.0649 | 2276.395 | 2117.3923 | 1892.6214 |  | 8.6363 | 10.8047 | 13.5565 | 17.0542 | 21.5066 | 27.1817 | 34.4243 | 43.678 | 55.5136 | 70.6661 | 90.0826 | 114.9831 | 146.941 | 187.9849 | 240.7317 | 308.5581 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 6.5687 | 8.737 | 11.4888 | 14.9865 | 19.4389 | 25.114 | 32.3566 | 41.6103 | 53.4459 | 68.5984 | 88.0149 | 112.9154 | 144.8733 | 185.9172 | 238.664 | 306.4904 | 374.7306 | 374.3234 | 373.5176 | 372.4116 | 370.8866 | 368.7751 | 365.8409 | 361.75 | 356.0292 | 348.0076 | 336.7331 | 320.8526 | 298.4415 | 266.7606 |  | 0.098101 | 0.12273 | 0.15399 | 0.19372 | 0.2443 | 0.30876 | 0.39103 | 0.49614 | 0.63059 | 0.80271 | 1.0233 | 1.3061 | 1.6691 | 2.1353 | 2.7345 | 3.5049 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 |  | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.028113 | 0.037265 | 0.049828 | 0.067152 | 0.091136 | 0.12447 | 0.17093 | 0.23592 | 0.32704 | 0.4551 | 0.63549 | 0.89006 | 1.2499 |  | 0.074614 | 0.099244 | 0.1305 | 0.17023 | 0.22081 | 0.28527 | 0.36754 | 0.47266 | 0.6071 | 0.77922 | 0.99977 | 1.2826 | 1.6456 | 2.1119 | 2.711 | 3.4815 | 4.2566 | 4.252 | 4.2428 | 4.2303 | 4.2129 | 4.189 | 4.1556 | 4.1092 | 4.0442 | 3.9531 | 3.825 | 3.6446 | 3.39 | 3.0302 |  | 98.4004 | 130.8826 | 172.1052 | 224.5025 | 291.2001 | 376.215 | 484.7118 | 623.3346 | 800.6351 | 1027.6246 | 1318.4883 | 1691.5065 | 2170.2451 | 2785.0945 | 3575.2569 | 4591.3158 | 5613.5733 | 5607.4733 | 5595.4033 | 5578.8348 | 5555.989 | 5524.3587 | 5480.4044 | 5419.1211 | 5333.4214 | 5213.2562 | 5044.3608 | 4806.4654 | 4470.741 | 3996.1513
| TRUE | 2933 | 22010532 | MLN | Blank | 22 | BUS NO.2 | BUS PROT | X | ABB | RADHA_3110 | RADHA 3110 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 81.7572 | 388.9293 | 470.6866 | 49.6875 | 5.9058 | 1351.1962 |  | 9.9406 | 0.043268 | 0.0040813 | 0.039187 | 240.22 | 1142.7562 | 1382.9762 | 145.9922 | 17.3524 | 3970.0988 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.2313 |  | 1877.476 | 5516.4197 | 45.4605 | 5470.9592 |  | 0.040956 |  | 6.8759 | 7.1634 | 7.4628 | 7.7748 | 8.0999 | 8.4385 | 8.7913 | 9.1588 | 9.5417 | 9.9406 | 10.3562 | 10.7891 | 11.2402 | 11.7101 | 12.1996 | 12.7097 | 13.241 | 13.7946 | 14.3713 | 14.9721 | 15.598 | 16.2501 | 16.9294 | 17.6372 | 18.3745 | 19.1427 | 19.943 | 20.7767 | 21.6453 | 22.5502 |  | 0.016353 | 0.018172 | 0.020209 | 0.022489 | 0.025043 | 0.027904 | 0.031112 | 0.034708 | 0.038742 | 0.043268 | 0.048348 | 0.05405 | 0.060454 | 0.067647 | 0.075729 | 0.084812 | 0.095022 | 0.1065 | 0.11941 | 0.13394 | 0.15027 | 0.16866 | 0.18936 | 0.21265 | 0.23889 | 0.26843 | 0.3017 | 0.33918 | 0.3814 | 0.42899 |  | 0.0015424 | 0.0017141 | 0.0019062 | 0.0021213 | 0.0023622 | 0.0026321 | 0.0029346 | 0.0032739 | 0.0036544 | 0.0040813 | 0.0045604 | 0.0050983 | 0.0057023 | 0.0063808 | 0.0071431 | 0.0079999 | 0.0089629 | 0.010046 | 0.011264 | 0.012633 | 0.014175 | 0.015909 | 0.017861 | 0.020059 | 0.022533 | 0.025319 | 0.028458 | 0.031993 | 0.035976 | 0.040464 | 2084.8382 | 2316.8247 | 2576.4654 | 2867.171 | 3192.7821 | 3557.6231 | 3966.5646 | 4425.0932 | 4939.39 | 5516.4197 | 6164.0308 | 6891.0695 | 7707.5068 | 8624.5839 | 9654.9747 | 10812.9706 | 12114.6882 | 13578.3045 | 15224.3225 | 17075.8707 | 19159.0422 | 21503.2769 | 24141.7939 | 27112.0793 | 30456.4384 | 34222.618 | 38464.511 | 43242.9513 | 48626.6129 | 54693.0248 |  | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 31.2493 | 37.4035 | 49.5805 | 66.2959 | 89.3443 | 121.2551 | 165.5992 | 227.426 | 313.8858 | 435.1166 | 605.5098 | 845.515 | 1184.2166 | 1663.0151 |  | 90.7871 | 100.8893 | 112.1957 | 124.8548 | 139.034 | 154.9215 | 172.7294 | 192.6967 | 215.0924 | 240.22 | 268.4211 | 300.0809 | 335.6338 | 375.5692 | 420.4389 | 470.8654 | 527.5505 | 591.2856 | 662.9637 | 743.5919 | 834.3064 | 936.3893 | 1051.287 | 1180.6321 | 1326.2668 | 1490.2702 | 1674.9891 | 1883.0728 | 2117.5116 | 2381.6817 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 76.5752 | 86.6774 | 97.9838 | 110.6429 | 124.8221 | 140.7096 | 158.5175 | 178.4848 | 200.8805 | 226.0081 | 254.2092 | 285.869 | 321.4219 | 361.3573 | 406.227 | 456.6535 | 513.3386 | 574.2749 | 640.415 | 713.4411 | 793.6735 | 881.2436 | 975.9741 | 1077.201 | 1183.5145 | 1292.3833 | 1399.609 | 1498.5407 | 1578.9412 | 1625.3583 |  | 431.8855 | 479.9428 | 533.7288 | 593.95 | 661.4021 | 736.9809 | 821.6954 | 916.682 | 1023.2214 | 1142.7562 | 1276.9124 | 1427.5224 | 1596.6518 | 1786.6293 | 2000.0803 | 2239.9655 | 2509.6233 | 2812.8194 | 3153.8009 | 3537.3592 | 3968.8994 | 4454.5204 | 5001.1034 | 5616.4142 | 6309.2163 | 7089.4008 | 7968.1319 | 8958.0117 | 10073.2664 | 11329.9565 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 431.819 | 479.8762 | 533.6622 | 593.8834 | 661.3355 | 736.9143 | 821.6288 | 916.6155 | 1023.1548 | 1142.6897 | 1276.8458 | 1427.4558 | 1596.5852 | 1786.5627 | 2000.0138 | 2239.8989 | 2509.5567 | 2812.7397 | 3153.6953 | 3537.2179 | 3968.7091 | 4454.262 | 5000.7506 | 5615.9296 | 6308.5475 | 7088.4738 | 7966.8419 | 8956.2103 | 10070.7434 | 11326.4134 |  | 508.3942 | 566.5536 | 631.646 | 704.5264 | 786.1577 | 877.6239 | 980.1463 | 1095.1002 | 1224.0354 | 1368.6977 | 1531.055 | 1713.3249 | 1918.0071 | 2147.92 | 2406.2408 | 2696.5524 | 3022.8953 | 3387.0146 | 3794.1102 | 4250.6591 | 4762.3825 | 5335.5056 | 5976.7247 | 6693.1306 | 7492.0621 | 8380.857 | 9366.4509 | 10454.751 | 11649.6846 | 12951.7717 |  | 55.1753 | 61.3148 | 68.1862 | 75.8798 | 84.4971 | 94.1526 | 104.9753 | 117.1102 | 130.7211 | 145.9922 | 163.1313 | 182.3724 | 203.9794 | 228.2499 | 255.5192 | 286.1656 | 320.6156 | 359.3502 | 402.9122 | 451.9134 | 507.0446 | 569.0849 | 638.9133 | 717.522 | 806.0306 | 905.7026 | 1017.9644 | 1144.426 | 1286.9048 | 1447.4526 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 40.5042 | 46.6437 | 53.5151 | 61.2086 | 69.8259 | 79.4815 | 90.3041 | 102.4391 | 116.05 | 131.3211 | 148.4601 | 167.7012 | 189.3083 | 213.5787 | 240.8481 | 271.4945 | 305.9445 | 341.7898 | 379.6348 | 420.7884 | 465.0987 | 512.1572 | 561.1667 | 610.7485 | 658.6654 | 701.4212 | 733.6857 | 747.468 | 730.9309 | 666.6892 |  | 6.5581 | 7.2878 | 8.1045 | 9.019 | 10.0432 | 11.1908 | 12.4772 | 13.9196 | 15.5373 | 17.3524 | 19.3896 | 21.6765 | 24.2447 | 27.1295 | 30.3707 | 34.0132 | 38.1079 | 42.7119 | 47.8896 | 53.7138 | 60.2666 | 67.6406 | 75.9403 | 85.2837 | 95.8037 | 107.6505 | 120.9938 | 136.0249 | 152.9597 | 172.0422 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 4.4904 | 5.2201 | 6.0368 | 6.9513 | 7.9755 | 9.1232 | 10.4095 | 11.8519 | 13.4696 | 15.2847 | 17.3219 | 19.6088 | 22.177 | 25.0618 | 28.303 | 31.9455 | 36.0402 | 40.237 | 44.6089 | 49.3272 | 54.3549 | 59.6175 | 64.983 | 70.2354 | 75.0346 | 78.8599 | 80.9287 | 80.0791 | 74.6029 | 62.0044 |  | 1500.4322 | 1667.39 | 1854.2502 | 2063.4674 | 2297.8057 | 2560.3772 | 2854.6874 | 3184.6847 | 3554.8177 | 3970.0988 | 4436.1766 | 4959.4173 | 5546.9971 | 6207.0061 | 6948.5656 | 7781.9609 | 8718.7909 | 9772.1374 | 10956.7561 | 12289.2924 | 13788.5252 | 15475.6418 | 17374.5497 | 19512.2273 | 21919.1211 | 24629.5939 | 27682.4317 | 31121.416 | 34995.9705 | 39361.8919 |  | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.27685 | 0.36698 | 0.49071 | 0.6613 | 0.8975 | 1.2257 | 1.6833 | 2.3233 | 3.2206 | 4.4818 | 6.2583 | 8.7653 | 12.3092 |  | 1500.2009 | 1667.1587 | 1854.0189 | 2063.2361 | 2297.5744 | 2560.1459 | 2854.4561 | 3184.4534 | 3554.5864 | 3969.8675 | 4435.9453 | 4959.186 | 5546.7658 | 6206.7748 | 6948.3343 | 7781.7296 | 8718.5596 | 9771.8605 | 10956.3891 | 12288.8017 | 13787.8639 | 15474.7443 | 17373.324 | 19510.544 | 21916.7978 | 24626.3732 | 27677.9498 | 31115.1577 | 34987.2052 | 39349.5826 |  | 2053.5896 | 2285.5761 | 2545.2168 | 2835.9224 | 3161.5335 | 3526.3745 | 3935.316 | 4393.8446 | 4908.1414 | 5485.1711 | 6132.7822 | 6859.8209 | 7676.2582 | 8593.3353 | 9623.7261 | 10781.722 | 12083.4396 | 13540.9019 | 15174.7431 | 17009.5764 | 19069.7 | 21382.0246 | 23976.1985 | 26884.6585 | 30142.5598 | 33787.5114 | 37859.0151 | 42397.4559 | 47442.4236 | 53030.0479
| FALSE | 2934 | 22008113 | MLN | Blank | 22 | BUS NO.2 | DISTANCE | Y | Schweitzer | SEL_311A | SEL 311A | SEL 300s | Digital |  | 0.0034106 | 1 |  | 6.6 | 0.017308 | 8.0863e-08 | 0.017308 | 47.5966 | 0.0056604 | 47.6023 | 49.1308 | 6.9249 | 0.07866 |  | 15.598 | 0.17662 | 8.2518e-07 | 0.17662 | 485.7084 | 0.057763 | 485.7661 | 501.3643 | 70.6661 | 0.80271 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 14.2118 | 0.0016901 | 14.2135 | 14.6699 | 2.0677 | 0.023487 |  | 103.7366 | 1058.5992 | 30.9746 | 1027.6246 |  | 0.086007 |  | 7.1928 | 7.8388 | 8.5428 | 9.3101 | 10.1463 | 11.0575 | 12.0507 | 13.133 | 14.3125 | 15.598 | 16.9989 | 18.5257 | 20.1895 | 22.0028 | 23.979 | 26.1326 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021585 | 0.027005 | 0.033883 | 0.042625 | 0.053753 | 0.067937 | 0.086039 | 0.10917 | 0.13875 | 0.17662 | 0.22515 | 0.28739 | 0.36726 | 0.46984 | 0.60168 | 0.7712 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.0085e-07 | 1.2617e-07 | 1.583e-07 | 1.9915e-07 | 2.5114e-07 | 3.1741e-07 | 4.0198e-07 | 5.1004e-07 | 6.4824e-07 | 8.2518e-07 | 1.0519e-06 | 1.3427e-06 | 1.7159e-06 | 2.1951e-06 | 2.8111e-06 | 3.6031e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 129.375 | 161.8572 | 203.0799 | 255.4771 | 322.1747 | 407.1896 | 515.6864 | 654.3093 | 831.6097 | 1058.5992 | 1349.4629 | 1722.4811 | 2201.2197 | 2816.0691 | 3606.2315 | 4622.2904 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 |  | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 37.0747 | 49.1447 | 65.7131 | 88.5589 | 120.1892 | 164.1436 | 225.4269 | 311.1266 | 431.2918 | 600.1872 | 838.0826 | 1173.807 | 1648.3967 |  | 59.3601 | 74.2636 | 93.1775 | 117.2184 | 147.8208 | 186.8275 | 236.6081 | 300.2113 | 381.5606 | 485.7084 | 619.163 | 790.3118 | 1009.9675 | 1292.0738 | 1654.6175 | 2120.8074 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 45.1482 | 60.0518 | 78.9656 | 103.0066 | 133.6089 | 172.6156 | 222.3963 | 285.9995 | 367.3488 | 471.4965 | 604.9511 | 776.1 | 995.7557 | 1277.8619 | 1640.4056 | 2106.5956 | 2575.6296 | 2572.8307 | 2567.2928 | 2559.6908 | 2549.2086 | 2534.696 | 2514.5288 | 2486.4106 | 2447.0898 | 2391.9554 | 2314.4625 | 2205.3109 | 2051.2732 | 1833.5212 |  | 0.0070594 | 0.0088318 | 0.011081 | 0.01394 | 0.01758 | 0.022218 | 0.028139 | 0.035703 | 0.045377 | 0.057763 | 0.073634 | 0.093988 | 0.12011 | 0.15366 | 0.19678 | 0.25222 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 |  | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.002023 | 0.0026816 | 0.0035857 | 0.0048322 | 0.0065582 | 0.0089565 | 0.0123 | 0.016977 | 0.023534 | 0.032749 | 0.04573 | 0.064049 | 0.089945 |  | 0.0053692 | 0.0071416 | 0.009391 | 0.01225 | 0.015889 | 0.020528 | 0.026448 | 0.034012 | 0.043687 | 0.056073 | 0.071944 | 0.092298 | 0.11842 | 0.15197 | 0.19509 | 0.25053 | 0.30631 | 0.30597 | 0.30532 | 0.30441 | 0.30316 | 0.30144 | 0.29904 | 0.2957 | 0.29102 | 0.28446 | 0.27525 | 0.26227 | 0.24395 | 0.21805 |  | 45.1536 | 60.0589 | 78.975 | 103.0189 | 133.6248 | 172.6361 | 222.4228 | 286.0335 | 367.3925 | 471.5526 | 605.0231 | 776.1923 | 995.8741 | 1278.0139 | 1640.6007 | 2106.8461 | 2575.9359 | 2573.1367 | 2567.5981 | 2559.9952 | 2549.5118 | 2534.9974 | 2514.8278 | 2486.7063 | 2447.3808 | 2392.2398 | 2314.7377 | 2205.5732 | 2051.5172 | 1833.7392 |  | 61.2734 | 76.6573 | 96.1809 | 120.9968 | 152.5855 | 192.8495 | 244.2348 | 309.8881 | 393.8595 | 501.3643 | 639.1205 | 815.786 | 1042.5219 | 1333.7214 | 1707.951 | 2189.1677 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 46.6035 | 61.9874 | 81.5109 | 106.3268 | 137.9156 | 178.1796 | 229.5649 | 295.2182 | 379.1896 | 486.6944 | 624.4506 | 801.1161 | 1027.852 | 1319.0515 | 1693.2811 | 2174.4978 | 2658.6503 | 2655.7612 | 2650.0447 | 2642.1978 | 2631.3777 | 2616.3973 | 2595.58 | 2566.5555 | 2525.9672 | 2469.0557 | 2389.0649 | 2276.395 | 2117.3923 | 1892.6214 |  | 8.6363 | 10.8047 | 13.5565 | 17.0542 | 21.5066 | 27.1817 | 34.4243 | 43.678 | 55.5136 | 70.6661 | 90.0826 | 114.9831 | 146.941 | 187.9849 | 240.7317 | 308.5581 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 6.5687 | 8.737 | 11.4888 | 14.9865 | 19.4389 | 25.114 | 32.3566 | 41.6103 | 53.4459 | 68.5984 | 88.0149 | 112.9154 | 144.8733 | 185.9172 | 238.664 | 306.4904 | 374.7306 | 374.3234 | 373.5176 | 372.4116 | 370.8866 | 368.7751 | 365.8409 | 361.75 | 356.0292 | 348.0076 | 336.7331 | 320.8526 | 298.4415 | 266.7606 |  | 0.098101 | 0.12273 | 0.15399 | 0.19372 | 0.2443 | 0.30876 | 0.39103 | 0.49614 | 0.63059 | 0.80271 | 1.0233 | 1.3061 | 1.6691 | 2.1353 | 2.7345 | 3.5049 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 |  | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.028113 | 0.037265 | 0.049828 | 0.067152 | 0.091136 | 0.12447 | 0.17093 | 0.23592 | 0.32704 | 0.4551 | 0.63549 | 0.89006 | 1.2499 |  | 0.074614 | 0.099244 | 0.1305 | 0.17023 | 0.22081 | 0.28527 | 0.36754 | 0.47266 | 0.6071 | 0.77922 | 0.99977 | 1.2826 | 1.6456 | 2.1119 | 2.711 | 3.4815 | 4.2566 | 4.252 | 4.2428 | 4.2303 | 4.2129 | 4.189 | 4.1556 | 4.1092 | 4.0442 | 3.9531 | 3.825 | 3.6446 | 3.39 | 3.0302 |  | 98.4004 | 130.8826 | 172.1052 | 224.5025 | 291.2001 | 376.215 | 484.7118 | 623.3346 | 800.6351 | 1027.6246 | 1318.4883 | 1691.5065 | 2170.2451 | 2785.0945 | 3575.2569 | 4591.3158 | 5613.5733 | 5607.4733 | 5595.4033 | 5578.8348 | 5555.989 | 5524.3587 | 5480.4044 | 5419.1211 | 5333.4214 | 5213.2562 | 5044.3608 | 4806.4654 | 4470.741 | 3996.1513
| FALSE | 2935 | 22015508 | MLN | Blank | 22 | BUS NO.3 | HIBP | X | RMS | 2V73 | RMS - 2V73 | RMS 2V73 | Electronic |  | 0.033587 | 2190 |  | 0.91058 | 0.004397 | 0.00041475 | 0.0039823 | 12.2059 | 29.0325 | 41.2384 | 14.8361 | 1.7634 | 403.4524 |  | 3.0201 | 0.004397 | 0.00041475 | 0.0039823 | 12.2059 | 29.0325 | 41.2384 | 14.8361 | 1.7634 | 403.4524 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.2313 |  | 461.2903 | 461.2903 | 31.1987 | 430.0916 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.005263 | 0.0069764 | 0.0093284 | 0.012571 | 0.017062 | 0.023301 | 0.032001 | 0.044166 | 0.061224 | 0.0852 | 0.11897 | 0.16663 | 0.234 | 0.32938 | 0.4646 | 0.65653 | 0.80128 | 0.80128 |  | 0.00041475 | 0.00041475 | 0.00041475 | 0.00041475 | 0.00041475 | 0.00041475 | 0.00041475 | 0.00041475 | 0.00041475 | 0.00041475 | 0.00041475 | 0.00041475 | 0.00049643 | 0.00065805 | 0.0008799 | 0.0011858 | 0.0016093 | 0.0021979 | 0.0030185 | 0.004166 | 0.005775 | 0.0080365 | 0.011222 | 0.015717 | 0.022072 | 0.031069 | 0.043824 | 0.061927 | 0.07558 | 0.07558 | 461.2903 | 461.2903 | 461.2903 | 461.2903 | 461.2903 | 461.2903 | 461.2903 | 461.2903 | 461.2903 | 461.2903 | 461.2903 | 461.2903 | 552.1356 | 731.8884 | 978.634 | 1318.8659 | 1789.9211 | 2444.5118 | 3357.1751 | 4633.4601 | 6423.023 | 8938.3021 | 12481.1647 | 17480.9481 | 24548.7864 | 34555.2255 | 48741.1464 | 68876.3343 | 84061.5647 | 84061.5647 |  | 31.1987 | 31.1987 | 31.1987 | 31.1987 | 31.1987 | 31.1987 | 31.1987 | 31.1987 | 31.1987 | 31.1987 | 31.1987 | 31.1987 | 31.1987 | 31.1987 | 31.1987 | 31.1987 | 31.1987 | 37.3428 | 49.5002 | 66.1884 | 89.1995 | 121.0586 | 165.3308 | 227.0574 | 313.377 | 434.4113 | 604.5284 | 844.1444 | 1182.2971 | 1660.3195 |  | 12.2059 | 12.2059 | 12.2059 | 12.2059 | 12.2059 | 12.2059 | 12.2059 | 12.2059 | 12.2059 | 12.2059 | 12.2059 | 12.2059 | 14.6097 | 19.366 | 25.895 | 34.8977 | 47.362 | 64.6827 | 88.832 | 122.603 | 169.9555 | 236.5107 | 330.2561 | 462.5521 | 649.5696 | 914.3436 | 1289.7081 | 1822.4924 | 2224.299 | 2224.299 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | -2.006 | -2.006 | -2.006 | -2.006 | -2.006 | -2.006 | -2.006 | -2.006 | -2.006 | -2.006 | -2.006 | -2.006 | 0.39781 | 5.1541 | 11.6831 | 20.6858 | 33.1501 | 47.6719 | 66.2833 | 92.4523 | 129.3226 | 181.365 | 254.9431 | 359.1209 | 506.8174 | 716.4567 | 1014.328 | 1437.9603 | 1685.7286 | 1467.9756 |  | 29.0325 | 29.0325 | 29.0325 | 29.0325 | 29.0325 | 29.0325 | 29.0325 | 29.0325 | 29.0325 | 29.0325 | 29.0325 | 29.0325 | 34.7501 | 46.0633 | 61.5929 | 83.0063 | 112.6533 | 153.8517 | 211.2926 | 291.6189 | 404.2497 | 562.5553 | 785.5346 | 1100.209 | 1545.0418 | 2174.8232 | 3067.6511 | 4334.9116 | 5290.6336 | 5290.6336 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019922 | 0.026408 | 0.035311 | 0.047588 | 0.064584 | 0.088203 | 0.12113 | 0.16719 | 0.23176 | 0.32251 | 0.45035 | 0.63075 | 0.88577 |  | 29.0159 | 29.0159 | 29.0159 | 29.0159 | 29.0159 | 29.0159 | 29.0159 | 29.0159 | 29.0159 | 29.0159 | 29.0159 | 29.0159 | 34.7334 | 46.0467 | 61.5762 | 82.9896 | 112.6367 | 153.8318 | 211.2662 | 291.5836 | 404.2021 | 562.4908 | 785.4464 | 1100.0879 | 1544.8747 | 2174.5914 | 3067.3286 | 4334.4612 | 5290.0029 | 5289.7479 |  | 27.0099 | 27.0099 | 27.0099 | 27.0099 | 27.0099 | 27.0099 | 27.0099 | 27.0099 | 27.0099 | 27.0099 | 27.0099 | 27.0099 | 35.1313 | 51.2008 | 73.2594 | 103.6754 | 145.7868 | 201.5037 | 277.5495 | 384.0359 | 533.5247 | 743.8557 | 1040.3895 | 1459.2088 | 2051.6921 | 2891.0481 | 4081.6566 | 5772.4215 | 6975.7315 | 6757.7235 |  | 14.8361 | 14.8361 | 14.8361 | 14.8361 | 14.8361 | 14.8361 | 14.8361 | 14.8361 | 14.8361 | 14.8361 | 14.8361 | 14.8361 | 17.7579 | 23.5392 | 31.4751 | 42.4177 | 57.5679 | 78.621 | 107.9743 | 149.0225 | 206.5788 | 287.4758 | 401.4222 | 562.2265 | 789.544 | 1111.3735 | 1567.6245 | 2215.2173 | 2703.6083 | 2703.6083 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 0.16499 | 0.16499 | 0.16499 | 0.16499 | 0.16499 | 0.16499 | 0.16499 | 0.16499 | 0.16499 | 0.16499 | 0.16499 | 0.16499 | 3.0868 | 8.868 | 16.8039 | 27.7465 | 42.8967 | 61.0605 | 84.6969 | 117.8974 | 164.6329 | 230.5482 | 323.6756 | 455.453 | 642.1788 | 907.0921 | 1283.3457 | 1818.2593 | 2147.6344 | 1922.8449 |  | 1.7634 | 1.7634 | 1.7634 | 1.7634 | 1.7634 | 1.7634 | 1.7634 | 1.7634 | 1.7634 | 1.7634 | 1.7634 | 1.7634 | 2.1107 | 2.7978 | 3.7411 | 5.0417 | 6.8424 | 9.3448 | 12.8337 | 17.7126 | 24.5537 | 34.169 | 47.7125 | 66.8255 | 93.8441 | 132.0963 | 186.3257 | 263.2976 | 321.3471 | 321.3471 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | -0.30429 | -0.30429 | -0.30429 | -0.30429 | -0.30429 | -0.30429 | -0.30429 | -0.30429 | -0.30429 | -0.30429 | -0.30429 | -0.30429 | 0.042988 | 0.73014 | 1.6734 | 2.974 | 4.7747 | 6.8699 | 9.553 | 13.326 | 18.642 | 26.1458 | 36.7552 | 51.7772 | 73.075 | 103.3057 | 146.2605 | 207.3519 | 242.9903 | 211.3093 |  | 403.4524 | 403.4524 | 403.4524 | 403.4524 | 403.4524 | 403.4524 | 403.4524 | 403.4524 | 403.4524 | 403.4524 | 403.4524 | 403.4524 | 482.9072 | 640.1221 | 855.93 | 1153.5026 | 1565.4955 | 2138.0117 | 2936.2425 | 4052.5031 | 5617.6854 | 7817.5913 | 10916.2393 | 15289.135 | 21470.7868 | 30222.589 | 42629.8371 | 60240.4154 | 73521.6766 | 73521.6766 |  | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.2313 | 0.27685 | 0.36698 | 0.49071 | 0.6613 | 0.8975 | 1.2257 | 1.6833 | 2.3233 | 3.2206 | 4.4818 | 6.2583 | 8.7653 | 12.3092 |  | 403.2211 | 403.2211 | 403.2211 | 403.2211 | 403.2211 | 403.2211 | 403.2211 | 403.2211 | 403.2211 | 403.2211 | 403.2211 | 403.2211 | 482.6759 | 639.8908 | 855.6987 | 1153.2713 | 1565.2642 | 2137.7348 | 2935.8755 | 4052.0124 | 5617.0241 | 7816.6938 | 10915.0136 | 15287.4517 | 21468.4635 | 30219.3683 | 42625.3552 | 60234.1571 | 73512.9113 | 73509.3674 |  | 430.0916 | 430.0916 | 430.0916 | 430.0916 | 430.0916 | 430.0916 | 430.0916 | 430.0916 | 430.0916 | 430.0916 | 430.0916 | 430.0916 | 520.9369 | 700.6898 | 947.4353 | 1287.6672 | 1758.7224 | 2407.169 | 3307.6749 | 4567.2717 | 6333.8236 | 8817.2435 | 12315.8339 | 17253.8907 | 24235.4094 | 34120.8142 | 48136.6181 | 68032.1898 | 82879.2675 | 82401.2451
| FALSE | 2936 | 22015513 | MLN | Blank | 22 | BUS NO.3 | SINGLE ZONE BUS DIST | Y | Schweitzer | SEL_311C_1 | SEL 311C | SEL 300s | Digital |  | 0.0034106 | 1 |  | 1.0927 | 0.0051679 | 2.4145e-08 | 0.0051679 | 14.2118 | 0.0016901 | 14.2135 | 14.6699 | 2.0677 | 0.023487 |  | 5.2187 | 0.0096441 | 4.5058e-08 | 0.0096441 | 26.5213 | 0.003154 | 26.5245 | 27.3762 | 3.8586 | 0.04383 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 14.2118 | 0.0016901 | 14.2135 | 14.6699 | 2.0677 | 0.023487 |  | 30.9746 | 57.8032 | 30.9746 | 26.8285 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 2.4145e-08 | 3.1051e-08 | 4.5058e-08 | 6.6302e-08 | 9.8754e-08 | 1.4864e-07 | 2.2574e-07 | 3.4546e-07 | 5.3215e-07 | 8.2428e-07 | 1.2828e-06 | 2.0044e-06 | 3.1425e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 39.8347 | 57.8032 | 85.0564 | 126.6878 | 190.6819 | 289.5888 | 443.1817 | 682.6763 | 1057.4395 | 1645.662 | 2571.3482 | 4031.3821 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 | 5644.5479 |  | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 30.9746 | 37.0747 | 49.1447 | 65.7131 | 88.5589 | 120.1892 | 164.1436 | 225.4269 | 311.1266 | 431.2918 | 600.1872 | 838.0826 | 1173.807 | 1648.3967 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 18.277 | 26.5213 | 39.0257 | 58.1271 | 87.489 | 132.8696 | 203.3414 | 313.2267 | 485.1763 | 755.0655 | 1179.7905 | 1849.6858 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 | 2589.8414 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0652 | 12.3095 | 24.8139 | 43.9153 | 73.2772 | 118.6578 | 189.1296 | 299.0149 | 470.9644 | 738.0548 | 1157.2419 | 1819.5352 | 2549.2086 | 2534.696 | 2514.5288 | 2486.4106 | 2447.0898 | 2391.9554 | 2314.4625 | 2205.3109 | 2051.2732 | 1833.5212 |  | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0021736 | 0.003154 | 0.0046411 | 0.0069128 | 0.010405 | 0.015802 | 0.024182 | 0.03725 | 0.0577 | 0.089796 | 0.14031 | 0.21997 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 |  | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.0016901 | 0.002023 | 0.0026816 | 0.0035857 | 0.0048322 | 0.0065582 | 0.0089565 | 0.0123 | 0.016977 | 0.023534 | 0.032749 | 0.04573 | 0.064049 | 0.089945 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00048346 | 0.0014639 | 0.002951 | 0.0052226 | 0.0087145 | 0.014111 | 0.022492 | 0.03556 | 0.056009 | 0.087773 | 0.13762 | 0.21639 | 0.30316 | 0.30144 | 0.29904 | 0.2957 | 0.29102 | 0.28446 | 0.27525 | 0.26227 | 0.24395 | 0.21805 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0657 | 12.311 | 24.8168 | 43.9205 | 73.2859 | 118.6719 | 189.152 | 299.0505 | 471.0204 | 738.1426 | 1157.3795 | 1819.7516 | 2549.5118 | 2534.9974 | 2514.8278 | 2486.7063 | 2447.3808 | 2392.2398 | 2314.7377 | 2205.5732 | 2051.5172 | 1833.7392 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 18.8662 | 27.3762 | 40.2836 | 60.0007 | 90.309 | 137.1525 | 209.8957 | 323.323 | 500.815 | 779.4037 | 1217.8189 | 1909.307 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1963 | 12.7063 | 25.6137 | 45.3308 | 75.6391 | 122.4825 | 195.2258 | 308.6531 | 486.1451 | 761.8447 | 1194.5434 | 1878.1846 | 2631.3777 | 2616.3973 | 2595.58 | 2566.5555 | 2525.9672 | 2469.0557 | 2389.0649 | 2276.395 | 2117.3923 | 1892.6214 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6591 | 3.8586 | 5.6779 | 8.457 | 12.7288 | 19.3313 | 29.5843 | 45.5716 | 70.5887 | 109.8551 | 171.6487 | 269.1124 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59145 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2636 | 27.5166 | 43.5039 | 68.521 | 107.3802 | 168.3681 | 264.7257 | 370.8866 | 368.7751 | 365.8409 | 361.75 | 356.0292 | 348.0076 | 336.7331 | 320.8526 | 298.4415 | 266.7606 |  | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.030206 | 0.04383 | 0.064496 | 0.096064 | 0.14459 | 0.21959 | 0.33605 | 0.51765 | 0.80183 | 1.2479 | 1.9498 | 3.0569 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 | 4.2801 |  | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.023487 | 0.028113 | 0.037265 | 0.049828 | 0.067152 | 0.091136 | 0.12447 | 0.17093 | 0.23592 | 0.32704 | 0.4551 | 0.63549 | 0.89006 | 1.2499 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0067184 | 0.020343 | 0.041009 | 0.072577 | 0.1211 | 0.1961 | 0.31256 | 0.49417 | 0.77834 | 1.2197 | 1.9125 | 3.0071 | 4.2129 | 4.189 | 4.1556 | 4.1092 | 4.0442 | 3.9531 | 3.825 | 3.6446 | 3.39 | 3.0302 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8601 | 26.8285 | 54.0818 | 95.7132 | 159.7072 | 258.6142 | 412.207 | 651.7016 | 1026.4649 | 1608.5873 | 2522.2036 | 3965.669 | 5555.989 | 5524.3587 | 5480.4044 | 5419.1211 | 5333.4214 | 5213.2562 | 5044.3608 | 4806.4654 | 4470.741 | 3996.1513
| TRUE | 2937 | 22004047 | MLN | Blank | 22 | CAP NO.1 | NEUTRAL BALANCE | X | ASEA | GROUP_2749 | GROUP 2749 | GROUP 2000s | Electronic |  | 0.2894 | 2190 |  | 8.25 | 0.026286 | 0.013817 | 0.012468 | 152.1704 | 3868.8382 | 4021.0086 | 153.0587 | 10.655 | 13440.8983 |  | 12.8738 | 0.087882 | 0.046196 | 0.041686 | 508.7605 | 12934.9209 | 13443.6814 | 511.7303 | 35.6237 | 44937.7683 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.57365 | 28.9984 | 14.6814 | 2.0677 | 1.9929 |  | 17625.6206 | 58928.8037 | 47.7405 | 58881.0632 |  | 0.044498 |  | 8.6254 | 9.0179 | 9.4282 | 9.8572 | 10.3058 | 10.7747 | 11.265 | 11.7776 | 12.3135 | 12.8738 | 13.4595 | 14.072 | 14.7123 | 15.3818 | 16.0817 | 16.8134 | 17.5785 | 18.3783 | 19.2146 | 20.0889 | 21.003 | 21.9587 | 22.9579 | 24.0025 | 25.0947 | 26.2366 | 27.4304 | 28 | 28 | 28 |  | 0.029574 | 0.033298 | 0.037515 | 0.042294 | 0.047711 | 0.053853 | 0.06082 | 0.068725 | 0.077697 | 0.087882 | 0.09945 | 0.11259 | 0.12752 | 0.14449 | 0.16378 | 0.18571 | 0.21065 | 0.23903 | 0.27131 | 0.30805 | 0.34986 | 0.39746 | 0.45166 | 0.51338 | 0.58367 | 0.66374 | 0.75496 | 0.80128 | 0.80128 | 0.80128 |  | 0.015546 | 0.017503 | 0.01972 | 0.022232 | 0.02508 | 0.028308 | 0.031971 | 0.036126 | 0.040842 | 0.046196 | 0.052277 | 0.059184 | 0.067032 | 0.075951 | 0.086091 | 0.09762 | 0.11073 | 0.12565 | 0.14262 | 0.16193 | 0.18391 | 0.20893 | 0.23742 | 0.26986 | 0.30681 | 0.3489 | 0.39685 | 0.4212 | 0.4212 | 0.4212 | 19830.8493 | 22327.6495 | 25155.6825 | 28360.0981 | 31992.303 | 36110.8369 | 40782.3721 | 46082.8543 | 52098.8043 | 58928.8037 | 66685.1901 | 75495.9924 | 85507.1394 | 96884.9811 | 109819.1665 | 124525.9293 | 141251.8386 | 160278.0811 | 181925.3505 | 206559.4294 | 234597.5638 | 266515.7414 | 302857.0025 | 344240.9313 | 391374.4939 | 445064.4165 | 506231.3213 | 537290.8283 | 537290.8283 | 537290.8283 |  | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 40.1385 | 53.2059 | 71.1435 | 95.8773 | 130.1215 | 177.7081 | 244.0558 | 336.8375 | 466.933 | 649.7856 | 907.3402 | 1270.8083 | 1784.6172 |  | 171.2092 | 192.7653 | 217.181 | 244.8463 | 276.2048 | 311.7621 | 352.0937 | 397.8553 | 449.7939 | 508.7605 | 575.7251 | 651.7929 | 738.224 | 836.4543 | 948.1213 | 1075.0918 | 1219.4946 | 1383.7572 | 1570.6484 | 1783.3262 | 2025.3928 | 2300.9576 | 2614.7091 | 2971.9963 | 3378.9229 | 3842.4536 | 4370.5367 | 4638.6883 | 4638.6883 | 4638.6883 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 156.9968 | 178.5529 | 202.9686 | 230.6339 | 261.9924 | 297.5497 | 337.8813 | 383.6429 | 435.5815 | 494.5481 | 561.5127 | 637.5806 | 724.0116 | 822.2419 | 933.9089 | 1060.8794 | 1205.2822 | 1366.7459 | 1548.0989 | 1753.1744 | 1984.7584 | 2245.81 | 2539.3935 | 2868.5615 | 3236.1656 | 3644.5598 | 4095.147 | 4254.1427 | 4100.099 | 3882.3384 |  | 4352.8877 | 4900.9375 | 5521.693 | 6225.0649 | 7022.3369 | 7926.3584 | 8951.7643 | 10115.2245 | 11435.7305 | 12934.9209 | 14637.4542 | 16571.4325 | 18768.8875 | 21266.3331 | 24105.3975 | 27333.544 | 31004.8949 | 35181.1708 | 39932.7643 | 45339.9649 | 51494.3585 | 58500.4247 | 66477.3615 | 75561.1679 | 85907.0237 | 97692.006 | 111118.192 | 117935.7793 | 117935.7793 | 117935.7793 |  | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.68662 | 0.91016 | 1.217 | 1.6401 | 2.2259 | 3.0399 | 4.1749 | 5.7621 | 7.9875 | 11.1155 | 15.5213 | 21.7389 | 30.5284 |  | 4352.3141 | 4900.3638 | 5521.1194 | 6224.4912 | 7021.7632 | 7925.7848 | 8951.1906 | 10114.6508 | 11435.1568 | 12934.3473 | 14636.8805 | 16570.8589 | 18768.3139 | 21265.7595 | 24104.8238 | 27332.9704 | 31004.3213 | 35180.4842 | 39931.8541 | 45338.7479 | 51492.7184 | 58498.1988 | 66474.3215 | 75556.993 | 85901.2617 | 97684.0184 | 111107.0765 | 117920.258 | 117914.0404 | 117905.251 |  | 4509.3109 | 5078.9167 | 5724.088 | 6455.1251 | 7283.7556 | 8223.3345 | 9289.0719 | 10498.2937 | 11870.7383 | 13428.8954 | 15198.3932 | 17208.4394 | 19492.3255 | 22088.0014 | 25038.7328 | 28393.8498 | 32209.6034 | 36547.2301 | 41479.953 | 47091.9222 | 53477.4768 | 60744.0089 | 69013.7151 | 78425.5545 | 89137.4273 | 101328.5782 | 115202.2234 | 122174.4007 | 122014.1394 | 121787.5893 |  | 172.2086 | 193.8905 | 218.4488 | 246.2755 | 277.8171 | 313.582 | 354.149 | 400.1777 | 452.4195 | 511.7303 | 579.0858 | 655.5977 | 742.5333 | 841.337 | 953.6558 | 1081.3675 | 1226.6132 | 1391.8347 | 1579.8169 | 1793.7361 | 2037.2158 | 2314.3892 | 2629.9722 | 2989.345 | 3398.6469 | 3864.8835 | 4396.0492 | 4665.7661 | 4665.7661 | 4665.7661 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 157.5272 | 179.2091 | 203.7674 | 231.5941 | 263.1357 | 298.9006 | 339.4676 | 385.4963 | 437.7381 | 497.0489 | 564.4044 | 640.9163 | 727.8518 | 826.6556 | 938.9744 | 1066.6861 | 1211.9318 | 1374.262 | 1556.5232 | 1762.5893 | 1995.2404 | 2257.4217 | 2552.1711 | 2882.4967 | 3251.1785 | 3660.4589 | 4111.5712 | 4268.5299 | 4109.4026 | 3884.4555 |  | 11.9882 | 13.4975 | 15.2071 | 17.1443 | 19.34 | 21.8297 | 24.6538 | 27.858 | 31.4948 | 35.6237 | 40.3126 | 45.6389 | 51.6908 | 58.569 | 66.3879 | 75.2785 | 85.3896 | 96.8914 | 109.9776 | 124.8694 | 141.819 | 161.1142 | 183.0833 | 208.1007 | 236.5939 | 269.0505 | 306.0272 | 324.8033 | 324.8033 | 324.8033 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 9.9204 | 11.4298 | 13.1394 | 15.0765 | 17.2723 | 19.762 | 22.5861 | 25.7903 | 29.4271 | 33.556 | 38.2448 | 43.5712 | 49.6231 | 56.5012 | 64.3202 | 73.2108 | 83.3219 | 94.4165 | 106.6969 | 120.4827 | 135.9073 | 153.091 | 172.1258 | 193.0523 | 215.8246 | 240.2597 | 265.9617 | 268.8571 | 246.4458 | 214.7645 |  | 15122.5556 | 17026.5588 | 19183.1525 | 21626.7671 | 24396.6042 | 27537.3047 | 31099.7114 | 35141.7388 | 39729.3658 | 44937.7683 | 50852.6125 | 57571.5304 | 65205.8039 | 73882.2877 | 83745.6039 | 94960.6475 | 107715.4463 | 122224.427 | 138732.1433 | 157517.5328 | 178898.7778 | 203238.8556 | 230951.8765 | 262510.3213 | 298453.3064 | 339396.0229 | 386040.5163 | 409725.7914 | 409725.7914 | 409725.7914 |  | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 2.3854 | 3.162 | 4.2281 | 5.698 | 7.7331 | 10.5612 | 14.5042 | 20.0183 | 27.7498 | 38.6168 | 53.9233 | 75.5242 | 106.0599 |  | 15120.5626 | 17024.5658 | 19181.1596 | 21624.7742 | 24394.6112 | 27535.3117 | 31097.7184 | 35139.7459 | 39727.3728 | 44935.7753 | 50850.6196 | 57569.5374 | 65203.8109 | 73880.2948 | 83743.611 | 94958.6545 | 107713.4533 | 122222.0416 | 138728.9813 | 157513.3047 | 178893.0798 | 203231.1225 | 230941.3153 | 262495.8171 | 298433.2882 | 339368.273 | 386001.8995 | 409671.8681 | 409650.2672 | 409619.7315 |  | 19797.3212 | 22294.1214 | 25122.1544 | 28326.5699 | 31958.7749 | 36077.3088 | 40748.844 | 46049.3262 | 52065.2762 | 58895.2756 | 66651.662 | 75462.4643 | 85473.6113 | 96851.453 | 109785.6384 | 124492.4012 | 141218.3105 | 160237.9501 | 181872.1544 | 206488.299 | 234501.7042 | 266385.644 | 302679.3273 | 343996.9206 | 391037.7186 | 444597.5698 | 505581.6558 | 536383.6557 | 536020.2548 | 535506.5409
| TRUE | 2938 | 22004046 | MLN | Blank | 22 | CAP NO.1 | OC & EF | X | GEC | M1AM_3238 | M1AM 3238 | M1AM | Electronic |  | 0.2894 | 2190 |  | 5.5 | 0.0093284 | 0.0049035 | 0.0044248 | 54.003 | 1372.9933 | 1426.9963 | 54.3183 | 3.7813 | 4769.9753 |  | 8.0475 | 0.024619 | 0.012941 | 0.011678 | 142.5215 | 3623.5215 | 3766.043 | 143.3535 | 9.9794 | 12588.6328 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.57365 | 28.9984 | 14.6814 | 2.0677 | 1.9929 |  | 6255.0712 | 16508.0088 | 47.7405 | 16460.2683 |  | 0.038062 |  | 5.7134 | 5.935 | 6.1653 | 6.4045 | 6.6529 | 6.911 | 7.1791 | 7.4577 | 7.747 | 8.0475 | 8.3597 | 8.6841 | 9.021 | 9.3709 | 9.7345 | 10.1121 | 10.5045 | 10.912 | 11.3353 | 11.7751 | 12.2319 | 12.7064 | 13.1994 | 13.7115 | 14.2434 | 14.796 | 15.37 | 15.9663 | 16.5857 | 17.2292 |  | 0.010247 | 0.011264 | 0.012392 | 0.013642 | 0.015029 | 0.016568 | 0.018276 | 0.020172 | 0.022278 | 0.024619 | 0.02722 | 0.030112 | 0.033328 | 0.036906 | 0.040888 | 0.045319 | 0.050253 | 0.055747 | 0.061867 | 0.068685 | 0.076283 | 0.084752 | 0.094194 | 0.10472 | 0.11646 | 0.12956 | 0.14418 | 0.16048 | 0.17869 | 0.199 |  | 0.0053864 | 0.0059212 | 0.006514 | 0.0071712 | 0.0079002 | 0.008709 | 0.0096068 | 0.010604 | 0.011711 | 0.012941 | 0.014309 | 0.015829 | 0.017519 | 0.0194 | 0.021493 | 0.023822 | 0.026416 | 0.029304 | 0.032521 | 0.036105 | 0.040099 | 0.044551 | 0.049514 | 0.055048 | 0.061221 | 0.068106 | 0.075788 | 0.08436 | 0.093928 | 0.10461 | 6870.9561 | 7553.245 | 8309.4096 | 9147.7839 | 10077.6655 | 11109.429 | 12254.6526 | 13526.2591 | 14938.6753 | 16508.0088 | 18252.2461 | 20191.4754 | 22348.1342 | 24747.288 | 27416.9409 | 30388.3845 | 33696.5875 | 37380.632 | 41484.2025 | 46056.1324 | 51151.0168 | 56829.8978 | 63161.0326 | 70220.7528 | 78094.4268 | 86877.5383 | 96676.8928 | 107611.9694 | 119816.4352 | 133439.8402 |  | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 33.5343 | 40.1385 | 53.2059 | 71.1435 | 95.8773 | 130.1215 | 177.7081 | 244.0558 | 336.8375 | 466.933 | 649.7856 | 907.3402 | 1270.8083 | 1784.6172 |  | 59.3202 | 65.2108 | 71.7391 | 78.9772 | 87.0053 | 95.913 | 105.8003 | 116.7787 | 128.9727 | 142.5215 | 157.5804 | 174.3226 | 192.9421 | 213.6552 | 236.7035 | 262.3574 | 290.9187 | 322.7248 | 358.1529 | 397.6246 | 441.6111 | 490.6396 | 545.2994 | 606.2493 | 674.2265 | 750.0553 | 834.6578 | 929.0655 | 1034.4325 | 1152.0499 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 45.1079 | 50.9984 | 57.5267 | 64.7648 | 72.7929 | 81.7006 | 91.5879 | 102.5663 | 114.7603 | 128.3091 | 143.368 | 160.1103 | 178.7297 | 199.4428 | 222.4912 | 248.145 | 276.7063 | 305.7135 | 335.6034 | 367.4728 | 400.9768 | 435.492 | 469.9838 | 502.8145 | 531.4692 | 552.1615 | 559.268 | 544.5199 | 495.8432 | 395.7 |  | 1508.1805 | 1657.9435 | 1823.9223 | 2007.9461 | 2212.0559 | 2438.5288 | 2689.9063 | 2969.025 | 3279.0515 | 3623.5215 | 4006.3831 | 4432.0455 | 4905.4339 | 5432.0501 | 6018.0411 | 6670.2754 | 7396.4287 | 8205.0795 | 9105.8166 | 10109.359 | 11227.6903 | 12474.2094 | 13863.8987 | 15413.5131 | 17141.791 | 19069.6912 | 21220.6576 | 23620.9159 | 26299.8062 | 29290.1548 |  | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.68662 | 0.91016 | 1.217 | 1.6401 | 2.2259 | 3.0399 | 4.1749 | 5.7621 | 7.9875 | 11.1155 | 15.5213 | 21.7389 | 30.5284 |  | 1507.6069 | 1657.3698 | 1823.3486 | 2007.3724 | 2211.4822 | 2437.9552 | 2689.3327 | 2968.4514 | 3278.4779 | 3622.9479 | 4005.8094 | 4431.4718 | 4904.8602 | 5431.4764 | 6017.4675 | 6669.7018 | 7395.8551 | 8204.3929 | 9104.9065 | 10108.142 | 11226.0502 | 12471.9835 | 13860.8587 | 15409.3382 | 17136.0289 | 19061.7037 | 21209.5421 | 23605.3946 | 26278.0673 | 29259.6265 |  | 1552.7147 | 1708.3682 | 1880.8753 | 2072.1372 | 2284.2751 | 2519.6558 | 2780.9206 | 3071.0176 | 3393.2382 | 3751.257 | 4149.1774 | 4591.5821 | 5083.5899 | 5630.9192 | 6239.9586 | 6917.8468 | 7672.5614 | 8510.1064 | 9440.5098 | 10475.6148 | 11627.027 | 12907.4755 | 14330.8425 | 15912.1526 | 17667.4982 | 19613.8651 | 21768.8101 | 24149.9145 | 26773.9105 | 29655.3264 |  | 59.6665 | 65.5914 | 72.1579 | 79.4382 | 87.5132 | 96.4729 | 106.4179 | 117.4603 | 129.7256 | 143.3535 | 158.5002 | 175.3402 | 194.0684 | 214.9023 | 238.0853 | 263.8889 | 292.6169 | 324.6087 | 360.2436 | 399.9457 | 444.189 | 493.5037 | 548.4825 | 609.7882 | 678.1622 | 754.4336 | 839.53 | 934.4888 | 1040.4709 | 1158.7748 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 44.9851 | 50.91 | 57.4765 | 64.7568 | 72.8318 | 81.7915 | 91.7364 | 102.7789 | 115.0442 | 128.6721 | 143.8188 | 160.6588 | 179.387 | 200.2209 | 223.4039 | 249.2075 | 277.9355 | 307.036 | 336.9499 | 368.7988 | 402.2137 | 436.5361 | 470.6814 | 502.9399 | 530.6938 | 550.009 | 555.052 | 537.2527 | 484.1074 | 377.4643 |  | 4.1536 | 4.5661 | 5.0232 | 5.53 | 6.0922 | 6.7159 | 7.4082 | 8.1769 | 9.0307 | 9.9794 | 11.0339 | 12.2062 | 13.5099 | 14.9602 | 16.5741 | 18.3704 | 20.3703 | 22.5974 | 25.078 | 27.8419 | 30.9218 | 34.3548 | 38.1821 | 42.4499 | 47.2097 | 52.5192 | 58.4432 | 65.0536 | 72.4315 | 80.6671 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 2.0859 | 2.4984 | 2.9555 | 3.4623 | 4.0244 | 4.6482 | 5.3405 | 6.1092 | 6.963 | 7.9117 | 8.9661 | 10.1384 | 11.4422 | 12.8925 | 14.5064 | 16.3027 | 18.3026 | 20.1224 | 21.7974 | 23.4552 | 25.0101 | 26.3316 | 27.2247 | 27.4015 | 26.4404 | 23.7284 | 18.3776 | 9.1074 | -5.926 | -29.3716 |  | 5239.6351 | 5759.9332 | 6336.5672 | 6975.8924 | 7684.999 | 8471.7985 | 9345.1199 | 10314.8182 | 11391.8948 | 12588.6328 | 13918.7487 | 15397.5609 | 17042.18 | 18871.7201 | 20907.5369 | 23173.4923 | 25696.2528 | 28505.6216 | 31634.9113 | 35121.3613 | 39006.6045 | 43337.1903 | 48165.17 | 53548.7523 | 59553.0375 | 66250.839 | 73723.6043 | 82062.4455 | 91369.2941 | 101758.1936 |  | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 1.9929 | 2.3854 | 3.162 | 4.2281 | 5.698 | 7.7331 | 10.5612 | 14.5042 | 20.0183 | 27.7498 | 38.6168 | 53.9233 | 75.5242 | 106.0599 |  | 5237.6422 | 5757.9403 | 6334.5742 | 6973.8994 | 7683.006 | 8469.8055 | 9343.127 | 10312.8253 | 11389.9018 | 12586.6399 | 13916.7557 | 15395.5679 | 17040.187 | 18869.7272 | 20905.5439 | 23171.4994 | 25694.2599 | 28503.2362 | 31631.7493 | 35117.1332 | 39000.9065 | 43329.4571 | 48154.6088 | 53534.2481 | 59533.0192 | 66223.0891 | 73684.9875 | 82008.5222 | 91293.7699 | 101652.1337 |  | 6837.4279 | 7519.7169 | 8275.8815 | 9114.2557 | 10044.1374 | 11075.9009 | 12221.1244 | 13492.731 | 14905.1472 | 16474.4807 | 18218.718 | 20157.9473 | 22314.6061 | 24713.7598 | 27383.4128 | 30354.8564 | 33663.0594 | 37340.501 | 41431.0064 | 45985.002 | 51055.1572 | 56699.8004 | 62983.3574 | 69976.7421 | 77757.6515 | 86410.6917 | 96027.2273 | 106704.7968 | 118545.8617 | 131655.5528
| FALSE | 2939 | 22015499 | MLN | Blank | 22 | CB BT 1-2 | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 0.91058 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 3.0201 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 30.9493 | 30.9493 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 58.3019 | 80.8821 | 112.601 | 157.2532 | 220.2334 | 309.2177 | 435.1372 | 613.5683 | 866.7208 | 1226.2799 | 1737.4704 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 58.3019 | 80.8821 | 112.601 | 157.2532 | 220.2334 | 309.2177 | 435.1372 | 613.5683 | 866.7208 | 1226.2799 | 1737.4704 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 60.1807 | 83.4884 | 116.2294 | 162.3205 | 227.3302 | 319.182 | 449.1591 | 633.3399 | 894.65 | 1265.7955 | 1793.4586 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3824 | 22.8789 | 32.042 | 44.9884 | 63.3085 | 89.2686 | 126.1 | 178.4126 | 252.7861 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 126.965 | 176.1381 | 245.2129 | 342.4527 | 479.6056 | 673.3881 | 947.6048 | 1336.1769 | 1887.4709 | 2670.488 | 3783.7151 | 4467.0862 | 3992.8845
| FALSE | 2940 | 22015482 | MLN | Blank | 22 | CB BT 2-3 | CB MGMT & CB FAIL | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0 | 1 |  | 1.0927 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 5.2187 | 0.0096441 | 0 | 0.0096441 | 26.5213 | 0 | 26.5213 | 27.376 | 3.8586 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 57.7559 | 30.9493 | 26.8066 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 39.8022 | 57.7559 | 84.9868 | 126.5842 | 190.526 | 289.3521 | 442.8194 | 682.1182 | 1056.5751 | 1644.3167 | 2569.2462 | 4028.0865 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 18.277 | 26.5213 | 39.0257 | 58.1271 | 87.4889 | 132.8696 | 203.3413 | 313.2266 | 485.176 | 755.0652 | 1179.79 | 1849.6849 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0652 | 12.3095 | 24.8139 | 43.9153 | 73.2771 | 118.6578 | 189.1295 | 299.0148 | 470.9642 | 738.0545 | 1157.2413 | 1819.5343 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0652 | 12.3095 | 24.8139 | 43.9153 | 73.2771 | 118.6578 | 189.1295 | 299.0148 | 470.9642 | 738.0545 | 1157.2413 | 1819.5343 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 18.866 | 27.376 | 40.2833 | 60.0002 | 90.3082 | 137.1512 | 209.8938 | 323.32 | 500.8103 | 779.3964 | 1217.8075 | 1909.2892 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1962 | 12.7062 | 25.6135 | 45.3304 | 75.6384 | 122.4814 | 195.224 | 308.6502 | 486.1406 | 761.8376 | 1194.5323 | 1878.167 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6591 | 3.8586 | 5.6779 | 8.457 | 12.7288 | 19.3313 | 29.5843 | 45.5716 | 70.5887 | 109.8551 | 171.6487 | 269.1123 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59145 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2636 | 27.5166 | 43.5039 | 68.521 | 107.3802 | 168.3681 | 264.7257 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8529 | 26.8066 | 54.0375 | 95.6349 | 159.5767 | 258.4028 | 411.8701 | 651.1689 | 1025.6258 | 1607.2723 | 2520.1417 | 3962.4271 | 5551.4471 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 2941 | 22004012 | MLN | Blank | 22 | CB TR NO.1 | CB FAIL | Y | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 12.8738 | 0.087882 | 0 | 0.087882 | 483.3526 | 0 | 483.3526 | 249.4641 | 35.1617 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 767.9784 | 45.1611 | 722.8173 |  | 0.044498 |  | 8.6254 | 9.0179 | 9.4282 | 9.8572 | 10.3058 | 10.7747 | 11.265 | 11.7776 | 12.3135 | 12.8738 | 13.4595 | 14.072 | 14.7123 | 15.3818 | 16.0817 | 16.8134 | 17.5785 | 18.3783 | 19.2146 | 20.0889 | 21.003 | 21.9587 | 22.9579 | 24.0025 | 25.0947 | 26.2366 | 27.4304 | 28 | 28 | 28 |  | 0.029574 | 0.033298 | 0.037515 | 0.042294 | 0.047711 | 0.053853 | 0.06082 | 0.068725 | 0.077697 | 0.087882 | 0.09945 | 0.11259 | 0.12752 | 0.14449 | 0.16378 | 0.18571 | 0.21065 | 0.23903 | 0.27131 | 0.30805 | 0.34986 | 0.39746 | 0.45166 | 0.51338 | 0.58367 | 0.66374 | 0.75496 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258.4418 | 290.9808 | 327.8366 | 369.5976 | 416.9336 | 470.6076 | 531.4885 | 600.566 | 678.9677 | 767.9784 | 869.062 | 983.8871 | 1114.3555 | 1262.6351 | 1431.1974 | 1622.8605 | 1840.8377 | 2088.7936 | 2370.9075 | 2691.9464 | 3057.3481 | 3473.3156 | 3946.9262 | 4486.2544 | 5100.5136 | 5800.2172 | 6597.3633 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 162.6589 | 183.1384 | 206.3348 | 232.6185 | 262.411 | 296.1925 | 334.5099 | 377.9861 | 427.3308 | 483.3526 | 546.9729 | 619.2419 | 701.3565 | 794.6811 | 900.7714 | 1021.4009 | 1158.5921 | 1314.6513 | 1492.2091 | 1694.2655 | 1924.2431 | 2186.0461 | 2484.1286 | 2823.5726 | 3210.1769 | 3650.5586 | 4152.2688 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.4471 | 168.9266 | 192.123 | 218.4066 | 248.1991 | 281.9806 | 320.298 | 363.7743 | 413.119 | 469.1408 | 532.7611 | 605.0301 | 687.1447 | 780.4693 | 886.5596 | 1007.1891 | 1144.3803 | 1297.6407 | 1469.6604 | 1664.1149 | 1883.6104 | 2130.9007 | 2408.816 | 2720.1419 | 3067.4253 | 3452.6726 | 3876.89 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.4471 | 168.9266 | 192.123 | 218.4066 | 248.1991 | 281.9806 | 320.298 | 363.7743 | 413.119 | 469.1408 | 532.7611 | 605.0301 | 687.1447 | 780.4693 | 886.5596 | 1007.1891 | 1144.3803 | 1297.6407 | 1469.6604 | 1664.1149 | 1883.6104 | 2130.9007 | 2408.816 | 2720.1419 | 3067.4253 | 3452.6726 | 3876.89 | 4022.4983 | 3868.4608 | 3650.7088 |  | 83.9502 | 94.5199 | 106.4919 | 120.0572 | 135.4334 | 152.8685 | 172.6446 | 195.0832 | 220.5506 | 249.4641 | 282.2993 | 319.5982 | 361.9785 | 410.1445 | 464.8989 | 527.1573 | 597.9633 | 678.5073 | 770.147 | 874.4308 | 993.125 | 1128.2446 | 1282.0886 | 1457.2797 | 1656.8108 | 1884.0971 | 2143.0358 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.2804 | 79.8501 | 91.8221 | 105.3874 | 120.7637 | 138.1987 | 157.9748 | 180.4134 | 205.8808 | 234.7943 | 267.6295 | 304.9284 | 347.3087 | 395.4747 | 450.2292 | 512.4875 | 583.2935 | 660.9485 | 746.8718 | 843.3086 | 951.1829 | 1071.3222 | 1204.3491 | 1350.5161 | 1509.4592 | 1679.8345 | 1858.7832 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8327 | 13.3225 | 15.0099 | 16.9219 | 19.0892 | 21.5467 | 24.3341 | 27.4968 | 31.0864 | 35.1617 | 39.7898 | 45.047 | 51.0205 | 57.8094 | 65.527 | 74.3023 | 84.2823 | 95.6349 | 108.5514 | 123.2501 | 139.9799 | 159.0249 | 180.7091 | 205.4021 | 233.5258 | 265.5615 | 302.0587 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.765 | 11.2548 | 12.9422 | 14.8542 | 17.0215 | 19.479 | 22.2664 | 25.4291 | 29.0187 | 33.094 | 37.7221 | 42.9793 | 48.9528 | 55.7417 | 63.4593 | 72.2346 | 82.2146 | 93.16 | 105.2708 | 118.8635 | 134.0682 | 151.0018 | 169.7518 | 190.3538 | 212.7567 | 236.7709 | 261.9936 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 227.4925 | 260.0315 | 296.8873 | 338.6483 | 385.9843 | 439.6583 | 500.5392 | 569.6167 | 648.0184 | 737.0291 | 838.1127 | 952.9378 | 1083.4062 | 1231.6858 | 1400.2481 | 1591.9112 | 1809.8884 | 2051.7492 | 2321.803 | 2626.287 | 2968.8615 | 3353.2247 | 3782.9168 | 4261.0118 | 4789.6413 | 5369.278 | 5997.6667 | 6164.7429 | 5829.293 | 5355.0913
| FALSE | 2942 | 22015496 | MLN | Blank | 22 | CB TR NO.1 | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 0.91058 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 3.0201 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 30.9493 | 30.9493 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 58.3019 | 80.8821 | 112.601 | 157.2532 | 220.2334 | 309.2177 | 435.1372 | 613.5683 | 866.7208 | 1226.2799 | 1737.4704 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 58.3019 | 80.8821 | 112.601 | 157.2532 | 220.2334 | 309.2177 | 435.1372 | 613.5683 | 866.7208 | 1226.2799 | 1737.4704 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 60.1807 | 83.4884 | 116.2294 | 162.3205 | 227.3302 | 319.182 | 449.1591 | 633.3399 | 894.65 | 1265.7955 | 1793.4586 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3824 | 22.8789 | 32.042 | 44.9884 | 63.3085 | 89.2686 | 126.1 | 178.4126 | 252.7861 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 126.965 | 176.1381 | 245.2129 | 342.4527 | 479.6056 | 673.3881 | 947.6048 | 1336.1769 | 1887.4709 | 2670.488 | 3783.7151 | 4467.0862 | 3992.8845
| TRUE | 2943 | 22004013 | MLN | Blank | 22 | CB TR NO.2 | CB FAIL | Y | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 12.8738 | 0.087882 | 0 | 0.087882 | 483.3526 | 0 | 483.3526 | 249.4641 | 35.1617 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 767.9784 | 45.1611 | 722.8173 |  | 0.044498 |  | 8.6254 | 9.0179 | 9.4282 | 9.8572 | 10.3058 | 10.7747 | 11.265 | 11.7776 | 12.3135 | 12.8738 | 13.4595 | 14.072 | 14.7123 | 15.3818 | 16.0817 | 16.8134 | 17.5785 | 18.3783 | 19.2146 | 20.0889 | 21.003 | 21.9587 | 22.9579 | 24.0025 | 25.0947 | 26.2366 | 27.4304 | 28 | 28 | 28 |  | 0.029574 | 0.033298 | 0.037515 | 0.042294 | 0.047711 | 0.053853 | 0.06082 | 0.068725 | 0.077697 | 0.087882 | 0.09945 | 0.11259 | 0.12752 | 0.14449 | 0.16378 | 0.18571 | 0.21065 | 0.23903 | 0.27131 | 0.30805 | 0.34986 | 0.39746 | 0.45166 | 0.51338 | 0.58367 | 0.66374 | 0.75496 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258.4418 | 290.9808 | 327.8366 | 369.5976 | 416.9336 | 470.6076 | 531.4885 | 600.566 | 678.9677 | 767.9784 | 869.062 | 983.8871 | 1114.3555 | 1262.6351 | 1431.1974 | 1622.8605 | 1840.8377 | 2088.7936 | 2370.9075 | 2691.9464 | 3057.3481 | 3473.3156 | 3946.9262 | 4486.2544 | 5100.5136 | 5800.2172 | 6597.3633 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 162.6589 | 183.1384 | 206.3348 | 232.6185 | 262.411 | 296.1925 | 334.5099 | 377.9861 | 427.3308 | 483.3526 | 546.9729 | 619.2419 | 701.3565 | 794.6811 | 900.7714 | 1021.4009 | 1158.5921 | 1314.6513 | 1492.2091 | 1694.2655 | 1924.2431 | 2186.0461 | 2484.1286 | 2823.5726 | 3210.1769 | 3650.5586 | 4152.2688 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.4471 | 168.9266 | 192.123 | 218.4066 | 248.1991 | 281.9806 | 320.298 | 363.7743 | 413.119 | 469.1408 | 532.7611 | 605.0301 | 687.1447 | 780.4693 | 886.5596 | 1007.1891 | 1144.3803 | 1297.6407 | 1469.6604 | 1664.1149 | 1883.6104 | 2130.9007 | 2408.816 | 2720.1419 | 3067.4253 | 3452.6726 | 3876.89 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.4471 | 168.9266 | 192.123 | 218.4066 | 248.1991 | 281.9806 | 320.298 | 363.7743 | 413.119 | 469.1408 | 532.7611 | 605.0301 | 687.1447 | 780.4693 | 886.5596 | 1007.1891 | 1144.3803 | 1297.6407 | 1469.6604 | 1664.1149 | 1883.6104 | 2130.9007 | 2408.816 | 2720.1419 | 3067.4253 | 3452.6726 | 3876.89 | 4022.4983 | 3868.4608 | 3650.7088 |  | 83.9502 | 94.5199 | 106.4919 | 120.0572 | 135.4334 | 152.8685 | 172.6446 | 195.0832 | 220.5506 | 249.4641 | 282.2993 | 319.5982 | 361.9785 | 410.1445 | 464.8989 | 527.1573 | 597.9633 | 678.5073 | 770.147 | 874.4308 | 993.125 | 1128.2446 | 1282.0886 | 1457.2797 | 1656.8108 | 1884.0971 | 2143.0358 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.2804 | 79.8501 | 91.8221 | 105.3874 | 120.7637 | 138.1987 | 157.9748 | 180.4134 | 205.8808 | 234.7943 | 267.6295 | 304.9284 | 347.3087 | 395.4747 | 450.2292 | 512.4875 | 583.2935 | 660.9485 | 746.8718 | 843.3086 | 951.1829 | 1071.3222 | 1204.3491 | 1350.5161 | 1509.4592 | 1679.8345 | 1858.7832 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8327 | 13.3225 | 15.0099 | 16.9219 | 19.0892 | 21.5467 | 24.3341 | 27.4968 | 31.0864 | 35.1617 | 39.7898 | 45.047 | 51.0205 | 57.8094 | 65.527 | 74.3023 | 84.2823 | 95.6349 | 108.5514 | 123.2501 | 139.9799 | 159.0249 | 180.7091 | 205.4021 | 233.5258 | 265.5615 | 302.0587 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.765 | 11.2548 | 12.9422 | 14.8542 | 17.0215 | 19.479 | 22.2664 | 25.4291 | 29.0187 | 33.094 | 37.7221 | 42.9793 | 48.9528 | 55.7417 | 63.4593 | 72.2346 | 82.2146 | 93.16 | 105.2708 | 118.8635 | 134.0682 | 151.0018 | 169.7518 | 190.3538 | 212.7567 | 236.7709 | 261.9936 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 227.4925 | 260.0315 | 296.8873 | 338.6483 | 385.9843 | 439.6583 | 500.5392 | 569.6167 | 648.0184 | 737.0291 | 838.1127 | 952.9378 | 1083.4062 | 1231.6858 | 1400.2481 | 1591.9112 | 1809.8884 | 2051.7492 | 2321.803 | 2626.287 | 2968.8615 | 3353.2247 | 3782.9168 | 4261.0118 | 4789.6413 | 5369.278 | 5997.6667 | 6164.7429 | 5829.293 | 5355.0913
| FALSE | 2944 | 22015497 | MLN | Blank | 22 | CB TR NO.2 | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 0.91058 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 3.0201 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 30.9493 | 30.9493 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 58.3019 | 80.8821 | 112.601 | 157.2532 | 220.2334 | 309.2177 | 435.1372 | 613.5683 | 866.7208 | 1226.2799 | 1737.4704 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 58.3019 | 80.8821 | 112.601 | 157.2532 | 220.2334 | 309.2177 | 435.1372 | 613.5683 | 866.7208 | 1226.2799 | 1737.4704 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 60.1807 | 83.4884 | 116.2294 | 162.3205 | 227.3302 | 319.182 | 449.1591 | 633.3399 | 894.65 | 1265.7955 | 1793.4586 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3824 | 22.8789 | 32.042 | 44.9884 | 63.3085 | 89.2686 | 126.1 | 178.4126 | 252.7861 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 126.965 | 176.1381 | 245.2129 | 342.4527 | 479.6056 | 673.3881 | 947.6048 | 1336.1769 | 1887.4709 | 2670.488 | 3783.7151 | 4467.0862 | 3992.8845
| FALSE | 2945 | 22015481 | MLN | Blank | 22 | CB TR NO.3 | CB MGMT & CB FAIL | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0 | 1 |  | 1.0927 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 5.2187 | 0.0096441 | 0 | 0.0096441 | 26.5213 | 0 | 26.5213 | 27.376 | 3.8586 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 57.7559 | 30.9493 | 26.8066 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 39.8022 | 57.7559 | 84.9868 | 126.5842 | 190.526 | 289.3521 | 442.8194 | 682.1182 | 1056.5751 | 1644.3167 | 2569.2462 | 4028.0865 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 18.277 | 26.5213 | 39.0257 | 58.1271 | 87.4889 | 132.8696 | 203.3413 | 313.2266 | 485.176 | 755.0652 | 1179.79 | 1849.6849 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0652 | 12.3095 | 24.8139 | 43.9153 | 73.2771 | 118.6578 | 189.1295 | 299.0148 | 470.9642 | 738.0545 | 1157.2413 | 1819.5343 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0652 | 12.3095 | 24.8139 | 43.9153 | 73.2771 | 118.6578 | 189.1295 | 299.0148 | 470.9642 | 738.0545 | 1157.2413 | 1819.5343 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 18.866 | 27.376 | 40.2833 | 60.0002 | 90.3082 | 137.1512 | 209.8938 | 323.32 | 500.8103 | 779.3964 | 1217.8075 | 1909.2892 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1962 | 12.7062 | 25.6135 | 45.3304 | 75.6384 | 122.4814 | 195.224 | 308.6502 | 486.1406 | 761.8376 | 1194.5323 | 1878.167 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6591 | 3.8586 | 5.6779 | 8.457 | 12.7288 | 19.3313 | 29.5843 | 45.5716 | 70.5887 | 109.8551 | 171.6487 | 269.1123 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59145 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2636 | 27.5166 | 43.5039 | 68.521 | 107.3802 | 168.3681 | 264.7257 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8529 | 26.8066 | 54.0375 | 95.6349 | 159.5767 | 258.4028 | 411.8701 | 651.1689 | 1025.6258 | 1607.2723 | 2520.1417 | 3962.4271 | 5551.4471 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 2946 | 22015498 | MLN | Blank | 22 | CB TR NO.3 | CB FAIL | Y | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 0.91058 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 3.0201 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 30.9493 | 30.9493 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 58.3019 | 80.8821 | 112.601 | 157.2532 | 220.2334 | 309.2177 | 435.1372 | 613.5683 | 866.7208 | 1226.2799 | 1737.4704 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 58.3019 | 80.8821 | 112.601 | 157.2532 | 220.2334 | 309.2177 | 435.1372 | 613.5683 | 866.7208 | 1226.2799 | 1737.4704 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 60.1807 | 83.4884 | 116.2294 | 162.3205 | 227.3302 | 319.182 | 449.1591 | 633.3399 | 894.65 | 1265.7955 | 1793.4586 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3824 | 22.8789 | 32.042 | 44.9884 | 63.3085 | 89.2686 | 126.1 | 178.4126 | 252.7861 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 126.965 | 176.1381 | 245.2129 | 342.4527 | 479.6056 | 673.3881 | 947.6048 | 1336.1769 | 1887.4709 | 2670.488 | 3783.7151 | 4467.0862 | 3992.8845
| TRUE | 2947 | 22004017 | MLN | Blank | 22 | ALL FEEDERS | MASTER EARTH FAULT | X | ASEA | GROUP_2650 | GROUP 2650 | GROUP 2000s | Electronic |  | 0.81881 | 2190 |  | 8.25 | 0.026286 | 0.02098 | 0.0053053 | 156.1101 | 5874.4876 | 6030.5977 | 193.7249 | 10.7267 | 20408.8115 |  | 12.8738 | 0.087882 | 0.070145 | 0.017738 | 521.9322 | 19640.5298 | 20162.4621 | 647.6921 | 35.8632 | 68234.0141 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 28.4268 | 1.6231 | 30.0499 | 14.7027 | 2.0677 | 5.6388 |  | 26643.8608 | 89080.0315 | 52.4591 | 89027.5724 |  | 0.044498 |  | 8.6254 | 9.0179 | 9.4282 | 9.8572 | 10.3058 | 10.7747 | 11.265 | 11.7776 | 12.3135 | 12.8738 | 13.4595 | 14.072 | 14.7123 | 15.3818 | 16.0817 | 16.8134 | 17.5785 | 18.3783 | 19.2146 | 20.0889 | 21.003 | 21.9587 | 22.9579 | 24.0025 | 25.0947 | 26.2366 | 27.4304 | 28 | 28 | 28 |  | 0.029574 | 0.033298 | 0.037515 | 0.042294 | 0.047711 | 0.053853 | 0.06082 | 0.068725 | 0.077697 | 0.087882 | 0.09945 | 0.11259 | 0.12752 | 0.14449 | 0.16378 | 0.18571 | 0.21065 | 0.23903 | 0.27131 | 0.30805 | 0.34986 | 0.39746 | 0.45166 | 0.51338 | 0.58367 | 0.66374 | 0.75496 | 0.80128 | 0.80128 | 0.80128 |  | 0.023605 | 0.026577 | 0.029944 | 0.033758 | 0.038081 | 0.042984 | 0.048544 | 0.054854 | 0.062015 | 0.070145 | 0.079377 | 0.089865 | 0.10178 | 0.11533 | 0.13072 | 0.14823 | 0.16814 | 0.19078 | 0.21655 | 0.24587 | 0.27925 | 0.31724 | 0.3605 | 0.40976 | 0.46586 | 0.52977 | 0.60258 | 0.63955 | 0.63955 | 0.63955 | 29977.4061 | 33751.7071 | 38026.7177 | 42870.6892 | 48361.3306 | 54587.1337 | 61648.8841 | 69661.3855 | 78755.4275 | 89080.0315 | 100805.0132 | 114123.9081 | 129257.3104 | 146456.6837 | 166008.7121 | 188240.2663 | 213524.0737 | 242285.1918 | 275008.3987 | 312246.6317 | 354630.6229 | 402879.9014 | 457815.3571 | 520373.5874 | 591623.2816 | 672783.9313 | 765247.1999 | 812198.4645 | 812198.4645 | 812198.4645 |  | 38.2632 | 38.2632 | 38.2632 | 38.2632 | 38.2632 | 38.2632 | 38.2632 | 38.2632 | 38.2632 | 38.2632 | 38.2632 | 38.2632 | 38.2632 | 38.2632 | 38.2632 | 38.2632 | 38.2632 | 45.7987 | 60.7089 | 81.176 | 109.3976 | 148.4708 | 202.768 | 278.4718 | 384.3374 | 532.7785 | 741.4165 | 1035.2907 | 1450.014 | 2036.2788 |  | 175.6418 | 197.7559 | 222.8038 | 251.1853 | 283.3557 | 319.8336 | 361.2093 | 408.1557 | 461.4389 | 521.9322 | 590.6305 | 668.6678 | 757.3365 | 858.11 | 972.668 | 1102.9258 | 1251.0671 | 1419.5825 | 1611.3123 | 1829.4962 | 2077.8299 | 2360.5291 | 2682.4035 | 3048.9409 | 3466.4027 | 3941.9341 | 4483.6892 | 4758.7832 | 4758.7832 | 4758.7832 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 161.4284 | 183.5425 | 208.5904 | 236.9719 | 269.1423 | 305.6202 | 346.9959 | 393.9423 | 447.2255 | 507.7188 | 576.4171 | 654.4544 | 743.123 | 843.8966 | 958.4546 | 1088.7123 | 1236.8537 | 1402.5699 | 1588.7611 | 1799.3422 | 2037.1926 | 2305.3775 | 2607.0825 | 2945.4985 | 3323.6351 | 3744.026 | 4208.2795 | 4374.2097 | 4220.1549 | 4002.3785 |  | 6609.4738 | 7441.6387 | 8384.201 | 9452.2087 | 10662.7955 | 12035.472 | 13592.4598 | 15359.0709 | 17364.1421 | 19640.5298 | 22225.6755 | 25162.25 | 28498.8905 | 32291.0401 | 36601.9074 | 41503.5615 | 47078.1821 | 53419.4865 | 60634.3596 | 68844.714 | 78189.6146 | 88827.7047 | 100939.9754 | 114732.9295 | 130442.1937 | 148336.6436 | 168723.1158 | 179075.0174 | 179075.0174 | 179075.0174 |  | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.9427 | 2.5752 | 3.4434 | 4.6405 | 6.2979 | 8.6011 | 11.8123 | 16.303 | 22.5996 | 31.4497 | 43.9154 | 61.5073 | 86.3757 |  | 6607.8508 | 7440.0156 | 8382.5779 | 9450.5857 | 10661.1724 | 12033.849 | 13590.8367 | 15357.4479 | 17362.519 | 19638.9068 | 22224.0524 | 25160.627 | 28497.2674 | 32289.417 | 36600.2843 | 41501.9385 | 47076.559 | 53417.5438 | 60631.7844 | 68841.2706 | 78184.9742 | 88821.4068 | 100931.3743 | 114721.1172 | 130425.8907 | 148314.044 | 168691.6661 | 179031.102 | 179013.5101 | 178988.6417 |  | 6769.2791 | 7623.5581 | 8591.1683 | 9687.5575 | 10930.3147 | 12339.4691 | 13937.8327 | 15751.3901 | 17809.7446 | 20146.6256 | 22800.4695 | 25815.0813 | 29240.3905 | 33133.3136 | 37558.7389 | 42590.6508 | 48313.4127 | 54820.1137 | 62220.5455 | 70640.6129 | 80222.1668 | 91126.7843 | 103538.4568 | 117666.6158 | 133749.5258 | 152058.07 | 172899.9456 | 183405.3117 | 183233.6649 | 182991.0201 |  | 217.9628 | 245.4053 | 276.4885 | 311.7085 | 351.6305 | 396.8977 | 448.2429 | 506.5011 | 572.6229 | 647.6921 | 732.9433 | 829.7837 | 939.8171 | 1064.8721 | 1207.0329 | 1368.6764 | 1552.5124 | 1761.6317 | 1999.5589 | 2270.3144 | 2578.4842 | 2929.3 | 3328.7302 | 3783.5849 | 4301.6344 | 4891.7455 | 5564.0368 | 5905.4148 | 5905.4148 | 5905.4148 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 203.2601 | 230.7026 | 261.7858 | 297.0059 | 336.9278 | 382.195 | 433.5403 | 491.7984 | 557.9202 | 632.9894 | 718.2406 | 815.081 | 925.1144 | 1050.1694 | 1192.3302 | 1353.9737 | 1537.8097 | 1744.0335 | 1976.2314 | 2239.1224 | 2536.448 | 2872.2498 | 3250.8164 | 3676.5818 | 4153.9523 | 4687.0246 | 5279.1465 | 5507.6029 | 5348.2449 | 5122.9719 |  | 12.0687 | 13.5883 | 15.3094 | 17.2595 | 19.47 | 21.9765 | 24.8195 | 28.0453 | 31.7065 | 35.8632 | 40.5836 | 45.9457 | 52.0383 | 58.9627 | 66.8342 | 75.7845 | 85.9637 | 97.5427 | 110.7169 | 125.7089 | 142.7724 | 162.1973 | 184.3141 | 209.4997 | 238.1844 | 270.8593 | 308.0845 | 326.9868 | 326.9868 | 326.9868 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 10.001 | 11.5205 | 13.2416 | 15.1918 | 17.4023 | 19.9087 | 22.7518 | 25.9776 | 29.6388 | 33.7954 | 38.5158 | 43.8779 | 49.9706 | 56.8949 | 64.7665 | 73.7168 | 83.8959 | 95.0678 | 107.4362 | 121.3221 | 136.8606 | 154.174 | 173.3565 | 194.451 | 217.4148 | 242.0679 | 268.0183 | 271.0396 | 248.6279 | 216.9461 |  | 22962.2589 | 25853.3189 | 29127.9151 | 32838.3271 | 37044.0789 | 41812.9539 | 47222.1525 | 53359.6125 | 60325.517 | 68234.0141 | 77215.1803 | 87417.261 | 99009.228 | 112183.6989 | 127160.2695 | 144189.3181 | 163556.3484 | 185586.9484 | 210652.451 | 239176.3982 | 271641.9217 | 308600.1704 | 350679.9339 | 398598.6324 | 453174.8664 | 515342.7488 | 586168.2736 | 622132.2624 | 622132.2624 | 622132.2624 |  | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 6.7492 | 8.9465 | 11.9627 | 16.1217 | 21.8798 | 29.8814 | 41.0377 | 56.6389 | 78.5143 | 109.2608 | 152.5683 | 213.6851 | 300.0815 |  | 22956.6202 | 25847.6801 | 29122.2764 | 32832.6883 | 37038.4401 | 41807.3152 | 47216.5137 | 53353.9738 | 60319.8783 | 68228.3754 | 77209.5416 | 87411.6222 | 99003.5892 | 112178.0601 | 127154.6307 | 144183.6793 | 163550.7097 | 185580.1992 | 210643.5045 | 239164.4355 | 271625.8001 | 308578.2906 | 350650.0525 | 398557.5947 | 453118.2275 | 515264.2345 | 586059.0128 | 621979.6941 | 621918.5773 | 621832.1808 |  | 29939.1604 | 33713.4614 | 37988.4721 | 42832.4435 | 48323.0849 | 54548.888 | 61610.6384 | 69623.1398 | 78717.1818 | 89041.7858 | 100766.7675 | 114085.6624 | 129219.0647 | 146418.438 | 165970.4664 | 188202.0206 | 213485.828 | 242239.4142 | 274947.7177 | 312165.4929 | 354521.2754 | 402731.4987 | 457612.6821 | 520095.2433 | 591239.1203 | 672251.397 | 764506.1232 | 811163.6483 | 810749.1151 | 810163.1189
| FALSE | 2948 | 22015504 | MLN | Blank | 22 | ALL FEEDERS | BUEF & Y MEF | Y | Schweitzer | SEL_351 | SEL 351 | SEL 300s | Digital |  | 0.15703 | 1 |  | 1.0927 | 0.0051679 | 1.1117e-06 | 0.0051668 | 14.2121 | 0.077816 | 14.2899 | 14.6761 | 2.0677 | 1.0814 |  | 5.2187 | 0.0096441 | 2.0745e-06 | 0.009642 | 26.5219 | 0.14522 | 26.6671 | 27.3877 | 3.8586 | 2.018 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 14.2121 | 0.077816 | 14.2899 | 14.6761 | 2.0677 | 1.0814 |  | 32.1151 | 59.9315 | 32.1151 | 27.8164 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.4296e-06 | 2.0745e-06 | 3.0526e-06 | 4.5467e-06 | 6.8434e-06 | 1.0393e-05 | 1.5905e-05 | 2.4501e-05 | 3.7951e-05 | 5.9062e-05 | 9.2284e-05 | 0.00014468 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 41.3015 | 59.9315 | 88.1882 | 131.3525 | 197.7028 | 300.2516 | 459.4998 | 707.8127 | 1096.3749 | 1706.2559 | 2666.0264 | 4179.8192 | 5852.3826 | 5852.3826 | 5852.3826 | 5852.3826 | 5852.3826 | 5852.3826 | 5852.3826 | 5852.3826 | 5852.3826 | 5852.3826 |  | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 32.1151 | 38.4398 | 50.9542 | 68.1327 | 91.8197 | 124.6147 | 170.1874 | 233.7272 | 322.5824 | 447.1721 | 622.2863 | 868.9411 | 1217.027 | 1709.0913 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 18.2774 | 26.5219 | 39.0265 | 58.1283 | 87.4908 | 132.8724 | 203.3457 | 313.2333 | 485.1865 | 755.0814 | 1179.8153 | 1849.7247 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0653 | 12.3098 | 24.8144 | 43.9162 | 73.2787 | 118.6603 | 189.1335 | 299.0212 | 470.9743 | 738.0704 | 1157.2662 | 1819.5735 | 2549.2623 | 2534.7493 | 2514.5817 | 2486.463 | 2447.1413 | 2392.0057 | 2314.5112 | 2205.3573 | 2051.3164 | 1833.5597 |  | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.10007 | 0.14522 | 0.21368 | 0.31827 | 0.47904 | 0.72752 | 1.1134 | 1.7151 | 2.6566 | 4.1343 | 6.4599 | 10.1278 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 |  | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.093141 | 0.12346 | 0.16509 | 0.22248 | 0.30195 | 0.41237 | 0.56633 | 0.78163 | 1.0835 | 1.5078 | 2.1055 | 2.9489 | 4.1412 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022259 | 0.0674 | 0.13587 | 0.24046 | 0.40122 | 0.6497 | 1.0356 | 1.6372 | 2.5787 | 4.0412 | 6.3364 | 9.9628 | 13.958 | 13.8786 | 13.7681 | 13.6142 | 13.3989 | 13.097 | 12.6727 | 12.075 | 11.2316 | 10.0393 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0876 | 12.3772 | 24.9503 | 44.1567 | 73.6799 | 119.31 | 190.1691 | 300.6584 | 473.5531 | 742.1115 | 1163.6026 | 1829.5362 | 2563.2203 | 2548.6279 | 2528.3498 | 2500.0772 | 2460.5401 | 2405.1027 | 2327.1839 | 2217.4323 | 2062.548 | 1843.5991 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 18.8741 | 27.3877 | 40.3006 | 60.026 | 90.347 | 137.2102 | 209.9841 | 323.4591 | 501.0258 | 779.7317 | 1218.3314 | 1910.1106 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.198 | 12.7116 | 25.6245 | 45.3499 | 75.6709 | 122.5341 | 195.308 | 308.783 | 486.3497 | 762.1653 | 1195.0462 | 1878.975 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6592 | 3.8586 | 5.6779 | 8.457 | 12.7289 | 19.3314 | 29.5845 | 45.5719 | 70.5891 | 109.8557 | 171.6496 | 269.1138 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59146 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2637 | 27.5168 | 43.5042 | 68.5214 | 107.3808 | 168.369 | 264.7271 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.3907 | 2.018 | 2.9695 | 4.4229 | 6.657 | 10.11 | 15.4722 | 23.8334 | 36.917 | 57.4528 | 89.7701 | 140.7423 | 197.0606 | 197.0606 | 197.0606 | 197.0606 | 197.0606 | 197.0606 | 197.0606 | 197.0606 | 197.0606 | 197.0606 |  | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 1.2943 | 1.7157 | 2.2942 | 3.0917 | 4.196 | 5.7305 | 7.87 | 10.8619 | 15.0571 | 20.9535 | 29.2589 | 40.9796 | 57.5483 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30932 | 0.93663 | 1.8881 | 3.3415 | 5.5756 | 9.0287 | 14.3908 | 22.752 | 35.8356 | 56.1585 | 88.0543 | 138.4481 | 193.9689 | 192.8646 | 191.3301 | 189.1906 | 186.1987 | 182.0035 | 176.1071 | 167.8017 | 156.081 | 139.5123 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1864 | 27.8164 | 56.0731 | 99.2374 | 165.5877 | 268.1365 | 427.3847 | 675.6976 | 1064.2598 | 1667.8161 | 2615.0722 | 4111.6865 | 5760.5629 | 5727.7679 | 5682.1952 | 5618.6554 | 5529.8002 | 5405.2105 | 5230.0962 | 4983.4414 | 4635.3555 | 4143.2913
| TRUE | 2949 | 22009940 | MLN | MLN011 | 22 | MLN 11 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 3.6241 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 11.7363 |  | 10.5848 | 0.060301 | 4.7442e-05 | 0.060253 | 165.8402 | 3.321 | 169.1611 | 171.4401 | 24.1268 | 136.9416 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 11.7363 |  | 42.9944 | 501.6696 | 42.9944 | 458.6752 |  | 0.10718 |  | 4.0341 | 4.4905 | 4.9985 | 5.564 | 6.1935 | 6.8943 | 7.6743 | 8.5425 | 9.509 | 10.5848 | 11.7823 | 13.1153 | 14.5992 | 16.2509 | 18.0895 | 20.1361 | 22.4142 | 24.9501 | 27.7729 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.005268 | 0.0067412 | 0.0086907 | 0.011281 | 0.014733 | 0.019351 | 0.025546 | 0.033879 | 0.045116 | 0.060301 | 0.080864 | 0.10876 | 0.14667 | 0.19826 | 0.26856 | 0.36449 | 0.49551 | 0.67465 | 0.91979 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.1447e-06 | 5.3037e-06 | 6.8375e-06 | 8.8752e-06 | 1.1592e-05 | 1.5225e-05 | 2.0099e-05 | 2.6655e-05 | 3.5495e-05 | 4.7442e-05 | 6.3621e-05 | 8.5569e-05 | 0.00011539 | 0.00015598 | 0.0002113 | 0.00028677 | 0.00038985 | 0.00053079 | 0.00072366 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 43.8271 | 56.0831 | 72.3022 | 93.8485 | 122.5734 | 160.993 | 212.5321 | 281.8577 | 375.3378 | 501.6696 | 672.7437 | 904.8303 | 1220.2096 | 1649.4141 | 2234.3116 | 3032.3465 | 4122.3766 | 5612.7061 | 7652.1446 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 |  | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 51.4616 | 68.2154 | 91.2133 | 122.9245 | 166.829 | 227.8399 | 312.9044 | 431.8602 | 598.6558 | 833.0916 | 1163.303 | 1629.3062 | 2288.0618 |  | 14.4882 | 18.5398 | 23.9014 | 31.0241 | 40.5199 | 53.2205 | 70.2581 | 93.1755 | 124.0778 | 165.8402 | 222.3932 | 299.1156 | 403.3726 | 545.2575 | 738.6108 | 1002.4224 | 1362.7607 | 1855.4286 | 2529.619 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0.27525 | 4.3268 | 9.6885 | 16.8112 | 26.3069 | 39.0076 | 56.0452 | 78.9626 | 109.8649 | 151.6272 | 208.1803 | 284.9027 | 389.1596 | 531.0446 | 724.3979 | 988.2095 | 1348.5478 | 1838.4166 | 2507.0686 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.29013 | 0.37126 | 0.47863 | 0.62126 | 0.81141 | 1.0657 | 1.4069 | 1.8659 | 2.4847 | 3.321 | 4.4534 | 5.9898 | 8.0776 | 10.9188 | 14.7908 | 20.0736 | 27.2894 | 37.1552 | 50.6559 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.005512 | 0.086645 | 0.19401 | 0.33665 | 0.5268 | 0.78113 | 1.1223 | 1.5812 | 2.2001 | 3.0364 | 4.1688 | 5.7052 | 7.793 | 10.6342 | 14.5061 | 19.789 | 27.0048 | 36.8145 | 50.2043 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0.28077 | 4.4135 | 9.8825 | 17.1478 | 26.8337 | 39.7887 | 57.1675 | 80.5438 | 112.065 | 154.6636 | 212.3491 | 290.6079 | 396.9526 | 541.6788 | 738.9041 | 1007.9985 | 1375.5526 | 1875.2311 | 2557.2729 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.9774 | 19.1658 | 24.7085 | 32.0717 | 41.8881 | 55.0176 | 72.6305 | 96.3218 | 128.2676 | 171.4401 | 229.9028 | 309.2158 | 416.9932 | 563.6692 | 763.5515 | 1036.2711 | 1408.7769 | 1918.0807 | 2615.0364 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0.28455 | 4.4729 | 10.0156 | 17.3788 | 27.1952 | 40.3247 | 57.9376 | 81.6289 | 113.5747 | 156.7472 | 215.2099 | 294.5229 | 402.3004 | 548.9763 | 748.8586 | 1021.5782 | 1394.0841 | 1900.4942 | 2591.7245 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.1078 | 2.6972 | 3.4772 | 4.5135 | 5.8949 | 7.7426 | 10.2213 | 13.5554 | 18.0511 | 24.1268 | 32.3543 | 43.516 | 58.6836 | 79.3253 | 107.4548 | 145.8347 | 198.2576 | 269.9321 | 368.0148 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.040045 | 0.62948 | 1.4095 | 2.4457 | 3.8272 | 5.6749 | 8.1536 | 11.4877 | 15.9834 | 22.0591 | 30.2866 | 41.4483 | 56.6158 | 77.2576 | 105.3871 | 143.767 | 196.1899 | 267.4571 | 364.7342 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 11.9635 | 15.3091 | 19.7365 | 25.618 | 33.4591 | 43.9465 | 58.0152 | 76.9392 | 102.4566 | 136.9416 | 183.64 | 246.993 | 333.0826 | 450.2433 | 609.9037 | 827.7446 | 1125.2919 | 1532.1096 | 2088.8185 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 |  | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 14.0476 | 18.6209 | 24.8986 | 33.5549 | 45.5396 | 62.1938 | 85.414 | 117.8856 | 163.4161 | 227.4104 | 317.5487 | 444.7544 | 624.576 |  | 0.22729 | 3.5729 | 8.0002 | 13.8817 | 21.7228 | 32.2103 | 46.279 | 65.2029 | 90.7203 | 125.2053 | 171.9037 | 235.2568 | 321.3464 | 438.507 | 598.1675 | 816.0084 | 1113.5557 | 1518.0621 | 2070.1976 | 2113.8155 | 2105.1592 | 2093.1745 | 2076.5203 | 2053.3001 | 2020.8285 | 1975.298 | 1911.3037 | 1821.1654 | 1693.9597 | 1514.1381 |  | 0.83265 | 13.0887 | 29.3078 | 50.8541 | 79.579 | 117.9986 | 169.5376 | 238.8633 | 332.3434 | 458.6752 | 629.7493 | 861.8358 | 1177.2152 | 1606.4197 | 2191.3172 | 2989.3521 | 4079.3822 | 5561.2445 | 7583.9292 | 7743.718 | 7712.0068 | 7668.1023 | 7607.0914 | 7522.0269 | 7403.0711 | 7236.2755 | 7001.8397 | 6671.6283 | 6205.6251 | 5546.8695
| TRUE | 2950 | 22009307 | MLN | MLN012 | 22 | MLN 12 | DISTANCE | Y | Schweitzer | SEL_311A | SEL 311A | SEL 300s | Digital |  | 0.081865 | 1 |  | 4.6061 | 0.0071552 | 8.0242e-07 | 0.0071544 | 19.6772 | 0.056169 | 19.7333 | 20.3156 | 2.8628 | 1.1581 |  | 11.9319 | 0.083722 | 9.3888e-06 | 0.083712 | 230.2367 | 0.65722 | 230.8939 | 237.7065 | 33.4971 | 13.5503 |  | 0.0051679 | 5.7955e-07 | 0.0051674 | 14.212 | 0.040569 | 14.2526 | 14.6731 | 2.0677 | 0.83643 |  | 44.0698 | 515.6479 | 31.8298 | 483.8181 |  | 0.095183 |  | 5.0661 | 5.572 | 6.1284 | 6.7404 | 7.4135 | 8.1538 | 8.968 | 9.8636 | 10.8485 | 11.9319 | 13.1234 | 14.4339 | 15.8753 | 17.4606 | 19.2042 | 21.1219 | 23.2311 | 25.551 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0089761 | 0.01132 | 0.014347 | 0.018263 | 0.023345 | 0.029952 | 0.03856 | 0.049796 | 0.064486 | 0.083722 | 0.10895 | 0.14207 | 0.18561 | 0.2429 | 0.31838 | 0.4179 | 0.54922 | 0.72263 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.0066e-06 | 1.2695e-06 | 1.6089e-06 | 2.0481e-06 | 2.618e-06 | 3.359e-06 | 4.3243e-06 | 5.5843e-06 | 7.2317e-06 | 9.3888e-06 | 1.2218e-05 | 1.5932e-05 | 2.0815e-05 | 2.724e-05 | 3.5705e-05 | 4.6865e-05 | 6.1592e-05 | 8.1039e-05 | 0.00010561 | 0.00010561 | 0.00010561 | 0.00010561 | 0.00010561 | 0.00010561 | 0.00010561 | 0.00010561 | 0.00010561 | 0.00010561 | 0.00010561 | 0.00010561 | 55.2847 | 69.7227 | 88.3618 | 112.4862 | 143.7845 | 184.4789 | 237.4965 | 306.6969 | 397.1726 | 515.6479 | 671.0079 | 875 | 1143.1645 | 1496.0695 | 1960.9506 | 2573.8874 | 3382.6937 | 4450.7568 | 5800.3803 | 5800.3803 | 5800.3803 | 5800.3803 | 5800.3803 | 5800.3803 | 5800.3803 | 5800.3803 | 5800.3803 | 5800.3803 | 5800.3803 | 5800.3803 |  | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 38.0982 | 50.5015 | 67.5273 | 91.0038 | 123.5074 | 168.6752 | 231.6504 | 319.716 | 443.1987 | 616.7569 | 861.22 | 1206.2129 | 1693.9049 |  | 24.6846 | 31.1312 | 39.4535 | 50.2251 | 64.1998 | 82.3698 | 106.0422 | 136.9402 | 177.3375 | 230.2367 | 299.605 | 390.6874 | 510.4228 | 667.9949 | 875.5643 | 1149.2405 | 1510.3724 | 1987.2625 | 2589.8692 | 2589.8692 | 2589.8692 | 2589.8692 | 2589.8692 | 2589.8692 | 2589.8692 | 2589.8692 | 2589.8692 | 2589.8692 | 2589.8692 | 2589.8692 |  | 14.212 | 14.212 | 14.212 | 14.212 | 14.212 | 14.212 | 14.212 | 14.212 | 14.212 | 14.212 | 14.212 | 14.212 | 14.212 | 14.212 | 14.212 | 14.212 | 14.212 | 17.0109 | 22.5489 | 30.1509 | 40.6332 | 55.146 | 75.3134 | 103.4319 | 142.7532 | 197.8882 | 275.3819 | 384.5347 | 538.574 | 756.3284 |  | 10.4726 | 16.9192 | 25.2415 | 36.0131 | 49.9878 | 68.1578 | 91.8302 | 122.7282 | 163.1255 | 216.0247 | 285.393 | 376.4754 | 496.2109 | 653.7829 | 861.3523 | 1135.0285 | 1496.1604 | 1970.2516 | 2567.3203 | 2559.7183 | 2549.236 | 2534.7232 | 2514.5558 | 2486.4374 | 2447.1161 | 2391.9811 | 2314.4873 | 2205.3346 | 2051.2953 | 1833.5409 |  | 0.070463 | 0.088865 | 0.11262 | 0.14337 | 0.18326 | 0.23513 | 0.3027 | 0.3909 | 0.50622 | 0.65722 | 0.85523 | 1.1152 | 1.457 | 1.9068 | 2.4993 | 3.2805 | 4.3114 | 5.6727 | 7.3929 | 7.3929 | 7.3929 | 7.3929 | 7.3929 | 7.3929 | 7.3929 | 7.3929 | 7.3929 | 7.3929 | 7.3929 | 7.3929 |  | 0.040569 | 0.040569 | 0.040569 | 0.040569 | 0.040569 | 0.040569 | 0.040569 | 0.040569 | 0.040569 | 0.040569 | 0.040569 | 0.040569 | 0.040569 | 0.040569 | 0.040569 | 0.040569 | 0.040569 | 0.048558 | 0.064367 | 0.086067 | 0.11599 | 0.15742 | 0.21498 | 0.29525 | 0.40749 | 0.56488 | 0.78609 | 1.0977 | 1.5374 | 2.159 |  | 0.029894 | 0.048296 | 0.072053 | 0.1028 | 0.14269 | 0.19456 | 0.26213 | 0.35033 | 0.46565 | 0.61665 | 0.81466 | 1.0747 | 1.4165 | 1.8662 | 2.4588 | 3.24 | 4.2708 | 5.6241 | 7.3285 | 7.3068 | 7.2769 | 7.2355 | 7.1779 | 7.0976 | 6.9854 | 6.828 | 6.6068 | 6.2952 | 5.8555 | 5.2339 |  | 10.5025 | 16.9675 | 25.3136 | 36.1159 | 50.1305 | 68.3524 | 92.0923 | 123.0785 | 163.5912 | 216.6414 | 286.2076 | 377.5501 | 497.6273 | 655.6492 | 863.811 | 1138.2685 | 1500.4313 | 1975.8758 | 2574.6488 | 2567.0251 | 2556.5129 | 2541.9587 | 2521.7337 | 2493.535 | 2454.1014 | 2398.809 | 2321.0941 | 2211.6298 | 2057.1508 | 1838.7748 |  | 25.4855 | 32.1412 | 40.7336 | 51.8546 | 66.2827 | 85.0422 | 109.4826 | 141.383 | 183.091 | 237.7065 | 309.3253 | 403.3629 | 526.983 | 689.6673 | 903.971 | 1186.5264 | 1559.3749 | 2051.7371 | 2673.8948 | 2673.8948 | 2673.8948 | 2673.8948 | 2673.8948 | 2673.8948 | 2673.8948 | 2673.8948 | 2673.8948 | 2673.8948 | 2673.8948 | 2673.8948 |  | 14.6731 | 14.6731 | 14.6731 | 14.6731 | 14.6731 | 14.6731 | 14.6731 | 14.6731 | 14.6731 | 14.6731 | 14.6731 | 14.6731 | 14.6731 | 14.6731 | 14.6731 | 14.6731 | 14.6731 | 17.5628 | 23.2805 | 31.1291 | 41.9515 | 56.9352 | 77.7569 | 106.7876 | 147.3847 | 204.3084 | 284.3164 | 397.0105 | 556.0474 | 780.8667 |  | 10.8124 | 17.4681 | 26.0605 | 37.1815 | 51.6096 | 70.3691 | 94.8095 | 126.71 | 168.418 | 223.0334 | 294.6523 | 388.6898 | 512.3099 | 674.9942 | 889.2979 | 1171.8533 | 1544.7018 | 2034.1744 | 2650.6143 | 2642.7657 | 2631.9433 | 2616.9596 | 2596.1379 | 2567.1072 | 2526.5102 | 2469.5864 | 2389.5784 | 2276.8843 | 2117.8474 | 1893.0282 |  | 3.5914 | 4.5293 | 5.7401 | 7.3072 | 9.3404 | 11.984 | 15.428 | 19.9234 | 25.8008 | 33.4971 | 43.5894 | 56.841 | 74.2613 | 97.1864 | 127.3856 | 167.2026 | 219.7436 | 289.1262 | 376.7993 | 376.7993 | 376.7993 | 376.7993 | 376.7993 | 376.7993 | 376.7993 | 376.7993 | 376.7993 | 376.7993 | 376.7993 | 376.7993 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.357 | 110.038 |  | 1.5237 | 2.4616 | 3.6724 | 5.2395 | 7.2727 | 9.9163 | 13.3603 | 17.8557 | 23.7331 | 31.4294 | 41.5217 | 54.7733 | 72.1936 | 95.1187 | 125.3179 | 165.1349 | 217.6759 | 286.6513 | 373.5186 | 372.4126 | 370.8875 | 368.7761 | 365.8419 | 361.751 | 356.0301 | 348.0086 | 336.734 | 320.8534 | 298.4423 | 266.7613 |  | 1.4528 | 1.8322 | 2.322 | 2.9559 | 3.7784 | 4.8478 | 6.241 | 8.0595 | 10.437 | 13.5503 | 17.6329 | 22.9935 | 30.0404 | 39.3142 | 51.5304 | 67.6374 | 88.8914 | 116.9583 | 152.4241 | 152.4241 | 152.4241 | 152.4241 | 152.4241 | 152.4241 | 152.4241 | 152.4241 | 152.4241 | 152.4241 | 152.4241 | 152.4241 |  | 0.83643 | 0.83643 | 0.83643 | 0.83643 | 0.83643 | 0.83643 | 0.83643 | 0.83643 | 0.83643 | 0.83643 | 0.83643 | 0.83643 | 0.83643 | 0.83643 | 0.83643 | 0.83643 | 0.83643 | 1.0012 | 1.3271 | 1.7745 | 2.3914 | 3.2456 | 4.4325 | 6.0874 | 8.4016 | 11.6465 | 16.2073 | 22.6314 | 31.6972 | 44.5129 |  | 0.61636 | 0.99576 | 1.4856 | 2.1195 | 2.942 | 4.0114 | 5.4046 | 7.223 | 9.6006 | 12.7139 | 16.7965 | 22.1571 | 29.204 | 38.4777 | 50.694 | 66.8009 | 88.055 | 115.9571 | 151.097 | 150.6496 | 150.0327 | 149.1785 | 147.9916 | 146.3367 | 144.0225 | 140.7776 | 136.2168 | 129.7927 | 120.7269 | 107.9112 |  | 23.455 | 37.893 | 56.532 | 80.6565 | 111.9548 | 152.6491 | 205.6668 | 274.8672 | 365.3428 | 483.8181 | 639.1781 | 843.1703 | 1111.3348 | 1464.2398 | 1929.1209 | 2542.0576 | 3350.864 | 4412.6585 | 5749.8788 | 5732.853 | 5709.3764 | 5676.8729 | 5631.7051 | 5568.7299 | 5480.6642 | 5357.1816 | 5183.6233 | 4939.1602 | 4594.1673 | 4106.4754
| TRUE | 2951 | 22008111 | MLN | MLN012 | 22 | MLN 12 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 6.6 | 0.017308 | 1.3617e-05 | 0.017294 | 47.6003 | 0.9532 | 48.5536 | 49.2077 | 6.925 | 19.6529 |  | 15.598 | 0.17662 | 0.00013896 | 0.17648 | 485.7464 | 9.7271 | 495.4735 | 502.1485 | 70.6675 | 200.5511 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.8681 |  | 124.3391 | 1268.8406 | 37.1263 | 1231.7143 |  | 0.086007 |  | 7.1928 | 7.8388 | 8.5428 | 9.3101 | 10.1463 | 11.0575 | 12.0507 | 13.133 | 14.3125 | 15.598 | 16.9989 | 18.5257 | 20.1895 | 22.0028 | 23.979 | 26.1326 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021585 | 0.027005 | 0.033883 | 0.042625 | 0.053753 | 0.067937 | 0.086039 | 0.10917 | 0.13875 | 0.17662 | 0.22515 | 0.28739 | 0.36726 | 0.46984 | 0.60168 | 0.7712 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.6983e-05 | 2.1246e-05 | 2.6658e-05 | 3.3536e-05 | 4.2291e-05 | 5.345e-05 | 6.7692e-05 | 8.5889e-05 | 0.00010916 | 0.00013896 | 0.00017714 | 0.0002261 | 0.00028895 | 0.00036966 | 0.00047338 | 0.00060675 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 155.0693 | 194.0026 | 243.4122 | 306.2157 | 386.1597 | 488.0588 | 618.1035 | 784.2573 | 996.7702 | 1268.8406 | 1617.4709 | 2064.5716 | 2638.3894 | 3375.3499 | 4322.4413 | 5540.2929 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 |  | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 44.4378 | 58.905 | 78.764 | 106.147 | 144.0592 | 196.743 | 270.1974 | 372.9174 | 516.9478 | 719.3864 | 1004.5286 | 1406.929 | 1975.7738 |  | 59.3647 | 74.2694 | 93.1847 | 117.2276 | 147.8323 | 186.8421 | 236.6266 | 300.2348 | 381.5905 | 485.7464 | 619.2114 | 790.3736 | 1010.0465 | 1292.1748 | 1654.7469 | 2120.9733 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 45.1518 | 60.0565 | 78.9718 | 103.0147 | 133.6194 | 172.6291 | 222.4137 | 286.0219 | 367.3775 | 471.5334 | 604.9984 | 776.1607 | 995.8335 | 1277.9619 | 1640.5339 | 2106.7603 | 2575.831 | 2573.032 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 1.1888 | 1.4873 | 1.866 | 2.3475 | 2.9604 | 3.7415 | 4.7385 | 6.0122 | 7.6414 | 9.7271 | 12.3998 | 15.8273 | 20.2263 | 25.8759 | 33.1365 | 42.4727 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.90417 | 1.2026 | 1.5814 | 2.0629 | 2.6757 | 3.4569 | 4.4539 | 5.7276 | 7.3568 | 9.4425 | 12.1152 | 15.5427 | 19.9417 | 25.5913 | 32.8519 | 42.1881 | 51.5813 | 51.5252 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 46.0559 | 61.2591 | 80.5532 | 105.0776 | 136.2951 | 176.086 | 226.8676 | 291.7495 | 374.7343 | 480.9759 | 617.1136 | 791.7034 | 1015.7752 | 1303.5532 | 1673.3858 | 2148.9484 | 2627.4123 | 2624.5572 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 61.3693 | 76.7773 | 96.3313 | 121.186 | 152.8242 | 193.1511 | 244.6168 | 310.3728 | 394.4756 | 502.1485 | 640.1202 | 817.0621 | 1044.1526 | 1335.8076 | 1710.6226 | 2192.592 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 46.6764 | 62.0844 | 81.6384 | 106.4932 | 138.1313 | 178.4583 | 229.9239 | 295.6799 | 379.7827 | 487.4556 | 625.4274 | 802.3692 | 1029.4598 | 1321.1147 | 1695.9297 | 2177.8991 | 2662.8089 | 2659.9153 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 8.6365 | 10.8049 | 13.5567 | 17.0545 | 21.507 | 27.1822 | 34.425 | 43.6789 | 55.5147 | 70.6675 | 90.0843 | 114.9854 | 146.9439 | 187.9886 | 240.7364 | 308.5641 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 6.5688 | 8.7372 | 11.489 | 14.9868 | 19.4393 | 25.1145 | 32.3573 | 41.6111 | 53.4469 | 68.5998 | 88.0166 | 112.9177 | 144.8762 | 185.9209 | 238.6687 | 306.4964 | 374.7379 | 374.3307 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 24.51 | 30.6638 | 38.4734 | 48.4 | 61.0359 | 77.1419 | 97.6966 | 123.9586 | 157.5481 | 200.5511 | 255.6551 | 326.3233 | 417.0201 | 533.503 | 683.1989 | 875.6908 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 |  | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 7.0238 | 9.3104 | 12.4493 | 16.7774 | 22.7698 | 31.0969 | 42.707 | 58.9428 | 81.708 | 113.7052 | 158.7744 | 222.3772 | 312.288 |  | 18.6419 | 24.7956 | 32.6053 | 42.5319 | 55.1677 | 71.2738 | 91.8284 | 118.0905 | 151.68 | 194.683 | 249.787 | 320.4551 | 411.1519 | 527.6349 | 677.3308 | 869.8227 | 1063.4889 | 1062.3333 | 1060.0466 | 1056.9077 | 1052.5796 | 1046.5873 | 1038.2601 | 1026.65 | 1010.4143 | 987.649 | 955.6519 | 910.5827 | 846.9799 | 757.0691 |  | 117.943 | 156.8763 | 206.2859 | 269.0894 | 349.0334 | 450.9326 | 580.9772 | 747.131 | 959.6439 | 1231.7143 | 1580.3446 | 2027.4454 | 2601.2631 | 3338.2236 | 4285.315 | 5503.1666 | 6728.448 | 6721.1364 | 6706.6693 | 6686.8103 | 6659.4272 | 6621.515 | 6568.8312 | 6495.3768 | 6392.6569 | 6248.6265 | 6046.1879 | 5761.0456 | 5358.6453 | 4789.8005
| TRUE | 2952 | 22005017 | MLN | MLN013 | 22 | MLN 13 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 6.6 | 0.017308 | 1.3617e-05 | 0.017294 | 47.6003 | 0.9532 | 48.5536 | 49.2077 | 6.925 | 39.3057 |  | 15.598 | 0.17662 | 0.00013896 | 0.17648 | 485.7464 | 9.7271 | 495.4735 | 502.1485 | 70.6675 | 401.1023 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 11.7363 |  | 143.9919 | 1469.3918 | 42.9944 | 1426.3974 |  | 0.086007 |  | 7.1928 | 7.8388 | 8.5428 | 9.3101 | 10.1463 | 11.0575 | 12.0507 | 13.133 | 14.3125 | 15.598 | 16.9989 | 18.5257 | 20.1895 | 22.0028 | 23.979 | 26.1326 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021585 | 0.027005 | 0.033883 | 0.042625 | 0.053753 | 0.067937 | 0.086039 | 0.10917 | 0.13875 | 0.17662 | 0.22515 | 0.28739 | 0.36726 | 0.46984 | 0.60168 | 0.7712 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.6983e-05 | 2.1246e-05 | 2.6658e-05 | 3.3536e-05 | 4.2291e-05 | 5.345e-05 | 6.7692e-05 | 8.5889e-05 | 0.00010916 | 0.00013896 | 0.00017714 | 0.0002261 | 0.00028895 | 0.00036966 | 0.00047338 | 0.00060675 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 179.5793 | 224.6663 | 281.8856 | 354.6157 | 447.1956 | 565.2007 | 715.8 | 908.2159 | 1154.3183 | 1469.3918 | 1873.126 | 2390.8949 | 3055.4095 | 3908.8529 | 5005.6402 | 6415.9837 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 | 7834.9313 |  | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 42.9944 | 51.4616 | 68.2154 | 91.2133 | 122.9245 | 166.829 | 227.8399 | 312.9044 | 431.8602 | 598.6558 | 833.0916 | 1163.303 | 1629.3062 | 2288.0618 |  | 59.3647 | 74.2694 | 93.1847 | 117.2276 | 147.8323 | 186.8421 | 236.6266 | 300.2348 | 381.5905 | 485.7464 | 619.2114 | 790.3736 | 1010.0465 | 1292.1748 | 1654.7469 | 2120.9733 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 45.1518 | 60.0565 | 78.9718 | 103.0147 | 133.6194 | 172.6291 | 222.4137 | 286.0219 | 367.3775 | 471.5334 | 604.9984 | 776.1607 | 995.8335 | 1277.9619 | 1640.5339 | 2106.7603 | 2575.831 | 2573.032 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 1.1888 | 1.4873 | 1.866 | 2.3475 | 2.9604 | 3.7415 | 4.7385 | 6.0122 | 7.6414 | 9.7271 | 12.3998 | 15.8273 | 20.2263 | 25.8759 | 33.1365 | 42.4727 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.90417 | 1.2026 | 1.5814 | 2.0629 | 2.6757 | 3.4569 | 4.4539 | 5.7276 | 7.3568 | 9.4425 | 12.1152 | 15.5427 | 19.9417 | 25.5913 | 32.8519 | 42.1881 | 51.5813 | 51.5252 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 46.0559 | 61.2591 | 80.5532 | 105.0776 | 136.2951 | 176.086 | 226.8676 | 291.7495 | 374.7343 | 480.9759 | 617.1136 | 791.7034 | 1015.7752 | 1303.5532 | 1673.3858 | 2148.9484 | 2627.4123 | 2624.5572 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 61.3693 | 76.7773 | 96.3313 | 121.186 | 152.8242 | 193.1511 | 244.6168 | 310.3728 | 394.4756 | 502.1485 | 640.1202 | 817.0621 | 1044.1526 | 1335.8076 | 1710.6226 | 2192.592 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 46.6764 | 62.0844 | 81.6384 | 106.4932 | 138.1313 | 178.4583 | 229.9239 | 295.6799 | 379.7827 | 487.4556 | 625.4274 | 802.3692 | 1029.4598 | 1321.1147 | 1695.9297 | 2177.8991 | 2662.8089 | 2659.9153 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 8.6365 | 10.8049 | 13.5567 | 17.0545 | 21.507 | 27.1822 | 34.425 | 43.6789 | 55.5147 | 70.6675 | 90.0843 | 114.9854 | 146.9439 | 187.9886 | 240.7364 | 308.5641 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 6.5688 | 8.7372 | 11.489 | 14.9868 | 19.4393 | 25.1145 | 32.3573 | 41.6111 | 53.4469 | 68.5998 | 88.0166 | 112.9177 | 144.8762 | 185.9209 | 238.6687 | 306.4964 | 374.7379 | 374.3307 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 49.0201 | 61.3275 | 76.9468 | 96.8 | 122.0717 | 154.2838 | 195.3931 | 247.9172 | 315.0962 | 401.1023 | 511.3103 | 652.6465 | 834.0401 | 1067.006 | 1366.3978 | 1751.3816 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 | 2138.7141 |  | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 11.7363 | 14.0476 | 18.6209 | 24.8986 | 33.5549 | 45.5396 | 62.1938 | 85.414 | 117.8856 | 163.4161 | 227.4104 | 317.5487 | 444.7544 | 624.576 |  | 37.2838 | 49.5913 | 65.2105 | 85.0638 | 110.3355 | 142.5475 | 183.6569 | 236.1809 | 303.3599 | 389.366 | 499.574 | 640.9103 | 822.3039 | 1055.2698 | 1354.6616 | 1739.6454 | 2126.9778 | 2124.6665 | 2120.0932 | 2113.8155 | 2105.1592 | 2093.1745 | 2076.5203 | 2053.3001 | 2020.8285 | 1975.298 | 1911.3037 | 1821.1654 | 1693.9597 | 1514.1381 |  | 136.5849 | 181.6719 | 238.8912 | 311.6213 | 404.2012 | 522.2063 | 672.8056 | 865.2215 | 1111.3239 | 1426.3974 | 1830.1316 | 2347.9005 | 3012.415 | 3865.8585 | 4962.6458 | 6372.9893 | 7791.9369 | 7783.4697 | 7766.7159 | 7743.718 | 7712.0068 | 7668.1023 | 7607.0914 | 7522.0269 | 7403.0711 | 7236.2755 | 7001.8397 | 6671.6283 | 6205.6251 | 5546.8695
| TRUE | 2953 | 22009939 | MLN | MLN014 | 22 | MLN 14 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 3.6241 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.8681 |  | 10.5848 | 0.060301 | 4.7442e-05 | 0.060253 | 165.8402 | 3.321 | 169.1611 | 171.4401 | 24.1268 | 68.4708 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.8681 |  | 37.1263 | 433.1988 | 37.1263 | 396.0725 |  | 0.10718 |  | 4.0341 | 4.4905 | 4.9985 | 5.564 | 6.1935 | 6.8943 | 7.6743 | 8.5425 | 9.509 | 10.5848 | 11.7823 | 13.1153 | 14.5992 | 16.2509 | 18.0895 | 20.1361 | 22.4142 | 24.9501 | 27.7729 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.005268 | 0.0067412 | 0.0086907 | 0.011281 | 0.014733 | 0.019351 | 0.025546 | 0.033879 | 0.045116 | 0.060301 | 0.080864 | 0.10876 | 0.14667 | 0.19826 | 0.26856 | 0.36449 | 0.49551 | 0.67465 | 0.91979 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.1447e-06 | 5.3037e-06 | 6.8375e-06 | 8.8752e-06 | 1.1592e-05 | 1.5225e-05 | 2.0099e-05 | 2.6655e-05 | 3.5495e-05 | 4.7442e-05 | 6.3621e-05 | 8.5569e-05 | 0.00011539 | 0.00015598 | 0.0002113 | 0.00028677 | 0.00038985 | 0.00053079 | 0.00072366 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 37.8453 | 48.4286 | 62.434 | 81.0395 | 105.8438 | 139.0197 | 183.5244 | 243.3881 | 324.1095 | 433.1988 | 580.9237 | 781.3338 | 1053.6683 | 1424.2925 | 1929.3597 | 2618.4742 | 3559.7307 | 4846.6513 | 6607.7353 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 | 6765.5743 |  | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 37.1263 | 44.4378 | 58.905 | 78.764 | 106.147 | 144.0592 | 196.743 | 270.1974 | 372.9174 | 516.9478 | 719.3864 | 1004.5286 | 1406.929 | 1975.7738 |  | 14.4882 | 18.5398 | 23.9014 | 31.0241 | 40.5199 | 53.2205 | 70.2581 | 93.1755 | 124.0778 | 165.8402 | 222.3932 | 299.1156 | 403.3726 | 545.2575 | 738.6108 | 1002.4224 | 1362.7607 | 1855.4286 | 2529.619 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0.27525 | 4.3268 | 9.6885 | 16.8112 | 26.3069 | 39.0076 | 56.0452 | 78.9626 | 109.8649 | 151.6272 | 208.1803 | 284.9027 | 389.1596 | 531.0446 | 724.3979 | 988.2095 | 1348.5478 | 1838.4166 | 2507.0686 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.29013 | 0.37126 | 0.47863 | 0.62126 | 0.81141 | 1.0657 | 1.4069 | 1.8659 | 2.4847 | 3.321 | 4.4534 | 5.9898 | 8.0776 | 10.9188 | 14.7908 | 20.0736 | 27.2894 | 37.1552 | 50.6559 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.005512 | 0.086645 | 0.19401 | 0.33665 | 0.5268 | 0.78113 | 1.1223 | 1.5812 | 2.2001 | 3.0364 | 4.1688 | 5.7052 | 7.793 | 10.6342 | 14.5061 | 19.789 | 27.0048 | 36.8145 | 50.2043 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0.28077 | 4.4135 | 9.8825 | 17.1478 | 26.8337 | 39.7887 | 57.1675 | 80.5438 | 112.065 | 154.6636 | 212.3491 | 290.6079 | 396.9526 | 541.6788 | 738.9041 | 1007.9985 | 1375.5526 | 1875.2311 | 2557.2729 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.9774 | 19.1658 | 24.7085 | 32.0717 | 41.8881 | 55.0176 | 72.6305 | 96.3218 | 128.2676 | 171.4401 | 229.9028 | 309.2158 | 416.9932 | 563.6692 | 763.5515 | 1036.2711 | 1408.7769 | 1918.0807 | 2615.0364 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0.28455 | 4.4729 | 10.0156 | 17.3788 | 27.1952 | 40.3247 | 57.9376 | 81.6289 | 113.5747 | 156.7472 | 215.2099 | 294.5229 | 402.3004 | 548.9763 | 748.8586 | 1021.5782 | 1394.0841 | 1900.4942 | 2591.7245 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.1078 | 2.6972 | 3.4772 | 4.5135 | 5.8949 | 7.7426 | 10.2213 | 13.5554 | 18.0511 | 24.1268 | 32.3543 | 43.516 | 58.6836 | 79.3253 | 107.4548 | 145.8347 | 198.2576 | 269.9321 | 368.0148 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.040045 | 0.62948 | 1.4095 | 2.4457 | 3.8272 | 5.6749 | 8.1536 | 11.4877 | 15.9834 | 22.0591 | 30.2866 | 41.4483 | 56.6158 | 77.2576 | 105.3871 | 143.767 | 196.1899 | 267.4571 | 364.7342 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 5.9818 | 7.6546 | 9.8682 | 12.809 | 16.7295 | 21.9733 | 29.0076 | 38.4696 | 51.2283 | 68.4708 | 91.82 | 123.4965 | 166.5413 | 225.1216 | 304.9519 | 413.8723 | 562.646 | 766.0548 | 1044.4093 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 | 1069.357 |  | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 5.8681 | 7.0238 | 9.3104 | 12.4493 | 16.7774 | 22.7698 | 31.0969 | 42.707 | 58.9428 | 81.708 | 113.7052 | 158.7744 | 222.3772 | 312.288 |  | 0.11364 | 1.7864 | 4.0001 | 6.9409 | 10.8614 | 16.1051 | 23.1395 | 32.6015 | 45.3602 | 62.6027 | 85.9519 | 117.6284 | 160.6732 | 219.2535 | 299.0837 | 408.0042 | 556.7778 | 759.031 | 1035.0988 | 1056.9077 | 1052.5796 | 1046.5873 | 1038.2601 | 1026.65 | 1010.4143 | 987.649 | 955.6519 | 910.5827 | 846.9799 | 757.0691 |  | 0.71901 | 11.3023 | 25.3077 | 43.9132 | 68.7176 | 101.8934 | 146.3982 | 206.2619 | 286.9832 | 396.0725 | 543.7975 | 744.2075 | 1016.542 | 1387.1662 | 1892.2335 | 2581.3479 | 3522.6044 | 4802.2135 | 6548.8304 | 6686.8103 | 6659.4272 | 6621.515 | 6568.8312 | 6495.3768 | 6392.6569 | 6248.6265 | 6046.1879 | 5761.0456 | 5358.6453 | 4789.8005
| TRUE | 2954 | 22009938 | MLN | MLN021 | 22 | MLN 21 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 3.6241 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.9974 |  | 10.5848 | 0.060301 | 4.7442e-05 | 0.060253 | 165.8402 | 3.321 | 169.1611 | 171.4401 | 24.1268 | 69.9794 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.9974 |  | 37.2556 | 434.7075 | 37.2556 | 397.4519 |  | 0.10718 |  | 4.0341 | 4.4905 | 4.9985 | 5.564 | 6.1935 | 6.8943 | 7.6743 | 8.5425 | 9.509 | 10.5848 | 11.7823 | 13.1153 | 14.5992 | 16.2509 | 18.0895 | 20.1361 | 22.4142 | 24.9501 | 27.7729 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.005268 | 0.0067412 | 0.0086907 | 0.011281 | 0.014733 | 0.019351 | 0.025546 | 0.033879 | 0.045116 | 0.060301 | 0.080864 | 0.10876 | 0.14667 | 0.19826 | 0.26856 | 0.36449 | 0.49551 | 0.67465 | 0.91979 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.1447e-06 | 5.3037e-06 | 6.8375e-06 | 8.8752e-06 | 1.1592e-05 | 1.5225e-05 | 2.0099e-05 | 2.6655e-05 | 3.5495e-05 | 4.7442e-05 | 6.3621e-05 | 8.5569e-05 | 0.00011539 | 0.00015598 | 0.0002113 | 0.00028677 | 0.00038985 | 0.00053079 | 0.00072366 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 37.9771 | 48.5972 | 62.6514 | 81.3217 | 106.2124 | 139.5039 | 184.1636 | 244.2357 | 325.2382 | 434.7075 | 582.9468 | 784.0548 | 1057.3377 | 1429.2526 | 1936.0788 | 2627.5931 | 3572.1276 | 4863.53 | 6630.747 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 |  | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 44.5926 | 59.1101 | 79.0383 | 106.5167 | 144.5609 | 197.4282 | 271.1384 | 374.2161 | 518.7481 | 721.8917 | 1008.0269 | 1411.8287 | 1982.6545 |  | 14.4882 | 18.5398 | 23.9014 | 31.0241 | 40.5199 | 53.2205 | 70.2581 | 93.1755 | 124.0778 | 165.8402 | 222.3932 | 299.1156 | 403.3726 | 545.2575 | 738.6108 | 1002.4224 | 1362.7607 | 1855.4286 | 2529.619 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0.27525 | 4.3268 | 9.6885 | 16.8112 | 26.3069 | 39.0076 | 56.0452 | 78.9626 | 109.8649 | 151.6272 | 208.1803 | 284.9027 | 389.1596 | 531.0446 | 724.3979 | 988.2095 | 1348.5478 | 1838.4166 | 2507.0686 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.29013 | 0.37126 | 0.47863 | 0.62126 | 0.81141 | 1.0657 | 1.4069 | 1.8659 | 2.4847 | 3.321 | 4.4534 | 5.9898 | 8.0776 | 10.9188 | 14.7908 | 20.0736 | 27.2894 | 37.1552 | 50.6559 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.005512 | 0.086645 | 0.19401 | 0.33665 | 0.5268 | 0.78113 | 1.1223 | 1.5812 | 2.2001 | 3.0364 | 4.1688 | 5.7052 | 7.793 | 10.6342 | 14.5061 | 19.789 | 27.0048 | 36.8145 | 50.2043 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0.28077 | 4.4135 | 9.8825 | 17.1478 | 26.8337 | 39.7887 | 57.1675 | 80.5438 | 112.065 | 154.6636 | 212.3491 | 290.6079 | 396.9526 | 541.6788 | 738.9041 | 1007.9985 | 1375.5526 | 1875.2311 | 2557.2729 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.9774 | 19.1658 | 24.7085 | 32.0717 | 41.8881 | 55.0176 | 72.6305 | 96.3218 | 128.2676 | 171.4401 | 229.9028 | 309.2158 | 416.9932 | 563.6692 | 763.5515 | 1036.2711 | 1408.7769 | 1918.0807 | 2615.0364 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0.28455 | 4.4729 | 10.0156 | 17.3788 | 27.1952 | 40.3247 | 57.9376 | 81.6289 | 113.5747 | 156.7472 | 215.2099 | 294.5229 | 402.3004 | 548.9763 | 748.8586 | 1021.5782 | 1394.0841 | 1900.4942 | 2591.7245 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.1078 | 2.6972 | 3.4772 | 4.5135 | 5.8949 | 7.7426 | 10.2213 | 13.5554 | 18.0511 | 24.1268 | 32.3543 | 43.516 | 58.6836 | 79.3253 | 107.4548 | 145.8347 | 198.2576 | 269.9321 | 368.0148 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.040045 | 0.62948 | 1.4095 | 2.4457 | 3.8272 | 5.6749 | 8.1536 | 11.4877 | 15.9834 | 22.0591 | 30.2866 | 41.4483 | 56.6158 | 77.2576 | 105.3871 | 143.767 | 196.1899 | 267.4571 | 364.7342 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 6.1136 | 7.8232 | 10.0857 | 13.0912 | 17.0981 | 22.4574 | 29.6467 | 39.3172 | 52.357 | 69.9794 | 93.8431 | 126.2175 | 170.2108 | 230.0818 | 311.6709 | 422.9913 | 575.0429 | 782.9335 | 1067.421 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 |  | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 7.1785 | 9.5156 | 12.7236 | 17.1471 | 23.2715 | 31.7821 | 43.648 | 60.2415 | 83.5083 | 116.2105 | 162.2727 | 227.2769 | 319.1687 |  | 0.11615 | 1.8258 | 4.0882 | 7.0938 | 11.1007 | 16.46 | 23.6493 | 33.3198 | 46.3596 | 63.982 | 87.8456 | 120.2201 | 164.2133 | 224.0844 | 305.6735 | 416.9938 | 569.0454 | 775.7549 | 1057.9054 | 1080.1948 | 1075.7713 | 1069.6469 | 1061.1363 | 1049.2704 | 1032.6769 | 1009.4101 | 976.7079 | 930.6458 | 865.6415 | 773.7497 |  | 0.72151 | 11.3417 | 25.3958 | 44.0662 | 68.9569 | 102.2483 | 146.908 | 206.9802 | 287.9826 | 397.4519 | 545.6913 | 746.7992 | 1020.0821 | 1391.9971 | 1898.8232 | 2590.3376 | 3534.872 | 4818.9374 | 6571.6369 | 6710.0974 | 6682.6189 | 6644.5747 | 6591.7074 | 6517.9972 | 6414.9196 | 6270.3876 | 6067.2439 | 5781.1087 | 5377.307 | 4806.4811
| TRUE | 2955 | 22009802 | MLN | MLN022 | 22 | MLN 22 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 4.0857 | 0.0054221 | 4.2659e-06 | 0.0054179 | 14.9121 | 0.29862 | 15.2107 | 15.4156 | 2.1694 | 6.2924 |  | 11.2347 | 0.070957 | 5.5827e-05 | 0.070902 | 195.148 | 3.9079 | 199.0559 | 201.7376 | 28.3906 | 82.3464 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.9974 |  | 39.0882 | 511.5305 | 37.2556 | 474.275 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0068474 | 0.0087043 | 0.011132 | 0.014316 | 0.018505 | 0.024029 | 0.031333 | 0.041011 | 0.053862 | 0.070957 | 0.093738 | 0.12414 | 0.16478 | 0.21915 | 0.292 | 0.38971 | 0.52087 | 0.69709 | 0.93404 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 5.3872e-06 | 6.8482e-06 | 8.7584e-06 | 1.1264e-05 | 1.4559e-05 | 1.8905e-05 | 2.4651e-05 | 3.2266e-05 | 4.2376e-05 | 5.5827e-05 | 7.375e-05 | 9.767e-05 | 0.00012964 | 0.00017242 | 0.00022974 | 0.00030661 | 0.0004098 | 0.00054844 | 0.00073487 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 49.3625 | 62.7494 | 80.2516 | 103.2067 | 133.4013 | 173.2249 | 225.8773 | 295.6472 | 388.2891 | 511.5305 | 675.7573 | 894.9377 | 1187.8709 | 1579.873 | 2105.0549 | 2809.4002 | 3754.926 | 5025.3075 | 6733.4835 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 |  | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 44.5926 | 59.1101 | 79.0383 | 106.5167 | 144.5609 | 197.4282 | 271.1384 | 374.2161 | 518.7481 | 721.8917 | 1008.0269 | 1411.8287 | 1982.6545 |  | 18.8317 | 23.9388 | 30.6159 | 39.3732 | 50.8924 | 66.085 | 86.1718 | 112.7889 | 148.1316 | 195.148 | 257.8003 | 341.4172 | 453.1708 | 602.7189 | 803.0749 | 1071.7815 | 1432.498 | 1917.1465 | 2568.8127 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 4.6188 | 9.7259 | 16.4029 | 25.1602 | 36.6794 | 51.8721 | 71.9589 | 98.576 | 133.9187 | 180.9351 | 243.5873 | 327.2043 | 438.9578 | 588.506 | 788.862 | 1057.5686 | 1418.2851 | 1900.1345 | 2546.2623 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.37711 | 0.47938 | 0.61309 | 0.78845 | 1.0191 | 1.3234 | 1.7256 | 2.2586 | 2.9664 | 3.9079 | 5.1625 | 6.8369 | 9.0748 | 12.0695 | 16.0817 | 21.4625 | 28.6859 | 38.3911 | 51.4408 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.092491 | 0.19476 | 0.32847 | 0.50384 | 0.73451 | 1.0387 | 1.441 | 1.974 | 2.6817 | 3.6232 | 4.8779 | 6.5523 | 8.7902 | 11.7849 | 15.797 | 21.1779 | 28.4013 | 38.0504 | 50.9892 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 4.7113 | 9.9206 | 16.7314 | 25.6641 | 37.4139 | 52.9108 | 73.3999 | 100.55 | 136.6004 | 184.5584 | 248.4652 | 333.7566 | 447.748 | 600.2909 | 804.659 | 1078.7465 | 1446.6864 | 1938.1849 | 2597.2515 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 19.4676 | 24.7471 | 31.6497 | 40.7027 | 52.6108 | 68.3165 | 89.0816 | 116.5974 | 153.1336 | 201.7376 | 266.5054 | 352.9458 | 468.4729 | 623.0709 | 830.1923 | 1107.9722 | 1480.869 | 1981.8826 | 2655.5536 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 4.7747 | 10.0543 | 16.9568 | 26.0098 | 37.918 | 53.6236 | 74.3887 | 101.9046 | 138.4407 | 187.0447 | 251.8125 | 338.253 | 453.7801 | 608.378 | 815.4994 | 1093.2794 | 1466.1762 | 1964.2961 | 2632.2417 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.7397 | 3.4827 | 4.4541 | 5.7281 | 7.4039 | 9.6142 | 12.5365 | 16.4088 | 21.5505 | 28.3906 | 37.5054 | 49.6702 | 65.9283 | 87.6849 | 116.8332 | 155.9253 | 208.4031 | 278.9109 | 373.7168 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.67195 | 1.4149 | 2.3863 | 3.6604 | 5.3362 | 7.5465 | 10.4687 | 14.3411 | 19.4828 | 26.3229 | 35.4377 | 47.6024 | 63.8606 | 85.6172 | 114.7655 | 153.8575 | 206.3354 | 276.436 | 370.4362 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 7.9464 | 10.1014 | 12.9189 | 16.6143 | 21.475 | 27.8858 | 36.3618 | 47.5934 | 62.507 | 82.3464 | 108.7837 | 144.0675 | 191.224 | 254.3287 | 338.8728 | 452.2586 | 604.4699 | 808.9765 | 1083.9595 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 |  | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 7.1785 | 9.5156 | 12.7236 | 17.1471 | 23.2715 | 31.7821 | 43.648 | 60.2415 | 83.5083 | 116.2105 | 162.2727 | 227.2769 | 319.1687 |  | 1.949 | 4.104 | 6.9215 | 10.6168 | 15.4776 | 21.8884 | 30.3644 | 41.596 | 56.5095 | 76.349 | 102.7863 | 138.0701 | 185.2266 | 248.3313 | 332.8754 | 446.2612 | 598.4724 | 801.798 | 1074.4439 | 1080.1948 | 1075.7713 | 1069.6469 | 1061.1363 | 1049.2704 | 1032.6769 | 1009.4101 | 976.7079 | 930.6458 | 865.6415 | 773.7497 |  | 12.1069 | 25.4938 | 42.996 | 65.9511 | 96.1457 | 135.9694 | 188.6217 | 258.3916 | 351.0335 | 474.275 | 638.5017 | 857.6821 | 1150.6153 | 1542.6174 | 2067.7993 | 2772.1446 | 3717.6704 | 4980.7149 | 6674.3733 | 6710.0974 | 6682.6189 | 6644.5747 | 6591.7074 | 6517.9972 | 6414.9196 | 6270.3876 | 6067.2439 | 5781.1087 | 5377.307 | 4806.4811
| TRUE | 2956 | 22013029 | MLN | MLN023 | 22 | MLN 23 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 1.7651 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.9974 |  | 7.1689 | 0.021401 | 1.6837e-05 | 0.021384 | 58.8568 | 1.1786 | 60.0354 | 60.8442 | 8.5626 | 24.8358 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.9974 |  | 37.2556 | 154.2781 | 37.2556 | 117.0225 |  | 0.14015 |  | 2.0307 | 2.3362 | 2.6877 | 3.0921 | 3.5573 | 4.0924 | 4.7082 | 5.4165 | 6.2314 | 7.1689 | 8.2475 | 9.4883 | 10.9158 | 12.5581 | 14.4475 | 16.6211 | 19.1217 | 21.9985 | 25.3082 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054426 | 0.0075349 | 0.01056 | 0.014961 | 0.021401 | 0.030869 | 0.044852 | 0.065583 | 0.096424 | 0.14244 | 0.21128 | 0.3145 | 0.46958 | 0.70298 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.282e-06 | 5.9282e-06 | 8.3082e-06 | 1.1771e-05 | 1.6837e-05 | 2.4287e-05 | 3.5288e-05 | 5.1599e-05 | 7.5863e-05 | 0.00011207 | 0.00016623 | 0.00024744 | 0.00036945 | 0.00055308 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 39.2353 | 54.3189 | 76.1272 | 107.8562 | 154.2781 | 222.535 | 323.3397 | 472.7904 | 695.1188 | 1026.8523 | 1523.1238 | 2267.2416 | 3385.2123 | 5067.7874 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 | 6789.1356 |  | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 37.2556 | 44.5926 | 59.1101 | 79.0383 | 106.5167 | 144.5609 | 197.4282 | 271.1384 | 374.2161 | 518.7481 | 721.8917 | 1008.0269 | 1411.8287 | 1982.6545 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.9682 | 20.7226 | 29.0424 | 41.147 | 58.8568 | 84.8967 | 123.3536 | 180.3688 | 265.1867 | 391.7424 | 581.0692 | 864.9489 | 1291.4529 | 1933.3525 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0.75527 | 6.5096 | 14.8294 | 26.934 | 44.6439 | 70.6838 | 109.1406 | 166.1558 | 250.9737 | 377.5295 | 566.8562 | 850.736 | 1274.4409 | 1910.8021 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.29974 | 0.41497 | 0.58158 | 0.82397 | 1.1786 | 1.7001 | 2.4702 | 3.6119 | 5.3104 | 7.8447 | 11.636 | 17.3207 | 25.8615 | 38.7156 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0 | 0 | 0.015124 | 0.13036 | 0.29696 | 0.53936 | 0.894 | 1.4155 | 2.1856 | 3.3273 | 5.0258 | 7.5601 | 11.3514 | 17.0361 | 25.5208 | 38.264 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 0 | 0 | 0.7704 | 6.64 | 15.1264 | 27.4734 | 45.5379 | 72.0993 | 111.3262 | 169.4831 | 255.9995 | 385.0896 | 578.2076 | 867.7721 | 1299.9617 | 1949.0661 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 15.4736 | 21.4223 | 30.0231 | 42.5364 | 60.8442 | 87.7634 | 127.5188 | 186.4593 | 274.1412 | 404.9704 | 600.6901 | 894.1556 | 1335.0612 | 1998.6358 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0.78078 | 6.7294 | 15.3302 | 27.8435 | 46.1514 | 73.0706 | 112.826 | 171.7664 | 259.4483 | 390.2775 | 585.9972 | 879.4627 | 1317.4748 | 1975.3239 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1776 | 3.0148 | 4.2252 | 5.9862 | 8.5626 | 12.351 | 17.9458 | 26.2405 | 38.58 | 56.9916 | 84.5353 | 125.8348 | 187.8836 | 281.2686 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0.10988 | 0.94704 | 2.1574 | 3.9184 | 6.4949 | 10.2832 | 15.878 | 24.1727 | 36.5122 | 54.9239 | 82.4676 | 123.767 | 185.4086 | 277.9879 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 6.3161 | 8.7443 | 12.255 | 17.3627 | 24.8358 | 35.8238 | 52.0514 | 76.11 | 111.9006 | 165.3032 | 245.1932 | 364.9817 | 544.9532 | 815.8149 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 | 1092.9184 |  | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 5.9974 | 7.1785 | 9.5156 | 12.7236 | 17.1471 | 23.2715 | 31.7821 | 43.648 | 60.2415 | 83.5083 | 116.2105 | 162.2727 | 227.2769 | 319.1687 |  | 0 | 0 | 0 | 0 | 0 | 0.3187 | 2.7469 | 6.2576 | 11.3653 | 18.8383 | 29.8264 | 46.054 | 70.1126 | 105.9031 | 159.3058 | 239.1958 | 358.9843 | 537.7746 | 806.2994 | 1080.1948 | 1075.7713 | 1069.6469 | 1061.1363 | 1049.2704 | 1032.6769 | 1009.4101 | 976.7079 | 930.6458 | 865.6415 | 773.7497 |  | 0 | 0 | 0 | 0 | 0 | 1.9798 | 17.0633 | 38.8716 | 70.6006 | 117.0225 | 185.2795 | 286.0841 | 435.5348 | 657.8632 | 989.5967 | 1485.8682 | 2229.9861 | 3340.6197 | 5008.6773 | 6710.0974 | 6682.6189 | 6644.5747 | 6591.7074 | 6517.9972 | 6414.9196 | 6270.3876 | 6067.2439 | 5781.1087 | 5377.307 | 4806.4811
| TRUE | 2957 | 22009937 | MLN | MLN024 | 22 | MLN 24 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 3.6241 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 11.9948 |  | 10.5848 | 0.060301 | 4.7442e-05 | 0.060253 | 165.8402 | 3.321 | 169.1611 | 171.4401 | 24.1268 | 139.9588 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 11.9948 |  | 43.253 | 504.6869 | 43.253 | 461.4339 |  | 0.10718 |  | 4.0341 | 4.4905 | 4.9985 | 5.564 | 6.1935 | 6.8943 | 7.6743 | 8.5425 | 9.509 | 10.5848 | 11.7823 | 13.1153 | 14.5992 | 16.2509 | 18.0895 | 20.1361 | 22.4142 | 24.9501 | 27.7729 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.005268 | 0.0067412 | 0.0086907 | 0.011281 | 0.014733 | 0.019351 | 0.025546 | 0.033879 | 0.045116 | 0.060301 | 0.080864 | 0.10876 | 0.14667 | 0.19826 | 0.26856 | 0.36449 | 0.49551 | 0.67465 | 0.91979 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.1447e-06 | 5.3037e-06 | 6.8375e-06 | 8.8752e-06 | 1.1592e-05 | 1.5225e-05 | 2.0099e-05 | 2.6655e-05 | 3.5495e-05 | 4.7442e-05 | 6.3621e-05 | 8.5569e-05 | 0.00011539 | 0.00015598 | 0.0002113 | 0.00028677 | 0.00038985 | 0.00053079 | 0.00072366 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 44.0907 | 56.4205 | 72.7371 | 94.413 | 123.3106 | 161.9613 | 213.8103 | 283.5529 | 377.5952 | 504.6869 | 676.7899 | 910.2723 | 1227.5485 | 1659.3344 | 2247.7497 | 3050.5844 | 4147.1704 | 5646.4634 | 7698.168 | 7882.0541 | 7882.0541 | 7882.0541 | 7882.0541 | 7882.0541 | 7882.0541 | 7882.0541 | 7882.0541 | 7882.0541 | 7882.0541 | 7882.0541 |  | 43.253 | 43.253 | 43.253 | 43.253 | 43.253 | 43.253 | 43.253 | 43.253 | 43.253 | 43.253 | 43.253 | 43.253 | 43.253 | 43.253 | 43.253 | 43.253 | 43.253 | 51.7711 | 68.6257 | 91.7619 | 123.6638 | 167.8324 | 229.2103 | 314.7864 | 434.4576 | 602.2564 | 838.1022 | 1170.2996 | 1639.1056 | 2301.8232 |  | 14.4882 | 18.5398 | 23.9014 | 31.0241 | 40.5199 | 53.2205 | 70.2581 | 93.1755 | 124.0778 | 165.8402 | 222.3932 | 299.1156 | 403.3726 | 545.2575 | 738.6108 | 1002.4224 | 1362.7607 | 1855.4286 | 2529.619 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0.27525 | 4.3268 | 9.6885 | 16.8112 | 26.3069 | 39.0076 | 56.0452 | 78.9626 | 109.8649 | 151.6272 | 208.1803 | 284.9027 | 389.1596 | 531.0446 | 724.3979 | 988.2095 | 1348.5478 | 1838.4166 | 2507.0686 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.29013 | 0.37126 | 0.47863 | 0.62126 | 0.81141 | 1.0657 | 1.4069 | 1.8659 | 2.4847 | 3.321 | 4.4534 | 5.9898 | 8.0776 | 10.9188 | 14.7908 | 20.0736 | 27.2894 | 37.1552 | 50.6559 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.005512 | 0.086645 | 0.19401 | 0.33665 | 0.5268 | 0.78113 | 1.1223 | 1.5812 | 2.2001 | 3.0364 | 4.1688 | 5.7052 | 7.793 | 10.6342 | 14.5061 | 19.789 | 27.0048 | 36.8145 | 50.2043 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0.28077 | 4.4135 | 9.8825 | 17.1478 | 26.8337 | 39.7887 | 57.1675 | 80.5438 | 112.065 | 154.6636 | 212.3491 | 290.6079 | 396.9526 | 541.6788 | 738.9041 | 1007.9985 | 1375.5526 | 1875.2311 | 2557.2729 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.9774 | 19.1658 | 24.7085 | 32.0717 | 41.8881 | 55.0176 | 72.6305 | 96.3218 | 128.2676 | 171.4401 | 229.9028 | 309.2158 | 416.9932 | 563.6692 | 763.5515 | 1036.2711 | 1408.7769 | 1918.0807 | 2615.0364 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0.28455 | 4.4729 | 10.0156 | 17.3788 | 27.1952 | 40.3247 | 57.9376 | 81.6289 | 113.5747 | 156.7472 | 215.2099 | 294.5229 | 402.3004 | 548.9763 | 748.8586 | 1021.5782 | 1394.0841 | 1900.4942 | 2591.7245 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.1078 | 2.6972 | 3.4772 | 4.5135 | 5.8949 | 7.7426 | 10.2213 | 13.5554 | 18.0511 | 24.1268 | 32.3543 | 43.516 | 58.6836 | 79.3253 | 107.4548 | 145.8347 | 198.2576 | 269.9321 | 368.0148 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.040045 | 0.62948 | 1.4095 | 2.4457 | 3.8272 | 5.6749 | 8.1536 | 11.4877 | 15.9834 | 22.0591 | 30.2866 | 41.4483 | 56.6158 | 77.2576 | 105.3871 | 143.767 | 196.1899 | 267.4571 | 364.7342 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 12.2271 | 15.6464 | 20.1713 | 26.1824 | 34.1963 | 44.9148 | 59.2935 | 78.6344 | 104.714 | 139.9588 | 187.6861 | 252.4351 | 340.4215 | 460.1636 | 623.3419 | 845.9825 | 1150.0857 | 1565.8669 | 2134.8419 | 2185.8369 | 2185.8369 | 2185.8369 | 2185.8369 | 2185.8369 | 2185.8369 | 2185.8369 | 2185.8369 | 2185.8369 | 2185.8369 | 2185.8369 |  | 11.9948 | 11.9948 | 11.9948 | 11.9948 | 11.9948 | 11.9948 | 11.9948 | 11.9948 | 11.9948 | 11.9948 | 11.9948 | 11.9948 | 11.9948 | 11.9948 | 11.9948 | 11.9948 | 11.9948 | 14.3571 | 19.0312 | 25.4472 | 34.2942 | 46.543 | 63.5642 | 87.296 | 120.483 | 167.0166 | 232.421 | 324.5453 | 454.5538 | 638.3374 |  | 0.2323 | 3.6516 | 8.1765 | 14.1876 | 22.2014 | 32.92 | 47.2986 | 66.6395 | 92.7192 | 127.964 | 175.6913 | 240.4402 | 328.4267 | 448.1688 | 611.347 | 833.9877 | 1138.0909 | 1551.5099 | 2115.8108 | 2160.3896 | 2151.5426 | 2139.2939 | 2122.2727 | 2098.5409 | 2065.3539 | 2018.8202 | 1953.4159 | 1861.2915 | 1731.2831 | 1547.4994 |  | 0.83766 | 13.1675 | 29.4841 | 51.1599 | 80.0576 | 118.7083 | 170.5573 | 240.2999 | 334.3422 | 461.4339 | 633.5369 | 867.0193 | 1184.2955 | 1616.0814 | 2204.4967 | 3007.3314 | 4103.9174 | 5594.6923 | 7629.5423 | 7790.2922 | 7758.3903 | 7714.2217 | 7652.8438 | 7567.2677 | 7447.5965 | 7279.7977 | 7043.9519 | 6711.7545 | 6242.9485 | 5580.2308
| FALSE | 2958 | 22015490 | MLN | MLN032 | 22 | MLN 32 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.81881 | 1 |  | 1.0927 | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 5.6388 |  | 5.2187 | 0.0096441 | 1.0817e-05 | 0.0096333 | 26.5243 | 0.75722 | 27.2815 | 27.4374 | 3.8587 | 10.5227 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 5.6388 |  | 37.0284 | 69.1004 | 37.0284 | 32.072 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 5.7967e-06 | 7.4548e-06 | 1.0817e-05 | 1.5918e-05 | 2.3709e-05 | 3.5685e-05 | 5.4194e-05 | 8.2938e-05 | 0.00012776 | 0.00019789 | 0.00030797 | 0.00048121 | 0.00075444 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 47.6202 | 69.1004 | 101.68 | 151.448 | 227.9492 | 346.1868 | 529.7983 | 816.1004 | 1264.1084 | 1967.2947 | 3073.8996 | 4819.2865 | 6747.734 | 6747.734 | 6747.734 | 6747.734 | 6747.734 | 6747.734 | 6747.734 | 6747.734 | 6747.734 | 6747.734 |  | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 37.0284 | 44.3207 | 58.7497 | 78.5563 | 105.8671 | 143.6794 | 196.2242 | 269.4849 | 371.934 | 515.5846 | 717.4894 | 1001.8797 | 1403.219 | 1970.5638 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 18.2791 | 26.5243 | 39.0301 | 58.1336 | 87.4988 | 132.8845 | 203.3641 | 313.2617 | 485.2305 | 755.1499 | 1179.9223 | 1849.8924 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0657 | 12.3109 | 24.8167 | 43.9202 | 73.2853 | 118.6711 | 189.1507 | 299.0483 | 471.017 | 738.1373 | 1157.3711 | 1819.7384 | 2549.4934 | 2534.9791 | 2514.8096 | 2486.6884 | 2447.3631 | 2392.2225 | 2314.721 | 2205.5572 | 2051.5024 | 1833.726 |  | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.52183 | 0.75722 | 1.1142 | 1.6596 | 2.4979 | 3.7936 | 5.8057 | 8.943 | 13.8524 | 21.5581 | 33.6845 | 52.8109 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 |  | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.48568 | 0.64379 | 0.86084 | 1.1601 | 1.5745 | 2.1503 | 2.9531 | 4.0757 | 5.6499 | 7.8624 | 10.9788 | 15.3768 | 21.5939 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11607 | 0.35145 | 0.70847 | 1.2538 | 2.0922 | 3.3878 | 5.3999 | 8.5373 | 13.4466 | 21.0724 | 33.0408 | 51.9501 | 72.7832 | 72.3689 | 71.7931 | 70.9902 | 69.8676 | 68.2934 | 66.0809 | 62.9645 | 58.5665 | 52.3494 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1817 | 12.6623 | 25.5251 | 45.174 | 75.3775 | 122.0589 | 194.5506 | 307.5856 | 484.4637 | 759.2097 | 1190.4119 | 1871.6885 | 2622.2766 | 2607.3479 | 2586.6027 | 2557.6786 | 2517.2307 | 2460.516 | 2380.8019 | 2268.5217 | 2110.0689 | 1886.0754 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 18.9083 | 27.4374 | 40.3736 | 60.1348 | 90.5108 | 137.4588 | 210.3646 | 324.0453 | 501.9338 | 781.1448 | 1220.5395 | 1913.5723 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2056 | 12.7347 | 25.6709 | 45.4321 | 75.8081 | 122.7561 | 195.6619 | 309.3426 | 487.2311 | 763.5466 | 1197.212 | 1882.3804 | 2637.2561 | 2622.2422 | 2601.3784 | 2572.2891 | 2531.6101 | 2474.5714 | 2394.402 | 2281.4804 | 2122.1224 | 1896.8494 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6592 | 3.8587 | 5.678 | 8.4572 | 12.7292 | 19.3319 | 29.5851 | 45.5729 | 70.5907 | 109.8582 | 171.6535 | 269.1199 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59147 | 1.791 | 3.6103 | 6.3895 | 10.6615 | 17.2641 | 27.5174 | 43.5051 | 68.5229 | 107.3832 | 168.3728 | 264.7331 | 370.8969 | 368.7854 | 365.8512 | 361.7601 | 356.0391 | 348.0174 | 336.7425 | 320.8615 | 298.4498 | 266.768 |  | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 7.2517 | 10.5227 | 15.484 | 23.0628 | 34.7126 | 52.718 | 80.6788 | 124.2775 | 192.501 | 299.5837 | 468.0998 | 733.8909 | 1027.5589 | 1027.5589 | 1027.5589 | 1027.5589 | 1027.5589 | 1027.5589 | 1027.5589 | 1027.5589 | 1027.5589 | 1027.5589 |  | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 5.6388 | 6.7492 | 8.9465 | 11.9627 | 16.1217 | 21.8798 | 29.8814 | 41.0377 | 56.6389 | 78.5143 | 109.2608 | 152.5683 | 213.6851 | 300.0815 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6129 | 4.884 | 9.8453 | 17.4241 | 29.0738 | 47.0793 | 75.04 | 118.6387 | 186.8623 | 292.8345 | 459.1533 | 721.9282 | 1011.4372 | 1005.6791 | 997.6775 | 986.5212 | 970.92 | 949.0446 | 918.2981 | 874.9906 | 813.8738 | 727.4774 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5918 | 32.072 | 64.6516 | 114.4196 | 190.9209 | 309.1584 | 492.7699 | 779.072 | 1227.08 | 1922.974 | 3015.15 | 4740.7302 | 6641.8668 | 6604.0546 | 6551.5097 | 6478.249 | 6375.7999 | 6232.1493 | 6030.2445 | 5745.8542 | 5344.5149 | 4777.1701
| FALSE | 2959 | 22015511 | MLN | Blank | 22 | TRANS NO.1 | BUEF STAGE 2 & 3 | BU | Siemens | 7SR11 | 7SR11 | SIEMENS 7SR11 | Digital |  | 0.0068096 | 1 |  | 0.91058 | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0053028 | 27.137 | 14.6701 | 2.0677 | 0.0064484 |  | 3.0201 | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0053028 | 27.137 | 14.6701 | 2.0677 | 0.0064484 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0053028 | 27.137 | 14.6701 | 2.0677 | 0.0064484 |  | 43.8812 | 43.8812 | 43.8812 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 5.7701e-08 | 7.6486e-08 | 1.0227e-07 | 1.3783e-07 | 1.8706e-07 | 2.5546e-07 | 3.5084e-07 | 4.8422e-07 | 6.7124e-07 | 9.341e-07 | 1.3044e-06 | 1.8269e-06 | 2.5655e-06 | 3.6112e-06 | 5.0937e-06 | 7.198e-06 | 8.7849e-06 | 8.7849e-06 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 52.523 | 69.6224 | 93.0946 | 125.4598 | 170.2699 | 232.5392 | 319.3582 | 440.7675 | 611.0033 | 850.2744 | 1187.2965 | 1662.9113 | 2335.254 | 3287.1371 | 4636.6021 | 6552.0034 | 7996.5298 | 7996.5298 |  | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 52.523 | 69.6224 | 93.0946 | 125.4598 | 170.2699 | 232.5392 | 319.3582 | 440.7675 | 611.0033 | 850.2744 | 1187.2965 | 1662.9113 | 2335.254 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 | 2032.433 | 2866.8057 | 4051.096 | 4944.245 | 4944.245 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9158 | 30.4286 | 50.44 | 78.146 | 111.3038 | 154.4114 | 214.9657 | 300.211 | 420.446 | 590.3253 | 830.7173 | 1171.3588 | 1654.6504 | 2341.082 | 3316.992 | 3916.0689 | 3500.3602 |  | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0063471 | 0.0084135 | 0.01125 | 0.015161 | 0.020576 | 0.028101 | 0.038593 | 0.053264 | 0.073837 | 0.10275 | 0.14348 | 0.20095 | 0.2822 | 0.39723 | 0.56031 | 0.79178 | 0.96634 | 0.96634 |  | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0063471 | 0.0084135 | 0.01125 | 0.015161 | 0.020576 | 0.028101 | 0.038593 | 0.053264 | 0.073837 | 0.10275 | 0.14348 | 0.20095 | 0.2822 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010443 | 0.0031107 | 0.0059472 | 0.0098584 | 0.015273 | 0.021754 | 0.030179 | 0.042014 | 0.058675 | 0.082175 | 0.11538 | 0.16236 | 0.22894 | 0.3234 | 0.45756 | 0.6483 | 0.76538 | 0.68414 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3443 | 15.9189 | 30.4345 | 50.4498 | 78.1613 | 111.3256 | 154.4415 | 215.0077 | 300.2696 | 420.5282 | 590.4407 | 830.8796 | 1171.5877 | 1654.9738 | 2341.5395 | 3317.6403 | 3916.8343 | 3501.0443 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 | 1098.9332 | 1550.0771 | 2190.4209 | 2673.3451 | 2673.3451 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8891 | 8.6056 | 16.4527 | 27.2728 | 42.2534 | 60.1818 | 83.49 | 116.2316 | 162.3236 | 227.3344 | 319.1879 | 449.1675 | 633.3518 | 894.6667 | 1265.8192 | 1793.4921 | 2117.412 | 1892.639 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 | 154.8906 | 218.4777 | 308.7319 | 376.7983 | 376.7983 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3824 | 22.8789 | 32.042 | 44.9884 | 63.3085 | 89.2686 | 126.1 | 178.4126 | 252.7862 | 298.4415 | 266.7606 |  | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0077183 | 0.010231 | 0.01368 | 0.018437 | 0.025021 | 0.034172 | 0.04693 | 0.064771 | 0.089788 | 0.12495 | 0.17448 | 0.24437 | 0.34317 | 0.48305 | 0.68136 | 0.96283 | 1.1751 | 1.1751 |  | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0077183 | 0.010231 | 0.01368 | 0.018437 | 0.025021 | 0.034172 | 0.04693 | 0.064771 | 0.089788 | 0.12495 | 0.17448 | 0.24437 | 0.34317 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012699 | 0.0037827 | 0.007232 | 0.011988 | 0.018573 | 0.026454 | 0.036699 | 0.051091 | 0.071351 | 0.099928 | 0.1403 | 0.19744 | 0.2784 | 0.39326 | 0.55641 | 0.78835 | 0.93073 | 0.83193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6418 | 25.7412 | 49.2134 | 81.5786 | 126.3887 | 180.0162 | 249.7358 | 347.6729 | 485.5435 | 680.0045 | 954.7573 | 1343.5531 | 1894.4865 | 2676.1338 | 3786.3277 | 5364.7069 | 6333.6185 | 5661.2759
| TRUE | 2960 | 22004056 | MLN | Blank | 22 | TRANS NO.1 | DIFFERENTIAL | Y | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.0068096 | 2190 |  | 8.25 | 0.026286 | 0.00052975 | 0.025756 | 276.5552 | 233.0884 | 509.6437 | 77.6223 | 10.5222 | 70.861 |  | 12.8738 | 0.087882 | 0.0017711 | 0.086111 | 924.6238 | 779.2987 | 1703.9225 | 259.5192 | 35.1794 | 236.9138 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.0064484 |  | 668.6491 | 2235.5349 | 71.0288 | 2164.5061 |  | 0.044498 |  | 8.6254 | 9.0179 | 9.4282 | 9.8572 | 10.3058 | 10.7747 | 11.265 | 11.7776 | 12.3135 | 12.8738 | 13.4595 | 14.072 | 14.7123 | 15.3818 | 16.0817 | 16.8134 | 17.5785 | 18.3783 | 19.2146 | 20.0889 | 21.003 | 21.9587 | 22.9579 | 24.0025 | 25.0947 | 26.2366 | 27.4304 | 28 | 28 | 28 |  | 0.029574 | 0.033298 | 0.037515 | 0.042294 | 0.047711 | 0.053853 | 0.06082 | 0.068725 | 0.077697 | 0.087882 | 0.09945 | 0.11259 | 0.12752 | 0.14449 | 0.16378 | 0.18571 | 0.21065 | 0.23903 | 0.27131 | 0.30805 | 0.34986 | 0.39746 | 0.45166 | 0.51338 | 0.58367 | 0.66374 | 0.75496 | 0.80128 | 0.80128 | 0.80128 |  | 0.00059603 | 0.00067107 | 0.00075607 | 0.00085238 | 0.00096154 | 0.0010853 | 0.0012257 | 0.001385 | 0.0015659 | 0.0017711 | 0.0020043 | 0.0022691 | 0.00257 | 0.0029119 | 0.0033007 | 0.0037427 | 0.0042454 | 0.0048172 | 0.0054679 | 0.0062082 | 0.0070509 | 0.0080103 | 0.0091025 | 0.010346 | 0.011763 | 0.013377 | 0.015215 | 0.016149 | 0.016149 | 0.016149 | 752.3071 | 847.0262 | 954.311 | 1075.8743 | 1213.6664 | 1369.9079 | 1547.1282 | 1748.2084 | 1976.4306 | 2235.5349 | 2529.7827 | 2864.031 | 3243.8159 | 3675.448 | 4166.1218 | 4724.0405 | 5358.5579 | 6080.3413 | 6901.5564 | 7836.0797 | 8899.74 | 10110.5944 | 11489.2437 | 13059.1927 | 14847.2609 | 16884.0525 | 19204.4924 | 20382.7721 | 20382.7721 | 20382.7721 |  | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 52.5424 | 69.6481 | 93.1289 | 125.5061 | 170.3327 | 232.625 | 319.476 | 440.93 | 611.2287 | 850.5881 | 1187.7345 | 1663.5247 | 2336.1154 |  | 311.1564 | 350.3325 | 394.7058 | 444.9848 | 501.976 | 566.5979 | 639.8968 | 723.0641 | 817.4575 | 924.6238 | 1046.3255 | 1184.5716 | 1341.6518 | 1520.1761 | 1723.1202 | 1953.877 | 2216.3153 | 2514.847 | 2854.504 | 3241.0256 | 3680.9586 | 4181.7715 | 4751.9849 | 5401.3204 | 6140.8707 | 6983.2937 | 7943.0344 | 8430.3744 | 8430.3744 | 8430.3744 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 284.0247 | 323.2008 | 367.5741 | 417.8531 | 474.8443 | 539.4662 | 612.7651 | 695.9324 | 790.3258 | 897.4921 | 1019.1939 | 1157.44 | 1314.5201 | 1493.0444 | 1695.9885 | 1926.7453 | 2189.1836 | 2482.3721 | 2811.4565 | 3183.4653 | 3603.3869 | 4076.4938 | 4608.2062 | 5203.8616 | 5868.3447 | 6605.511 | 7417.3108 | 7696.2703 | 7402.1983 | 6986.4896 |  | 262.2513 | 295.27 | 332.6691 | 375.0456 | 423.0793 | 477.5445 | 539.3228 | 609.4186 | 688.976 | 779.2987 | 881.8723 | 998.39 | 1130.7815 | 1281.2467 | 1452.2937 | 1646.782 | 1867.9723 | 2119.5831 | 2405.8555 | 2731.6266 | 3102.4144 | 3524.5135 | 4005.1052 | 4552.3833 | 5175.6969 | 5885.7144 | 6694.6107 | 7105.3543 | 7105.3543 | 7105.3543 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 262.2301 | 295.2488 | 332.6479 | 375.0244 | 423.0581 | 477.5233 | 539.3016 | 609.3974 | 688.9548 | 779.2775 | 881.8511 | 998.3688 | 1130.7603 | 1281.2255 | 1452.2725 | 1646.7608 | 1867.9511 | 2119.5577 | 2405.8218 | 2731.5816 | 3102.3538 | 3524.4312 | 4004.9928 | 4552.2289 | 5175.4838 | 5885.4191 | 6694.1997 | 7104.7804 | 7104.5505 | 7104.2255 |  | 546.2548 | 618.4496 | 700.222 | 792.8775 | 897.9024 | 1016.9896 | 1152.0667 | 1305.3298 | 1479.2806 | 1676.7696 | 1901.045 | 2155.8087 | 2445.2804 | 2774.2699 | 3148.261 | 3573.5061 | 4057.1347 | 4601.9298 | 5217.2784 | 5915.0469 | 6705.7407 | 7600.925 | 8613.199 | 9756.0905 | 11043.8285 | 12490.9301 | 14111.5104 | 14801.0507 | 14506.7488 | 14090.7151 |  | 87.334 | 98.3297 | 110.7842 | 124.8963 | 140.8923 | 159.0301 | 179.6033 | 202.9464 | 229.4403 | 259.5192 | 293.6779 | 332.4802 | 376.5688 | 426.6761 | 483.6376 | 548.4054 | 622.0654 | 705.8559 | 801.1893 | 909.6764 | 1033.1548 | 1173.7207 | 1333.7656 | 1516.0182 | 1723.5918 | 1960.0393 | 2229.415 | 2366.1994 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 72.6639 | 83.6597 | 96.1142 | 110.2263 | 126.2223 | 144.3601 | 164.9333 | 188.2763 | 214.7702 | 244.8492 | 279.0079 | 317.8102 | 361.8987 | 412.0061 | 468.9675 | 533.7353 | 607.3953 | 688.2967 | 777.9136 | 878.5537 | 991.2119 | 1116.7972 | 1256.0247 | 1409.2526 | 1576.2375 | 1755.7729 | 1945.1571 | 1969.2705 | 1810.2663 | 1585.4933 |  | 11.8387 | 13.3292 | 15.0175 | 16.9305 | 19.0988 | 21.5575 | 24.3463 | 27.5106 | 31.102 | 35.1794 | 39.8098 | 45.0697 | 51.0462 | 57.8386 | 65.56 | 74.3397 | 84.3248 | 95.6831 | 108.6061 | 123.3122 | 140.0505 | 159.105 | 180.8001 | 205.5055 | 233.6434 | 265.6953 | 302.2108 | 320.7528 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 9.771 | 11.2615 | 12.9498 | 14.8628 | 17.0311 | 19.4898 | 22.2786 | 25.4429 | 29.0343 | 33.1117 | 37.7421 | 43.002 | 48.9785 | 55.7709 | 63.4923 | 72.272 | 82.2571 | 93.2082 | 105.3255 | 118.9256 | 134.1388 | 151.0819 | 169.8428 | 190.4573 | 212.8743 | 236.9047 | 262.1457 | 264.8071 | 242.396 | 210.7151 |  | 79.7267 | 89.7647 | 101.1344 | 114.0172 | 128.6199 | 145.1778 | 163.959 | 185.2687 | 209.4549 | 236.9138 | 268.0971 | 303.5195 | 343.7677 | 389.5105 | 441.5103 | 500.6364 | 567.8803 | 644.3722 | 731.4016 | 830.4389 | 943.1617 | 1071.4836 | 1217.5878 | 1383.9652 | 1573.4581 | 1789.3098 | 2035.2215 | 2160.0912 | 2160.0912 | 2160.0912 |  | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0077183 | 0.010231 | 0.01368 | 0.018437 | 0.025021 | 0.034172 | 0.04693 | 0.064771 | 0.089788 | 0.12495 | 0.17448 | 0.24437 | 0.34317 |  | 79.7203 | 89.7583 | 101.1279 | 114.0108 | 128.6135 | 145.1714 | 163.9525 | 185.2622 | 209.4484 | 236.9073 | 268.0906 | 303.513 | 343.7612 | 389.504 | 441.5038 | 500.63 | 567.8738 | 644.3645 | 731.3913 | 830.4252 | 943.1433 | 1071.4586 | 1217.5536 | 1383.9183 | 1573.3933 | 1789.22 | 2035.0965 | 2159.9168 | 2159.8469 | 2159.7481 |  | 708.41 | 803.1291 | 910.4139 | 1031.9772 | 1169.7693 | 1326.0108 | 1503.2311 | 1704.3113 | 1932.5335 | 2191.6378 | 2485.8856 | 2820.1339 | 3199.9188 | 3631.5509 | 4122.2247 | 4680.1434 | 5314.6608 | 6027.7992 | 6831.9088 | 7742.9514 | 8774.2347 | 9940.2627 | 11256.6202 | 12739.7187 | 14406.3337 | 16272.8277 | 18353.9098 | 19195.0451 | 18719.258 | 18046.6715
| FALSE | 2961 | 22015515 | MLN | Blank | 22 | TRANS NO.1 | VOLTAGE REGULATION | C | A-EBERLE | REG_D | REG D | REG D | Digital |  | 0 | 1 |  | 0.91058 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 3.0201 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 43.8691 | 43.8691 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 | 3286.2344 | 4635.3288 | 6550.2041 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 | 2032.4311 | 2866.803 | 4051.0922 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 111.3037 | 154.4112 | 214.9655 | 300.2107 | 420.4456 | 590.3248 | 830.7165 | 1171.3577 | 1654.6488 | 2341.0798 | 3316.9889 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 111.3037 | 154.4112 | 214.9655 | 300.2107 | 420.4456 | 590.3248 | 830.7165 | 1171.3577 | 1654.6488 | 2341.0798 | 3316.9889 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 60.1807 | 83.4884 | 116.2294 | 162.3205 | 227.3302 | 319.182 | 449.1591 | 633.3399 | 894.65 | 1265.7955 | 1793.4586 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3824 | 22.8789 | 32.042 | 44.9884 | 63.3085 | 89.2686 | 126.1 | 178.4126 | 252.7861 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6395 | 25.7341 | 49.1999 | 81.5562 | 126.354 | 179.9668 | 249.6672 | 347.5774 | 485.4101 | 679.8177 | 954.4951 | 1343.1841 | 1893.9662 | 2675.3989 | 3785.2879 | 5363.2336 | 6331.8792 | 5659.7211
| FALSE | 2962 | 22015486 | MLN | Blank | 22 | TRANS NO.1 | DIFFERENTIAL & REF | X | Schweitzer | SEL_787 | SEL 787 | SEL 700s | Digital |  | 0.066046 | 1 |  | 0.91058 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 3.0201 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 43.986 | 43.986 | 43.986 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 8.5205e-05 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 | 3294.9899 | 4647.6787 | 6567.6558 | 8015.6331 | 8015.6331 |  | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 78.1466 | 111.3047 | 154.4126 | 214.9675 | 300.2134 | 420.4494 | 590.3301 | 830.724 | 1171.3683 | 1654.6638 | 2341.101 | 3317.0189 | 3916.1007 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.14814 | 0.21099 | 0.29271 | 0.4075 | 0.5691 | 0.79702 | 1.1191 | 1.5748 | 2.2205 | 3.1366 | 4.4379 | 6.2879 | 7.4235 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 78.2948 | 111.5157 | 154.7053 | 215.375 | 300.7825 | 421.2464 | 591.4492 | 832.2988 | 1173.5888 | 1657.8005 | 2345.5389 | 3323.3067 | 3923.5242 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 42.2603 | 60.1915 | 83.5035 | 116.2505 | 162.3499 | 227.3713 | 319.2397 | 449.2404 | 633.4545 | 894.8119 | 1266.0246 | 1793.7831 | 2117.7556 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3825 | 22.879 | 32.042 | 44.9885 | 63.3087 | 89.2688 | 126.1003 | 178.413 | 252.7867 | 298.4421 | 266.7611 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 | 4.6851 | 6.6085 | 9.3385 | 11.3974 | 11.3974 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012317 | 0.036689 | 0.070143 | 0.11627 | 0.18014 | 0.25658 | 0.35595 | 0.49554 | 0.69204 | 0.96921 | 1.3608 | 1.915 | 2.7002 | 3.8143 | 5.3966 | 7.6463 | 9.0273 | 8.069 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6625 | 25.8027 | 49.331 | 81.7735 | 126.6907 | 180.4462 | 250.3324 | 348.5034 | 486.7034 | 681.629 | 957.0382 | 1346.7627 | 1899.0123 | 2682.527 | 3795.373 | 5377.5229 | 6348.7492 | 5674.8003
| FALSE | 2963 | 22015488 | MLN | Blank | 22 | TRANS NO.1 | TX MECH. PROT. & COOLING | X | Schweitzer | SEL_2414 | SEL 2414 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 0.91058 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 3.0201 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 43.986 | 43.986 | 43.986 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 8.5205e-05 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 | 3294.9899 | 4647.6787 | 6567.6558 | 8015.6331 | 8015.6331 |  | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 78.1466 | 111.3047 | 154.4126 | 214.9675 | 300.2134 | 420.4494 | 590.3301 | 830.724 | 1171.3683 | 1654.6638 | 2341.101 | 3317.0189 | 3916.1007 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.14814 | 0.21099 | 0.29271 | 0.4075 | 0.5691 | 0.79702 | 1.1191 | 1.5748 | 2.2205 | 3.1366 | 4.4379 | 6.2879 | 7.4235 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 78.2948 | 111.5157 | 154.7053 | 215.375 | 300.7825 | 421.2464 | 591.4492 | 832.2988 | 1173.5888 | 1657.8005 | 2345.5389 | 3323.3067 | 3923.5242 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 42.2603 | 60.1915 | 83.5035 | 116.2505 | 162.3499 | 227.3713 | 319.2397 | 449.2404 | 633.4545 | 894.8119 | 1266.0246 | 1793.7831 | 2117.7556 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3825 | 22.879 | 32.042 | 44.9885 | 63.3087 | 89.2688 | 126.1003 | 178.413 | 252.7867 | 298.4421 | 266.7611 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 | 4.6851 | 6.6085 | 9.3385 | 11.3974 | 11.3974 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012317 | 0.036689 | 0.070143 | 0.11627 | 0.18014 | 0.25658 | 0.35595 | 0.49554 | 0.69204 | 0.96921 | 1.3608 | 1.915 | 2.7002 | 3.8143 | 5.3966 | 7.6463 | 9.0273 | 8.069 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6625 | 25.8027 | 49.331 | 81.7735 | 126.6907 | 180.4462 | 250.3324 | 348.5034 | 486.7034 | 681.629 | 957.0382 | 1346.7627 | 1899.0123 | 2682.527 | 3795.373 | 5377.5229 | 6348.7492 | 5674.8003
| FALSE | 2964 | 22015922 | MLN | Blank | 22 | TRANS NO.1 | TRANS MGMT | C | Schweitzer | SEL_2440 | SEL 2440 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 0.91058 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 3.0201 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 43.986 | 43.986 | 43.986 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 8.5205e-05 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 | 3294.9899 | 4647.6787 | 6567.6558 | 8015.6331 | 8015.6331 |  | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 78.1466 | 111.3047 | 154.4126 | 214.9675 | 300.2134 | 420.4494 | 590.3301 | 830.724 | 1171.3683 | 1654.6638 | 2341.101 | 3317.0189 | 3916.1007 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.14814 | 0.21099 | 0.29271 | 0.4075 | 0.5691 | 0.79702 | 1.1191 | 1.5748 | 2.2205 | 3.1366 | 4.4379 | 6.2879 | 7.4235 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 78.2948 | 111.5157 | 154.7053 | 215.375 | 300.7825 | 421.2464 | 591.4492 | 832.2988 | 1173.5888 | 1657.8005 | 2345.5389 | 3323.3067 | 3923.5242 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 42.2603 | 60.1915 | 83.5035 | 116.2505 | 162.3499 | 227.3713 | 319.2397 | 449.2404 | 633.4545 | 894.8119 | 1266.0246 | 1793.7831 | 2117.7556 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3825 | 22.879 | 32.042 | 44.9885 | 63.3087 | 89.2688 | 126.1003 | 178.413 | 252.7867 | 298.4421 | 266.7611 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 | 4.6851 | 6.6085 | 9.3385 | 11.3974 | 11.3974 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012317 | 0.036689 | 0.070143 | 0.11627 | 0.18014 | 0.25658 | 0.35595 | 0.49554 | 0.69204 | 0.96921 | 1.3608 | 1.915 | 2.7002 | 3.8143 | 5.3966 | 7.6463 | 9.0273 | 8.069 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6625 | 25.8027 | 49.331 | 81.7735 | 126.6907 | 180.4462 | 250.3324 | 348.5034 | 486.7034 | 681.629 | 957.0382 | 1346.7627 | 1899.0123 | 2682.527 | 3795.373 | 5377.5229 | 6348.7492 | 5674.8003
| FALSE | 2965 | 22015512 | MLN | Blank | 22 | TRANS NO.2 | BUEF STAGE 2 & 3 | BU | Siemens | 7SR11 | 7SR11 | SIEMENS 7SR11 | Digital |  | 0.0068096 | 1 |  | 0.91058 | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0053028 | 27.137 | 14.6701 | 2.0677 | 0.0064484 |  | 3.0201 | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0053028 | 27.137 | 14.6701 | 2.0677 | 0.0064484 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0053028 | 27.137 | 14.6701 | 2.0677 | 0.0064484 |  | 43.8812 | 43.8812 | 43.8812 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 5.7701e-08 | 7.6486e-08 | 1.0227e-07 | 1.3783e-07 | 1.8706e-07 | 2.5546e-07 | 3.5084e-07 | 4.8422e-07 | 6.7124e-07 | 9.341e-07 | 1.3044e-06 | 1.8269e-06 | 2.5655e-06 | 3.6112e-06 | 5.0937e-06 | 7.198e-06 | 8.7849e-06 | 8.7849e-06 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 52.523 | 69.6224 | 93.0946 | 125.4598 | 170.2699 | 232.5392 | 319.3582 | 440.7675 | 611.0033 | 850.2744 | 1187.2965 | 1662.9113 | 2335.254 | 3287.1371 | 4636.6021 | 6552.0034 | 7996.5298 | 7996.5298 |  | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 52.523 | 69.6224 | 93.0946 | 125.4598 | 170.2699 | 232.5392 | 319.3582 | 440.7675 | 611.0033 | 850.2744 | 1187.2965 | 1662.9113 | 2335.254 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 | 2032.433 | 2866.8057 | 4051.096 | 4944.245 | 4944.245 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9158 | 30.4286 | 50.44 | 78.146 | 111.3038 | 154.4114 | 214.9657 | 300.211 | 420.446 | 590.3253 | 830.7173 | 1171.3588 | 1654.6504 | 2341.082 | 3316.992 | 3916.0689 | 3500.3602 |  | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0063471 | 0.0084135 | 0.01125 | 0.015161 | 0.020576 | 0.028101 | 0.038593 | 0.053264 | 0.073837 | 0.10275 | 0.14348 | 0.20095 | 0.2822 | 0.39723 | 0.56031 | 0.79178 | 0.96634 | 0.96634 |  | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0063471 | 0.0084135 | 0.01125 | 0.015161 | 0.020576 | 0.028101 | 0.038593 | 0.053264 | 0.073837 | 0.10275 | 0.14348 | 0.20095 | 0.2822 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010443 | 0.0031107 | 0.0059472 | 0.0098584 | 0.015273 | 0.021754 | 0.030179 | 0.042014 | 0.058675 | 0.082175 | 0.11538 | 0.16236 | 0.22894 | 0.3234 | 0.45756 | 0.6483 | 0.76538 | 0.68414 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3443 | 15.9189 | 30.4345 | 50.4498 | 78.1613 | 111.3256 | 154.4415 | 215.0077 | 300.2696 | 420.5282 | 590.4407 | 830.8796 | 1171.5877 | 1654.9738 | 2341.5395 | 3317.6403 | 3916.8343 | 3501.0443 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 | 1098.9332 | 1550.0771 | 2190.4209 | 2673.3451 | 2673.3451 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8891 | 8.6056 | 16.4527 | 27.2728 | 42.2534 | 60.1818 | 83.49 | 116.2316 | 162.3236 | 227.3344 | 319.1879 | 449.1675 | 633.3518 | 894.6667 | 1265.8192 | 1793.4921 | 2117.412 | 1892.639 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 | 154.8906 | 218.4777 | 308.7319 | 376.7983 | 376.7983 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3824 | 22.8789 | 32.042 | 44.9884 | 63.3085 | 89.2686 | 126.1 | 178.4126 | 252.7862 | 298.4415 | 266.7606 |  | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0077183 | 0.010231 | 0.01368 | 0.018437 | 0.025021 | 0.034172 | 0.04693 | 0.064771 | 0.089788 | 0.12495 | 0.17448 | 0.24437 | 0.34317 | 0.48305 | 0.68136 | 0.96283 | 1.1751 | 1.1751 |  | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0077183 | 0.010231 | 0.01368 | 0.018437 | 0.025021 | 0.034172 | 0.04693 | 0.064771 | 0.089788 | 0.12495 | 0.17448 | 0.24437 | 0.34317 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012699 | 0.0037827 | 0.007232 | 0.011988 | 0.018573 | 0.026454 | 0.036699 | 0.051091 | 0.071351 | 0.099928 | 0.1403 | 0.19744 | 0.2784 | 0.39326 | 0.55641 | 0.78835 | 0.93073 | 0.83193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6418 | 25.7412 | 49.2134 | 81.5786 | 126.3887 | 180.0162 | 249.7358 | 347.6729 | 485.5435 | 680.0045 | 954.7573 | 1343.5531 | 1894.4865 | 2676.1338 | 3786.3277 | 5364.7069 | 6333.6185 | 5661.2759
| TRUE | 2966 | 22010608 | MLN | Blank | 22 | TRANS NO.2 | DIFFERENTIAL | Y | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.0068096 | 2190 |  | 8.25 | 0.026286 | 0.00052975 | 0.025756 | 276.5552 | 233.0884 | 509.6437 | 77.6223 | 10.5222 | 70.861 |  | 12.8738 | 0.087882 | 0.0017711 | 0.086111 | 924.6238 | 779.2987 | 1703.9225 | 259.5192 | 35.1794 | 236.9138 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.0064484 |  | 668.6491 | 2235.5349 | 71.0288 | 2164.5061 |  | 0.044498 |  | 8.6254 | 9.0179 | 9.4282 | 9.8572 | 10.3058 | 10.7747 | 11.265 | 11.7776 | 12.3135 | 12.8738 | 13.4595 | 14.072 | 14.7123 | 15.3818 | 16.0817 | 16.8134 | 17.5785 | 18.3783 | 19.2146 | 20.0889 | 21.003 | 21.9587 | 22.9579 | 24.0025 | 25.0947 | 26.2366 | 27.4304 | 28 | 28 | 28 |  | 0.029574 | 0.033298 | 0.037515 | 0.042294 | 0.047711 | 0.053853 | 0.06082 | 0.068725 | 0.077697 | 0.087882 | 0.09945 | 0.11259 | 0.12752 | 0.14449 | 0.16378 | 0.18571 | 0.21065 | 0.23903 | 0.27131 | 0.30805 | 0.34986 | 0.39746 | 0.45166 | 0.51338 | 0.58367 | 0.66374 | 0.75496 | 0.80128 | 0.80128 | 0.80128 |  | 0.00059603 | 0.00067107 | 0.00075607 | 0.00085238 | 0.00096154 | 0.0010853 | 0.0012257 | 0.001385 | 0.0015659 | 0.0017711 | 0.0020043 | 0.0022691 | 0.00257 | 0.0029119 | 0.0033007 | 0.0037427 | 0.0042454 | 0.0048172 | 0.0054679 | 0.0062082 | 0.0070509 | 0.0080103 | 0.0091025 | 0.010346 | 0.011763 | 0.013377 | 0.015215 | 0.016149 | 0.016149 | 0.016149 | 752.3071 | 847.0262 | 954.311 | 1075.8743 | 1213.6664 | 1369.9079 | 1547.1282 | 1748.2084 | 1976.4306 | 2235.5349 | 2529.7827 | 2864.031 | 3243.8159 | 3675.448 | 4166.1218 | 4724.0405 | 5358.5579 | 6080.3413 | 6901.5564 | 7836.0797 | 8899.74 | 10110.5944 | 11489.2437 | 13059.1927 | 14847.2609 | 16884.0525 | 19204.4924 | 20382.7721 | 20382.7721 | 20382.7721 |  | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 43.8974 | 52.5424 | 69.6481 | 93.1289 | 125.5061 | 170.3327 | 232.625 | 319.476 | 440.93 | 611.2287 | 850.5881 | 1187.7345 | 1663.5247 | 2336.1154 |  | 311.1564 | 350.3325 | 394.7058 | 444.9848 | 501.976 | 566.5979 | 639.8968 | 723.0641 | 817.4575 | 924.6238 | 1046.3255 | 1184.5716 | 1341.6518 | 1520.1761 | 1723.1202 | 1953.877 | 2216.3153 | 2514.847 | 2854.504 | 3241.0256 | 3680.9586 | 4181.7715 | 4751.9849 | 5401.3204 | 6140.8707 | 6983.2937 | 7943.0344 | 8430.3744 | 8430.3744 | 8430.3744 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 284.0247 | 323.2008 | 367.5741 | 417.8531 | 474.8443 | 539.4662 | 612.7651 | 695.9324 | 790.3258 | 897.4921 | 1019.1939 | 1157.44 | 1314.5201 | 1493.0444 | 1695.9885 | 1926.7453 | 2189.1836 | 2482.3721 | 2811.4565 | 3183.4653 | 3603.3869 | 4076.4938 | 4608.2062 | 5203.8616 | 5868.3447 | 6605.511 | 7417.3108 | 7696.2703 | 7402.1983 | 6986.4896 |  | 262.2513 | 295.27 | 332.6691 | 375.0456 | 423.0793 | 477.5445 | 539.3228 | 609.4186 | 688.976 | 779.2987 | 881.8723 | 998.39 | 1130.7815 | 1281.2467 | 1452.2937 | 1646.782 | 1867.9723 | 2119.5831 | 2405.8555 | 2731.6266 | 3102.4144 | 3524.5135 | 4005.1052 | 4552.3833 | 5175.6969 | 5885.7144 | 6694.6107 | 7105.3543 | 7105.3543 | 7105.3543 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 262.2301 | 295.2488 | 332.6479 | 375.0244 | 423.0581 | 477.5233 | 539.3016 | 609.3974 | 688.9548 | 779.2775 | 881.8511 | 998.3688 | 1130.7603 | 1281.2255 | 1452.2725 | 1646.7608 | 1867.9511 | 2119.5577 | 2405.8218 | 2731.5816 | 3102.3538 | 3524.4312 | 4004.9928 | 4552.2289 | 5175.4838 | 5885.4191 | 6694.1997 | 7104.7804 | 7104.5505 | 7104.2255 |  | 546.2548 | 618.4496 | 700.222 | 792.8775 | 897.9024 | 1016.9896 | 1152.0667 | 1305.3298 | 1479.2806 | 1676.7696 | 1901.045 | 2155.8087 | 2445.2804 | 2774.2699 | 3148.261 | 3573.5061 | 4057.1347 | 4601.9298 | 5217.2784 | 5915.0469 | 6705.7407 | 7600.925 | 8613.199 | 9756.0905 | 11043.8285 | 12490.9301 | 14111.5104 | 14801.0507 | 14506.7488 | 14090.7151 |  | 87.334 | 98.3297 | 110.7842 | 124.8963 | 140.8923 | 159.0301 | 179.6033 | 202.9464 | 229.4403 | 259.5192 | 293.6779 | 332.4802 | 376.5688 | 426.6761 | 483.6376 | 548.4054 | 622.0654 | 705.8559 | 801.1893 | 909.6764 | 1033.1548 | 1173.7207 | 1333.7656 | 1516.0182 | 1723.5918 | 1960.0393 | 2229.415 | 2366.1994 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 72.6639 | 83.6597 | 96.1142 | 110.2263 | 126.2223 | 144.3601 | 164.9333 | 188.2763 | 214.7702 | 244.8492 | 279.0079 | 317.8102 | 361.8987 | 412.0061 | 468.9675 | 533.7353 | 607.3953 | 688.2967 | 777.9136 | 878.5537 | 991.2119 | 1116.7972 | 1256.0247 | 1409.2526 | 1576.2375 | 1755.7729 | 1945.1571 | 1969.2705 | 1810.2663 | 1585.4933 |  | 11.8387 | 13.3292 | 15.0175 | 16.9305 | 19.0988 | 21.5575 | 24.3463 | 27.5106 | 31.102 | 35.1794 | 39.8098 | 45.0697 | 51.0462 | 57.8386 | 65.56 | 74.3397 | 84.3248 | 95.6831 | 108.6061 | 123.3122 | 140.0505 | 159.105 | 180.8001 | 205.5055 | 233.6434 | 265.6953 | 302.2108 | 320.7528 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 9.771 | 11.2615 | 12.9498 | 14.8628 | 17.0311 | 19.4898 | 22.2786 | 25.4429 | 29.0343 | 33.1117 | 37.7421 | 43.002 | 48.9785 | 55.7709 | 63.4923 | 72.272 | 82.2571 | 93.2082 | 105.3255 | 118.9256 | 134.1388 | 151.0819 | 169.8428 | 190.4573 | 212.8743 | 236.9047 | 262.1457 | 264.8071 | 242.396 | 210.7151 |  | 79.7267 | 89.7647 | 101.1344 | 114.0172 | 128.6199 | 145.1778 | 163.959 | 185.2687 | 209.4549 | 236.9138 | 268.0971 | 303.5195 | 343.7677 | 389.5105 | 441.5103 | 500.6364 | 567.8803 | 644.3722 | 731.4016 | 830.4389 | 943.1617 | 1071.4836 | 1217.5878 | 1383.9652 | 1573.4581 | 1789.3098 | 2035.2215 | 2160.0912 | 2160.0912 | 2160.0912 |  | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0077183 | 0.010231 | 0.01368 | 0.018437 | 0.025021 | 0.034172 | 0.04693 | 0.064771 | 0.089788 | 0.12495 | 0.17448 | 0.24437 | 0.34317 |  | 79.7203 | 89.7583 | 101.1279 | 114.0108 | 128.6135 | 145.1714 | 163.9525 | 185.2622 | 209.4484 | 236.9073 | 268.0906 | 303.513 | 343.7612 | 389.504 | 441.5038 | 500.63 | 567.8738 | 644.3645 | 731.3913 | 830.4252 | 943.1433 | 1071.4586 | 1217.5536 | 1383.9183 | 1573.3933 | 1789.22 | 2035.0965 | 2159.9168 | 2159.8469 | 2159.7481 |  | 708.41 | 803.1291 | 910.4139 | 1031.9772 | 1169.7693 | 1326.0108 | 1503.2311 | 1704.3113 | 1932.5335 | 2191.6378 | 2485.8856 | 2820.1339 | 3199.9188 | 3631.5509 | 4122.2247 | 4680.1434 | 5314.6608 | 6027.7992 | 6831.9088 | 7742.9514 | 8774.2347 | 9940.2627 | 11256.6202 | 12739.7187 | 14406.3337 | 16272.8277 | 18353.9098 | 19195.0451 | 18719.258 | 18046.6715
| FALSE | 2967 | 22015516 | MLN | Blank | 22 | TRANS NO.2 | VOLTAGE REGULATION | C | A-EBERLE | REG_D | REG D | REG D | Digital |  | 0 | 1 |  | 0.91058 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 3.0201 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 43.8691 | 43.8691 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 | 3286.2344 | 4635.3288 | 6550.2041 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 | 2032.4311 | 2866.803 | 4051.0922 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 111.3037 | 154.4112 | 214.9655 | 300.2107 | 420.4456 | 590.3248 | 830.7165 | 1171.3577 | 1654.6488 | 2341.0798 | 3316.9889 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 111.3037 | 154.4112 | 214.9655 | 300.2107 | 420.4456 | 590.3248 | 830.7165 | 1171.3577 | 1654.6488 | 2341.0798 | 3316.9889 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 60.1807 | 83.4884 | 116.2294 | 162.3205 | 227.3302 | 319.182 | 449.1591 | 633.3399 | 894.65 | 1265.7955 | 1793.4586 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3824 | 22.8789 | 32.042 | 44.9884 | 63.3085 | 89.2686 | 126.1 | 178.4126 | 252.7861 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6395 | 25.7341 | 49.1999 | 81.5562 | 126.354 | 179.9668 | 249.6672 | 347.5774 | 485.4101 | 679.8177 | 954.4951 | 1343.1841 | 1893.9662 | 2675.3989 | 3785.2879 | 5363.2336 | 6331.8792 | 5659.7211
| FALSE | 2968 | 22015487 | MLN | Blank | 22 | TRANS NO.2 | DIFFERENTIAL & REF | X | Schweitzer | SEL_787 | SEL 787 | SEL 700s | Digital |  | 0.066046 | 1 |  | 0.91058 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 3.0201 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 43.986 | 43.986 | 43.986 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 8.5205e-05 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 | 3294.9899 | 4647.6787 | 6567.6558 | 8015.6331 | 8015.6331 |  | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 78.1466 | 111.3047 | 154.4126 | 214.9675 | 300.2134 | 420.4494 | 590.3301 | 830.724 | 1171.3683 | 1654.6638 | 2341.101 | 3317.0189 | 3916.1007 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.14814 | 0.21099 | 0.29271 | 0.4075 | 0.5691 | 0.79702 | 1.1191 | 1.5748 | 2.2205 | 3.1366 | 4.4379 | 6.2879 | 7.4235 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 78.2948 | 111.5157 | 154.7053 | 215.375 | 300.7825 | 421.2464 | 591.4492 | 832.2988 | 1173.5888 | 1657.8005 | 2345.5389 | 3323.3067 | 3923.5242 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 42.2603 | 60.1915 | 83.5035 | 116.2505 | 162.3499 | 227.3713 | 319.2397 | 449.2404 | 633.4545 | 894.8119 | 1266.0246 | 1793.7831 | 2117.7556 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3825 | 22.879 | 32.042 | 44.9885 | 63.3087 | 89.2688 | 126.1003 | 178.413 | 252.7867 | 298.4421 | 266.7611 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 | 4.6851 | 6.6085 | 9.3385 | 11.3974 | 11.3974 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012317 | 0.036689 | 0.070143 | 0.11627 | 0.18014 | 0.25658 | 0.35595 | 0.49554 | 0.69204 | 0.96921 | 1.3608 | 1.915 | 2.7002 | 3.8143 | 5.3966 | 7.6463 | 9.0273 | 8.069 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6625 | 25.8027 | 49.331 | 81.7735 | 126.6907 | 180.4462 | 250.3324 | 348.5034 | 486.7034 | 681.629 | 957.0382 | 1346.7627 | 1899.0123 | 2682.527 | 3795.373 | 5377.5229 | 6348.7492 | 5674.8003
| FALSE | 2969 | 22015489 | MLN | Blank | 22 | TRANS NO.2 | TX MECH. PROT. & COOLING | X | Schweitzer | SEL_2414 | SEL 2414 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 0.91058 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 3.0201 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 43.986 | 43.986 | 43.986 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 8.5205e-05 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 | 3294.9899 | 4647.6787 | 6567.6558 | 8015.6331 | 8015.6331 |  | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 78.1466 | 111.3047 | 154.4126 | 214.9675 | 300.2134 | 420.4494 | 590.3301 | 830.724 | 1171.3683 | 1654.6638 | 2341.101 | 3317.0189 | 3916.1007 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.14814 | 0.21099 | 0.29271 | 0.4075 | 0.5691 | 0.79702 | 1.1191 | 1.5748 | 2.2205 | 3.1366 | 4.4379 | 6.2879 | 7.4235 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 78.2948 | 111.5157 | 154.7053 | 215.375 | 300.7825 | 421.2464 | 591.4492 | 832.2988 | 1173.5888 | 1657.8005 | 2345.5389 | 3323.3067 | 3923.5242 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 42.2603 | 60.1915 | 83.5035 | 116.2505 | 162.3499 | 227.3713 | 319.2397 | 449.2404 | 633.4545 | 894.8119 | 1266.0246 | 1793.7831 | 2117.7556 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3825 | 22.879 | 32.042 | 44.9885 | 63.3087 | 89.2688 | 126.1003 | 178.413 | 252.7867 | 298.4421 | 266.7611 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 | 4.6851 | 6.6085 | 9.3385 | 11.3974 | 11.3974 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012317 | 0.036689 | 0.070143 | 0.11627 | 0.18014 | 0.25658 | 0.35595 | 0.49554 | 0.69204 | 0.96921 | 1.3608 | 1.915 | 2.7002 | 3.8143 | 5.3966 | 7.6463 | 9.0273 | 8.069 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6625 | 25.8027 | 49.331 | 81.7735 | 126.6907 | 180.4462 | 250.3324 | 348.5034 | 486.7034 | 681.629 | 957.0382 | 1346.7627 | 1899.0123 | 2682.527 | 3795.373 | 5377.5229 | 6348.7492 | 5674.8003
| FALSE | 2970 | 22015923 | MLN | Blank | 22 | TRANS NO.2 | TRANS MGMT | C | Schweitzer | SEL_2440 | SEL 2440 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 0.91058 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 3.0201 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 43.986 | 43.986 | 43.986 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 8.5205e-05 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 | 3294.9899 | 4647.6787 | 6567.6558 | 8015.6331 | 8015.6331 |  | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 78.1466 | 111.3047 | 154.4126 | 214.9675 | 300.2134 | 420.4494 | 590.3301 | 830.724 | 1171.3683 | 1654.6638 | 2341.101 | 3317.0189 | 3916.1007 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.14814 | 0.21099 | 0.29271 | 0.4075 | 0.5691 | 0.79702 | 1.1191 | 1.5748 | 2.2205 | 3.1366 | 4.4379 | 6.2879 | 7.4235 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 78.2948 | 111.5157 | 154.7053 | 215.375 | 300.7825 | 421.2464 | 591.4492 | 832.2988 | 1173.5888 | 1657.8005 | 2345.5389 | 3323.3067 | 3923.5242 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 42.2603 | 60.1915 | 83.5035 | 116.2505 | 162.3499 | 227.3713 | 319.2397 | 449.2404 | 633.4545 | 894.8119 | 1266.0246 | 1793.7831 | 2117.7556 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3825 | 22.879 | 32.042 | 44.9885 | 63.3087 | 89.2688 | 126.1003 | 178.413 | 252.7867 | 298.4421 | 266.7611 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 | 4.6851 | 6.6085 | 9.3385 | 11.3974 | 11.3974 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012317 | 0.036689 | 0.070143 | 0.11627 | 0.18014 | 0.25658 | 0.35595 | 0.49554 | 0.69204 | 0.96921 | 1.3608 | 1.915 | 2.7002 | 3.8143 | 5.3966 | 7.6463 | 9.0273 | 8.069 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6625 | 25.8027 | 49.331 | 81.7735 | 126.6907 | 180.4462 | 250.3324 | 348.5034 | 486.7034 | 681.629 | 957.0382 | 1346.7627 | 1899.0123 | 2682.527 | 3795.373 | 5377.5229 | 6348.7492 | 5674.8003
| FALSE | 2971 | 22015514 | MLN | Blank | 22 | TRANS NO.3 | BUEF STAGE 2 & 3 | BU | Siemens | 7SR11 | 7SR11 | SIEMENS 7SR11 | Digital |  | 0.0068096 | 1 |  | 0.91058 | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0053028 | 27.137 | 14.6701 | 2.0677 | 0.0064484 |  | 3.0201 | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0053028 | 27.137 | 14.6701 | 2.0677 | 0.0064484 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0053028 | 27.137 | 14.6701 | 2.0677 | 0.0064484 |  | 43.8812 | 43.8812 | 43.8812 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 5.7701e-08 | 7.6486e-08 | 1.0227e-07 | 1.3783e-07 | 1.8706e-07 | 2.5546e-07 | 3.5084e-07 | 4.8422e-07 | 6.7124e-07 | 9.341e-07 | 1.3044e-06 | 1.8269e-06 | 2.5655e-06 | 3.6112e-06 | 5.0937e-06 | 7.198e-06 | 8.7849e-06 | 8.7849e-06 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 52.523 | 69.6224 | 93.0946 | 125.4598 | 170.2699 | 232.5392 | 319.3582 | 440.7675 | 611.0033 | 850.2744 | 1187.2965 | 1662.9113 | 2335.254 | 3287.1371 | 4636.6021 | 6552.0034 | 7996.5298 | 7996.5298 |  | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 52.523 | 69.6224 | 93.0946 | 125.4598 | 170.2699 | 232.5392 | 319.3582 | 440.7675 | 611.0033 | 850.2744 | 1187.2965 | 1662.9113 | 2335.254 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 | 2032.433 | 2866.8057 | 4051.096 | 4944.245 | 4944.245 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9158 | 30.4286 | 50.44 | 78.146 | 111.3038 | 154.4114 | 214.9657 | 300.211 | 420.446 | 590.3253 | 830.7173 | 1171.3588 | 1654.6504 | 2341.082 | 3316.992 | 3916.0689 | 3500.3602 |  | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0063471 | 0.0084135 | 0.01125 | 0.015161 | 0.020576 | 0.028101 | 0.038593 | 0.053264 | 0.073837 | 0.10275 | 0.14348 | 0.20095 | 0.2822 | 0.39723 | 0.56031 | 0.79178 | 0.96634 | 0.96634 |  | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0063471 | 0.0084135 | 0.01125 | 0.015161 | 0.020576 | 0.028101 | 0.038593 | 0.053264 | 0.073837 | 0.10275 | 0.14348 | 0.20095 | 0.2822 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010443 | 0.0031107 | 0.0059472 | 0.0098584 | 0.015273 | 0.021754 | 0.030179 | 0.042014 | 0.058675 | 0.082175 | 0.11538 | 0.16236 | 0.22894 | 0.3234 | 0.45756 | 0.6483 | 0.76538 | 0.68414 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3443 | 15.9189 | 30.4345 | 50.4498 | 78.1613 | 111.3256 | 154.4415 | 215.0077 | 300.2696 | 420.5282 | 590.4407 | 830.8796 | 1171.5877 | 1654.9738 | 2341.5395 | 3317.6403 | 3916.8343 | 3501.0443 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 | 1098.9332 | 1550.0771 | 2190.4209 | 2673.3451 | 2673.3451 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8891 | 8.6056 | 16.4527 | 27.2728 | 42.2534 | 60.1818 | 83.49 | 116.2316 | 162.3236 | 227.3344 | 319.1879 | 449.1675 | 633.3518 | 894.6667 | 1265.8192 | 1793.4921 | 2117.412 | 1892.639 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 | 154.8906 | 218.4777 | 308.7319 | 376.7983 | 376.7983 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3824 | 22.8789 | 32.042 | 44.9884 | 63.3085 | 89.2686 | 126.1 | 178.4126 | 252.7862 | 298.4415 | 266.7606 |  | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0077183 | 0.010231 | 0.01368 | 0.018437 | 0.025021 | 0.034172 | 0.04693 | 0.064771 | 0.089788 | 0.12495 | 0.17448 | 0.24437 | 0.34317 | 0.48305 | 0.68136 | 0.96283 | 1.1751 | 1.1751 |  | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0077183 | 0.010231 | 0.01368 | 0.018437 | 0.025021 | 0.034172 | 0.04693 | 0.064771 | 0.089788 | 0.12495 | 0.17448 | 0.24437 | 0.34317 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012699 | 0.0037827 | 0.007232 | 0.011988 | 0.018573 | 0.026454 | 0.036699 | 0.051091 | 0.071351 | 0.099928 | 0.1403 | 0.19744 | 0.2784 | 0.39326 | 0.55641 | 0.78835 | 0.93073 | 0.83193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6418 | 25.7412 | 49.2134 | 81.5786 | 126.3887 | 180.0162 | 249.7358 | 347.6729 | 485.5435 | 680.0045 | 954.7573 | 1343.5531 | 1894.4865 | 2676.1338 | 3786.3277 | 5364.7069 | 6333.6185 | 5661.2759
| FALSE | 2972 | 22015503 | MLN | Blank | 22 | TRANS NO.3 | DIFFERENTIAL & REF | Y | GE | GE_T60 | GE T60 | GE RELAYS | Digital |  | 0.0068096 | 1 |  | 1.0927 | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0053028 | 27.137 | 14.6701 | 2.0677 | 0.0064484 |  | 5.2187 | 0.0096441 | 8.9962e-08 | 0.009644 | 50.6317 | 0.0098958 | 50.6416 | 27.3765 | 3.8586 | 0.012034 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 27.1317 | 0.0053028 | 27.137 | 14.6701 | 2.0677 | 0.0064484 |  | 43.8812 | 81.8887 | 43.8812 | 38.0075 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 4.8207e-08 | 6.1997e-08 | 8.9962e-08 | 1.3238e-07 | 1.9717e-07 | 2.9677e-07 | 4.507e-07 | 6.8975e-07 | 1.0625e-06 | 1.6457e-06 | 2.5612e-06 | 4.0019e-06 | 6.2742e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 56.4332 | 81.8887 | 120.4979 | 179.4763 | 270.1356 | 410.2553 | 627.8475 | 967.1352 | 1498.0556 | 2331.3798 | 3642.7829 | 5711.1866 | 7996.5298 | 7996.5298 | 7996.5298 | 7996.5298 | 7996.5298 | 7996.5298 | 7996.5298 | 7996.5298 | 7996.5298 | 7996.5298 |  | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 43.8812 | 52.523 | 69.6224 | 93.0946 | 125.4598 | 170.2699 | 232.5392 | 319.3582 | 440.7675 | 611.0033 | 850.2744 | 1187.2965 | 1662.9113 | 2335.254 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 34.8926 | 50.6317 | 74.5037 | 110.97 | 167.0245 | 253.6603 | 388.1974 | 597.9786 | 926.246 | 1441.4894 | 2252.3284 | 3531.22 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 | 4944.245 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7609 | 23.5 | 47.372 | 83.8383 | 139.8928 | 226.5287 | 361.0657 | 570.8469 | 899.1143 | 1409.0144 | 2209.281 | 3473.6597 | 4866.6733 | 4838.9673 | 4800.4662 | 4746.7862 | 4671.719 | 4566.4623 | 4418.5213 | 4210.1409 | 3916.0689 | 3500.3602 |  | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0068197 | 0.0098958 | 0.014562 | 0.021689 | 0.032644 | 0.049577 | 0.075872 | 0.11687 | 0.18103 | 0.28173 | 0.44021 | 0.69017 | 0.96634 | 0.96634 | 0.96634 | 0.96634 | 0.96634 | 0.96634 | 0.96634 | 0.96634 | 0.96634 | 0.96634 |  | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0053028 | 0.0063471 | 0.0084135 | 0.01125 | 0.015161 | 0.020576 | 0.028101 | 0.038593 | 0.053264 | 0.073837 | 0.10275 | 0.14348 | 0.20095 | 0.2822 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015168 | 0.004593 | 0.0092587 | 0.016386 | 0.027342 | 0.044274 | 0.070569 | 0.11157 | 0.17573 | 0.27539 | 0.4318 | 0.67892 | 0.95118 | 0.94576 | 0.93824 | 0.92775 | 0.91307 | 0.8925 | 0.86359 | 0.82286 | 0.76538 | 0.68414 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7624 | 23.5046 | 47.3812 | 83.8547 | 139.9202 | 226.5729 | 361.1363 | 570.9584 | 899.2901 | 1409.2898 | 2209.7128 | 3474.3386 | 4867.6245 | 4839.913 | 4801.4045 | 4747.7139 | 4672.6321 | 4567.3548 | 4419.3849 | 4210.9638 | 3916.8343 | 3501.0443 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 18.8664 | 27.3765 | 40.284 | 60.0013 | 90.3099 | 137.1537 | 209.8977 | 323.326 | 500.8197 | 779.4109 | 1217.8302 | 1909.3248 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1963 | 12.7064 | 25.614 | 45.3312 | 75.6398 | 122.4837 | 195.2276 | 308.656 | 486.1496 | 761.8518 | 1194.5546 | 1878.2021 | 2631.4022 | 2616.4216 | 2595.6042 | 2566.5794 | 2525.9907 | 2469.0787 | 2389.0872 | 2276.4162 | 2117.412 | 1892.639 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6591 | 3.8586 | 5.6779 | 8.457 | 12.7288 | 19.3313 | 29.5843 | 45.5716 | 70.5887 | 109.8551 | 171.6488 | 269.1124 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59145 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2636 | 27.5166 | 43.5039 | 68.521 | 107.3802 | 168.3681 | 264.7258 | 370.8866 | 368.7751 | 365.841 | 361.7501 | 356.0292 | 348.0077 | 336.7332 | 320.8526 | 298.4415 | 266.7606 |  | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0082929 | 0.012034 | 0.017707 | 0.026374 | 0.039697 | 0.060288 | 0.092263 | 0.14212 | 0.22014 | 0.3426 | 0.53531 | 0.83927 | 1.1751 | 1.1751 | 1.1751 | 1.1751 | 1.1751 | 1.1751 | 1.1751 | 1.1751 | 1.1751 | 1.1751 |  | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0064484 | 0.0077183 | 0.010231 | 0.01368 | 0.018437 | 0.025021 | 0.034172 | 0.04693 | 0.064771 | 0.089788 | 0.12495 | 0.17448 | 0.24437 | 0.34317 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018445 | 0.0055853 | 0.011259 | 0.019926 | 0.033248 | 0.053839 | 0.085815 | 0.13567 | 0.21369 | 0.33488 | 0.52508 | 0.82559 | 1.1567 | 1.1501 | 1.1409 | 1.1282 | 1.1103 | 1.0853 | 1.0502 | 1.0006 | 0.93073 | 0.83193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.552 | 38.0075 | 76.6167 | 135.5951 | 226.2544 | 366.3741 | 583.9663 | 923.254 | 1454.1744 | 2278.8567 | 3573.1605 | 5618.0921 | 7871.07 | 7826.2599 | 7763.9906 | 7677.1716 | 7555.7624 | 7385.5265 | 7146.2554 | 6809.2333 | 6333.6185 | 5661.2759
| FALSE | 2973 | 22015517 | MLN | Blank | 22 | TRANS NO.3 | VOLTAGE REGULATION | C | A-EBERLE | REG_D | REG D | REG D | Digital |  | 0 | 1 |  | 0.91058 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 3.0201 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 43.8691 | 43.8691 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 | 3286.2344 | 4635.3288 | 6550.2041 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 | 2032.4311 | 2866.803 | 4051.0922 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 111.3037 | 154.4112 | 214.9655 | 300.2107 | 420.4456 | 590.3248 | 830.7165 | 1171.3577 | 1654.6488 | 2341.0798 | 3316.9889 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 111.3037 | 154.4112 | 214.9655 | 300.2107 | 420.4456 | 590.3248 | 830.7165 | 1171.3577 | 1654.6488 | 2341.0798 | 3316.9889 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 60.1807 | 83.4884 | 116.2294 | 162.3205 | 227.3302 | 319.182 | 449.1591 | 633.3399 | 894.65 | 1265.7955 | 1793.4586 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3824 | 22.8789 | 32.042 | 44.9884 | 63.3085 | 89.2686 | 126.1 | 178.4126 | 252.7861 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6395 | 25.7341 | 49.1999 | 81.5562 | 126.354 | 179.9668 | 249.6672 | 347.5774 | 485.4101 | 679.8177 | 954.4951 | 1343.1841 | 1893.9662 | 2675.3989 | 3785.2879 | 5363.2336 | 6331.8792 | 5659.7211
| FALSE | 2974 | 22015501 | MLN | Blank | 22 | TRANS NO.3 | DIFFERENTIAL & REF | X | Schweitzer | SEL_787 | SEL 787 | SEL 700s | Digital |  | 0.066046 | 1 |  | 0.91058 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 3.0201 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 43.986 | 43.986 | 43.986 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 8.5205e-05 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 | 3294.9899 | 4647.6787 | 6567.6558 | 8015.6331 | 8015.6331 |  | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 78.1466 | 111.3047 | 154.4126 | 214.9675 | 300.2134 | 420.4494 | 590.3301 | 830.724 | 1171.3683 | 1654.6638 | 2341.101 | 3317.0189 | 3916.1007 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.14814 | 0.21099 | 0.29271 | 0.4075 | 0.5691 | 0.79702 | 1.1191 | 1.5748 | 2.2205 | 3.1366 | 4.4379 | 6.2879 | 7.4235 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 78.2948 | 111.5157 | 154.7053 | 215.375 | 300.7825 | 421.2464 | 591.4492 | 832.2988 | 1173.5888 | 1657.8005 | 2345.5389 | 3323.3067 | 3923.5242 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 42.2603 | 60.1915 | 83.5035 | 116.2505 | 162.3499 | 227.3713 | 319.2397 | 449.2404 | 633.4545 | 894.8119 | 1266.0246 | 1793.7831 | 2117.7556 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3825 | 22.879 | 32.042 | 44.9885 | 63.3087 | 89.2688 | 126.1003 | 178.413 | 252.7867 | 298.4421 | 266.7611 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 | 4.6851 | 6.6085 | 9.3385 | 11.3974 | 11.3974 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012317 | 0.036689 | 0.070143 | 0.11627 | 0.18014 | 0.25658 | 0.35595 | 0.49554 | 0.69204 | 0.96921 | 1.3608 | 1.915 | 2.7002 | 3.8143 | 5.3966 | 7.6463 | 9.0273 | 8.069 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6625 | 25.8027 | 49.331 | 81.7735 | 126.6907 | 180.4462 | 250.3324 | 348.5034 | 486.7034 | 681.629 | 957.0382 | 1346.7627 | 1899.0123 | 2682.527 | 3795.373 | 5377.5229 | 6348.7492 | 5674.8003
| FALSE | 2975 | 22015502 | MLN | Blank | 22 | TRANS NO.3 | TX MECH. PROT. & COOLING | X | Schweitzer | SEL_2414 | SEL 2414 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 0.91058 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 3.0201 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 43.986 | 43.986 | 43.986 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 8.5205e-05 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 | 3294.9899 | 4647.6787 | 6567.6558 | 8015.6331 | 8015.6331 |  | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 78.1466 | 111.3047 | 154.4126 | 214.9675 | 300.2134 | 420.4494 | 590.3301 | 830.724 | 1171.3683 | 1654.6638 | 2341.101 | 3317.0189 | 3916.1007 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.14814 | 0.21099 | 0.29271 | 0.4075 | 0.5691 | 0.79702 | 1.1191 | 1.5748 | 2.2205 | 3.1366 | 4.4379 | 6.2879 | 7.4235 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 78.2948 | 111.5157 | 154.7053 | 215.375 | 300.7825 | 421.2464 | 591.4492 | 832.2988 | 1173.5888 | 1657.8005 | 2345.5389 | 3323.3067 | 3923.5242 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 42.2603 | 60.1915 | 83.5035 | 116.2505 | 162.3499 | 227.3713 | 319.2397 | 449.2404 | 633.4545 | 894.8119 | 1266.0246 | 1793.7831 | 2117.7556 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3825 | 22.879 | 32.042 | 44.9885 | 63.3087 | 89.2688 | 126.1003 | 178.413 | 252.7867 | 298.4421 | 266.7611 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 | 4.6851 | 6.6085 | 9.3385 | 11.3974 | 11.3974 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012317 | 0.036689 | 0.070143 | 0.11627 | 0.18014 | 0.25658 | 0.35595 | 0.49554 | 0.69204 | 0.96921 | 1.3608 | 1.915 | 2.7002 | 3.8143 | 5.3966 | 7.6463 | 9.0273 | 8.069 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6625 | 25.8027 | 49.331 | 81.7735 | 126.6907 | 180.4462 | 250.3324 | 348.5034 | 486.7034 | 681.629 | 957.0382 | 1346.7627 | 1899.0123 | 2682.527 | 3795.373 | 5377.5229 | 6348.7492 | 5674.8003
| FALSE | 2976 | 22015924 | MLN | Blank | 22 | TRANS NO.3 | TRANS MGMT | C | Schweitzer | SEL_2440 | SEL 2440 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 0.91058 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 3.0201 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.062544 |  | 43.986 | 43.986 | 43.986 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.5965e-07 | 7.4185e-07 | 9.9195e-07 | 1.3368e-06 | 1.8143e-06 | 2.4778e-06 | 3.4029e-06 | 4.6965e-06 | 6.5104e-06 | 9.0599e-06 | 1.2651e-05 | 1.7719e-05 | 2.4883e-05 | 3.5025e-05 | 4.9404e-05 | 6.9813e-05 | 8.5205e-05 | 8.5205e-05 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 | 3294.9899 | 4647.6787 | 6567.6558 | 8015.6331 | 8015.6331 |  | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 43.986 | 52.6485 | 69.7887 | 93.317 | 125.7596 | 170.6767 | 233.0948 | 320.1211 | 441.8204 | 612.463 | 852.3057 | 1190.1329 | 1666.8839 | 2340.8328 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 | 2032.4495 | 2866.8289 | 4051.1289 | 4944.2851 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3433 | 15.9159 | 30.4288 | 50.4404 | 78.1466 | 111.3047 | 154.4126 | 214.9675 | 300.2134 | 420.4494 | 590.3301 | 830.724 | 1171.3683 | 1654.6638 | 2341.101 | 3317.0189 | 3916.1007 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 | 3.8528 | 5.4345 | 7.6795 | 9.3726 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010129 | 0.030171 | 0.057682 | 0.095617 | 0.14814 | 0.21099 | 0.29271 | 0.4075 | 0.5691 | 0.79702 | 1.1191 | 1.5748 | 2.2205 | 3.1366 | 4.4379 | 6.2879 | 7.4235 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3534 | 15.9461 | 30.4865 | 50.536 | 78.2948 | 111.5157 | 154.7053 | 215.375 | 300.7825 | 421.2464 | 591.4492 | 832.2988 | 1173.5888 | 1657.8005 | 2345.5389 | 3323.3067 | 3923.5242 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 | 1099.1115 | 1550.3286 | 2190.7764 | 2673.779 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8896 | 8.607 | 16.4554 | 27.2772 | 42.2603 | 60.1915 | 83.5035 | 116.2505 | 162.3499 | 227.3713 | 319.2397 | 449.2404 | 633.4545 | 894.8119 | 1266.0246 | 1793.7831 | 2117.7556 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 | 154.891 | 218.4782 | 308.7325 | 376.7991 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3825 | 22.879 | 32.042 | 44.9885 | 63.3087 | 89.2688 | 126.1003 | 178.413 | 252.7867 | 298.4421 | 266.7611 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 | 4.6851 | 6.6085 | 9.3385 | 11.3974 | 11.3974 |  | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.062544 | 0.074861 | 0.099232 | 0.13269 | 0.17882 | 0.24268 | 0.33144 | 0.45518 | 0.62822 | 0.87086 | 1.2119 | 1.6922 | 2.3701 | 3.3284 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012317 | 0.036689 | 0.070143 | 0.11627 | 0.18014 | 0.25658 | 0.35595 | 0.49554 | 0.69204 | 0.96921 | 1.3608 | 1.915 | 2.7002 | 3.8143 | 5.3966 | 7.6463 | 9.0273 | 8.069 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6625 | 25.8027 | 49.331 | 81.7735 | 126.6907 | 180.4462 | 250.3324 | 348.5034 | 486.7034 | 681.629 | 957.0382 | 1346.7627 | 1899.0123 | 2682.527 | 3795.373 | 5377.5229 | 6348.7492 | 5674.8003
| FALSE | 2977 | 22015493 | MLN | Blank | 66 | CB A | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 0.91058 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 3.0201 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 43.8691 | 43.8691 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 | 3286.2344 | 4635.3288 | 6550.2041 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 | 2032.4311 | 2866.803 | 4051.0922 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 111.3037 | 154.4112 | 214.9655 | 300.2107 | 420.4456 | 590.3248 | 830.7165 | 1171.3577 | 1654.6488 | 2341.0798 | 3316.9889 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 111.3037 | 154.4112 | 214.9655 | 300.2107 | 420.4456 | 590.3248 | 830.7165 | 1171.3577 | 1654.6488 | 2341.0798 | 3316.9889 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 60.1807 | 83.4884 | 116.2294 | 162.3205 | 227.3302 | 319.182 | 449.1591 | 633.3399 | 894.65 | 1265.7955 | 1793.4586 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3824 | 22.8789 | 32.042 | 44.9884 | 63.3085 | 89.2686 | 126.1 | 178.4126 | 252.7861 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6395 | 25.7341 | 49.1999 | 81.5562 | 126.354 | 179.9668 | 249.6672 | 347.5774 | 485.4101 | 679.8177 | 954.4951 | 1343.1841 | 1893.9662 | 2675.3989 | 3785.2879 | 5363.2336 | 6331.8792 | 5659.7211
| FALSE | 2978 | 22015494 | MLN | Blank | 66 | CB B | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 0.91058 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 3.0201 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 43.8691 | 43.8691 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 | 3286.2344 | 4635.3288 | 6550.2041 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 | 2032.4311 | 2866.803 | 4051.0922 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 111.3037 | 154.4112 | 214.9655 | 300.2107 | 420.4456 | 590.3248 | 830.7165 | 1171.3577 | 1654.6488 | 2341.0798 | 3316.9889 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 111.3037 | 154.4112 | 214.9655 | 300.2107 | 420.4456 | 590.3248 | 830.7165 | 1171.3577 | 1654.6488 | 2341.0798 | 3316.9889 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 60.1807 | 83.4884 | 116.2294 | 162.3205 | 227.3302 | 319.182 | 449.1591 | 633.3399 | 894.65 | 1265.7955 | 1793.4586 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3824 | 22.8789 | 32.042 | 44.9884 | 63.3085 | 89.2686 | 126.1 | 178.4126 | 252.7861 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6395 | 25.7341 | 49.1999 | 81.5562 | 126.354 | 179.9668 | 249.6672 | 347.5774 | 485.4101 | 679.8177 | 954.4951 | 1343.1841 | 1893.9662 | 2675.3989 | 3785.2879 | 5363.2336 | 6331.8792 | 5659.7211
| FALSE | 2979 | 22015495 | MLN | Blank | 66 | CB C | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 0.91058 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 3.0201 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 43.8691 | 43.8691 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 | 3286.2344 | 4635.3288 | 6550.2041 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 | 2032.4311 | 2866.803 | 4051.0922 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 111.3037 | 154.4112 | 214.9655 | 300.2107 | 420.4456 | 590.3248 | 830.7165 | 1171.3577 | 1654.6488 | 2341.0798 | 3316.9889 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 111.3037 | 154.4112 | 214.9655 | 300.2107 | 420.4456 | 590.3248 | 830.7165 | 1171.3577 | 1654.6488 | 2341.0798 | 3316.9889 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 60.1807 | 83.4884 | 116.2294 | 162.3205 | 227.3302 | 319.182 | 449.1591 | 633.3399 | 894.65 | 1265.7955 | 1793.4586 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3824 | 22.8789 | 32.042 | 44.9884 | 63.3085 | 89.2686 | 126.1 | 178.4126 | 252.7861 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6395 | 25.7341 | 49.1999 | 81.5562 | 126.354 | 179.9668 | 249.6672 | 347.5774 | 485.4101 | 679.8177 | 954.4951 | 1343.1841 | 1893.9662 | 2675.3989 | 3785.2879 | 5363.2336 | 6331.8792 | 5659.7211
| FALSE | 2980 | 22015500 | MLN | Blank | 66 | CB C | CB FAIL | Y | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 0.91058 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 3.0201 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 43.8691 | 43.8691 | 0 |  | 0.11989 |  | 1.0266 | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 | 3286.2344 | 4635.3288 | 6550.2041 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 | 2032.4311 | 2866.803 | 4051.0922 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 111.3037 | 154.4112 | 214.9655 | 300.2107 | 420.4456 | 590.3248 | 830.7165 | 1171.3577 | 1654.6488 | 2341.0798 | 3316.9889 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3432 | 15.9157 | 30.4286 | 50.4399 | 78.1459 | 111.3037 | 154.4112 | 214.9655 | 300.2107 | 420.4456 | 590.3248 | 830.7165 | 1171.3577 | 1654.6488 | 2341.0798 | 3316.9889 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 60.1807 | 83.4884 | 116.2294 | 162.3205 | 227.3302 | 319.182 | 449.1591 | 633.3399 | 894.65 | 1265.7955 | 1793.4586 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.4824 | 11.7676 | 16.3824 | 22.8789 | 32.042 | 44.9884 | 63.3085 | 89.2686 | 126.1 | 178.4126 | 252.7861 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6395 | 25.7341 | 49.1999 | 81.5562 | 126.354 | 179.9668 | 249.6672 | 347.5774 | 485.4101 | 679.8177 | 954.4951 | 1343.1841 | 1893.9662 | 2675.3989 | 3785.2879 | 5363.2336 | 6331.8792 | 5659.7211
| FALSE | 2981 | 22015480 | MLN | Blank | 66 | CB D | CB MGMT & CB FAIL | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0 | 1 |  | 1.0927 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 5.2187 | 0.0096441 | 0 | 0.0096441 | 50.6316 | 0 | 50.6316 | 27.376 | 3.8586 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 81.8662 | 43.8691 | 37.9971 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 56.4177 | 81.8662 | 120.4648 | 179.427 | 270.0614 | 410.1426 | 627.6751 | 966.8696 | 1497.6442 | 2330.7395 | 3641.7825 | 5709.6182 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 34.8925 | 50.6316 | 74.5036 | 110.9699 | 167.0244 | 253.6601 | 388.197 | 597.978 | 926.2452 | 1441.488 | 2252.3263 | 3531.2167 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7609 | 23.5 | 47.3719 | 83.8382 | 139.8927 | 226.5284 | 361.0654 | 570.8463 | 899.1135 | 1409.0131 | 2209.2789 | 3473.6565 | 4866.6688 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7609 | 23.5 | 47.3719 | 83.8382 | 139.8927 | 226.5284 | 361.0654 | 570.8463 | 899.1135 | 1409.0131 | 2209.2789 | 3473.6565 | 4866.6688 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 18.866 | 27.376 | 40.2833 | 60.0002 | 90.3082 | 137.1512 | 209.8938 | 323.32 | 500.8103 | 779.3964 | 1217.8075 | 1909.2892 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1962 | 12.7062 | 25.6135 | 45.3304 | 75.6384 | 122.4814 | 195.224 | 308.6502 | 486.1406 | 761.8376 | 1194.5323 | 1878.167 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6591 | 3.8586 | 5.6779 | 8.457 | 12.7288 | 19.3313 | 29.5843 | 45.5716 | 70.5887 | 109.8551 | 171.6487 | 269.1123 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59145 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2636 | 27.5166 | 43.5039 | 68.521 | 107.3802 | 168.3681 | 264.7257 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5485 | 37.9971 | 76.5956 | 135.5579 | 226.1922 | 366.2735 | 583.8059 | 923.0005 | 1453.7751 | 2278.2309 | 3572.1793 | 5616.5492 | 7868.9084 | 7824.1106 | 7761.8584 | 7675.0633 | 7553.6874 | 7383.4983 | 7144.2929 | 6807.3633 | 6331.8792 | 5659.7211
| FALSE | 2982 | 22015483 | MLN | MLN-DPTS NO.1 | 66 | DPTS NO.1 LINE | DISTANCE & DIR EF | Y | GE | GE_L90 | GE L90 | GE RELAYS | Digital |  | 0.016937 | 1 |  | 1.0927 | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.016039 |  | 5.2187 | 0.0096441 | 2.2376e-07 | 0.0096439 | 50.6318 | 0.024613 | 50.6564 | 27.3772 | 3.8586 | 0.029931 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.016039 |  | 43.8991 | 81.9221 | 43.8991 | 38.023 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.542e-07 | 2.2376e-07 | 3.2926e-07 | 4.9041e-07 | 7.3813e-07 | 1.121e-06 | 1.7156e-06 | 2.6427e-06 | 4.0934e-06 | 6.3704e-06 | 9.9538e-06 | 1.5606e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 56.4562 | 81.9221 | 120.5471 | 179.5496 | 270.2459 | 410.4228 | 628.1039 | 967.5302 | 1498.6675 | 2332.332 | 3644.2708 | 5713.5193 | 7999.7958 | 7999.7958 | 7999.7958 | 7999.7958 | 7999.7958 | 7999.7958 | 7999.7958 | 7999.7958 | 7999.7958 | 7999.7958 |  | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 52.5445 | 69.6508 | 93.1326 | 125.5111 | 170.3395 | 232.6342 | 319.4886 | 440.9475 | 611.2529 | 850.6217 | 1187.7815 | 1663.5904 | 2336.2077 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 34.8926 | 50.6318 | 74.5038 | 110.9702 | 167.0247 | 253.6607 | 388.1979 | 597.9794 | 926.2473 | 1441.4914 | 2252.3315 | 3531.2249 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7609 | 23.5 | 47.3721 | 83.8384 | 139.893 | 226.529 | 361.0662 | 570.8477 | 899.1156 | 1409.0164 | 2209.284 | 3473.6645 | 4866.6801 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.016962 | 0.024613 | 0.036218 | 0.053945 | 0.081195 | 0.12331 | 0.18871 | 0.29069 | 0.45027 | 0.70074 | 1.0949 | 1.7166 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015787 | 0.020926 | 0.027982 | 0.03771 | 0.051178 | 0.069894 | 0.09599 | 0.13248 | 0.18365 | 0.25557 | 0.35687 | 0.49982 | 0.70191 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0037728 | 0.011424 | 0.023029 | 0.040756 | 0.068005 | 0.11012 | 0.17552 | 0.2775 | 0.43708 | 0.68496 | 1.074 | 1.6886 | 2.3658 | 2.3523 | 2.3336 | 2.3075 | 2.271 | 2.2199 | 2.148 | 2.0467 | 1.9037 | 1.7016 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7647 | 23.5115 | 47.3951 | 83.8792 | 139.961 | 226.6391 | 361.2417 | 571.1252 | 899.5527 | 1409.7014 | 2210.358 | 3475.3532 | 4869.0459 | 4841.3263 | 4802.8065 | 4749.1003 | 4673.9965 | 4568.6886 | 4420.6754 | 4212.1934 | 3917.978 | 3502.0667 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 18.8669 | 27.3772 | 40.2851 | 60.003 | 90.3124 | 137.1575 | 209.9035 | 323.335 | 500.8336 | 779.4325 | 1217.864 | 1909.3778 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1964 | 12.7068 | 25.6147 | 45.3325 | 75.6419 | 122.4871 | 195.233 | 308.6645 | 486.1631 | 761.8729 | 1194.5877 | 1878.2542 | 2631.4752 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6591 | 3.8586 | 5.6779 | 8.457 | 12.7289 | 19.3313 | 29.5843 | 45.5716 | 70.5887 | 109.8552 | 171.6488 | 269.1125 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59145 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2636 | 27.5166 | 43.504 | 68.5211 | 107.3803 | 168.3682 | 264.7259 | 370.8867 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.020627 | 0.029931 | 0.044043 | 0.065599 | 0.098736 | 0.14995 | 0.22948 | 0.35349 | 0.54755 | 0.85213 | 1.3315 | 2.0875 | 2.9228 | 2.9228 | 2.9228 | 2.9228 | 2.9228 | 2.9228 | 2.9228 | 2.9228 | 2.9228 | 2.9228 |  | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.019197 | 0.025447 | 0.034027 | 0.045856 | 0.062234 | 0.084994 | 0.11673 | 0.1611 | 0.22332 | 0.31078 | 0.43396 | 0.6078 | 0.85355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0045878 | 0.013892 | 0.028004 | 0.049561 | 0.082697 | 0.13391 | 0.21344 | 0.33745 | 0.53151 | 0.83293 | 1.306 | 2.0534 | 2.8769 | 2.8605 | 2.8378 | 2.806 | 2.7617 | 2.6994 | 2.612 | 2.4888 | 2.315 | 2.0692 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5571 | 38.023 | 76.648 | 135.6505 | 226.3468 | 366.5237 | 584.2048 | 923.6311 | 1454.7683 | 2279.7875 | 3574.6199 | 5620.3866 | 7874.2847 | 7829.4563 | 7767.1616 | 7680.3072 | 7558.8484 | 7388.543 | 7149.1741 | 6812.0144 | 6336.2054 | 5663.5881
| FALSE | 2983 | 22015505 | MLN | MLN-DPTS NO.1 | 66 | DPTS NO.1 LINE | CURRENT DIFF, DIST & DEF | X | Schweitzer | SEL_311L | SEL 311L | SEL 300s | Digital |  | 0.15703 | 1 |  | 1.0927 | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.1487 |  | 5.2187 | 0.0096441 | 2.0745e-06 | 0.009642 | 50.6327 | 0.2282 | 50.8609 | 27.3877 | 3.8586 | 0.2775 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.1487 |  | 44.147 | 82.3848 | 44.147 | 38.2378 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.4296e-06 | 2.0745e-06 | 3.0526e-06 | 4.5467e-06 | 6.8434e-06 | 1.0393e-05 | 1.5905e-05 | 2.4501e-05 | 3.7951e-05 | 5.9062e-05 | 9.2284e-05 | 0.00014468 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 56.775 | 82.3848 | 121.2278 | 180.5636 | 271.7721 | 412.7406 | 631.6511 | 972.9942 | 1507.131 | 2345.5035 | 3664.8513 | 5745.7856 | 8044.9737 | 8044.9737 | 8044.9737 | 8044.9737 | 8044.9737 | 8044.9737 | 8044.9737 | 8044.9737 | 8044.9737 | 8044.9737 |  | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 52.8412 | 70.0442 | 93.6586 | 126.2199 | 171.3015 | 233.948 | 321.2929 | 443.4377 | 614.7048 | 855.4255 | 1194.4893 | 1672.9854 | 2349.4012 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 34.8933 | 50.6327 | 74.5052 | 110.9723 | 167.0279 | 253.6656 | 388.2054 | 597.9909 | 926.2651 | 1441.519 | 2252.3748 | 3531.2926 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.761 | 23.5005 | 47.373 | 83.84 | 139.8957 | 226.5333 | 361.0731 | 570.8586 | 899.1328 | 1409.0434 | 2209.3264 | 3473.7312 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.15726 | 0.2282 | 0.33579 | 0.50014 | 0.75278 | 1.1432 | 1.7496 | 2.6951 | 4.1746 | 6.4968 | 10.1512 | 15.9152 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034978 | 0.10591 | 0.21351 | 0.37786 | 0.6305 | 1.021 | 1.6273 | 2.5728 | 4.0523 | 6.3504 | 9.9572 | 15.6558 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.796 | 23.6064 | 47.5865 | 84.2179 | 140.5262 | 227.5543 | 362.7004 | 573.4314 | 903.1851 | 1415.3939 | 2219.2836 | 3489.387 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 18.8741 | 27.3877 | 40.3006 | 60.026 | 90.347 | 137.2102 | 209.9841 | 323.4591 | 501.0258 | 779.7317 | 1218.3314 | 1910.1106 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.198 | 12.7116 | 25.6245 | 45.3499 | 75.6709 | 122.5341 | 195.308 | 308.783 | 486.3497 | 762.1653 | 1195.0462 | 1878.975 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6592 | 3.8586 | 5.6779 | 8.457 | 12.7289 | 19.3314 | 29.5845 | 45.5719 | 70.5891 | 109.8557 | 171.6496 | 269.1138 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59146 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2637 | 27.5168 | 43.5042 | 68.5214 | 107.3808 | 168.369 | 264.7271 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.19123 | 0.2775 | 0.40833 | 0.60819 | 0.91541 | 1.3902 | 2.1276 | 3.2773 | 5.0764 | 7.9003 | 12.3443 | 19.3534 | 27.0977 | 27.0977 | 27.0977 | 27.0977 | 27.0977 | 27.0977 | 27.0977 | 27.0977 | 27.0977 | 27.0977 |  | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.17798 | 0.23593 | 0.31547 | 0.42514 | 0.57699 | 0.788 | 1.0822 | 1.4936 | 2.0705 | 2.8813 | 4.0234 | 5.6351 | 7.9134 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042535 | 0.1288 | 0.25963 | 0.45949 | 0.76671 | 1.2415 | 1.9789 | 3.1286 | 4.9277 | 7.7223 | 12.1083 | 19.038 | 26.6726 | 26.5207 | 26.3097 | 26.0155 | 25.6041 | 25.0272 | 24.2164 | 23.0744 | 21.4627 | 19.1843 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.628 | 38.2378 | 77.0808 | 136.4166 | 227.6251 | 368.5936 | 587.504 | 928.8472 | 1462.984 | 2292.6623 | 3594.8071 | 5652.1271 | 7918.7538 | 7873.6722 | 7811.0257 | 7723.6808 | 7601.536 | 7430.2688 | 7189.5482 | 6850.4844 | 6371.9883 | 5695.5725
| FALSE | 2984 | 22015485 | MLN | MLN-DPTS NO.2 | 66 | DPTS NO.2 LINE | DISTANCE & DIR EF | Y | GE | GE_L90 | GE L90 | GE RELAYS | Digital |  | 0.016937 | 1 |  | 1.0927 | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.016039 |  | 5.2187 | 0.0096441 | 2.2376e-07 | 0.0096439 | 50.6318 | 0.024613 | 50.6564 | 27.3772 | 3.8586 | 0.029931 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.016039 |  | 43.8991 | 81.9221 | 43.8991 | 38.023 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.542e-07 | 2.2376e-07 | 3.2926e-07 | 4.9041e-07 | 7.3813e-07 | 1.121e-06 | 1.7156e-06 | 2.6427e-06 | 4.0934e-06 | 6.3704e-06 | 9.9538e-06 | 1.5606e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 56.4562 | 81.9221 | 120.5471 | 179.5496 | 270.2459 | 410.4228 | 628.1039 | 967.5302 | 1498.6675 | 2332.332 | 3644.2708 | 5713.5193 | 7999.7958 | 7999.7958 | 7999.7958 | 7999.7958 | 7999.7958 | 7999.7958 | 7999.7958 | 7999.7958 | 7999.7958 | 7999.7958 |  | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 43.8991 | 52.5445 | 69.6508 | 93.1326 | 125.5111 | 170.3395 | 232.6342 | 319.4886 | 440.9475 | 611.2529 | 850.6217 | 1187.7815 | 1663.5904 | 2336.2077 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 34.8926 | 50.6318 | 74.5038 | 110.9702 | 167.0247 | 253.6607 | 388.1979 | 597.9794 | 926.2473 | 1441.4914 | 2252.3315 | 3531.2249 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7609 | 23.5 | 47.3721 | 83.8384 | 139.893 | 226.529 | 361.0662 | 570.8477 | 899.1156 | 1409.0164 | 2209.284 | 3473.6645 | 4866.6801 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.016962 | 0.024613 | 0.036218 | 0.053945 | 0.081195 | 0.12331 | 0.18871 | 0.29069 | 0.45027 | 0.70074 | 1.0949 | 1.7166 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015787 | 0.020926 | 0.027982 | 0.03771 | 0.051178 | 0.069894 | 0.09599 | 0.13248 | 0.18365 | 0.25557 | 0.35687 | 0.49982 | 0.70191 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0037728 | 0.011424 | 0.023029 | 0.040756 | 0.068005 | 0.11012 | 0.17552 | 0.2775 | 0.43708 | 0.68496 | 1.074 | 1.6886 | 2.3658 | 2.3523 | 2.3336 | 2.3075 | 2.271 | 2.2199 | 2.148 | 2.0467 | 1.9037 | 1.7016 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7647 | 23.5115 | 47.3951 | 83.8792 | 139.961 | 226.6391 | 361.2417 | 571.1252 | 899.5527 | 1409.7014 | 2210.358 | 3475.3532 | 4869.0459 | 4841.3263 | 4802.8065 | 4749.1003 | 4673.9965 | 4568.6886 | 4420.6754 | 4212.1934 | 3917.978 | 3502.0667 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 18.8669 | 27.3772 | 40.2851 | 60.003 | 90.3124 | 137.1575 | 209.9035 | 323.335 | 500.8336 | 779.4325 | 1217.864 | 1909.3778 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1964 | 12.7068 | 25.6147 | 45.3325 | 75.6419 | 122.4871 | 195.233 | 308.6645 | 486.1631 | 761.8729 | 1194.5877 | 1878.2542 | 2631.4752 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6591 | 3.8586 | 5.6779 | 8.457 | 12.7289 | 19.3313 | 29.5843 | 45.5716 | 70.5887 | 109.8552 | 171.6488 | 269.1125 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59145 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2636 | 27.5166 | 43.504 | 68.5211 | 107.3803 | 168.3682 | 264.7259 | 370.8867 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.020627 | 0.029931 | 0.044043 | 0.065599 | 0.098736 | 0.14995 | 0.22948 | 0.35349 | 0.54755 | 0.85213 | 1.3315 | 2.0875 | 2.9228 | 2.9228 | 2.9228 | 2.9228 | 2.9228 | 2.9228 | 2.9228 | 2.9228 | 2.9228 | 2.9228 |  | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.016039 | 0.019197 | 0.025447 | 0.034027 | 0.045856 | 0.062234 | 0.084994 | 0.11673 | 0.1611 | 0.22332 | 0.31078 | 0.43396 | 0.6078 | 0.85355 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0045878 | 0.013892 | 0.028004 | 0.049561 | 0.082697 | 0.13391 | 0.21344 | 0.33745 | 0.53151 | 0.83293 | 1.306 | 2.0534 | 2.8769 | 2.8605 | 2.8378 | 2.806 | 2.7617 | 2.6994 | 2.612 | 2.4888 | 2.315 | 2.0692 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5571 | 38.023 | 76.648 | 135.6505 | 226.3468 | 366.5237 | 584.2048 | 923.6311 | 1454.7683 | 2279.7875 | 3574.6199 | 5620.3866 | 7874.2847 | 7829.4563 | 7767.1616 | 7680.3072 | 7558.8484 | 7388.543 | 7149.1741 | 6812.0144 | 6336.2054 | 5663.5881
| FALSE | 2985 | 22015484 | MLN | MLN-DPTS NO.2 | 66 | DPTS NO.2 LINE | CURRENT DIFF, DIST & DEF | X | Schweitzer | SEL_311L | SEL 311L | SEL 300s | Digital |  | 0.15703 | 1 |  | 1.0927 | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.1487 |  | 5.2187 | 0.0096441 | 2.0745e-06 | 0.009642 | 50.6327 | 0.2282 | 50.8609 | 27.3877 | 3.8586 | 0.2775 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.1487 |  | 44.147 | 82.3848 | 44.147 | 38.2378 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.4296e-06 | 2.0745e-06 | 3.0526e-06 | 4.5467e-06 | 6.8434e-06 | 1.0393e-05 | 1.5905e-05 | 2.4501e-05 | 3.7951e-05 | 5.9062e-05 | 9.2284e-05 | 0.00014468 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 56.775 | 82.3848 | 121.2278 | 180.5636 | 271.7721 | 412.7406 | 631.6511 | 972.9942 | 1507.131 | 2345.5035 | 3664.8513 | 5745.7856 | 8044.9737 | 8044.9737 | 8044.9737 | 8044.9737 | 8044.9737 | 8044.9737 | 8044.9737 | 8044.9737 | 8044.9737 | 8044.9737 |  | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 44.147 | 52.8412 | 70.0442 | 93.6586 | 126.2199 | 171.3015 | 233.948 | 321.2929 | 443.4377 | 614.7048 | 855.4255 | 1194.4893 | 1672.9854 | 2349.4012 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 34.8933 | 50.6327 | 74.5052 | 110.9723 | 167.0279 | 253.6656 | 388.2054 | 597.9909 | 926.2651 | 1441.519 | 2252.3748 | 3531.2926 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.761 | 23.5005 | 47.373 | 83.84 | 139.8957 | 226.5333 | 361.0731 | 570.8586 | 899.1328 | 1409.0434 | 2209.3264 | 3473.7312 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.15726 | 0.2282 | 0.33579 | 0.50014 | 0.75278 | 1.1432 | 1.7496 | 2.6951 | 4.1746 | 6.4968 | 10.1512 | 15.9152 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034978 | 0.10591 | 0.21351 | 0.37786 | 0.6305 | 1.021 | 1.6273 | 2.5728 | 4.0523 | 6.3504 | 9.9572 | 15.6558 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.796 | 23.6064 | 47.5865 | 84.2179 | 140.5262 | 227.5543 | 362.7004 | 573.4314 | 903.1851 | 1415.3939 | 2219.2836 | 3489.387 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 18.8741 | 27.3877 | 40.3006 | 60.026 | 90.347 | 137.2102 | 209.9841 | 323.4591 | 501.0258 | 779.7317 | 1218.3314 | 1910.1106 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.198 | 12.7116 | 25.6245 | 45.3499 | 75.6709 | 122.5341 | 195.308 | 308.783 | 486.3497 | 762.1653 | 1195.0462 | 1878.975 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6592 | 3.8586 | 5.6779 | 8.457 | 12.7289 | 19.3314 | 29.5845 | 45.5719 | 70.5891 | 109.8557 | 171.6496 | 269.1138 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59146 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2637 | 27.5168 | 43.5042 | 68.5214 | 107.3808 | 168.369 | 264.7271 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.19123 | 0.2775 | 0.40833 | 0.60819 | 0.91541 | 1.3902 | 2.1276 | 3.2773 | 5.0764 | 7.9003 | 12.3443 | 19.3534 | 27.0977 | 27.0977 | 27.0977 | 27.0977 | 27.0977 | 27.0977 | 27.0977 | 27.0977 | 27.0977 | 27.0977 |  | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.1487 | 0.17798 | 0.23593 | 0.31547 | 0.42514 | 0.57699 | 0.788 | 1.0822 | 1.4936 | 2.0705 | 2.8813 | 4.0234 | 5.6351 | 7.9134 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042535 | 0.1288 | 0.25963 | 0.45949 | 0.76671 | 1.2415 | 1.9789 | 3.1286 | 4.9277 | 7.7223 | 12.1083 | 19.038 | 26.6726 | 26.5207 | 26.3097 | 26.0155 | 25.6041 | 25.0272 | 24.2164 | 23.0744 | 21.4627 | 19.1843 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.628 | 38.2378 | 77.0808 | 136.4166 | 227.6251 | 368.5936 | 587.504 | 928.8472 | 1462.984 | 2292.6623 | 3594.8071 | 5652.1271 | 7918.7538 | 7873.6722 | 7811.0257 | 7723.6808 | 7601.536 | 7430.2688 | 7189.5482 | 6850.4844 | 6371.9883 | 5695.5725
| FALSE | 2986 | 22015491 | MLN | Blank | 66 | STATION GPS CLOCK | GPS CLOCK | C | Tekron | TCG01_G | TCG01 G | GPS Clock | Digital |  | 0.2894 | 1 |  | 1.0266 | 0.0051679 | 2.0488e-06 | 0.0051659 | 27.1327 | 0.22536 | 27.3581 | 14.6814 | 2.0677 | 0.27405 |  | 3.4047 | 0.0051679 | 2.0488e-06 | 0.0051659 | 27.1327 | 0.22536 | 27.3581 | 14.6814 | 2.0677 | 0.27405 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 27.1327 | 0.22536 | 27.3581 | 14.6814 | 2.0677 | 0.27405 |  | 44.3813 | 44.3813 | 44.3813 | 0 |  | 0.11989 |  | 1.1573 | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 |  | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.4522e-06 | 3.2506e-06 | 4.3465e-06 | 5.8575e-06 | 7.9497e-06 | 1.0857e-05 | 1.491e-05 | 2.0579e-05 | 2.8527e-05 | 3.9698e-05 | 5.5433e-05 | 7.7639e-05 | 0.00010903 | 0.00015347 | 0.00021648 | 0.0003059 | 0.00037335 | 0.00037335 | 0.00037335 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 53.1216 | 70.4158 | 94.1555 | 126.8896 | 172.2104 | 235.1893 | 322.9977 | 445.7906 | 617.9666 | 859.9645 | 1200.8275 | 1681.8625 | 2361.8675 | 3324.5988 | 4689.4428 | 6626.6729 | 8087.6617 | 8087.6617 | 8087.6617 |  | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 44.3813 | 53.1216 | 70.4158 | 94.1555 | 126.8896 | 172.2104 | 235.1893 | 322.9977 | 445.7906 | 617.9666 | 859.9645 | 1200.8275 | 1681.8625 | 2361.8675 |  | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 32.4762 | 43.0491 | 57.5625 | 77.5747 | 105.2818 | 143.7843 | 197.4664 | 272.5365 | 377.7973 | 525.744 | 734.1325 | 1028.2159 | 1443.9407 | 2032.5117 | 2866.9166 | 4051.2528 | 4944.4364 | 4944.4364 | 4944.4364 |  | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 27.1327 | 32.4762 | 43.0491 | 57.5625 | 77.5747 | 105.2818 | 143.7843 | 197.4664 | 272.5365 | 377.7973 | 525.744 | 734.1325 | 1028.2159 | 1443.9407 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3434 | 15.9164 | 30.4298 | 50.4419 | 78.149 | 116.6516 | 164.9903 | 229.4874 | 320.2348 | 448.1694 | 628.8507 | 884.4316 | 1246.4742 | 1759.9752 | 2489.1194 | 3525.5088 | 4210.3039 | 3916.2205 | 3500.4957 |  | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.26975 | 0.35756 | 0.47811 | 0.64433 | 0.87446 | 1.1943 | 1.6401 | 2.2637 | 3.138 | 4.3668 | 6.0977 | 8.5403 | 11.9933 | 16.8819 | 23.8124 | 33.6495 | 41.0682 | 41.0682 | 41.0682 |  | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.22536 | 0.26975 | 0.35756 | 0.47811 | 0.64433 | 0.87446 | 1.1943 | 1.6401 | 2.2637 | 3.138 | 4.3668 | 6.0977 | 8.5403 | 11.9933 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044382 | 0.1322 | 0.25275 | 0.41897 | 0.6491 | 0.9689 | 1.3704 | 1.9061 | 2.6599 | 3.7225 | 5.2232 | 7.346 | 10.3531 | 14.6182 | 20.6745 | 29.2827 | 34.9705 | 32.5279 | 29.0749 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3878 | 16.0486 | 30.6825 | 50.8609 | 78.7981 | 117.6205 | 166.3607 | 231.3935 | 322.8946 | 451.8918 | 634.0739 | 891.7776 | 1256.8274 | 1774.5934 | 2509.7938 | 3554.7915 | 4245.2744 | 3948.7484 | 3529.5706 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 | 1099.784 | 1551.2772 | 2192.1168 | 2675.4148 | 2675.4148 | 2675.4148 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8913 | 8.6123 | 16.4654 | 27.2939 | 42.2861 | 63.1197 | 89.2756 | 124.1747 | 173.2778 | 242.5027 | 340.2686 | 478.5624 | 674.4622 | 952.3155 | 1346.8526 | 1907.6388 | 2278.1786 | 2119.0513 | 1894.1043 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 | 154.8921 | 218.4799 | 308.7349 | 376.8019 | 376.8019 | 376.8019 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.319 | 3.844 | 5.9555 | 8.8897 | 12.5735 | 17.4886 | 24.4042 | 34.1538 | 47.923 | 67.4001 | 94.9904 | 134.1229 | 189.689 | 268.6694 | 320.8557 | 298.4444 | 266.7632 |  | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.32802 | 0.43481 | 0.5814 | 0.78353 | 1.0634 | 1.4523 | 1.9945 | 2.7527 | 3.8159 | 5.3102 | 7.415 | 10.3853 | 14.5843 | 20.529 | 28.9568 | 40.9189 | 49.9404 | 49.9404 | 49.9404 |  | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.27405 | 0.32802 | 0.43481 | 0.5814 | 0.78353 | 1.0634 | 1.4523 | 1.9945 | 2.7527 | 3.8159 | 5.3102 | 7.415 | 10.3853 | 14.5843 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053971 | 0.16076 | 0.30735 | 0.50948 | 0.78933 | 1.1782 | 1.6665 | 2.3179 | 3.2345 | 4.5267 | 6.3516 | 8.933 | 12.5898 | 17.7763 | 25.1409 | 35.6088 | 42.5254 | 39.5551 | 35.3561 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7403 | 26.0346 | 49.7742 | 82.5084 | 127.8291 | 190.8081 | 269.8761 | 375.3748 | 523.8111 | 733.0749 | 1028.6171 | 1446.6732 | 2038.8698 | 2878.8081 | 4071.4763 | 5766.7083 | 6886.8342 | 6405.7992 | 5725.7942
| TRUE | 3658 | 22005021 | SA | Blank | 22 | BUS ALL | OV-UV SUPERVISION | C | RMS | 2V67 | 2V67 | 2V6X | Digital |  | 0 | 1 |  | 5.5 | 0.010964 | 0 | 0.010964 | 45.2259 | 0 | 45.2259 | 31.1222 | 4.3866 | 0 |  | 11.3746 | 0.073406 | 0 | 0.073406 | 302.8017 | 0 | 302.8017 | 208.3728 | 29.3699 | 0 |  | 0.0051679 | 0 | 0.0051679 | 21.3177 | 0 | 21.3177 | 14.6698 | 2.0677 | 0 |  | 80.7347 | 540.5445 | 38.0552 | 502.4893 |  | 0.072663 |  | 5.9145 | 6.3603 | 6.8397 | 7.3552 | 7.9095 | 8.5056 | 9.1467 | 9.8361 | 10.5774 | 11.3746 | 12.2319 | 13.1538 | 14.1452 | 15.2113 | 16.3577 | 17.5906 | 18.9164 | 20.3421 | 21.8752 | 23.5239 | 25.2969 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.013125 | 0.015756 | 0.01896 | 0.022871 | 0.027649 | 0.033493 | 0.040649 | 0.049422 | 0.060186 | 0.073406 | 0.089657 | 0.10965 | 0.13426 | 0.16458 | 0.20196 | 0.24807 | 0.30498 | 0.37525 | 0.46207 | 0.56938 | 0.70207 | 0.86622 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6519 | 116.0195 | 139.6197 | 168.4161 | 203.5978 | 246.6316 | 299.3292 | 363.928 | 443.1934 | 540.5445 | 660.2101 | 807.4225 | 988.6581 | 1211.9355 | 1487.1856 | 1826.7116 | 2245.7591 | 2763.2249 | 3402.5362 | 4192.7435 | 5169.877 | 6378.632 | 6934.8537 | 6934.8537 | 6934.8537 | 6934.8537 | 6934.8537 | 6934.8537 | 6934.8537 | 6934.8537 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 54.1424 | 64.9917 | 78.212 | 94.3432 | 114.0512 | 138.1579 | 167.678 | 203.8649 | 248.2677 | 302.8017 | 369.8359 | 452.3012 | 553.8256 | 678.901 | 833.0903 | 1023.2857 | 1258.0274 | 1547.9009 | 1906.0297 | 2348.6874 | 2896.0572 | 3573.1765 | 3884.7603 | 3884.7603 | 3884.7603 | 3884.7603 | 3884.7603 | 3884.7603 | 3884.7603 | 3884.7603 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 39.9305 | 50.7799 | 64.0002 | 80.1314 | 99.8394 | 123.9461 | 153.4661 | 189.653 | 234.0559 | 288.5899 | 355.6241 | 438.0894 | 539.6138 | 664.6891 | 818.8785 | 1009.0739 | 1243.8155 | 1530.8902 | 1883.4811 | 2318.5368 | 2855.4244 | 3518.0311 | 3809.4477 | 3781.3296 | 3742.0087 | 3686.8743 | 3609.3815 | 3500.23 | 3346.1924 | 3128.4404 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 39.9305 | 50.7799 | 64.0002 | 80.1314 | 99.8394 | 123.9461 | 153.4661 | 189.653 | 234.0559 | 288.5899 | 355.6241 | 438.0894 | 539.6138 | 664.6891 | 818.8785 | 1009.0739 | 1243.8155 | 1530.8902 | 1883.4811 | 2318.5368 | 2855.4244 | 3518.0311 | 3809.4477 | 3781.3296 | 3742.0087 | 3686.8743 | 3609.3815 | 3500.23 | 3346.1924 | 3128.4404 |  | 37.258 | 44.724 | 53.8216 | 64.9222 | 78.4843 | 95.0733 | 115.3875 | 140.2895 | 170.8453 | 208.3728 | 254.5023 | 311.2508 | 381.1148 | 467.1852 | 573.2906 | 704.1734 | 865.7107 | 1065.187 | 1311.6331 | 1616.2477 | 1992.9198 | 2458.879 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 22.5882 | 30.0542 | 39.1518 | 50.2524 | 63.8145 | 80.4035 | 100.7177 | 125.6197 | 156.1755 | 193.703 | 239.8325 | 296.581 | 366.445 | 452.5155 | 558.6208 | 689.5036 | 851.0409 | 1047.6282 | 1288.3579 | 1585.1255 | 1950.9777 | 2401.9566 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 5.2515 | 6.3038 | 7.5861 | 9.1507 | 11.0623 | 13.4005 | 16.2637 | 19.7737 | 24.0805 | 29.3699 | 35.8718 | 43.8705 | 53.7177 | 65.8493 | 80.8047 | 99.2525 | 122.021 | 150.137 | 184.8733 | 227.8084 | 280.9 | 346.5765 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 3.1838 | 4.2361 | 5.5184 | 7.083 | 8.9946 | 11.3328 | 14.1961 | 17.706 | 22.0128 | 27.3022 | 33.8042 | 41.8028 | 51.65 | 63.7816 | 78.737 | 97.1848 | 119.9533 | 147.6621 | 181.5927 | 223.4218 | 274.9883 | 338.5533 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 65.7026 | 85.0702 | 108.6704 | 137.4668 | 172.6485 | 215.6823 | 268.3799 | 332.9787 | 412.2441 | 509.5952 | 629.2608 | 776.4732 | 957.7088 | 1180.9862 | 1456.2363 | 1795.7623 | 2214.8098 | 2726.1805 | 3353.4317 | 4127.0841 | 5081.3905 | 6258.541 | 6770.8443 | 6709.6111 | 6623.9815 | 6503.9145 | 6335.1572 | 6097.4563 | 5762.0063 | 5287.8046
| TRUE | 3659 | 22014607 | SA | Blank | 22 | BUS ALL | VOLTAGE REGULATION | C | RMS | 2V164S | 2V164 S | 2V164S | Digital |  | 0 | 1 |  | 1.1573 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 3.8384 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 30.9493 | 30.9493 | 0 |  | 0.11989 |  | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 125.7409 | 175.3373 | 245.2282 | 343.8976 | 483.4225 | 681.0073 | 961.1761 | 1358.9071 | 1924.1147 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 125.7409 | 175.3373 | 245.2282 | 343.8976 | 483.4225 | 681.0073 | 961.1761 | 1358.9071 | 1924.1147 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 129.7928 | 180.9874 | 253.1305 | 354.9794 | 499.0003 | 702.9521 | 992.149 | 1402.6966 | 1986.1174 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.2942 | 25.51 | 35.6785 | 50.034 | 70.3336 | 99.0804 | 139.8424 | 197.7086 | 279.9412 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 133.0601 | 194.2933 | 273.8279 | 381.8347 | 534.0372 | 748.9109 | 1052.7564 | 1483.0397 | 2093.1675 | 2959.3123 | 4190.1734 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 3660 | 22009879 | SA | Blank | 22 | BUS NO.1 | BUS PROT | X | GEC | CDG14_984 | CDG14 984 | CDG14 | Electromechanical |  | 0.033587 | 2190 |  | 8.25 | 0.0054067 | 0.00050998 | 0.0048967 | 30.0172 | 142.7954 | 172.8125 | 18.2427 | 2.1683 | 797.288 |  | 11.3866 | 0.012884 | 0.0012153 | 0.011669 | 71.5296 | 340.2754 | 411.805 | 43.4717 | 5.167 | 1899.9043 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.37173 |  | 990.5116 | 2360.348 | 45.6009 | 2314.7471 |  | 0.032223 |  | 8.5202 | 8.7992 | 9.0873 | 9.3849 | 9.6922 | 10.0096 | 10.3374 | 10.6759 | 11.0256 | 11.3866 | 11.7595 | 12.1446 | 12.5423 | 12.953 | 13.3772 | 13.8153 | 14.2677 | 14.7349 | 15.2174 | 15.7158 | 16.2304 | 16.7619 | 17.3108 | 17.8777 | 18.4631 | 19.0678 | 19.6922 | 20.337 | 21.003 | 21.6908 |  | 0.0058881 | 0.0064147 | 0.006991 | 0.0076217 | 0.0083121 | 0.009068 | 0.0098958 | 0.010802 | 0.011796 | 0.012884 | 0.014076 | 0.015383 | 0.016816 | 0.018387 | 0.020109 | 0.021998 | 0.02407 | 0.026342 | 0.028836 | 0.031571 | 0.034573 | 0.037868 | 0.041485 | 0.045455 | 0.049813 | 0.054599 | 0.059854 | 0.065625 | 0.071963 | 0.078925 |  | 0.00055539 | 0.00060507 | 0.00065942 | 0.00071891 | 0.00078404 | 0.00085534 | 0.00093342 | 0.0010189 | 0.0011126 | 0.0012153 | 0.0013278 | 0.001451 | 0.0015862 | 0.0017343 | 0.0018968 | 0.002075 | 0.0022704 | 0.0024847 | 0.0027199 | 0.002978 | 0.0032611 | 0.0035719 | 0.003913 | 0.0042875 | 0.0046986 | 0.00515 | 0.0056457 | 0.00619 | 0.0067879 | 0.0074446 | 1078.7037 | 1175.1858 | 1280.7594 | 1396.3047 | 1522.7885 | 1661.2727 | 1812.9242 | 1979.025 | 2160.9837 | 2360.348 | 2578.8191 | 2818.2663 | 3080.7445 | 3368.5121 | 3684.0519 | 4030.0929 | 4409.6359 | 4825.9795 | 5282.7511 | 5783.9389 | 6333.9286 | 6937.5432 | 7600.0867 | 8327.3924 | 9125.8761 | 10002.5947 | 10965.3103 | 12022.5613 | 13183.7403 | 14459.1802 |  | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 37.5716 | 49.8033 | 66.5938 | 89.7458 | 121.8 | 166.3434 | 228.4481 | 315.2963 | 437.072 | 608.2309 | 849.3146 | 1189.5384 | 1670.4885 |  | 32.6898 | 35.6137 | 38.813 | 42.3146 | 46.1476 | 50.3444 | 54.9401 | 59.9738 | 65.488 | 71.5296 | 78.1503 | 85.4067 | 93.361 | 102.0817 | 111.6441 | 122.1308 | 133.6327 | 146.2499 | 160.0922 | 175.2805 | 191.9478 | 210.2402 | 230.3183 | 252.3591 | 276.5569 | 303.1256 | 332.3004 | 364.3401 | 399.5293 | 438.1811 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 18.4779 | 21.4018 | 24.6011 | 28.1027 | 31.9358 | 36.1325 | 40.7282 | 45.7619 | 51.2761 | 57.3177 | 63.9384 | 71.1948 | 79.1491 | 87.8699 | 97.4322 | 107.9189 | 119.4208 | 129.2391 | 137.5434 | 145.1298 | 151.3149 | 155.0945 | 155.0054 | 148.9279 | 133.8047 | 105.2388 | 56.9204 | -20.192 | -139.0411 | -318.1423 |  | 155.5094 | 169.4186 | 184.6384 | 201.2958 | 219.5301 | 239.4944 | 261.357 | 285.3026 | 311.5344 | 340.2754 | 371.7709 | 406.2904 | 444.1301 | 485.6156 | 531.1048 | 580.9912 | 635.7074 | 695.7288 | 761.5785 | 833.8313 | 913.1196 | 1000.1386 | 1095.653 | 1200.5038 | 1315.6158 | 1442.0064 | 1580.7946 | 1733.2113 | 1900.6106 | 2084.4821 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 155.4428 | 169.352 | 184.5718 | 201.2292 | 219.4635 | 239.4279 | 261.2904 | 285.2361 | 311.4678 | 340.2088 | 371.7043 | 406.2238 | 444.0635 | 485.549 | 531.0382 | 580.9246 | 635.6408 | 695.6491 | 761.4728 | 833.6901 | 912.9293 | 999.8803 | 1095.3002 | 1200.0193 | 1314.947 | 1441.0793 | 1579.5045 | 1731.4099 | 1898.0876 | 2080.939 |  | 173.9207 | 190.7538 | 209.173 | 229.3319 | 251.3993 | 275.5603 | 302.0187 | 330.9979 | 362.7439 | 397.5266 | 435.6428 | 477.4186 | 523.2127 | 573.4189 | 628.4704 | 688.8435 | 755.0616 | 824.8882 | 899.0163 | 978.8199 | 1064.2441 | 1154.9748 | 1250.3056 | 1348.9472 | 1448.7517 | 1546.3181 | 1636.4249 | 1711.2179 | 1759.0465 | 1762.7968 |  | 19.867 | 21.644 | 23.5884 | 25.7164 | 28.046 | 30.5965 | 33.3895 | 36.4487 | 39.7999 | 43.4717 | 47.4954 | 51.9054 | 56.7396 | 62.0396 | 67.851 | 74.2242 | 81.2145 | 88.8825 | 97.2951 | 106.5257 | 116.6551 | 127.7722 | 139.9746 | 153.3697 | 168.0758 | 184.2228 | 201.9536 | 221.4255 | 242.8115 | 266.3019 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 5.1959 | 6.9728 | 8.9172 | 11.0453 | 13.3748 | 15.9253 | 18.7184 | 21.7776 | 25.1288 | 28.8006 | 32.8243 | 37.2343 | 42.0685 | 47.3684 | 53.1799 | 59.5531 | 66.5433 | 71.322 | 74.0177 | 75.4006 | 74.7092 | 70.8445 | 62.2279 | 46.5962 | 20.7106 | -20.0587 | -82.3252 | -175.5325 | -313.1624 | -514.4615 |  | 2.3614 | 2.5726 | 2.8037 | 3.0566 | 3.3335 | 3.6367 | 3.9686 | 4.3322 | 4.7306 | 5.167 | 5.6452 | 6.1694 | 6.744 | 7.3739 | 8.0647 | 8.8222 | 9.653 | 10.5644 | 11.5644 | 12.6615 | 13.8655 | 15.1868 | 16.6372 | 18.2293 | 19.9773 | 21.8965 | 24.0039 | 26.3183 | 28.8602 | 31.6523 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0.29367 | 0.50488 | 0.73599 | 0.98893 | 1.2658 | 1.569 | 1.9009 | 2.2645 | 2.6629 | 3.0993 | 3.5775 | 4.1017 | 4.6763 | 5.3062 | 5.997 | 6.7545 | 7.5853 | 8.0895 | 8.2837 | 8.2749 | 7.9538 | 7.1637 | 5.6799 | 3.1811 | -0.79183 | -6.8942 | -16.0612 | -29.6274 | -49.4966 | -78.3855 |  | 868.2761 | 945.937 | 1030.9159 | 1123.9213 | 1225.7313 | 1337.2007 | 1459.2689 | 1592.9677 | 1739.4308 | 1899.9043 | 2075.7572 | 2268.4944 | 2479.7698 | 2711.4013 | 2965.3873 | 3243.9246 | 3549.4283 | 3884.554 | 4252.221 | 4655.6398 | 5098.3406 | 5584.2054 | 6117.5035 | 6702.9304 | 7345.6503 | 8051.3435 | 8826.2578 | 9677.2661 | 10611.9287 | 11638.5628 |  | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.44494 | 0.58979 | 0.78863 | 1.0628 | 1.4424 | 1.9699 | 2.7054 | 3.7339 | 5.176 | 7.2029 | 10.0579 | 14.087 | 19.7826 |  | 867.9043 | 945.5653 | 1030.5442 | 1123.5495 | 1225.3595 | 1336.829 | 1458.8972 | 1592.596 | 1739.0591 | 1899.5326 | 2075.3855 | 2268.1227 | 2479.3981 | 2711.0296 | 2965.0155 | 3243.5528 | 3549.0566 | 3884.109 | 4251.6312 | 4654.8512 | 5097.2778 | 5582.763 | 6115.5336 | 6700.225 | 7341.9165 | 8046.1675 | 8819.0549 | 9667.2082 | 10597.8417 | 11618.7801 |  | 1047.3146 | 1143.7968 | 1249.3704 | 1364.9157 | 1491.3994 | 1629.8837 | 1781.5352 | 1947.636 | 2129.5946 | 2328.959 | 2547.4301 | 2786.8773 | 3049.3555 | 3337.1231 | 3652.6628 | 3998.7039 | 4378.2468 | 4788.4088 | 5232.9489 | 5717.3466 | 6244.1848 | 6815.746 | 7433.7471 | 8098.9495 | 8810.587 | 9565.5327 | 10357.0933 | 11173.2662 | 11994.2292 | 12788.7299
| TRUE | 3661 | 22009880 | SA | Blank | 22 | BUS NO.1 | BUS PROT | X | GEC | CDG14_984 | CDG14 984 | CDG14 | Electromechanical |  | 0.033587 | 2190 |  | 8.25 | 0.0054067 | 0.00050998 | 0.0048967 | 30.0172 | 142.7954 | 172.8125 | 18.2427 | 2.1683 | 797.288 |  | 11.9015 | 0.014549 | 0.0013724 | 0.013177 | 80.7762 | 384.2624 | 465.0386 | 49.0912 | 5.8349 | 2145.5028 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.37173 |  | 990.5116 | 2665.4676 | 45.6009 | 2619.8667 |  | 0.036645 |  | 8.5579 | 8.8774 | 9.2087 | 9.5524 | 9.909 | 10.2788 | 10.6625 | 11.0604 | 11.4733 | 11.9015 | 12.3457 | 12.8065 | 13.2845 | 13.7804 | 14.2947 | 14.8283 | 15.3818 | 15.9559 | 16.5514 | 17.1692 | 17.8101 | 18.4748 | 19.1644 | 19.8797 | 20.6217 | 21.3914 | 22.1898 | 23.0181 | 23.8772 | 24.7684 |  | 0.0059576 | 0.0065678 | 0.0072438 | 0.007993 | 0.0088234 | 0.0097442 | 0.010765 | 0.011898 | 0.013155 | 0.014549 | 0.016097 | 0.017816 | 0.019724 | 0.021844 | 0.024198 | 0.026813 | 0.02972 | 0.032949 | 0.03654 | 0.040531 | 0.044968 | 0.049903 | 0.055391 | 0.061495 | 0.068286 | 0.075841 | 0.084248 | 0.093603 | 0.10402 | 0.1156 |  | 0.00056195 | 0.0006195 | 0.00068327 | 0.00075394 | 0.00083227 | 0.00091912 | 0.0010154 | 0.0011223 | 0.0012408 | 0.0013724 | 0.0015184 | 0.0016805 | 0.0018605 | 0.0020604 | 0.0022825 | 0.0025292 | 0.0028033 | 0.003108 | 0.0034466 | 0.0038231 | 0.0042416 | 0.0047071 | 0.0052247 | 0.0058005 | 0.0064411 | 0.0071537 | 0.0079467 | 0.0088291 | 0.0098113 | 0.010904 | 1091.4383 | 1203.2258 | 1327.0762 | 1464.327 | 1616.4664 | 1785.1504 | 1972.2221 | 2179.7333 | 2409.9676 | 2665.4676 | 2949.064 | 3263.9087 | 3613.5119 | 4001.7825 | 4433.0741 | 4912.2362 | 5444.6705 | 6036.3946 | 6694.1127 | 7425.2944 | 8238.2623 | 9142.2905 | 10147.7138 | 11266.0496 | 12510.1337 | 13894.2729 | 15434.4131 | 17148.3294 | 19055.8355 | 21179.0198 |  | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 37.5716 | 49.8033 | 66.5938 | 89.7458 | 121.8 | 166.3434 | 228.4481 | 315.2963 | 437.072 | 608.2309 | 849.3146 | 1189.5384 | 1670.4885 |  | 33.0757 | 36.4634 | 40.2166 | 44.376 | 48.9865 | 54.0984 | 59.7676 | 66.0562 | 73.0333 | 80.7762 | 89.3705 | 98.9118 | 109.5064 | 121.2728 | 134.343 | 148.8638 | 164.9991 | 182.9311 | 202.8631 | 225.0213 | 249.6581 | 277.0544 | 307.5234 | 341.4142 | 379.1158 | 421.0618 | 467.7353 | 519.675 | 577.4814 | 641.8238 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 18.8638 | 22.2515 | 26.0048 | 30.1641 | 34.7746 | 39.8866 | 45.5557 | 51.8443 | 58.8215 | 66.5643 | 75.1586 | 84.6999 | 95.2945 | 107.0609 | 120.1311 | 134.652 | 150.7872 | 165.9204 | 180.3143 | 194.8706 | 209.0251 | 221.9087 | 232.2105 | 237.9831 | 236.3636 | 223.1749 | 192.3552 | 135.1429 | 38.911 | -114.4995 |  | 157.3453 | 173.4609 | 191.3156 | 211.1021 | 233.035 | 257.353 | 284.3219 | 314.2374 | 347.4287 | 384.2624 | 425.1466 | 470.5356 | 520.9356 | 576.9099 | 639.0863 | 708.1638 | 784.9213 | 870.2262 | 965.0449 | 1070.4544 | 1187.6545 | 1317.9821 | 1462.9272 | 1624.1501 | 1803.5013 | 2003.0433 | 2225.0749 | 2472.1586 | 2747.1508 | 3053.2359 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 157.2787 | 173.3943 | 191.249 | 211.0355 | 232.9684 | 257.2865 | 284.2553 | 314.1708 | 347.3621 | 384.1958 | 425.08 | 470.469 | 520.869 | 576.8433 | 639.0197 | 708.0973 | 784.8547 | 870.1465 | 964.9393 | 1070.3132 | 1187.4642 | 1317.7238 | 1462.5744 | 1623.6656 | 1802.8326 | 2002.1162 | 2223.7848 | 2470.3572 | 2744.6278 | 3049.6928 |  | 176.1425 | 195.6458 | 217.2538 | 241.1996 | 267.7431 | 297.173 | 329.8111 | 366.0151 | 406.1836 | 450.7602 | 500.2386 | 555.1689 | 616.1635 | 683.9042 | 759.1508 | 842.7492 | 935.6419 | 1036.0668 | 1145.2536 | 1265.1838 | 1396.4893 | 1539.6325 | 1694.7849 | 1861.6486 | 2039.1962 | 2225.2911 | 2416.14 | 2605.5 | 2783.5388 | 2935.1933 |  | 20.1016 | 22.1604 | 24.4414 | 26.9692 | 29.7713 | 32.878 | 36.3234 | 40.1452 | 44.3856 | 49.0912 | 54.3144 | 60.113 | 66.5518 | 73.7028 | 81.6461 | 90.4711 | 100.2772 | 111.1753 | 123.2888 | 136.7553 | 151.7282 | 168.3781 | 186.8955 | 207.4924 | 230.4053 | 255.8977 | 284.2633 | 315.8293 | 350.9608 | 390.0645 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 5.4304 | 7.4893 | 9.7703 | 12.2981 | 15.1001 | 18.2069 | 21.6523 | 25.4741 | 29.7144 | 34.4201 | 39.6432 | 45.4419 | 51.8807 | 59.0317 | 66.975 | 75.8 | 85.6061 | 93.6148 | 100.0114 | 105.6303 | 109.7822 | 111.4505 | 109.1489 | 100.7189 | 83.0402 | 51.6163 | -0.015525 | -81.1287 | -205.0131 | -390.6989 |  | 2.3892 | 2.634 | 2.9051 | 3.2055 | 3.5386 | 3.9078 | 4.3173 | 4.7716 | 5.2756 | 5.8349 | 6.4557 | 7.145 | 7.9103 | 8.7602 | 9.7043 | 10.7533 | 11.9188 | 13.2141 | 14.6539 | 16.2545 | 18.0342 | 20.0132 | 22.2141 | 24.6623 | 27.3857 | 30.4156 | 33.7871 | 37.539 | 41.7147 | 46.3625 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0.32155 | 0.56626 | 0.83738 | 1.1378 | 1.4709 | 1.8401 | 2.2497 | 2.7039 | 3.2079 | 3.7672 | 4.388 | 5.0773 | 5.8426 | 6.6925 | 7.6367 | 8.6856 | 9.8511 | 10.7392 | 11.3733 | 11.8679 | 12.1225 | 11.99 | 11.2568 | 9.614 | 6.6166 | 1.625 | -6.278 | -18.4067 | -36.6421 | -63.6753 |  | 878.5265 | 968.5071 | 1068.1975 | 1178.6742 | 1301.135 | 1436.913 | 1587.4919 | 1754.5229 | 1939.8444 | 2145.5028 | 2373.7768 | 2627.2033 | 2908.6078 | 3221.1367 | 3568.2944 | 3953.9842 | 4382.5541 | 4858.8479 | 5388.262 | 5976.8087 | 6631.1873 | 7358.8627 | 8168.1536 | 9068.3305 | 10069.7256 | 11183.8544 | 12423.5526 | 13803.1275 | 15338.5278 | 17047.533 |  | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.44494 | 0.58979 | 0.78863 | 1.0628 | 1.4424 | 1.9699 | 2.7054 | 3.7339 | 5.176 | 7.2029 | 10.0579 | 14.087 | 19.7826 |  | 878.1547 | 968.1354 | 1067.8258 | 1178.3024 | 1300.7633 | 1436.5413 | 1587.1202 | 1754.1512 | 1939.4727 | 2145.1311 | 2373.405 | 2626.8316 | 2908.2361 | 3220.765 | 3567.9227 | 3953.6124 | 4382.1824 | 4858.403 | 5387.6722 | 5976.0201 | 6630.1245 | 7357.4203 | 8166.1837 | 9065.6251 | 10065.9917 | 11178.6785 | 12416.3497 | 13793.0695 | 15324.4408 | 17027.7504 |  | 1060.0492 | 1171.8368 | 1295.6872 | 1432.938 | 1585.0774 | 1753.7613 | 1940.8331 | 2148.3443 | 2378.5786 | 2634.0786 | 2917.6749 | 3232.5197 | 3582.1229 | 3970.3935 | 4401.6851 | 4880.8472 | 5413.2815 | 5998.8239 | 6644.3105 | 7358.7021 | 8148.5185 | 9020.4933 | 9981.3742 | 11037.6067 | 12194.8446 | 13457.2109 | 14826.1961 | 16299.0342 | 17866.3244 | 19508.5695
| TRUE | 3662 | 22009881 | SA | Blank | 22 | BUS NO.1 | BUS PROT | X | GEC | CDG14_984 | CDG14 984 | CDG14 | Electromechanical |  | 0.033587 | 2190 |  | 8.25 | 0.0054067 | 0.00050998 | 0.0048967 | 30.0172 | 142.7954 | 172.8125 | 18.2427 | 2.1683 | 797.288 |  | 11.9015 | 0.014549 | 0.0013724 | 0.013177 | 80.7762 | 384.2624 | 465.0386 | 49.0912 | 5.8349 | 2145.5028 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.37173 |  | 990.5116 | 2665.4676 | 45.6009 | 2619.8667 |  | 0.036645 |  | 8.5579 | 8.8774 | 9.2087 | 9.5524 | 9.909 | 10.2788 | 10.6625 | 11.0604 | 11.4733 | 11.9015 | 12.3457 | 12.8065 | 13.2845 | 13.7804 | 14.2947 | 14.8283 | 15.3818 | 15.9559 | 16.5514 | 17.1692 | 17.8101 | 18.4748 | 19.1644 | 19.8797 | 20.6217 | 21.3914 | 22.1898 | 23.0181 | 23.8772 | 24.7684 |  | 0.0059576 | 0.0065678 | 0.0072438 | 0.007993 | 0.0088234 | 0.0097442 | 0.010765 | 0.011898 | 0.013155 | 0.014549 | 0.016097 | 0.017816 | 0.019724 | 0.021844 | 0.024198 | 0.026813 | 0.02972 | 0.032949 | 0.03654 | 0.040531 | 0.044968 | 0.049903 | 0.055391 | 0.061495 | 0.068286 | 0.075841 | 0.084248 | 0.093603 | 0.10402 | 0.1156 |  | 0.00056195 | 0.0006195 | 0.00068327 | 0.00075394 | 0.00083227 | 0.00091912 | 0.0010154 | 0.0011223 | 0.0012408 | 0.0013724 | 0.0015184 | 0.0016805 | 0.0018605 | 0.0020604 | 0.0022825 | 0.0025292 | 0.0028033 | 0.003108 | 0.0034466 | 0.0038231 | 0.0042416 | 0.0047071 | 0.0052247 | 0.0058005 | 0.0064411 | 0.0071537 | 0.0079467 | 0.0088291 | 0.0098113 | 0.010904 | 1091.4383 | 1203.2258 | 1327.0762 | 1464.327 | 1616.4664 | 1785.1504 | 1972.2221 | 2179.7333 | 2409.9676 | 2665.4676 | 2949.064 | 3263.9087 | 3613.5119 | 4001.7825 | 4433.0741 | 4912.2362 | 5444.6705 | 6036.3946 | 6694.1127 | 7425.2944 | 8238.2623 | 9142.2905 | 10147.7138 | 11266.0496 | 12510.1337 | 13894.2729 | 15434.4131 | 17148.3294 | 19055.8355 | 21179.0198 |  | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 37.5716 | 49.8033 | 66.5938 | 89.7458 | 121.8 | 166.3434 | 228.4481 | 315.2963 | 437.072 | 608.2309 | 849.3146 | 1189.5384 | 1670.4885 |  | 33.0757 | 36.4634 | 40.2166 | 44.376 | 48.9865 | 54.0984 | 59.7676 | 66.0562 | 73.0333 | 80.7762 | 89.3705 | 98.9118 | 109.5064 | 121.2728 | 134.343 | 148.8638 | 164.9991 | 182.9311 | 202.8631 | 225.0213 | 249.6581 | 277.0544 | 307.5234 | 341.4142 | 379.1158 | 421.0618 | 467.7353 | 519.675 | 577.4814 | 641.8238 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 18.8638 | 22.2515 | 26.0048 | 30.1641 | 34.7746 | 39.8866 | 45.5557 | 51.8443 | 58.8215 | 66.5643 | 75.1586 | 84.6999 | 95.2945 | 107.0609 | 120.1311 | 134.652 | 150.7872 | 165.9204 | 180.3143 | 194.8706 | 209.0251 | 221.9087 | 232.2105 | 237.9831 | 236.3636 | 223.1749 | 192.3552 | 135.1429 | 38.911 | -114.4995 |  | 157.3453 | 173.4609 | 191.3156 | 211.1021 | 233.035 | 257.353 | 284.3219 | 314.2374 | 347.4287 | 384.2624 | 425.1466 | 470.5356 | 520.9356 | 576.9099 | 639.0863 | 708.1638 | 784.9213 | 870.2262 | 965.0449 | 1070.4544 | 1187.6545 | 1317.9821 | 1462.9272 | 1624.1501 | 1803.5013 | 2003.0433 | 2225.0749 | 2472.1586 | 2747.1508 | 3053.2359 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 157.2787 | 173.3943 | 191.249 | 211.0355 | 232.9684 | 257.2865 | 284.2553 | 314.1708 | 347.3621 | 384.1958 | 425.08 | 470.469 | 520.869 | 576.8433 | 639.0197 | 708.0973 | 784.8547 | 870.1465 | 964.9393 | 1070.3132 | 1187.4642 | 1317.7238 | 1462.5744 | 1623.6656 | 1802.8326 | 2002.1162 | 2223.7848 | 2470.3572 | 2744.6278 | 3049.6928 |  | 176.1425 | 195.6458 | 217.2538 | 241.1996 | 267.7431 | 297.173 | 329.8111 | 366.0151 | 406.1836 | 450.7602 | 500.2386 | 555.1689 | 616.1635 | 683.9042 | 759.1508 | 842.7492 | 935.6419 | 1036.0668 | 1145.2536 | 1265.1838 | 1396.4893 | 1539.6325 | 1694.7849 | 1861.6486 | 2039.1962 | 2225.2911 | 2416.14 | 2605.5 | 2783.5388 | 2935.1933 |  | 20.1016 | 22.1604 | 24.4414 | 26.9692 | 29.7713 | 32.878 | 36.3234 | 40.1452 | 44.3856 | 49.0912 | 54.3144 | 60.113 | 66.5518 | 73.7028 | 81.6461 | 90.4711 | 100.2772 | 111.1753 | 123.2888 | 136.7553 | 151.7282 | 168.3781 | 186.8955 | 207.4924 | 230.4053 | 255.8977 | 284.2633 | 315.8293 | 350.9608 | 390.0645 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 5.4304 | 7.4893 | 9.7703 | 12.2981 | 15.1001 | 18.2069 | 21.6523 | 25.4741 | 29.7144 | 34.4201 | 39.6432 | 45.4419 | 51.8807 | 59.0317 | 66.975 | 75.8 | 85.6061 | 93.6148 | 100.0114 | 105.6303 | 109.7822 | 111.4505 | 109.1489 | 100.7189 | 83.0402 | 51.6163 | -0.015525 | -81.1287 | -205.0131 | -390.6989 |  | 2.3892 | 2.634 | 2.9051 | 3.2055 | 3.5386 | 3.9078 | 4.3173 | 4.7716 | 5.2756 | 5.8349 | 6.4557 | 7.145 | 7.9103 | 8.7602 | 9.7043 | 10.7533 | 11.9188 | 13.2141 | 14.6539 | 16.2545 | 18.0342 | 20.0132 | 22.2141 | 24.6623 | 27.3857 | 30.4156 | 33.7871 | 37.539 | 41.7147 | 46.3625 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0.32155 | 0.56626 | 0.83738 | 1.1378 | 1.4709 | 1.8401 | 2.2497 | 2.7039 | 3.2079 | 3.7672 | 4.388 | 5.0773 | 5.8426 | 6.6925 | 7.6367 | 8.6856 | 9.8511 | 10.7392 | 11.3733 | 11.8679 | 12.1225 | 11.99 | 11.2568 | 9.614 | 6.6166 | 1.625 | -6.278 | -18.4067 | -36.6421 | -63.6753 |  | 878.5265 | 968.5071 | 1068.1975 | 1178.6742 | 1301.135 | 1436.913 | 1587.4919 | 1754.5229 | 1939.8444 | 2145.5028 | 2373.7768 | 2627.2033 | 2908.6078 | 3221.1367 | 3568.2944 | 3953.9842 | 4382.5541 | 4858.8479 | 5388.262 | 5976.8087 | 6631.1873 | 7358.8627 | 8168.1536 | 9068.3305 | 10069.7256 | 11183.8544 | 12423.5526 | 13803.1275 | 15338.5278 | 17047.533 |  | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.44494 | 0.58979 | 0.78863 | 1.0628 | 1.4424 | 1.9699 | 2.7054 | 3.7339 | 5.176 | 7.2029 | 10.0579 | 14.087 | 19.7826 |  | 878.1547 | 968.1354 | 1067.8258 | 1178.3024 | 1300.7633 | 1436.5413 | 1587.1202 | 1754.1512 | 1939.4727 | 2145.1311 | 2373.405 | 2626.8316 | 2908.2361 | 3220.765 | 3567.9227 | 3953.6124 | 4382.1824 | 4858.403 | 5387.6722 | 5976.0201 | 6630.1245 | 7357.4203 | 8166.1837 | 9065.6251 | 10065.9917 | 11178.6785 | 12416.3497 | 13793.0695 | 15324.4408 | 17027.7504 |  | 1060.0492 | 1171.8368 | 1295.6872 | 1432.938 | 1585.0774 | 1753.7613 | 1940.8331 | 2148.3443 | 2378.5786 | 2634.0786 | 2917.6749 | 3232.5197 | 3582.1229 | 3970.3935 | 4401.6851 | 4880.8472 | 5413.2815 | 5998.8239 | 6644.3105 | 7358.7021 | 8148.5185 | 9020.4933 | 9981.3742 | 11037.6067 | 12194.8446 | 13457.2109 | 14826.1961 | 16299.0342 | 17866.3244 | 19508.5695
| TRUE | 3663 | 22005005 | SA | Blank | 22 | BUS NO.1 | DISTANCE | X | Schweitzer | SEL_311A | SEL 311A | SEL 300s | Digital |  | 0.033587 | 1 |  | 6.6 | 0.017308 | 7.9633e-07 | 0.017307 | 47.5968 | 0.055743 | 47.6526 | 49.1349 | 6.9249 | 1.245 |  | 15.598 | 0.17662 | 8.1263e-06 | 0.17661 | 485.7104 | 0.56884 | 486.2792 | 501.4057 | 70.6662 | 12.7044 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.37173 |  | 104.9573 | 1071.0555 | 31.3391 | 1039.7164 |  | 0.086007 |  | 7.1928 | 7.8388 | 8.5428 | 9.3101 | 10.1463 | 11.0575 | 12.0507 | 13.133 | 14.3125 | 15.598 | 16.9989 | 18.5257 | 20.1895 | 22.0028 | 23.979 | 26.1326 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021585 | 0.027005 | 0.033883 | 0.042625 | 0.053753 | 0.067937 | 0.086039 | 0.10917 | 0.13875 | 0.17662 | 0.22515 | 0.28739 | 0.36726 | 0.46984 | 0.60168 | 0.7712 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 9.9315e-07 | 1.2425e-06 | 1.5589e-06 | 1.9612e-06 | 2.4732e-06 | 3.1258e-06 | 3.9587e-06 | 5.0228e-06 | 6.3838e-06 | 8.1263e-06 | 1.0359e-05 | 1.3223e-05 | 1.6898e-05 | 2.1618e-05 | 2.7683e-05 | 3.5483e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 130.8973 | 163.7617 | 205.4695 | 258.4832 | 325.9657 | 411.9809 | 521.7544 | 662.0084 | 841.3951 | 1071.0555 | 1365.3418 | 1742.7491 | 2227.1209 | 2849.2051 | 3648.6652 | 4676.6798 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 |  | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 37.5109 | 49.723 | 66.4863 | 89.601 | 121.6035 | 166.075 | 228.0794 | 314.7875 | 436.3667 | 607.2495 | 847.9441 | 1187.6189 | 1667.7929 |  | 59.3603 | 74.2639 | 93.1778 | 117.2189 | 147.8214 | 186.8282 | 236.6091 | 300.2126 | 381.5622 | 485.7104 | 619.1655 | 790.3151 | 1009.9717 | 1292.0791 | 1654.6243 | 2120.8162 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 45.1484 | 60.052 | 78.966 | 103.007 | 133.6095 | 172.6163 | 222.3972 | 286.0007 | 367.3503 | 471.4985 | 604.9536 | 776.1032 | 995.7598 | 1277.8672 | 1640.4124 | 2106.6043 | 2575.6402 | 2572.8414 | 2567.3034 | 2559.7014 | 2549.2192 | 2534.7064 | 2514.5392 | 2486.4209 | 2447.0999 | 2391.9652 | 2314.472 | 2205.32 | 2051.2817 | 1833.5287 |  | 0.06952 | 0.086975 | 0.10913 | 0.13728 | 0.17312 | 0.21881 | 0.27711 | 0.3516 | 0.44687 | 0.56884 | 0.72514 | 0.92558 | 1.1828 | 1.5132 | 1.9378 | 2.4838 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019922 | 0.026408 | 0.035311 | 0.047588 | 0.064584 | 0.088203 | 0.12113 | 0.16719 | 0.23176 | 0.32251 | 0.45035 | 0.63075 | 0.88577 |  | 0.052876 | 0.07033 | 0.092482 | 0.12064 | 0.15648 | 0.20216 | 0.26046 | 0.33495 | 0.43022 | 0.5522 | 0.7085 | 0.90894 | 1.1662 | 1.4966 | 1.9212 | 2.4672 | 3.0165 | 3.0132 | 3.0067 | 2.9978 | 2.9855 | 2.9685 | 2.9449 | 2.912 | 2.8659 | 2.8014 | 2.7106 | 2.5828 | 2.4024 | 2.1473 |  | 45.2013 | 60.1223 | 79.0584 | 103.1277 | 133.766 | 172.8185 | 222.6577 | 286.3356 | 367.7805 | 472.0507 | 605.6621 | 777.0121 | 996.926 | 1279.3638 | 1642.3336 | 2109.0714 | 2578.6567 | 2575.8546 | 2570.3101 | 2562.6992 | 2552.2047 | 2537.675 | 2517.4841 | 2489.3329 | 2449.9658 | 2394.7666 | 2317.1826 | 2207.9028 | 2053.6841 | 1835.6761 |  | 61.2785 | 76.6637 | 96.1888 | 121.0068 | 152.5981 | 192.8654 | 244.255 | 309.9137 | 393.8921 | 501.4057 | 639.1734 | 815.8535 | 1042.6081 | 1333.8317 | 1708.0922 | 2189.3487 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 46.6074 | 61.9926 | 81.5177 | 106.3356 | 137.927 | 178.1943 | 229.5838 | 295.2426 | 379.221 | 486.7346 | 624.5022 | 801.1824 | 1027.937 | 1319.1605 | 1693.4211 | 2174.6776 | 2658.8701 | 2655.9808 | 2650.2638 | 2642.4162 | 2631.5953 | 2616.6136 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 8.6364 | 10.8047 | 13.5565 | 17.0542 | 21.5066 | 27.1817 | 34.4244 | 43.678 | 55.5136 | 70.6662 | 90.0826 | 114.9833 | 146.9412 | 187.9851 | 240.732 | 308.5584 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 6.5687 | 8.737 | 11.4888 | 14.9865 | 19.4389 | 25.114 | 32.3567 | 41.6104 | 53.4459 | 68.5985 | 88.0149 | 112.9156 | 144.8735 | 185.9174 | 238.6643 | 306.4907 | 374.7309 | 374.3237 | 373.518 | 372.412 | 370.8869 | 368.7755 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 1.5526 | 1.9425 | 2.4372 | 3.066 | 3.8665 | 4.8867 | 6.1888 | 7.8524 | 9.9803 | 12.7044 | 16.1951 | 20.6717 | 26.4171 | 33.796 | 43.2788 | 55.4727 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 |  | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.44494 | 0.58979 | 0.78863 | 1.0628 | 1.4424 | 1.9699 | 2.7054 | 3.7339 | 5.176 | 7.2029 | 10.0579 | 14.087 | 19.7826 |  | 1.1809 | 1.5707 | 2.0655 | 2.6943 | 3.4947 | 4.515 | 5.8171 | 7.4807 | 9.6085 | 12.3327 | 15.8233 | 20.3 | 26.0454 | 33.4243 | 42.9071 | 55.101 | 67.3692 | 67.296 | 67.1511 | 66.9523 | 66.6781 | 66.2985 | 65.771 | 65.0356 | 64.0071 | 62.5649 | 60.538 | 57.683 | 53.6539 | 47.9583 |  | 99.5582 | 132.4226 | 174.1304 | 227.1441 | 294.6266 | 380.6418 | 490.4153 | 630.6693 | 810.056 | 1039.7164 | 1334.0027 | 1711.41 | 2195.7818 | 2817.866 | 3617.3261 | 4645.3407 | 5679.6269 | 5673.4551 | 5661.2431 | 5644.4797 | 5621.3651 | 5589.3625 | 5544.891 | 5482.8866 | 5396.1785 | 5274.5993 | 5103.7166 | 4863.0219 | 4523.3472 | 4043.1731
| TRUE | 3664 | 22009882 | SA | Blank | 22 | BUS NO.2 | BUS PROT | X | GEC | CDG14_984 | CDG14 984 | CDG14 | Electromechanical |  | 0.033587 | 2190 |  | 8.25 | 0.0054067 | 0.00050998 | 0.0048967 | 30.0172 | 142.7954 | 172.8125 | 18.2427 | 2.1683 | 797.288 |  | 11.3866 | 0.012884 | 0.0012153 | 0.011669 | 71.5296 | 340.2754 | 411.805 | 43.4717 | 5.167 | 1899.9043 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.37173 |  | 990.5116 | 2360.348 | 45.6009 | 2314.7471 |  | 0.032223 |  | 8.5202 | 8.7992 | 9.0873 | 9.3849 | 9.6922 | 10.0096 | 10.3374 | 10.6759 | 11.0256 | 11.3866 | 11.7595 | 12.1446 | 12.5423 | 12.953 | 13.3772 | 13.8153 | 14.2677 | 14.7349 | 15.2174 | 15.7158 | 16.2304 | 16.7619 | 17.3108 | 17.8777 | 18.4631 | 19.0678 | 19.6922 | 20.337 | 21.003 | 21.6908 |  | 0.0058881 | 0.0064147 | 0.006991 | 0.0076217 | 0.0083121 | 0.009068 | 0.0098958 | 0.010802 | 0.011796 | 0.012884 | 0.014076 | 0.015383 | 0.016816 | 0.018387 | 0.020109 | 0.021998 | 0.02407 | 0.026342 | 0.028836 | 0.031571 | 0.034573 | 0.037868 | 0.041485 | 0.045455 | 0.049813 | 0.054599 | 0.059854 | 0.065625 | 0.071963 | 0.078925 |  | 0.00055539 | 0.00060507 | 0.00065942 | 0.00071891 | 0.00078404 | 0.00085534 | 0.00093342 | 0.0010189 | 0.0011126 | 0.0012153 | 0.0013278 | 0.001451 | 0.0015862 | 0.0017343 | 0.0018968 | 0.002075 | 0.0022704 | 0.0024847 | 0.0027199 | 0.002978 | 0.0032611 | 0.0035719 | 0.003913 | 0.0042875 | 0.0046986 | 0.00515 | 0.0056457 | 0.00619 | 0.0067879 | 0.0074446 | 1078.7037 | 1175.1858 | 1280.7594 | 1396.3047 | 1522.7885 | 1661.2727 | 1812.9242 | 1979.025 | 2160.9837 | 2360.348 | 2578.8191 | 2818.2663 | 3080.7445 | 3368.5121 | 3684.0519 | 4030.0929 | 4409.6359 | 4825.9795 | 5282.7511 | 5783.9389 | 6333.9286 | 6937.5432 | 7600.0867 | 8327.3924 | 9125.8761 | 10002.5947 | 10965.3103 | 12022.5613 | 13183.7403 | 14459.1802 |  | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 37.5716 | 49.8033 | 66.5938 | 89.7458 | 121.8 | 166.3434 | 228.4481 | 315.2963 | 437.072 | 608.2309 | 849.3146 | 1189.5384 | 1670.4885 |  | 32.6898 | 35.6137 | 38.813 | 42.3146 | 46.1476 | 50.3444 | 54.9401 | 59.9738 | 65.488 | 71.5296 | 78.1503 | 85.4067 | 93.361 | 102.0817 | 111.6441 | 122.1308 | 133.6327 | 146.2499 | 160.0922 | 175.2805 | 191.9478 | 210.2402 | 230.3183 | 252.3591 | 276.5569 | 303.1256 | 332.3004 | 364.3401 | 399.5293 | 438.1811 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 18.4779 | 21.4018 | 24.6011 | 28.1027 | 31.9358 | 36.1325 | 40.7282 | 45.7619 | 51.2761 | 57.3177 | 63.9384 | 71.1948 | 79.1491 | 87.8699 | 97.4322 | 107.9189 | 119.4208 | 129.2391 | 137.5434 | 145.1298 | 151.3149 | 155.0945 | 155.0054 | 148.9279 | 133.8047 | 105.2388 | 56.9204 | -20.192 | -139.0411 | -318.1423 |  | 155.5094 | 169.4186 | 184.6384 | 201.2958 | 219.5301 | 239.4944 | 261.357 | 285.3026 | 311.5344 | 340.2754 | 371.7709 | 406.2904 | 444.1301 | 485.6156 | 531.1048 | 580.9912 | 635.7074 | 695.7288 | 761.5785 | 833.8313 | 913.1196 | 1000.1386 | 1095.653 | 1200.5038 | 1315.6158 | 1442.0064 | 1580.7946 | 1733.2113 | 1900.6106 | 2084.4821 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 155.4428 | 169.352 | 184.5718 | 201.2292 | 219.4635 | 239.4279 | 261.2904 | 285.2361 | 311.4678 | 340.2088 | 371.7043 | 406.2238 | 444.0635 | 485.549 | 531.0382 | 580.9246 | 635.6408 | 695.6491 | 761.4728 | 833.6901 | 912.9293 | 999.8803 | 1095.3002 | 1200.0193 | 1314.947 | 1441.0793 | 1579.5045 | 1731.4099 | 1898.0876 | 2080.939 |  | 173.9207 | 190.7538 | 209.173 | 229.3319 | 251.3993 | 275.5603 | 302.0187 | 330.9979 | 362.7439 | 397.5266 | 435.6428 | 477.4186 | 523.2127 | 573.4189 | 628.4704 | 688.8435 | 755.0616 | 824.8882 | 899.0163 | 978.8199 | 1064.2441 | 1154.9748 | 1250.3056 | 1348.9472 | 1448.7517 | 1546.3181 | 1636.4249 | 1711.2179 | 1759.0465 | 1762.7968 |  | 19.867 | 21.644 | 23.5884 | 25.7164 | 28.046 | 30.5965 | 33.3895 | 36.4487 | 39.7999 | 43.4717 | 47.4954 | 51.9054 | 56.7396 | 62.0396 | 67.851 | 74.2242 | 81.2145 | 88.8825 | 97.2951 | 106.5257 | 116.6551 | 127.7722 | 139.9746 | 153.3697 | 168.0758 | 184.2228 | 201.9536 | 221.4255 | 242.8115 | 266.3019 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 5.1959 | 6.9728 | 8.9172 | 11.0453 | 13.3748 | 15.9253 | 18.7184 | 21.7776 | 25.1288 | 28.8006 | 32.8243 | 37.2343 | 42.0685 | 47.3684 | 53.1799 | 59.5531 | 66.5433 | 71.322 | 74.0177 | 75.4006 | 74.7092 | 70.8445 | 62.2279 | 46.5962 | 20.7106 | -20.0587 | -82.3252 | -175.5325 | -313.1624 | -514.4615 |  | 2.3614 | 2.5726 | 2.8037 | 3.0566 | 3.3335 | 3.6367 | 3.9686 | 4.3322 | 4.7306 | 5.167 | 5.6452 | 6.1694 | 6.744 | 7.3739 | 8.0647 | 8.8222 | 9.653 | 10.5644 | 11.5644 | 12.6615 | 13.8655 | 15.1868 | 16.6372 | 18.2293 | 19.9773 | 21.8965 | 24.0039 | 26.3183 | 28.8602 | 31.6523 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0.29367 | 0.50488 | 0.73599 | 0.98893 | 1.2658 | 1.569 | 1.9009 | 2.2645 | 2.6629 | 3.0993 | 3.5775 | 4.1017 | 4.6763 | 5.3062 | 5.997 | 6.7545 | 7.5853 | 8.0895 | 8.2837 | 8.2749 | 7.9538 | 7.1637 | 5.6799 | 3.1811 | -0.79183 | -6.8942 | -16.0612 | -29.6274 | -49.4966 | -78.3855 |  | 868.2761 | 945.937 | 1030.9159 | 1123.9213 | 1225.7313 | 1337.2007 | 1459.2689 | 1592.9677 | 1739.4308 | 1899.9043 | 2075.7572 | 2268.4944 | 2479.7698 | 2711.4013 | 2965.3873 | 3243.9246 | 3549.4283 | 3884.554 | 4252.221 | 4655.6398 | 5098.3406 | 5584.2054 | 6117.5035 | 6702.9304 | 7345.6503 | 8051.3435 | 8826.2578 | 9677.2661 | 10611.9287 | 11638.5628 |  | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.44494 | 0.58979 | 0.78863 | 1.0628 | 1.4424 | 1.9699 | 2.7054 | 3.7339 | 5.176 | 7.2029 | 10.0579 | 14.087 | 19.7826 |  | 867.9043 | 945.5653 | 1030.5442 | 1123.5495 | 1225.3595 | 1336.829 | 1458.8972 | 1592.596 | 1739.0591 | 1899.5326 | 2075.3855 | 2268.1227 | 2479.3981 | 2711.0296 | 2965.0155 | 3243.5528 | 3549.0566 | 3884.109 | 4251.6312 | 4654.8512 | 5097.2778 | 5582.763 | 6115.5336 | 6700.225 | 7341.9165 | 8046.1675 | 8819.0549 | 9667.2082 | 10597.8417 | 11618.7801 |  | 1047.3146 | 1143.7968 | 1249.3704 | 1364.9157 | 1491.3994 | 1629.8837 | 1781.5352 | 1947.636 | 2129.5946 | 2328.959 | 2547.4301 | 2786.8773 | 3049.3555 | 3337.1231 | 3652.6628 | 3998.7039 | 4378.2468 | 4788.4088 | 5232.9489 | 5717.3466 | 6244.1848 | 6815.746 | 7433.7471 | 8098.9495 | 8810.587 | 9565.5327 | 10357.0933 | 11173.2662 | 11994.2292 | 12788.7299
| TRUE | 3665 | 22009883 | SA | Blank | 22 | BUS NO.2 | BUS PROT | X | GEC | CDG14_984 | CDG14 984 | CDG14 | Electromechanical |  | 0.033587 | 2190 |  | 8.25 | 0.0054067 | 0.00050998 | 0.0048967 | 30.0172 | 142.7954 | 172.8125 | 18.2427 | 2.1683 | 797.288 |  | 11.9015 | 0.014549 | 0.0013724 | 0.013177 | 80.7762 | 384.2624 | 465.0386 | 49.0912 | 5.8349 | 2145.5028 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.37173 |  | 990.5116 | 2665.4676 | 45.6009 | 2619.8667 |  | 0.036645 |  | 8.5579 | 8.8774 | 9.2087 | 9.5524 | 9.909 | 10.2788 | 10.6625 | 11.0604 | 11.4733 | 11.9015 | 12.3457 | 12.8065 | 13.2845 | 13.7804 | 14.2947 | 14.8283 | 15.3818 | 15.9559 | 16.5514 | 17.1692 | 17.8101 | 18.4748 | 19.1644 | 19.8797 | 20.6217 | 21.3914 | 22.1898 | 23.0181 | 23.8772 | 24.7684 |  | 0.0059576 | 0.0065678 | 0.0072438 | 0.007993 | 0.0088234 | 0.0097442 | 0.010765 | 0.011898 | 0.013155 | 0.014549 | 0.016097 | 0.017816 | 0.019724 | 0.021844 | 0.024198 | 0.026813 | 0.02972 | 0.032949 | 0.03654 | 0.040531 | 0.044968 | 0.049903 | 0.055391 | 0.061495 | 0.068286 | 0.075841 | 0.084248 | 0.093603 | 0.10402 | 0.1156 |  | 0.00056195 | 0.0006195 | 0.00068327 | 0.00075394 | 0.00083227 | 0.00091912 | 0.0010154 | 0.0011223 | 0.0012408 | 0.0013724 | 0.0015184 | 0.0016805 | 0.0018605 | 0.0020604 | 0.0022825 | 0.0025292 | 0.0028033 | 0.003108 | 0.0034466 | 0.0038231 | 0.0042416 | 0.0047071 | 0.0052247 | 0.0058005 | 0.0064411 | 0.0071537 | 0.0079467 | 0.0088291 | 0.0098113 | 0.010904 | 1091.4383 | 1203.2258 | 1327.0762 | 1464.327 | 1616.4664 | 1785.1504 | 1972.2221 | 2179.7333 | 2409.9676 | 2665.4676 | 2949.064 | 3263.9087 | 3613.5119 | 4001.7825 | 4433.0741 | 4912.2362 | 5444.6705 | 6036.3946 | 6694.1127 | 7425.2944 | 8238.2623 | 9142.2905 | 10147.7138 | 11266.0496 | 12510.1337 | 13894.2729 | 15434.4131 | 17148.3294 | 19055.8355 | 21179.0198 |  | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 37.5716 | 49.8033 | 66.5938 | 89.7458 | 121.8 | 166.3434 | 228.4481 | 315.2963 | 437.072 | 608.2309 | 849.3146 | 1189.5384 | 1670.4885 |  | 33.0757 | 36.4634 | 40.2166 | 44.376 | 48.9865 | 54.0984 | 59.7676 | 66.0562 | 73.0333 | 80.7762 | 89.3705 | 98.9118 | 109.5064 | 121.2728 | 134.343 | 148.8638 | 164.9991 | 182.9311 | 202.8631 | 225.0213 | 249.6581 | 277.0544 | 307.5234 | 341.4142 | 379.1158 | 421.0618 | 467.7353 | 519.675 | 577.4814 | 641.8238 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 18.8638 | 22.2515 | 26.0048 | 30.1641 | 34.7746 | 39.8866 | 45.5557 | 51.8443 | 58.8215 | 66.5643 | 75.1586 | 84.6999 | 95.2945 | 107.0609 | 120.1311 | 134.652 | 150.7872 | 165.9204 | 180.3143 | 194.8706 | 209.0251 | 221.9087 | 232.2105 | 237.9831 | 236.3636 | 223.1749 | 192.3552 | 135.1429 | 38.911 | -114.4995 |  | 157.3453 | 173.4609 | 191.3156 | 211.1021 | 233.035 | 257.353 | 284.3219 | 314.2374 | 347.4287 | 384.2624 | 425.1466 | 470.5356 | 520.9356 | 576.9099 | 639.0863 | 708.1638 | 784.9213 | 870.2262 | 965.0449 | 1070.4544 | 1187.6545 | 1317.9821 | 1462.9272 | 1624.1501 | 1803.5013 | 2003.0433 | 2225.0749 | 2472.1586 | 2747.1508 | 3053.2359 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 157.2787 | 173.3943 | 191.249 | 211.0355 | 232.9684 | 257.2865 | 284.2553 | 314.1708 | 347.3621 | 384.1958 | 425.08 | 470.469 | 520.869 | 576.8433 | 639.0197 | 708.0973 | 784.8547 | 870.1465 | 964.9393 | 1070.3132 | 1187.4642 | 1317.7238 | 1462.5744 | 1623.6656 | 1802.8326 | 2002.1162 | 2223.7848 | 2470.3572 | 2744.6278 | 3049.6928 |  | 176.1425 | 195.6458 | 217.2538 | 241.1996 | 267.7431 | 297.173 | 329.8111 | 366.0151 | 406.1836 | 450.7602 | 500.2386 | 555.1689 | 616.1635 | 683.9042 | 759.1508 | 842.7492 | 935.6419 | 1036.0668 | 1145.2536 | 1265.1838 | 1396.4893 | 1539.6325 | 1694.7849 | 1861.6486 | 2039.1962 | 2225.2911 | 2416.14 | 2605.5 | 2783.5388 | 2935.1933 |  | 20.1016 | 22.1604 | 24.4414 | 26.9692 | 29.7713 | 32.878 | 36.3234 | 40.1452 | 44.3856 | 49.0912 | 54.3144 | 60.113 | 66.5518 | 73.7028 | 81.6461 | 90.4711 | 100.2772 | 111.1753 | 123.2888 | 136.7553 | 151.7282 | 168.3781 | 186.8955 | 207.4924 | 230.4053 | 255.8977 | 284.2633 | 315.8293 | 350.9608 | 390.0645 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 5.4304 | 7.4893 | 9.7703 | 12.2981 | 15.1001 | 18.2069 | 21.6523 | 25.4741 | 29.7144 | 34.4201 | 39.6432 | 45.4419 | 51.8807 | 59.0317 | 66.975 | 75.8 | 85.6061 | 93.6148 | 100.0114 | 105.6303 | 109.7822 | 111.4505 | 109.1489 | 100.7189 | 83.0402 | 51.6163 | -0.015525 | -81.1287 | -205.0131 | -390.6989 |  | 2.3892 | 2.634 | 2.9051 | 3.2055 | 3.5386 | 3.9078 | 4.3173 | 4.7716 | 5.2756 | 5.8349 | 6.4557 | 7.145 | 7.9103 | 8.7602 | 9.7043 | 10.7533 | 11.9188 | 13.2141 | 14.6539 | 16.2545 | 18.0342 | 20.0132 | 22.2141 | 24.6623 | 27.3857 | 30.4156 | 33.7871 | 37.539 | 41.7147 | 46.3625 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0.32155 | 0.56626 | 0.83738 | 1.1378 | 1.4709 | 1.8401 | 2.2497 | 2.7039 | 3.2079 | 3.7672 | 4.388 | 5.0773 | 5.8426 | 6.6925 | 7.6367 | 8.6856 | 9.8511 | 10.7392 | 11.3733 | 11.8679 | 12.1225 | 11.99 | 11.2568 | 9.614 | 6.6166 | 1.625 | -6.278 | -18.4067 | -36.6421 | -63.6753 |  | 878.5265 | 968.5071 | 1068.1975 | 1178.6742 | 1301.135 | 1436.913 | 1587.4919 | 1754.5229 | 1939.8444 | 2145.5028 | 2373.7768 | 2627.2033 | 2908.6078 | 3221.1367 | 3568.2944 | 3953.9842 | 4382.5541 | 4858.8479 | 5388.262 | 5976.8087 | 6631.1873 | 7358.8627 | 8168.1536 | 9068.3305 | 10069.7256 | 11183.8544 | 12423.5526 | 13803.1275 | 15338.5278 | 17047.533 |  | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.44494 | 0.58979 | 0.78863 | 1.0628 | 1.4424 | 1.9699 | 2.7054 | 3.7339 | 5.176 | 7.2029 | 10.0579 | 14.087 | 19.7826 |  | 878.1547 | 968.1354 | 1067.8258 | 1178.3024 | 1300.7633 | 1436.5413 | 1587.1202 | 1754.1512 | 1939.4727 | 2145.1311 | 2373.405 | 2626.8316 | 2908.2361 | 3220.765 | 3567.9227 | 3953.6124 | 4382.1824 | 4858.403 | 5387.6722 | 5976.0201 | 6630.1245 | 7357.4203 | 8166.1837 | 9065.6251 | 10065.9917 | 11178.6785 | 12416.3497 | 13793.0695 | 15324.4408 | 17027.7504 |  | 1060.0492 | 1171.8368 | 1295.6872 | 1432.938 | 1585.0774 | 1753.7613 | 1940.8331 | 2148.3443 | 2378.5786 | 2634.0786 | 2917.6749 | 3232.5197 | 3582.1229 | 3970.3935 | 4401.6851 | 4880.8472 | 5413.2815 | 5998.8239 | 6644.3105 | 7358.7021 | 8148.5185 | 9020.4933 | 9981.3742 | 11037.6067 | 12194.8446 | 13457.2109 | 14826.1961 | 16299.0342 | 17866.3244 | 19508.5695
| TRUE | 3666 | 22009884 | SA | Blank | 22 | BUS NO.2 | BUS PROT | X | GEC | CDG14_984 | CDG14 984 | CDG14 | Electromechanical |  | 0.033587 | 2190 |  | 8.25 | 0.0054067 | 0.00050998 | 0.0048967 | 30.0172 | 142.7954 | 172.8125 | 18.2427 | 2.1683 | 797.288 |  | 11.9015 | 0.014549 | 0.0013724 | 0.013177 | 80.7762 | 384.2624 | 465.0386 | 49.0912 | 5.8349 | 2145.5028 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.37173 |  | 990.5116 | 2665.4676 | 45.6009 | 2619.8667 |  | 0.036645 |  | 8.5579 | 8.8774 | 9.2087 | 9.5524 | 9.909 | 10.2788 | 10.6625 | 11.0604 | 11.4733 | 11.9015 | 12.3457 | 12.8065 | 13.2845 | 13.7804 | 14.2947 | 14.8283 | 15.3818 | 15.9559 | 16.5514 | 17.1692 | 17.8101 | 18.4748 | 19.1644 | 19.8797 | 20.6217 | 21.3914 | 22.1898 | 23.0181 | 23.8772 | 24.7684 |  | 0.0059576 | 0.0065678 | 0.0072438 | 0.007993 | 0.0088234 | 0.0097442 | 0.010765 | 0.011898 | 0.013155 | 0.014549 | 0.016097 | 0.017816 | 0.019724 | 0.021844 | 0.024198 | 0.026813 | 0.02972 | 0.032949 | 0.03654 | 0.040531 | 0.044968 | 0.049903 | 0.055391 | 0.061495 | 0.068286 | 0.075841 | 0.084248 | 0.093603 | 0.10402 | 0.1156 |  | 0.00056195 | 0.0006195 | 0.00068327 | 0.00075394 | 0.00083227 | 0.00091912 | 0.0010154 | 0.0011223 | 0.0012408 | 0.0013724 | 0.0015184 | 0.0016805 | 0.0018605 | 0.0020604 | 0.0022825 | 0.0025292 | 0.0028033 | 0.003108 | 0.0034466 | 0.0038231 | 0.0042416 | 0.0047071 | 0.0052247 | 0.0058005 | 0.0064411 | 0.0071537 | 0.0079467 | 0.0088291 | 0.0098113 | 0.010904 | 1091.4383 | 1203.2258 | 1327.0762 | 1464.327 | 1616.4664 | 1785.1504 | 1972.2221 | 2179.7333 | 2409.9676 | 2665.4676 | 2949.064 | 3263.9087 | 3613.5119 | 4001.7825 | 4433.0741 | 4912.2362 | 5444.6705 | 6036.3946 | 6694.1127 | 7425.2944 | 8238.2623 | 9142.2905 | 10147.7138 | 11266.0496 | 12510.1337 | 13894.2729 | 15434.4131 | 17148.3294 | 19055.8355 | 21179.0198 |  | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 37.5716 | 49.8033 | 66.5938 | 89.7458 | 121.8 | 166.3434 | 228.4481 | 315.2963 | 437.072 | 608.2309 | 849.3146 | 1189.5384 | 1670.4885 |  | 33.0757 | 36.4634 | 40.2166 | 44.376 | 48.9865 | 54.0984 | 59.7676 | 66.0562 | 73.0333 | 80.7762 | 89.3705 | 98.9118 | 109.5064 | 121.2728 | 134.343 | 148.8638 | 164.9991 | 182.9311 | 202.8631 | 225.0213 | 249.6581 | 277.0544 | 307.5234 | 341.4142 | 379.1158 | 421.0618 | 467.7353 | 519.675 | 577.4814 | 641.8238 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 18.8638 | 22.2515 | 26.0048 | 30.1641 | 34.7746 | 39.8866 | 45.5557 | 51.8443 | 58.8215 | 66.5643 | 75.1586 | 84.6999 | 95.2945 | 107.0609 | 120.1311 | 134.652 | 150.7872 | 165.9204 | 180.3143 | 194.8706 | 209.0251 | 221.9087 | 232.2105 | 237.9831 | 236.3636 | 223.1749 | 192.3552 | 135.1429 | 38.911 | -114.4995 |  | 157.3453 | 173.4609 | 191.3156 | 211.1021 | 233.035 | 257.353 | 284.3219 | 314.2374 | 347.4287 | 384.2624 | 425.1466 | 470.5356 | 520.9356 | 576.9099 | 639.0863 | 708.1638 | 784.9213 | 870.2262 | 965.0449 | 1070.4544 | 1187.6545 | 1317.9821 | 1462.9272 | 1624.1501 | 1803.5013 | 2003.0433 | 2225.0749 | 2472.1586 | 2747.1508 | 3053.2359 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 157.2787 | 173.3943 | 191.249 | 211.0355 | 232.9684 | 257.2865 | 284.2553 | 314.1708 | 347.3621 | 384.1958 | 425.08 | 470.469 | 520.869 | 576.8433 | 639.0197 | 708.0973 | 784.8547 | 870.1465 | 964.9393 | 1070.3132 | 1187.4642 | 1317.7238 | 1462.5744 | 1623.6656 | 1802.8326 | 2002.1162 | 2223.7848 | 2470.3572 | 2744.6278 | 3049.6928 |  | 176.1425 | 195.6458 | 217.2538 | 241.1996 | 267.7431 | 297.173 | 329.8111 | 366.0151 | 406.1836 | 450.7602 | 500.2386 | 555.1689 | 616.1635 | 683.9042 | 759.1508 | 842.7492 | 935.6419 | 1036.0668 | 1145.2536 | 1265.1838 | 1396.4893 | 1539.6325 | 1694.7849 | 1861.6486 | 2039.1962 | 2225.2911 | 2416.14 | 2605.5 | 2783.5388 | 2935.1933 |  | 20.1016 | 22.1604 | 24.4414 | 26.9692 | 29.7713 | 32.878 | 36.3234 | 40.1452 | 44.3856 | 49.0912 | 54.3144 | 60.113 | 66.5518 | 73.7028 | 81.6461 | 90.4711 | 100.2772 | 111.1753 | 123.2888 | 136.7553 | 151.7282 | 168.3781 | 186.8955 | 207.4924 | 230.4053 | 255.8977 | 284.2633 | 315.8293 | 350.9608 | 390.0645 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 5.4304 | 7.4893 | 9.7703 | 12.2981 | 15.1001 | 18.2069 | 21.6523 | 25.4741 | 29.7144 | 34.4201 | 39.6432 | 45.4419 | 51.8807 | 59.0317 | 66.975 | 75.8 | 85.6061 | 93.6148 | 100.0114 | 105.6303 | 109.7822 | 111.4505 | 109.1489 | 100.7189 | 83.0402 | 51.6163 | -0.015525 | -81.1287 | -205.0131 | -390.6989 |  | 2.3892 | 2.634 | 2.9051 | 3.2055 | 3.5386 | 3.9078 | 4.3173 | 4.7716 | 5.2756 | 5.8349 | 6.4557 | 7.145 | 7.9103 | 8.7602 | 9.7043 | 10.7533 | 11.9188 | 13.2141 | 14.6539 | 16.2545 | 18.0342 | 20.0132 | 22.2141 | 24.6623 | 27.3857 | 30.4156 | 33.7871 | 37.539 | 41.7147 | 46.3625 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0.32155 | 0.56626 | 0.83738 | 1.1378 | 1.4709 | 1.8401 | 2.2497 | 2.7039 | 3.2079 | 3.7672 | 4.388 | 5.0773 | 5.8426 | 6.6925 | 7.6367 | 8.6856 | 9.8511 | 10.7392 | 11.3733 | 11.8679 | 12.1225 | 11.99 | 11.2568 | 9.614 | 6.6166 | 1.625 | -6.278 | -18.4067 | -36.6421 | -63.6753 |  | 878.5265 | 968.5071 | 1068.1975 | 1178.6742 | 1301.135 | 1436.913 | 1587.4919 | 1754.5229 | 1939.8444 | 2145.5028 | 2373.7768 | 2627.2033 | 2908.6078 | 3221.1367 | 3568.2944 | 3953.9842 | 4382.5541 | 4858.8479 | 5388.262 | 5976.8087 | 6631.1873 | 7358.8627 | 8168.1536 | 9068.3305 | 10069.7256 | 11183.8544 | 12423.5526 | 13803.1275 | 15338.5278 | 17047.533 |  | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.44494 | 0.58979 | 0.78863 | 1.0628 | 1.4424 | 1.9699 | 2.7054 | 3.7339 | 5.176 | 7.2029 | 10.0579 | 14.087 | 19.7826 |  | 878.1547 | 968.1354 | 1067.8258 | 1178.3024 | 1300.7633 | 1436.5413 | 1587.1202 | 1754.1512 | 1939.4727 | 2145.1311 | 2373.405 | 2626.8316 | 2908.2361 | 3220.765 | 3567.9227 | 3953.6124 | 4382.1824 | 4858.403 | 5387.6722 | 5976.0201 | 6630.1245 | 7357.4203 | 8166.1837 | 9065.6251 | 10065.9917 | 11178.6785 | 12416.3497 | 13793.0695 | 15324.4408 | 17027.7504 |  | 1060.0492 | 1171.8368 | 1295.6872 | 1432.938 | 1585.0774 | 1753.7613 | 1940.8331 | 2148.3443 | 2378.5786 | 2634.0786 | 2917.6749 | 3232.5197 | 3582.1229 | 3970.3935 | 4401.6851 | 4880.8472 | 5413.2815 | 5998.8239 | 6644.3105 | 7358.7021 | 8148.5185 | 9020.4933 | 9981.3742 | 11037.6067 | 12194.8446 | 13457.2109 | 14826.1961 | 16299.0342 | 17866.3244 | 19508.5695
| TRUE | 3667 | 22005006 | SA | Blank | 22 | BUS NO.2 | DISTANCE | X | Schweitzer | SEL_311A | SEL 311A | SEL 300s | Digital |  | 0.033587 | 1 |  | 6.6 | 0.017308 | 7.9633e-07 | 0.017307 | 47.5968 | 0.055743 | 47.6526 | 49.1349 | 6.9249 | 1.245 |  | 15.598 | 0.17662 | 8.1263e-06 | 0.17661 | 485.7104 | 0.56884 | 486.2792 | 501.4057 | 70.6662 | 12.7044 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.37173 |  | 104.9573 | 1071.0555 | 31.3391 | 1039.7164 |  | 0.086007 |  | 7.1928 | 7.8388 | 8.5428 | 9.3101 | 10.1463 | 11.0575 | 12.0507 | 13.133 | 14.3125 | 15.598 | 16.9989 | 18.5257 | 20.1895 | 22.0028 | 23.979 | 26.1326 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021585 | 0.027005 | 0.033883 | 0.042625 | 0.053753 | 0.067937 | 0.086039 | 0.10917 | 0.13875 | 0.17662 | 0.22515 | 0.28739 | 0.36726 | 0.46984 | 0.60168 | 0.7712 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 9.9315e-07 | 1.2425e-06 | 1.5589e-06 | 1.9612e-06 | 2.4732e-06 | 3.1258e-06 | 3.9587e-06 | 5.0228e-06 | 6.3838e-06 | 8.1263e-06 | 1.0359e-05 | 1.3223e-05 | 1.6898e-05 | 2.1618e-05 | 2.7683e-05 | 3.5483e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 130.8973 | 163.7617 | 205.4695 | 258.4832 | 325.9657 | 411.9809 | 521.7544 | 662.0084 | 841.3951 | 1071.0555 | 1365.3418 | 1742.7491 | 2227.1209 | 2849.2051 | 3648.6652 | 4676.6798 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 |  | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 37.5109 | 49.723 | 66.4863 | 89.601 | 121.6035 | 166.075 | 228.0794 | 314.7875 | 436.3667 | 607.2495 | 847.9441 | 1187.6189 | 1667.7929 |  | 59.3603 | 74.2639 | 93.1778 | 117.2189 | 147.8214 | 186.8282 | 236.6091 | 300.2126 | 381.5622 | 485.7104 | 619.1655 | 790.3151 | 1009.9717 | 1292.0791 | 1654.6243 | 2120.8162 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 45.1484 | 60.052 | 78.966 | 103.007 | 133.6095 | 172.6163 | 222.3972 | 286.0007 | 367.3503 | 471.4985 | 604.9536 | 776.1032 | 995.7598 | 1277.8672 | 1640.4124 | 2106.6043 | 2575.6402 | 2572.8414 | 2567.3034 | 2559.7014 | 2549.2192 | 2534.7064 | 2514.5392 | 2486.4209 | 2447.0999 | 2391.9652 | 2314.472 | 2205.32 | 2051.2817 | 1833.5287 |  | 0.06952 | 0.086975 | 0.10913 | 0.13728 | 0.17312 | 0.21881 | 0.27711 | 0.3516 | 0.44687 | 0.56884 | 0.72514 | 0.92558 | 1.1828 | 1.5132 | 1.9378 | 2.4838 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019922 | 0.026408 | 0.035311 | 0.047588 | 0.064584 | 0.088203 | 0.12113 | 0.16719 | 0.23176 | 0.32251 | 0.45035 | 0.63075 | 0.88577 |  | 0.052876 | 0.07033 | 0.092482 | 0.12064 | 0.15648 | 0.20216 | 0.26046 | 0.33495 | 0.43022 | 0.5522 | 0.7085 | 0.90894 | 1.1662 | 1.4966 | 1.9212 | 2.4672 | 3.0165 | 3.0132 | 3.0067 | 2.9978 | 2.9855 | 2.9685 | 2.9449 | 2.912 | 2.8659 | 2.8014 | 2.7106 | 2.5828 | 2.4024 | 2.1473 |  | 45.2013 | 60.1223 | 79.0584 | 103.1277 | 133.766 | 172.8185 | 222.6577 | 286.3356 | 367.7805 | 472.0507 | 605.6621 | 777.0121 | 996.926 | 1279.3638 | 1642.3336 | 2109.0714 | 2578.6567 | 2575.8546 | 2570.3101 | 2562.6992 | 2552.2047 | 2537.675 | 2517.4841 | 2489.3329 | 2449.9658 | 2394.7666 | 2317.1826 | 2207.9028 | 2053.6841 | 1835.6761 |  | 61.2785 | 76.6637 | 96.1888 | 121.0068 | 152.5981 | 192.8654 | 244.255 | 309.9137 | 393.8921 | 501.4057 | 639.1734 | 815.8535 | 1042.6081 | 1333.8317 | 1708.0922 | 2189.3487 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 46.6074 | 61.9926 | 81.5177 | 106.3356 | 137.927 | 178.1943 | 229.5838 | 295.2426 | 379.221 | 486.7346 | 624.5022 | 801.1824 | 1027.937 | 1319.1605 | 1693.4211 | 2174.6776 | 2658.8701 | 2655.9808 | 2650.2638 | 2642.4162 | 2631.5953 | 2616.6136 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 8.6364 | 10.8047 | 13.5565 | 17.0542 | 21.5066 | 27.1817 | 34.4244 | 43.678 | 55.5136 | 70.6662 | 90.0826 | 114.9833 | 146.9412 | 187.9851 | 240.732 | 308.5584 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 6.5687 | 8.737 | 11.4888 | 14.9865 | 19.4389 | 25.114 | 32.3567 | 41.6104 | 53.4459 | 68.5985 | 88.0149 | 112.9156 | 144.8735 | 185.9174 | 238.6643 | 306.4907 | 374.7309 | 374.3237 | 373.518 | 372.412 | 370.8869 | 368.7755 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 1.5526 | 1.9425 | 2.4372 | 3.066 | 3.8665 | 4.8867 | 6.1888 | 7.8524 | 9.9803 | 12.7044 | 16.1951 | 20.6717 | 26.4171 | 33.796 | 43.2788 | 55.4727 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 |  | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.44494 | 0.58979 | 0.78863 | 1.0628 | 1.4424 | 1.9699 | 2.7054 | 3.7339 | 5.176 | 7.2029 | 10.0579 | 14.087 | 19.7826 |  | 1.1809 | 1.5707 | 2.0655 | 2.6943 | 3.4947 | 4.515 | 5.8171 | 7.4807 | 9.6085 | 12.3327 | 15.8233 | 20.3 | 26.0454 | 33.4243 | 42.9071 | 55.101 | 67.3692 | 67.296 | 67.1511 | 66.9523 | 66.6781 | 66.2985 | 65.771 | 65.0356 | 64.0071 | 62.5649 | 60.538 | 57.683 | 53.6539 | 47.9583 |  | 99.5582 | 132.4226 | 174.1304 | 227.1441 | 294.6266 | 380.6418 | 490.4153 | 630.6693 | 810.056 | 1039.7164 | 1334.0027 | 1711.41 | 2195.7818 | 2817.866 | 3617.3261 | 4645.3407 | 5679.6269 | 5673.4551 | 5661.2431 | 5644.4797 | 5621.3651 | 5589.3625 | 5544.891 | 5482.8866 | 5396.1785 | 5274.5993 | 5103.7166 | 4863.0219 | 4523.3472 | 4043.1731
| TRUE | 3668 | 22009885 | SA | Blank | 22 | BUS NO.3 | BUS PROT | X | GEC | CDG14_2250 | CDG14 2250 | CDG14 | Electromechanical |  | 0.033587 | 2190 |  | 5.7576 | 0.0021484 | 0.00020265 | 0.0019457 | 7.4548 | 21.278 | 28.7327 | 7.2489 | 0.8616 | 316.8108 |  | 9.2969 | 0.0074313 | 0.00070096 | 0.0067304 | 25.7861 | 73.6006 | 99.3867 | 25.0742 | 2.9803 | 1095.8506 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 17.7649 | 0.024967 | 17.7898 | 14.6711 | 2.0677 | 0.37173 |  | 353.6541 | 1223.2918 | 34.9004 | 1188.3914 |  | 0.047915 |  | 6.0402 | 6.3367 | 6.6477 | 6.974 | 7.3163 | 7.6754 | 8.0521 | 8.4473 | 8.8619 | 9.2969 | 9.7532 | 10.2319 | 10.7341 | 11.261 | 11.8137 | 12.3935 | 13.0018 | 13.6399 | 14.3094 | 15.0118 | 15.7486 | 16.5215 | 17.3324 | 18.1831 | 19.0756 | 20.0118 | 20.9941 | 22.0245 | 23.1055 | 24.2395 |  | 0.0024211 | 0.0027315 | 0.0030852 | 0.0034882 | 0.0039479 | 0.0044725 | 0.0050714 | 0.0057556 | 0.0065374 | 0.0074313 | 0.0084539 | 0.009624 | 0.010964 | 0.012498 | 0.014256 | 0.01627 | 0.01858 | 0.021229 | 0.024267 | 0.027754 | 0.031757 | 0.036353 | 0.041632 | 0.047695 | 0.054663 | 0.06267 | 0.071875 | 0.082459 | 0.094629 | 0.10863 |  | 0.00022837 | 0.00025765 | 0.00029101 | 0.00032903 | 0.00037239 | 0.00042187 | 0.00047836 | 0.00054289 | 0.00061664 | 0.00070096 | 0.00079741 | 0.00090778 | 0.0010341 | 0.0011789 | 0.0013447 | 0.0015347 | 0.0017525 | 0.0020024 | 0.002289 | 0.0026179 | 0.0029955 | 0.003429 | 0.0039269 | 0.0044989 | 0.005156 | 0.0059114 | 0.0067796 | 0.0077779 | 0.0089259 | 0.010246 | 398.5423 | 449.6446 | 507.8576 | 574.2102 | 649.8838 | 736.2354 | 834.8234 | 947.4389 | 1076.1398 | 1223.2918 | 1391.6148 | 1584.2364 | 1804.7539 | 2057.305 | 2346.6507 | 2678.2693 | 3058.4656 | 3494.497 | 3994.718 | 4568.7481 | 5227.6639 | 5984.2221 | 6853.1156 | 7851.2694 | 8998.1817 | 10316.3178 | 11831.5634 | 13573.7485 | 15577.2518 | 17881.697 |  | 31.3476 | 31.3476 | 31.3476 | 31.3476 | 31.3476 | 31.3476 | 31.3476 | 31.3476 | 31.3476 | 31.3476 | 31.3476 | 31.3476 | 31.3476 | 31.3476 | 31.3476 | 31.3476 | 31.3476 | 37.5211 | 49.7365 | 66.5044 | 89.6253 | 121.6365 | 166.12 | 228.1413 | 314.8729 | 436.4851 | 607.4142 | 848.1741 | 1187.9411 | 1668.2454 |  | 8.401 | 9.4782 | 10.7053 | 12.1039 | 13.6991 | 15.5193 | 17.5975 | 19.9713 | 22.6842 | 25.7861 | 29.3342 | 33.3946 | 38.0429 | 43.3665 | 49.4657 | 56.456 | 64.4702 | 73.6615 | 84.2058 | 96.3059 | 110.1954 | 126.143 | 144.4587 | 165.499 | 189.6751 | 217.4605 | 249.4008 | 286.1247 | 328.3571 | 376.9332 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | -5.8109 | -4.7337 | -3.5066 | -2.108 | -0.51281 | 1.3074 | 3.3856 | 5.7594 | 8.4724 | 11.5742 | 15.1223 | 19.1827 | 23.831 | 29.1546 | 35.2538 | 42.2441 | 50.2583 | 56.6507 | 61.657 | 66.1552 | 69.5624 | 70.9974 | 69.1457 | 62.0679 | 46.9229 | 19.5736 | -25.9793 | -98.4074 | -210.2133 | -379.3902 |  | 23.9787 | 27.0533 | 30.5558 | 34.548 | 39.1009 | 44.2964 | 50.228 | 57.0036 | 64.7471 | 73.6006 | 83.7279 | 95.3172 | 108.5849 | 123.7799 | 141.1887 | 161.1408 | 184.0158 | 210.25 | 240.3463 | 274.8835 | 314.5278 | 360.0469 | 412.3248 | 472.3798 | 541.3849 | 620.6919 | 711.8583 | 816.6786 | 937.2215 | 1075.8708 |  | 0.024967 | 0.024967 | 0.024967 | 0.024967 | 0.024967 | 0.024967 | 0.024967 | 0.024967 | 0.024967 | 0.024967 | 0.024967 | 0.024967 | 0.024967 | 0.024967 | 0.024967 | 0.024967 | 0.024967 | 0.029883 | 0.039612 | 0.052967 | 0.071381 | 0.096876 | 0.1323 | 0.1817 | 0.25078 | 0.34763 | 0.48377 | 0.67552 | 0.94613 | 1.3287 |  | 23.9537 | 27.0284 | 30.5308 | 34.523 | 39.076 | 44.2714 | 50.2031 | 56.9787 | 64.7221 | 73.5756 | 83.703 | 95.2923 | 108.5599 | 123.7549 | 141.1637 | 161.1159 | 183.9908 | 210.2201 | 240.3067 | 274.8305 | 314.4564 | 359.95 | 412.1925 | 472.198 | 541.1341 | 620.3443 | 711.3745 | 816.0031 | 936.2754 | 1074.5422 |  | 18.1428 | 22.2947 | 27.0242 | 32.415 | 38.5632 | 45.5788 | 53.5886 | 62.7381 | 73.1945 | 85.1499 | 98.8253 | 114.4749 | 132.3909 | 152.9095 | 176.4175 | 203.36 | 234.2491 | 266.8709 | 301.9637 | 340.9857 | 384.0189 | 430.9474 | 481.3382 | 534.2659 | 588.057 | 639.9179 | 685.3952 | 717.5958 | 726.0621 | 695.152 |  | 8.169 | 9.2165 | 10.4097 | 11.7697 | 13.3209 | 15.0908 | 17.1116 | 19.4199 | 22.0579 | 25.0742 | 28.5243 | 32.4725 | 36.9925 | 42.1692 | 48.1 | 54.8972 | 62.6902 | 71.6277 | 81.8809 | 93.6469 | 107.1529 | 122.6603 | 140.4702 | 160.9297 | 184.4382 | 211.4565 | 242.5149 | 278.2249 | 319.2913 | 366.5261 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | -6.5021 | -5.4546 | -4.2614 | -2.9014 | -1.3503 | 0.41969 | 2.4405 | 4.7488 | 7.3868 | 10.403 | 13.8532 | 17.8014 | 22.3214 | 27.498 | 33.4288 | 40.2261 | 48.0191 | 54.0673 | 58.6035 | 62.5219 | 65.2069 | 65.7326 | 62.7236 | 54.1562 | 37.0731 | 7.175 | -41.7639 | -118.7331 | -236.6826 | -414.2372 |  | 0.97096 | 1.0955 | 1.2373 | 1.3989 | 1.5833 | 1.7937 | 2.0339 | 2.3082 | 2.6218 | 2.9803 | 3.3904 | 3.8596 | 4.3969 | 5.0122 | 5.7171 | 6.525 | 7.4513 | 8.5136 | 9.7322 | 11.1307 | 12.736 | 14.5792 | 16.6961 | 19.1279 | 21.9221 | 25.1334 | 28.825 | 33.0694 | 37.9505 | 43.5648 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | -1.0967 | -0.97223 | -0.83041 | -0.66876 | -0.4844 | -0.27402 | -0.033832 | 0.24053 | 0.55408 | 0.91259 | 1.3227 | 1.7919 | 2.3292 | 2.9445 | 3.6494 | 4.4573 | 5.3836 | 6.0387 | 6.4516 | 6.7441 | 6.8243 | 6.5561 | 5.7388 | 4.0796 | 1.153 | -3.6572 | -11.2402 | -22.8763 | -40.4063 | -66.473 |  | 357.0226 | 402.8012 | 454.9496 | 514.3896 | 582.1797 | 659.5352 | 747.8525 | 848.7358 | 964.0287 | 1095.8506 | 1246.6379 | 1419.1925 | 1616.7366 | 1842.9773 | 2102.1793 | 2399.2503 | 2739.8382 | 3130.4443 | 3578.5528 | 4092.7811 | 4683.0518 | 5360.7926 | 6139.1658 | 7033.333 | 8060.7614 | 9241.5755 | 10598.9645 | 12159.6508 | 13954.4314 | 16018.8021 |  | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.44494 | 0.58979 | 0.78863 | 1.0628 | 1.4424 | 1.9699 | 2.7054 | 3.7339 | 5.176 | 7.2029 | 10.0579 | 14.087 | 19.7826 |  | 356.6509 | 402.4294 | 454.5778 | 514.0179 | 581.8079 | 659.1635 | 747.4808 | 848.364 | 963.657 | 1095.4789 | 1246.2662 | 1418.8207 | 1616.3649 | 1842.6056 | 2101.8076 | 2398.8785 | 2739.4664 | 3129.9993 | 3577.963 | 4091.9925 | 4681.989 | 5359.3502 | 6137.1959 | 7030.6276 | 8057.0275 | 9236.3995 | 10591.7616 | 12149.5929 | 13940.3444 | 15999.0195 |  | 367.1949 | 418.2972 | 476.5102 | 542.8628 | 618.5364 | 704.888 | 803.476 | 916.0915 | 1044.7923 | 1191.9444 | 1360.2674 | 1552.889 | 1773.4064 | 2025.9576 | 2315.3033 | 2646.9219 | 3027.1182 | 3456.9761 | 3944.9819 | 4502.2441 | 5138.0391 | 5862.5863 | 6686.9965 | 7623.1294 | 8683.3106 | 9879.8352 | 11224.1526 | 12725.5793 | 14389.3176 | 16213.4612
| TRUE | 3669 | 22009886 | SA | Blank | 22 | BUS NO.3 | BUS PROT | X | GEC | CDG14_2250 | CDG14 2250 | CDG14 | Electromechanical |  | 0.033587 | 2190 |  | 8.25 | 0.0054067 | 0.00050998 | 0.0048967 | 30.0172 | 142.7954 | 172.8125 | 18.2427 | 2.1683 | 797.288 |  | 11.9015 | 0.014549 | 0.0013724 | 0.013177 | 80.7762 | 384.2624 | 465.0386 | 49.0912 | 5.8349 | 2145.5028 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.37173 |  | 990.5116 | 2665.4676 | 45.6009 | 2619.8667 |  | 0.036645 |  | 8.5579 | 8.8774 | 9.2087 | 9.5524 | 9.909 | 10.2788 | 10.6625 | 11.0604 | 11.4733 | 11.9015 | 12.3457 | 12.8065 | 13.2845 | 13.7804 | 14.2947 | 14.8283 | 15.3818 | 15.9559 | 16.5514 | 17.1692 | 17.8101 | 18.4748 | 19.1644 | 19.8797 | 20.6217 | 21.3914 | 22.1898 | 23.0181 | 23.8772 | 24.7684 |  | 0.0059576 | 0.0065678 | 0.0072438 | 0.007993 | 0.0088234 | 0.0097442 | 0.010765 | 0.011898 | 0.013155 | 0.014549 | 0.016097 | 0.017816 | 0.019724 | 0.021844 | 0.024198 | 0.026813 | 0.02972 | 0.032949 | 0.03654 | 0.040531 | 0.044968 | 0.049903 | 0.055391 | 0.061495 | 0.068286 | 0.075841 | 0.084248 | 0.093603 | 0.10402 | 0.1156 |  | 0.00056195 | 0.0006195 | 0.00068327 | 0.00075394 | 0.00083227 | 0.00091912 | 0.0010154 | 0.0011223 | 0.0012408 | 0.0013724 | 0.0015184 | 0.0016805 | 0.0018605 | 0.0020604 | 0.0022825 | 0.0025292 | 0.0028033 | 0.003108 | 0.0034466 | 0.0038231 | 0.0042416 | 0.0047071 | 0.0052247 | 0.0058005 | 0.0064411 | 0.0071537 | 0.0079467 | 0.0088291 | 0.0098113 | 0.010904 | 1091.4383 | 1203.2258 | 1327.0762 | 1464.327 | 1616.4664 | 1785.1504 | 1972.2221 | 2179.7333 | 2409.9676 | 2665.4676 | 2949.064 | 3263.9087 | 3613.5119 | 4001.7825 | 4433.0741 | 4912.2362 | 5444.6705 | 6036.3946 | 6694.1127 | 7425.2944 | 8238.2623 | 9142.2905 | 10147.7138 | 11266.0496 | 12510.1337 | 13894.2729 | 15434.4131 | 17148.3294 | 19055.8355 | 21179.0198 |  | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 37.5716 | 49.8033 | 66.5938 | 89.7458 | 121.8 | 166.3434 | 228.4481 | 315.2963 | 437.072 | 608.2309 | 849.3146 | 1189.5384 | 1670.4885 |  | 33.0757 | 36.4634 | 40.2166 | 44.376 | 48.9865 | 54.0984 | 59.7676 | 66.0562 | 73.0333 | 80.7762 | 89.3705 | 98.9118 | 109.5064 | 121.2728 | 134.343 | 148.8638 | 164.9991 | 182.9311 | 202.8631 | 225.0213 | 249.6581 | 277.0544 | 307.5234 | 341.4142 | 379.1158 | 421.0618 | 467.7353 | 519.675 | 577.4814 | 641.8238 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 18.8638 | 22.2515 | 26.0048 | 30.1641 | 34.7746 | 39.8866 | 45.5557 | 51.8443 | 58.8215 | 66.5643 | 75.1586 | 84.6999 | 95.2945 | 107.0609 | 120.1311 | 134.652 | 150.7872 | 165.9204 | 180.3143 | 194.8706 | 209.0251 | 221.9087 | 232.2105 | 237.9831 | 236.3636 | 223.1749 | 192.3552 | 135.1429 | 38.911 | -114.4995 |  | 157.3453 | 173.4609 | 191.3156 | 211.1021 | 233.035 | 257.353 | 284.3219 | 314.2374 | 347.4287 | 384.2624 | 425.1466 | 470.5356 | 520.9356 | 576.9099 | 639.0863 | 708.1638 | 784.9213 | 870.2262 | 965.0449 | 1070.4544 | 1187.6545 | 1317.9821 | 1462.9272 | 1624.1501 | 1803.5013 | 2003.0433 | 2225.0749 | 2472.1586 | 2747.1508 | 3053.2359 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 157.2787 | 173.3943 | 191.249 | 211.0355 | 232.9684 | 257.2865 | 284.2553 | 314.1708 | 347.3621 | 384.1958 | 425.08 | 470.469 | 520.869 | 576.8433 | 639.0197 | 708.0973 | 784.8547 | 870.1465 | 964.9393 | 1070.3132 | 1187.4642 | 1317.7238 | 1462.5744 | 1623.6656 | 1802.8326 | 2002.1162 | 2223.7848 | 2470.3572 | 2744.6278 | 3049.6928 |  | 176.1425 | 195.6458 | 217.2538 | 241.1996 | 267.7431 | 297.173 | 329.8111 | 366.0151 | 406.1836 | 450.7602 | 500.2386 | 555.1689 | 616.1635 | 683.9042 | 759.1508 | 842.7492 | 935.6419 | 1036.0668 | 1145.2536 | 1265.1838 | 1396.4893 | 1539.6325 | 1694.7849 | 1861.6486 | 2039.1962 | 2225.2911 | 2416.14 | 2605.5 | 2783.5388 | 2935.1933 |  | 20.1016 | 22.1604 | 24.4414 | 26.9692 | 29.7713 | 32.878 | 36.3234 | 40.1452 | 44.3856 | 49.0912 | 54.3144 | 60.113 | 66.5518 | 73.7028 | 81.6461 | 90.4711 | 100.2772 | 111.1753 | 123.2888 | 136.7553 | 151.7282 | 168.3781 | 186.8955 | 207.4924 | 230.4053 | 255.8977 | 284.2633 | 315.8293 | 350.9608 | 390.0645 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 5.4304 | 7.4893 | 9.7703 | 12.2981 | 15.1001 | 18.2069 | 21.6523 | 25.4741 | 29.7144 | 34.4201 | 39.6432 | 45.4419 | 51.8807 | 59.0317 | 66.975 | 75.8 | 85.6061 | 93.6148 | 100.0114 | 105.6303 | 109.7822 | 111.4505 | 109.1489 | 100.7189 | 83.0402 | 51.6163 | -0.015525 | -81.1287 | -205.0131 | -390.6989 |  | 2.3892 | 2.634 | 2.9051 | 3.2055 | 3.5386 | 3.9078 | 4.3173 | 4.7716 | 5.2756 | 5.8349 | 6.4557 | 7.145 | 7.9103 | 8.7602 | 9.7043 | 10.7533 | 11.9188 | 13.2141 | 14.6539 | 16.2545 | 18.0342 | 20.0132 | 22.2141 | 24.6623 | 27.3857 | 30.4156 | 33.7871 | 37.539 | 41.7147 | 46.3625 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0.32155 | 0.56626 | 0.83738 | 1.1378 | 1.4709 | 1.8401 | 2.2497 | 2.7039 | 3.2079 | 3.7672 | 4.388 | 5.0773 | 5.8426 | 6.6925 | 7.6367 | 8.6856 | 9.8511 | 10.7392 | 11.3733 | 11.8679 | 12.1225 | 11.99 | 11.2568 | 9.614 | 6.6166 | 1.625 | -6.278 | -18.4067 | -36.6421 | -63.6753 |  | 878.5265 | 968.5071 | 1068.1975 | 1178.6742 | 1301.135 | 1436.913 | 1587.4919 | 1754.5229 | 1939.8444 | 2145.5028 | 2373.7768 | 2627.2033 | 2908.6078 | 3221.1367 | 3568.2944 | 3953.9842 | 4382.5541 | 4858.8479 | 5388.262 | 5976.8087 | 6631.1873 | 7358.8627 | 8168.1536 | 9068.3305 | 10069.7256 | 11183.8544 | 12423.5526 | 13803.1275 | 15338.5278 | 17047.533 |  | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.44494 | 0.58979 | 0.78863 | 1.0628 | 1.4424 | 1.9699 | 2.7054 | 3.7339 | 5.176 | 7.2029 | 10.0579 | 14.087 | 19.7826 |  | 878.1547 | 968.1354 | 1067.8258 | 1178.3024 | 1300.7633 | 1436.5413 | 1587.1202 | 1754.1512 | 1939.4727 | 2145.1311 | 2373.405 | 2626.8316 | 2908.2361 | 3220.765 | 3567.9227 | 3953.6124 | 4382.1824 | 4858.403 | 5387.6722 | 5976.0201 | 6630.1245 | 7357.4203 | 8166.1837 | 9065.6251 | 10065.9917 | 11178.6785 | 12416.3497 | 13793.0695 | 15324.4408 | 17027.7504 |  | 1060.0492 | 1171.8368 | 1295.6872 | 1432.938 | 1585.0774 | 1753.7613 | 1940.8331 | 2148.3443 | 2378.5786 | 2634.0786 | 2917.6749 | 3232.5197 | 3582.1229 | 3970.3935 | 4401.6851 | 4880.8472 | 5413.2815 | 5998.8239 | 6644.3105 | 7358.7021 | 8148.5185 | 9020.4933 | 9981.3742 | 11037.6067 | 12194.8446 | 13457.2109 | 14826.1961 | 16299.0342 | 17866.3244 | 19508.5695
| TRUE | 3670 | 22009887 | SA | Blank | 22 | BUS NO.3 | BUS PROT | X | GEC | CDG14_2250 | CDG14 2250 | CDG14 | Electromechanical |  | 0.033587 | 2190 |  | 8.25 | 0.0054067 | 0.00050998 | 0.0048967 | 30.0172 | 142.7954 | 172.8125 | 18.2427 | 2.1683 | 797.288 |  | 11.9015 | 0.014549 | 0.0013724 | 0.013177 | 80.7762 | 384.2624 | 465.0386 | 49.0912 | 5.8349 | 2145.5028 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.37173 |  | 990.5116 | 2665.4676 | 45.6009 | 2619.8667 |  | 0.036645 |  | 8.5579 | 8.8774 | 9.2087 | 9.5524 | 9.909 | 10.2788 | 10.6625 | 11.0604 | 11.4733 | 11.9015 | 12.3457 | 12.8065 | 13.2845 | 13.7804 | 14.2947 | 14.8283 | 15.3818 | 15.9559 | 16.5514 | 17.1692 | 17.8101 | 18.4748 | 19.1644 | 19.8797 | 20.6217 | 21.3914 | 22.1898 | 23.0181 | 23.8772 | 24.7684 |  | 0.0059576 | 0.0065678 | 0.0072438 | 0.007993 | 0.0088234 | 0.0097442 | 0.010765 | 0.011898 | 0.013155 | 0.014549 | 0.016097 | 0.017816 | 0.019724 | 0.021844 | 0.024198 | 0.026813 | 0.02972 | 0.032949 | 0.03654 | 0.040531 | 0.044968 | 0.049903 | 0.055391 | 0.061495 | 0.068286 | 0.075841 | 0.084248 | 0.093603 | 0.10402 | 0.1156 |  | 0.00056195 | 0.0006195 | 0.00068327 | 0.00075394 | 0.00083227 | 0.00091912 | 0.0010154 | 0.0011223 | 0.0012408 | 0.0013724 | 0.0015184 | 0.0016805 | 0.0018605 | 0.0020604 | 0.0022825 | 0.0025292 | 0.0028033 | 0.003108 | 0.0034466 | 0.0038231 | 0.0042416 | 0.0047071 | 0.0052247 | 0.0058005 | 0.0064411 | 0.0071537 | 0.0079467 | 0.0088291 | 0.0098113 | 0.010904 | 1091.4383 | 1203.2258 | 1327.0762 | 1464.327 | 1616.4664 | 1785.1504 | 1972.2221 | 2179.7333 | 2409.9676 | 2665.4676 | 2949.064 | 3263.9087 | 3613.5119 | 4001.7825 | 4433.0741 | 4912.2362 | 5444.6705 | 6036.3946 | 6694.1127 | 7425.2944 | 8238.2623 | 9142.2905 | 10147.7138 | 11266.0496 | 12510.1337 | 13894.2729 | 15434.4131 | 17148.3294 | 19055.8355 | 21179.0198 |  | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 31.3897 | 37.5716 | 49.8033 | 66.5938 | 89.7458 | 121.8 | 166.3434 | 228.4481 | 315.2963 | 437.072 | 608.2309 | 849.3146 | 1189.5384 | 1670.4885 |  | 33.0757 | 36.4634 | 40.2166 | 44.376 | 48.9865 | 54.0984 | 59.7676 | 66.0562 | 73.0333 | 80.7762 | 89.3705 | 98.9118 | 109.5064 | 121.2728 | 134.343 | 148.8638 | 164.9991 | 182.9311 | 202.8631 | 225.0213 | 249.6581 | 277.0544 | 307.5234 | 341.4142 | 379.1158 | 421.0618 | 467.7353 | 519.675 | 577.4814 | 641.8238 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 18.8638 | 22.2515 | 26.0048 | 30.1641 | 34.7746 | 39.8866 | 45.5557 | 51.8443 | 58.8215 | 66.5643 | 75.1586 | 84.6999 | 95.2945 | 107.0609 | 120.1311 | 134.652 | 150.7872 | 165.9204 | 180.3143 | 194.8706 | 209.0251 | 221.9087 | 232.2105 | 237.9831 | 236.3636 | 223.1749 | 192.3552 | 135.1429 | 38.911 | -114.4995 |  | 157.3453 | 173.4609 | 191.3156 | 211.1021 | 233.035 | 257.353 | 284.3219 | 314.2374 | 347.4287 | 384.2624 | 425.1466 | 470.5356 | 520.9356 | 576.9099 | 639.0863 | 708.1638 | 784.9213 | 870.2262 | 965.0449 | 1070.4544 | 1187.6545 | 1317.9821 | 1462.9272 | 1624.1501 | 1803.5013 | 2003.0433 | 2225.0749 | 2472.1586 | 2747.1508 | 3053.2359 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 157.2787 | 173.3943 | 191.249 | 211.0355 | 232.9684 | 257.2865 | 284.2553 | 314.1708 | 347.3621 | 384.1958 | 425.08 | 470.469 | 520.869 | 576.8433 | 639.0197 | 708.0973 | 784.8547 | 870.1465 | 964.9393 | 1070.3132 | 1187.4642 | 1317.7238 | 1462.5744 | 1623.6656 | 1802.8326 | 2002.1162 | 2223.7848 | 2470.3572 | 2744.6278 | 3049.6928 |  | 176.1425 | 195.6458 | 217.2538 | 241.1996 | 267.7431 | 297.173 | 329.8111 | 366.0151 | 406.1836 | 450.7602 | 500.2386 | 555.1689 | 616.1635 | 683.9042 | 759.1508 | 842.7492 | 935.6419 | 1036.0668 | 1145.2536 | 1265.1838 | 1396.4893 | 1539.6325 | 1694.7849 | 1861.6486 | 2039.1962 | 2225.2911 | 2416.14 | 2605.5 | 2783.5388 | 2935.1933 |  | 20.1016 | 22.1604 | 24.4414 | 26.9692 | 29.7713 | 32.878 | 36.3234 | 40.1452 | 44.3856 | 49.0912 | 54.3144 | 60.113 | 66.5518 | 73.7028 | 81.6461 | 90.4711 | 100.2772 | 111.1753 | 123.2888 | 136.7553 | 151.7282 | 168.3781 | 186.8955 | 207.4924 | 230.4053 | 255.8977 | 284.2633 | 315.8293 | 350.9608 | 390.0645 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 5.4304 | 7.4893 | 9.7703 | 12.2981 | 15.1001 | 18.2069 | 21.6523 | 25.4741 | 29.7144 | 34.4201 | 39.6432 | 45.4419 | 51.8807 | 59.0317 | 66.975 | 75.8 | 85.6061 | 93.6148 | 100.0114 | 105.6303 | 109.7822 | 111.4505 | 109.1489 | 100.7189 | 83.0402 | 51.6163 | -0.015525 | -81.1287 | -205.0131 | -390.6989 |  | 2.3892 | 2.634 | 2.9051 | 3.2055 | 3.5386 | 3.9078 | 4.3173 | 4.7716 | 5.2756 | 5.8349 | 6.4557 | 7.145 | 7.9103 | 8.7602 | 9.7043 | 10.7533 | 11.9188 | 13.2141 | 14.6539 | 16.2545 | 18.0342 | 20.0132 | 22.2141 | 24.6623 | 27.3857 | 30.4156 | 33.7871 | 37.539 | 41.7147 | 46.3625 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0.32155 | 0.56626 | 0.83738 | 1.1378 | 1.4709 | 1.8401 | 2.2497 | 2.7039 | 3.2079 | 3.7672 | 4.388 | 5.0773 | 5.8426 | 6.6925 | 7.6367 | 8.6856 | 9.8511 | 10.7392 | 11.3733 | 11.8679 | 12.1225 | 11.99 | 11.2568 | 9.614 | 6.6166 | 1.625 | -6.278 | -18.4067 | -36.6421 | -63.6753 |  | 878.5265 | 968.5071 | 1068.1975 | 1178.6742 | 1301.135 | 1436.913 | 1587.4919 | 1754.5229 | 1939.8444 | 2145.5028 | 2373.7768 | 2627.2033 | 2908.6078 | 3221.1367 | 3568.2944 | 3953.9842 | 4382.5541 | 4858.8479 | 5388.262 | 5976.8087 | 6631.1873 | 7358.8627 | 8168.1536 | 9068.3305 | 10069.7256 | 11183.8544 | 12423.5526 | 13803.1275 | 15338.5278 | 17047.533 |  | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.44494 | 0.58979 | 0.78863 | 1.0628 | 1.4424 | 1.9699 | 2.7054 | 3.7339 | 5.176 | 7.2029 | 10.0579 | 14.087 | 19.7826 |  | 878.1547 | 968.1354 | 1067.8258 | 1178.3024 | 1300.7633 | 1436.5413 | 1587.1202 | 1754.1512 | 1939.4727 | 2145.1311 | 2373.405 | 2626.8316 | 2908.2361 | 3220.765 | 3567.9227 | 3953.6124 | 4382.1824 | 4858.403 | 5387.6722 | 5976.0201 | 6630.1245 | 7357.4203 | 8166.1837 | 9065.6251 | 10065.9917 | 11178.6785 | 12416.3497 | 13793.0695 | 15324.4408 | 17027.7504 |  | 1060.0492 | 1171.8368 | 1295.6872 | 1432.938 | 1585.0774 | 1753.7613 | 1940.8331 | 2148.3443 | 2378.5786 | 2634.0786 | 2917.6749 | 3232.5197 | 3582.1229 | 3970.3935 | 4401.6851 | 4880.8472 | 5413.2815 | 5998.8239 | 6644.3105 | 7358.7021 | 8148.5185 | 9020.4933 | 9981.3742 | 11037.6067 | 12194.8446 | 13457.2109 | 14826.1961 | 16299.0342 | 17866.3244 | 19508.5695
| TRUE | 3671 | 22005007 | SA | Blank | 22 | BUS NO.3 | DISTANCE | X | Schweitzer | SEL_311A | SEL 311A | SEL 300s | Digital |  | 0.033587 | 1 |  | 6.6 | 0.017308 | 7.9633e-07 | 0.017307 | 47.5968 | 0.055743 | 47.6526 | 49.1349 | 6.9249 | 1.245 |  | 15.598 | 0.17662 | 8.1263e-06 | 0.17661 | 485.7104 | 0.56884 | 486.2792 | 501.4057 | 70.6662 | 12.7044 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.37173 |  | 104.9573 | 1071.0555 | 31.3391 | 1039.7164 |  | 0.086007 |  | 7.1928 | 7.8388 | 8.5428 | 9.3101 | 10.1463 | 11.0575 | 12.0507 | 13.133 | 14.3125 | 15.598 | 16.9989 | 18.5257 | 20.1895 | 22.0028 | 23.979 | 26.1326 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021585 | 0.027005 | 0.033883 | 0.042625 | 0.053753 | 0.067937 | 0.086039 | 0.10917 | 0.13875 | 0.17662 | 0.22515 | 0.28739 | 0.36726 | 0.46984 | 0.60168 | 0.7712 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 9.9315e-07 | 1.2425e-06 | 1.5589e-06 | 1.9612e-06 | 2.4732e-06 | 3.1258e-06 | 3.9587e-06 | 5.0228e-06 | 6.3838e-06 | 8.1263e-06 | 1.0359e-05 | 1.3223e-05 | 1.6898e-05 | 2.1618e-05 | 2.7683e-05 | 3.5483e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 130.8973 | 163.7617 | 205.4695 | 258.4832 | 325.9657 | 411.9809 | 521.7544 | 662.0084 | 841.3951 | 1071.0555 | 1365.3418 | 1742.7491 | 2227.1209 | 2849.2051 | 3648.6652 | 4676.6798 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 | 5710.966 |  | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 31.3391 | 37.5109 | 49.723 | 66.4863 | 89.601 | 121.6035 | 166.075 | 228.0794 | 314.7875 | 436.3667 | 607.2495 | 847.9441 | 1187.6189 | 1667.7929 |  | 59.3603 | 74.2639 | 93.1778 | 117.2189 | 147.8214 | 186.8282 | 236.6091 | 300.2126 | 381.5622 | 485.7104 | 619.1655 | 790.3151 | 1009.9717 | 1292.0791 | 1654.6243 | 2120.8162 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 45.1484 | 60.052 | 78.966 | 103.007 | 133.6095 | 172.6163 | 222.3972 | 286.0007 | 367.3503 | 471.4985 | 604.9536 | 776.1032 | 995.7598 | 1277.8672 | 1640.4124 | 2106.6043 | 2575.6402 | 2572.8414 | 2567.3034 | 2559.7014 | 2549.2192 | 2534.7064 | 2514.5392 | 2486.4209 | 2447.0999 | 2391.9652 | 2314.472 | 2205.32 | 2051.2817 | 1833.5287 |  | 0.06952 | 0.086975 | 0.10913 | 0.13728 | 0.17312 | 0.21881 | 0.27711 | 0.3516 | 0.44687 | 0.56884 | 0.72514 | 0.92558 | 1.1828 | 1.5132 | 1.9378 | 2.4838 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019922 | 0.026408 | 0.035311 | 0.047588 | 0.064584 | 0.088203 | 0.12113 | 0.16719 | 0.23176 | 0.32251 | 0.45035 | 0.63075 | 0.88577 |  | 0.052876 | 0.07033 | 0.092482 | 0.12064 | 0.15648 | 0.20216 | 0.26046 | 0.33495 | 0.43022 | 0.5522 | 0.7085 | 0.90894 | 1.1662 | 1.4966 | 1.9212 | 2.4672 | 3.0165 | 3.0132 | 3.0067 | 2.9978 | 2.9855 | 2.9685 | 2.9449 | 2.912 | 2.8659 | 2.8014 | 2.7106 | 2.5828 | 2.4024 | 2.1473 |  | 45.2013 | 60.1223 | 79.0584 | 103.1277 | 133.766 | 172.8185 | 222.6577 | 286.3356 | 367.7805 | 472.0507 | 605.6621 | 777.0121 | 996.926 | 1279.3638 | 1642.3336 | 2109.0714 | 2578.6567 | 2575.8546 | 2570.3101 | 2562.6992 | 2552.2047 | 2537.675 | 2517.4841 | 2489.3329 | 2449.9658 | 2394.7666 | 2317.1826 | 2207.9028 | 2053.6841 | 1835.6761 |  | 61.2785 | 76.6637 | 96.1888 | 121.0068 | 152.5981 | 192.8654 | 244.255 | 309.9137 | 393.8921 | 501.4057 | 639.1734 | 815.8535 | 1042.6081 | 1333.8317 | 1708.0922 | 2189.3487 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 46.6074 | 61.9926 | 81.5177 | 106.3356 | 137.927 | 178.1943 | 229.5838 | 295.2426 | 379.221 | 486.7346 | 624.5022 | 801.1824 | 1027.937 | 1319.1605 | 1693.4211 | 2174.6776 | 2658.8701 | 2655.9808 | 2650.2638 | 2642.4162 | 2631.5953 | 2616.6136 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 8.6364 | 10.8047 | 13.5565 | 17.0542 | 21.5066 | 27.1817 | 34.4244 | 43.678 | 55.5136 | 70.6662 | 90.0826 | 114.9833 | 146.9412 | 187.9851 | 240.732 | 308.5584 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 6.5687 | 8.737 | 11.4888 | 14.9865 | 19.4389 | 25.114 | 32.3567 | 41.6104 | 53.4459 | 68.5985 | 88.0149 | 112.9156 | 144.8735 | 185.9174 | 238.6643 | 306.4907 | 374.7309 | 374.3237 | 373.518 | 372.412 | 370.8869 | 368.7755 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 1.5526 | 1.9425 | 2.4372 | 3.066 | 3.8665 | 4.8867 | 6.1888 | 7.8524 | 9.9803 | 12.7044 | 16.1951 | 20.6717 | 26.4171 | 33.796 | 43.2788 | 55.4727 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 | 67.7409 |  | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.37173 | 0.44494 | 0.58979 | 0.78863 | 1.0628 | 1.4424 | 1.9699 | 2.7054 | 3.7339 | 5.176 | 7.2029 | 10.0579 | 14.087 | 19.7826 |  | 1.1809 | 1.5707 | 2.0655 | 2.6943 | 3.4947 | 4.515 | 5.8171 | 7.4807 | 9.6085 | 12.3327 | 15.8233 | 20.3 | 26.0454 | 33.4243 | 42.9071 | 55.101 | 67.3692 | 67.296 | 67.1511 | 66.9523 | 66.6781 | 66.2985 | 65.771 | 65.0356 | 64.0071 | 62.5649 | 60.538 | 57.683 | 53.6539 | 47.9583 |  | 99.5582 | 132.4226 | 174.1304 | 227.1441 | 294.6266 | 380.6418 | 490.4153 | 630.6693 | 810.056 | 1039.7164 | 1334.0027 | 1711.41 | 2195.7818 | 2817.866 | 3617.3261 | 4645.3407 | 5679.6269 | 5673.4551 | 5661.2431 | 5644.4797 | 5621.3651 | 5589.3625 | 5544.891 | 5482.8866 | 5396.1785 | 5274.5993 | 5103.7166 | 4863.0219 | 4523.3472 | 4043.1731
| TRUE | 3672 | 22004135 | SA | Blank | 22 | CAP NO.1 | OVERCURRENT | X | English Electric | CDG11_521 | CDG11 521 | CDG11 | Electromechanical |  | 0.2894 | 2190 |  | 9.9 | 0.0088019 | 0.0046268 | 0.0041751 | 50.955 | 1295.4993 | 1346.4543 | 51.2524 | 3.5679 | 7233.3312 |  | 13.9533 | 0.022617 | 0.011889 | 0.010728 | 130.9327 | 3328.8817 | 3459.8143 | 131.697 | 9.168 | 18586.582 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.57365 | 28.9984 | 14.6814 | 2.0677 | 3.2029 |  | 8634.6058 | 22187.2612 | 48.9505 | 22138.3107 |  | 0.034318 |  | 10.2456 | 10.6034 | 10.9736 | 11.3567 | 11.7532 | 12.1636 | 12.5882 | 13.0277 | 13.4826 | 13.9533 | 14.4405 | 14.9446 | 15.4664 | 16.0064 | 16.5653 | 17.1436 | 17.7422 | 18.3616 | 19.0027 | 19.6661 | 20.3528 | 21.0634 | 21.7988 | 22.5598 | 23.3475 | 24.1626 | 25.0062 | 25.8793 | 26.7829 | 27.718 |  | 0.0096591 | 0.010604 | 0.011644 | 0.012791 | 0.014056 | 0.01545 | 0.016987 | 0.018683 | 0.020553 | 0.022617 | 0.024894 | 0.027408 | 0.030182 | 0.033244 | 0.036626 | 0.04036 | 0.044483 | 0.049038 | 0.05407 | 0.059628 | 0.06577 | 0.072556 | 0.080057 | 0.088346 | 0.097509 | 0.10764 | 0.11884 | 0.13122 | 0.14491 | 0.16005 |  | 0.0050774 | 0.0055738 | 0.0061209 | 0.0067238 | 0.0073885 | 0.0081213 | 0.0089295 | 0.0098208 | 0.010804 | 0.011889 | 0.013086 | 0.014407 | 0.015865 | 0.017475 | 0.019253 | 0.021215 | 0.023383 | 0.025777 | 0.028422 | 0.031344 | 0.034572 | 0.03814 | 0.042083 | 0.04644 | 0.051257 | 0.056581 | 0.062468 | 0.068976 | 0.076173 | 0.084131 | 9475.5383 | 10402.0135 | 11422.9375 | 12548.1569 | 13788.5591 | 15156.1833 | 16664.3436 | 18327.7645 | 20162.7322 | 22187.2612 | 24421.2789 | 26886.8306 | 29608.306 | 32612.6898 | 35929.8405 | 39592.7973 | 43638.122 | 48106.2761 | 53042.0394 | 58494.9733 | 64519.9342 | 71177.6422 | 78535.3108 | 86667.3447 | 95656.1128 | 105592.8046 | 116578.3787 | 128724.6138 | 142155.2733 | 157007.3947 |  | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 41.5868 | 55.1257 | 73.7105 | 99.3367 | 134.8165 | 184.1202 | 252.8618 | 348.9914 | 483.781 | 673.2314 | 940.0792 | 1316.662 | 1849.0103 |  | 55.9176 | 61.3849 | 67.4096 | 74.0499 | 81.3698 | 89.4405 | 98.3405 | 108.1568 | 118.9854 | 130.9327 | 144.1162 | 158.666 | 174.7261 | 192.4557 | 212.0311 | 233.6471 | 257.5196 | 283.8873 | 313.0145 | 345.1937 | 380.7485 | 420.0373 | 463.4568 | 511.446 | 564.491 | 623.1299 | 687.9586 | 759.6366 | 838.8943 | 926.5404 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 41.7052 | 47.1725 | 53.1973 | 59.8375 | 67.1574 | 75.2281 | 84.1281 | 93.9444 | 104.773 | 116.7203 | 129.9038 | 144.4536 | 160.5137 | 178.2434 | 197.8187 | 219.4347 | 243.3072 | 266.876 | 290.465 | 315.0419 | 340.1141 | 364.8897 | 388.1412 | 408.0112 | 421.7337 | 425.2361 | 412.5688 | 375.091 | 300.305 | 170.1905 |  | 1421.6692 | 1560.6736 | 1713.8486 | 1882.6717 | 2068.7764 | 2273.9688 | 2500.2467 | 2749.8193 | 3025.13 | 3328.8817 | 3664.0641 | 4033.9849 | 4442.3034 | 4893.0683 | 5390.7594 | 5940.3338 | 6547.277 | 7217.6597 | 7958.2004 | 8776.3353 | 9680.2946 | 10679.1886 | 11783.1017 | 13003.1972 | 14351.8335 | 15842.6922 | 17490.9207 | 19313.2898 | 21328.3684 | 23556.7171 |  | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.68662 | 0.91016 | 1.217 | 1.6401 | 2.2259 | 3.0399 | 4.1749 | 5.7621 | 7.9875 | 11.1155 | 15.5213 | 21.7389 | 30.5284 |  | 1421.0955 | 1560.0999 | 1713.275 | 1882.0981 | 2068.2027 | 2273.3952 | 2499.6731 | 2749.2456 | 3024.5563 | 3328.308 | 3663.4905 | 4033.4113 | 4441.7298 | 4892.4947 | 5390.1857 | 5939.7601 | 6546.7033 | 7216.973 | 7957.2903 | 8775.1183 | 9678.6545 | 10676.9627 | 11780.0618 | 12999.0223 | 14346.0715 | 15834.7047 | 17479.8052 | 19297.7685 | 21306.6295 | 23526.1888 |  | 1462.8007 | 1607.2724 | 1766.4722 | 1941.9355 | 2135.3601 | 2348.6233 | 2583.8012 | 2843.19 | 3129.3294 | 3445.0283 | 3793.3942 | 4177.8649 | 4602.2435 | 5070.738 | 5588.0045 | 6159.1948 | 6790.0105 | 7483.849 | 8247.7553 | 9090.1602 | 10018.7686 | 11041.8524 | 12168.203 | 13407.0335 | 14767.8052 | 16259.9408 | 17892.374 | 19672.8595 | 21606.9345 | 23696.3793 |  | 56.244 | 61.7432 | 67.8031 | 74.4821 | 81.8448 | 89.9626 | 98.9146 | 108.7881 | 119.68 | 131.697 | 144.9574 | 159.5922 | 175.7461 | 193.5792 | 213.2688 | 235.011 | 259.0229 | 285.5445 | 314.8417 | 347.2087 | 382.9711 | 422.4892 | 466.1621 | 514.4315 | 567.7861 | 626.7673 | 691.9744 | 764.0709 | 843.7912 | 931.949 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 41.5625 | 47.0618 | 53.1217 | 59.8007 | 67.1634 | 75.2812 | 84.2331 | 94.1067 | 104.9985 | 117.0155 | 130.276 | 144.9108 | 161.0646 | 178.8978 | 198.5874 | 220.3296 | 244.3414 | 267.9718 | 291.548 | 316.0619 | 340.9957 | 365.5217 | 388.361 | 407.5832 | 420.3177 | 422.3428 | 407.4964 | 366.8347 | 287.4277 | 150.6385 |  | 3.9154 | 4.2982 | 4.7201 | 5.185 | 5.6976 | 6.2627 | 6.8859 | 7.5732 | 8.3314 | 9.168 | 10.0911 | 11.1099 | 12.2344 | 13.4758 | 14.8465 | 16.3601 | 18.0317 | 19.8779 | 21.9174 | 24.1706 | 26.6602 | 29.4112 | 32.4515 | 35.8117 | 39.5259 | 43.6319 | 48.1712 | 53.1901 | 58.7398 | 64.8768 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.8477 | 2.2305 | 2.6523 | 3.1173 | 3.6298 | 4.195 | 4.8181 | 5.5055 | 6.2637 | 7.1003 | 8.0234 | 9.0422 | 10.1667 | 11.4081 | 12.7788 | 14.2924 | 15.9639 | 17.403 | 18.6368 | 19.784 | 20.7484 | 21.388 | 21.4941 | 20.7633 | 18.7567 | 14.841 | 8.1057 | -2.7561 | -19.6177 | -45.1619 |  | 7937.7922 | 8713.9136 | 9569.156 | 10511.7682 | 11550.8706 | 12696.5488 | 13959.9559 | 15353.4271 | 16890.6055 | 18586.582 | 20458.0502 | 22523.4776 | 24803.2959 | 27320.1107 | 30098.9346 | 33167.4453 | 36556.2709 | 40299.3067 | 44434.0653 | 49002.065 | 54049.2598 | 59626.5158 | 65790.1387 | 72602.4583 | 80132.4763 | 88456.5833 | 97659.3538 | 107834.4265 | 119085.4795 | 131527.3114 |  | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.8337 | 5.0818 | 6.7951 | 9.1575 | 12.4282 | 16.9733 | 23.3103 | 32.1721 | 44.5979 | 62.0625 | 86.6622 | 121.3779 | 170.453 |  | 7934.5893 | 8710.7107 | 9565.9531 | 10508.5652 | 11547.6677 | 12693.3458 | 13956.753 | 15350.2242 | 16887.4025 | 18583.379 | 20454.8472 | 22520.2747 | 24800.093 | 27316.9078 | 30095.7317 | 33164.2424 | 36553.068 | 40295.473 | 44428.9835 | 48995.2699 | 54040.1024 | 59614.0876 | 65773.1654 | 72579.148 | 80100.3041 | 88411.9854 | 97597.2913 | 107747.7643 | 118964.1016 | 131356.8584 |  | 9440.8002 | 10367.2754 | 11388.1994 | 12513.4188 | 13753.821 | 15121.4452 | 16629.6055 | 18293.0264 | 20127.9941 | 22152.5231 | 24386.5408 | 26852.0925 | 29573.5679 | 32577.9517 | 35895.1024 | 39558.0592 | 43603.3839 | 48064.6968 | 52986.9235 | 58421.2759 | 64420.6152 | 71042.8497 | 78351.2234 | 86414.528 | 95307.1837 | 105109.1099 | 115905.2674 | 127784.7024 | 140838.8462 | 155158.7142
| TRUE | 3673 | 22004136 | SA | Blank | 22 | CAP NO.1 | OVERCURRENT | X | English Electric | CDG11_521 | CDG11 521 | CDG11 | Electromechanical |  | 0.2894 | 2190 |  | 9.9 | 0.0088019 | 0.0046268 | 0.0041751 | 50.955 | 1295.4993 | 1346.4543 | 51.2524 | 3.5679 | 7233.3312 |  | 14.6263 | 0.025802 | 0.013563 | 0.012239 | 149.3696 | 3797.6299 | 3946.9995 | 150.2415 | 10.4589 | 21203.8058 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.57365 | 28.9984 | 14.6814 | 2.0677 | 3.2029 |  | 8634.6058 | 25311.5058 | 48.9505 | 25262.5553 |  | 0.039029 |  | 10.294 | 10.7037 | 11.1297 | 11.5727 | 12.0333 | 12.5122 | 13.0102 | 13.528 | 14.0664 | 14.6263 | 15.2084 | 15.8137 | 16.4431 | 17.0975 | 17.778 | 18.4856 | 19.2213 | 19.9863 | 20.7818 | 21.6089 | 22.4689 | 23.3632 | 24.2931 | 25.2599 | 26.2653 | 27.3106 | 28 | 28 | 28 | 28 |  | 0.0097834 | 0.010879 | 0.012103 | 0.01347 | 0.014998 | 0.016705 | 0.018613 | 0.020747 | 0.023133 | 0.025802 | 0.028788 | 0.032129 | 0.035868 | 0.040053 | 0.044739 | 0.049986 | 0.055861 | 0.062442 | 0.069814 | 0.078073 | 0.087327 | 0.097698 | 0.10932 | 0.12235 | 0.13696 | 0.15333 | 0.16481 | 0.16481 | 0.16481 | 0.16481 |  | 0.0051427 | 0.0057188 | 0.0063621 | 0.0070807 | 0.0078837 | 0.008781 | 0.0097842 | 0.010906 | 0.01216 | 0.013563 | 0.015133 | 0.016889 | 0.018854 | 0.021054 | 0.023517 | 0.026275 | 0.029364 | 0.032823 | 0.036698 | 0.04104 | 0.045904 | 0.051356 | 0.057466 | 0.064314 | 0.071992 | 0.0806 | 0.086636 | 0.086636 | 0.086636 | 0.086636 | 9597.4462 | 10672.4637 | 11873.0364 | 13214.1611 | 14712.6503 | 16387.3547 | 18259.4122 | 20352.5271 | 22693.2852 | 25311.5058 | 28240.6383 | 31518.207 | 35186.3112 | 39292.1861 | 43888.8338 | 49035.7312 | 54799.6258 | 61255.4292 | 68487.2211 | 76589.3775 | 85667.8372 | 95841.5254 | 107243.9533 | 120025.0146 | 134353.0041 | 150416.8863 | 161682.2402 | 161682.2402 | 161682.2402 | 161682.2402 |  | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 41.5868 | 55.1257 | 73.7105 | 99.3367 | 134.8165 | 184.1202 | 252.8618 | 348.9914 | 483.781 | 673.2314 | 940.0792 | 1316.662 | 1849.0103 |  | 56.637 | 62.9809 | 70.0658 | 77.9801 | 86.8231 | 96.7059 | 107.7534 | 120.1054 | 133.9188 | 149.3696 | 166.6552 | 185.9969 | 207.6433 | 231.8731 | 258.9991 | 289.3723 | 323.3865 | 361.4838 | 404.1604 | 451.9733 | 505.5476 | 565.5851 | 632.8737 | 708.298 | 792.8511 | 887.6482 | 954.1279 | 954.1279 | 954.1279 | 954.1279 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 42.4246 | 48.7685 | 55.8534 | 63.7677 | 72.6107 | 82.4935 | 93.541 | 105.893 | 119.7064 | 135.1572 | 152.4428 | 171.7845 | 193.431 | 217.6608 | 244.7867 | 275.1599 | 309.1741 | 344.4725 | 381.6109 | 421.8215 | 464.9133 | 510.4375 | 557.5582 | 604.8632 | 650.0939 | 689.7544 | 678.7381 | 569.5823 | 415.5386 | 197.778 |  | 1439.9597 | 1601.2507 | 1781.3795 | 1982.5961 | 2207.423 | 2458.6885 | 2739.564 | 3053.606 | 3404.8033 | 3797.6299 | 4237.1044 | 4728.8568 | 5279.2034 | 5895.2313 | 6584.8927 | 7357.1111 | 8221.9012 | 9190.5023 | 10275.5294 | 11491.1422 | 12853.2354 | 14379.652 | 16090.4235 | 18008.0392 | 20157.7494 | 22567.9055 | 24258.1109 | 24258.1109 | 24258.1109 | 24258.1109 |  | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.68662 | 0.91016 | 1.217 | 1.6401 | 2.2259 | 3.0399 | 4.1749 | 5.7621 | 7.9875 | 11.1155 | 15.5213 | 21.7389 | 30.5284 |  | 1439.3861 | 1600.6771 | 1780.8059 | 1982.0225 | 2206.8494 | 2458.1149 | 2738.9904 | 3053.0324 | 3404.2297 | 3797.0563 | 4236.5308 | 4728.2832 | 5278.6298 | 5894.6577 | 6584.319 | 7356.5375 | 8221.3275 | 9189.8156 | 10274.6192 | 11489.9252 | 12851.5953 | 14377.4261 | 16087.3835 | 18003.8643 | 20151.9873 | 22559.9179 | 24246.9954 | 24242.5896 | 24236.372 | 24227.5826 |  | 1481.8106 | 1649.4456 | 1836.6593 | 2045.7902 | 2279.4601 | 2540.6084 | 2832.5314 | 3158.9254 | 3523.9361 | 3932.2135 | 4388.9736 | 4900.0677 | 5472.0607 | 6112.3184 | 6829.1058 | 7631.6974 | 8530.5016 | 9534.2881 | 10656.2301 | 11911.7467 | 13316.5086 | 14887.8637 | 16644.9417 | 18608.7275 | 20802.0812 | 23249.6723 | 24925.7336 | 24812.1719 | 24651.9106 | 24425.3606 |  | 56.9676 | 63.3486 | 70.4748 | 78.4353 | 87.3299 | 97.2704 | 108.3824 | 120.8065 | 134.7006 | 150.2415 | 167.628 | 187.0827 | 208.8554 | 233.2267 | 260.511 | 291.0615 | 325.2742 | 363.5939 | 406.5197 | 454.6117 | 508.4987 | 568.8867 | 636.5681 | 712.4326 | 797.4793 | 892.8297 | 959.6975 | 959.6975 | 959.6975 | 959.6975 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 42.2862 | 48.6671 | 55.7934 | 63.7539 | 72.6485 | 82.589 | 93.701 | 106.1251 | 120.0191 | 135.5601 | 152.9466 | 172.4012 | 194.174 | 218.5453 | 245.8296 | 276.38 | 310.5928 | 346.0212 | 383.226 | 423.4648 | 466.5233 | 511.9191 | 558.767 | 605.5843 | 650.0109 | 688.4051 | 675.2195 | 562.4613 | 403.334 | 178.3869 |  | 3.9657 | 4.41 | 4.906 | 5.4602 | 6.0794 | 6.7714 | 7.5449 | 8.4098 | 9.3771 | 10.4589 | 11.6693 | 13.0236 | 14.5393 | 16.2359 | 18.1353 | 20.262 | 22.6437 | 25.3113 | 28.2995 | 31.6474 | 35.3987 | 39.6026 | 44.3141 | 49.5954 | 55.5158 | 62.1536 | 66.8085 | 66.8085 | 66.8085 | 66.8085 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.898 | 2.3422 | 2.8383 | 3.3925 | 4.0117 | 4.7037 | 5.4772 | 6.3421 | 7.3094 | 8.3912 | 9.6016 | 10.9559 | 12.4716 | 14.1682 | 16.0675 | 18.1943 | 20.576 | 22.8364 | 25.0189 | 27.2607 | 29.4869 | 31.5793 | 33.3567 | 34.547 | 34.7466 | 33.3627 | 26.743 | 10.8623 | -11.549 | -43.2302 |  | 8039.9162 | 8940.4735 | 9946.2102 | 11069.6893 | 12324.9949 | 13727.9184 | 15296.1674 | 17049.5993 | 19010.4854 | 21203.8058 | 23657.5814 | 26403.247 | 29476.0697 | 32915.6191 | 36766.2958 | 41077.9244 | 45906.4202 | 51314.5379 | 57372.7121 | 64160.0029 | 71765.1567 | 80287.799 | 89839.7739 | 100546.6493 | 112549.4084 | 126006.3493 | 135443.4954 | 135443.4954 | 135443.4954 | 135443.4954 |  | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.8337 | 5.0818 | 6.7951 | 9.1575 | 12.4282 | 16.9733 | 23.3103 | 32.1721 | 44.5979 | 62.0625 | 86.6622 | 121.3779 | 170.453 |  | 8036.7132 | 8937.2706 | 9943.0073 | 11066.4864 | 12321.7919 | 13724.7155 | 15292.9644 | 17046.3964 | 19007.2825 | 21200.6029 | 23654.3785 | 26400.0441 | 29472.8667 | 32912.4161 | 36763.0928 | 41074.7215 | 45903.2173 | 51310.7042 | 57367.6303 | 64153.2078 | 71755.9993 | 80275.3708 | 89822.8006 | 100523.339 | 112517.2363 | 125961.7515 | 135381.4329 | 135356.8332 | 135322.1176 | 135273.0425 |  | 9562.708 | 10637.7256 | 11838.2983 | 13179.423 | 14677.9122 | 16352.6166 | 18224.674 | 20317.789 | 22658.5471 | 25276.7677 | 28205.9002 | 31483.4689 | 35151.5731 | 39257.448 | 43854.0957 | 49000.9931 | 54764.8877 | 61213.8498 | 68432.1053 | 76515.6801 | 85568.5181 | 95706.7329 | 107059.866 | 119772.1978 | 134004.0749 | 149933.1916 | 161009.129 | 160742.3288 | 160365.8131 | 159833.5597
| TRUE | 3674 | 22004137 | SA | Blank | 22 | CAP NO.1 | OVERCURRENT | X | English Electric | CDG11_521 | CDG11 521 | CDG11 | Electromechanical |  | 0.2894 | 2190 |  | 9.9 | 0.0088019 | 0.0046268 | 0.0041751 | 50.955 | 1295.4993 | 1346.4543 | 51.2524 | 3.5679 | 7233.3312 |  | 14.6263 | 0.025802 | 0.013563 | 0.012239 | 149.3696 | 3797.6299 | 3946.9995 | 150.2415 | 10.4589 | 21203.8058 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.57365 | 28.9984 | 14.6814 | 2.0677 | 3.2029 |  | 8634.6058 | 25311.5058 | 48.9505 | 25262.5553 |  | 0.039029 |  | 10.294 | 10.7037 | 11.1297 | 11.5727 | 12.0333 | 12.5122 | 13.0102 | 13.528 | 14.0664 | 14.6263 | 15.2084 | 15.8137 | 16.4431 | 17.0975 | 17.778 | 18.4856 | 19.2213 | 19.9863 | 20.7818 | 21.6089 | 22.4689 | 23.3632 | 24.2931 | 25.2599 | 26.2653 | 27.3106 | 28 | 28 | 28 | 28 |  | 0.0097834 | 0.010879 | 0.012103 | 0.01347 | 0.014998 | 0.016705 | 0.018613 | 0.020747 | 0.023133 | 0.025802 | 0.028788 | 0.032129 | 0.035868 | 0.040053 | 0.044739 | 0.049986 | 0.055861 | 0.062442 | 0.069814 | 0.078073 | 0.087327 | 0.097698 | 0.10932 | 0.12235 | 0.13696 | 0.15333 | 0.16481 | 0.16481 | 0.16481 | 0.16481 |  | 0.0051427 | 0.0057188 | 0.0063621 | 0.0070807 | 0.0078837 | 0.008781 | 0.0097842 | 0.010906 | 0.01216 | 0.013563 | 0.015133 | 0.016889 | 0.018854 | 0.021054 | 0.023517 | 0.026275 | 0.029364 | 0.032823 | 0.036698 | 0.04104 | 0.045904 | 0.051356 | 0.057466 | 0.064314 | 0.071992 | 0.0806 | 0.086636 | 0.086636 | 0.086636 | 0.086636 | 9597.4462 | 10672.4637 | 11873.0364 | 13214.1611 | 14712.6503 | 16387.3547 | 18259.4122 | 20352.5271 | 22693.2852 | 25311.5058 | 28240.6383 | 31518.207 | 35186.3112 | 39292.1861 | 43888.8338 | 49035.7312 | 54799.6258 | 61255.4292 | 68487.2211 | 76589.3775 | 85667.8372 | 95841.5254 | 107243.9533 | 120025.0146 | 134353.0041 | 150416.8863 | 161682.2402 | 161682.2402 | 161682.2402 | 161682.2402 |  | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 41.5868 | 55.1257 | 73.7105 | 99.3367 | 134.8165 | 184.1202 | 252.8618 | 348.9914 | 483.781 | 673.2314 | 940.0792 | 1316.662 | 1849.0103 |  | 56.637 | 62.9809 | 70.0658 | 77.9801 | 86.8231 | 96.7059 | 107.7534 | 120.1054 | 133.9188 | 149.3696 | 166.6552 | 185.9969 | 207.6433 | 231.8731 | 258.9991 | 289.3723 | 323.3865 | 361.4838 | 404.1604 | 451.9733 | 505.5476 | 565.5851 | 632.8737 | 708.298 | 792.8511 | 887.6482 | 954.1279 | 954.1279 | 954.1279 | 954.1279 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 42.4246 | 48.7685 | 55.8534 | 63.7677 | 72.6107 | 82.4935 | 93.541 | 105.893 | 119.7064 | 135.1572 | 152.4428 | 171.7845 | 193.431 | 217.6608 | 244.7867 | 275.1599 | 309.1741 | 344.4725 | 381.6109 | 421.8215 | 464.9133 | 510.4375 | 557.5582 | 604.8632 | 650.0939 | 689.7544 | 678.7381 | 569.5823 | 415.5386 | 197.778 |  | 1439.9597 | 1601.2507 | 1781.3795 | 1982.5961 | 2207.423 | 2458.6885 | 2739.564 | 3053.606 | 3404.8033 | 3797.6299 | 4237.1044 | 4728.8568 | 5279.2034 | 5895.2313 | 6584.8927 | 7357.1111 | 8221.9012 | 9190.5023 | 10275.5294 | 11491.1422 | 12853.2354 | 14379.652 | 16090.4235 | 18008.0392 | 20157.7494 | 22567.9055 | 24258.1109 | 24258.1109 | 24258.1109 | 24258.1109 |  | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.68662 | 0.91016 | 1.217 | 1.6401 | 2.2259 | 3.0399 | 4.1749 | 5.7621 | 7.9875 | 11.1155 | 15.5213 | 21.7389 | 30.5284 |  | 1439.3861 | 1600.6771 | 1780.8059 | 1982.0225 | 2206.8494 | 2458.1149 | 2738.9904 | 3053.0324 | 3404.2297 | 3797.0563 | 4236.5308 | 4728.2832 | 5278.6298 | 5894.6577 | 6584.319 | 7356.5375 | 8221.3275 | 9189.8156 | 10274.6192 | 11489.9252 | 12851.5953 | 14377.4261 | 16087.3835 | 18003.8643 | 20151.9873 | 22559.9179 | 24246.9954 | 24242.5896 | 24236.372 | 24227.5826 |  | 1481.8106 | 1649.4456 | 1836.6593 | 2045.7902 | 2279.4601 | 2540.6084 | 2832.5314 | 3158.9254 | 3523.9361 | 3932.2135 | 4388.9736 | 4900.0677 | 5472.0607 | 6112.3184 | 6829.1058 | 7631.6974 | 8530.5016 | 9534.2881 | 10656.2301 | 11911.7467 | 13316.5086 | 14887.8637 | 16644.9417 | 18608.7275 | 20802.0812 | 23249.6723 | 24925.7336 | 24812.1719 | 24651.9106 | 24425.3606 |  | 56.9676 | 63.3486 | 70.4748 | 78.4353 | 87.3299 | 97.2704 | 108.3824 | 120.8065 | 134.7006 | 150.2415 | 167.628 | 187.0827 | 208.8554 | 233.2267 | 260.511 | 291.0615 | 325.2742 | 363.5939 | 406.5197 | 454.6117 | 508.4987 | 568.8867 | 636.5681 | 712.4326 | 797.4793 | 892.8297 | 959.6975 | 959.6975 | 959.6975 | 959.6975 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 42.2862 | 48.6671 | 55.7934 | 63.7539 | 72.6485 | 82.589 | 93.701 | 106.1251 | 120.0191 | 135.5601 | 152.9466 | 172.4012 | 194.174 | 218.5453 | 245.8296 | 276.38 | 310.5928 | 346.0212 | 383.226 | 423.4648 | 466.5233 | 511.9191 | 558.767 | 605.5843 | 650.0109 | 688.4051 | 675.2195 | 562.4613 | 403.334 | 178.3869 |  | 3.9657 | 4.41 | 4.906 | 5.4602 | 6.0794 | 6.7714 | 7.5449 | 8.4098 | 9.3771 | 10.4589 | 11.6693 | 13.0236 | 14.5393 | 16.2359 | 18.1353 | 20.262 | 22.6437 | 25.3113 | 28.2995 | 31.6474 | 35.3987 | 39.6026 | 44.3141 | 49.5954 | 55.5158 | 62.1536 | 66.8085 | 66.8085 | 66.8085 | 66.8085 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 1.898 | 2.3422 | 2.8383 | 3.3925 | 4.0117 | 4.7037 | 5.4772 | 6.3421 | 7.3094 | 8.3912 | 9.6016 | 10.9559 | 12.4716 | 14.1682 | 16.0675 | 18.1943 | 20.576 | 22.8364 | 25.0189 | 27.2607 | 29.4869 | 31.5793 | 33.3567 | 34.547 | 34.7466 | 33.3627 | 26.743 | 10.8623 | -11.549 | -43.2302 |  | 8039.9162 | 8940.4735 | 9946.2102 | 11069.6893 | 12324.9949 | 13727.9184 | 15296.1674 | 17049.5993 | 19010.4854 | 21203.8058 | 23657.5814 | 26403.247 | 29476.0697 | 32915.6191 | 36766.2958 | 41077.9244 | 45906.4202 | 51314.5379 | 57372.7121 | 64160.0029 | 71765.1567 | 80287.799 | 89839.7739 | 100546.6493 | 112549.4084 | 126006.3493 | 135443.4954 | 135443.4954 | 135443.4954 | 135443.4954 |  | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.8337 | 5.0818 | 6.7951 | 9.1575 | 12.4282 | 16.9733 | 23.3103 | 32.1721 | 44.5979 | 62.0625 | 86.6622 | 121.3779 | 170.453 |  | 8036.7132 | 8937.2706 | 9943.0073 | 11066.4864 | 12321.7919 | 13724.7155 | 15292.9644 | 17046.3964 | 19007.2825 | 21200.6029 | 23654.3785 | 26400.0441 | 29472.8667 | 32912.4161 | 36763.0928 | 41074.7215 | 45903.2173 | 51310.7042 | 57367.6303 | 64153.2078 | 71755.9993 | 80275.3708 | 89822.8006 | 100523.339 | 112517.2363 | 125961.7515 | 135381.4329 | 135356.8332 | 135322.1176 | 135273.0425 |  | 9562.708 | 10637.7256 | 11838.2983 | 13179.423 | 14677.9122 | 16352.6166 | 18224.674 | 20317.789 | 22658.5471 | 25276.7677 | 28205.9002 | 31483.4689 | 35151.5731 | 39257.448 | 43854.0957 | 49000.9931 | 54764.8877 | 61213.8498 | 68432.1053 | 76515.6801 | 85568.5181 | 95706.7329 | 107059.866 | 119772.1978 | 134004.0749 | 149933.1916 | 161009.129 | 160742.3288 | 160365.8131 | 159833.5597
| TRUE | 3675 | 22004138 | SA | Blank | 22 | CAP NO.1 | CURRENT BALANCE | C | ASEA | RRIL_2099 | RRIL 2099 | RRIL | Electronic |  | 0.2894 | 2190 |  | 5.5 | 0.0093284 | 0.0049035 | 0.0044248 | 54.003 | 1372.9933 | 1426.9963 | 54.3183 | 3.7813 | 7666.0136 |  | 7.7282 | 0.022137 | 0.011637 | 0.010501 | 128.1554 | 3258.273 | 3386.4284 | 128.9035 | 8.9735 | 18192.3434 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.57365 | 28.9984 | 14.6814 | 2.0677 | 3.2029 |  | 9151.1095 | 21716.6489 | 48.9505 | 21667.6984 |  | 0.034013 |  | 5.6903 | 5.8872 | 6.0908 | 6.3016 | 6.5196 | 6.7452 | 6.9785 | 7.22 | 7.4698 | 7.7282 | 7.9956 | 8.2722 | 8.5584 | 8.8545 | 9.1608 | 9.4778 | 9.8057 | 10.145 | 10.4959 | 10.8591 | 11.2348 | 11.6235 | 12.0256 | 12.4417 | 12.8721 | 13.3175 | 13.7782 | 14.2549 | 14.7481 | 15.2584 |  | 0.010145 | 0.011039 | 0.012019 | 0.013094 | 0.014274 | 0.015567 | 0.016987 | 0.018546 | 0.020257 | 0.022137 | 0.024203 | 0.026473 | 0.028968 | 0.031712 | 0.034729 | 0.038048 | 0.0417 | 0.045719 | 0.050142 | 0.055012 | 0.060375 | 0.066281 | 0.072786 | 0.079954 | 0.087852 | 0.096556 | 0.10615 | 0.11673 | 0.12839 | 0.14125 |  | 0.0053326 | 0.0058028 | 0.0063181 | 0.0068832 | 0.007503 | 0.0081831 | 0.0089294 | 0.0097487 | 0.010648 | 0.011637 | 0.012722 | 0.013916 | 0.015227 | 0.01667 | 0.018256 | 0.02 | 0.02192 | 0.024032 | 0.026358 | 0.028918 | 0.031736 | 0.034841 | 0.038261 | 0.042028 | 0.04618 | 0.050756 | 0.055799 | 0.061359 | 0.06749 | 0.074251 | 9951.8515 | 10829.283 | 11791.067 | 12845.6524 | 14002.3552 | 15271.4496 | 16664.2672 | 18193.3083 | 19872.3634 | 21716.6489 | 23742.9558 | 25969.8152 | 28417.6809 | 31109.1311 | 34069.0915 | 37325.0824 | 40907.4918 | 44849.8771 | 49189.299 | 53966.6913 | 59227.269 | 65020.9805 | 71403.0075 | 78434.3182 | 86182.2788 | 94721.3306 | 104133.7387 | 114510.4209 | 125951.8639 | 138569.1379 |  | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 41.5868 | 55.1257 | 73.7105 | 99.3367 | 134.8165 | 184.1202 | 252.8618 | 348.9914 | 483.781 | 673.2314 | 940.0792 | 1316.662 | 1849.0103 |  | 58.7284 | 63.9063 | 69.5821 | 75.8054 | 82.6314 | 90.1207 | 98.3401 | 107.3633 | 117.2719 | 128.1554 | 140.1132 | 153.2545 | 167.6999 | 183.5829 | 201.0503 | 220.2648 | 241.4055 | 264.6705 | 290.2785 | 318.4711 | 349.5151 | 383.7053 | 421.3672 | 462.8608 | 508.5835 | 558.9746 | 614.5196 | 675.755 | 743.2739 | 817.7316 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 44.516 | 49.694 | 55.3697 | 61.5931 | 68.4191 | 75.9083 | 84.1277 | 93.1509 | 103.0595 | 113.9431 | 125.9008 | 139.0421 | 153.4875 | 169.3705 | 186.838 | 206.0524 | 227.1931 | 247.6592 | 267.729 | 288.3193 | 308.8808 | 328.5577 | 346.0517 | 359.426 | 365.8262 | 361.0808 | 339.1299 | 291.2094 | 204.6846 | 61.3817 |  | 1493.1332 | 1624.7792 | 1769.0812 | 1927.3067 | 2100.8534 | 2291.2629 | 2500.2353 | 2729.6461 | 2981.5643 | 3258.273 | 3562.2914 | 3896.3999 | 4263.6672 | 4667.4808 | 5111.5806 | 5600.0955 | 6137.5849 | 6729.0835 | 7380.1518 | 8096.9313 | 8886.2058 | 9755.4695 | 10713.0015 | 11767.9492 | 12930.42 | 14211.5828 | 15623.7802 | 17180.6532 | 18897.2783 | 20790.32 |  | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.68662 | 0.91016 | 1.217 | 1.6401 | 2.2259 | 3.0399 | 4.1749 | 5.7621 | 7.9875 | 11.1155 | 15.5213 | 21.7389 | 30.5284 |  | 1492.5595 | 1624.2056 | 1768.5075 | 1926.733 | 2100.2798 | 2290.6892 | 2499.6616 | 2729.0724 | 2980.9907 | 3257.6993 | 3561.7178 | 3895.8262 | 4263.0935 | 4666.9072 | 5111.0069 | 5599.5219 | 6137.0112 | 6728.3969 | 7379.2416 | 8095.7142 | 8884.5657 | 9753.2436 | 10709.9615 | 11763.7743 | 12924.658 | 14203.5953 | 15612.6647 | 17165.1318 | 18875.5393 | 20759.7917 |  | 1537.0755 | 1673.8995 | 1823.8772 | 1988.3261 | 2168.6988 | 2366.5976 | 2583.7893 | 2822.2233 | 3084.0501 | 3371.6424 | 3687.6186 | 4034.8683 | 4416.5811 | 4836.2776 | 5297.8449 | 5805.5743 | 6364.2043 | 6976.056 | 7646.9706 | 8384.0336 | 9193.4465 | 10081.8012 | 11056.0132 | 12123.2003 | 13290.4842 | 14564.676 | 15951.7946 | 17456.3413 | 19080.2239 | 20821.1734 |  | 59.0712 | 64.2794 | 69.9883 | 76.248 | 83.1138 | 90.6468 | 98.9141 | 107.99 | 117.9564 | 128.9035 | 140.9311 | 154.1491 | 168.6789 | 184.6545 | 202.224 | 221.5505 | 242.8147 | 266.2155 | 291.973 | 320.3302 | 351.5554 | 385.9451 | 423.8269 | 465.5627 | 511.5523 | 562.2375 | 618.1068 | 679.6997 | 747.6126 | 822.505 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 44.3898 | 49.598 | 55.3068 | 61.5665 | 68.4324 | 75.9653 | 84.2327 | 93.3086 | 103.275 | 114.2221 | 126.2497 | 139.4676 | 153.9974 | 169.9731 | 187.5425 | 206.8691 | 228.1332 | 248.6427 | 268.6793 | 289.1833 | 309.58 | 328.9776 | 346.0258 | 358.7144 | 364.0838 | 357.8129 | 333.6288 | 282.4635 | 191.2491 | 41.1945 |  | 4.1122 | 4.4748 | 4.8722 | 5.3079 | 5.7859 | 6.3103 | 6.8858 | 7.5176 | 8.2114 | 8.9735 | 9.8108 | 10.731 | 11.7424 | 12.8546 | 14.0776 | 15.4231 | 16.9033 | 18.5324 | 20.3254 | 22.2995 | 24.4732 | 26.8672 | 29.5043 | 32.4097 | 35.6113 | 39.1397 | 43.029 | 47.3167 | 52.0444 | 57.258 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 2.0445 | 2.407 | 2.8045 | 3.2402 | 3.7182 | 4.2426 | 4.8181 | 5.4499 | 6.1437 | 6.9058 | 7.7431 | 8.6632 | 9.6747 | 10.7869 | 12.0099 | 13.3553 | 14.8356 | 16.0574 | 17.0448 | 17.9128 | 18.5615 | 18.844 | 18.5469 | 17.3614 | 14.842 | 10.3488 | 2.9635 | -8.6295 | -26.3131 | -52.7808 |  | 8336.8065 | 9071.8432 | 9877.5433 | 10760.9844 | 11729.9707 | 12793.1089 | 13959.8919 | 15240.7912 | 16647.3594 | 18192.3434 | 19889.8093 | 21755.2809 | 23805.8926 | 26060.5583 | 28540.1589 | 31267.7485 | 34268.7835 | 37571.3753 | 41206.5703 | 45208.6592 | 49615.5194 | 54468.9934 | 59815.3076 | 65705.5358 | 72196.1118 | 79349.396 | 87234.3032 | 95926.9963 | 105511.6547 | 116081.3232 |  | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.8337 | 5.0818 | 6.7951 | 9.1575 | 12.4282 | 16.9733 | 23.3103 | 32.1721 | 44.5979 | 62.0625 | 86.6622 | 121.3779 | 170.453 |  | 8333.6036 | 9068.6403 | 9874.3404 | 10757.7814 | 11726.7677 | 12789.906 | 13956.689 | 15237.5883 | 16644.1565 | 18189.1404 | 19886.6063 | 21752.0779 | 23802.6896 | 26057.3554 | 28536.956 | 31264.5456 | 34265.5805 | 37567.5415 | 41201.4885 | 45201.8642 | 49606.362 | 54456.5652 | 59798.3342 | 65682.2255 | 72163.9396 | 79304.7981 | 87172.2406 | 95840.3341 | 105390.2768 | 115910.8703 |  | 9917.1134 | 10794.5449 | 11756.3289 | 12810.9143 | 13967.6171 | 15236.7115 | 16629.5291 | 18158.5702 | 19837.6253 | 21681.9108 | 23708.2177 | 25935.0771 | 28382.9428 | 31074.393 | 34034.3534 | 37290.3443 | 40872.7537 | 44808.2977 | 49134.1831 | 53892.9939 | 59127.9499 | 64886.188 | 71218.9202 | 78181.5015 | 85833.3497 | 94237.6359 | 103460.6274 | 113570.5094 | 124635.4367 | 136720.4573
| TRUE | 3676 | 22004139 | SA | Blank | 22 | CAP NO.1 | CURRENT BALANCE | C | ASEA | RRIL_2099 | RRIL 2099 | RRIL | Electronic |  | 0.2894 | 2190 |  | 5.5 | 0.0093284 | 0.0049035 | 0.0044248 | 54.003 | 1372.9933 | 1426.9963 | 54.3183 | 3.7813 | 7666.0136 |  | 7.5248 | 0.020648 | 0.010854 | 0.0097942 | 119.5336 | 3039.0672 | 3158.6007 | 120.2313 | 8.3698 | 16968.4226 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.57365 | 28.9984 | 14.6814 | 2.0677 | 3.2029 |  | 9151.1095 | 20255.6245 | 48.9505 | 20206.674 |  | 0.031345 |  | 5.6751 | 5.8558 | 6.0423 | 6.2347 | 6.4332 | 6.6381 | 6.8494 | 7.0675 | 7.2926 | 7.5248 | 7.7644 | 8.0116 | 8.2667 | 8.5299 | 8.8015 | 9.0818 | 9.3709 | 9.6693 | 9.9772 | 10.2949 | 10.6227 | 10.9609 | 11.31 | 11.6701 | 12.0417 | 12.4251 | 12.8207 | 13.229 | 13.6502 | 14.0848 |  | 0.010078 | 0.010893 | 0.011781 | 0.012746 | 0.013798 | 0.014944 | 0.016191 | 0.017551 | 0.019033 | 0.020648 | 0.022409 | 0.024331 | 0.026426 | 0.028713 | 0.031208 | 0.033932 | 0.036906 | 0.040154 | 0.043701 | 0.047575 | 0.051808 | 0.056433 | 0.061488 | 0.067014 | 0.073054 | 0.079659 | 0.086882 | 0.094782 | 0.10342 | 0.11288 |  | 0.0052975 | 0.0057262 | 0.0061926 | 0.0067003 | 0.0072531 | 0.0078552 | 0.0085111 | 0.0092257 | 0.010005 | 0.010854 | 0.01178 | 0.01279 | 0.013891 | 0.015093 | 0.016405 | 0.017837 | 0.0194 | 0.021107 | 0.022972 | 0.025008 | 0.027233 | 0.029665 | 0.032322 | 0.035226 | 0.038402 | 0.041874 | 0.04567 | 0.049823 | 0.054365 | 0.059335 | 9886.3713 | 10686.2728 | 11556.7425 | 12504.2664 | 13535.9415 | 14659.5347 | 15883.5462 | 17217.2804 | 18670.9227 | 20255.6245 | 21983.5953 | 23868.2055 | 25924.0972 | 28167.307 | 30615.4007 | 33287.6203 | 36205.0462 | 39390.7744 | 42870.1113 | 46670.7879 | 50823.1937 | 55360.6346 | 60319.6149 | 65740.1478 | 71666.0951 | 78145.541 | 85231.2015 | 92980.8746 | 101457.9336 | 110731.8693 |  | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 41.5868 | 55.1257 | 73.7105 | 99.3367 | 134.8165 | 184.1202 | 252.8618 | 348.9914 | 483.781 | 673.2314 | 940.0792 | 1316.662 | 1849.0103 |  | 58.342 | 63.0624 | 68.1993 | 73.7908 | 79.879 | 86.5096 | 93.7328 | 101.6035 | 110.1818 | 119.5336 | 129.7308 | 140.8523 | 152.9847 | 166.2224 | 180.6692 | 196.4387 | 213.6552 | 232.4549 | 252.9874 | 275.4161 | 299.9205 | 326.6971 | 355.9613 | 387.9493 | 422.9198 | 461.1566 | 502.9709 | 548.7037 | 598.729 | 653.4568 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 44.1296 | 48.85 | 53.9869 | 59.5785 | 65.6666 | 72.2972 | 79.5204 | 87.3911 | 95.9695 | 105.3212 | 115.5184 | 126.6399 | 138.7723 | 152.01 | 166.4569 | 182.2263 | 199.4428 | 215.4436 | 230.4379 | 245.2644 | 259.2862 | 271.5495 | 280.6457 | 284.5145 | 280.1625 | 263.2628 | 227.5812 | 164.1581 | 60.1397 | -102.8931 |  | 1483.3088 | 1603.3226 | 1733.9242 | 1876.0866 | 2030.8747 | 2199.4538 | 2383.0993 | 2583.207 | 2801.3053 | 3039.0672 | 3298.3245 | 3581.0833 | 3889.5405 | 4226.1021 | 4593.4036 | 4994.332 | 5432.0501 | 5910.0231 | 6432.0479 | 7002.2851 | 7625.2943 | 8306.0725 | 9050.0967 | 9863.3702 | 10752.474 | 11724.6223 | 12787.7245 | 13950.4522 | 15222.3139 | 16613.7355 |  | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.68662 | 0.91016 | 1.217 | 1.6401 | 2.2259 | 3.0399 | 4.1749 | 5.7621 | 7.9875 | 11.1155 | 15.5213 | 21.7389 | 30.5284 |  | 1482.7352 | 1602.749 | 1733.3505 | 1875.5129 | 2030.3011 | 2198.8802 | 2382.5256 | 2582.6334 | 2800.7316 | 3038.4935 | 3297.7509 | 3580.5097 | 3888.9669 | 4225.5285 | 4592.83 | 4993.7584 | 5431.4764 | 5909.3365 | 6431.1378 | 7001.0681 | 7623.6542 | 8303.8466 | 9047.0568 | 9859.1953 | 10746.7119 | 11716.6348 | 12776.609 | 13934.9309 | 15200.5749 | 16583.2071 |  | 1526.8647 | 1651.599 | 1787.3374 | 1935.0914 | 2095.9677 | 2271.1774 | 2462.046 | 2670.0245 | 2896.7011 | 3143.8147 | 3413.2692 | 3707.1496 | 4027.7392 | 4377.5385 | 4759.2868 | 5175.9846 | 5630.9192 | 6124.7801 | 6661.5756 | 7246.3325 | 7882.9404 | 8575.3962 | 9327.7025 | 10143.7098 | 11026.8745 | 11979.8976 | 13004.1902 | 14099.089 | 15260.7146 | 16480.3141 |  | 58.6825 | 63.4305 | 68.5974 | 74.2216 | 80.3453 | 87.0146 | 94.28 | 102.1966 | 110.825 | 120.2313 | 130.4881 | 141.6745 | 153.8777 | 167.1927 | 181.7239 | 197.5854 | 214.9023 | 233.8119 | 254.4642 | 277.0239 | 301.6713 | 328.6042 | 358.0392 | 390.2139 | 425.3885 | 463.8486 | 505.907 | 551.9067 | 602.224 | 657.2713 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 44.0011 | 48.7491 | 53.916 | 59.5402 | 65.6639 | 72.3332 | 79.5986 | 87.5152 | 96.1436 | 105.5499 | 115.8066 | 126.9931 | 139.1963 | 152.5113 | 167.0425 | 182.904 | 200.2209 | 216.2391 | 231.1705 | 245.877 | 259.696 | 271.6366 | 280.2381 | 283.3656 | 277.9201 | 259.424 | 221.429 | 154.6705 | 45.8605 | -124.0392 |  | 4.0851 | 4.4157 | 4.7753 | 5.1669 | 5.5932 | 6.0574 | 6.5632 | 7.1143 | 7.715 | 8.3698 | 9.0838 | 9.8626 | 10.7121 | 11.639 | 12.6506 | 13.7547 | 14.9602 | 16.2766 | 17.7143 | 19.2848 | 21.0006 | 22.8755 | 24.9246 | 27.1644 | 29.6131 | 32.2904 | 35.2183 | 38.4205 | 41.9233 | 45.7554 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 2.0174 | 2.3479 | 2.7076 | 3.0992 | 3.5255 | 3.9897 | 4.4955 | 5.0466 | 5.6473 | 6.3021 | 7.0161 | 7.7948 | 8.6444 | 9.5713 | 10.5828 | 11.687 | 12.8925 | 13.8017 | 14.4337 | 14.8981 | 15.0888 | 14.8523 | 13.9672 | 12.116 | 8.8438 | 3.4995 | -4.8472 | -17.5257 | -36.4342 | -64.2834 |  | 8281.9528 | 8952.0416 | 9681.2464 | 10475.0005 | 11339.2493 | 12280.4992 | 13305.8709 | 14423.1589 | 15640.8956 | 16968.4226 | 18415.9682 | 19994.7328 | 21716.9822 | 23596.1508 | 25646.9534 | 27885.5095 | 30329.4784 | 32998.2078 | 35912.8975 | 39096.778 | 42575.3069 | 46376.3852 | 50530.593 | 55071.45 | 60035.6997 | 65463.623 | 71399.3809 | 77891.3915 | 84992.7435 | 92761.6503 |  | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.8337 | 5.0818 | 6.7951 | 9.1575 | 12.4282 | 16.9733 | 23.3103 | 32.1721 | 44.5979 | 62.0625 | 86.6622 | 121.3779 | 170.453 |  | 8278.7498 | 8948.8387 | 9678.0434 | 10471.7975 | 11336.0464 | 12277.2963 | 13302.668 | 14419.9559 | 15637.6927 | 16965.2197 | 18412.7653 | 19991.5298 | 21713.7793 | 23592.9478 | 25643.7505 | 27882.3066 | 30326.2754 | 32994.3741 | 35907.8157 | 39089.9829 | 42566.1495 | 46363.957 | 50513.6197 | 55048.1396 | 60003.5276 | 65419.0252 | 71337.3184 | 77804.7293 | 84871.3656 | 92591.1973 |  | 9851.6332 | 10651.5347 | 11522.0044 | 12469.5282 | 13501.2034 | 14624.7966 | 15848.8081 | 17182.5423 | 18636.1846 | 20220.8864 | 21948.8572 | 23833.4674 | 25889.3591 | 28132.5689 | 30580.6626 | 33252.8822 | 36170.3081 | 39349.195 | 42814.9954 | 46597.0905 | 50723.8747 | 55225.8421 | 60135.5275 | 65487.331 | 71317.1659 | 77661.8463 | 84558.0903 | 92040.9632 | 100141.5065 | 108883.1888
| TRUE | 3677 | 22004140 | SA | Blank | 22 | CAP NO.1 | CURRENT BALANCE | C | ASEA | RRIL_2099 | RRIL 2099 | RRIL | Electronic |  | 0.2894 | 2190 |  | 5.5 | 0.0093284 | 0.0049035 | 0.0044248 | 54.003 | 1372.9933 | 1426.9963 | 54.3183 | 3.7813 | 7666.0136 |  | 7.5248 | 0.020648 | 0.010854 | 0.0097942 | 119.5336 | 3039.0672 | 3158.6007 | 120.2313 | 8.3698 | 16968.4226 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.57365 | 28.9984 | 14.6814 | 2.0677 | 3.2029 |  | 9151.1095 | 20255.6245 | 48.9505 | 20206.674 |  | 0.031345 |  | 5.6751 | 5.8558 | 6.0423 | 6.2347 | 6.4332 | 6.6381 | 6.8494 | 7.0675 | 7.2926 | 7.5248 | 7.7644 | 8.0116 | 8.2667 | 8.5299 | 8.8015 | 9.0818 | 9.3709 | 9.6693 | 9.9772 | 10.2949 | 10.6227 | 10.9609 | 11.31 | 11.6701 | 12.0417 | 12.4251 | 12.8207 | 13.229 | 13.6502 | 14.0848 |  | 0.010078 | 0.010893 | 0.011781 | 0.012746 | 0.013798 | 0.014944 | 0.016191 | 0.017551 | 0.019033 | 0.020648 | 0.022409 | 0.024331 | 0.026426 | 0.028713 | 0.031208 | 0.033932 | 0.036906 | 0.040154 | 0.043701 | 0.047575 | 0.051808 | 0.056433 | 0.061488 | 0.067014 | 0.073054 | 0.079659 | 0.086882 | 0.094782 | 0.10342 | 0.11288 |  | 0.0052975 | 0.0057262 | 0.0061926 | 0.0067003 | 0.0072531 | 0.0078552 | 0.0085111 | 0.0092257 | 0.010005 | 0.010854 | 0.01178 | 0.01279 | 0.013891 | 0.015093 | 0.016405 | 0.017837 | 0.0194 | 0.021107 | 0.022972 | 0.025008 | 0.027233 | 0.029665 | 0.032322 | 0.035226 | 0.038402 | 0.041874 | 0.04567 | 0.049823 | 0.054365 | 0.059335 | 9886.3713 | 10686.2728 | 11556.7425 | 12504.2664 | 13535.9415 | 14659.5347 | 15883.5462 | 17217.2804 | 18670.9227 | 20255.6245 | 21983.5953 | 23868.2055 | 25924.0972 | 28167.307 | 30615.4007 | 33287.6203 | 36205.0462 | 39390.7744 | 42870.1113 | 46670.7879 | 50823.1937 | 55360.6346 | 60319.6149 | 65740.1478 | 71666.0951 | 78145.541 | 85231.2015 | 92980.8746 | 101457.9336 | 110731.8693 |  | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 34.7443 | 41.5868 | 55.1257 | 73.7105 | 99.3367 | 134.8165 | 184.1202 | 252.8618 | 348.9914 | 483.781 | 673.2314 | 940.0792 | 1316.662 | 1849.0103 |  | 58.342 | 63.0624 | 68.1993 | 73.7908 | 79.879 | 86.5096 | 93.7328 | 101.6035 | 110.1818 | 119.5336 | 129.7308 | 140.8523 | 152.9847 | 166.2224 | 180.6692 | 196.4387 | 213.6552 | 232.4549 | 252.9874 | 275.4161 | 299.9205 | 326.6971 | 355.9613 | 387.9493 | 422.9198 | 461.1566 | 502.9709 | 548.7037 | 598.729 | 653.4568 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 44.1296 | 48.85 | 53.9869 | 59.5785 | 65.6666 | 72.2972 | 79.5204 | 87.3911 | 95.9695 | 105.3212 | 115.5184 | 126.6399 | 138.7723 | 152.01 | 166.4569 | 182.2263 | 199.4428 | 215.4436 | 230.4379 | 245.2644 | 259.2862 | 271.5495 | 280.6457 | 284.5145 | 280.1625 | 263.2628 | 227.5812 | 164.1581 | 60.1397 | -102.8931 |  | 1483.3088 | 1603.3226 | 1733.9242 | 1876.0866 | 2030.8747 | 2199.4538 | 2383.0993 | 2583.207 | 2801.3053 | 3039.0672 | 3298.3245 | 3581.0833 | 3889.5405 | 4226.1021 | 4593.4036 | 4994.332 | 5432.0501 | 5910.0231 | 6432.0479 | 7002.2851 | 7625.2943 | 8306.0725 | 9050.0967 | 9863.3702 | 10752.474 | 11724.6223 | 12787.7245 | 13950.4522 | 15222.3139 | 16613.7355 |  | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.68662 | 0.91016 | 1.217 | 1.6401 | 2.2259 | 3.0399 | 4.1749 | 5.7621 | 7.9875 | 11.1155 | 15.5213 | 21.7389 | 30.5284 |  | 1482.7352 | 1602.749 | 1733.3505 | 1875.5129 | 2030.3011 | 2198.8802 | 2382.5256 | 2582.6334 | 2800.7316 | 3038.4935 | 3297.7509 | 3580.5097 | 3888.9669 | 4225.5285 | 4592.83 | 4993.7584 | 5431.4764 | 5909.3365 | 6431.1378 | 7001.0681 | 7623.6542 | 8303.8466 | 9047.0568 | 9859.1953 | 10746.7119 | 11716.6348 | 12776.609 | 13934.9309 | 15200.5749 | 16583.2071 |  | 1526.8647 | 1651.599 | 1787.3374 | 1935.0914 | 2095.9677 | 2271.1774 | 2462.046 | 2670.0245 | 2896.7011 | 3143.8147 | 3413.2692 | 3707.1496 | 4027.7392 | 4377.5385 | 4759.2868 | 5175.9846 | 5630.9192 | 6124.7801 | 6661.5756 | 7246.3325 | 7882.9404 | 8575.3962 | 9327.7025 | 10143.7098 | 11026.8745 | 11979.8976 | 13004.1902 | 14099.089 | 15260.7146 | 16480.3141 |  | 58.6825 | 63.4305 | 68.5974 | 74.2216 | 80.3453 | 87.0146 | 94.28 | 102.1966 | 110.825 | 120.2313 | 130.4881 | 141.6745 | 153.8777 | 167.1927 | 181.7239 | 197.5854 | 214.9023 | 233.8119 | 254.4642 | 277.0239 | 301.6713 | 328.6042 | 358.0392 | 390.2139 | 425.3885 | 463.8486 | 505.907 | 551.9067 | 602.224 | 657.2713 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 44.0011 | 48.7491 | 53.916 | 59.5402 | 65.6639 | 72.3332 | 79.5986 | 87.5152 | 96.1436 | 105.5499 | 115.8066 | 126.9931 | 139.1963 | 152.5113 | 167.0425 | 182.904 | 200.2209 | 216.2391 | 231.1705 | 245.877 | 259.696 | 271.6366 | 280.2381 | 283.3656 | 277.9201 | 259.424 | 221.429 | 154.6705 | 45.8605 | -124.0392 |  | 4.0851 | 4.4157 | 4.7753 | 5.1669 | 5.5932 | 6.0574 | 6.5632 | 7.1143 | 7.715 | 8.3698 | 9.0838 | 9.8626 | 10.7121 | 11.639 | 12.6506 | 13.7547 | 14.9602 | 16.2766 | 17.7143 | 19.2848 | 21.0006 | 22.8755 | 24.9246 | 27.1644 | 29.6131 | 32.2904 | 35.2183 | 38.4205 | 41.9233 | 45.7554 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 2.0174 | 2.3479 | 2.7076 | 3.0992 | 3.5255 | 3.9897 | 4.4955 | 5.0466 | 5.6473 | 6.3021 | 7.0161 | 7.7948 | 8.6444 | 9.5713 | 10.5828 | 11.687 | 12.8925 | 13.8017 | 14.4337 | 14.8981 | 15.0888 | 14.8523 | 13.9672 | 12.116 | 8.8438 | 3.4995 | -4.8472 | -17.5257 | -36.4342 | -64.2834 |  | 8281.9528 | 8952.0416 | 9681.2464 | 10475.0005 | 11339.2493 | 12280.4992 | 13305.8709 | 14423.1589 | 15640.8956 | 16968.4226 | 18415.9682 | 19994.7328 | 21716.9822 | 23596.1508 | 25646.9534 | 27885.5095 | 30329.4784 | 32998.2078 | 35912.8975 | 39096.778 | 42575.3069 | 46376.3852 | 50530.593 | 55071.45 | 60035.6997 | 65463.623 | 71399.3809 | 77891.3915 | 84992.7435 | 92761.6503 |  | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.2029 | 3.8337 | 5.0818 | 6.7951 | 9.1575 | 12.4282 | 16.9733 | 23.3103 | 32.1721 | 44.5979 | 62.0625 | 86.6622 | 121.3779 | 170.453 |  | 8278.7498 | 8948.8387 | 9678.0434 | 10471.7975 | 11336.0464 | 12277.2963 | 13302.668 | 14419.9559 | 15637.6927 | 16965.2197 | 18412.7653 | 19991.5298 | 21713.7793 | 23592.9478 | 25643.7505 | 27882.3066 | 30326.2754 | 32994.3741 | 35907.8157 | 39089.9829 | 42566.1495 | 46363.957 | 50513.6197 | 55048.1396 | 60003.5276 | 65419.0252 | 71337.3184 | 77804.7293 | 84871.3656 | 92591.1973 |  | 9851.6332 | 10651.5347 | 11522.0044 | 12469.5282 | 13501.2034 | 14624.7966 | 15848.8081 | 17182.5423 | 18636.1846 | 20220.8864 | 21948.8572 | 23833.4674 | 25889.3591 | 28132.5689 | 30580.6626 | 33252.8822 | 36170.3081 | 39349.195 | 42814.9954 | 46597.0905 | 50723.8747 | 55225.8421 | 60135.5275 | 65487.331 | 71317.1659 | 77661.8463 | 84558.0903 | 92040.9632 | 100141.5065 | 108883.1888
| TRUE | 3678 | 22009897 | SA | Blank | 22 | CB BT1-2 | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 2.6788 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 7.9912 | 0.028405 | 0 | 0.028405 | 78.1138 | 0 | 78.1138 | 80.631 | 11.3649 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 170.1097 | 30.9493 | 139.1604 |  | 0.1093 |  | 2.9882 | 3.3333 | 3.7183 | 4.1477 | 4.6268 | 5.1611 | 5.7572 | 6.4221 | 7.1638 | 7.9912 | 8.9141 | 9.9436 | 11.092 | 12.373 | 13.802 | 15.3961 | 17.1742 | 19.1577 | 21.3702 | 23.8383 | 26.5915 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0056115 | 0.007231 | 0.0093884 | 0.012274 | 0.016146 | 0.021361 | 0.028405 | 0.037944 | 0.050895 | 0.068518 | 0.092545 | 0.12536 | 0.17026 | 0.23179 | 0.31619 | 0.43213 | 0.59157 | 0.81102 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 33.606 | 43.3043 | 56.2243 | 73.5036 | 96.696 | 127.9273 | 170.1097 | 227.238 | 304.7987 | 410.3342 | 554.2243 | 750.765 | 1019.6616 | 1388.0949 | 1893.5808 | 2587.9296 | 3542.7291 | 4856.9407 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 15.4318 | 19.8852 | 25.818 | 33.7526 | 44.4025 | 58.7438 | 78.1138 | 104.347 | 139.9626 | 188.4242 | 254.4981 | 344.749 | 468.2255 | 637.4089 | 869.5265 | 1188.3693 | 1626.8103 | 2230.2923 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 1.2199 | 5.6734 | 11.6062 | 19.5408 | 30.1907 | 44.532 | 63.902 | 90.1352 | 125.7508 | 174.2124 | 240.2863 | 330.5371 | 454.0136 | 623.1971 | 852.5158 | 1165.8207 | 1596.6597 | 2189.6595 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1.2199 | 5.6734 | 11.6062 | 19.5408 | 30.1907 | 44.532 | 63.902 | 90.1352 | 125.7508 | 174.2124 | 240.2863 | 330.5371 | 454.0136 | 623.1971 | 852.5158 | 1165.8207 | 1596.6597 | 2189.6595 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 15.929 | 20.526 | 26.65 | 34.8403 | 45.8333 | 60.6368 | 80.631 | 107.7095 | 144.4728 | 194.496 | 262.6991 | 355.8582 | 483.3136 | 657.9488 | 897.5461 | 1226.6633 | 1679.2327 | 2302.1612 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 1.2592 | 5.8562 | 11.9802 | 20.1705 | 31.1635 | 45.967 | 65.9612 | 93.0397 | 129.803 | 179.8262 | 248.0293 | 341.1884 | 468.6438 | 643.279 | 879.9873 | 1203.3881 | 1648.1105 | 2260.2191 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.2452 | 2.8931 | 3.7563 | 4.9107 | 6.4602 | 8.5467 | 11.3649 | 15.1815 | 20.3633 | 27.414 | 37.0272 | 50.1578 | 68.1225 | 92.7372 | 126.5082 | 172.8969 | 236.6861 | 324.4872 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0.17749 | 0.82543 | 1.6886 | 2.843 | 4.3925 | 6.479 | 9.2972 | 13.1138 | 18.2956 | 25.3463 | 34.9595 | 48.0902 | 66.0549 | 90.6695 | 124.0333 | 169.6163 | 232.2995 | 318.5756 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2.6567 | 12.355 | 25.275 | 42.5543 | 65.7467 | 96.978 | 139.1604 | 196.2887 | 273.8494 | 379.3849 | 523.275 | 719.8157 | 988.7123 | 1357.1456 | 1856.5364 | 2538.825 | 3477.0697 | 4768.4542 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 3679 | 22009898 | SA | Blank | 22 | CB BT2-3 | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 2.6788 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 7.9912 | 0.028405 | 0 | 0.028405 | 78.1138 | 0 | 78.1138 | 80.631 | 11.3649 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 170.1097 | 30.9493 | 139.1604 |  | 0.1093 |  | 2.9882 | 3.3333 | 3.7183 | 4.1477 | 4.6268 | 5.1611 | 5.7572 | 6.4221 | 7.1638 | 7.9912 | 8.9141 | 9.9436 | 11.092 | 12.373 | 13.802 | 15.3961 | 17.1742 | 19.1577 | 21.3702 | 23.8383 | 26.5915 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0056115 | 0.007231 | 0.0093884 | 0.012274 | 0.016146 | 0.021361 | 0.028405 | 0.037944 | 0.050895 | 0.068518 | 0.092545 | 0.12536 | 0.17026 | 0.23179 | 0.31619 | 0.43213 | 0.59157 | 0.81102 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 33.606 | 43.3043 | 56.2243 | 73.5036 | 96.696 | 127.9273 | 170.1097 | 227.238 | 304.7987 | 410.3342 | 554.2243 | 750.765 | 1019.6616 | 1388.0949 | 1893.5808 | 2587.9296 | 3542.7291 | 4856.9407 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 15.4318 | 19.8852 | 25.818 | 33.7526 | 44.4025 | 58.7438 | 78.1138 | 104.347 | 139.9626 | 188.4242 | 254.4981 | 344.749 | 468.2255 | 637.4089 | 869.5265 | 1188.3693 | 1626.8103 | 2230.2923 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 1.2199 | 5.6734 | 11.6062 | 19.5408 | 30.1907 | 44.532 | 63.902 | 90.1352 | 125.7508 | 174.2124 | 240.2863 | 330.5371 | 454.0136 | 623.1971 | 852.5158 | 1165.8207 | 1596.6597 | 2189.6595 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1.2199 | 5.6734 | 11.6062 | 19.5408 | 30.1907 | 44.532 | 63.902 | 90.1352 | 125.7508 | 174.2124 | 240.2863 | 330.5371 | 454.0136 | 623.1971 | 852.5158 | 1165.8207 | 1596.6597 | 2189.6595 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 15.929 | 20.526 | 26.65 | 34.8403 | 45.8333 | 60.6368 | 80.631 | 107.7095 | 144.4728 | 194.496 | 262.6991 | 355.8582 | 483.3136 | 657.9488 | 897.5461 | 1226.6633 | 1679.2327 | 2302.1612 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 1.2592 | 5.8562 | 11.9802 | 20.1705 | 31.1635 | 45.967 | 65.9612 | 93.0397 | 129.803 | 179.8262 | 248.0293 | 341.1884 | 468.6438 | 643.279 | 879.9873 | 1203.3881 | 1648.1105 | 2260.2191 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.2452 | 2.8931 | 3.7563 | 4.9107 | 6.4602 | 8.5467 | 11.3649 | 15.1815 | 20.3633 | 27.414 | 37.0272 | 50.1578 | 68.1225 | 92.7372 | 126.5082 | 172.8969 | 236.6861 | 324.4872 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0.17749 | 0.82543 | 1.6886 | 2.843 | 4.3925 | 6.479 | 9.2972 | 13.1138 | 18.2956 | 25.3463 | 34.9595 | 48.0902 | 66.0549 | 90.6695 | 124.0333 | 169.6163 | 232.2995 | 318.5756 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2.6567 | 12.355 | 25.275 | 42.5543 | 65.7467 | 96.978 | 139.1604 | 196.2887 | 273.8494 | 379.3849 | 523.275 | 719.8157 | 988.7123 | 1357.1456 | 1856.5364 | 2538.825 | 3477.0697 | 4768.4542 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 3680 | 22009894 | SA | Blank | 22 | CB TR NO.1 | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 2.6788 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 7.9912 | 0.028405 | 0 | 0.028405 | 78.1138 | 0 | 78.1138 | 80.631 | 11.3649 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 170.1097 | 30.9493 | 139.1604 |  | 0.1093 |  | 2.9882 | 3.3333 | 3.7183 | 4.1477 | 4.6268 | 5.1611 | 5.7572 | 6.4221 | 7.1638 | 7.9912 | 8.9141 | 9.9436 | 11.092 | 12.373 | 13.802 | 15.3961 | 17.1742 | 19.1577 | 21.3702 | 23.8383 | 26.5915 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0056115 | 0.007231 | 0.0093884 | 0.012274 | 0.016146 | 0.021361 | 0.028405 | 0.037944 | 0.050895 | 0.068518 | 0.092545 | 0.12536 | 0.17026 | 0.23179 | 0.31619 | 0.43213 | 0.59157 | 0.81102 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 33.606 | 43.3043 | 56.2243 | 73.5036 | 96.696 | 127.9273 | 170.1097 | 227.238 | 304.7987 | 410.3342 | 554.2243 | 750.765 | 1019.6616 | 1388.0949 | 1893.5808 | 2587.9296 | 3542.7291 | 4856.9407 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 15.4318 | 19.8852 | 25.818 | 33.7526 | 44.4025 | 58.7438 | 78.1138 | 104.347 | 139.9626 | 188.4242 | 254.4981 | 344.749 | 468.2255 | 637.4089 | 869.5265 | 1188.3693 | 1626.8103 | 2230.2923 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 1.2199 | 5.6734 | 11.6062 | 19.5408 | 30.1907 | 44.532 | 63.902 | 90.1352 | 125.7508 | 174.2124 | 240.2863 | 330.5371 | 454.0136 | 623.1971 | 852.5158 | 1165.8207 | 1596.6597 | 2189.6595 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1.2199 | 5.6734 | 11.6062 | 19.5408 | 30.1907 | 44.532 | 63.902 | 90.1352 | 125.7508 | 174.2124 | 240.2863 | 330.5371 | 454.0136 | 623.1971 | 852.5158 | 1165.8207 | 1596.6597 | 2189.6595 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 15.929 | 20.526 | 26.65 | 34.8403 | 45.8333 | 60.6368 | 80.631 | 107.7095 | 144.4728 | 194.496 | 262.6991 | 355.8582 | 483.3136 | 657.9488 | 897.5461 | 1226.6633 | 1679.2327 | 2302.1612 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 1.2592 | 5.8562 | 11.9802 | 20.1705 | 31.1635 | 45.967 | 65.9612 | 93.0397 | 129.803 | 179.8262 | 248.0293 | 341.1884 | 468.6438 | 643.279 | 879.9873 | 1203.3881 | 1648.1105 | 2260.2191 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.2452 | 2.8931 | 3.7563 | 4.9107 | 6.4602 | 8.5467 | 11.3649 | 15.1815 | 20.3633 | 27.414 | 37.0272 | 50.1578 | 68.1225 | 92.7372 | 126.5082 | 172.8969 | 236.6861 | 324.4872 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0.17749 | 0.82543 | 1.6886 | 2.843 | 4.3925 | 6.479 | 9.2972 | 13.1138 | 18.2956 | 25.3463 | 34.9595 | 48.0902 | 66.0549 | 90.6695 | 124.0333 | 169.6163 | 232.2995 | 318.5756 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2.6567 | 12.355 | 25.275 | 42.5543 | 65.7467 | 96.978 | 139.1604 | 196.2887 | 273.8494 | 379.3849 | 523.275 | 719.8157 | 988.7123 | 1357.1456 | 1856.5364 | 2538.825 | 3477.0697 | 4768.4542 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 3681 | 22009895 | SA | Blank | 22 | CB TR NO.2 | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 2.6788 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 7.9912 | 0.028405 | 0 | 0.028405 | 78.1138 | 0 | 78.1138 | 80.631 | 11.3649 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 170.1097 | 30.9493 | 139.1604 |  | 0.1093 |  | 2.9882 | 3.3333 | 3.7183 | 4.1477 | 4.6268 | 5.1611 | 5.7572 | 6.4221 | 7.1638 | 7.9912 | 8.9141 | 9.9436 | 11.092 | 12.373 | 13.802 | 15.3961 | 17.1742 | 19.1577 | 21.3702 | 23.8383 | 26.5915 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0056115 | 0.007231 | 0.0093884 | 0.012274 | 0.016146 | 0.021361 | 0.028405 | 0.037944 | 0.050895 | 0.068518 | 0.092545 | 0.12536 | 0.17026 | 0.23179 | 0.31619 | 0.43213 | 0.59157 | 0.81102 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 33.606 | 43.3043 | 56.2243 | 73.5036 | 96.696 | 127.9273 | 170.1097 | 227.238 | 304.7987 | 410.3342 | 554.2243 | 750.765 | 1019.6616 | 1388.0949 | 1893.5808 | 2587.9296 | 3542.7291 | 4856.9407 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 15.4318 | 19.8852 | 25.818 | 33.7526 | 44.4025 | 58.7438 | 78.1138 | 104.347 | 139.9626 | 188.4242 | 254.4981 | 344.749 | 468.2255 | 637.4089 | 869.5265 | 1188.3693 | 1626.8103 | 2230.2923 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 1.2199 | 5.6734 | 11.6062 | 19.5408 | 30.1907 | 44.532 | 63.902 | 90.1352 | 125.7508 | 174.2124 | 240.2863 | 330.5371 | 454.0136 | 623.1971 | 852.5158 | 1165.8207 | 1596.6597 | 2189.6595 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1.2199 | 5.6734 | 11.6062 | 19.5408 | 30.1907 | 44.532 | 63.902 | 90.1352 | 125.7508 | 174.2124 | 240.2863 | 330.5371 | 454.0136 | 623.1971 | 852.5158 | 1165.8207 | 1596.6597 | 2189.6595 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 15.929 | 20.526 | 26.65 | 34.8403 | 45.8333 | 60.6368 | 80.631 | 107.7095 | 144.4728 | 194.496 | 262.6991 | 355.8582 | 483.3136 | 657.9488 | 897.5461 | 1226.6633 | 1679.2327 | 2302.1612 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 1.2592 | 5.8562 | 11.9802 | 20.1705 | 31.1635 | 45.967 | 65.9612 | 93.0397 | 129.803 | 179.8262 | 248.0293 | 341.1884 | 468.6438 | 643.279 | 879.9873 | 1203.3881 | 1648.1105 | 2260.2191 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.2452 | 2.8931 | 3.7563 | 4.9107 | 6.4602 | 8.5467 | 11.3649 | 15.1815 | 20.3633 | 27.414 | 37.0272 | 50.1578 | 68.1225 | 92.7372 | 126.5082 | 172.8969 | 236.6861 | 324.4872 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0.17749 | 0.82543 | 1.6886 | 2.843 | 4.3925 | 6.479 | 9.2972 | 13.1138 | 18.2956 | 25.3463 | 34.9595 | 48.0902 | 66.0549 | 90.6695 | 124.0333 | 169.6163 | 232.2995 | 318.5756 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2.6567 | 12.355 | 25.275 | 42.5543 | 65.7467 | 96.978 | 139.1604 | 196.2887 | 273.8494 | 379.3849 | 523.275 | 719.8157 | 988.7123 | 1357.1456 | 1856.5364 | 2538.825 | 3477.0697 | 4768.4542 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 3682 | 22009896 | SA | Blank | 22 | CB TR NO.3 | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 2.6788 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 7.9912 | 0.028405 | 0 | 0.028405 | 78.1138 | 0 | 78.1138 | 80.631 | 11.3649 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 170.1097 | 30.9493 | 139.1604 |  | 0.1093 |  | 2.9882 | 3.3333 | 3.7183 | 4.1477 | 4.6268 | 5.1611 | 5.7572 | 6.4221 | 7.1638 | 7.9912 | 8.9141 | 9.9436 | 11.092 | 12.373 | 13.802 | 15.3961 | 17.1742 | 19.1577 | 21.3702 | 23.8383 | 26.5915 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0056115 | 0.007231 | 0.0093884 | 0.012274 | 0.016146 | 0.021361 | 0.028405 | 0.037944 | 0.050895 | 0.068518 | 0.092545 | 0.12536 | 0.17026 | 0.23179 | 0.31619 | 0.43213 | 0.59157 | 0.81102 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 33.606 | 43.3043 | 56.2243 | 73.5036 | 96.696 | 127.9273 | 170.1097 | 227.238 | 304.7987 | 410.3342 | 554.2243 | 750.765 | 1019.6616 | 1388.0949 | 1893.5808 | 2587.9296 | 3542.7291 | 4856.9407 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 15.4318 | 19.8852 | 25.818 | 33.7526 | 44.4025 | 58.7438 | 78.1138 | 104.347 | 139.9626 | 188.4242 | 254.4981 | 344.749 | 468.2255 | 637.4089 | 869.5265 | 1188.3693 | 1626.8103 | 2230.2923 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 1.2199 | 5.6734 | 11.6062 | 19.5408 | 30.1907 | 44.532 | 63.902 | 90.1352 | 125.7508 | 174.2124 | 240.2863 | 330.5371 | 454.0136 | 623.1971 | 852.5158 | 1165.8207 | 1596.6597 | 2189.6595 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1.2199 | 5.6734 | 11.6062 | 19.5408 | 30.1907 | 44.532 | 63.902 | 90.1352 | 125.7508 | 174.2124 | 240.2863 | 330.5371 | 454.0136 | 623.1971 | 852.5158 | 1165.8207 | 1596.6597 | 2189.6595 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 15.929 | 20.526 | 26.65 | 34.8403 | 45.8333 | 60.6368 | 80.631 | 107.7095 | 144.4728 | 194.496 | 262.6991 | 355.8582 | 483.3136 | 657.9488 | 897.5461 | 1226.6633 | 1679.2327 | 2302.1612 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 1.2592 | 5.8562 | 11.9802 | 20.1705 | 31.1635 | 45.967 | 65.9612 | 93.0397 | 129.803 | 179.8262 | 248.0293 | 341.1884 | 468.6438 | 643.279 | 879.9873 | 1203.3881 | 1648.1105 | 2260.2191 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.2452 | 2.8931 | 3.7563 | 4.9107 | 6.4602 | 8.5467 | 11.3649 | 15.1815 | 20.3633 | 27.414 | 37.0272 | 50.1578 | 68.1225 | 92.7372 | 126.5082 | 172.8969 | 236.6861 | 324.4872 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0.17749 | 0.82543 | 1.6886 | 2.843 | 4.3925 | 6.479 | 9.2972 | 13.1138 | 18.2956 | 25.3463 | 34.9595 | 48.0902 | 66.0549 | 90.6695 | 124.0333 | 169.6163 | 232.2995 | 318.5756 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2.6567 | 12.355 | 25.275 | 42.5543 | 65.7467 | 96.978 | 139.1604 | 196.2887 | 273.8494 | 379.3849 | 523.275 | 719.8157 | 988.7123 | 1357.1456 | 1856.5364 | 2538.825 | 3477.0697 | 4768.4542 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 3683 | 22005013 | SA | Blank | 22 | ALL FEEDERS | BUEF BUS2 | BU | RMS | 2C137 | RMS - 2C137 | RMS 2C13X | Electronic |  | 0.15703 | 2190 |  | 6.6 | 0.014726 | 0.0051892 | 0.0095369 | 62.8855 | 726.4845 | 789.37 | 71.2617 | 5.9438 | 8112.5529 |  | 14.9721 | 0.13394 | 0.047196 | 0.086739 | 571.951 | 6607.4644 | 7179.4155 | 648.1342 | 54.0594 | 73784.6473 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 21.3182 | 0.15563 | 21.4738 | 14.6761 | 2.0677 | 1.7379 |  | 8979.1284 | 81666.2564 | 39.9555 | 81626.3008 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.018172 | 0.022489 | 0.027904 | 0.034708 | 0.043268 | 0.05405 | 0.067647 | 0.084812 | 0.1065 | 0.13394 | 0.16866 | 0.21265 | 0.26843 | 0.33918 | 0.42899 | 0.54305 | 0.688 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0064035 | 0.0079246 | 0.009833 | 0.012231 | 0.015247 | 0.019046 | 0.023838 | 0.029886 | 0.037529 | 0.047196 | 0.059433 | 0.074935 | 0.094588 | 0.11952 | 0.15117 | 0.19136 | 0.24244 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 11080.3369 | 13712.3974 | 17014.5208 | 21163.2428 | 26382.5693 | 32956.9048 | 41247.5294 | 51713.6048 | 64938.9606 | 81666.2564 | 102840.5613 | 129664.9558 | 163671.4836 | 206811.7059 | 261572.2888 | 331122.564 | 419502.9286 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 |  | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 39.3208 | 52.122 | 69.6942 | 93.9241 | 127.4707 | 174.0879 | 239.084 | 329.9756 | 457.4208 | 636.5485 | 888.8563 | 1244.9199 | 1748.2618 |  | 77.6013 | 96.035 | 119.1615 | 148.2171 | 184.7708 | 230.8143 | 288.8778 | 362.1771 | 454.8011 | 571.951 | 720.2456 | 908.1108 | 1146.2761 | 1448.4094 | 1831.926 | 2319.0226 | 2937.996 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 63.3892 | 81.8229 | 104.9494 | 134.005 | 170.5587 | 216.6021 | 274.6657 | 347.965 | 440.589 | 557.7389 | 706.0335 | 893.8986 | 1132.0639 | 1434.1972 | 1817.7139 | 2304.8105 | 2923.7839 | 3404.7319 | 3399.1938 | 3391.5917 | 3381.1093 | 3366.5963 | 3346.4287 | 3318.31 | 3278.9883 | 3223.8527 | 3146.3582 | 3037.2043 | 2883.1634 | 2665.4067 |  | 896.4894 | 1109.4445 | 1376.6131 | 1712.2785 | 2134.5645 | 2666.4817 | 3337.2606 | 4184.0513 | 5254.0901 | 6607.4644 | 8320.6379 | 10490.9497 | 13242.3544 | 16732.7493 | 21163.3259 | 26790.5089 | 33941.1993 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 |  | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.18628 | 0.24693 | 0.33018 | 0.44496 | 0.60389 | 0.82474 | 1.1327 | 1.5633 | 2.167 | 3.0156 | 4.2109 | 5.8978 | 8.2824 |  | 896.3338 | 1109.2889 | 1376.4575 | 1712.1229 | 2134.4088 | 2666.326 | 3337.105 | 4183.8957 | 5253.9345 | 6607.3088 | 8320.4823 | 10490.794 | 13242.1987 | 16732.5936 | 21163.1702 | 26790.3532 | 33941.0436 | 39529.4991 | 39529.4384 | 39529.3552 | 39529.2404 | 39529.0815 | 39528.8606 | 39528.5527 | 39528.1221 | 39527.5183 | 39526.6697 | 39525.4744 | 39523.7876 | 39521.403 |  | 959.723 | 1191.1117 | 1481.4069 | 1846.1279 | 2304.9675 | 2882.9282 | 3611.7707 | 4531.8606 | 5694.5235 | 7165.0477 | 9026.5158 | 11384.6927 | 14374.2627 | 18166.7909 | 22980.8842 | 29095.1637 | 36864.8275 | 42934.231 | 42928.6322 | 42920.9469 | 42910.3497 | 42895.6778 | 42875.2893 | 42846.8627 | 42807.1104 | 42751.371 | 42673.0279 | 42562.6787 | 42406.951 | 42186.8097 |  | 87.9377 | 108.8268 | 135.0336 | 167.9595 | 209.382 | 261.5584 | 327.3559 | 410.4187 | 515.3801 | 648.1342 | 816.1814 | 1029.0699 | 1298.9586 | 1641.3356 | 2075.9362 | 2627.9134 | 3329.3333 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 73.2616 | 94.1507 | 120.3576 | 153.2834 | 194.7059 | 246.8823 | 312.6798 | 395.7426 | 500.704 | 633.4581 | 801.5053 | 1014.3938 | 1284.2825 | 1626.6595 | 2061.2601 | 2613.2373 | 3314.6572 | 3859.9483 | 3854.2294 | 3846.3791 | 3835.5545 | 3820.5678 | 3799.7417 | 3770.7051 | 3730.0997 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 7.3347 | 9.077 | 11.2629 | 14.0091 | 17.4641 | 21.816 | 27.304 | 34.2321 | 42.9867 | 54.0594 | 68.0759 | 85.8324 | 108.3432 | 136.9001 | 173.1492 | 219.1884 | 277.6923 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 5.267 | 7.0093 | 9.1952 | 11.9414 | 15.3964 | 19.7483 | 25.2363 | 32.1644 | 40.919 | 51.9917 | 66.0082 | 83.7647 | 106.2755 | 134.8324 | 171.0815 | 217.1207 | 275.6246 | 320.9399 | 320.1342 | 319.0282 | 317.5031 | 315.3917 | 312.4575 | 308.3665 | 302.6457 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 10010.9738 | 12389.0141 | 15372.4497 | 19120.7785 | 23836.388 | 29776.2345 | 37266.731 | 46722.7257 | 58671.7026 | 73784.6473 | 92915.4204 | 117150.993 | 147875.5514 | 186852.3115 | 236327.9515 | 299165.9307 | 379016.7077 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 |  | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 2.0802 | 2.7574 | 3.687 | 4.9689 | 6.7436 | 9.2098 | 12.6482 | 17.4567 | 24.1989 | 33.6753 | 47.0231 | 65.8599 | 92.4881 |  | 10009.2359 | 12387.2762 | 15370.7117 | 19119.0406 | 23834.65 | 29774.4965 | 37264.9931 | 46720.9877 | 58669.9646 | 73782.9094 | 92913.6825 | 117149.2551 | 147873.8134 | 186850.5736 | 236326.2135 | 299164.1928 | 379014.9698 | 441420.4836 | 441419.8064 | 441418.8768 | 441417.595 | 441415.8203 | 441413.3541 | 441409.9156 | 441405.1072 | 441398.365 | 441388.8886 | 441375.5408 | 441356.704 | 441330.0757 |  | 11047.4875 | 13679.5479 | 16981.6713 | 21130.3933 | 26349.7198 | 32924.0553 | 41214.6799 | 51680.7553 | 64906.1111 | 81633.4069 | 102807.7118 | 129632.1063 | 163638.6341 | 206778.8564 | 261539.4394 | 331089.7146 | 419470.0791 | 488535.6029 | 488522.8023 | 488505.231 | 488481.0023 | 488447.4575 | 488400.8426 | 488335.8499 | 488244.9629 | 488117.5242 | 487938.4058 | 487686.1108 | 487330.0654 | 486826.7493
| TRUE | 3684 | 22005009 | SA | Blank | 22 | ALL FEEDERS | MASTER EARTH FAULT | X | RMS | 2C137 | RMS - 2C137 | RMS 2C13X | Electronic |  | 0.81881 | 2190 |  | 6.6 | 0.014726 | 0.011754 | 0.0029722 | 65.5934 | 1645.5384 | 1711.1318 | 108.5309 | 6.0094 | 18375.501 |  | 14.9721 | 0.13394 | 0.1069 | 0.027033 | 596.58 | 14966.3702 | 15562.9501 | 987.1017 | 54.6565 | 167127.3989 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 21.3201 | 0.81153 | 22.1317 | 14.7027 | 2.0677 | 9.0623 |  | 20201.1732 | 183732.1072 | 47.9644 | 183684.1429 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.018172 | 0.022489 | 0.027904 | 0.034708 | 0.043268 | 0.05405 | 0.067647 | 0.084812 | 0.1065 | 0.13394 | 0.16866 | 0.21265 | 0.26843 | 0.33918 | 0.42899 | 0.54305 | 0.688 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.014504 | 0.01795 | 0.022272 | 0.027703 | 0.034535 | 0.043141 | 0.053994 | 0.067694 | 0.085006 | 0.1069 | 0.13462 | 0.16973 | 0.21425 | 0.27072 | 0.3424 | 0.43345 | 0.54914 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 24928.4557 | 30850.0448 | 38279.1363 | 47612.8987 | 59355.2988 | 74146.1877 | 92798.3702 | 116344.8652 | 146099.1676 | 183732.1072 | 231369.8934 | 291719.2072 | 368226.8285 | 465283.3645 | 588483.2972 | 744956.9644 | 943794.4199 | 1099192.0517 | 1099192.0517 | 1099192.0517 | 1099192.0517 | 1099192.0517 | 1099192.0517 | 1099192.0517 | 1099192.0517 | 1099192.0517 | 1099192.0517 | 1099192.0517 | 1099192.0517 | 1099192.0517 |  | 40.8664 | 40.8664 | 40.8664 | 40.8664 | 40.8664 | 40.8664 | 40.8664 | 40.8664 | 40.8664 | 40.8664 | 40.8664 | 40.8664 | 40.8664 | 40.8664 | 40.8664 | 40.8664 | 40.8664 | 48.9146 | 64.8391 | 86.6987 | 116.8404 | 158.5719 | 216.5631 | 297.4174 | 410.4855 | 569.0257 | 791.8582 | 1105.726 | 1548.6647 | 2174.8156 |  | 80.9429 | 100.1704 | 124.2927 | 154.5995 | 192.7272 | 240.7534 | 301.3172 | 377.7729 | 474.3854 | 596.58 | 751.2603 | 947.2151 | 1195.6361 | 1510.7797 | 1910.811 | 2418.8826 | 3064.5098 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 | 3569.0874 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 66.7295 | 85.957 | 110.0793 | 140.3861 | 178.5138 | 226.54 | 287.1038 | 363.5595 | 460.172 | 582.3665 | 737.0469 | 933.0017 | 1181.4227 | 1496.5662 | 1896.5976 | 2404.6692 | 3050.2963 | 3552.0748 | 3546.5362 | 3538.9334 | 3528.4501 | 3513.9358 | 3493.7663 | 3465.6451 | 3426.3198 | 3371.1792 | 3293.6777 | 3184.5139 | 3030.4591 | 2812.6827 |  | 2030.6113 | 2512.9695 | 3118.1253 | 3878.4308 | 4834.9382 | 6039.7679 | 7559.1293 | 9477.1695 | 11900.8825 | 14966.3702 | 18846.8283 | 23762.7365 | 29994.861 | 37900.8502 | 47936.4168 | 60682.3808 | 76879.1959 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 | 89537.5087 |  | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.81153 | 0.97135 | 1.2876 | 1.7217 | 2.3202 | 3.1489 | 4.3005 | 5.9062 | 8.1515 | 11.2998 | 15.7249 | 21.9577 | 30.7536 | 43.1878 |  | 2029.7998 | 2512.158 | 3117.3137 | 3877.6193 | 4834.1266 | 6038.9564 | 7558.3178 | 9476.358 | 11900.071 | 14965.5586 | 18846.0167 | 23761.9249 | 29994.0495 | 37900.0387 | 47935.6053 | 60681.5693 | 76878.3844 | 89536.5373 | 89536.2211 | 89535.787 | 89535.1884 | 89534.3597 | 89533.2081 | 89531.6025 | 89529.3572 | 89526.2089 | 89521.7838 | 89515.551 | 89506.755 | 89494.3208 |  | 2096.5293 | 2598.115 | 3227.393 | 4018.0054 | 5012.6404 | 6265.4964 | 7845.4216 | 9839.9175 | 12360.243 | 15547.9252 | 19583.0636 | 24694.9266 | 31175.4722 | 39396.6049 | 49832.2029 | 63086.2384 | 79928.6807 | 93088.6121 | 93082.7573 | 93074.7204 | 93063.6385 | 93048.2955 | 93026.9745 | 92997.2476 | 92955.677 | 92897.3881 | 92815.4615 | 92700.0649 | 92537.2141 | 92307.0035 |  | 133.9283 | 165.742 | 205.6549 | 255.8005 | 318.8866 | 398.3508 | 498.5597 | 625.0634 | 784.9185 | 987.1017 | 1243.0359 | 1567.2629 | 1978.3005 | 2499.7372 | 3161.6295 | 4002.285 | 5070.5402 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 119.2256 | 151.0393 | 190.9522 | 241.0978 | 304.1839 | 383.6481 | 483.857 | 610.3607 | 770.2158 | 972.399 | 1228.3332 | 1552.5602 | 1963.5978 | 2485.0345 | 3146.9268 | 3987.5823 | 5055.8375 | 5887.8166 | 5882.0873 | 5874.2228 | 5863.3786 | 5848.3647 | 5827.5009 | 5798.4116 | 5757.7326 | 5700.6939 | 5620.5245 | 5507.6029 | 5348.2449 | 5122.9719 |  | 7.4157 | 9.1772 | 11.3872 | 14.1638 | 17.657 | 22.057 | 27.6056 | 34.6102 | 43.4615 | 54.6565 | 68.8277 | 86.7804 | 109.5398 | 138.4122 | 175.0616 | 221.6092 | 280.7593 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 5.3479 | 7.1095 | 9.3195 | 12.0961 | 15.5892 | 19.9892 | 25.5378 | 32.5424 | 41.3937 | 52.5887 | 66.76 | 84.7127 | 107.4721 | 136.3444 | 172.9938 | 219.5415 | 278.6915 | 324.5119 | 323.7061 | 322.6001 | 321.075 | 318.9635 | 316.0292 | 311.9382 | 306.2172 | 298.1954 | 286.9206 | 271.0396 | 248.6279 | 216.9461 |  | 22675.5575 | 28061.9856 | 34819.6762 | 43309.9039 | 53991.0898 | 67445.2586 | 84411.7583 | 105830.2492 | 132895.5196 | 167127.3989 | 210459.9412 | 265355.2123 | 334948.491 | 423233.5853 | 535299.3784 | 677631.8068 | 858499.4148 | 999853.054 | 999853.054 | 999853.054 | 999853.054 | 999853.054 | 999853.054 | 999853.054 | 999853.054 | 999853.054 | 999853.054 | 999853.054 | 999853.054 | 999853.054 |  | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 10.847 | 14.3783 | 19.2257 | 25.9098 | 35.1639 | 48.0236 | 65.9533 | 91.0266 | 126.1834 | 175.5973 | 245.1985 | 343.4217 | 482.2728 |  | 22666.4952 | 28052.9233 | 34810.6139 | 43300.8416 | 53982.0276 | 67436.1963 | 84402.696 | 105821.1869 | 132886.4574 | 167118.3367 | 210450.8789 | 265346.15 | 334939.4287 | 423224.523 | 535290.3161 | 677622.7445 | 858490.3525 | 999842.207 | 999838.6757 | 999833.8282 | 999827.1442 | 999817.8901 | 999805.0304 | 999787.1007 | 999762.0274 | 999726.8706 | 999677.4567 | 999607.8555 | 999509.6323 | 999370.7812 |  | 24887.598 | 30809.1871 | 38238.2786 | 47572.041 | 59314.4412 | 74105.33 | 92757.5125 | 116304.0075 | 146058.3099 | 183691.2496 | 231329.0358 | 291678.3495 | 368185.9708 | 465242.5068 | 588442.4396 | 744916.1068 | 943753.5622 | 1099143.1476 | 1099127.2264 | 1099105.3716 | 1099075.2363 | 1099033.5138 | 1098975.535 | 1098894.6981 | 1098781.6542 | 1098623.1481 | 1098400.3633 | 1098086.5629 | 1097643.7193 | 1097017.7027
| TRUE | 3685 | 22005012 | SA | Blank | 22 | ALL FEEDERS | BUEF BUS1 | BU | RMS | 2C137 | RMS - 2C137 | RMS 2C13X | Electronic |  | 0.15703 | 2190 |  | 6.6 | 0.014726 | 0.0051892 | 0.0095369 | 62.8855 | 726.4845 | 789.37 | 71.2617 | 5.9438 | 8112.5529 |  | 14.9721 | 0.13394 | 0.047196 | 0.086739 | 571.951 | 6607.4644 | 7179.4155 | 648.1342 | 54.0594 | 73784.6473 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 21.3182 | 0.15563 | 21.4738 | 14.6761 | 2.0677 | 1.7379 |  | 8979.1284 | 81666.2564 | 39.9555 | 81626.3008 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.018172 | 0.022489 | 0.027904 | 0.034708 | 0.043268 | 0.05405 | 0.067647 | 0.084812 | 0.1065 | 0.13394 | 0.16866 | 0.21265 | 0.26843 | 0.33918 | 0.42899 | 0.54305 | 0.688 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0064035 | 0.0079246 | 0.009833 | 0.012231 | 0.015247 | 0.019046 | 0.023838 | 0.029886 | 0.037529 | 0.047196 | 0.059433 | 0.074935 | 0.094588 | 0.11952 | 0.15117 | 0.19136 | 0.24244 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 11080.3369 | 13712.3974 | 17014.5208 | 21163.2428 | 26382.5693 | 32956.9048 | 41247.5294 | 51713.6048 | 64938.9606 | 81666.2564 | 102840.5613 | 129664.9558 | 163671.4836 | 206811.7059 | 261572.2888 | 331122.564 | 419502.9286 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 |  | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 39.3208 | 52.122 | 69.6942 | 93.9241 | 127.4707 | 174.0879 | 239.084 | 329.9756 | 457.4208 | 636.5485 | 888.8563 | 1244.9199 | 1748.2618 |  | 77.6013 | 96.035 | 119.1615 | 148.2171 | 184.7708 | 230.8143 | 288.8778 | 362.1771 | 454.8011 | 571.951 | 720.2456 | 908.1108 | 1146.2761 | 1448.4094 | 1831.926 | 2319.0226 | 2937.996 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 63.3892 | 81.8229 | 104.9494 | 134.005 | 170.5587 | 216.6021 | 274.6657 | 347.965 | 440.589 | 557.7389 | 706.0335 | 893.8986 | 1132.0639 | 1434.1972 | 1817.7139 | 2304.8105 | 2923.7839 | 3404.7319 | 3399.1938 | 3391.5917 | 3381.1093 | 3366.5963 | 3346.4287 | 3318.31 | 3278.9883 | 3223.8527 | 3146.3582 | 3037.2043 | 2883.1634 | 2665.4067 |  | 896.4894 | 1109.4445 | 1376.6131 | 1712.2785 | 2134.5645 | 2666.4817 | 3337.2606 | 4184.0513 | 5254.0901 | 6607.4644 | 8320.6379 | 10490.9497 | 13242.3544 | 16732.7493 | 21163.3259 | 26790.5089 | 33941.1993 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 |  | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.18628 | 0.24693 | 0.33018 | 0.44496 | 0.60389 | 0.82474 | 1.1327 | 1.5633 | 2.167 | 3.0156 | 4.2109 | 5.8978 | 8.2824 |  | 896.3338 | 1109.2889 | 1376.4575 | 1712.1229 | 2134.4088 | 2666.326 | 3337.105 | 4183.8957 | 5253.9345 | 6607.3088 | 8320.4823 | 10490.794 | 13242.1987 | 16732.5936 | 21163.1702 | 26790.3532 | 33941.0436 | 39529.4991 | 39529.4384 | 39529.3552 | 39529.2404 | 39529.0815 | 39528.8606 | 39528.5527 | 39528.1221 | 39527.5183 | 39526.6697 | 39525.4744 | 39523.7876 | 39521.403 |  | 959.723 | 1191.1117 | 1481.4069 | 1846.1279 | 2304.9675 | 2882.9282 | 3611.7707 | 4531.8606 | 5694.5235 | 7165.0477 | 9026.5158 | 11384.6927 | 14374.2627 | 18166.7909 | 22980.8842 | 29095.1637 | 36864.8275 | 42934.231 | 42928.6322 | 42920.9469 | 42910.3497 | 42895.6778 | 42875.2893 | 42846.8627 | 42807.1104 | 42751.371 | 42673.0279 | 42562.6787 | 42406.951 | 42186.8097 |  | 87.9377 | 108.8268 | 135.0336 | 167.9595 | 209.382 | 261.5584 | 327.3559 | 410.4187 | 515.3801 | 648.1342 | 816.1814 | 1029.0699 | 1298.9586 | 1641.3356 | 2075.9362 | 2627.9134 | 3329.3333 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 73.2616 | 94.1507 | 120.3576 | 153.2834 | 194.7059 | 246.8823 | 312.6798 | 395.7426 | 500.704 | 633.4581 | 801.5053 | 1014.3938 | 1284.2825 | 1626.6595 | 2061.2601 | 2613.2373 | 3314.6572 | 3859.9483 | 3854.2294 | 3846.3791 | 3835.5545 | 3820.5678 | 3799.7417 | 3770.7051 | 3730.0997 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 7.3347 | 9.077 | 11.2629 | 14.0091 | 17.4641 | 21.816 | 27.304 | 34.2321 | 42.9867 | 54.0594 | 68.0759 | 85.8324 | 108.3432 | 136.9001 | 173.1492 | 219.1884 | 277.6923 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 5.267 | 7.0093 | 9.1952 | 11.9414 | 15.3964 | 19.7483 | 25.2363 | 32.1644 | 40.919 | 51.9917 | 66.0082 | 83.7647 | 106.2755 | 134.8324 | 171.0815 | 217.1207 | 275.6246 | 320.9399 | 320.1342 | 319.0282 | 317.5031 | 315.3917 | 312.4575 | 308.3665 | 302.6457 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 10010.9738 | 12389.0141 | 15372.4497 | 19120.7785 | 23836.388 | 29776.2345 | 37266.731 | 46722.7257 | 58671.7026 | 73784.6473 | 92915.4204 | 117150.993 | 147875.5514 | 186852.3115 | 236327.9515 | 299165.9307 | 379016.7077 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 |  | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 2.0802 | 2.7574 | 3.687 | 4.9689 | 6.7436 | 9.2098 | 12.6482 | 17.4567 | 24.1989 | 33.6753 | 47.0231 | 65.8599 | 92.4881 |  | 10009.2359 | 12387.2762 | 15370.7117 | 19119.0406 | 23834.65 | 29774.4965 | 37264.9931 | 46720.9877 | 58669.9646 | 73782.9094 | 92913.6825 | 117149.2551 | 147873.8134 | 186850.5736 | 236326.2135 | 299164.1928 | 379014.9698 | 441420.4836 | 441419.8064 | 441418.8768 | 441417.595 | 441415.8203 | 441413.3541 | 441409.9156 | 441405.1072 | 441398.365 | 441388.8886 | 441375.5408 | 441356.704 | 441330.0757 |  | 11047.4875 | 13679.5479 | 16981.6713 | 21130.3933 | 26349.7198 | 32924.0553 | 41214.6799 | 51680.7553 | 64906.1111 | 81633.4069 | 102807.7118 | 129632.1063 | 163638.6341 | 206778.8564 | 261539.4394 | 331089.7146 | 419470.0791 | 488535.6029 | 488522.8023 | 488505.231 | 488481.0023 | 488447.4575 | 488400.8426 | 488335.8499 | 488244.9629 | 488117.5242 | 487938.4058 | 487686.1108 | 487330.0654 | 486826.7493
| TRUE | 3686 | 22005014 | SA | Blank | 22 | ALL FEEDERS | BUEF BUS3 | BU | RMS | 2C137 | RMS - 2C137 | RMS 2C13X | Electronic |  | 0.15703 | 2190 |  | 6.6 | 0.014726 | 0.0051892 | 0.0095369 | 62.8855 | 726.4845 | 789.37 | 71.2617 | 5.9438 | 8112.5529 |  | 14.9721 | 0.13394 | 0.047196 | 0.086739 | 571.951 | 6607.4644 | 7179.4155 | 648.1342 | 54.0594 | 73784.6473 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 21.3182 | 0.15563 | 21.4738 | 14.6761 | 2.0677 | 1.7379 |  | 8979.1284 | 81666.2564 | 39.9555 | 81626.3008 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.018172 | 0.022489 | 0.027904 | 0.034708 | 0.043268 | 0.05405 | 0.067647 | 0.084812 | 0.1065 | 0.13394 | 0.16866 | 0.21265 | 0.26843 | 0.33918 | 0.42899 | 0.54305 | 0.688 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0064035 | 0.0079246 | 0.009833 | 0.012231 | 0.015247 | 0.019046 | 0.023838 | 0.029886 | 0.037529 | 0.047196 | 0.059433 | 0.074935 | 0.094588 | 0.11952 | 0.15117 | 0.19136 | 0.24244 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 11080.3369 | 13712.3974 | 17014.5208 | 21163.2428 | 26382.5693 | 32956.9048 | 41247.5294 | 51713.6048 | 64938.9606 | 81666.2564 | 102840.5613 | 129664.9558 | 163671.4836 | 206811.7059 | 261572.2888 | 331122.564 | 419502.9286 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 | 488574.9216 |  | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 32.8512 | 39.3208 | 52.122 | 69.6942 | 93.9241 | 127.4707 | 174.0879 | 239.084 | 329.9756 | 457.4208 | 636.5485 | 888.8563 | 1244.9199 | 1748.2618 |  | 77.6013 | 96.035 | 119.1615 | 148.2171 | 184.7708 | 230.8143 | 288.8778 | 362.1771 | 454.8011 | 571.951 | 720.2456 | 908.1108 | 1146.2761 | 1448.4094 | 1831.926 | 2319.0226 | 2937.996 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 | 3421.7429 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 63.3892 | 81.8229 | 104.9494 | 134.005 | 170.5587 | 216.6021 | 274.6657 | 347.965 | 440.589 | 557.7389 | 706.0335 | 893.8986 | 1132.0639 | 1434.1972 | 1817.7139 | 2304.8105 | 2923.7839 | 3404.7319 | 3399.1938 | 3391.5917 | 3381.1093 | 3366.5963 | 3346.4287 | 3318.31 | 3278.9883 | 3223.8527 | 3146.3582 | 3037.2043 | 2883.1634 | 2665.4067 |  | 896.4894 | 1109.4445 | 1376.6131 | 1712.2785 | 2134.5645 | 2666.4817 | 3337.2606 | 4184.0513 | 5254.0901 | 6607.4644 | 8320.6379 | 10490.9497 | 13242.3544 | 16732.7493 | 21163.3259 | 26790.5089 | 33941.1993 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 | 39529.6854 |  | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.15563 | 0.18628 | 0.24693 | 0.33018 | 0.44496 | 0.60389 | 0.82474 | 1.1327 | 1.5633 | 2.167 | 3.0156 | 4.2109 | 5.8978 | 8.2824 |  | 896.3338 | 1109.2889 | 1376.4575 | 1712.1229 | 2134.4088 | 2666.326 | 3337.105 | 4183.8957 | 5253.9345 | 6607.3088 | 8320.4823 | 10490.794 | 13242.1987 | 16732.5936 | 21163.1702 | 26790.3532 | 33941.0436 | 39529.4991 | 39529.4384 | 39529.3552 | 39529.2404 | 39529.0815 | 39528.8606 | 39528.5527 | 39528.1221 | 39527.5183 | 39526.6697 | 39525.4744 | 39523.7876 | 39521.403 |  | 959.723 | 1191.1117 | 1481.4069 | 1846.1279 | 2304.9675 | 2882.9282 | 3611.7707 | 4531.8606 | 5694.5235 | 7165.0477 | 9026.5158 | 11384.6927 | 14374.2627 | 18166.7909 | 22980.8842 | 29095.1637 | 36864.8275 | 42934.231 | 42928.6322 | 42920.9469 | 42910.3497 | 42895.6778 | 42875.2893 | 42846.8627 | 42807.1104 | 42751.371 | 42673.0279 | 42562.6787 | 42406.951 | 42186.8097 |  | 87.9377 | 108.8268 | 135.0336 | 167.9595 | 209.382 | 261.5584 | 327.3559 | 410.4187 | 515.3801 | 648.1342 | 816.1814 | 1029.0699 | 1298.9586 | 1641.3356 | 2075.9362 | 2627.9134 | 3329.3333 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 73.2616 | 94.1507 | 120.3576 | 153.2834 | 194.7059 | 246.8823 | 312.6798 | 395.7426 | 500.704 | 633.4581 | 801.5053 | 1014.3938 | 1284.2825 | 1626.6595 | 2061.2601 | 2613.2373 | 3314.6572 | 3859.9483 | 3854.2294 | 3846.3791 | 3835.5545 | 3820.5678 | 3799.7417 | 3770.7051 | 3730.0997 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 7.3347 | 9.077 | 11.2629 | 14.0091 | 17.4641 | 21.816 | 27.304 | 34.2321 | 42.9867 | 54.0594 | 68.0759 | 85.8324 | 108.3432 | 136.9001 | 173.1492 | 219.1884 | 277.6923 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 5.267 | 7.0093 | 9.1952 | 11.9414 | 15.3964 | 19.7483 | 25.2363 | 32.1644 | 40.919 | 51.9917 | 66.0082 | 83.7647 | 106.2755 | 134.8324 | 171.0815 | 217.1207 | 275.6246 | 320.9399 | 320.1342 | 319.0282 | 317.5031 | 315.3917 | 312.4575 | 308.3665 | 302.6457 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 10010.9738 | 12389.0141 | 15372.4497 | 19120.7785 | 23836.388 | 29776.2345 | 37266.731 | 46722.7257 | 58671.7026 | 73784.6473 | 92915.4204 | 117150.993 | 147875.5514 | 186852.3115 | 236327.9515 | 299165.9307 | 379016.7077 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 | 441422.5638 |  | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 2.0802 | 2.7574 | 3.687 | 4.9689 | 6.7436 | 9.2098 | 12.6482 | 17.4567 | 24.1989 | 33.6753 | 47.0231 | 65.8599 | 92.4881 |  | 10009.2359 | 12387.2762 | 15370.7117 | 19119.0406 | 23834.65 | 29774.4965 | 37264.9931 | 46720.9877 | 58669.9646 | 73782.9094 | 92913.6825 | 117149.2551 | 147873.8134 | 186850.5736 | 236326.2135 | 299164.1928 | 379014.9698 | 441420.4836 | 441419.8064 | 441418.8768 | 441417.595 | 441415.8203 | 441413.3541 | 441409.9156 | 441405.1072 | 441398.365 | 441388.8886 | 441375.5408 | 441356.704 | 441330.0757 |  | 11047.4875 | 13679.5479 | 16981.6713 | 21130.3933 | 26349.7198 | 32924.0553 | 41214.6799 | 51680.7553 | 64906.1111 | 81633.4069 | 102807.7118 | 129632.1063 | 163638.6341 | 206778.8564 | 261539.4394 | 331089.7146 | 419470.0791 | 488535.6029 | 488522.8023 | 488505.231 | 488481.0023 | 488447.4575 | 488400.8426 | 488335.8499 | 488244.9629 | 488117.5242 | 487938.4058 | 487686.1108 | 487330.0654 | 486826.7493
| TRUE | 3687 | 22009891 | SA | Blank | 22 | ALL FEEDERS | BUEF & Y MEF | BU | Schweitzer | SEL_351A | SEL 351 | SEL 300s | Digital |  | 0.15703 | 1 |  | 3.2146 | 0.0051679 | 1.1117e-06 | 0.0051668 | 14.2121 | 0.077816 | 14.2899 | 14.6761 | 2.0677 | 1.7379 |  | 9.9777 | 0.051368 | 1.105e-05 | 0.051357 | 141.2664 | 0.77348 | 142.0399 | 145.8782 | 20.5526 | 17.2747 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 14.2121 | 0.077816 | 14.2899 | 14.6761 | 2.0677 | 1.7379 |  | 32.7717 | 325.7454 | 32.7717 | 292.9737 |  | 0.11326 |  | 3.6001 | 4.0319 | 4.5154 | 5.0569 | 5.6634 | 6.3426 | 7.1033 | 7.9551 | 8.9092 | 9.9777 | 11.1743 | 12.5144 | 14.0152 | 15.696 | 17.5784 | 19.6866 | 22.0476 | 24.6917 | 27.6529 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0052615 | 0.006829 | 0.0089371 | 0.011784 | 0.015645 | 0.020898 | 0.02807 | 0.037889 | 0.051368 | 0.069918 | 0.095498 | 0.13084 | 0.17976 | 0.24758 | 0.34173 | 0.47259 | 0.65469 | 0.90833 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1318e-06 | 1.469e-06 | 1.9224e-06 | 2.5349e-06 | 3.3653e-06 | 4.4953e-06 | 6.038e-06 | 8.1501e-06 | 1.105e-05 | 1.504e-05 | 2.0542e-05 | 2.8145e-05 | 3.8668e-05 | 5.3257e-05 | 7.3509e-05 | 0.00010166 | 0.00014083 | 0.00019539 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 32.7717 | 33.365 | 43.3051 | 56.6732 | 74.7285 | 99.2097 | 132.5226 | 178 | 240.2662 | 325.7454 | 443.3721 | 605.5855 | 829.719 | 1139.9475 | 1570.0115 | 2167.0343 | 2996.8698 | 4151.5968 | 5760.0247 | 5972.0258 | 5972.0258 | 5972.0258 | 5972.0258 | 5972.0258 | 5972.0258 | 5972.0258 | 5972.0258 | 5972.0258 | 5972.0258 | 5972.0258 |  | 32.7717 | 32.7717 | 32.7717 | 32.7717 | 32.7717 | 32.7717 | 32.7717 | 32.7717 | 32.7717 | 32.7717 | 32.7717 | 32.7717 | 32.7717 | 32.7717 | 32.7717 | 32.7717 | 32.7717 | 39.2256 | 51.9959 | 69.5256 | 93.6968 | 127.1622 | 173.6666 | 238.5054 | 329.1771 | 456.3139 | 635.0081 | 886.7053 | 1241.9073 | 1744.0311 |  | 14.2121 | 14.4694 | 18.7802 | 24.5775 | 32.4076 | 43.0244 | 57.4712 | 77.1935 | 104.1965 | 141.2664 | 192.2778 | 262.625 | 359.8253 | 494.3625 | 680.8688 | 939.7805 | 1299.6563 | 1800.4282 | 2497.9571 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 | 2589.8959 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 0 | 0.25729 | 4.5681 | 10.3654 | 18.1955 | 28.8123 | 43.2591 | 62.9813 | 89.9844 | 127.0543 | 178.0656 | 248.4129 | 345.6132 | 480.1503 | 666.6567 | 925.5684 | 1285.4442 | 1783.4172 | 2475.408 | 2559.7447 | 2549.2623 | 2534.7493 | 2514.5817 | 2486.463 | 2447.1413 | 2392.0057 | 2314.5112 | 2205.3573 | 2051.3164 | 1833.5597 |  | 0.077816 | 0.079225 | 0.10283 | 0.13457 | 0.17744 | 0.23557 | 0.31467 | 0.42266 | 0.57051 | 0.77348 | 1.0528 | 1.438 | 1.9702 | 2.7068 | 3.728 | 5.1456 | 7.116 | 9.8579 | 13.6771 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 | 14.1805 |  | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.077816 | 0.093141 | 0.12346 | 0.16509 | 0.22248 | 0.30195 | 0.41237 | 0.56633 | 0.78163 | 1.0835 | 1.5078 | 2.1055 | 2.9489 | 4.1412 |  | 0 | 0.0014088 | 0.025012 | 0.056754 | 0.099626 | 0.15776 | 0.23686 | 0.34484 | 0.49269 | 0.69566 | 0.97497 | 1.3601 | 1.8923 | 2.629 | 3.6502 | 5.0678 | 7.0382 | 9.7648 | 13.5537 | 14.0154 | 13.958 | 13.8786 | 13.7681 | 13.6142 | 13.3989 | 13.097 | 12.6727 | 12.075 | 11.2316 | 10.0393 |  | 0 | 0.2587 | 4.5931 | 10.4222 | 18.2951 | 28.97 | 43.496 | 63.3262 | 90.4771 | 127.7499 | 179.0406 | 249.773 | 347.5055 | 482.7793 | 670.3069 | 930.6361 | 1292.4824 | 1793.1819 | 2488.9617 | 2573.7601 | 2563.2203 | 2548.6279 | 2528.3498 | 2500.0772 | 2460.5401 | 2405.1027 | 2327.1839 | 2217.4323 | 2062.548 | 1843.5991 |  | 14.6761 | 14.9418 | 19.3933 | 25.3799 | 33.4656 | 44.429 | 59.3474 | 79.7135 | 107.5981 | 145.8782 | 198.5548 | 271.1986 | 371.5721 | 510.5014 | 703.0964 | 970.4604 | 1342.0847 | 1859.2047 | 2579.5051 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0.26569 | 4.7172 | 10.7038 | 18.7895 | 29.7529 | 44.6713 | 65.0374 | 92.922 | 131.2021 | 183.8787 | 256.5225 | 356.896 | 495.8253 | 688.4203 | 955.7843 | 1327.4086 | 1841.6384 | 2556.2199 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.1051 | 2.7323 | 3.5758 | 4.7149 | 6.2596 | 8.3614 | 11.2308 | 15.1594 | 20.5526 | 27.9742 | 38.2089 | 52.3505 | 71.9241 | 99.0586 | 136.7273 | 189.0851 | 261.9417 | 363.4242 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0.037433 | 0.6646 | 1.5081 | 2.6472 | 4.1919 | 6.2937 | 9.1631 | 13.0917 | 18.4849 | 25.9065 | 36.1412 | 50.2828 | 69.8564 | 96.9909 | 134.6596 | 187.0174 | 259.4668 | 360.1436 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 1.7379 | 1.7694 | 2.2965 | 3.0055 | 3.9629 | 5.2612 | 7.0278 | 9.4396 | 12.7416 | 17.2747 | 23.5126 | 32.1149 | 44.001 | 60.4528 | 83.2596 | 114.9205 | 158.9277 | 220.1642 | 305.4611 | 316.7038 | 316.7038 | 316.7038 | 316.7038 | 316.7038 | 316.7038 | 316.7038 | 316.7038 | 316.7038 | 316.7038 | 316.7038 |  | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 1.7379 | 2.0802 | 2.7574 | 3.687 | 4.9689 | 6.7436 | 9.2098 | 12.6482 | 17.4567 | 24.1989 | 33.6753 | 47.0231 | 65.8599 | 92.4881 |  | 0 | 0.031463 | 0.5586 | 1.2675 | 2.225 | 3.5233 | 5.2899 | 7.7016 | 11.0037 | 15.5368 | 21.7746 | 30.377 | 42.2631 | 58.7149 | 81.5217 | 113.1825 | 157.1897 | 218.0841 | 302.7037 | 313.0168 | 311.7349 | 309.9602 | 307.494 | 304.0556 | 299.2471 | 292.5049 | 283.0285 | 269.6807 | 250.8439 | 224.2157 |  | 0 | 0.59329 | 10.5334 | 23.9016 | 41.9568 | 66.4381 | 99.7509 | 145.2283 | 207.4945 | 292.9737 | 410.6005 | 572.8138 | 796.9474 | 1107.1758 | 1537.2398 | 2134.2627 | 2964.0982 | 4112.3712 | 5708.0288 | 5902.5002 | 5878.3289 | 5844.8635 | 5798.3591 | 5733.5204 | 5642.8487 | 5515.7119 | 5337.0177 | 5085.3204 | 4730.1184 | 4227.9946
| TRUE | 3688 | 22008262 | SA | SA001 | 22 | SA1 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 27.3978 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 272.6948 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 11.0663 |  | 104.7864 | 1042.9568 | 42.3244 | 1000.6324 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 130.1598 | 162.2514 | 202.9172 | 254.5386 | 320.1736 | 403.7524 | 510.3287 | 646.4052 | 820.3535 | 1042.9568 | 1328.1111 | 1693.7315 | 2162.9238 | 2765.4998 | 3539.9358 | 4535.907 | 5817.5655 | 7467.7802 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 |  | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 50.6597 | 67.1524 | 89.7919 | 121.009 | 164.2294 | 224.2896 | 308.0285 | 425.1306 | 589.3271 | 820.1097 | 1145.1755 | 1603.9171 | 2252.4075 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 34.032 | 42.4228 | 53.0554 | 66.5525 | 83.7136 | 105.5664 | 133.4322 | 169.0112 | 214.4922 | 272.6948 | 347.2522 | 442.8485 | 565.525 | 723.0764 | 925.5629 | 1185.9727 | 1521.0793 | 1952.5497 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 |  | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 13.2456 | 17.5579 | 23.4773 | 31.6394 | 42.9399 | 58.6435 | 80.5381 | 111.156 | 154.0873 | 214.4285 | 299.4212 | 419.3653 | 588.9217 |  | 22.9657 | 31.3565 | 41.9891 | 55.4862 | 72.6473 | 94.5001 | 122.3659 | 157.9449 | 203.426 | 261.6285 | 336.1859 | 431.7822 | 554.4587 | 712.0101 | 914.4966 | 1174.9065 | 1510.013 | 1939.304 | 1999.0663 | 1993.1469 | 1984.9848 | 1973.6842 | 1957.9807 | 1936.086 | 1905.4681 | 1862.5368 | 1802.1956 | 1717.2029 | 1597.2589 | 1427.7025 |  | 87.8353 | 119.927 | 160.5928 | 212.2141 | 277.8492 | 361.4279 | 468.0042 | 604.0807 | 778.0291 | 1000.6324 | 1285.7867 | 1651.4071 | 2120.5994 | 2723.1753 | 3497.6113 | 4493.5826 | 5775.241 | 7417.1205 | 7645.6889 | 7623.0494 | 7591.8324 | 7548.612 | 7488.5518 | 7404.8128 | 7287.7108 | 7123.5143 | 6892.7316 | 6567.6659 | 6108.9243 | 5460.4339
| TRUE | 3689 | 22009779 | SA | SA010 | 22 | SA10 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 15.6419 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 155.6867 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 6.318 |  | 93.0306 | 925.9487 | 37.5761 | 888.3726 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 115.5573 | 144.0486 | 180.1522 | 225.9822 | 284.2537 | 358.4559 | 453.0755 | 573.8858 | 728.319 | 925.9487 | 1179.1119 | 1503.7137 | 1920.268 | 2455.2416 | 3142.7945 | 4027.0289 | 5164.8996 | 6629.9787 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 |  | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 44.9763 | 59.6187 | 79.7183 | 107.4331 | 145.8047 | 199.1268 | 273.4712 | 377.4357 | 523.2112 | 728.1026 | 1016.6996 | 1423.9755 | 1999.7125 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 19.4295 | 24.22 | 30.2903 | 37.9961 | 47.7937 | 60.2699 | 76.179 | 96.4917 | 122.4578 | 155.6867 | 198.2529 | 252.8307 | 322.8691 | 412.8182 | 528.4217 | 677.0947 | 868.4134 | 1114.7482 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 |  | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 7.5622 | 10.0241 | 13.4036 | 18.0635 | 24.5152 | 33.4807 | 45.9808 | 63.4611 | 87.9714 | 122.4214 | 170.9453 | 239.4237 | 336.2267 |  | 13.1116 | 17.902 | 23.9724 | 31.6781 | 41.4758 | 53.9519 | 69.861 | 90.1738 | 116.1398 | 149.3688 | 191.935 | 246.5127 | 316.5511 | 406.5003 | 522.1037 | 670.7767 | 862.0955 | 1107.186 | 1141.3054 | 1137.9259 | 1133.266 | 1126.8143 | 1117.8488 | 1105.3488 | 1087.8684 | 1063.3581 | 1028.9082 | 980.3842 | 911.9058 | 815.1028 |  | 77.9812 | 106.4725 | 142.5761 | 188.4061 | 246.6776 | 320.8798 | 415.4994 | 536.3096 | 690.7429 | 888.3726 | 1141.5358 | 1466.1376 | 1882.6918 | 2417.6655 | 3105.2184 | 3989.4528 | 5127.3235 | 6585.0025 | 6787.928 | 6767.8285 | 6740.1136 | 6701.7421 | 6648.4199 | 6574.0756 | 6470.111 | 6324.3355 | 6119.4442 | 5830.8471 | 5423.5712 | 4847.8342
| TRUE | 3690 | 22009780 | SA | SA011 | 22 | SA11 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 15.6419 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 155.6867 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 6.318 |  | 93.0306 | 925.9487 | 37.5761 | 888.3726 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 115.5573 | 144.0486 | 180.1522 | 225.9822 | 284.2537 | 358.4559 | 453.0755 | 573.8858 | 728.319 | 925.9487 | 1179.1119 | 1503.7137 | 1920.268 | 2455.2416 | 3142.7945 | 4027.0289 | 5164.8996 | 6629.9787 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 | 6847.5467 |  | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 37.5761 | 44.9763 | 59.6187 | 79.7183 | 107.4331 | 145.8047 | 199.1268 | 273.4712 | 377.4357 | 523.2112 | 728.1026 | 1016.6996 | 1423.9755 | 1999.7125 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 19.4295 | 24.22 | 30.2903 | 37.9961 | 47.7937 | 60.2699 | 76.179 | 96.4917 | 122.4578 | 155.6867 | 198.2529 | 252.8307 | 322.8691 | 412.8182 | 528.4217 | 677.0947 | 868.4134 | 1114.7482 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 | 1151.3295 |  | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 6.318 | 7.5622 | 10.0241 | 13.4036 | 18.0635 | 24.5152 | 33.4807 | 45.9808 | 63.4611 | 87.9714 | 122.4214 | 170.9453 | 239.4237 | 336.2267 |  | 13.1116 | 17.902 | 23.9724 | 31.6781 | 41.4758 | 53.9519 | 69.861 | 90.1738 | 116.1398 | 149.3688 | 191.935 | 246.5127 | 316.5511 | 406.5003 | 522.1037 | 670.7767 | 862.0955 | 1107.186 | 1141.3054 | 1137.9259 | 1133.266 | 1126.8143 | 1117.8488 | 1105.3488 | 1087.8684 | 1063.3581 | 1028.9082 | 980.3842 | 911.9058 | 815.1028 |  | 77.9812 | 106.4725 | 142.5761 | 188.4061 | 246.6776 | 320.8798 | 415.4994 | 536.3096 | 690.7429 | 888.3726 | 1141.5358 | 1466.1376 | 1882.6918 | 2417.6655 | 3105.2184 | 3989.4528 | 5127.3235 | 6585.0025 | 6787.928 | 6767.8285 | 6740.1136 | 6701.7421 | 6648.4199 | 6574.0756 | 6470.111 | 6324.3355 | 6119.4442 | 5830.8471 | 5423.5712 | 4847.8342
| TRUE | 3691 | 22009781 | SA | SA012 | 22 | SA12 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.1928 | 0.0095288 | 7.4969e-06 | 0.0095213 | 26.2062 | 0.52478 | 26.731 | 27.0911 | 3.8125 | 23.2984 |  | 12.6825 | 0.099093 | 7.7963e-05 | 0.099015 | 272.5279 | 5.4574 | 277.9853 | 281.7303 | 39.648 | 242.2889 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 12.6359 |  | 80.9331 | 841.6526 | 43.8941 | 797.7585 |  | 0.089295 |  | 5.6779 | 6.2082 | 6.7881 | 7.4221 | 8.1153 | 8.8733 | 9.7021 | 10.6083 | 11.5992 | 12.6825 | 13.8671 | 15.1624 | 16.5786 | 18.1271 | 19.8202 | 21.6714 | 23.6956 | 25.9088 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.011859 | 0.014821 | 0.018596 | 0.023416 | 0.029581 | 0.037483 | 0.047626 | 0.060666 | 0.077454 | 0.099093 | 0.12702 | 0.1631 | 0.20976 | 0.27015 | 0.34839 | 0.44983 | 0.58143 | 0.75227 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 9.3301e-06 | 1.1661e-05 | 1.4631e-05 | 1.8423e-05 | 2.3273e-05 | 2.949e-05 | 3.7471e-05 | 4.773e-05 | 6.0938e-05 | 7.7963e-05 | 9.9935e-05 | 0.00012832 | 0.00016503 | 0.00021255 | 0.0002741 | 0.00035391 | 0.00045744 | 0.00059185 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 100.7239 | 125.8851 | 157.9454 | 198.8813 | 251.2502 | 318.364 | 404.5153 | 515.2711 | 657.8562 | 841.6526 | 1078.8497 | 1385.2934 | 1781.5914 | 2294.5563 | 2959.0873 | 3820.6254 | 4938.3574 | 6389.3971 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 |  | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 52.5384 | 69.6428 | 93.1219 | 125.4967 | 170.3199 | 232.6075 | 319.4519 | 440.8968 | 611.1826 | 850.5239 | 1187.6449 | 1663.3992 | 2335.9392 |  | 32.6145 | 40.7617 | 51.1429 | 64.3979 | 81.355 | 103.0866 | 130.9825 | 166.8453 | 213.0145 | 272.5279 | 349.3326 | 448.5594 | 576.881 | 742.9796 | 958.1554 | 1237.1223 | 1599.045 | 2068.893 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 18.4016 | 26.5488 | 36.9299 | 50.185 | 67.1421 | 88.8736 | 116.7695 | 152.6324 | 198.8016 | 258.315 | 335.1197 | 434.3464 | 562.6681 | 728.7666 | 943.9424 | 1222.9093 | 1584.832 | 2051.881 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.65311 | 0.81626 | 1.0241 | 1.2896 | 1.6291 | 2.0643 | 2.6229 | 3.3411 | 4.2656 | 5.4574 | 6.9954 | 8.9825 | 11.5521 | 14.8782 | 19.1872 | 24.7735 | 32.0211 | 41.4298 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.36849 | 0.53164 | 0.73953 | 1.005 | 1.3445 | 1.7797 | 2.3383 | 3.0565 | 3.981 | 5.1728 | 6.7108 | 8.6978 | 11.2675 | 14.5936 | 18.9026 | 24.4889 | 31.7364 | 41.0891 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 18.77 | 27.0804 | 37.6695 | 51.19 | 68.4866 | 90.6533 | 119.1078 | 155.6888 | 202.7826 | 263.4878 | 341.8305 | 443.0442 | 573.9356 | 743.3603 | 962.845 | 1247.3982 | 1616.5685 | 2092.9702 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 33.7158 | 42.1381 | 52.8698 | 66.5725 | 84.1022 | 106.5675 | 135.4053 | 172.4791 | 220.2073 | 281.7303 | 361.1285 | 463.7058 | 596.3605 | 768.0677 | 990.5093 | 1278.896 | 1653.0398 | 2138.7531 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 19.0229 | 27.4452 | 38.1769 | 51.8796 | 69.4093 | 91.8746 | 120.7125 | 157.7863 | 205.5145 | 267.0375 | 346.4356 | 449.0129 | 581.6676 | 753.3748 | 975.8164 | 1264.2032 | 1638.3469 | 2121.1667 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 4.7448 | 5.9301 | 7.4404 | 9.3688 | 11.8357 | 14.9973 | 19.0556 | 24.273 | 30.9898 | 39.648 | 50.8217 | 65.2575 | 83.926 | 108.0904 | 139.3947 | 179.9794 | 232.6328 | 300.9874 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 2.6771 | 3.8624 | 5.3727 | 7.301 | 9.768 | 12.9295 | 16.9879 | 22.2053 | 28.9221 | 37.5803 | 48.754 | 63.1897 | 81.8583 | 106.0227 | 137.3269 | 177.9117 | 230.565 | 298.5124 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 28.9957 | 36.2389 | 45.4682 | 57.2525 | 72.3281 | 91.6484 | 116.449 | 148.3326 | 189.3789 | 242.2889 | 310.5715 | 398.7883 | 512.8717 | 660.5404 | 851.8408 | 1099.8542 | 1421.6189 | 1839.3337 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 |  | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 15.1244 | 20.0483 | 26.8073 | 36.1271 | 49.0305 | 66.9614 | 91.9615 | 126.9222 | 175.9429 | 244.8427 | 341.8907 | 478.8474 | 672.4534 |  | 16.3598 | 23.603 | 32.8323 | 44.6166 | 59.6922 | 79.0124 | 103.8131 | 135.6966 | 176.743 | 229.653 | 297.9356 | 386.1524 | 500.2358 | 647.9045 | 839.2049 | 1087.2183 | 1408.983 | 1824.2094 | 2282.6108 | 2275.8518 | 2266.532 | 2253.6286 | 2235.6977 | 2210.6975 | 2175.7368 | 2126.7162 | 2057.8163 | 1960.7684 | 1823.8116 | 1630.2056 |  | 56.8298 | 81.991 | 114.0513 | 154.9872 | 207.3561 | 274.47 | 360.6213 | 471.3771 | 613.9622 | 797.7585 | 1034.9557 | 1341.3993 | 1737.6973 | 2250.6622 | 2915.1932 | 3776.7314 | 4894.4634 | 6336.8586 | 7929.2334 | 7905.7544 | 7873.3796 | 7828.5564 | 7766.2688 | 7679.4243 | 7557.9795 | 7387.6936 | 7148.3523 | 6811.2313 | 6335.477 | 5662.9371
| TRUE | 3692 | 22008263 | SA | SA002 | 22 | SA2 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 27.3978 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 272.6948 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 11.0663 |  | 104.7864 | 1042.9568 | 42.3244 | 1000.6324 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 130.1598 | 162.2514 | 202.9172 | 254.5386 | 320.1736 | 403.7524 | 510.3287 | 646.4052 | 820.3535 | 1042.9568 | 1328.1111 | 1693.7315 | 2162.9238 | 2765.4998 | 3539.9358 | 4535.907 | 5817.5655 | 7467.7802 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 | 7712.8414 |  | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 42.3244 | 50.6597 | 67.1524 | 89.7919 | 121.009 | 164.2294 | 224.2896 | 308.0285 | 425.1306 | 589.3271 | 820.1097 | 1145.1755 | 1603.9171 | 2252.4075 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 34.032 | 42.4228 | 53.0554 | 66.5525 | 83.7136 | 105.5664 | 133.4322 | 169.0112 | 214.4922 | 272.6948 | 347.2522 | 442.8485 | 565.525 | 723.0764 | 925.5629 | 1185.9727 | 1521.0793 | 1952.5497 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 | 2016.6242 |  | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 11.0663 | 13.2456 | 17.5579 | 23.4773 | 31.6394 | 42.9399 | 58.6435 | 80.5381 | 111.156 | 154.0873 | 214.4285 | 299.4212 | 419.3653 | 588.9217 |  | 22.9657 | 31.3565 | 41.9891 | 55.4862 | 72.6473 | 94.5001 | 122.3659 | 157.9449 | 203.426 | 261.6285 | 336.1859 | 431.7822 | 554.4587 | 712.0101 | 914.4966 | 1174.9065 | 1510.013 | 1939.304 | 1999.0663 | 1993.1469 | 1984.9848 | 1973.6842 | 1957.9807 | 1936.086 | 1905.4681 | 1862.5368 | 1802.1956 | 1717.2029 | 1597.2589 | 1427.7025 |  | 87.8353 | 119.927 | 160.5928 | 212.2141 | 277.8492 | 361.4279 | 468.0042 | 604.0807 | 778.0291 | 1000.6324 | 1285.7867 | 1651.4071 | 2120.5994 | 2723.1753 | 3497.6113 | 4493.5826 | 5775.241 | 7417.1205 | 7645.6889 | 7623.0494 | 7591.8324 | 7548.612 | 7488.5518 | 7404.8128 | 7287.7108 | 7123.5143 | 6892.7316 | 6567.6659 | 6108.9243 | 5460.4339
| TRUE | 3693 | 22008264 | SA | SA003 | 22 | SA3 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 13.6989 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 136.3474 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.5331 |  | 91.0875 | 906.6094 | 36.7913 | 869.8181 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 113.1438 | 141.04 | 176.3895 | 221.2623 | 278.3168 | 350.9692 | 443.6126 | 561.8996 | 713.1074 | 906.6094 | 1154.485 | 1472.3073 | 1880.1614 | 2403.9616 | 3077.1543 | 3942.9207 | 5057.0258 | 6491.5054 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 |  | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 44.0369 | 58.3735 | 78.0533 | 105.1893 | 142.7594 | 194.9678 | 267.7595 | 369.5526 | 512.2834 | 712.8955 | 995.4649 | 1394.2344 | 1957.9466 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 17.016 | 21.2114 | 26.5277 | 33.2762 | 41.8568 | 52.7832 | 66.7161 | 84.5056 | 107.2461 | 136.3474 | 173.6261 | 221.4242 | 282.7625 | 361.5382 | 462.7815 | 592.9864 | 760.5396 | 976.2748 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 |  | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 6.6228 | 8.7789 | 11.7386 | 15.8197 | 21.47 | 29.3217 | 40.2691 | 55.578 | 77.0437 | 107.2143 | 149.7106 | 209.6826 | 294.4608 |  | 11.4829 | 15.6782 | 20.9946 | 27.7431 | 36.3237 | 47.2501 | 61.1829 | 78.9724 | 101.713 | 130.8143 | 168.0929 | 215.8911 | 277.2293 | 356.0051 | 457.2483 | 587.4532 | 755.0065 | 969.652 | 999.5331 | 996.5734 | 992.4924 | 986.8421 | 978.9903 | 968.043 | 952.7341 | 931.2684 | 901.0978 | 858.6015 | 798.6294 | 713.8512 |  | 76.3525 | 104.2487 | 139.5982 | 184.471 | 241.5255 | 314.1779 | 406.8213 | 525.1083 | 676.3161 | 869.8181 | 1117.6937 | 1435.516 | 1843.3701 | 2367.1703 | 3040.363 | 3906.1294 | 5020.2345 | 6447.4685 | 6646.1558 | 6626.476 | 6599.34 | 6561.7699 | 6509.5614 | 6436.7698 | 6334.9767 | 6192.2459 | 5991.6338 | 5709.0644 | 5310.2948 | 4746.5827
| TRUE | 3694 | 22008265 | SA | SA004 | 22 | SA4 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 13.6989 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 136.3474 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.5331 |  | 91.0875 | 906.6094 | 36.7913 | 869.8181 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 113.1438 | 141.04 | 176.3895 | 221.2623 | 278.3168 | 350.9692 | 443.6126 | 561.8996 | 713.1074 | 906.6094 | 1154.485 | 1472.3073 | 1880.1614 | 2403.9616 | 3077.1543 | 3942.9207 | 5057.0258 | 6491.5054 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 | 6704.5293 |  | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 36.7913 | 44.0369 | 58.3735 | 78.0533 | 105.1893 | 142.7594 | 194.9678 | 267.7595 | 369.5526 | 512.2834 | 712.8955 | 995.4649 | 1394.2344 | 1957.9466 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 17.016 | 21.2114 | 26.5277 | 33.2762 | 41.8568 | 52.7832 | 66.7161 | 84.5056 | 107.2461 | 136.3474 | 173.6261 | 221.4242 | 282.7625 | 361.5382 | 462.7815 | 592.9864 | 760.5396 | 976.2748 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 | 1008.3121 |  | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 5.5331 | 6.6228 | 8.7789 | 11.7386 | 15.8197 | 21.47 | 29.3217 | 40.2691 | 55.578 | 77.0437 | 107.2143 | 149.7106 | 209.6826 | 294.4608 |  | 11.4829 | 15.6782 | 20.9946 | 27.7431 | 36.3237 | 47.2501 | 61.1829 | 78.9724 | 101.713 | 130.8143 | 168.0929 | 215.8911 | 277.2293 | 356.0051 | 457.2483 | 587.4532 | 755.0065 | 969.652 | 999.5331 | 996.5734 | 992.4924 | 986.8421 | 978.9903 | 968.043 | 952.7341 | 931.2684 | 901.0978 | 858.6015 | 798.6294 | 713.8512 |  | 76.3525 | 104.2487 | 139.5982 | 184.471 | 241.5255 | 314.1779 | 406.8213 | 525.1083 | 676.3161 | 869.8181 | 1117.6937 | 1435.516 | 1843.3701 | 2367.1703 | 3040.363 | 3906.1294 | 5020.2345 | 6447.4685 | 6646.1558 | 6626.476 | 6599.34 | 6561.7699 | 6509.5614 | 6436.7698 | 6334.9767 | 6192.2459 | 5991.6338 | 5709.0644 | 5310.2948 | 4746.5827
| TRUE | 3695 | 22008266 | SA | SA005 | 22 | SA5 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 17.8715 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 177.8777 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 7.2185 |  | 95.2601 | 948.1397 | 38.4767 | 909.6631 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 118.3267 | 147.5009 | 184.4697 | 231.398 | 291.066 | 367.0465 | 463.9338 | 587.6393 | 745.7737 | 948.1397 | 1207.3701 | 1539.7513 | 1966.2885 | 2514.0832 | 3218.1138 | 4123.5395 | 5288.68 | 6788.8708 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 |  | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 46.0541 | 61.0475 | 81.6288 | 110.0078 | 149.299 | 203.899 | 280.0251 | 386.4812 | 535.7503 | 745.5521 | 1041.0655 | 1458.1021 | 2047.637 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 22.1989 | 27.6722 | 34.6078 | 43.4119 | 54.6061 | 68.8605 | 87.0373 | 110.2453 | 139.9124 | 177.8777 | 226.5112 | 288.8682 | 368.8897 | 471.6598 | 603.7409 | 773.6052 | 992.1938 | 1273.6402 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 |  | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 8.6401 | 11.4529 | 15.3141 | 20.6382 | 28.0095 | 38.2529 | 52.5347 | 72.5066 | 100.5106 | 139.8708 | 195.3113 | 273.5503 | 384.1512 |  | 14.9804 | 20.4537 | 27.3893 | 36.1934 | 47.3876 | 61.642 | 79.8188 | 103.0268 | 132.6939 | 170.6592 | 219.2927 | 281.6498 | 361.6712 | 464.4413 | 596.5224 | 766.3867 | 984.9753 | 1265.0002 | 1303.9828 | 1300.1216 | 1294.7975 | 1287.4262 | 1277.1829 | 1262.9011 | 1242.9292 | 1214.9252 | 1175.5649 | 1120.1245 | 1041.8855 | 931.2846 |  | 79.85 | 109.0242 | 145.993 | 192.9214 | 252.5894 | 328.5699 | 425.4571 | 549.1627 | 707.297 | 909.6631 | 1168.8935 | 1501.2746 | 1927.8119 | 2475.6065 | 3179.6371 | 4085.0628 | 5250.2034 | 6742.8166 | 6950.6055 | 6930.0242 | 6901.6451 | 6862.354 | 6807.754 | 6731.6279 | 6625.1718 | 6475.9027 | 6266.1009 | 5970.5875 | 5553.5509 | 4964.016
| TRUE | 3696 | 22008267 | SA | SA006 | 22 | SA6 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 17.8715 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 177.8777 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 7.2185 |  | 95.2601 | 948.1397 | 38.4767 | 909.6631 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 118.3267 | 147.5009 | 184.4697 | 231.398 | 291.066 | 367.0465 | 463.9338 | 587.6393 | 745.7737 | 948.1397 | 1207.3701 | 1539.7513 | 1966.2885 | 2514.0832 | 3218.1138 | 4123.5395 | 5288.68 | 6788.8708 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 |  | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 46.0541 | 61.0475 | 81.6288 | 110.0078 | 149.299 | 203.899 | 280.0251 | 386.4812 | 535.7503 | 745.5521 | 1041.0655 | 1458.1021 | 2047.637 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 22.1989 | 27.6722 | 34.6078 | 43.4119 | 54.6061 | 68.8605 | 87.0373 | 110.2453 | 139.9124 | 177.8777 | 226.5112 | 288.8682 | 368.8897 | 471.6598 | 603.7409 | 773.6052 | 992.1938 | 1273.6402 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 |  | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 8.6401 | 11.4529 | 15.3141 | 20.6382 | 28.0095 | 38.2529 | 52.5347 | 72.5066 | 100.5106 | 139.8708 | 195.3113 | 273.5503 | 384.1512 |  | 14.9804 | 20.4537 | 27.3893 | 36.1934 | 47.3876 | 61.642 | 79.8188 | 103.0268 | 132.6939 | 170.6592 | 219.2927 | 281.6498 | 361.6712 | 464.4413 | 596.5224 | 766.3867 | 984.9753 | 1265.0002 | 1303.9828 | 1300.1216 | 1294.7975 | 1287.4262 | 1277.1829 | 1262.9011 | 1242.9292 | 1214.9252 | 1175.5649 | 1120.1245 | 1041.8855 | 931.2846 |  | 79.85 | 109.0242 | 145.993 | 192.9214 | 252.5894 | 328.5699 | 425.4571 | 549.1627 | 707.297 | 909.6631 | 1168.8935 | 1501.2746 | 1927.8119 | 2475.6065 | 3179.6371 | 4085.0628 | 5250.2034 | 6742.8166 | 6950.6055 | 6930.0242 | 6901.6451 | 6862.354 | 6807.754 | 6731.6279 | 6625.1718 | 6475.9027 | 6266.1009 | 5970.5875 | 5553.5509 | 4964.016
| TRUE | 3697 | 22008210 | SA | SA007 | 22 | SA7 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 6.6 | 0.017308 | 1.3617e-05 | 0.017294 | 47.6003 | 0.9532 | 48.5536 | 49.2077 | 6.925 | 24.1753 |  | 15.598 | 0.17662 | 0.00013896 | 0.17648 | 485.7464 | 9.7271 | 495.4735 | 502.1485 | 70.6675 | 246.7017 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 7.2185 |  | 128.8616 | 1314.9911 | 38.4767 | 1276.5145 |  | 0.086007 |  | 7.1928 | 7.8388 | 8.5428 | 9.3101 | 10.1463 | 11.0575 | 12.0507 | 13.133 | 14.3125 | 15.598 | 16.9989 | 18.5257 | 20.1895 | 22.0028 | 23.979 | 26.1326 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021585 | 0.027005 | 0.033883 | 0.042625 | 0.053753 | 0.067937 | 0.086039 | 0.10917 | 0.13875 | 0.17662 | 0.22515 | 0.28739 | 0.36726 | 0.46984 | 0.60168 | 0.7712 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.6983e-05 | 2.1246e-05 | 2.6658e-05 | 3.3536e-05 | 4.2291e-05 | 5.345e-05 | 6.7692e-05 | 8.5889e-05 | 0.00010916 | 0.00013896 | 0.00017714 | 0.0002261 | 0.00028895 | 0.00036966 | 0.00047338 | 0.00060675 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 160.7095 | 201.0589 | 252.2657 | 317.3534 | 400.2052 | 505.8106 | 640.5852 | 812.7824 | 1033.0249 | 1314.9911 | 1676.3018 | 2139.6646 | 2734.3534 | 3498.1188 | 4479.6579 | 5741.8054 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 | 7011.653 |  | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 38.4767 | 46.0541 | 61.0475 | 81.6288 | 110.0078 | 149.299 | 203.899 | 280.0251 | 386.4812 | 535.7503 | 745.5521 | 1041.0655 | 1458.1021 | 2047.637 |  | 59.3647 | 74.2694 | 93.1847 | 117.2276 | 147.8323 | 186.8421 | 236.6266 | 300.2348 | 381.5905 | 485.7464 | 619.2114 | 790.3736 | 1010.0465 | 1292.1748 | 1654.7469 | 2120.9733 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 45.1518 | 60.0565 | 78.9718 | 103.0147 | 133.6194 | 172.6291 | 222.4137 | 286.0219 | 367.3775 | 471.5334 | 604.9984 | 776.1607 | 995.8335 | 1277.9619 | 1640.5339 | 2106.7603 | 2575.831 | 2573.032 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 1.1888 | 1.4873 | 1.866 | 2.3475 | 2.9604 | 3.7415 | 4.7385 | 6.0122 | 7.6414 | 9.7271 | 12.3998 | 15.8273 | 20.2263 | 25.8759 | 33.1365 | 42.4727 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.90417 | 1.2026 | 1.5814 | 2.0629 | 2.6757 | 3.4569 | 4.4539 | 5.7276 | 7.3568 | 9.4425 | 12.1152 | 15.5427 | 19.9417 | 25.5913 | 32.8519 | 42.1881 | 51.5813 | 51.5252 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 46.0559 | 61.2591 | 80.5532 | 105.0776 | 136.2951 | 176.086 | 226.8676 | 291.7495 | 374.7343 | 480.9759 | 617.1136 | 791.7034 | 1015.7752 | 1303.5532 | 1673.3858 | 2148.9484 | 2627.4123 | 2624.5572 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 61.3693 | 76.7773 | 96.3313 | 121.186 | 152.8242 | 193.1511 | 244.6168 | 310.3728 | 394.4756 | 502.1485 | 640.1202 | 817.0621 | 1044.1526 | 1335.8076 | 1710.6226 | 2192.592 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 46.6764 | 62.0844 | 81.6384 | 106.4932 | 138.1313 | 178.4583 | 229.9239 | 295.6799 | 379.7827 | 487.4556 | 625.4274 | 802.3692 | 1029.4598 | 1321.1147 | 1695.9297 | 2177.8991 | 2662.8089 | 2659.9153 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 8.6365 | 10.8049 | 13.5567 | 17.0545 | 21.507 | 27.1822 | 34.425 | 43.6789 | 55.5147 | 70.6675 | 90.0843 | 114.9854 | 146.9439 | 187.9886 | 240.7364 | 308.5641 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 6.5688 | 8.7372 | 11.489 | 14.9868 | 19.4393 | 25.1145 | 32.3573 | 41.6111 | 53.4469 | 68.5998 | 88.0166 | 112.9177 | 144.8762 | 185.9209 | 238.6687 | 306.4964 | 374.7379 | 374.3307 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 30.1502 | 37.7201 | 47.3268 | 59.5378 | 75.0813 | 94.8937 | 120.1783 | 152.4837 | 193.8028 | 246.7017 | 314.4861 | 401.4162 | 512.9841 | 656.2719 | 840.4155 | 1077.2034 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 | 1315.4358 |  | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 7.2185 | 8.6401 | 11.4529 | 15.3141 | 20.6382 | 28.0095 | 38.2529 | 52.5347 | 72.5066 | 100.5106 | 139.8708 | 195.3113 | 273.5503 | 384.1512 |  | 22.9317 | 30.5016 | 40.1083 | 52.3193 | 67.8628 | 87.6752 | 112.9598 | 145.2653 | 186.5843 | 239.4832 | 307.2676 | 394.1977 | 505.7656 | 649.0534 | 833.1971 | 1069.9849 | 1308.2173 | 1306.7957 | 1303.9828 | 1300.1216 | 1294.7975 | 1287.4262 | 1277.1829 | 1262.9011 | 1242.9292 | 1214.9252 | 1175.5649 | 1120.1245 | 1041.8855 | 931.2846 |  | 122.2329 | 162.5822 | 213.789 | 278.8768 | 361.7285 | 467.334 | 602.1086 | 774.3058 | 994.5483 | 1276.5145 | 1637.8251 | 2101.188 | 2695.8767 | 3459.6421 | 4441.1812 | 5703.3288 | 6973.1763 | 6965.5988 | 6950.6055 | 6930.0242 | 6901.6451 | 6862.354 | 6807.754 | 6731.6279 | 6625.1718 | 6475.9027 | 6266.1009 | 5970.5875 | 5553.5509 | 4964.016
| TRUE | 3698 | 22008268 | SA | SA008 | 22 | SA8 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.81881 | 1 |  | 5.8543 | 0.012795 | 1.4351e-05 | 0.01278 | 35.1894 | 1.0046 | 36.194 | 36.4008 | 5.1193 | 25.4787 |  | 13.88 | 0.12735 | 0.00014284 | 0.12721 | 350.2463 | 9.9989 | 360.2452 | 362.3031 | 50.9534 | 253.5937 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 10.2911 |  | 103.1928 | 1027.0954 | 41.6808 | 985.4146 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.7826e-05 | 2.2222e-05 | 2.7791e-05 | 3.4861e-05 | 4.385e-05 | 5.5297e-05 | 6.9893e-05 | 8.853e-05 | 0.00011235 | 0.00014284 | 0.0001819 | 0.00023197 | 0.00029623 | 0.00037876 | 0.00048482 | 0.00062123 | 0.00079676 | 0.0010228 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 0.0010563 | 128.1803 | 159.7839 | 199.8312 | 250.6675 | 315.3044 | 397.6121 | 502.5675 | 636.5746 | 807.8775 | 1027.0954 | 1307.913 | 1667.973 | 2130.0298 | 2723.4417 | 3486.1 | 4466.9244 | 5729.0912 | 7354.2093 | 7595.5435 | 7595.5435 | 7595.5435 | 7595.5435 | 7595.5435 | 7595.5435 | 7595.5435 | 7595.5435 | 7595.5435 | 7595.5435 | 7595.5435 | 7595.5435 |  | 41.6808 | 41.6808 | 41.6808 | 41.6808 | 41.6808 | 41.6808 | 41.6808 | 41.6808 | 41.6808 | 41.6808 | 41.6808 | 41.6808 | 41.6808 | 41.6808 | 41.6808 | 41.6808 | 41.6808 | 49.8893 | 66.1312 | 88.4263 | 119.1686 | 161.7317 | 220.8785 | 303.344 | 418.6652 | 580.3645 | 807.6374 | 1127.7595 | 1579.5245 | 2218.1526 |  | 43.7103 | 54.4874 | 68.1438 | 85.4793 | 107.5209 | 135.5884 | 171.3789 | 217.0762 | 275.4916 | 350.2463 | 446.007 | 568.7899 | 726.3543 | 928.7117 | 1188.7832 | 1523.2508 | 1953.6581 | 2507.8341 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 | 2590.1307 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 29.4969 | 40.2739 | 53.9304 | 71.2659 | 93.3075 | 121.3749 | 157.1654 | 202.8627 | 261.2782 | 336.0329 | 431.7936 | 554.5764 | 712.1409 | 914.4983 | 1174.5698 | 1509.0374 | 1939.4447 | 2490.8215 | 2567.5795 | 2559.9767 | 2549.4934 | 2534.9791 | 2514.8096 | 2486.6884 | 2447.3631 | 2392.2225 | 2314.721 | 2205.5572 | 2051.5024 | 1833.726 |  | 1.2478 | 1.5555 | 1.9454 | 2.4403 | 3.0695 | 3.8708 | 4.8925 | 6.1971 | 7.8648 | 9.9989 | 12.7327 | 16.2379 | 20.736 | 26.513 | 33.9375 | 43.4859 | 55.7732 | 71.5939 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 | 73.9433 |  | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.48568 | 0.64379 | 0.86084 | 1.1601 | 1.5745 | 2.1503 | 2.9531 | 4.0757 | 5.6499 | 7.8624 | 10.9788 | 15.3768 | 21.5939 |  | 0.84208 | 1.1497 | 1.5396 | 2.0345 | 2.6638 | 3.465 | 4.4868 | 5.7913 | 7.459 | 9.5931 | 12.3269 | 15.8321 | 20.3303 | 26.1072 | 33.5317 | 43.0802 | 55.3675 | 71.1082 | 73.2995 | 73.0825 | 72.7832 | 72.3689 | 71.7931 | 70.9902 | 69.8676 | 68.2934 | 66.0809 | 62.9645 | 58.5665 | 52.3494 |  | 30.339 | 41.4237 | 55.47 | 73.3004 | 95.9712 | 124.84 | 161.6522 | 208.6541 | 268.7372 | 345.626 | 444.1205 | 570.4085 | 732.4711 | 940.6055 | 1208.1015 | 1552.1176 | 1994.8121 | 2561.9298 | 2640.8791 | 2633.0592 | 2622.2766 | 2607.3479 | 2586.6027 | 2557.6786 | 2517.2307 | 2460.516 | 2380.8019 | 2268.5217 | 2110.0689 | 1886.0754 |  | 45.215 | 56.363 | 70.4895 | 88.4218 | 111.2221 | 140.2558 | 177.2783 | 224.5487 | 284.975 | 362.3031 | 461.3602 | 588.3696 | 751.358 | 960.6813 | 1229.7054 | 1575.6866 | 2020.91 | 2594.1628 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 | 2679.2923 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 30.5123 | 41.6603 | 55.7868 | 73.7191 | 96.5194 | 125.5531 | 162.5756 | 209.846 | 270.2723 | 347.6004 | 446.6575 | 573.6669 | 736.6553 | 945.9786 | 1215.0027 | 1560.9839 | 2006.2073 | 2576.5646 | 2655.9648 | 2648.1003 | 2637.2561 | 2622.2422 | 2601.3784 | 2572.2891 | 2531.6101 | 2474.5714 | 2394.402 | 2281.4804 | 2122.1224 | 1896.8494 |  | 6.3589 | 7.9267 | 9.9135 | 12.4354 | 15.642 | 19.7252 | 24.932 | 31.5799 | 40.0781 | 50.9534 | 64.8845 | 82.7468 | 105.6691 | 135.1077 | 172.9426 | 221.6005 | 284.2156 | 364.8364 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 | 376.8088 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 4.2912 | 5.859 | 7.8457 | 10.3677 | 13.5742 | 17.6575 | 22.8642 | 29.5122 | 38.0104 | 48.8856 | 62.8168 | 80.679 | 103.6013 | 133.04 | 170.8748 | 219.5328 | 282.1478 | 362.3614 | 373.5281 | 372.422 | 370.8969 | 368.7854 | 365.8512 | 361.7601 | 356.0391 | 348.0174 | 336.7425 | 320.8615 | 298.4498 | 266.768 |  | 31.6482 | 39.4512 | 49.3391 | 61.8908 | 77.8498 | 98.1719 | 124.0858 | 157.1727 | 199.468 | 253.5937 | 322.9287 | 411.8288 | 525.9124 | 672.4281 | 860.7313 | 1102.9005 | 1414.5343 | 1815.7821 | 1875.3684 | 1875.3684 | 1875.3684 | 1875.3684 | 1875.3684 | 1875.3684 | 1875.3684 | 1875.3684 | 1875.3684 | 1875.3684 | 1875.3684 | 1875.3684 |  | 10.2911 | 10.2911 | 10.2911 | 10.2911 | 10.2911 | 10.2911 | 10.2911 | 10.2911 | 10.2911 | 10.2911 | 10.2911 | 10.2911 | 10.2911 | 10.2911 | 10.2911 | 10.2911 | 10.2911 | 12.3178 | 16.328 | 21.8328 | 29.4232 | 39.9322 | 54.5357 | 74.8968 | 103.37 | 143.2942 | 199.4087 | 278.4481 | 389.9906 | 547.6703 |  | 21.3571 | 29.1601 | 39.048 | 51.5996 | 67.5587 | 87.8808 | 113.7947 | 146.8815 | 189.1769 | 243.3026 | 312.6375 | 401.5377 | 515.6213 | 662.1369 | 850.4401 | 1092.6094 | 1404.2432 | 1803.4642 | 1859.0404 | 1853.5356 | 1845.9452 | 1835.4362 | 1820.8327 | 1800.4717 | 1771.9984 | 1732.0742 | 1675.9597 | 1596.9203 | 1485.3779 | 1327.6982 |  | 86.4995 | 118.1031 | 158.1505 | 208.9867 | 273.6236 | 355.9313 | 460.8868 | 594.8938 | 766.1967 | 985.4146 | 1266.2323 | 1626.2922 | 2088.3491 | 2681.7609 | 3444.4192 | 4425.2436 | 5687.4104 | 7304.32 | 7529.4123 | 7507.1171 | 7476.3748 | 7433.8117 | 7374.6649 | 7292.1995 | 7176.8783 | 7015.179 | 6787.9061 | 6467.784 | 6016.019 | 5377.3909
| TRUE | 3699 | 22009778 | SA | SA009 | 22 | SA9 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 31.2839 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 311.3734 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 12.6359 |  | 108.6725 | 1081.6354 | 43.8941 | 1037.7414 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 134.9868 | 168.2686 | 210.4425 | 263.9783 | 332.0474 | 418.7258 | 529.2545 | 670.3775 | 850.7768 | 1081.6354 | 1377.3648 | 1756.5444 | 2243.1371 | 2868.0598 | 3671.2162 | 4704.1236 | 6033.313 | 7744.7269 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 | 7998.8763 |  | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 43.8941 | 52.5384 | 69.6428 | 93.1219 | 125.4967 | 170.3199 | 232.6075 | 319.4519 | 440.8968 | 611.1826 | 850.5239 | 1187.6449 | 1663.3992 | 2335.9392 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 38.859 | 48.44 | 60.5807 | 75.9922 | 95.5874 | 120.5398 | 152.358 | 192.9835 | 244.9155 | 311.3734 | 396.5059 | 505.6614 | 645.7382 | 825.6365 | 1056.8434 | 1354.1893 | 1736.8268 | 2229.4964 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 | 2302.659 |  | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 12.6359 | 15.1244 | 20.0483 | 26.8073 | 36.1271 | 49.0305 | 66.9614 | 91.9615 | 126.9222 | 175.9429 | 244.8427 | 341.8907 | 478.8474 | 672.4534 |  | 26.2231 | 35.804 | 47.9448 | 63.3563 | 82.9515 | 107.9039 | 139.7221 | 180.3475 | 232.2796 | 298.7375 | 383.87 | 493.0255 | 633.1023 | 813.0006 | 1044.2074 | 1341.5534 | 1724.1909 | 2214.372 | 2282.6108 | 2275.8518 | 2266.532 | 2253.6286 | 2235.6977 | 2210.6975 | 2175.7368 | 2126.7162 | 2057.8163 | 1960.7684 | 1823.8116 | 1630.2056 |  | 91.0927 | 124.3745 | 166.5485 | 220.0842 | 288.1533 | 374.8317 | 485.3604 | 626.4834 | 806.8827 | 1037.7414 | 1333.4708 | 1712.6504 | 2199.243 | 2824.1658 | 3627.3221 | 4660.2295 | 5989.4189 | 7692.1884 | 7929.2334 | 7905.7544 | 7873.3796 | 7828.5564 | 7766.2688 | 7679.4243 | 7557.9795 | 7387.6936 | 7148.3523 | 6811.2313 | 6335.477 | 5662.9371
| TRUE | 3700 | 22009859 | SA | Blank | 66 | CB CB A | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 2.6788 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 7.9912 | 0.028405 | 0 | 0.028405 | 149.1264 | 0 | 149.1264 | 80.631 | 11.3649 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 241.1223 | 43.8691 | 197.2531 |  | 0.1093 |  | 2.9882 | 3.3333 | 3.7183 | 4.1477 | 4.6268 | 5.1611 | 5.7572 | 6.4221 | 7.1638 | 7.9912 | 8.9141 | 9.9436 | 11.092 | 12.373 | 13.802 | 15.3961 | 17.1742 | 19.1577 | 21.3702 | 23.8383 | 26.5915 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0056115 | 0.007231 | 0.0093884 | 0.012274 | 0.016146 | 0.021361 | 0.028405 | 0.037944 | 0.050895 | 0.068518 | 0.092545 | 0.12536 | 0.17026 | 0.23179 | 0.31619 | 0.43213 | 0.59157 | 0.81102 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 47.6348 | 61.3818 | 79.6953 | 104.1878 | 137.0619 | 181.3307 | 241.1223 | 322.0989 | 432.0374 | 581.629 | 785.5863 | 1064.1731 | 1445.3211 | 1967.5575 | 2684.0594 | 3668.2653 | 5021.6476 | 6884.4791 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 29.4606 | 37.9627 | 49.289 | 64.4368 | 84.7684 | 112.1473 | 149.1264 | 199.2079 | 267.2013 | 359.719 | 485.86 | 658.1571 | 893.885 | 1216.8715 | 1660.0051 | 2268.705 | 3105.7288 | 4257.8307 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 2.329 | 10.831 | 22.1573 | 37.3052 | 57.6367 | 85.0156 | 121.9948 | 172.0763 | 240.0697 | 332.5873 | 458.7284 | 631.0255 | 866.7533 | 1189.7399 | 1627.5302 | 2225.6576 | 3048.1686 | 4180.2591 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2.329 | 10.831 | 22.1573 | 37.3052 | 57.6367 | 85.0156 | 121.9948 | 172.0763 | 240.0697 | 332.5873 | 458.7284 | 631.0255 | 866.7533 | 1189.7399 | 1627.5302 | 2225.6576 | 3048.1686 | 4180.2591 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 15.929 | 20.526 | 26.65 | 34.8403 | 45.8333 | 60.6368 | 80.631 | 107.7095 | 144.4728 | 194.496 | 262.6991 | 355.8582 | 483.3136 | 657.9488 | 897.5461 | 1226.6633 | 1679.2327 | 2302.1612 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 1.2592 | 5.8562 | 11.9802 | 20.1705 | 31.1635 | 45.967 | 65.9612 | 93.0397 | 129.803 | 179.8262 | 248.0293 | 341.1884 | 468.6438 | 643.279 | 879.9873 | 1203.3881 | 1648.1105 | 2260.2191 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.2452 | 2.8931 | 3.7563 | 4.9107 | 6.4602 | 8.5467 | 11.3649 | 15.1815 | 20.3633 | 27.414 | 37.0272 | 50.1578 | 68.1225 | 92.7372 | 126.5082 | 172.8969 | 236.6861 | 324.4872 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0.17749 | 0.82543 | 1.6886 | 2.843 | 4.3925 | 6.479 | 9.2972 | 13.1138 | 18.2956 | 25.3463 | 34.9595 | 48.0902 | 66.0549 | 90.6695 | 124.0333 | 169.6163 | 232.2995 | 318.5756 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 3.7657 | 17.5126 | 35.8261 | 60.3186 | 93.1928 | 137.4616 | 197.2531 | 278.2298 | 388.1683 | 537.7598 | 741.7171 | 1020.304 | 1401.4519 | 1923.6884 | 2631.5508 | 3598.662 | 4928.5786 | 6759.0538 | 7824.1106 | 7761.8584 | 7675.0633 | 7553.6874 | 7383.4983 | 7144.2929 | 6807.3633 | 6331.8792 | 5659.7211
| TRUE | 3701 | 22009860 | SA | Blank | 66 | CB CB B | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 2.6788 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 7.9912 | 0.028405 | 0 | 0.028405 | 149.1264 | 0 | 149.1264 | 80.631 | 11.3649 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 241.1223 | 43.8691 | 197.2531 |  | 0.1093 |  | 2.9882 | 3.3333 | 3.7183 | 4.1477 | 4.6268 | 5.1611 | 5.7572 | 6.4221 | 7.1638 | 7.9912 | 8.9141 | 9.9436 | 11.092 | 12.373 | 13.802 | 15.3961 | 17.1742 | 19.1577 | 21.3702 | 23.8383 | 26.5915 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0056115 | 0.007231 | 0.0093884 | 0.012274 | 0.016146 | 0.021361 | 0.028405 | 0.037944 | 0.050895 | 0.068518 | 0.092545 | 0.12536 | 0.17026 | 0.23179 | 0.31619 | 0.43213 | 0.59157 | 0.81102 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 47.6348 | 61.3818 | 79.6953 | 104.1878 | 137.0619 | 181.3307 | 241.1223 | 322.0989 | 432.0374 | 581.629 | 785.5863 | 1064.1731 | 1445.3211 | 1967.5575 | 2684.0594 | 3668.2653 | 5021.6476 | 6884.4791 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 29.4606 | 37.9627 | 49.289 | 64.4368 | 84.7684 | 112.1473 | 149.1264 | 199.2079 | 267.2013 | 359.719 | 485.86 | 658.1571 | 893.885 | 1216.8715 | 1660.0051 | 2268.705 | 3105.7288 | 4257.8307 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 2.329 | 10.831 | 22.1573 | 37.3052 | 57.6367 | 85.0156 | 121.9948 | 172.0763 | 240.0697 | 332.5873 | 458.7284 | 631.0255 | 866.7533 | 1189.7399 | 1627.5302 | 2225.6576 | 3048.1686 | 4180.2591 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2.329 | 10.831 | 22.1573 | 37.3052 | 57.6367 | 85.0156 | 121.9948 | 172.0763 | 240.0697 | 332.5873 | 458.7284 | 631.0255 | 866.7533 | 1189.7399 | 1627.5302 | 2225.6576 | 3048.1686 | 4180.2591 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 15.929 | 20.526 | 26.65 | 34.8403 | 45.8333 | 60.6368 | 80.631 | 107.7095 | 144.4728 | 194.496 | 262.6991 | 355.8582 | 483.3136 | 657.9488 | 897.5461 | 1226.6633 | 1679.2327 | 2302.1612 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 1.2592 | 5.8562 | 11.9802 | 20.1705 | 31.1635 | 45.967 | 65.9612 | 93.0397 | 129.803 | 179.8262 | 248.0293 | 341.1884 | 468.6438 | 643.279 | 879.9873 | 1203.3881 | 1648.1105 | 2260.2191 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.2452 | 2.8931 | 3.7563 | 4.9107 | 6.4602 | 8.5467 | 11.3649 | 15.1815 | 20.3633 | 27.414 | 37.0272 | 50.1578 | 68.1225 | 92.7372 | 126.5082 | 172.8969 | 236.6861 | 324.4872 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0.17749 | 0.82543 | 1.6886 | 2.843 | 4.3925 | 6.479 | 9.2972 | 13.1138 | 18.2956 | 25.3463 | 34.9595 | 48.0902 | 66.0549 | 90.6695 | 124.0333 | 169.6163 | 232.2995 | 318.5756 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 3.7657 | 17.5126 | 35.8261 | 60.3186 | 93.1928 | 137.4616 | 197.2531 | 278.2298 | 388.1683 | 537.7598 | 741.7171 | 1020.304 | 1401.4519 | 1923.6884 | 2631.5508 | 3598.662 | 4928.5786 | 6759.0538 | 7824.1106 | 7761.8584 | 7675.0633 | 7553.6874 | 7383.4983 | 7144.2929 | 6807.3633 | 6331.8792 | 5659.7211
| TRUE | 3702 | 22009861 | SA | Blank | 66 | CB CB B | CB FAIL | Y | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 2.6788 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 7.9912 | 0.028405 | 0 | 0.028405 | 149.1264 | 0 | 149.1264 | 80.631 | 11.3649 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 241.1223 | 43.8691 | 197.2531 |  | 0.1093 |  | 2.9882 | 3.3333 | 3.7183 | 4.1477 | 4.6268 | 5.1611 | 5.7572 | 6.4221 | 7.1638 | 7.9912 | 8.9141 | 9.9436 | 11.092 | 12.373 | 13.802 | 15.3961 | 17.1742 | 19.1577 | 21.3702 | 23.8383 | 26.5915 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0056115 | 0.007231 | 0.0093884 | 0.012274 | 0.016146 | 0.021361 | 0.028405 | 0.037944 | 0.050895 | 0.068518 | 0.092545 | 0.12536 | 0.17026 | 0.23179 | 0.31619 | 0.43213 | 0.59157 | 0.81102 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 47.6348 | 61.3818 | 79.6953 | 104.1878 | 137.0619 | 181.3307 | 241.1223 | 322.0989 | 432.0374 | 581.629 | 785.5863 | 1064.1731 | 1445.3211 | 1967.5575 | 2684.0594 | 3668.2653 | 5021.6476 | 6884.4791 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 29.4606 | 37.9627 | 49.289 | 64.4368 | 84.7684 | 112.1473 | 149.1264 | 199.2079 | 267.2013 | 359.719 | 485.86 | 658.1571 | 893.885 | 1216.8715 | 1660.0051 | 2268.705 | 3105.7288 | 4257.8307 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 2.329 | 10.831 | 22.1573 | 37.3052 | 57.6367 | 85.0156 | 121.9948 | 172.0763 | 240.0697 | 332.5873 | 458.7284 | 631.0255 | 866.7533 | 1189.7399 | 1627.5302 | 2225.6576 | 3048.1686 | 4180.2591 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2.329 | 10.831 | 22.1573 | 37.3052 | 57.6367 | 85.0156 | 121.9948 | 172.0763 | 240.0697 | 332.5873 | 458.7284 | 631.0255 | 866.7533 | 1189.7399 | 1627.5302 | 2225.6576 | 3048.1686 | 4180.2591 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 15.929 | 20.526 | 26.65 | 34.8403 | 45.8333 | 60.6368 | 80.631 | 107.7095 | 144.4728 | 194.496 | 262.6991 | 355.8582 | 483.3136 | 657.9488 | 897.5461 | 1226.6633 | 1679.2327 | 2302.1612 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 1.2592 | 5.8562 | 11.9802 | 20.1705 | 31.1635 | 45.967 | 65.9612 | 93.0397 | 129.803 | 179.8262 | 248.0293 | 341.1884 | 468.6438 | 643.279 | 879.9873 | 1203.3881 | 1648.1105 | 2260.2191 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.2452 | 2.8931 | 3.7563 | 4.9107 | 6.4602 | 8.5467 | 11.3649 | 15.1815 | 20.3633 | 27.414 | 37.0272 | 50.1578 | 68.1225 | 92.7372 | 126.5082 | 172.8969 | 236.6861 | 324.4872 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0.17749 | 0.82543 | 1.6886 | 2.843 | 4.3925 | 6.479 | 9.2972 | 13.1138 | 18.2956 | 25.3463 | 34.9595 | 48.0902 | 66.0549 | 90.6695 | 124.0333 | 169.6163 | 232.2995 | 318.5756 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 3.7657 | 17.5126 | 35.8261 | 60.3186 | 93.1928 | 137.4616 | 197.2531 | 278.2298 | 388.1683 | 537.7598 | 741.7171 | 1020.304 | 1401.4519 | 1923.6884 | 2631.5508 | 3598.662 | 4928.5786 | 6759.0538 | 7824.1106 | 7761.8584 | 7675.0633 | 7553.6874 | 7383.4983 | 7144.2929 | 6807.3633 | 6331.8792 | 5659.7211
| FALSE | 3703 | 22009856 | SA | SA-KTS NO.1 | 66 | KTS NO.1 LINE | DISTANCE & DIR EF | Y | Siemens | 7SD522 | 7SD522 | SIEMENS 7SD522 | Digital |  | 0.016937 | 1 |  | 2.6788 | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.010621 |  | 7.9912 | 0.028405 | 6.5904e-07 | 0.028404 | 149.1268 | 0.072494 | 149.1993 | 80.6347 | 11.3649 | 0.058377 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.010621 |  | 43.8937 | 241.2572 | 43.8937 | 197.3635 |  | 0.1093 |  | 2.9882 | 3.3333 | 3.7183 | 4.1477 | 4.6268 | 5.1611 | 5.7572 | 6.4221 | 7.1638 | 7.9912 | 8.9141 | 9.9436 | 11.092 | 12.373 | 13.802 | 15.3961 | 17.1742 | 19.1577 | 21.3702 | 23.8383 | 26.5915 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0056115 | 0.007231 | 0.0093884 | 0.012274 | 0.016146 | 0.021361 | 0.028405 | 0.037944 | 0.050895 | 0.068518 | 0.092545 | 0.12536 | 0.17026 | 0.23179 | 0.31619 | 0.43213 | 0.59157 | 0.81102 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.302e-07 | 1.6777e-07 | 2.1782e-07 | 2.8477e-07 | 3.7462e-07 | 4.9562e-07 | 6.5904e-07 | 8.8036e-07 | 1.1808e-06 | 1.5897e-06 | 2.1472e-06 | 2.9086e-06 | 3.9504e-06 | 5.3778e-06 | 7.3361e-06 | 1.0026e-05 | 1.3725e-05 | 1.8817e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 43.8937 | 43.8937 | 43.8937 | 47.6615 | 61.4161 | 79.7399 | 104.2461 | 137.1386 | 181.4322 | 241.2572 | 322.2792 | 432.2792 | 581.9545 | 786.026 | 1064.7688 | 1446.1301 | 1968.6588 | 2685.5618 | 3670.3186 | 5024.4584 | 6888.3327 | 7998.8085 | 7998.8085 | 7998.8085 | 7998.8085 | 7998.8085 | 7998.8085 | 7998.8085 | 7998.8085 | 7998.8085 |  | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 52.538 | 69.6422 | 93.1211 | 125.4956 | 170.3185 | 232.6055 | 319.4492 | 440.8931 | 611.1774 | 850.5167 | 1187.6349 | 1663.3851 | 2335.9194 |  | 27.1317 | 27.1317 | 27.1317 | 29.4607 | 37.9628 | 49.2891 | 64.437 | 84.7686 | 112.1475 | 149.1268 | 199.2084 | 267.202 | 359.7198 | 485.8612 | 658.1587 | 893.887 | 1216.8744 | 1660.009 | 2268.7103 | 3105.736 | 4257.8406 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 0 | 0 | 0 | 2.329 | 10.831 | 22.1574 | 37.3052 | 57.6369 | 85.0158 | 121.995 | 172.0767 | 240.0702 | 332.5881 | 458.7294 | 631.0269 | 866.7553 | 1189.7426 | 1627.534 | 2225.6628 | 3048.1757 | 4180.2688 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.013189 | 0.013189 | 0.013189 | 0.014322 | 0.018455 | 0.023961 | 0.031324 | 0.041208 | 0.054518 | 0.072494 | 0.09684 | 0.12989 | 0.17487 | 0.23619 | 0.31995 | 0.43454 | 0.59155 | 0.80697 | 1.1029 | 1.5098 | 2.0698 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015787 | 0.020926 | 0.027982 | 0.03771 | 0.051178 | 0.069894 | 0.09599 | 0.13248 | 0.18365 | 0.25557 | 0.35687 | 0.49982 | 0.70191 |  | 0 | 0 | 0 | 0.0011322 | 0.0052652 | 0.010771 | 0.018135 | 0.028019 | 0.041328 | 0.059305 | 0.083651 | 0.1167 | 0.16168 | 0.223 | 0.30676 | 0.42135 | 0.57836 | 0.79118 | 1.0819 | 1.4818 | 2.0321 | 2.3523 | 2.3336 | 2.3075 | 2.271 | 2.2199 | 2.148 | 2.0467 | 1.9037 | 1.7016 |  | 0 | 0 | 0 | 2.3301 | 10.8363 | 22.1681 | 37.3234 | 57.6649 | 85.0571 | 122.0543 | 172.1603 | 240.1869 | 332.7497 | 458.9524 | 631.3337 | 867.1767 | 1190.321 | 1628.3252 | 2226.7447 | 3049.6575 | 4182.3009 | 4841.3263 | 4802.8065 | 4749.1003 | 4673.9965 | 4568.6886 | 4420.6754 | 4212.1934 | 3917.978 | 3502.0667 |  | 14.6705 | 14.6705 | 14.6705 | 15.9298 | 20.5269 | 26.6512 | 34.8419 | 45.8355 | 60.6396 | 80.6347 | 107.7145 | 144.4795 | 194.505 | 262.7113 | 355.8747 | 483.336 | 657.9793 | 897.5878 | 1226.7202 | 1679.3106 | 2302.268 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 0 | 0 | 0 | 1.2593 | 5.8565 | 11.9808 | 20.1714 | 31.165 | 45.9691 | 65.9643 | 93.044 | 129.809 | 179.8346 | 248.0408 | 341.2042 | 468.6655 | 643.3088 | 880.0281 | 1203.4439 | 1648.187 | 2260.324 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 2.0677 | 2.0677 | 2.0677 | 2.2452 | 2.8931 | 3.7563 | 4.9107 | 6.4602 | 8.5467 | 11.3649 | 15.1815 | 20.3633 | 27.414 | 37.0272 | 50.1579 | 68.1226 | 92.7373 | 126.5083 | 172.897 | 236.6863 | 324.4874 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0.17749 | 0.82543 | 1.6886 | 2.843 | 4.3925 | 6.479 | 9.2972 | 13.1139 | 18.2956 | 25.3463 | 34.9595 | 48.0902 | 66.0549 | 90.6696 | 124.0334 | 169.6164 | 232.2996 | 318.5757 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.010621 | 0.010621 | 0.010621 | 0.011533 | 0.014861 | 0.019295 | 0.025224 | 0.033184 | 0.043901 | 0.058377 | 0.077982 | 0.1046 | 0.14082 | 0.1902 | 0.25764 | 0.34992 | 0.47636 | 0.64983 | 0.88811 | 1.2158 | 1.6668 | 1.9355 | 1.9355 | 1.9355 | 1.9355 | 1.9355 | 1.9355 | 1.9355 | 1.9355 | 1.9355 |  | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.012713 | 0.016851 | 0.022533 | 0.030366 | 0.041212 | 0.056284 | 0.077297 | 0.10668 | 0.14789 | 0.2058 | 0.28737 | 0.40249 | 0.56522 |  | 0 | 0 | 0 | 0.00091169 | 0.0042399 | 0.0086737 | 0.014604 | 0.022563 | 0.03328 | 0.047756 | 0.067361 | 0.093978 | 0.13019 | 0.17957 | 0.24702 | 0.3393 | 0.46574 | 0.63711 | 0.87126 | 1.1932 | 1.6364 | 1.8943 | 1.8792 | 1.8582 | 1.8288 | 1.7876 | 1.7297 | 1.6481 | 1.533 | 1.3703 |  | 0 | 0 | 0 | 3.7678 | 17.5224 | 35.8462 | 60.3524 | 93.2449 | 137.5385 | 197.3635 | 278.3855 | 388.3855 | 538.0608 | 742.1323 | 1020.8751 | 1402.2364 | 1924.7651 | 2633.0238 | 3600.6763 | 4931.3373 | 6762.8371 | 7828.4901 | 7766.203 | 7679.3593 | 7557.9155 | 7387.6311 | 7148.2918 | 6811.1737 | 6335.4234 | 5662.8891
| FALSE | 3704 | 22009855 | SA | SA-KTS NO.1 | 66 | KTS NO.1 LINE | CURRENT DIFF & DEF | X | Schweitzer | SEL_311L | SEL 311L | SEL 300s | Digital |  | 0.15703 | 1 |  | 3.2146 | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.09847 |  | 9.9777 | 0.051368 | 1.105e-05 | 0.051357 | 269.6904 | 1.2155 | 270.9059 | 145.8782 | 20.5526 | 0.97878 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.09847 |  | 44.0968 | 438.3155 | 44.0968 | 394.2187 |  | 0.11326 |  | 3.6001 | 4.0319 | 4.5154 | 5.0569 | 5.6634 | 6.3426 | 7.1033 | 7.9551 | 8.9092 | 9.9777 | 11.1743 | 12.5144 | 14.0152 | 15.696 | 17.5784 | 19.6866 | 22.0476 | 24.6917 | 27.6529 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0052615 | 0.006829 | 0.0089371 | 0.011784 | 0.015645 | 0.020898 | 0.02807 | 0.037889 | 0.051368 | 0.069918 | 0.095498 | 0.13084 | 0.17976 | 0.24758 | 0.34173 | 0.47259 | 0.65469 | 0.90833 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1318e-06 | 1.469e-06 | 1.9224e-06 | 2.5349e-06 | 3.3653e-06 | 4.4953e-06 | 6.038e-06 | 8.1501e-06 | 1.105e-05 | 1.504e-05 | 2.0542e-05 | 2.8145e-05 | 3.8668e-05 | 5.3257e-05 | 7.3509e-05 | 0.00010166 | 0.00014083 | 0.00019539 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 44.0968 | 44.8951 | 58.2704 | 76.2582 | 100.5529 | 133.4943 | 178.3193 | 239.5126 | 323.2966 | 438.3155 | 596.5913 | 814.8618 | 1116.4508 | 1533.8871 | 2112.5713 | 2915.9114 | 4032.519 | 5586.293 | 7750.5565 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 |  | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 52.7811 | 69.9645 | 93.552 | 126.0763 | 171.1065 | 233.6818 | 320.9274 | 442.9331 | 614.0054 | 854.4522 | 1193.1303 | 1671.0819 | 2346.7281 |  | 27.1322 | 27.6234 | 35.8531 | 46.9208 | 61.869 | 82.1375 | 109.7178 | 147.3693 | 198.9207 | 269.6904 | 367.0757 | 501.375 | 686.9392 | 943.7829 | 1299.8405 | 1794.1264 | 2481.162 | 3437.1811 | 4768.8273 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 0 | 0.4912 | 8.7208 | 19.7885 | 34.7368 | 55.0053 | 82.5856 | 120.2371 | 171.7884 | 242.5582 | 339.9435 | 474.2428 | 659.8069 | 916.6506 | 1272.7083 | 1766.9941 | 2454.0298 | 3404.7055 | 4725.7789 | 4886.7853 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.12228 | 0.1245 | 0.16159 | 0.21147 | 0.27884 | 0.37019 | 0.49449 | 0.66418 | 0.89652 | 1.2155 | 1.6544 | 2.2596 | 3.096 | 4.2535 | 5.8583 | 8.0859 | 11.1823 | 15.491 | 21.4926 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0 | 0.0022138 | 0.039304 | 0.089185 | 0.15656 | 0.2479 | 0.3722 | 0.5419 | 0.77423 | 1.0932 | 1.5321 | 2.1374 | 2.9737 | 4.1313 | 5.736 | 7.9637 | 11.0601 | 15.3447 | 21.2986 | 22.0242 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 0 | 0.49341 | 8.7601 | 19.8777 | 34.8933 | 55.2532 | 82.9578 | 120.779 | 172.5626 | 243.6513 | 341.4756 | 476.3801 | 662.7806 | 920.7819 | 1278.4442 | 1774.9578 | 2465.0898 | 3420.0501 | 4747.0776 | 4908.8095 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 14.6761 | 14.9418 | 19.3933 | 25.3799 | 33.4656 | 44.429 | 59.3474 | 79.7135 | 107.5981 | 145.8782 | 198.5548 | 271.1986 | 371.5721 | 510.5014 | 703.0964 | 970.4604 | 1342.0847 | 1859.2047 | 2579.5051 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0.26569 | 4.7172 | 10.7038 | 18.7895 | 29.7529 | 44.6713 | 65.0374 | 92.922 | 131.2021 | 183.8787 | 256.5225 | 356.896 | 495.8253 | 688.4203 | 955.7843 | 1327.4086 | 1841.6384 | 2556.2199 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.1051 | 2.7323 | 3.5758 | 4.7149 | 6.2596 | 8.3614 | 11.2308 | 15.1594 | 20.5526 | 27.9742 | 38.2089 | 52.3505 | 71.9241 | 99.0586 | 136.7273 | 189.0851 | 261.9417 | 363.4242 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0.037433 | 0.6646 | 1.5081 | 2.6472 | 4.1919 | 6.2937 | 9.1631 | 13.0917 | 18.4849 | 25.9065 | 36.1412 | 50.2828 | 69.8564 | 96.9909 | 134.6596 | 187.0174 | 259.4668 | 360.1436 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.09847 | 0.10025 | 0.13012 | 0.17029 | 0.22454 | 0.2981 | 0.39819 | 0.53484 | 0.72193 | 0.97878 | 1.3322 | 1.8196 | 2.4931 | 3.4252 | 4.7175 | 6.5113 | 9.0048 | 12.4744 | 17.3073 | 17.9443 | 17.9443 | 17.9443 | 17.9443 | 17.9443 | 17.9443 | 17.9443 | 17.9443 | 17.9443 | 17.9443 | 17.9443 |  | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.11786 | 0.15623 | 0.20891 | 0.28153 | 0.38209 | 0.52182 | 0.71664 | 0.98909 | 1.3711 | 1.908 | 2.6643 | 3.7316 | 5.2403 |  | 0 | 0.0017827 | 0.03165 | 0.071818 | 0.12607 | 0.19963 | 0.29972 | 0.43637 | 0.62346 | 0.88031 | 1.2337 | 1.7211 | 2.3946 | 3.3268 | 4.619 | 6.4129 | 8.9063 | 12.3565 | 17.1511 | 17.7354 | 17.6628 | 17.5622 | 17.4225 | 17.2277 | 16.9552 | 16.5732 | 16.0363 | 15.28 | 14.2127 | 12.704 |  | 0 | 0.79832 | 14.1736 | 32.1614 | 56.4561 | 89.3975 | 134.2225 | 195.4159 | 279.1998 | 394.2187 | 552.4945 | 770.765 | 1072.354 | 1489.7903 | 2068.4745 | 2871.8146 | 3988.4222 | 5533.5119 | 7680.592 | 7942.2682 | 7909.744 | 7864.7137 | 7802.1384 | 7714.8929 | 7592.8871 | 7421.8148 | 7181.368 | 6842.69 | 6364.7384 | 5689.0922
| FALSE | 3705 | 22004072 | SA | SA-KTS NO.1 | 66 | KTS NO.1 LINE | VOLT LEAKAGE TIMER | X | English Electric | VAT_864 | VAT 864 | VAT | Electromechanical |  | 0 | 2190 |  | 9.9 | 0.0088019 | 0 | 0.0088019 | 92.4196 | 0 | 92.4196 | 24.9851 | 3.5216 | 0 |  | 14.6263 | 0.025802 | 0 | 0.025802 | 270.9191 | 0 | 270.9191 | 73.2414 | 10.3233 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 120.9263 | 354.4838 | 71.0008 | 283.483 |  | 0.039029 |  | 10.294 | 10.7037 | 11.1297 | 11.5727 | 12.0333 | 12.5122 | 13.0102 | 13.528 | 14.0664 | 14.6263 | 15.2084 | 15.8137 | 16.4431 | 17.0975 | 17.778 | 18.4856 | 19.2213 | 19.9863 | 20.7818 | 21.6089 | 22.4689 | 23.3632 | 24.2931 | 25.2599 | 26.2653 | 27.3106 | 28 | 28 | 28 | 28 |  | 0.0097834 | 0.010879 | 0.012103 | 0.01347 | 0.014998 | 0.016705 | 0.018613 | 0.020747 | 0.023133 | 0.025802 | 0.028788 | 0.032129 | 0.035868 | 0.040053 | 0.044739 | 0.049986 | 0.055861 | 0.062442 | 0.069814 | 0.078073 | 0.087327 | 0.097698 | 0.10932 | 0.12235 | 0.13696 | 0.15333 | 0.16481 | 0.16481 | 0.16481 | 0.16481 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.4108 | 149.4662 | 166.2801 | 185.0623 | 206.0484 | 229.5024 | 255.7203 | 285.0341 | 317.816 | 354.4838 | 395.5059 | 441.4077 | 492.779 | 550.2811 | 614.6565 | 686.738 | 767.4605 | 857.873 | 959.1532 | 1072.6226 | 1199.7651 | 1342.246 | 1501.9353 | 1680.9321 | 1881.5935 | 2106.5657 | 2264.3353 | 2264.3353 | 2264.3353 | 2264.3353 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 102.7253 | 114.2316 | 127.0818 | 141.4364 | 157.4753 | 175.4003 | 195.4377 | 217.8411 | 242.8952 | 270.9191 | 302.2707 | 337.3518 | 376.613 | 420.5598 | 469.7595 | 524.8488 | 586.5421 | 655.6411 | 733.0458 | 819.7664 | 916.9367 | 1025.8297 | 1147.8744 | 1284.6752 | 1438.0333 | 1609.9714 | 1730.5489 | 1730.5489 | 1730.5489 | 1730.5489 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 75.5936 | 87.0999 | 99.9501 | 114.3047 | 130.3436 | 148.2687 | 168.306 | 190.7095 | 215.7635 | 243.7874 | 275.1391 | 310.2202 | 349.4813 | 393.4281 | 442.6279 | 497.7172 | 559.4104 | 623.1662 | 689.9984 | 762.2062 | 839.3651 | 920.5521 | 1004.0958 | 1087.2166 | 1165.5076 | 1232.1891 | 1204.8257 | 996.4456 | 702.3738 | 286.6655 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 75.5936 | 87.0999 | 99.9501 | 114.3047 | 130.3436 | 148.2687 | 168.306 | 190.7095 | 215.7635 | 243.7874 | 275.1391 | 310.2202 | 349.4813 | 393.4281 | 442.6279 | 497.7172 | 559.4104 | 623.1662 | 689.9984 | 762.2062 | 839.3651 | 920.5521 | 1004.0958 | 1087.2166 | 1165.5076 | 1232.1891 | 1204.8257 | 996.4456 | 702.3738 | 286.6655 |  | 27.7712 | 30.8819 | 34.3559 | 38.2365 | 42.5726 | 47.4185 | 52.8355 | 58.8921 | 65.6654 | 73.2414 | 81.7172 | 91.2012 | 101.8152 | 113.696 | 126.9969 | 141.8899 | 158.5684 | 177.2489 | 198.1748 | 221.6192 | 247.8887 | 277.3273 | 310.3214 | 347.3047 | 388.7642 | 435.2467 | 467.8442 | 467.8442 | 467.8442 | 467.8442 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 13.1014 | 16.2121 | 19.6861 | 23.5667 | 27.9028 | 32.7487 | 38.1657 | 44.2223 | 50.9956 | 58.5717 | 67.0474 | 76.5314 | 87.1454 | 99.0262 | 112.3271 | 127.2201 | 143.8986 | 159.6901 | 174.8996 | 190.4971 | 205.9466 | 220.4049 | 232.5819 | 240.5411 | 241.4126 | 230.9841 | 183.5916 | 70.9227 | -88.0786 | -312.8474 |  | 3.9143 | 4.3528 | 4.8424 | 5.3894 | 6.0006 | 6.6836 | 7.4471 | 8.3008 | 9.2555 | 10.3233 | 11.518 | 12.8547 | 14.3507 | 16.0253 | 17.9001 | 19.9992 | 22.35 | 24.983 | 27.9325 | 31.237 | 34.9397 | 39.089 | 43.7395 | 48.9522 | 54.7959 | 61.3476 | 65.9422 | 65.9422 | 65.9422 | 65.9422 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 1.8466 | 2.2851 | 2.7747 | 3.3217 | 3.9329 | 4.6159 | 5.3794 | 6.2331 | 7.1878 | 8.2556 | 9.4503 | 10.787 | 12.2831 | 13.9576 | 15.8324 | 17.9315 | 20.2824 | 22.5082 | 24.6519 | 26.8504 | 29.028 | 31.0658 | 32.7822 | 33.904 | 34.0269 | 32.557 | 25.877 | 9.9965 | -12.4146 | -44.0955 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 90.5416 | 105.5971 | 122.4109 | 141.1932 | 162.1793 | 185.6333 | 211.8512 | 241.1649 | 273.9469 | 310.6147 | 351.6367 | 397.5386 | 448.9098 | 506.412 | 570.7873 | 642.8688 | 723.5913 | 805.3644 | 889.5499 | 979.5536 | 1074.3397 | 1172.0229 | 1269.4599 | 1361.6616 | 1440.947 | 1495.7302 | 1414.2943 | 1077.3648 | 601.8807 | -70.2774
| FALSE | 3706 | 22009857 | SA | SA-KTS NO.2 | 66 | KTS NO.2 LINE | CURRENT DIFF & DEF | Y | Siemens | 7SD522 | 7SD522 | SIEMENS 7SD522 | Digital |  | 0.016937 | 1 |  | 2.6788 | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.010621 |  | 7.9912 | 0.028405 | 6.5904e-07 | 0.028404 | 149.1268 | 0.072494 | 149.1993 | 80.6347 | 11.3649 | 0.058377 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.010621 |  | 43.8937 | 241.2572 | 43.8937 | 197.3635 |  | 0.1093 |  | 2.9882 | 3.3333 | 3.7183 | 4.1477 | 4.6268 | 5.1611 | 5.7572 | 6.4221 | 7.1638 | 7.9912 | 8.9141 | 9.9436 | 11.092 | 12.373 | 13.802 | 15.3961 | 17.1742 | 19.1577 | 21.3702 | 23.8383 | 26.5915 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0056115 | 0.007231 | 0.0093884 | 0.012274 | 0.016146 | 0.021361 | 0.028405 | 0.037944 | 0.050895 | 0.068518 | 0.092545 | 0.12536 | 0.17026 | 0.23179 | 0.31619 | 0.43213 | 0.59157 | 0.81102 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.199e-07 | 1.199e-07 | 1.199e-07 | 1.302e-07 | 1.6777e-07 | 2.1782e-07 | 2.8477e-07 | 3.7462e-07 | 4.9562e-07 | 6.5904e-07 | 8.8036e-07 | 1.1808e-06 | 1.5897e-06 | 2.1472e-06 | 2.9086e-06 | 3.9504e-06 | 5.3778e-06 | 7.3361e-06 | 1.0026e-05 | 1.3725e-05 | 1.8817e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 43.8937 | 43.8937 | 43.8937 | 47.6615 | 61.4161 | 79.7399 | 104.2461 | 137.1386 | 181.4322 | 241.2572 | 322.2792 | 432.2792 | 581.9545 | 786.026 | 1064.7688 | 1446.1301 | 1968.6588 | 2685.5618 | 3670.3186 | 5024.4584 | 6888.3327 | 7998.8085 | 7998.8085 | 7998.8085 | 7998.8085 | 7998.8085 | 7998.8085 | 7998.8085 | 7998.8085 | 7998.8085 |  | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 43.8937 | 52.538 | 69.6422 | 93.1211 | 125.4956 | 170.3185 | 232.6055 | 319.4492 | 440.8931 | 611.1774 | 850.5167 | 1187.6349 | 1663.3851 | 2335.9194 |  | 27.1317 | 27.1317 | 27.1317 | 29.4607 | 37.9628 | 49.2891 | 64.437 | 84.7686 | 112.1475 | 149.1268 | 199.2084 | 267.202 | 359.7198 | 485.8612 | 658.1587 | 893.887 | 1216.8744 | 1660.009 | 2268.7103 | 3105.736 | 4257.8406 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 0 | 0 | 0 | 2.329 | 10.831 | 22.1574 | 37.3052 | 57.6369 | 85.0158 | 121.995 | 172.0767 | 240.0702 | 332.5881 | 458.7294 | 631.0269 | 866.7553 | 1189.7426 | 1627.534 | 2225.6628 | 3048.1757 | 4180.2688 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.013189 | 0.013189 | 0.013189 | 0.014322 | 0.018455 | 0.023961 | 0.031324 | 0.041208 | 0.054518 | 0.072494 | 0.09684 | 0.12989 | 0.17487 | 0.23619 | 0.31995 | 0.43454 | 0.59155 | 0.80697 | 1.1029 | 1.5098 | 2.0698 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015787 | 0.020926 | 0.027982 | 0.03771 | 0.051178 | 0.069894 | 0.09599 | 0.13248 | 0.18365 | 0.25557 | 0.35687 | 0.49982 | 0.70191 |  | 0 | 0 | 0 | 0.0011322 | 0.0052652 | 0.010771 | 0.018135 | 0.028019 | 0.041328 | 0.059305 | 0.083651 | 0.1167 | 0.16168 | 0.223 | 0.30676 | 0.42135 | 0.57836 | 0.79118 | 1.0819 | 1.4818 | 2.0321 | 2.3523 | 2.3336 | 2.3075 | 2.271 | 2.2199 | 2.148 | 2.0467 | 1.9037 | 1.7016 |  | 0 | 0 | 0 | 2.3301 | 10.8363 | 22.1681 | 37.3234 | 57.6649 | 85.0571 | 122.0543 | 172.1603 | 240.1869 | 332.7497 | 458.9524 | 631.3337 | 867.1767 | 1190.321 | 1628.3252 | 2226.7447 | 3049.6575 | 4182.3009 | 4841.3263 | 4802.8065 | 4749.1003 | 4673.9965 | 4568.6886 | 4420.6754 | 4212.1934 | 3917.978 | 3502.0667 |  | 14.6705 | 14.6705 | 14.6705 | 15.9298 | 20.5269 | 26.6512 | 34.8419 | 45.8355 | 60.6396 | 80.6347 | 107.7145 | 144.4795 | 194.505 | 262.7113 | 355.8747 | 483.336 | 657.9793 | 897.5878 | 1226.7202 | 1679.3106 | 2302.268 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 0 | 0 | 0 | 1.2593 | 5.8565 | 11.9808 | 20.1714 | 31.165 | 45.9691 | 65.9643 | 93.044 | 129.809 | 179.8346 | 248.0408 | 341.2042 | 468.6655 | 643.3088 | 880.0281 | 1203.4439 | 1648.187 | 2260.324 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 2.0677 | 2.0677 | 2.0677 | 2.2452 | 2.8931 | 3.7563 | 4.9107 | 6.4602 | 8.5467 | 11.3649 | 15.1815 | 20.3633 | 27.414 | 37.0272 | 50.1579 | 68.1226 | 92.7373 | 126.5083 | 172.897 | 236.6863 | 324.4874 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 0 | 0 | 0 | 0.17749 | 0.82543 | 1.6886 | 2.843 | 4.3925 | 6.479 | 9.2972 | 13.1139 | 18.2956 | 25.3463 | 34.9595 | 48.0902 | 66.0549 | 90.6696 | 124.0334 | 169.6164 | 232.2996 | 318.5757 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.010621 | 0.010621 | 0.010621 | 0.011533 | 0.014861 | 0.019295 | 0.025224 | 0.033184 | 0.043901 | 0.058377 | 0.077982 | 0.1046 | 0.14082 | 0.1902 | 0.25764 | 0.34992 | 0.47636 | 0.64983 | 0.88811 | 1.2158 | 1.6668 | 1.9355 | 1.9355 | 1.9355 | 1.9355 | 1.9355 | 1.9355 | 1.9355 | 1.9355 | 1.9355 |  | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.010621 | 0.012713 | 0.016851 | 0.022533 | 0.030366 | 0.041212 | 0.056284 | 0.077297 | 0.10668 | 0.14789 | 0.2058 | 0.28737 | 0.40249 | 0.56522 |  | 0 | 0 | 0 | 0.00091169 | 0.0042399 | 0.0086737 | 0.014604 | 0.022563 | 0.03328 | 0.047756 | 0.067361 | 0.093978 | 0.13019 | 0.17957 | 0.24702 | 0.3393 | 0.46574 | 0.63711 | 0.87126 | 1.1932 | 1.6364 | 1.8943 | 1.8792 | 1.8582 | 1.8288 | 1.7876 | 1.7297 | 1.6481 | 1.533 | 1.3703 |  | 0 | 0 | 0 | 3.7678 | 17.5224 | 35.8462 | 60.3524 | 93.2449 | 137.5385 | 197.3635 | 278.3855 | 388.3855 | 538.0608 | 742.1323 | 1020.8751 | 1402.2364 | 1924.7651 | 2633.0238 | 3600.6763 | 4931.3373 | 6762.8371 | 7828.4901 | 7766.203 | 7679.3593 | 7557.9155 | 7387.6311 | 7148.2918 | 6811.1737 | 6335.4234 | 5662.8891
| FALSE | 3707 | 22009858 | SA | SA-KTS NO.2 | 66 | KTS NO.2 LINE | DISTANCE & DIR EF | X | Schweitzer | SEL_311L | SEL 311L | SEL 300s | Digital |  | 0.15703 | 1 |  | 3.2146 | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.09847 |  | 9.9777 | 0.051368 | 1.105e-05 | 0.051357 | 269.6904 | 1.2155 | 270.9059 | 145.8782 | 20.5526 | 0.97878 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.09847 |  | 44.0968 | 438.3155 | 44.0968 | 394.2187 |  | 0.11326 |  | 3.6001 | 4.0319 | 4.5154 | 5.0569 | 5.6634 | 6.3426 | 7.1033 | 7.9551 | 8.9092 | 9.9777 | 11.1743 | 12.5144 | 14.0152 | 15.696 | 17.5784 | 19.6866 | 22.0476 | 24.6917 | 27.6529 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0052615 | 0.006829 | 0.0089371 | 0.011784 | 0.015645 | 0.020898 | 0.02807 | 0.037889 | 0.051368 | 0.069918 | 0.095498 | 0.13084 | 0.17976 | 0.24758 | 0.34173 | 0.47259 | 0.65469 | 0.90833 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1318e-06 | 1.469e-06 | 1.9224e-06 | 2.5349e-06 | 3.3653e-06 | 4.4953e-06 | 6.038e-06 | 8.1501e-06 | 1.105e-05 | 1.504e-05 | 2.0542e-05 | 2.8145e-05 | 3.8668e-05 | 5.3257e-05 | 7.3509e-05 | 0.00010166 | 0.00014083 | 0.00019539 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 44.0968 | 44.8951 | 58.2704 | 76.2582 | 100.5529 | 133.4943 | 178.3193 | 239.5126 | 323.2966 | 438.3155 | 596.5913 | 814.8618 | 1116.4508 | 1533.8871 | 2112.5713 | 2915.9114 | 4032.519 | 5586.293 | 7750.5565 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 | 8035.8202 |  | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 44.0968 | 52.7811 | 69.9645 | 93.552 | 126.0763 | 171.1065 | 233.6818 | 320.9274 | 442.9331 | 614.0054 | 854.4522 | 1193.1303 | 1671.0819 | 2346.7281 |  | 27.1322 | 27.6234 | 35.8531 | 46.9208 | 61.869 | 82.1375 | 109.7178 | 147.3693 | 198.9207 | 269.6904 | 367.0757 | 501.375 | 686.9392 | 943.7829 | 1299.8405 | 1794.1264 | 2481.162 | 3437.1811 | 4768.8273 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 0 | 0.4912 | 8.7208 | 19.7885 | 34.7368 | 55.0053 | 82.5856 | 120.2371 | 171.7884 | 242.5582 | 339.9435 | 474.2428 | 659.8069 | 916.6506 | 1272.7083 | 1766.9941 | 2454.0298 | 3404.7055 | 4725.7789 | 4886.7853 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.12228 | 0.1245 | 0.16159 | 0.21147 | 0.27884 | 0.37019 | 0.49449 | 0.66418 | 0.89652 | 1.2155 | 1.6544 | 2.2596 | 3.096 | 4.2535 | 5.8583 | 8.0859 | 11.1823 | 15.491 | 21.4926 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0 | 0.0022138 | 0.039304 | 0.089185 | 0.15656 | 0.2479 | 0.3722 | 0.5419 | 0.77423 | 1.0932 | 1.5321 | 2.1374 | 2.9737 | 4.1313 | 5.736 | 7.9637 | 11.0601 | 15.3447 | 21.2986 | 22.0242 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 0 | 0.49341 | 8.7601 | 19.8777 | 34.8933 | 55.2532 | 82.9578 | 120.779 | 172.5626 | 243.6513 | 341.4756 | 476.3801 | 662.7806 | 920.7819 | 1278.4442 | 1774.9578 | 2465.0898 | 3420.0501 | 4747.0776 | 4908.8095 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 14.6761 | 14.9418 | 19.3933 | 25.3799 | 33.4656 | 44.429 | 59.3474 | 79.7135 | 107.5981 | 145.8782 | 198.5548 | 271.1986 | 371.5721 | 510.5014 | 703.0964 | 970.4604 | 1342.0847 | 1859.2047 | 2579.5051 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0.26569 | 4.7172 | 10.7038 | 18.7895 | 29.7529 | 44.6713 | 65.0374 | 92.922 | 131.2021 | 183.8787 | 256.5225 | 356.896 | 495.8253 | 688.4203 | 955.7843 | 1327.4086 | 1841.6384 | 2556.2199 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.1051 | 2.7323 | 3.5758 | 4.7149 | 6.2596 | 8.3614 | 11.2308 | 15.1594 | 20.5526 | 27.9742 | 38.2089 | 52.3505 | 71.9241 | 99.0586 | 136.7273 | 189.0851 | 261.9417 | 363.4242 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0.037433 | 0.6646 | 1.5081 | 2.6472 | 4.1919 | 6.2937 | 9.1631 | 13.0917 | 18.4849 | 25.9065 | 36.1412 | 50.2828 | 69.8564 | 96.9909 | 134.6596 | 187.0174 | 259.4668 | 360.1436 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.09847 | 0.10025 | 0.13012 | 0.17029 | 0.22454 | 0.2981 | 0.39819 | 0.53484 | 0.72193 | 0.97878 | 1.3322 | 1.8196 | 2.4931 | 3.4252 | 4.7175 | 6.5113 | 9.0048 | 12.4744 | 17.3073 | 17.9443 | 17.9443 | 17.9443 | 17.9443 | 17.9443 | 17.9443 | 17.9443 | 17.9443 | 17.9443 | 17.9443 | 17.9443 |  | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.09847 | 0.11786 | 0.15623 | 0.20891 | 0.28153 | 0.38209 | 0.52182 | 0.71664 | 0.98909 | 1.3711 | 1.908 | 2.6643 | 3.7316 | 5.2403 |  | 0 | 0.0017827 | 0.03165 | 0.071818 | 0.12607 | 0.19963 | 0.29972 | 0.43637 | 0.62346 | 0.88031 | 1.2337 | 1.7211 | 2.3946 | 3.3268 | 4.619 | 6.4129 | 8.9063 | 12.3565 | 17.1511 | 17.7354 | 17.6628 | 17.5622 | 17.4225 | 17.2277 | 16.9552 | 16.5732 | 16.0363 | 15.28 | 14.2127 | 12.704 |  | 0 | 0.79832 | 14.1736 | 32.1614 | 56.4561 | 89.3975 | 134.2225 | 195.4159 | 279.1998 | 394.2187 | 552.4945 | 770.765 | 1072.354 | 1489.7903 | 2068.4745 | 2871.8146 | 3988.4222 | 5533.5119 | 7680.592 | 7942.2682 | 7909.744 | 7864.7137 | 7802.1384 | 7714.8929 | 7592.8871 | 7421.8148 | 7181.368 | 6842.69 | 6364.7384 | 5689.0922
| FALSE | 3708 | 22015964 | SA | SA-KTS NO.2 | 66 | KTS NO.2 LINE | VOLT LEAKAGE TIMER | X | English Electric | VAT_864 | VAT 864 | VAT | Electromechanical |  | 0 | 2190 |  | 9.9 | 0.0088019 | 0 | 0.0088019 | 92.4196 | 0 | 92.4196 | 24.9851 | 3.5216 | 0 |  | 14.6263 | 0.025802 | 0 | 0.025802 | 270.9191 | 0 | 270.9191 | 73.2414 | 10.3233 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 120.9263 | 354.4838 | 71.0008 | 283.483 |  | 0.039029 |  | 10.294 | 10.7037 | 11.1297 | 11.5727 | 12.0333 | 12.5122 | 13.0102 | 13.528 | 14.0664 | 14.6263 | 15.2084 | 15.8137 | 16.4431 | 17.0975 | 17.778 | 18.4856 | 19.2213 | 19.9863 | 20.7818 | 21.6089 | 22.4689 | 23.3632 | 24.2931 | 25.2599 | 26.2653 | 27.3106 | 28 | 28 | 28 | 28 |  | 0.0097834 | 0.010879 | 0.012103 | 0.01347 | 0.014998 | 0.016705 | 0.018613 | 0.020747 | 0.023133 | 0.025802 | 0.028788 | 0.032129 | 0.035868 | 0.040053 | 0.044739 | 0.049986 | 0.055861 | 0.062442 | 0.069814 | 0.078073 | 0.087327 | 0.097698 | 0.10932 | 0.12235 | 0.13696 | 0.15333 | 0.16481 | 0.16481 | 0.16481 | 0.16481 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.4108 | 149.4662 | 166.2801 | 185.0623 | 206.0484 | 229.5024 | 255.7203 | 285.0341 | 317.816 | 354.4838 | 395.5059 | 441.4077 | 492.779 | 550.2811 | 614.6565 | 686.738 | 767.4605 | 857.873 | 959.1532 | 1072.6226 | 1199.7651 | 1342.246 | 1501.9353 | 1680.9321 | 1881.5935 | 2106.5657 | 2264.3353 | 2264.3353 | 2264.3353 | 2264.3353 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 102.7253 | 114.2316 | 127.0818 | 141.4364 | 157.4753 | 175.4003 | 195.4377 | 217.8411 | 242.8952 | 270.9191 | 302.2707 | 337.3518 | 376.613 | 420.5598 | 469.7595 | 524.8488 | 586.5421 | 655.6411 | 733.0458 | 819.7664 | 916.9367 | 1025.8297 | 1147.8744 | 1284.6752 | 1438.0333 | 1609.9714 | 1730.5489 | 1730.5489 | 1730.5489 | 1730.5489 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 75.5936 | 87.0999 | 99.9501 | 114.3047 | 130.3436 | 148.2687 | 168.306 | 190.7095 | 215.7635 | 243.7874 | 275.1391 | 310.2202 | 349.4813 | 393.4281 | 442.6279 | 497.7172 | 559.4104 | 623.1662 | 689.9984 | 762.2062 | 839.3651 | 920.5521 | 1004.0958 | 1087.2166 | 1165.5076 | 1232.1891 | 1204.8257 | 996.4456 | 702.3738 | 286.6655 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 75.5936 | 87.0999 | 99.9501 | 114.3047 | 130.3436 | 148.2687 | 168.306 | 190.7095 | 215.7635 | 243.7874 | 275.1391 | 310.2202 | 349.4813 | 393.4281 | 442.6279 | 497.7172 | 559.4104 | 623.1662 | 689.9984 | 762.2062 | 839.3651 | 920.5521 | 1004.0958 | 1087.2166 | 1165.5076 | 1232.1891 | 1204.8257 | 996.4456 | 702.3738 | 286.6655 |  | 27.7712 | 30.8819 | 34.3559 | 38.2365 | 42.5726 | 47.4185 | 52.8355 | 58.8921 | 65.6654 | 73.2414 | 81.7172 | 91.2012 | 101.8152 | 113.696 | 126.9969 | 141.8899 | 158.5684 | 177.2489 | 198.1748 | 221.6192 | 247.8887 | 277.3273 | 310.3214 | 347.3047 | 388.7642 | 435.2467 | 467.8442 | 467.8442 | 467.8442 | 467.8442 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 13.1014 | 16.2121 | 19.6861 | 23.5667 | 27.9028 | 32.7487 | 38.1657 | 44.2223 | 50.9956 | 58.5717 | 67.0474 | 76.5314 | 87.1454 | 99.0262 | 112.3271 | 127.2201 | 143.8986 | 159.6901 | 174.8996 | 190.4971 | 205.9466 | 220.4049 | 232.5819 | 240.5411 | 241.4126 | 230.9841 | 183.5916 | 70.9227 | -88.0786 | -312.8474 |  | 3.9143 | 4.3528 | 4.8424 | 5.3894 | 6.0006 | 6.6836 | 7.4471 | 8.3008 | 9.2555 | 10.3233 | 11.518 | 12.8547 | 14.3507 | 16.0253 | 17.9001 | 19.9992 | 22.35 | 24.983 | 27.9325 | 31.237 | 34.9397 | 39.089 | 43.7395 | 48.9522 | 54.7959 | 61.3476 | 65.9422 | 65.9422 | 65.9422 | 65.9422 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 1.8466 | 2.2851 | 2.7747 | 3.3217 | 3.9329 | 4.6159 | 5.3794 | 6.2331 | 7.1878 | 8.2556 | 9.4503 | 10.787 | 12.2831 | 13.9576 | 15.8324 | 17.9315 | 20.2824 | 22.5082 | 24.6519 | 26.8504 | 29.028 | 31.0658 | 32.7822 | 33.904 | 34.0269 | 32.557 | 25.877 | 9.9965 | -12.4146 | -44.0955 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 90.5416 | 105.5971 | 122.4109 | 141.1932 | 162.1793 | 185.6333 | 211.8512 | 241.1649 | 273.9469 | 310.6147 | 351.6367 | 397.5386 | 448.9098 | 506.412 | 570.7873 | 642.8688 | 723.5913 | 805.3644 | 889.5499 | 979.5536 | 1074.3397 | 1172.0229 | 1269.4599 | 1361.6616 | 1440.947 | 1495.7302 | 1414.2943 | 1077.3648 | 601.8807 | -70.2774
| TRUE | 3709 | 22004151 | SA | Blank | 66 | TRANS TR NO.1 | OVERCURRENT | Blank | English Electric | CDG11_522 | CDG11 522 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 675.3447 | 769.3759 | 33.699 | 3.537 | 135.9582 |  | 14.6263 | 0.025802 | 0.0044993 | 0.021302 | 275.6434 | 1979.7072 | 2255.3506 | 98.7852 | 10.3683 | 398.5481 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.041417 |  | 942.57 | 2763.0522 | 71.2511 | 2691.8011 |  | 0.039029 |  | 10.294 | 10.7037 | 11.1297 | 11.5727 | 12.0333 | 12.5122 | 13.0102 | 13.528 | 14.0664 | 14.6263 | 15.2084 | 15.8137 | 16.4431 | 17.0975 | 17.778 | 18.4856 | 19.2213 | 19.9863 | 20.7818 | 21.6089 | 22.4689 | 23.3632 | 24.2931 | 25.2599 | 26.2653 | 27.3106 | 28 | 28 | 28 | 28 |  | 0.0097834 | 0.010879 | 0.012103 | 0.01347 | 0.014998 | 0.016705 | 0.018613 | 0.020747 | 0.023133 | 0.025802 | 0.028788 | 0.032129 | 0.035868 | 0.040053 | 0.044739 | 0.049986 | 0.055861 | 0.062442 | 0.069814 | 0.078073 | 0.087327 | 0.097698 | 0.10932 | 0.12235 | 0.13696 | 0.15333 | 0.16481 | 0.16481 | 0.16481 | 0.16481 |  | 0.001706 | 0.0018971 | 0.0021105 | 0.0023489 | 0.0026153 | 0.002913 | 0.0032458 | 0.0036178 | 0.0040339 | 0.0044993 | 0.00502 | 0.0056026 | 0.0062547 | 0.0069845 | 0.0078016 | 0.0087165 | 0.0097411 | 0.010889 | 0.012174 | 0.013614 | 0.015228 | 0.017037 | 0.019064 | 0.021335 | 0.023882 | 0.026738 | 0.02874 | 0.02874 | 0.02874 | 0.02874 | 1047.6755 | 1165.0265 | 1296.0833 | 1442.483 | 1606.0609 | 1788.8749 | 1993.2322 | 2221.7206 | 2477.2423 | 2763.0522 | 3082.8019 | 3440.5875 | 3841.0048 | 4289.2099 | 4790.9887 | 5352.8339 | 5982.0316 | 6686.7594 | 7476.1956 | 8360.6424 | 9351.6643 | 10462.2435 | 11706.9543 | 13102.1593 | 14666.2299 | 16419.7939 | 17649.5414 | 17649.5414 | 17649.5414 | 17649.5414 |  | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 52.8111 | 70.0043 | 93.6052 | 126.148 | 171.2039 | 233.8148 | 321.11 | 443.1852 | 614.3548 | 854.9384 | 1193.8092 | 1672.0328 | 2348.0635 |  | 104.5166 | 116.2236 | 129.2979 | 143.9028 | 160.2214 | 178.459 | 198.8458 | 221.6399 | 247.1308 | 275.6434 | 307.5417 | 343.2346 | 383.1804 | 427.8935 | 477.9512 | 534.0012 | 596.7702 | 667.0742 | 745.8287 | 834.0615 | 932.9263 | 1043.7182 | 1167.8911 | 1307.0774 | 1463.1098 | 1638.0462 | 1760.7263 | 1760.7263 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 77.3847 | 89.0917 | 102.166 | 116.7709 | 133.0895 | 151.3271 | 171.7139 | 194.508 | 219.9989 | 248.5114 | 280.4098 | 316.1027 | 356.0485 | 400.7616 | 450.8193 | 506.8692 | 569.6383 | 634.599 | 702.7809 | 776.5008 | 855.354 | 938.4397 | 1024.1112 | 1109.617 | 1190.5816 | 1260.2605 | 1234.9984 | 1026.6163 | 732.5419 | 316.8298 |  | 750.652 | 834.7332 | 928.6344 | 1033.5288 | 1150.7312 | 1281.7161 | 1428.1367 | 1591.847 | 1774.9264 | 1979.7072 | 2208.8056 | 2465.1565 | 2752.0526 | 3073.1883 | 3432.7093 | 3835.2673 | 4286.083 | 4791.0154 | 5356.6409 | 5990.3407 | 6700.4009 | 7496.123 | 8387.9493 | 9387.6038 | 10508.2493 | 11764.6654 | 12645.7707 | 12645.7707 | 12645.7707 | 12645.7707 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 750.4463 | 834.5274 | 928.4287 | 1033.3231 | 1150.5255 | 1281.5104 | 1427.931 | 1591.6413 | 1774.7207 | 1979.5015 | 2208.5999 | 2464.9507 | 2751.8468 | 3072.9826 | 3432.5036 | 3835.0616 | 4285.8773 | 4790.7692 | 5356.3144 | 5989.9042 | 6699.8127 | 7495.3247 | 8386.8591 | 9386.1065 | 10506.1828 | 11761.8008 | 12641.7843 | 12640.2043 | 12637.9744 | 12634.8223 |  | 827.831 | 923.6191 | 1030.5947 | 1150.0939 | 1283.615 | 1432.8374 | 1599.6448 | 1786.1492 | 1994.7196 | 2228.0129 | 2489.0097 | 2781.0534 | 3107.8953 | 3473.7442 | 3883.3229 | 4341.9308 | 4855.5156 | 5425.3682 | 6059.0953 | 6766.405 | 7555.1667 | 8433.7643 | 9410.9703 | 10495.7235 | 11696.7644 | 13022.0612 | 13876.7827 | 13666.8206 | 13370.5163 | 12951.6521 |  | 37.4567 | 41.6523 | 46.3378 | 51.5719 | 57.4202 | 63.9562 | 71.2624 | 79.4314 | 88.5669 | 98.7852 | 110.217 | 123.0086 | 137.3244 | 153.3487 | 171.2884 | 191.3756 | 213.8708 | 239.0664 | 267.2905 | 298.9114 | 334.3426 | 374.0483 | 418.5494 | 468.4311 | 524.3501 | 587.0438 | 631.01 | 631.01 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.7843 | 26.9798 | 31.6654 | 36.8995 | 42.7478 | 49.2838 | 56.59 | 64.759 | 73.8944 | 84.1128 | 95.5445 | 108.3362 | 122.652 | 138.6763 | 156.616 | 176.7032 | 199.1984 | 221.5044 | 244.011 | 267.7836 | 292.3929 | 317.1156 | 340.7959 | 361.6481 | 376.9718 | 382.7443 | 346.706 | 234.0168 | 74.9867 | -149.8228 |  | 3.9314 | 4.3717 | 4.8635 | 5.4129 | 6.0267 | 6.7127 | 7.4796 | 8.337 | 9.2958 | 10.3683 | 11.5682 | 12.9107 | 14.4133 | 16.0952 | 17.9781 | 20.0864 | 22.4475 | 25.0919 | 28.0543 | 31.3731 | 35.0919 | 39.2594 | 43.9301 | 49.1656 | 55.0347 | 61.615 | 66.2296 | 66.2296 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8637 | 2.304 | 2.7958 | 3.3452 | 3.959 | 4.645 | 5.4119 | 6.2693 | 7.2281 | 8.3006 | 9.5005 | 10.843 | 12.3456 | 14.0275 | 15.9104 | 18.0187 | 20.3798 | 22.617 | 24.7736 | 26.9865 | 29.1802 | 31.2362 | 32.9728 | 34.1173 | 34.2656 | 32.8243 | 26.1644 | 10.2838 | -12.1274 | -43.8084 |  | 151.1188 | 168.0457 | 186.9496 | 208.0666 | 231.6614 | 258.0309 | 287.5078 | 320.4654 | 357.3223 | 398.5481 | 444.6695 | 496.2772 | 554.0341 | 618.6841 | 691.0617 | 772.1034 | 862.8601 | 964.5114 | 1078.3813 | 1205.9556 | 1348.9026 | 1509.0947 | 1688.6343 | 1889.8814 | 2115.4861 | 2368.4236 | 2545.8048 | 2545.8048 | 2545.8048 | 2545.8048 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 151.0774 | 168.0043 | 186.9082 | 208.0252 | 231.62 | 257.9894 | 287.4663 | 320.424 | 357.2809 | 398.5067 | 444.628 | 496.2357 | 553.9927 | 618.6427 | 691.0203 | 772.0619 | 862.8187 | 964.4618 | 1078.3155 | 1205.8678 | 1348.7842 | 1508.934 | 1688.4148 | 1889.58 | 2115.07 | 2367.8469 | 2545.0023 | 2544.6842 | 2544.2353 | 2543.6007 |  | 1003.5563 | 1120.9073 | 1251.9641 | 1398.3638 | 1561.9417 | 1744.7557 | 1949.113 | 2177.6015 | 2433.1231 | 2718.933 | 3038.6827 | 3396.4683 | 3796.8856 | 4245.0907 | 4746.8695 | 5308.7147 | 5937.9124 | 6633.9515 | 7406.1956 | 8267.0429 | 9225.524 | 10291.0501 | 11473.1538 | 12781.069 | 14223.0719 | 15805.4767 | 16794.6553 | 16455.8053 | 15977.611 | 15301.6217
| TRUE | 3710 | 22004149 | SA | Blank | 66 | TRANS TR NO.1 | OVERCURRENT | Blank | English Electric | CDG11_522 | CDG11 522 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 675.3447 | 769.3759 | 33.699 | 3.537 | 135.9582 |  | 13.9533 | 0.022617 | 0.003944 | 0.018673 | 241.6202 | 1735.3484 | 1976.9686 | 86.592 | 9.0885 | 349.3546 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.041417 |  | 942.57 | 2422.0037 | 71.2511 | 2350.7526 |  | 0.034318 |  | 10.2456 | 10.6034 | 10.9736 | 11.3567 | 11.7532 | 12.1636 | 12.5882 | 13.0277 | 13.4826 | 13.9533 | 14.4405 | 14.9446 | 15.4664 | 16.0064 | 16.5653 | 17.1436 | 17.7422 | 18.3616 | 19.0027 | 19.6661 | 20.3528 | 21.0634 | 21.7988 | 22.5598 | 23.3475 | 24.1626 | 25.0062 | 25.8793 | 26.7829 | 27.718 |  | 0.0096591 | 0.010604 | 0.011644 | 0.012791 | 0.014056 | 0.01545 | 0.016987 | 0.018683 | 0.020553 | 0.022617 | 0.024894 | 0.027408 | 0.030182 | 0.033244 | 0.036626 | 0.04036 | 0.044483 | 0.049038 | 0.05407 | 0.059628 | 0.06577 | 0.072556 | 0.080057 | 0.088346 | 0.097509 | 0.10764 | 0.11884 | 0.13122 | 0.14491 | 0.16005 |  | 0.0016844 | 0.001849 | 0.0020305 | 0.0022305 | 0.002451 | 0.0026941 | 0.0029622 | 0.0032579 | 0.0035841 | 0.003944 | 0.0043411 | 0.0047794 | 0.0052631 | 0.0057972 | 0.0063868 | 0.007038 | 0.007757 | 0.0085513 | 0.0094287 | 0.010398 | 0.011469 | 0.012652 | 0.01396 | 0.015406 | 0.017004 | 0.01877 | 0.020723 | 0.022882 | 0.025269 | 0.027909 | 1034.3678 | 1135.5036 | 1246.9496 | 1369.7807 | 1505.1854 | 1654.4779 | 1819.1115 | 2000.6937 | 2201.0023 | 2422.0037 | 2665.8733 | 2935.0177 | 3232.0991 | 3560.0634 | 3922.1698 | 4322.0252 | 4763.6206 | 5251.3728 | 5790.1701 | 6385.4227 | 7043.119 | 7769.8871 | 8573.0642 | 9460.7725 | 10442.0035 | 11526.7118 | 12725.918 | 14051.8241 | 15517.9405 | 17139.2264 |  | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 52.8111 | 70.0043 | 93.6052 | 126.148 | 171.2039 | 233.8148 | 321.11 | 443.1852 | 614.3548 | 854.9384 | 1193.8092 | 1672.0328 | 2348.0635 |  | 103.189 | 113.2784 | 124.3963 | 136.65 | 150.158 | 165.0515 | 181.4754 | 199.5901 | 219.573 | 241.6202 | 265.9487 | 292.7987 | 322.4357 | 355.1536 | 391.2775 | 431.1672 | 475.221 | 523.8794 | 577.63 | 637.0127 | 702.6248 | 775.1275 | 855.2528 | 943.811 | 1041.6991 | 1149.91 | 1269.5434 | 1401.8164 | 1548.0769 | 1709.8171 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.0571 | 86.1465 | 97.2644 | 109.518 | 123.0261 | 137.9196 | 154.3435 | 172.4582 | 192.4411 | 214.4883 | 238.8168 | 265.6668 | 295.3038 | 328.0216 | 364.1456 | 404.0353 | 448.0891 | 491.4042 | 534.5822 | 579.452 | 625.0525 | 669.8489 | 711.4729 | 746.3506 | 769.1708 | 772.1243 | 743.8155 | 667.7064 | 519.8924 | 265.9206 |  | 741.1172 | 813.5803 | 893.4305 | 981.4381 | 1078.4546 | 1185.4216 | 1303.3804 | 1433.4828 | 1577.0024 | 1735.3484 | 1910.0793 | 2102.9192 | 2315.776 | 2550.76 | 2810.2068 | 3096.7003 | 3413.1002 | 3762.5712 | 4148.6156 | 4575.1099 | 5046.3446 | 5567.0687 | 6142.5394 | 6778.5761 | 7481.6211 | 8258.8068 | 9118.0295 | 10068.0319 | 11118.4938 | 12280.1336 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 740.9114 | 813.3745 | 893.2248 | 981.2324 | 1078.2489 | 1185.2159 | 1303.1747 | 1433.2771 | 1576.7967 | 1735.1427 | 1909.8735 | 2102.7135 | 2315.5702 | 2550.5543 | 2810.001 | 3096.4945 | 3412.8945 | 3762.3249 | 4148.2892 | 4574.6734 | 5045.7564 | 5566.2704 | 6141.4492 | 6777.0788 | 7479.5547 | 8255.9423 | 9114.0432 | 10062.4654 | 11110.6975 | 12269.1852 |  | 816.9685 | 899.521 | 990.4891 | 1090.7504 | 1201.2749 | 1323.1354 | 1457.5182 | 1605.7353 | 1769.2378 | 1949.631 | 2148.6904 | 2368.3803 | 2610.874 | 2878.5759 | 3174.1466 | 3500.5298 | 3860.9835 | 4253.7291 | 4682.8714 | 5154.1254 | 5670.8088 | 6236.1194 | 6852.9221 | 7523.4294 | 8248.7255 | 9028.0666 | 9857.8586 | 10730.1718 | 11630.59 | 12535.1057 |  | 36.9809 | 40.5968 | 44.5812 | 48.9727 | 53.8137 | 59.1512 | 65.0372 | 71.5292 | 78.6907 | 86.592 | 95.3109 | 104.9334 | 115.5547 | 127.2801 | 140.2262 | 154.5219 | 170.3099 | 187.7482 | 207.0114 | 228.2929 | 251.807 | 277.7906 | 306.506 | 338.2435 | 373.3247 | 412.1054 | 454.9796 | 502.3837 | 554.8006 | 612.7651 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.3085 | 25.9243 | 29.9088 | 34.3002 | 39.1413 | 44.4788 | 50.3648 | 56.8568 | 64.0182 | 71.9195 | 80.6384 | 90.2609 | 100.8822 | 112.6077 | 125.5538 | 139.8495 | 155.6375 | 170.1862 | 183.7319 | 197.1652 | 209.8574 | 220.8579 | 228.7524 | 231.4605 | 225.9464 | 207.8058 | 170.6756 | 105.3904 | -1.2227 | -168.0677 |  | 3.8814 | 4.261 | 4.6792 | 5.1401 | 5.6482 | 6.2084 | 6.8262 | 7.5076 | 8.2592 | 9.0885 | 10.0036 | 11.0136 | 12.1284 | 13.3591 | 14.7179 | 16.2183 | 17.8754 | 19.7057 | 21.7275 | 23.9612 | 26.4292 | 29.1563 | 32.1703 | 35.5014 | 39.1834 | 43.2538 | 47.7538 | 52.7292 | 58.2308 | 64.3146 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8137 | 2.1933 | 2.6115 | 3.0724 | 3.5805 | 4.1407 | 4.7585 | 5.4399 | 6.1915 | 7.0208 | 7.9359 | 8.9459 | 10.0607 | 11.2914 | 12.6502 | 14.1506 | 15.8077 | 17.2308 | 18.4469 | 19.5745 | 20.5175 | 21.1332 | 21.2129 | 20.4531 | 18.4143 | 14.4631 | 7.6886 | -3.2166 | -20.1261 | -45.7233 |  | 149.1993 | 163.7873 | 179.8625 | 197.5799 | 217.1109 | 238.6452 | 262.3922 | 288.584 | 317.4769 | 349.3546 | 384.5309 | 423.3528 | 466.2044 | 513.5106 | 565.7415 | 623.4175 | 687.1141 | 757.4684 | 835.1856 | 921.046 | 1015.9134 | 1120.7439 | 1236.5958 | 1364.6406 | 1506.1753 | 1662.6357 | 1835.6116 | 2026.8629 | 2238.3385 | 2472.196 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 149.1578 | 163.7459 | 179.8211 | 197.5385 | 217.0695 | 238.6037 | 262.3508 | 288.5426 | 317.4355 | 349.3132 | 384.4894 | 423.3113 | 466.163 | 513.4692 | 565.7001 | 623.3761 | 687.0726 | 757.4188 | 835.1199 | 920.9582 | 1015.795 | 1120.5832 | 1236.3763 | 1364.3391 | 1505.7593 | 1662.059 | 1834.8091 | 2025.7423 | 2236.769 | 2469.9919 |  | 990.2486 | 1091.3844 | 1202.8304 | 1325.6615 | 1461.0662 | 1610.3587 | 1774.9923 | 1956.5745 | 2156.8831 | 2377.8845 | 2621.7542 | 2890.8985 | 3187.9799 | 3515.9442 | 3878.0507 | 4277.906 | 4719.5014 | 5198.5649 | 5720.1701 | 6291.8232 | 6916.9787 | 7598.6936 | 8339.2637 | 9139.6822 | 9998.8455 | 10912.3945 | 11871.0319 | 12858.088 | 13846.0101 | 14791.3066
| TRUE | 3711 | 22004150 | SA | Blank | 66 | TRANS TR NO.1 | OVERCURRENT | Blank | English Electric | CDG11_522 | CDG11 522 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 675.3447 | 769.3759 | 33.699 | 3.537 | 135.9582 |  | 14.6263 | 0.025802 | 0.0044993 | 0.021302 | 275.6434 | 1979.7072 | 2255.3506 | 98.7852 | 10.3683 | 398.5481 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.041417 |  | 942.57 | 2763.0522 | 71.2511 | 2691.8011 |  | 0.039029 |  | 10.294 | 10.7037 | 11.1297 | 11.5727 | 12.0333 | 12.5122 | 13.0102 | 13.528 | 14.0664 | 14.6263 | 15.2084 | 15.8137 | 16.4431 | 17.0975 | 17.778 | 18.4856 | 19.2213 | 19.9863 | 20.7818 | 21.6089 | 22.4689 | 23.3632 | 24.2931 | 25.2599 | 26.2653 | 27.3106 | 28 | 28 | 28 | 28 |  | 0.0097834 | 0.010879 | 0.012103 | 0.01347 | 0.014998 | 0.016705 | 0.018613 | 0.020747 | 0.023133 | 0.025802 | 0.028788 | 0.032129 | 0.035868 | 0.040053 | 0.044739 | 0.049986 | 0.055861 | 0.062442 | 0.069814 | 0.078073 | 0.087327 | 0.097698 | 0.10932 | 0.12235 | 0.13696 | 0.15333 | 0.16481 | 0.16481 | 0.16481 | 0.16481 |  | 0.001706 | 0.0018971 | 0.0021105 | 0.0023489 | 0.0026153 | 0.002913 | 0.0032458 | 0.0036178 | 0.0040339 | 0.0044993 | 0.00502 | 0.0056026 | 0.0062547 | 0.0069845 | 0.0078016 | 0.0087165 | 0.0097411 | 0.010889 | 0.012174 | 0.013614 | 0.015228 | 0.017037 | 0.019064 | 0.021335 | 0.023882 | 0.026738 | 0.02874 | 0.02874 | 0.02874 | 0.02874 | 1047.6755 | 1165.0265 | 1296.0833 | 1442.483 | 1606.0609 | 1788.8749 | 1993.2322 | 2221.7206 | 2477.2423 | 2763.0522 | 3082.8019 | 3440.5875 | 3841.0048 | 4289.2099 | 4790.9887 | 5352.8339 | 5982.0316 | 6686.7594 | 7476.1956 | 8360.6424 | 9351.6643 | 10462.2435 | 11706.9543 | 13102.1593 | 14666.2299 | 16419.7939 | 17649.5414 | 17649.5414 | 17649.5414 | 17649.5414 |  | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 52.8111 | 70.0043 | 93.6052 | 126.148 | 171.2039 | 233.8148 | 321.11 | 443.1852 | 614.3548 | 854.9384 | 1193.8092 | 1672.0328 | 2348.0635 |  | 104.5166 | 116.2236 | 129.2979 | 143.9028 | 160.2214 | 178.459 | 198.8458 | 221.6399 | 247.1308 | 275.6434 | 307.5417 | 343.2346 | 383.1804 | 427.8935 | 477.9512 | 534.0012 | 596.7702 | 667.0742 | 745.8287 | 834.0615 | 932.9263 | 1043.7182 | 1167.8911 | 1307.0774 | 1463.1098 | 1638.0462 | 1760.7263 | 1760.7263 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 77.3847 | 89.0917 | 102.166 | 116.7709 | 133.0895 | 151.3271 | 171.7139 | 194.508 | 219.9989 | 248.5114 | 280.4098 | 316.1027 | 356.0485 | 400.7616 | 450.8193 | 506.8692 | 569.6383 | 634.599 | 702.7809 | 776.5008 | 855.354 | 938.4397 | 1024.1112 | 1109.617 | 1190.5816 | 1260.2605 | 1234.9984 | 1026.6163 | 732.5419 | 316.8298 |  | 750.652 | 834.7332 | 928.6344 | 1033.5288 | 1150.7312 | 1281.7161 | 1428.1367 | 1591.847 | 1774.9264 | 1979.7072 | 2208.8056 | 2465.1565 | 2752.0526 | 3073.1883 | 3432.7093 | 3835.2673 | 4286.083 | 4791.0154 | 5356.6409 | 5990.3407 | 6700.4009 | 7496.123 | 8387.9493 | 9387.6038 | 10508.2493 | 11764.6654 | 12645.7707 | 12645.7707 | 12645.7707 | 12645.7707 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 750.4463 | 834.5274 | 928.4287 | 1033.3231 | 1150.5255 | 1281.5104 | 1427.931 | 1591.6413 | 1774.7207 | 1979.5015 | 2208.5999 | 2464.9507 | 2751.8468 | 3072.9826 | 3432.5036 | 3835.0616 | 4285.8773 | 4790.7692 | 5356.3144 | 5989.9042 | 6699.8127 | 7495.3247 | 8386.8591 | 9386.1065 | 10506.1828 | 11761.8008 | 12641.7843 | 12640.2043 | 12637.9744 | 12634.8223 |  | 827.831 | 923.6191 | 1030.5947 | 1150.0939 | 1283.615 | 1432.8374 | 1599.6448 | 1786.1492 | 1994.7196 | 2228.0129 | 2489.0097 | 2781.0534 | 3107.8953 | 3473.7442 | 3883.3229 | 4341.9308 | 4855.5156 | 5425.3682 | 6059.0953 | 6766.405 | 7555.1667 | 8433.7643 | 9410.9703 | 10495.7235 | 11696.7644 | 13022.0612 | 13876.7827 | 13666.8206 | 13370.5163 | 12951.6521 |  | 37.4567 | 41.6523 | 46.3378 | 51.5719 | 57.4202 | 63.9562 | 71.2624 | 79.4314 | 88.5669 | 98.7852 | 110.217 | 123.0086 | 137.3244 | 153.3487 | 171.2884 | 191.3756 | 213.8708 | 239.0664 | 267.2905 | 298.9114 | 334.3426 | 374.0483 | 418.5494 | 468.4311 | 524.3501 | 587.0438 | 631.01 | 631.01 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.7843 | 26.9798 | 31.6654 | 36.8995 | 42.7478 | 49.2838 | 56.59 | 64.759 | 73.8944 | 84.1128 | 95.5445 | 108.3362 | 122.652 | 138.6763 | 156.616 | 176.7032 | 199.1984 | 221.5044 | 244.011 | 267.7836 | 292.3929 | 317.1156 | 340.7959 | 361.6481 | 376.9718 | 382.7443 | 346.706 | 234.0168 | 74.9867 | -149.8228 |  | 3.9314 | 4.3717 | 4.8635 | 5.4129 | 6.0267 | 6.7127 | 7.4796 | 8.337 | 9.2958 | 10.3683 | 11.5682 | 12.9107 | 14.4133 | 16.0952 | 17.9781 | 20.0864 | 22.4475 | 25.0919 | 28.0543 | 31.3731 | 35.0919 | 39.2594 | 43.9301 | 49.1656 | 55.0347 | 61.615 | 66.2296 | 66.2296 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8637 | 2.304 | 2.7958 | 3.3452 | 3.959 | 4.645 | 5.4119 | 6.2693 | 7.2281 | 8.3006 | 9.5005 | 10.843 | 12.3456 | 14.0275 | 15.9104 | 18.0187 | 20.3798 | 22.617 | 24.7736 | 26.9865 | 29.1802 | 31.2362 | 32.9728 | 34.1173 | 34.2656 | 32.8243 | 26.1644 | 10.2838 | -12.1274 | -43.8084 |  | 151.1188 | 168.0457 | 186.9496 | 208.0666 | 231.6614 | 258.0309 | 287.5078 | 320.4654 | 357.3223 | 398.5481 | 444.6695 | 496.2772 | 554.0341 | 618.6841 | 691.0617 | 772.1034 | 862.8601 | 964.5114 | 1078.3813 | 1205.9556 | 1348.9026 | 1509.0947 | 1688.6343 | 1889.8814 | 2115.4861 | 2368.4236 | 2545.8048 | 2545.8048 | 2545.8048 | 2545.8048 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 151.0774 | 168.0043 | 186.9082 | 208.0252 | 231.62 | 257.9894 | 287.4663 | 320.424 | 357.2809 | 398.5067 | 444.628 | 496.2357 | 553.9927 | 618.6427 | 691.0203 | 772.0619 | 862.8187 | 964.4618 | 1078.3155 | 1205.8678 | 1348.7842 | 1508.934 | 1688.4148 | 1889.58 | 2115.07 | 2367.8469 | 2545.0023 | 2544.6842 | 2544.2353 | 2543.6007 |  | 1003.5563 | 1120.9073 | 1251.9641 | 1398.3638 | 1561.9417 | 1744.7557 | 1949.113 | 2177.6015 | 2433.1231 | 2718.933 | 3038.6827 | 3396.4683 | 3796.8856 | 4245.0907 | 4746.8695 | 5308.7147 | 5937.9124 | 6633.9515 | 7406.1956 | 8267.0429 | 9225.524 | 10291.0501 | 11473.1538 | 12781.069 | 14223.0719 | 15805.4767 | 16794.6553 | 16455.8053 | 15977.611 | 15301.6217
| TRUE | 3712 | 22004146 | SA | Blank | 66 | TRANS TR NO.1 | DIFFERENTIAL | X | Reyrolle | DUOBIAS_959 | DUOBIAS 979 | DUOBIAS | Electronic |  | 0.066046 | 2190 |  | 6.6 | 0.014726 | 0.0025679 | 0.012158 | 157.3198 | 1129.892 | 1287.2118 | 56.3804 | 5.9176 | 227.4661 |  | 9.2475 | 0.035616 | 0.0062108 | 0.029405 | 380.492 | 2732.7441 | 3113.2361 | 136.3609 | 14.3122 | 550.147 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.041417 |  | 1576.9758 | 3814.0562 | 71.2511 | 3742.8051 |  | 0.033728 |  | 6.8264 | 7.0606 | 7.3028 | 7.5533 | 7.8124 | 8.0804 | 8.3576 | 8.6443 | 8.9408 | 9.2475 | 9.5647 | 9.8928 | 10.2322 | 10.5832 | 10.9462 | 11.3217 | 11.7101 | 12.1118 | 12.5273 | 12.957 | 13.4015 | 13.8612 | 14.3367 | 14.8285 | 15.3371 | 15.8633 | 16.4074 | 16.9703 | 17.5524 | 18.1545 |  | 0.016052 | 0.017506 | 0.019102 | 0.020853 | 0.022774 | 0.024884 | 0.027201 | 0.029747 | 0.032543 | 0.035616 | 0.038994 | 0.042708 | 0.046792 | 0.051284 | 0.056226 | 0.061663 | 0.067647 | 0.074234 | 0.081484 | 0.089468 | 0.09826 | 0.10794 | 0.11861 | 0.13036 | 0.14331 | 0.15758 | 0.17331 | 0.19065 | 0.20977 | 0.23085 |  | 0.0027992 | 0.0030528 | 0.003331 | 0.0036363 | 0.0039714 | 0.0043393 | 0.0047434 | 0.0051872 | 0.0056749 | 0.0062108 | 0.0067999 | 0.0074475 | 0.0081597 | 0.008943 | 0.0098047 | 0.010753 | 0.011796 | 0.012945 | 0.014209 | 0.015601 | 0.017135 | 0.018823 | 0.020683 | 0.022733 | 0.024991 | 0.02748 | 0.030222 | 0.033246 | 0.036579 | 0.040255 | 1718.9773 | 1874.7169 | 2045.5716 | 2233.0591 | 2438.8527 | 2664.7976 | 2912.9284 | 3185.4892 | 3484.955 | 3814.0562 | 4175.8049 | 4573.5243 | 5010.8814 | 5491.9226 | 6021.1138 | 6603.3837 | 7244.1728 | 7949.4865 | 8725.9546 | 9580.8968 | 10522.3946 | 11559.3718 | 12701.6825 | 13960.2092 | 15346.9702 | 16875.2399 | 18559.68 | 20416.4861 | 22463.5487 | 24720.6322 |  | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 52.8111 | 70.0043 | 93.6052 | 126.148 | 171.2039 | 233.8148 | 321.11 | 443.1852 | 614.3548 | 854.9384 | 1193.8092 | 1672.0328 | 2348.0635 |  | 171.486 | 187.0226 | 204.0672 | 222.771 | 243.3011 | 265.8414 | 290.5951 | 317.7859 | 347.6607 | 380.492 | 416.5802 | 456.2569 | 499.8878 | 547.8767 | 600.6691 | 658.7566 | 722.682 | 793.0444 | 870.5052 | 955.7946 | 1049.7189 | 1153.1682 | 1267.1257 | 1392.6769 | 1531.0208 | 1683.4817 | 1851.5222 | 2036.758 | 2240.9739 | 2466.1416 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 144.3541 | 159.8907 | 176.9353 | 195.6391 | 216.1692 | 238.7095 | 263.4632 | 290.6539 | 320.5288 | 353.3601 | 389.4483 | 429.125 | 472.7559 | 520.7448 | 573.5372 | 631.6247 | 695.5501 | 760.5692 | 827.4574 | 898.2339 | 972.1466 | 1047.8897 | 1123.3458 | 1195.2165 | 1258.4926 | 1305.696 | 1325.7942 | 1302.648 | 1212.7895 | 1022.2451 |  | 1231.635 | 1343.2213 | 1465.6375 | 1599.9709 | 1747.4206 | 1909.3085 | 2087.0924 | 2282.3803 | 2496.9454 | 2732.7441 | 2991.9344 | 3276.8976 | 3590.2608 | 3934.9234 | 4314.0851 | 4731.2774 | 5190.3982 | 5695.7504 | 6252.0843 | 6864.6443 | 7539.2207 | 8282.2075 | 9100.665 | 10002.3904 | 10995.9948 | 12090.9891 | 13297.8785 | 14628.2668 | 16094.9726 | 17712.1568 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 1231.4292 | 1343.0156 | 1465.4318 | 1599.7652 | 1747.2149 | 1909.1027 | 2086.8867 | 2282.1746 | 2496.7397 | 2732.5384 | 2991.7287 | 3276.6918 | 3590.0551 | 3934.7177 | 4313.8794 | 4731.0716 | 5190.1924 | 5695.5042 | 6251.7579 | 6864.2078 | 7538.6326 | 8281.4092 | 9099.5748 | 10000.8932 | 10993.9284 | 12088.1246 | 13293.8921 | 14622.7004 | 16087.1764 | 17701.2084 |  | 1375.7833 | 1502.9063 | 1642.367 | 1795.4043 | 1963.384 | 2147.8123 | 2350.3499 | 2572.8285 | 2817.2685 | 3085.8984 | 3381.177 | 3705.8168 | 4062.811 | 4455.4625 | 4887.4165 | 5362.6963 | 5885.7425 | 6456.0734 | 7079.2153 | 7762.4417 | 8510.7792 | 9329.2989 | 10222.9206 | 11196.1096 | 12252.4209 | 13393.8205 | 14619.6863 | 15925.3484 | 17299.9658 | 18723.4535 |  | 61.4572 | 67.0253 | 73.1337 | 79.8368 | 87.1944 | 95.2724 | 104.1436 | 113.8883 | 124.5948 | 136.3609 | 149.2942 | 163.5136 | 179.1501 | 196.3483 | 215.2681 | 236.0855 | 258.9952 | 284.2117 | 311.9721 | 342.5382 | 376.1988 | 413.273 | 454.1132 | 499.1083 | 548.688 | 603.327 | 663.5495 | 729.9344 | 803.1214 | 883.8171 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 46.7848 | 52.3528 | 58.4613 | 65.1643 | 72.5219 | 80.6 | 89.4712 | 99.2158 | 109.9224 | 121.6885 | 134.6218 | 148.8411 | 164.4776 | 181.6759 | 200.5957 | 221.4131 | 244.3227 | 266.6497 | 288.6927 | 311.4104 | 334.2491 | 356.3403 | 376.3596 | 392.3253 | 401.3098 | 399.0274 | 379.2454 | 332.9411 | 247.0981 | 102.9843 |  | 6.4504 | 7.0348 | 7.676 | 8.3795 | 9.1517 | 9.9996 | 10.9307 | 11.9535 | 13.0772 | 14.3122 | 15.6696 | 17.1621 | 18.8032 | 20.6083 | 22.5941 | 24.7791 | 27.1836 | 29.8303 | 32.744 | 35.9521 | 39.4851 | 43.3763 | 47.6628 | 52.3854 | 57.5892 | 63.324 | 69.6448 | 76.6125 | 84.294 | 92.7637 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 4.3827 | 4.9671 | 5.6083 | 6.3118 | 7.0841 | 7.9319 | 8.863 | 9.8858 | 11.0095 | 12.2445 | 13.6019 | 15.0944 | 16.7355 | 18.5406 | 20.5264 | 22.7114 | 25.1159 | 27.3554 | 29.4633 | 31.5655 | 33.5734 | 35.3531 | 36.7055 | 37.3372 | 36.8201 | 34.5333 | 29.5796 | 20.6667 | 5.9371 | -17.2742 |  | 247.9487 | 270.4129 | 295.0573 | 322.1009 | 351.7849 | 384.3757 | 420.1666 | 459.4813 | 502.6768 | 550.147 | 602.3264 | 659.6942 | 722.7795 | 792.1658 | 868.4974 | 952.4851 | 1044.9138 | 1146.6497 | 1258.649 | 1381.9675 | 1517.771 | 1667.3467 | 1832.1158 | 2013.6482 | 2213.6774 | 2434.118 | 2677.085 | 2944.9144 | 3240.1868 | 3565.7529 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 247.9073 | 270.3715 | 295.0159 | 322.0594 | 351.7435 | 384.3343 | 420.1251 | 459.4398 | 502.6354 | 550.1056 | 602.2849 | 659.6528 | 722.738 | 792.1244 | 868.456 | 952.4437 | 1044.8724 | 1146.6001 | 1258.5833 | 1381.8797 | 1517.6526 | 1667.186 | 1831.8964 | 2013.3468 | 2213.2614 | 2433.5413 | 2676.2825 | 2943.7938 | 3238.6172 | 3563.5488 |  | 1674.8581 | 1830.5977 | 2001.4524 | 2188.9399 | 2394.7335 | 2620.6784 | 2868.8092 | 3141.37 | 3440.8358 | 3769.937 | 4131.6857 | 4529.4051 | 4966.7622 | 5447.8034 | 5976.9946 | 6559.2645 | 7200.0536 | 7896.6786 | 8655.9546 | 9487.2973 | 10396.2543 | 11388.1784 | 12467.8821 | 13639.1189 | 14903.8122 | 16260.9226 | 17704.7939 | 19222.7499 | 20791.6183 | 22372.7124
| TRUE | 3713 | 22004147 | SA | Blank | 66 | TRANS TR NO.1 | DIFFERENTIAL | X | Reyrolle | DUOBIAS_959 | DUOBIAS 979 | DUOBIAS | Electronic |  | 0.066046 | 2190 |  | 6.6 | 0.014726 | 0.0025679 | 0.012158 | 157.3198 | 1129.892 | 1287.2118 | 56.3804 | 5.9176 | 227.4661 |  | 9.2475 | 0.035616 | 0.0062108 | 0.029405 | 380.492 | 2732.7441 | 3113.2361 | 136.3609 | 14.3122 | 550.147 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.041417 |  | 1576.9758 | 3814.0562 | 71.2511 | 3742.8051 |  | 0.033728 |  | 6.8264 | 7.0606 | 7.3028 | 7.5533 | 7.8124 | 8.0804 | 8.3576 | 8.6443 | 8.9408 | 9.2475 | 9.5647 | 9.8928 | 10.2322 | 10.5832 | 10.9462 | 11.3217 | 11.7101 | 12.1118 | 12.5273 | 12.957 | 13.4015 | 13.8612 | 14.3367 | 14.8285 | 15.3371 | 15.8633 | 16.4074 | 16.9703 | 17.5524 | 18.1545 |  | 0.016052 | 0.017506 | 0.019102 | 0.020853 | 0.022774 | 0.024884 | 0.027201 | 0.029747 | 0.032543 | 0.035616 | 0.038994 | 0.042708 | 0.046792 | 0.051284 | 0.056226 | 0.061663 | 0.067647 | 0.074234 | 0.081484 | 0.089468 | 0.09826 | 0.10794 | 0.11861 | 0.13036 | 0.14331 | 0.15758 | 0.17331 | 0.19065 | 0.20977 | 0.23085 |  | 0.0027992 | 0.0030528 | 0.003331 | 0.0036363 | 0.0039714 | 0.0043393 | 0.0047434 | 0.0051872 | 0.0056749 | 0.0062108 | 0.0067999 | 0.0074475 | 0.0081597 | 0.008943 | 0.0098047 | 0.010753 | 0.011796 | 0.012945 | 0.014209 | 0.015601 | 0.017135 | 0.018823 | 0.020683 | 0.022733 | 0.024991 | 0.02748 | 0.030222 | 0.033246 | 0.036579 | 0.040255 | 1718.9773 | 1874.7169 | 2045.5716 | 2233.0591 | 2438.8527 | 2664.7976 | 2912.9284 | 3185.4892 | 3484.955 | 3814.0562 | 4175.8049 | 4573.5243 | 5010.8814 | 5491.9226 | 6021.1138 | 6603.3837 | 7244.1728 | 7949.4865 | 8725.9546 | 9580.8968 | 10522.3946 | 11559.3718 | 12701.6825 | 13960.2092 | 15346.9702 | 16875.2399 | 18559.68 | 20416.4861 | 22463.5487 | 24720.6322 |  | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 52.8111 | 70.0043 | 93.6052 | 126.148 | 171.2039 | 233.8148 | 321.11 | 443.1852 | 614.3548 | 854.9384 | 1193.8092 | 1672.0328 | 2348.0635 |  | 171.486 | 187.0226 | 204.0672 | 222.771 | 243.3011 | 265.8414 | 290.5951 | 317.7859 | 347.6607 | 380.492 | 416.5802 | 456.2569 | 499.8878 | 547.8767 | 600.6691 | 658.7566 | 722.682 | 793.0444 | 870.5052 | 955.7946 | 1049.7189 | 1153.1682 | 1267.1257 | 1392.6769 | 1531.0208 | 1683.4817 | 1851.5222 | 2036.758 | 2240.9739 | 2466.1416 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 144.3541 | 159.8907 | 176.9353 | 195.6391 | 216.1692 | 238.7095 | 263.4632 | 290.6539 | 320.5288 | 353.3601 | 389.4483 | 429.125 | 472.7559 | 520.7448 | 573.5372 | 631.6247 | 695.5501 | 760.5692 | 827.4574 | 898.2339 | 972.1466 | 1047.8897 | 1123.3458 | 1195.2165 | 1258.4926 | 1305.696 | 1325.7942 | 1302.648 | 1212.7895 | 1022.2451 |  | 1231.635 | 1343.2213 | 1465.6375 | 1599.9709 | 1747.4206 | 1909.3085 | 2087.0924 | 2282.3803 | 2496.9454 | 2732.7441 | 2991.9344 | 3276.8976 | 3590.2608 | 3934.9234 | 4314.0851 | 4731.2774 | 5190.3982 | 5695.7504 | 6252.0843 | 6864.6443 | 7539.2207 | 8282.2075 | 9100.665 | 10002.3904 | 10995.9948 | 12090.9891 | 13297.8785 | 14628.2668 | 16094.9726 | 17712.1568 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 1231.4292 | 1343.0156 | 1465.4318 | 1599.7652 | 1747.2149 | 1909.1027 | 2086.8867 | 2282.1746 | 2496.7397 | 2732.5384 | 2991.7287 | 3276.6918 | 3590.0551 | 3934.7177 | 4313.8794 | 4731.0716 | 5190.1924 | 5695.5042 | 6251.7579 | 6864.2078 | 7538.6326 | 8281.4092 | 9099.5748 | 10000.8932 | 10993.9284 | 12088.1246 | 13293.8921 | 14622.7004 | 16087.1764 | 17701.2084 |  | 1375.7833 | 1502.9063 | 1642.367 | 1795.4043 | 1963.384 | 2147.8123 | 2350.3499 | 2572.8285 | 2817.2685 | 3085.8984 | 3381.177 | 3705.8168 | 4062.811 | 4455.4625 | 4887.4165 | 5362.6963 | 5885.7425 | 6456.0734 | 7079.2153 | 7762.4417 | 8510.7792 | 9329.2989 | 10222.9206 | 11196.1096 | 12252.4209 | 13393.8205 | 14619.6863 | 15925.3484 | 17299.9658 | 18723.4535 |  | 61.4572 | 67.0253 | 73.1337 | 79.8368 | 87.1944 | 95.2724 | 104.1436 | 113.8883 | 124.5948 | 136.3609 | 149.2942 | 163.5136 | 179.1501 | 196.3483 | 215.2681 | 236.0855 | 258.9952 | 284.2117 | 311.9721 | 342.5382 | 376.1988 | 413.273 | 454.1132 | 499.1083 | 548.688 | 603.327 | 663.5495 | 729.9344 | 803.1214 | 883.8171 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 46.7848 | 52.3528 | 58.4613 | 65.1643 | 72.5219 | 80.6 | 89.4712 | 99.2158 | 109.9224 | 121.6885 | 134.6218 | 148.8411 | 164.4776 | 181.6759 | 200.5957 | 221.4131 | 244.3227 | 266.6497 | 288.6927 | 311.4104 | 334.2491 | 356.3403 | 376.3596 | 392.3253 | 401.3098 | 399.0274 | 379.2454 | 332.9411 | 247.0981 | 102.9843 |  | 6.4504 | 7.0348 | 7.676 | 8.3795 | 9.1517 | 9.9996 | 10.9307 | 11.9535 | 13.0772 | 14.3122 | 15.6696 | 17.1621 | 18.8032 | 20.6083 | 22.5941 | 24.7791 | 27.1836 | 29.8303 | 32.744 | 35.9521 | 39.4851 | 43.3763 | 47.6628 | 52.3854 | 57.5892 | 63.324 | 69.6448 | 76.6125 | 84.294 | 92.7637 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 4.3827 | 4.9671 | 5.6083 | 6.3118 | 7.0841 | 7.9319 | 8.863 | 9.8858 | 11.0095 | 12.2445 | 13.6019 | 15.0944 | 16.7355 | 18.5406 | 20.5264 | 22.7114 | 25.1159 | 27.3554 | 29.4633 | 31.5655 | 33.5734 | 35.3531 | 36.7055 | 37.3372 | 36.8201 | 34.5333 | 29.5796 | 20.6667 | 5.9371 | -17.2742 |  | 247.9487 | 270.4129 | 295.0573 | 322.1009 | 351.7849 | 384.3757 | 420.1666 | 459.4813 | 502.6768 | 550.147 | 602.3264 | 659.6942 | 722.7795 | 792.1658 | 868.4974 | 952.4851 | 1044.9138 | 1146.6497 | 1258.649 | 1381.9675 | 1517.771 | 1667.3467 | 1832.1158 | 2013.6482 | 2213.6774 | 2434.118 | 2677.085 | 2944.9144 | 3240.1868 | 3565.7529 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 247.9073 | 270.3715 | 295.0159 | 322.0594 | 351.7435 | 384.3343 | 420.1251 | 459.4398 | 502.6354 | 550.1056 | 602.2849 | 659.6528 | 722.738 | 792.1244 | 868.456 | 952.4437 | 1044.8724 | 1146.6001 | 1258.5833 | 1381.8797 | 1517.6526 | 1667.186 | 1831.8964 | 2013.3468 | 2213.2614 | 2433.5413 | 2676.2825 | 2943.7938 | 3238.6172 | 3563.5488 |  | 1674.8581 | 1830.5977 | 2001.4524 | 2188.9399 | 2394.7335 | 2620.6784 | 2868.8092 | 3141.37 | 3440.8358 | 3769.937 | 4131.6857 | 4529.4051 | 4966.7622 | 5447.8034 | 5976.9946 | 6559.2645 | 7200.0536 | 7896.6786 | 8655.9546 | 9487.2973 | 10396.2543 | 11388.1784 | 12467.8821 | 13639.1189 | 14903.8122 | 16260.9226 | 17704.7939 | 19222.7499 | 20791.6183 | 22372.7124
| TRUE | 3714 | 22004148 | SA | Blank | 66 | TRANS TR NO.1 | DIFFERENTIAL | X | Reyrolle | DUOBIAS_959 | DUOBIAS 979 | DUOBIAS | Electronic |  | 0.066046 | 2190 |  | 6.6 | 0.014726 | 0.0025679 | 0.012158 | 157.3198 | 1129.892 | 1287.2118 | 56.3804 | 5.9176 | 227.4661 |  | 9.2475 | 0.035616 | 0.0062108 | 0.029405 | 380.492 | 2732.7441 | 3113.2361 | 136.3609 | 14.3122 | 550.147 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.041417 |  | 1576.9758 | 3814.0562 | 71.2511 | 3742.8051 |  | 0.033728 |  | 6.8264 | 7.0606 | 7.3028 | 7.5533 | 7.8124 | 8.0804 | 8.3576 | 8.6443 | 8.9408 | 9.2475 | 9.5647 | 9.8928 | 10.2322 | 10.5832 | 10.9462 | 11.3217 | 11.7101 | 12.1118 | 12.5273 | 12.957 | 13.4015 | 13.8612 | 14.3367 | 14.8285 | 15.3371 | 15.8633 | 16.4074 | 16.9703 | 17.5524 | 18.1545 |  | 0.016052 | 0.017506 | 0.019102 | 0.020853 | 0.022774 | 0.024884 | 0.027201 | 0.029747 | 0.032543 | 0.035616 | 0.038994 | 0.042708 | 0.046792 | 0.051284 | 0.056226 | 0.061663 | 0.067647 | 0.074234 | 0.081484 | 0.089468 | 0.09826 | 0.10794 | 0.11861 | 0.13036 | 0.14331 | 0.15758 | 0.17331 | 0.19065 | 0.20977 | 0.23085 |  | 0.0027992 | 0.0030528 | 0.003331 | 0.0036363 | 0.0039714 | 0.0043393 | 0.0047434 | 0.0051872 | 0.0056749 | 0.0062108 | 0.0067999 | 0.0074475 | 0.0081597 | 0.008943 | 0.0098047 | 0.010753 | 0.011796 | 0.012945 | 0.014209 | 0.015601 | 0.017135 | 0.018823 | 0.020683 | 0.022733 | 0.024991 | 0.02748 | 0.030222 | 0.033246 | 0.036579 | 0.040255 | 1718.9773 | 1874.7169 | 2045.5716 | 2233.0591 | 2438.8527 | 2664.7976 | 2912.9284 | 3185.4892 | 3484.955 | 3814.0562 | 4175.8049 | 4573.5243 | 5010.8814 | 5491.9226 | 6021.1138 | 6603.3837 | 7244.1728 | 7949.4865 | 8725.9546 | 9580.8968 | 10522.3946 | 11559.3718 | 12701.6825 | 13960.2092 | 15346.9702 | 16875.2399 | 18559.68 | 20416.4861 | 22463.5487 | 24720.6322 |  | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 52.8111 | 70.0043 | 93.6052 | 126.148 | 171.2039 | 233.8148 | 321.11 | 443.1852 | 614.3548 | 854.9384 | 1193.8092 | 1672.0328 | 2348.0635 |  | 171.486 | 187.0226 | 204.0672 | 222.771 | 243.3011 | 265.8414 | 290.5951 | 317.7859 | 347.6607 | 380.492 | 416.5802 | 456.2569 | 499.8878 | 547.8767 | 600.6691 | 658.7566 | 722.682 | 793.0444 | 870.5052 | 955.7946 | 1049.7189 | 1153.1682 | 1267.1257 | 1392.6769 | 1531.0208 | 1683.4817 | 1851.5222 | 2036.758 | 2240.9739 | 2466.1416 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 144.3541 | 159.8907 | 176.9353 | 195.6391 | 216.1692 | 238.7095 | 263.4632 | 290.6539 | 320.5288 | 353.3601 | 389.4483 | 429.125 | 472.7559 | 520.7448 | 573.5372 | 631.6247 | 695.5501 | 760.5692 | 827.4574 | 898.2339 | 972.1466 | 1047.8897 | 1123.3458 | 1195.2165 | 1258.4926 | 1305.696 | 1325.7942 | 1302.648 | 1212.7895 | 1022.2451 |  | 1231.635 | 1343.2213 | 1465.6375 | 1599.9709 | 1747.4206 | 1909.3085 | 2087.0924 | 2282.3803 | 2496.9454 | 2732.7441 | 2991.9344 | 3276.8976 | 3590.2608 | 3934.9234 | 4314.0851 | 4731.2774 | 5190.3982 | 5695.7504 | 6252.0843 | 6864.6443 | 7539.2207 | 8282.2075 | 9100.665 | 10002.3904 | 10995.9948 | 12090.9891 | 13297.8785 | 14628.2668 | 16094.9726 | 17712.1568 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 1231.4292 | 1343.0156 | 1465.4318 | 1599.7652 | 1747.2149 | 1909.1027 | 2086.8867 | 2282.1746 | 2496.7397 | 2732.5384 | 2991.7287 | 3276.6918 | 3590.0551 | 3934.7177 | 4313.8794 | 4731.0716 | 5190.1924 | 5695.5042 | 6251.7579 | 6864.2078 | 7538.6326 | 8281.4092 | 9099.5748 | 10000.8932 | 10993.9284 | 12088.1246 | 13293.8921 | 14622.7004 | 16087.1764 | 17701.2084 |  | 1375.7833 | 1502.9063 | 1642.367 | 1795.4043 | 1963.384 | 2147.8123 | 2350.3499 | 2572.8285 | 2817.2685 | 3085.8984 | 3381.177 | 3705.8168 | 4062.811 | 4455.4625 | 4887.4165 | 5362.6963 | 5885.7425 | 6456.0734 | 7079.2153 | 7762.4417 | 8510.7792 | 9329.2989 | 10222.9206 | 11196.1096 | 12252.4209 | 13393.8205 | 14619.6863 | 15925.3484 | 17299.9658 | 18723.4535 |  | 61.4572 | 67.0253 | 73.1337 | 79.8368 | 87.1944 | 95.2724 | 104.1436 | 113.8883 | 124.5948 | 136.3609 | 149.2942 | 163.5136 | 179.1501 | 196.3483 | 215.2681 | 236.0855 | 258.9952 | 284.2117 | 311.9721 | 342.5382 | 376.1988 | 413.273 | 454.1132 | 499.1083 | 548.688 | 603.327 | 663.5495 | 729.9344 | 803.1214 | 883.8171 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 46.7848 | 52.3528 | 58.4613 | 65.1643 | 72.5219 | 80.6 | 89.4712 | 99.2158 | 109.9224 | 121.6885 | 134.6218 | 148.8411 | 164.4776 | 181.6759 | 200.5957 | 221.4131 | 244.3227 | 266.6497 | 288.6927 | 311.4104 | 334.2491 | 356.3403 | 376.3596 | 392.3253 | 401.3098 | 399.0274 | 379.2454 | 332.9411 | 247.0981 | 102.9843 |  | 6.4504 | 7.0348 | 7.676 | 8.3795 | 9.1517 | 9.9996 | 10.9307 | 11.9535 | 13.0772 | 14.3122 | 15.6696 | 17.1621 | 18.8032 | 20.6083 | 22.5941 | 24.7791 | 27.1836 | 29.8303 | 32.744 | 35.9521 | 39.4851 | 43.3763 | 47.6628 | 52.3854 | 57.5892 | 63.324 | 69.6448 | 76.6125 | 84.294 | 92.7637 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 4.3827 | 4.9671 | 5.6083 | 6.3118 | 7.0841 | 7.9319 | 8.863 | 9.8858 | 11.0095 | 12.2445 | 13.6019 | 15.0944 | 16.7355 | 18.5406 | 20.5264 | 22.7114 | 25.1159 | 27.3554 | 29.4633 | 31.5655 | 33.5734 | 35.3531 | 36.7055 | 37.3372 | 36.8201 | 34.5333 | 29.5796 | 20.6667 | 5.9371 | -17.2742 |  | 247.9487 | 270.4129 | 295.0573 | 322.1009 | 351.7849 | 384.3757 | 420.1666 | 459.4813 | 502.6768 | 550.147 | 602.3264 | 659.6942 | 722.7795 | 792.1658 | 868.4974 | 952.4851 | 1044.9138 | 1146.6497 | 1258.649 | 1381.9675 | 1517.771 | 1667.3467 | 1832.1158 | 2013.6482 | 2213.6774 | 2434.118 | 2677.085 | 2944.9144 | 3240.1868 | 3565.7529 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 247.9073 | 270.3715 | 295.0159 | 322.0594 | 351.7435 | 384.3343 | 420.1251 | 459.4398 | 502.6354 | 550.1056 | 602.2849 | 659.6528 | 722.738 | 792.1244 | 868.456 | 952.4437 | 1044.8724 | 1146.6001 | 1258.5833 | 1381.8797 | 1517.6526 | 1667.186 | 1831.8964 | 2013.3468 | 2213.2614 | 2433.5413 | 2676.2825 | 2943.7938 | 3238.6172 | 3563.5488 |  | 1674.8581 | 1830.5977 | 2001.4524 | 2188.9399 | 2394.7335 | 2620.6784 | 2868.8092 | 3141.37 | 3440.8358 | 3769.937 | 4131.6857 | 4529.4051 | 4966.7622 | 5447.8034 | 5976.9946 | 6559.2645 | 7200.0536 | 7896.6786 | 8655.9546 | 9487.2973 | 10396.2543 | 11388.1784 | 12467.8821 | 13639.1189 | 14903.8122 | 16260.9226 | 17704.7939 | 19222.7499 | 20791.6183 | 22372.7124
| TRUE | 3715 | 22004155 | SA | Blank | 66 | TRANS TR NO.2 | OVERCURRENT | Blank | English Electric | CDG11_522 | CDG11 522 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 675.3447 | 769.3759 | 33.699 | 3.537 | 135.9582 |  | 13.9533 | 0.022617 | 0.003944 | 0.018673 | 241.6202 | 1735.3484 | 1976.9686 | 86.592 | 9.0885 | 349.3546 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.041417 |  | 942.57 | 2422.0037 | 71.2511 | 2350.7526 |  | 0.034318 |  | 10.2456 | 10.6034 | 10.9736 | 11.3567 | 11.7532 | 12.1636 | 12.5882 | 13.0277 | 13.4826 | 13.9533 | 14.4405 | 14.9446 | 15.4664 | 16.0064 | 16.5653 | 17.1436 | 17.7422 | 18.3616 | 19.0027 | 19.6661 | 20.3528 | 21.0634 | 21.7988 | 22.5598 | 23.3475 | 24.1626 | 25.0062 | 25.8793 | 26.7829 | 27.718 |  | 0.0096591 | 0.010604 | 0.011644 | 0.012791 | 0.014056 | 0.01545 | 0.016987 | 0.018683 | 0.020553 | 0.022617 | 0.024894 | 0.027408 | 0.030182 | 0.033244 | 0.036626 | 0.04036 | 0.044483 | 0.049038 | 0.05407 | 0.059628 | 0.06577 | 0.072556 | 0.080057 | 0.088346 | 0.097509 | 0.10764 | 0.11884 | 0.13122 | 0.14491 | 0.16005 |  | 0.0016844 | 0.001849 | 0.0020305 | 0.0022305 | 0.002451 | 0.0026941 | 0.0029622 | 0.0032579 | 0.0035841 | 0.003944 | 0.0043411 | 0.0047794 | 0.0052631 | 0.0057972 | 0.0063868 | 0.007038 | 0.007757 | 0.0085513 | 0.0094287 | 0.010398 | 0.011469 | 0.012652 | 0.01396 | 0.015406 | 0.017004 | 0.01877 | 0.020723 | 0.022882 | 0.025269 | 0.027909 | 1034.3678 | 1135.5036 | 1246.9496 | 1369.7807 | 1505.1854 | 1654.4779 | 1819.1115 | 2000.6937 | 2201.0023 | 2422.0037 | 2665.8733 | 2935.0177 | 3232.0991 | 3560.0634 | 3922.1698 | 4322.0252 | 4763.6206 | 5251.3728 | 5790.1701 | 6385.4227 | 7043.119 | 7769.8871 | 8573.0642 | 9460.7725 | 10442.0035 | 11526.7118 | 12725.918 | 14051.8241 | 15517.9405 | 17139.2264 |  | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 52.8111 | 70.0043 | 93.6052 | 126.148 | 171.2039 | 233.8148 | 321.11 | 443.1852 | 614.3548 | 854.9384 | 1193.8092 | 1672.0328 | 2348.0635 |  | 103.189 | 113.2784 | 124.3963 | 136.65 | 150.158 | 165.0515 | 181.4754 | 199.5901 | 219.573 | 241.6202 | 265.9487 | 292.7987 | 322.4357 | 355.1536 | 391.2775 | 431.1672 | 475.221 | 523.8794 | 577.63 | 637.0127 | 702.6248 | 775.1275 | 855.2528 | 943.811 | 1041.6991 | 1149.91 | 1269.5434 | 1401.8164 | 1548.0769 | 1709.8171 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 76.0571 | 86.1465 | 97.2644 | 109.518 | 123.0261 | 137.9196 | 154.3435 | 172.4582 | 192.4411 | 214.4883 | 238.8168 | 265.6668 | 295.3038 | 328.0216 | 364.1456 | 404.0353 | 448.0891 | 491.4042 | 534.5822 | 579.452 | 625.0525 | 669.8489 | 711.4729 | 746.3506 | 769.1708 | 772.1243 | 743.8155 | 667.7064 | 519.8924 | 265.9206 |  | 741.1172 | 813.5803 | 893.4305 | 981.4381 | 1078.4546 | 1185.4216 | 1303.3804 | 1433.4828 | 1577.0024 | 1735.3484 | 1910.0793 | 2102.9192 | 2315.776 | 2550.76 | 2810.2068 | 3096.7003 | 3413.1002 | 3762.5712 | 4148.6156 | 4575.1099 | 5046.3446 | 5567.0687 | 6142.5394 | 6778.5761 | 7481.6211 | 8258.8068 | 9118.0295 | 10068.0319 | 11118.4938 | 12280.1336 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 740.9114 | 813.3745 | 893.2248 | 981.2324 | 1078.2489 | 1185.2159 | 1303.1747 | 1433.2771 | 1576.7967 | 1735.1427 | 1909.8735 | 2102.7135 | 2315.5702 | 2550.5543 | 2810.001 | 3096.4945 | 3412.8945 | 3762.3249 | 4148.2892 | 4574.6734 | 5045.7564 | 5566.2704 | 6141.4492 | 6777.0788 | 7479.5547 | 8255.9423 | 9114.0432 | 10062.4654 | 11110.6975 | 12269.1852 |  | 816.9685 | 899.521 | 990.4891 | 1090.7504 | 1201.2749 | 1323.1354 | 1457.5182 | 1605.7353 | 1769.2378 | 1949.631 | 2148.6904 | 2368.3803 | 2610.874 | 2878.5759 | 3174.1466 | 3500.5298 | 3860.9835 | 4253.7291 | 4682.8714 | 5154.1254 | 5670.8088 | 6236.1194 | 6852.9221 | 7523.4294 | 8248.7255 | 9028.0666 | 9857.8586 | 10730.1718 | 11630.59 | 12535.1057 |  | 36.9809 | 40.5968 | 44.5812 | 48.9727 | 53.8137 | 59.1512 | 65.0372 | 71.5292 | 78.6907 | 86.592 | 95.3109 | 104.9334 | 115.5547 | 127.2801 | 140.2262 | 154.5219 | 170.3099 | 187.7482 | 207.0114 | 228.2929 | 251.807 | 277.7906 | 306.506 | 338.2435 | 373.3247 | 412.1054 | 454.9796 | 502.3837 | 554.8006 | 612.7651 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.3085 | 25.9243 | 29.9088 | 34.3002 | 39.1413 | 44.4788 | 50.3648 | 56.8568 | 64.0182 | 71.9195 | 80.6384 | 90.2609 | 100.8822 | 112.6077 | 125.5538 | 139.8495 | 155.6375 | 170.1862 | 183.7319 | 197.1652 | 209.8574 | 220.8579 | 228.7524 | 231.4605 | 225.9464 | 207.8058 | 170.6756 | 105.3904 | -1.2227 | -168.0677 |  | 3.8814 | 4.261 | 4.6792 | 5.1401 | 5.6482 | 6.2084 | 6.8262 | 7.5076 | 8.2592 | 9.0885 | 10.0036 | 11.0136 | 12.1284 | 13.3591 | 14.7179 | 16.2183 | 17.8754 | 19.7057 | 21.7275 | 23.9612 | 26.4292 | 29.1563 | 32.1703 | 35.5014 | 39.1834 | 43.2538 | 47.7538 | 52.7292 | 58.2308 | 64.3146 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8137 | 2.1933 | 2.6115 | 3.0724 | 3.5805 | 4.1407 | 4.7585 | 5.4399 | 6.1915 | 7.0208 | 7.9359 | 8.9459 | 10.0607 | 11.2914 | 12.6502 | 14.1506 | 15.8077 | 17.2308 | 18.4469 | 19.5745 | 20.5175 | 21.1332 | 21.2129 | 20.4531 | 18.4143 | 14.4631 | 7.6886 | -3.2166 | -20.1261 | -45.7233 |  | 149.1993 | 163.7873 | 179.8625 | 197.5799 | 217.1109 | 238.6452 | 262.3922 | 288.584 | 317.4769 | 349.3546 | 384.5309 | 423.3528 | 466.2044 | 513.5106 | 565.7415 | 623.4175 | 687.1141 | 757.4684 | 835.1856 | 921.046 | 1015.9134 | 1120.7439 | 1236.5958 | 1364.6406 | 1506.1753 | 1662.6357 | 1835.6116 | 2026.8629 | 2238.3385 | 2472.196 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 149.1578 | 163.7459 | 179.8211 | 197.5385 | 217.0695 | 238.6037 | 262.3508 | 288.5426 | 317.4355 | 349.3132 | 384.4894 | 423.3113 | 466.163 | 513.4692 | 565.7001 | 623.3761 | 687.0726 | 757.4188 | 835.1199 | 920.9582 | 1015.795 | 1120.5832 | 1236.3763 | 1364.3391 | 1505.7593 | 1662.059 | 1834.8091 | 2025.7423 | 2236.769 | 2469.9919 |  | 990.2486 | 1091.3844 | 1202.8304 | 1325.6615 | 1461.0662 | 1610.3587 | 1774.9923 | 1956.5745 | 2156.8831 | 2377.8845 | 2621.7542 | 2890.8985 | 3187.9799 | 3515.9442 | 3878.0507 | 4277.906 | 4719.5014 | 5198.5649 | 5720.1701 | 6291.8232 | 6916.9787 | 7598.6936 | 8339.2637 | 9139.6822 | 9998.8455 | 10912.3945 | 11871.0319 | 12858.088 | 13846.0101 | 14791.3066
| TRUE | 3716 | 22004156 | SA | Blank | 66 | TRANS TR NO.2 | OVERCURRENT | Blank | English Electric | CDG11_522 | CDG11 522 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 675.3447 | 769.3759 | 33.699 | 3.537 | 135.9582 |  | 14.6263 | 0.025802 | 0.0044993 | 0.021302 | 275.6434 | 1979.7072 | 2255.3506 | 98.7852 | 10.3683 | 398.5481 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.041417 |  | 942.57 | 2763.0522 | 71.2511 | 2691.8011 |  | 0.039029 |  | 10.294 | 10.7037 | 11.1297 | 11.5727 | 12.0333 | 12.5122 | 13.0102 | 13.528 | 14.0664 | 14.6263 | 15.2084 | 15.8137 | 16.4431 | 17.0975 | 17.778 | 18.4856 | 19.2213 | 19.9863 | 20.7818 | 21.6089 | 22.4689 | 23.3632 | 24.2931 | 25.2599 | 26.2653 | 27.3106 | 28 | 28 | 28 | 28 |  | 0.0097834 | 0.010879 | 0.012103 | 0.01347 | 0.014998 | 0.016705 | 0.018613 | 0.020747 | 0.023133 | 0.025802 | 0.028788 | 0.032129 | 0.035868 | 0.040053 | 0.044739 | 0.049986 | 0.055861 | 0.062442 | 0.069814 | 0.078073 | 0.087327 | 0.097698 | 0.10932 | 0.12235 | 0.13696 | 0.15333 | 0.16481 | 0.16481 | 0.16481 | 0.16481 |  | 0.001706 | 0.0018971 | 0.0021105 | 0.0023489 | 0.0026153 | 0.002913 | 0.0032458 | 0.0036178 | 0.0040339 | 0.0044993 | 0.00502 | 0.0056026 | 0.0062547 | 0.0069845 | 0.0078016 | 0.0087165 | 0.0097411 | 0.010889 | 0.012174 | 0.013614 | 0.015228 | 0.017037 | 0.019064 | 0.021335 | 0.023882 | 0.026738 | 0.02874 | 0.02874 | 0.02874 | 0.02874 | 1047.6755 | 1165.0265 | 1296.0833 | 1442.483 | 1606.0609 | 1788.8749 | 1993.2322 | 2221.7206 | 2477.2423 | 2763.0522 | 3082.8019 | 3440.5875 | 3841.0048 | 4289.2099 | 4790.9887 | 5352.8339 | 5982.0316 | 6686.7594 | 7476.1956 | 8360.6424 | 9351.6643 | 10462.2435 | 11706.9543 | 13102.1593 | 14666.2299 | 16419.7939 | 17649.5414 | 17649.5414 | 17649.5414 | 17649.5414 |  | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 52.8111 | 70.0043 | 93.6052 | 126.148 | 171.2039 | 233.8148 | 321.11 | 443.1852 | 614.3548 | 854.9384 | 1193.8092 | 1672.0328 | 2348.0635 |  | 104.5166 | 116.2236 | 129.2979 | 143.9028 | 160.2214 | 178.459 | 198.8458 | 221.6399 | 247.1308 | 275.6434 | 307.5417 | 343.2346 | 383.1804 | 427.8935 | 477.9512 | 534.0012 | 596.7702 | 667.0742 | 745.8287 | 834.0615 | 932.9263 | 1043.7182 | 1167.8911 | 1307.0774 | 1463.1098 | 1638.0462 | 1760.7263 | 1760.7263 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 77.3847 | 89.0917 | 102.166 | 116.7709 | 133.0895 | 151.3271 | 171.7139 | 194.508 | 219.9989 | 248.5114 | 280.4098 | 316.1027 | 356.0485 | 400.7616 | 450.8193 | 506.8692 | 569.6383 | 634.599 | 702.7809 | 776.5008 | 855.354 | 938.4397 | 1024.1112 | 1109.617 | 1190.5816 | 1260.2605 | 1234.9984 | 1026.6163 | 732.5419 | 316.8298 |  | 750.652 | 834.7332 | 928.6344 | 1033.5288 | 1150.7312 | 1281.7161 | 1428.1367 | 1591.847 | 1774.9264 | 1979.7072 | 2208.8056 | 2465.1565 | 2752.0526 | 3073.1883 | 3432.7093 | 3835.2673 | 4286.083 | 4791.0154 | 5356.6409 | 5990.3407 | 6700.4009 | 7496.123 | 8387.9493 | 9387.6038 | 10508.2493 | 11764.6654 | 12645.7707 | 12645.7707 | 12645.7707 | 12645.7707 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 750.4463 | 834.5274 | 928.4287 | 1033.3231 | 1150.5255 | 1281.5104 | 1427.931 | 1591.6413 | 1774.7207 | 1979.5015 | 2208.5999 | 2464.9507 | 2751.8468 | 3072.9826 | 3432.5036 | 3835.0616 | 4285.8773 | 4790.7692 | 5356.3144 | 5989.9042 | 6699.8127 | 7495.3247 | 8386.8591 | 9386.1065 | 10506.1828 | 11761.8008 | 12641.7843 | 12640.2043 | 12637.9744 | 12634.8223 |  | 827.831 | 923.6191 | 1030.5947 | 1150.0939 | 1283.615 | 1432.8374 | 1599.6448 | 1786.1492 | 1994.7196 | 2228.0129 | 2489.0097 | 2781.0534 | 3107.8953 | 3473.7442 | 3883.3229 | 4341.9308 | 4855.5156 | 5425.3682 | 6059.0953 | 6766.405 | 7555.1667 | 8433.7643 | 9410.9703 | 10495.7235 | 11696.7644 | 13022.0612 | 13876.7827 | 13666.8206 | 13370.5163 | 12951.6521 |  | 37.4567 | 41.6523 | 46.3378 | 51.5719 | 57.4202 | 63.9562 | 71.2624 | 79.4314 | 88.5669 | 98.7852 | 110.217 | 123.0086 | 137.3244 | 153.3487 | 171.2884 | 191.3756 | 213.8708 | 239.0664 | 267.2905 | 298.9114 | 334.3426 | 374.0483 | 418.5494 | 468.4311 | 524.3501 | 587.0438 | 631.01 | 631.01 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.7843 | 26.9798 | 31.6654 | 36.8995 | 42.7478 | 49.2838 | 56.59 | 64.759 | 73.8944 | 84.1128 | 95.5445 | 108.3362 | 122.652 | 138.6763 | 156.616 | 176.7032 | 199.1984 | 221.5044 | 244.011 | 267.7836 | 292.3929 | 317.1156 | 340.7959 | 361.6481 | 376.9718 | 382.7443 | 346.706 | 234.0168 | 74.9867 | -149.8228 |  | 3.9314 | 4.3717 | 4.8635 | 5.4129 | 6.0267 | 6.7127 | 7.4796 | 8.337 | 9.2958 | 10.3683 | 11.5682 | 12.9107 | 14.4133 | 16.0952 | 17.9781 | 20.0864 | 22.4475 | 25.0919 | 28.0543 | 31.3731 | 35.0919 | 39.2594 | 43.9301 | 49.1656 | 55.0347 | 61.615 | 66.2296 | 66.2296 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8637 | 2.304 | 2.7958 | 3.3452 | 3.959 | 4.645 | 5.4119 | 6.2693 | 7.2281 | 8.3006 | 9.5005 | 10.843 | 12.3456 | 14.0275 | 15.9104 | 18.0187 | 20.3798 | 22.617 | 24.7736 | 26.9865 | 29.1802 | 31.2362 | 32.9728 | 34.1173 | 34.2656 | 32.8243 | 26.1644 | 10.2838 | -12.1274 | -43.8084 |  | 151.1188 | 168.0457 | 186.9496 | 208.0666 | 231.6614 | 258.0309 | 287.5078 | 320.4654 | 357.3223 | 398.5481 | 444.6695 | 496.2772 | 554.0341 | 618.6841 | 691.0617 | 772.1034 | 862.8601 | 964.5114 | 1078.3813 | 1205.9556 | 1348.9026 | 1509.0947 | 1688.6343 | 1889.8814 | 2115.4861 | 2368.4236 | 2545.8048 | 2545.8048 | 2545.8048 | 2545.8048 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 151.0774 | 168.0043 | 186.9082 | 208.0252 | 231.62 | 257.9894 | 287.4663 | 320.424 | 357.2809 | 398.5067 | 444.628 | 496.2357 | 553.9927 | 618.6427 | 691.0203 | 772.0619 | 862.8187 | 964.4618 | 1078.3155 | 1205.8678 | 1348.7842 | 1508.934 | 1688.4148 | 1889.58 | 2115.07 | 2367.8469 | 2545.0023 | 2544.6842 | 2544.2353 | 2543.6007 |  | 1003.5563 | 1120.9073 | 1251.9641 | 1398.3638 | 1561.9417 | 1744.7557 | 1949.113 | 2177.6015 | 2433.1231 | 2718.933 | 3038.6827 | 3396.4683 | 3796.8856 | 4245.0907 | 4746.8695 | 5308.7147 | 5937.9124 | 6633.9515 | 7406.1956 | 8267.0429 | 9225.524 | 10291.0501 | 11473.1538 | 12781.069 | 14223.0719 | 15805.4767 | 16794.6553 | 16455.8053 | 15977.611 | 15301.6217
| TRUE | 3717 | 22004157 | SA | Blank | 66 | TRANS TR NO.2 | OVERCURRENT | Blank | English Electric | CDG11_522 | CDG11 522 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 675.3447 | 769.3759 | 33.699 | 3.537 | 135.9582 |  | 14.6263 | 0.025802 | 0.0044993 | 0.021302 | 275.6434 | 1979.7072 | 2255.3506 | 98.7852 | 10.3683 | 398.5481 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.041417 |  | 942.57 | 2763.0522 | 71.2511 | 2691.8011 |  | 0.039029 |  | 10.294 | 10.7037 | 11.1297 | 11.5727 | 12.0333 | 12.5122 | 13.0102 | 13.528 | 14.0664 | 14.6263 | 15.2084 | 15.8137 | 16.4431 | 17.0975 | 17.778 | 18.4856 | 19.2213 | 19.9863 | 20.7818 | 21.6089 | 22.4689 | 23.3632 | 24.2931 | 25.2599 | 26.2653 | 27.3106 | 28 | 28 | 28 | 28 |  | 0.0097834 | 0.010879 | 0.012103 | 0.01347 | 0.014998 | 0.016705 | 0.018613 | 0.020747 | 0.023133 | 0.025802 | 0.028788 | 0.032129 | 0.035868 | 0.040053 | 0.044739 | 0.049986 | 0.055861 | 0.062442 | 0.069814 | 0.078073 | 0.087327 | 0.097698 | 0.10932 | 0.12235 | 0.13696 | 0.15333 | 0.16481 | 0.16481 | 0.16481 | 0.16481 |  | 0.001706 | 0.0018971 | 0.0021105 | 0.0023489 | 0.0026153 | 0.002913 | 0.0032458 | 0.0036178 | 0.0040339 | 0.0044993 | 0.00502 | 0.0056026 | 0.0062547 | 0.0069845 | 0.0078016 | 0.0087165 | 0.0097411 | 0.010889 | 0.012174 | 0.013614 | 0.015228 | 0.017037 | 0.019064 | 0.021335 | 0.023882 | 0.026738 | 0.02874 | 0.02874 | 0.02874 | 0.02874 | 1047.6755 | 1165.0265 | 1296.0833 | 1442.483 | 1606.0609 | 1788.8749 | 1993.2322 | 2221.7206 | 2477.2423 | 2763.0522 | 3082.8019 | 3440.5875 | 3841.0048 | 4289.2099 | 4790.9887 | 5352.8339 | 5982.0316 | 6686.7594 | 7476.1956 | 8360.6424 | 9351.6643 | 10462.2435 | 11706.9543 | 13102.1593 | 14666.2299 | 16419.7939 | 17649.5414 | 17649.5414 | 17649.5414 | 17649.5414 |  | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 52.8111 | 70.0043 | 93.6052 | 126.148 | 171.2039 | 233.8148 | 321.11 | 443.1852 | 614.3548 | 854.9384 | 1193.8092 | 1672.0328 | 2348.0635 |  | 104.5166 | 116.2236 | 129.2979 | 143.9028 | 160.2214 | 178.459 | 198.8458 | 221.6399 | 247.1308 | 275.6434 | 307.5417 | 343.2346 | 383.1804 | 427.8935 | 477.9512 | 534.0012 | 596.7702 | 667.0742 | 745.8287 | 834.0615 | 932.9263 | 1043.7182 | 1167.8911 | 1307.0774 | 1463.1098 | 1638.0462 | 1760.7263 | 1760.7263 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 77.3847 | 89.0917 | 102.166 | 116.7709 | 133.0895 | 151.3271 | 171.7139 | 194.508 | 219.9989 | 248.5114 | 280.4098 | 316.1027 | 356.0485 | 400.7616 | 450.8193 | 506.8692 | 569.6383 | 634.599 | 702.7809 | 776.5008 | 855.354 | 938.4397 | 1024.1112 | 1109.617 | 1190.5816 | 1260.2605 | 1234.9984 | 1026.6163 | 732.5419 | 316.8298 |  | 750.652 | 834.7332 | 928.6344 | 1033.5288 | 1150.7312 | 1281.7161 | 1428.1367 | 1591.847 | 1774.9264 | 1979.7072 | 2208.8056 | 2465.1565 | 2752.0526 | 3073.1883 | 3432.7093 | 3835.2673 | 4286.083 | 4791.0154 | 5356.6409 | 5990.3407 | 6700.4009 | 7496.123 | 8387.9493 | 9387.6038 | 10508.2493 | 11764.6654 | 12645.7707 | 12645.7707 | 12645.7707 | 12645.7707 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 750.4463 | 834.5274 | 928.4287 | 1033.3231 | 1150.5255 | 1281.5104 | 1427.931 | 1591.6413 | 1774.7207 | 1979.5015 | 2208.5999 | 2464.9507 | 2751.8468 | 3072.9826 | 3432.5036 | 3835.0616 | 4285.8773 | 4790.7692 | 5356.3144 | 5989.9042 | 6699.8127 | 7495.3247 | 8386.8591 | 9386.1065 | 10506.1828 | 11761.8008 | 12641.7843 | 12640.2043 | 12637.9744 | 12634.8223 |  | 827.831 | 923.6191 | 1030.5947 | 1150.0939 | 1283.615 | 1432.8374 | 1599.6448 | 1786.1492 | 1994.7196 | 2228.0129 | 2489.0097 | 2781.0534 | 3107.8953 | 3473.7442 | 3883.3229 | 4341.9308 | 4855.5156 | 5425.3682 | 6059.0953 | 6766.405 | 7555.1667 | 8433.7643 | 9410.9703 | 10495.7235 | 11696.7644 | 13022.0612 | 13876.7827 | 13666.8206 | 13370.5163 | 12951.6521 |  | 37.4567 | 41.6523 | 46.3378 | 51.5719 | 57.4202 | 63.9562 | 71.2624 | 79.4314 | 88.5669 | 98.7852 | 110.217 | 123.0086 | 137.3244 | 153.3487 | 171.2884 | 191.3756 | 213.8708 | 239.0664 | 267.2905 | 298.9114 | 334.3426 | 374.0483 | 418.5494 | 468.4311 | 524.3501 | 587.0438 | 631.01 | 631.01 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.7843 | 26.9798 | 31.6654 | 36.8995 | 42.7478 | 49.2838 | 56.59 | 64.759 | 73.8944 | 84.1128 | 95.5445 | 108.3362 | 122.652 | 138.6763 | 156.616 | 176.7032 | 199.1984 | 221.5044 | 244.011 | 267.7836 | 292.3929 | 317.1156 | 340.7959 | 361.6481 | 376.9718 | 382.7443 | 346.706 | 234.0168 | 74.9867 | -149.8228 |  | 3.9314 | 4.3717 | 4.8635 | 5.4129 | 6.0267 | 6.7127 | 7.4796 | 8.337 | 9.2958 | 10.3683 | 11.5682 | 12.9107 | 14.4133 | 16.0952 | 17.9781 | 20.0864 | 22.4475 | 25.0919 | 28.0543 | 31.3731 | 35.0919 | 39.2594 | 43.9301 | 49.1656 | 55.0347 | 61.615 | 66.2296 | 66.2296 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8637 | 2.304 | 2.7958 | 3.3452 | 3.959 | 4.645 | 5.4119 | 6.2693 | 7.2281 | 8.3006 | 9.5005 | 10.843 | 12.3456 | 14.0275 | 15.9104 | 18.0187 | 20.3798 | 22.617 | 24.7736 | 26.9865 | 29.1802 | 31.2362 | 32.9728 | 34.1173 | 34.2656 | 32.8243 | 26.1644 | 10.2838 | -12.1274 | -43.8084 |  | 151.1188 | 168.0457 | 186.9496 | 208.0666 | 231.6614 | 258.0309 | 287.5078 | 320.4654 | 357.3223 | 398.5481 | 444.6695 | 496.2772 | 554.0341 | 618.6841 | 691.0617 | 772.1034 | 862.8601 | 964.5114 | 1078.3813 | 1205.9556 | 1348.9026 | 1509.0947 | 1688.6343 | 1889.8814 | 2115.4861 | 2368.4236 | 2545.8048 | 2545.8048 | 2545.8048 | 2545.8048 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 151.0774 | 168.0043 | 186.9082 | 208.0252 | 231.62 | 257.9894 | 287.4663 | 320.424 | 357.2809 | 398.5067 | 444.628 | 496.2357 | 553.9927 | 618.6427 | 691.0203 | 772.0619 | 862.8187 | 964.4618 | 1078.3155 | 1205.8678 | 1348.7842 | 1508.934 | 1688.4148 | 1889.58 | 2115.07 | 2367.8469 | 2545.0023 | 2544.6842 | 2544.2353 | 2543.6007 |  | 1003.5563 | 1120.9073 | 1251.9641 | 1398.3638 | 1561.9417 | 1744.7557 | 1949.113 | 2177.6015 | 2433.1231 | 2718.933 | 3038.6827 | 3396.4683 | 3796.8856 | 4245.0907 | 4746.8695 | 5308.7147 | 5937.9124 | 6633.9515 | 7406.1956 | 8267.0429 | 9225.524 | 10291.0501 | 11473.1538 | 12781.069 | 14223.0719 | 15805.4767 | 16794.6553 | 16455.8053 | 15977.611 | 15301.6217
| TRUE | 3718 | 22004152 | SA | Blank | 66 | TRANS TR NO.2 | DIFFERENTIAL | X | Reyrolle | DUOBIAS_959 | DUOBIAS 979 | DUOBIAS | Electronic |  | 0.066046 | 2190 |  | 6.6 | 0.014726 | 0.0025679 | 0.012158 | 157.3198 | 1129.892 | 1287.2118 | 56.3804 | 5.9176 | 227.4661 |  | 9.2475 | 0.035616 | 0.0062108 | 0.029405 | 380.492 | 2732.7441 | 3113.2361 | 136.3609 | 14.3122 | 550.147 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.041417 |  | 1576.9758 | 3814.0562 | 71.2511 | 3742.8051 |  | 0.033728 |  | 6.8264 | 7.0606 | 7.3028 | 7.5533 | 7.8124 | 8.0804 | 8.3576 | 8.6443 | 8.9408 | 9.2475 | 9.5647 | 9.8928 | 10.2322 | 10.5832 | 10.9462 | 11.3217 | 11.7101 | 12.1118 | 12.5273 | 12.957 | 13.4015 | 13.8612 | 14.3367 | 14.8285 | 15.3371 | 15.8633 | 16.4074 | 16.9703 | 17.5524 | 18.1545 |  | 0.016052 | 0.017506 | 0.019102 | 0.020853 | 0.022774 | 0.024884 | 0.027201 | 0.029747 | 0.032543 | 0.035616 | 0.038994 | 0.042708 | 0.046792 | 0.051284 | 0.056226 | 0.061663 | 0.067647 | 0.074234 | 0.081484 | 0.089468 | 0.09826 | 0.10794 | 0.11861 | 0.13036 | 0.14331 | 0.15758 | 0.17331 | 0.19065 | 0.20977 | 0.23085 |  | 0.0027992 | 0.0030528 | 0.003331 | 0.0036363 | 0.0039714 | 0.0043393 | 0.0047434 | 0.0051872 | 0.0056749 | 0.0062108 | 0.0067999 | 0.0074475 | 0.0081597 | 0.008943 | 0.0098047 | 0.010753 | 0.011796 | 0.012945 | 0.014209 | 0.015601 | 0.017135 | 0.018823 | 0.020683 | 0.022733 | 0.024991 | 0.02748 | 0.030222 | 0.033246 | 0.036579 | 0.040255 | 1718.9773 | 1874.7169 | 2045.5716 | 2233.0591 | 2438.8527 | 2664.7976 | 2912.9284 | 3185.4892 | 3484.955 | 3814.0562 | 4175.8049 | 4573.5243 | 5010.8814 | 5491.9226 | 6021.1138 | 6603.3837 | 7244.1728 | 7949.4865 | 8725.9546 | 9580.8968 | 10522.3946 | 11559.3718 | 12701.6825 | 13960.2092 | 15346.9702 | 16875.2399 | 18559.68 | 20416.4861 | 22463.5487 | 24720.6322 |  | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 52.8111 | 70.0043 | 93.6052 | 126.148 | 171.2039 | 233.8148 | 321.11 | 443.1852 | 614.3548 | 854.9384 | 1193.8092 | 1672.0328 | 2348.0635 |  | 171.486 | 187.0226 | 204.0672 | 222.771 | 243.3011 | 265.8414 | 290.5951 | 317.7859 | 347.6607 | 380.492 | 416.5802 | 456.2569 | 499.8878 | 547.8767 | 600.6691 | 658.7566 | 722.682 | 793.0444 | 870.5052 | 955.7946 | 1049.7189 | 1153.1682 | 1267.1257 | 1392.6769 | 1531.0208 | 1683.4817 | 1851.5222 | 2036.758 | 2240.9739 | 2466.1416 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 144.3541 | 159.8907 | 176.9353 | 195.6391 | 216.1692 | 238.7095 | 263.4632 | 290.6539 | 320.5288 | 353.3601 | 389.4483 | 429.125 | 472.7559 | 520.7448 | 573.5372 | 631.6247 | 695.5501 | 760.5692 | 827.4574 | 898.2339 | 972.1466 | 1047.8897 | 1123.3458 | 1195.2165 | 1258.4926 | 1305.696 | 1325.7942 | 1302.648 | 1212.7895 | 1022.2451 |  | 1231.635 | 1343.2213 | 1465.6375 | 1599.9709 | 1747.4206 | 1909.3085 | 2087.0924 | 2282.3803 | 2496.9454 | 2732.7441 | 2991.9344 | 3276.8976 | 3590.2608 | 3934.9234 | 4314.0851 | 4731.2774 | 5190.3982 | 5695.7504 | 6252.0843 | 6864.6443 | 7539.2207 | 8282.2075 | 9100.665 | 10002.3904 | 10995.9948 | 12090.9891 | 13297.8785 | 14628.2668 | 16094.9726 | 17712.1568 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 1231.4292 | 1343.0156 | 1465.4318 | 1599.7652 | 1747.2149 | 1909.1027 | 2086.8867 | 2282.1746 | 2496.7397 | 2732.5384 | 2991.7287 | 3276.6918 | 3590.0551 | 3934.7177 | 4313.8794 | 4731.0716 | 5190.1924 | 5695.5042 | 6251.7579 | 6864.2078 | 7538.6326 | 8281.4092 | 9099.5748 | 10000.8932 | 10993.9284 | 12088.1246 | 13293.8921 | 14622.7004 | 16087.1764 | 17701.2084 |  | 1375.7833 | 1502.9063 | 1642.367 | 1795.4043 | 1963.384 | 2147.8123 | 2350.3499 | 2572.8285 | 2817.2685 | 3085.8984 | 3381.177 | 3705.8168 | 4062.811 | 4455.4625 | 4887.4165 | 5362.6963 | 5885.7425 | 6456.0734 | 7079.2153 | 7762.4417 | 8510.7792 | 9329.2989 | 10222.9206 | 11196.1096 | 12252.4209 | 13393.8205 | 14619.6863 | 15925.3484 | 17299.9658 | 18723.4535 |  | 61.4572 | 67.0253 | 73.1337 | 79.8368 | 87.1944 | 95.2724 | 104.1436 | 113.8883 | 124.5948 | 136.3609 | 149.2942 | 163.5136 | 179.1501 | 196.3483 | 215.2681 | 236.0855 | 258.9952 | 284.2117 | 311.9721 | 342.5382 | 376.1988 | 413.273 | 454.1132 | 499.1083 | 548.688 | 603.327 | 663.5495 | 729.9344 | 803.1214 | 883.8171 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 46.7848 | 52.3528 | 58.4613 | 65.1643 | 72.5219 | 80.6 | 89.4712 | 99.2158 | 109.9224 | 121.6885 | 134.6218 | 148.8411 | 164.4776 | 181.6759 | 200.5957 | 221.4131 | 244.3227 | 266.6497 | 288.6927 | 311.4104 | 334.2491 | 356.3403 | 376.3596 | 392.3253 | 401.3098 | 399.0274 | 379.2454 | 332.9411 | 247.0981 | 102.9843 |  | 6.4504 | 7.0348 | 7.676 | 8.3795 | 9.1517 | 9.9996 | 10.9307 | 11.9535 | 13.0772 | 14.3122 | 15.6696 | 17.1621 | 18.8032 | 20.6083 | 22.5941 | 24.7791 | 27.1836 | 29.8303 | 32.744 | 35.9521 | 39.4851 | 43.3763 | 47.6628 | 52.3854 | 57.5892 | 63.324 | 69.6448 | 76.6125 | 84.294 | 92.7637 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 4.3827 | 4.9671 | 5.6083 | 6.3118 | 7.0841 | 7.9319 | 8.863 | 9.8858 | 11.0095 | 12.2445 | 13.6019 | 15.0944 | 16.7355 | 18.5406 | 20.5264 | 22.7114 | 25.1159 | 27.3554 | 29.4633 | 31.5655 | 33.5734 | 35.3531 | 36.7055 | 37.3372 | 36.8201 | 34.5333 | 29.5796 | 20.6667 | 5.9371 | -17.2742 |  | 247.9487 | 270.4129 | 295.0573 | 322.1009 | 351.7849 | 384.3757 | 420.1666 | 459.4813 | 502.6768 | 550.147 | 602.3264 | 659.6942 | 722.7795 | 792.1658 | 868.4974 | 952.4851 | 1044.9138 | 1146.6497 | 1258.649 | 1381.9675 | 1517.771 | 1667.3467 | 1832.1158 | 2013.6482 | 2213.6774 | 2434.118 | 2677.085 | 2944.9144 | 3240.1868 | 3565.7529 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 247.9073 | 270.3715 | 295.0159 | 322.0594 | 351.7435 | 384.3343 | 420.1251 | 459.4398 | 502.6354 | 550.1056 | 602.2849 | 659.6528 | 722.738 | 792.1244 | 868.456 | 952.4437 | 1044.8724 | 1146.6001 | 1258.5833 | 1381.8797 | 1517.6526 | 1667.186 | 1831.8964 | 2013.3468 | 2213.2614 | 2433.5413 | 2676.2825 | 2943.7938 | 3238.6172 | 3563.5488 |  | 1674.8581 | 1830.5977 | 2001.4524 | 2188.9399 | 2394.7335 | 2620.6784 | 2868.8092 | 3141.37 | 3440.8358 | 3769.937 | 4131.6857 | 4529.4051 | 4966.7622 | 5447.8034 | 5976.9946 | 6559.2645 | 7200.0536 | 7896.6786 | 8655.9546 | 9487.2973 | 10396.2543 | 11388.1784 | 12467.8821 | 13639.1189 | 14903.8122 | 16260.9226 | 17704.7939 | 19222.7499 | 20791.6183 | 22372.7124
| TRUE | 3719 | 22004153 | SA | Blank | 66 | TRANS TR NO.2 | DIFFERENTIAL | X | Reyrolle | DUOBIAS_959 | DUOBIAS 979 | DUOBIAS | Electronic |  | 0.066046 | 2190 |  | 6.6 | 0.014726 | 0.0025679 | 0.012158 | 157.3198 | 1129.892 | 1287.2118 | 56.3804 | 5.9176 | 227.4661 |  | 9.2475 | 0.035616 | 0.0062108 | 0.029405 | 380.492 | 2732.7441 | 3113.2361 | 136.3609 | 14.3122 | 550.147 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.041417 |  | 1576.9758 | 3814.0562 | 71.2511 | 3742.8051 |  | 0.033728 |  | 6.8264 | 7.0606 | 7.3028 | 7.5533 | 7.8124 | 8.0804 | 8.3576 | 8.6443 | 8.9408 | 9.2475 | 9.5647 | 9.8928 | 10.2322 | 10.5832 | 10.9462 | 11.3217 | 11.7101 | 12.1118 | 12.5273 | 12.957 | 13.4015 | 13.8612 | 14.3367 | 14.8285 | 15.3371 | 15.8633 | 16.4074 | 16.9703 | 17.5524 | 18.1545 |  | 0.016052 | 0.017506 | 0.019102 | 0.020853 | 0.022774 | 0.024884 | 0.027201 | 0.029747 | 0.032543 | 0.035616 | 0.038994 | 0.042708 | 0.046792 | 0.051284 | 0.056226 | 0.061663 | 0.067647 | 0.074234 | 0.081484 | 0.089468 | 0.09826 | 0.10794 | 0.11861 | 0.13036 | 0.14331 | 0.15758 | 0.17331 | 0.19065 | 0.20977 | 0.23085 |  | 0.0027992 | 0.0030528 | 0.003331 | 0.0036363 | 0.0039714 | 0.0043393 | 0.0047434 | 0.0051872 | 0.0056749 | 0.0062108 | 0.0067999 | 0.0074475 | 0.0081597 | 0.008943 | 0.0098047 | 0.010753 | 0.011796 | 0.012945 | 0.014209 | 0.015601 | 0.017135 | 0.018823 | 0.020683 | 0.022733 | 0.024991 | 0.02748 | 0.030222 | 0.033246 | 0.036579 | 0.040255 | 1718.9773 | 1874.7169 | 2045.5716 | 2233.0591 | 2438.8527 | 2664.7976 | 2912.9284 | 3185.4892 | 3484.955 | 3814.0562 | 4175.8049 | 4573.5243 | 5010.8814 | 5491.9226 | 6021.1138 | 6603.3837 | 7244.1728 | 7949.4865 | 8725.9546 | 9580.8968 | 10522.3946 | 11559.3718 | 12701.6825 | 13960.2092 | 15346.9702 | 16875.2399 | 18559.68 | 20416.4861 | 22463.5487 | 24720.6322 |  | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 52.8111 | 70.0043 | 93.6052 | 126.148 | 171.2039 | 233.8148 | 321.11 | 443.1852 | 614.3548 | 854.9384 | 1193.8092 | 1672.0328 | 2348.0635 |  | 171.486 | 187.0226 | 204.0672 | 222.771 | 243.3011 | 265.8414 | 290.5951 | 317.7859 | 347.6607 | 380.492 | 416.5802 | 456.2569 | 499.8878 | 547.8767 | 600.6691 | 658.7566 | 722.682 | 793.0444 | 870.5052 | 955.7946 | 1049.7189 | 1153.1682 | 1267.1257 | 1392.6769 | 1531.0208 | 1683.4817 | 1851.5222 | 2036.758 | 2240.9739 | 2466.1416 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 144.3541 | 159.8907 | 176.9353 | 195.6391 | 216.1692 | 238.7095 | 263.4632 | 290.6539 | 320.5288 | 353.3601 | 389.4483 | 429.125 | 472.7559 | 520.7448 | 573.5372 | 631.6247 | 695.5501 | 760.5692 | 827.4574 | 898.2339 | 972.1466 | 1047.8897 | 1123.3458 | 1195.2165 | 1258.4926 | 1305.696 | 1325.7942 | 1302.648 | 1212.7895 | 1022.2451 |  | 1231.635 | 1343.2213 | 1465.6375 | 1599.9709 | 1747.4206 | 1909.3085 | 2087.0924 | 2282.3803 | 2496.9454 | 2732.7441 | 2991.9344 | 3276.8976 | 3590.2608 | 3934.9234 | 4314.0851 | 4731.2774 | 5190.3982 | 5695.7504 | 6252.0843 | 6864.6443 | 7539.2207 | 8282.2075 | 9100.665 | 10002.3904 | 10995.9948 | 12090.9891 | 13297.8785 | 14628.2668 | 16094.9726 | 17712.1568 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 1231.4292 | 1343.0156 | 1465.4318 | 1599.7652 | 1747.2149 | 1909.1027 | 2086.8867 | 2282.1746 | 2496.7397 | 2732.5384 | 2991.7287 | 3276.6918 | 3590.0551 | 3934.7177 | 4313.8794 | 4731.0716 | 5190.1924 | 5695.5042 | 6251.7579 | 6864.2078 | 7538.6326 | 8281.4092 | 9099.5748 | 10000.8932 | 10993.9284 | 12088.1246 | 13293.8921 | 14622.7004 | 16087.1764 | 17701.2084 |  | 1375.7833 | 1502.9063 | 1642.367 | 1795.4043 | 1963.384 | 2147.8123 | 2350.3499 | 2572.8285 | 2817.2685 | 3085.8984 | 3381.177 | 3705.8168 | 4062.811 | 4455.4625 | 4887.4165 | 5362.6963 | 5885.7425 | 6456.0734 | 7079.2153 | 7762.4417 | 8510.7792 | 9329.2989 | 10222.9206 | 11196.1096 | 12252.4209 | 13393.8205 | 14619.6863 | 15925.3484 | 17299.9658 | 18723.4535 |  | 61.4572 | 67.0253 | 73.1337 | 79.8368 | 87.1944 | 95.2724 | 104.1436 | 113.8883 | 124.5948 | 136.3609 | 149.2942 | 163.5136 | 179.1501 | 196.3483 | 215.2681 | 236.0855 | 258.9952 | 284.2117 | 311.9721 | 342.5382 | 376.1988 | 413.273 | 454.1132 | 499.1083 | 548.688 | 603.327 | 663.5495 | 729.9344 | 803.1214 | 883.8171 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 46.7848 | 52.3528 | 58.4613 | 65.1643 | 72.5219 | 80.6 | 89.4712 | 99.2158 | 109.9224 | 121.6885 | 134.6218 | 148.8411 | 164.4776 | 181.6759 | 200.5957 | 221.4131 | 244.3227 | 266.6497 | 288.6927 | 311.4104 | 334.2491 | 356.3403 | 376.3596 | 392.3253 | 401.3098 | 399.0274 | 379.2454 | 332.9411 | 247.0981 | 102.9843 |  | 6.4504 | 7.0348 | 7.676 | 8.3795 | 9.1517 | 9.9996 | 10.9307 | 11.9535 | 13.0772 | 14.3122 | 15.6696 | 17.1621 | 18.8032 | 20.6083 | 22.5941 | 24.7791 | 27.1836 | 29.8303 | 32.744 | 35.9521 | 39.4851 | 43.3763 | 47.6628 | 52.3854 | 57.5892 | 63.324 | 69.6448 | 76.6125 | 84.294 | 92.7637 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 4.3827 | 4.9671 | 5.6083 | 6.3118 | 7.0841 | 7.9319 | 8.863 | 9.8858 | 11.0095 | 12.2445 | 13.6019 | 15.0944 | 16.7355 | 18.5406 | 20.5264 | 22.7114 | 25.1159 | 27.3554 | 29.4633 | 31.5655 | 33.5734 | 35.3531 | 36.7055 | 37.3372 | 36.8201 | 34.5333 | 29.5796 | 20.6667 | 5.9371 | -17.2742 |  | 247.9487 | 270.4129 | 295.0573 | 322.1009 | 351.7849 | 384.3757 | 420.1666 | 459.4813 | 502.6768 | 550.147 | 602.3264 | 659.6942 | 722.7795 | 792.1658 | 868.4974 | 952.4851 | 1044.9138 | 1146.6497 | 1258.649 | 1381.9675 | 1517.771 | 1667.3467 | 1832.1158 | 2013.6482 | 2213.6774 | 2434.118 | 2677.085 | 2944.9144 | 3240.1868 | 3565.7529 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 247.9073 | 270.3715 | 295.0159 | 322.0594 | 351.7435 | 384.3343 | 420.1251 | 459.4398 | 502.6354 | 550.1056 | 602.2849 | 659.6528 | 722.738 | 792.1244 | 868.456 | 952.4437 | 1044.8724 | 1146.6001 | 1258.5833 | 1381.8797 | 1517.6526 | 1667.186 | 1831.8964 | 2013.3468 | 2213.2614 | 2433.5413 | 2676.2825 | 2943.7938 | 3238.6172 | 3563.5488 |  | 1674.8581 | 1830.5977 | 2001.4524 | 2188.9399 | 2394.7335 | 2620.6784 | 2868.8092 | 3141.37 | 3440.8358 | 3769.937 | 4131.6857 | 4529.4051 | 4966.7622 | 5447.8034 | 5976.9946 | 6559.2645 | 7200.0536 | 7896.6786 | 8655.9546 | 9487.2973 | 10396.2543 | 11388.1784 | 12467.8821 | 13639.1189 | 14903.8122 | 16260.9226 | 17704.7939 | 19222.7499 | 20791.6183 | 22372.7124
| TRUE | 3720 | 22004154 | SA | Blank | 66 | TRANS TR NO.2 | DIFFERENTIAL | X | Reyrolle | DUOBIAS_959 | DUOBIAS 979 | DUOBIAS | Electronic |  | 0.066046 | 2190 |  | 6.6 | 0.014726 | 0.0025679 | 0.012158 | 157.3198 | 1129.892 | 1287.2118 | 56.3804 | 5.9176 | 227.4661 |  | 9.2475 | 0.035616 | 0.0062108 | 0.029405 | 380.492 | 2732.7441 | 3113.2361 | 136.3609 | 14.3122 | 550.147 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.041417 |  | 1576.9758 | 3814.0562 | 71.2511 | 3742.8051 |  | 0.033728 |  | 6.8264 | 7.0606 | 7.3028 | 7.5533 | 7.8124 | 8.0804 | 8.3576 | 8.6443 | 8.9408 | 9.2475 | 9.5647 | 9.8928 | 10.2322 | 10.5832 | 10.9462 | 11.3217 | 11.7101 | 12.1118 | 12.5273 | 12.957 | 13.4015 | 13.8612 | 14.3367 | 14.8285 | 15.3371 | 15.8633 | 16.4074 | 16.9703 | 17.5524 | 18.1545 |  | 0.016052 | 0.017506 | 0.019102 | 0.020853 | 0.022774 | 0.024884 | 0.027201 | 0.029747 | 0.032543 | 0.035616 | 0.038994 | 0.042708 | 0.046792 | 0.051284 | 0.056226 | 0.061663 | 0.067647 | 0.074234 | 0.081484 | 0.089468 | 0.09826 | 0.10794 | 0.11861 | 0.13036 | 0.14331 | 0.15758 | 0.17331 | 0.19065 | 0.20977 | 0.23085 |  | 0.0027992 | 0.0030528 | 0.003331 | 0.0036363 | 0.0039714 | 0.0043393 | 0.0047434 | 0.0051872 | 0.0056749 | 0.0062108 | 0.0067999 | 0.0074475 | 0.0081597 | 0.008943 | 0.0098047 | 0.010753 | 0.011796 | 0.012945 | 0.014209 | 0.015601 | 0.017135 | 0.018823 | 0.020683 | 0.022733 | 0.024991 | 0.02748 | 0.030222 | 0.033246 | 0.036579 | 0.040255 | 1718.9773 | 1874.7169 | 2045.5716 | 2233.0591 | 2438.8527 | 2664.7976 | 2912.9284 | 3185.4892 | 3484.955 | 3814.0562 | 4175.8049 | 4573.5243 | 5010.8814 | 5491.9226 | 6021.1138 | 6603.3837 | 7244.1728 | 7949.4865 | 8725.9546 | 9580.8968 | 10522.3946 | 11559.3718 | 12701.6825 | 13960.2092 | 15346.9702 | 16875.2399 | 18559.68 | 20416.4861 | 22463.5487 | 24720.6322 |  | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 52.8111 | 70.0043 | 93.6052 | 126.148 | 171.2039 | 233.8148 | 321.11 | 443.1852 | 614.3548 | 854.9384 | 1193.8092 | 1672.0328 | 2348.0635 |  | 171.486 | 187.0226 | 204.0672 | 222.771 | 243.3011 | 265.8414 | 290.5951 | 317.7859 | 347.6607 | 380.492 | 416.5802 | 456.2569 | 499.8878 | 547.8767 | 600.6691 | 658.7566 | 722.682 | 793.0444 | 870.5052 | 955.7946 | 1049.7189 | 1153.1682 | 1267.1257 | 1392.6769 | 1531.0208 | 1683.4817 | 1851.5222 | 2036.758 | 2240.9739 | 2466.1416 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 144.3541 | 159.8907 | 176.9353 | 195.6391 | 216.1692 | 238.7095 | 263.4632 | 290.6539 | 320.5288 | 353.3601 | 389.4483 | 429.125 | 472.7559 | 520.7448 | 573.5372 | 631.6247 | 695.5501 | 760.5692 | 827.4574 | 898.2339 | 972.1466 | 1047.8897 | 1123.3458 | 1195.2165 | 1258.4926 | 1305.696 | 1325.7942 | 1302.648 | 1212.7895 | 1022.2451 |  | 1231.635 | 1343.2213 | 1465.6375 | 1599.9709 | 1747.4206 | 1909.3085 | 2087.0924 | 2282.3803 | 2496.9454 | 2732.7441 | 2991.9344 | 3276.8976 | 3590.2608 | 3934.9234 | 4314.0851 | 4731.2774 | 5190.3982 | 5695.7504 | 6252.0843 | 6864.6443 | 7539.2207 | 8282.2075 | 9100.665 | 10002.3904 | 10995.9948 | 12090.9891 | 13297.8785 | 14628.2668 | 16094.9726 | 17712.1568 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 1231.4292 | 1343.0156 | 1465.4318 | 1599.7652 | 1747.2149 | 1909.1027 | 2086.8867 | 2282.1746 | 2496.7397 | 2732.5384 | 2991.7287 | 3276.6918 | 3590.0551 | 3934.7177 | 4313.8794 | 4731.0716 | 5190.1924 | 5695.5042 | 6251.7579 | 6864.2078 | 7538.6326 | 8281.4092 | 9099.5748 | 10000.8932 | 10993.9284 | 12088.1246 | 13293.8921 | 14622.7004 | 16087.1764 | 17701.2084 |  | 1375.7833 | 1502.9063 | 1642.367 | 1795.4043 | 1963.384 | 2147.8123 | 2350.3499 | 2572.8285 | 2817.2685 | 3085.8984 | 3381.177 | 3705.8168 | 4062.811 | 4455.4625 | 4887.4165 | 5362.6963 | 5885.7425 | 6456.0734 | 7079.2153 | 7762.4417 | 8510.7792 | 9329.2989 | 10222.9206 | 11196.1096 | 12252.4209 | 13393.8205 | 14619.6863 | 15925.3484 | 17299.9658 | 18723.4535 |  | 61.4572 | 67.0253 | 73.1337 | 79.8368 | 87.1944 | 95.2724 | 104.1436 | 113.8883 | 124.5948 | 136.3609 | 149.2942 | 163.5136 | 179.1501 | 196.3483 | 215.2681 | 236.0855 | 258.9952 | 284.2117 | 311.9721 | 342.5382 | 376.1988 | 413.273 | 454.1132 | 499.1083 | 548.688 | 603.327 | 663.5495 | 729.9344 | 803.1214 | 883.8171 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 46.7848 | 52.3528 | 58.4613 | 65.1643 | 72.5219 | 80.6 | 89.4712 | 99.2158 | 109.9224 | 121.6885 | 134.6218 | 148.8411 | 164.4776 | 181.6759 | 200.5957 | 221.4131 | 244.3227 | 266.6497 | 288.6927 | 311.4104 | 334.2491 | 356.3403 | 376.3596 | 392.3253 | 401.3098 | 399.0274 | 379.2454 | 332.9411 | 247.0981 | 102.9843 |  | 6.4504 | 7.0348 | 7.676 | 8.3795 | 9.1517 | 9.9996 | 10.9307 | 11.9535 | 13.0772 | 14.3122 | 15.6696 | 17.1621 | 18.8032 | 20.6083 | 22.5941 | 24.7791 | 27.1836 | 29.8303 | 32.744 | 35.9521 | 39.4851 | 43.3763 | 47.6628 | 52.3854 | 57.5892 | 63.324 | 69.6448 | 76.6125 | 84.294 | 92.7637 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 4.3827 | 4.9671 | 5.6083 | 6.3118 | 7.0841 | 7.9319 | 8.863 | 9.8858 | 11.0095 | 12.2445 | 13.6019 | 15.0944 | 16.7355 | 18.5406 | 20.5264 | 22.7114 | 25.1159 | 27.3554 | 29.4633 | 31.5655 | 33.5734 | 35.3531 | 36.7055 | 37.3372 | 36.8201 | 34.5333 | 29.5796 | 20.6667 | 5.9371 | -17.2742 |  | 247.9487 | 270.4129 | 295.0573 | 322.1009 | 351.7849 | 384.3757 | 420.1666 | 459.4813 | 502.6768 | 550.147 | 602.3264 | 659.6942 | 722.7795 | 792.1658 | 868.4974 | 952.4851 | 1044.9138 | 1146.6497 | 1258.649 | 1381.9675 | 1517.771 | 1667.3467 | 1832.1158 | 2013.6482 | 2213.6774 | 2434.118 | 2677.085 | 2944.9144 | 3240.1868 | 3565.7529 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 247.9073 | 270.3715 | 295.0159 | 322.0594 | 351.7435 | 384.3343 | 420.1251 | 459.4398 | 502.6354 | 550.1056 | 602.2849 | 659.6528 | 722.738 | 792.1244 | 868.456 | 952.4437 | 1044.8724 | 1146.6001 | 1258.5833 | 1381.8797 | 1517.6526 | 1667.186 | 1831.8964 | 2013.3468 | 2213.2614 | 2433.5413 | 2676.2825 | 2943.7938 | 3238.6172 | 3563.5488 |  | 1674.8581 | 1830.5977 | 2001.4524 | 2188.9399 | 2394.7335 | 2620.6784 | 2868.8092 | 3141.37 | 3440.8358 | 3769.937 | 4131.6857 | 4529.4051 | 4966.7622 | 5447.8034 | 5976.9946 | 6559.2645 | 7200.0536 | 7896.6786 | 8655.9546 | 9487.2973 | 10396.2543 | 11388.1784 | 12467.8821 | 13639.1189 | 14903.8122 | 16260.9226 | 17704.7939 | 19222.7499 | 20791.6183 | 22372.7124
| TRUE | 3721 | 22004159 | SA | Blank | 66 | TRANS TR NO.3 | OVERCURRENT | Blank | English Electric | CDG11_521 | CDG11 521 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 6.9092 | 0.0034055 | 0.00059385 | 0.0028116 | 22.7381 | 97.9849 | 120.723 | 13.0382 | 1.3685 | 52.6027 |  | 11.5623 | 0.013437 | 0.0023431 | 0.011094 | 89.7179 | 386.6195 | 476.3375 | 51.445 | 5.3996 | 207.5546 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 33.9149 | 0.077148 | 33.992 | 14.6724 | 2.0677 | 0.041417 |  | 187.7324 | 740.7366 | 50.7736 | 689.9631 |  | 0.05149 |  | 7.2742 | 7.6586 | 8.0633 | 8.4893 | 8.9379 | 9.4102 | 9.9074 | 10.4309 | 10.982 | 11.5623 | 12.1733 | 12.8165 | 13.4937 | 14.2067 | 14.9573 | 15.7477 | 16.5798 | 17.4558 | 18.3782 | 19.3492 | 20.3716 | 21.4481 | 22.5813 | 23.7745 | 25.0307 | 26.3533 | 27.7458 | 28 | 28 | 28 |  | 0.0038894 | 0.004447 | 0.00509 | 0.0058317 | 0.006688 | 0.0076769 | 0.0088197 | 0.010141 | 0.011669 | 0.013437 | 0.015484 | 0.017854 | 0.020601 | 0.023783 | 0.027473 | 0.031752 | 0.036717 | 0.042477 | 0.049164 | 0.056928 | 0.065944 | 0.076418 | 0.088588 | 0.10273 | 0.11917 | 0.13829 | 0.16052 | 0.16481 | 0.16481 | 0.16481 |  | 0.00067823 | 0.00077547 | 0.00088759 | 0.0010169 | 0.0011663 | 0.0013387 | 0.001538 | 0.0017684 | 0.0020348 | 0.0023431 | 0.0027001 | 0.0031134 | 0.0035923 | 0.0041473 | 0.0047908 | 0.005537 | 0.0064027 | 0.0074072 | 0.0085732 | 0.0099271 | 0.011499 | 0.013326 | 0.015448 | 0.017914 | 0.020781 | 0.024115 | 0.027991 | 0.02874 | 0.02874 | 0.02874 | 214.4089 | 245.1488 | 280.5926 | 321.4838 | 368.6862 | 423.2025 | 486.1983 | 559.0273 | 643.2636 | 740.7366 | 853.5736 | 984.2484 | 1135.6385 | 1311.091 | 1514.5008 | 1750.3999 | 2024.063 | 2341.6297 | 2710.2475 | 3138.2383 | 3635.2919 | 4212.693 | 4883.5845 | 5663.2749 | 6569.5976 | 7623.3281 | 8848.6725 | 9085.6624 | 9085.6624 | 9085.6624 |  | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 52.6548 | 69.7971 | 93.3281 | 125.7746 | 170.6971 | 233.1227 | 320.1595 | 441.8733 | 612.5363 | 852.4077 | 1190.2754 | 1667.0834 | 2341.1129 |  | 25.9692 | 29.6924 | 33.9853 | 38.9381 | 44.6552 | 51.2582 | 58.8883 | 67.7093 | 77.912 | 89.7179 | 103.3847 | 119.212 | 137.5483 | 158.7991 | 183.4361 | 212.0082 | 245.1542 | 283.6178 | 328.2647 | 380.1029 | 440.306 | 510.2407 | 591.499 | 685.9349 | 795.7086 | 923.3363 | 1071.7498 | 1100.454 | 1100.454 | 1100.454 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | -1.1627 | 2.5605 | 6.8534 | 11.8062 | 17.5233 | 24.1263 | 31.7563 | 40.5774 | 50.7801 | 62.586 | 76.2528 | 92.0801 | 110.4164 | 131.6672 | 156.3042 | 184.8762 | 218.0223 | 251.1426 | 285.217 | 322.5422 | 362.7337 | 404.9621 | 447.7191 | 488.4745 | 523.1804 | 545.5506 | 546.0218 | 366.3439 | 72.2695 | -343.4425 |  | 111.9084 | 127.9528 | 146.4523 | 167.795 | 192.4318 | 220.886 | 253.766 | 291.7783 | 335.7446 | 386.6195 | 445.5136 | 513.7179 | 592.7343 | 684.3099 | 790.4775 | 913.6025 | 1056.438 | 1222.1885 | 1414.5846 | 1637.9698 | 1897.4016 | 2198.7699 | 2548.9345 | 2955.8856 | 3428.931 | 3978.9143 | 4618.4697 | 4742.164 | 4742.164 | 4742.164 |  | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.092342 | 0.1224 | 0.16367 | 0.22057 | 0.29936 | 0.40883 | 0.56147 | 0.77492 | 1.0742 | 1.4949 | 2.0874 | 2.9236 | 4.1057 |  | 111.8313 | 127.8756 | 146.3751 | 167.7179 | 192.3546 | 220.8089 | 253.6888 | 291.7012 | 335.6674 | 386.5424 | 445.4365 | 513.6408 | 592.6572 | 684.2328 | 790.4003 | 913.5253 | 1056.3608 | 1222.0962 | 1414.4622 | 1637.8061 | 1897.181 | 2198.4706 | 2548.5257 | 2955.3241 | 3428.156 | 3977.8401 | 4616.9748 | 4740.0766 | 4739.2404 | 4738.0583 |  | 110.6686 | 130.4361 | 153.2285 | 179.524 | 209.8779 | 244.9352 | 285.4452 | 332.2786 | 386.4475 | 449.1284 | 521.6892 | 605.7209 | 703.0736 | 815.9 | 946.7045 | 1098.4016 | 1274.3831 | 1473.2388 | 1699.6792 | 1960.3483 | 2259.9147 | 2603.4327 | 2996.2448 | 3443.7987 | 3951.3364 | 4523.3906 | 5162.9966 | 5106.4205 | 4811.5099 | 4394.6158 |  | 14.891 | 17.0259 | 19.4875 | 22.3274 | 25.6057 | 29.3919 | 33.767 | 38.8251 | 44.6754 | 51.445 | 59.2817 | 68.3572 | 78.8714 | 91.0568 | 105.1839 | 121.5674 | 140.5736 | 162.629 | 188.2299 | 217.9544 | 252.4753 | 292.5765 | 339.1707 | 393.3212 | 456.2663 | 529.4492 | 614.5508 | 631.01 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0.21851 | 2.3534 | 4.815 | 7.655 | 10.9333 | 14.7195 | 19.0946 | 24.1527 | 30.003 | 36.7726 | 44.6093 | 53.6848 | 64.199 | 76.3844 | 90.5114 | 106.8949 | 125.9011 | 145.067 | 164.9504 | 186.8266 | 210.5257 | 235.6438 | 261.4172 | 286.5382 | 308.8881 | 325.1496 | 330.2467 | 234.0168 | 74.9867 | -149.8228 |  | 1.5629 | 1.787 | 2.0454 | 2.3434 | 2.6875 | 3.0849 | 3.5441 | 4.075 | 4.689 | 5.3996 | 6.2221 | 7.1746 | 8.2782 | 9.5571 | 11.0399 | 12.7595 | 14.7543 | 17.0692 | 19.7562 | 22.8761 | 26.4993 | 30.7083 | 35.5987 | 41.2822 | 47.8888 | 55.5699 | 64.502 | 66.2296 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | -0.50477 | -0.28069 | -0.022328 | 0.27575 | 0.61983 | 1.0172 | 1.4764 | 2.0073 | 2.6213 | 3.3319 | 4.1544 | 5.1069 | 6.2105 | 7.4894 | 8.9722 | 10.6918 | 12.6866 | 14.5943 | 16.4756 | 18.4894 | 20.5876 | 22.6851 | 24.6414 | 26.2339 | 27.1197 | 26.7793 | 24.4368 | 10.2838 | -12.1274 | -43.8084 |  | 60.0774 | 68.6908 | 78.6221 | 90.0798 | 103.306 | 118.5815 | 136.2329 | 156.6396 | 180.2426 | 207.5546 | 239.1715 | 275.7867 | 318.2062 | 367.368 | 424.3635 | 490.4625 | 567.1429 | 656.1252 | 759.412 | 879.3351 | 1018.6097 | 1180.3976 | 1368.3816 | 1586.851 | 1840.8028 | 2136.0584 | 2479.4002 | 2545.8048 | 2545.8048 | 2545.8048 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 60.036 | 68.6493 | 78.5807 | 90.0384 | 103.2645 | 118.54 | 136.1915 | 156.5982 | 180.2012 | 207.5132 | 239.1301 | 275.7452 | 318.1648 | 367.3266 | 424.3221 | 490.4211 | 567.1015 | 656.0756 | 759.3463 | 879.2473 | 1018.4913 | 1180.2369 | 1368.1621 | 1586.5496 | 1840.3868 | 2135.4817 | 2478.5977 | 2544.6842 | 2544.2353 | 2543.6007 |  | 170.4183 | 201.1582 | 236.6019 | 277.4932 | 324.6955 | 379.2119 | 442.2076 | 515.0367 | 599.273 | 696.746 | 809.583 | 940.2578 | 1091.6478 | 1267.1004 | 1470.5102 | 1706.4093 | 1980.0724 | 2288.9757 | 2640.4515 | 3044.9116 | 3509.5192 | 4041.9985 | 4650.4654 | 5343.1204 | 6127.731 | 7010.8012 | 7996.2779 | 7895.4053 | 7418.6046 | 6744.5854
| TRUE | 3722 | 22004160 | SA | Blank | 66 | TRANS TR NO.3 | OVERCURRENT | Blank | English Electric | CDG11_521 | CDG11 521 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 675.3447 | 769.3759 | 33.699 | 3.537 | 135.9582 |  | 14.6263 | 0.025802 | 0.0044993 | 0.021302 | 275.6434 | 1979.7072 | 2255.3506 | 98.7852 | 10.3683 | 398.5481 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.041417 |  | 942.57 | 2763.0522 | 71.2511 | 2691.8011 |  | 0.039029 |  | 10.294 | 10.7037 | 11.1297 | 11.5727 | 12.0333 | 12.5122 | 13.0102 | 13.528 | 14.0664 | 14.6263 | 15.2084 | 15.8137 | 16.4431 | 17.0975 | 17.778 | 18.4856 | 19.2213 | 19.9863 | 20.7818 | 21.6089 | 22.4689 | 23.3632 | 24.2931 | 25.2599 | 26.2653 | 27.3106 | 28 | 28 | 28 | 28 |  | 0.0097834 | 0.010879 | 0.012103 | 0.01347 | 0.014998 | 0.016705 | 0.018613 | 0.020747 | 0.023133 | 0.025802 | 0.028788 | 0.032129 | 0.035868 | 0.040053 | 0.044739 | 0.049986 | 0.055861 | 0.062442 | 0.069814 | 0.078073 | 0.087327 | 0.097698 | 0.10932 | 0.12235 | 0.13696 | 0.15333 | 0.16481 | 0.16481 | 0.16481 | 0.16481 |  | 0.001706 | 0.0018971 | 0.0021105 | 0.0023489 | 0.0026153 | 0.002913 | 0.0032458 | 0.0036178 | 0.0040339 | 0.0044993 | 0.00502 | 0.0056026 | 0.0062547 | 0.0069845 | 0.0078016 | 0.0087165 | 0.0097411 | 0.010889 | 0.012174 | 0.013614 | 0.015228 | 0.017037 | 0.019064 | 0.021335 | 0.023882 | 0.026738 | 0.02874 | 0.02874 | 0.02874 | 0.02874 | 1047.6755 | 1165.0265 | 1296.0833 | 1442.483 | 1606.0609 | 1788.8749 | 1993.2322 | 2221.7206 | 2477.2423 | 2763.0522 | 3082.8019 | 3440.5875 | 3841.0048 | 4289.2099 | 4790.9887 | 5352.8339 | 5982.0316 | 6686.7594 | 7476.1956 | 8360.6424 | 9351.6643 | 10462.2435 | 11706.9543 | 13102.1593 | 14666.2299 | 16419.7939 | 17649.5414 | 17649.5414 | 17649.5414 | 17649.5414 |  | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 52.8111 | 70.0043 | 93.6052 | 126.148 | 171.2039 | 233.8148 | 321.11 | 443.1852 | 614.3548 | 854.9384 | 1193.8092 | 1672.0328 | 2348.0635 |  | 104.5166 | 116.2236 | 129.2979 | 143.9028 | 160.2214 | 178.459 | 198.8458 | 221.6399 | 247.1308 | 275.6434 | 307.5417 | 343.2346 | 383.1804 | 427.8935 | 477.9512 | 534.0012 | 596.7702 | 667.0742 | 745.8287 | 834.0615 | 932.9263 | 1043.7182 | 1167.8911 | 1307.0774 | 1463.1098 | 1638.0462 | 1760.7263 | 1760.7263 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 77.3847 | 89.0917 | 102.166 | 116.7709 | 133.0895 | 151.3271 | 171.7139 | 194.508 | 219.9989 | 248.5114 | 280.4098 | 316.1027 | 356.0485 | 400.7616 | 450.8193 | 506.8692 | 569.6383 | 634.599 | 702.7809 | 776.5008 | 855.354 | 938.4397 | 1024.1112 | 1109.617 | 1190.5816 | 1260.2605 | 1234.9984 | 1026.6163 | 732.5419 | 316.8298 |  | 750.652 | 834.7332 | 928.6344 | 1033.5288 | 1150.7312 | 1281.7161 | 1428.1367 | 1591.847 | 1774.9264 | 1979.7072 | 2208.8056 | 2465.1565 | 2752.0526 | 3073.1883 | 3432.7093 | 3835.2673 | 4286.083 | 4791.0154 | 5356.6409 | 5990.3407 | 6700.4009 | 7496.123 | 8387.9493 | 9387.6038 | 10508.2493 | 11764.6654 | 12645.7707 | 12645.7707 | 12645.7707 | 12645.7707 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 750.4463 | 834.5274 | 928.4287 | 1033.3231 | 1150.5255 | 1281.5104 | 1427.931 | 1591.6413 | 1774.7207 | 1979.5015 | 2208.5999 | 2464.9507 | 2751.8468 | 3072.9826 | 3432.5036 | 3835.0616 | 4285.8773 | 4790.7692 | 5356.3144 | 5989.9042 | 6699.8127 | 7495.3247 | 8386.8591 | 9386.1065 | 10506.1828 | 11761.8008 | 12641.7843 | 12640.2043 | 12637.9744 | 12634.8223 |  | 827.831 | 923.6191 | 1030.5947 | 1150.0939 | 1283.615 | 1432.8374 | 1599.6448 | 1786.1492 | 1994.7196 | 2228.0129 | 2489.0097 | 2781.0534 | 3107.8953 | 3473.7442 | 3883.3229 | 4341.9308 | 4855.5156 | 5425.3682 | 6059.0953 | 6766.405 | 7555.1667 | 8433.7643 | 9410.9703 | 10495.7235 | 11696.7644 | 13022.0612 | 13876.7827 | 13666.8206 | 13370.5163 | 12951.6521 |  | 37.4567 | 41.6523 | 46.3378 | 51.5719 | 57.4202 | 63.9562 | 71.2624 | 79.4314 | 88.5669 | 98.7852 | 110.217 | 123.0086 | 137.3244 | 153.3487 | 171.2884 | 191.3756 | 213.8708 | 239.0664 | 267.2905 | 298.9114 | 334.3426 | 374.0483 | 418.5494 | 468.4311 | 524.3501 | 587.0438 | 631.01 | 631.01 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.7843 | 26.9798 | 31.6654 | 36.8995 | 42.7478 | 49.2838 | 56.59 | 64.759 | 73.8944 | 84.1128 | 95.5445 | 108.3362 | 122.652 | 138.6763 | 156.616 | 176.7032 | 199.1984 | 221.5044 | 244.011 | 267.7836 | 292.3929 | 317.1156 | 340.7959 | 361.6481 | 376.9718 | 382.7443 | 346.706 | 234.0168 | 74.9867 | -149.8228 |  | 3.9314 | 4.3717 | 4.8635 | 5.4129 | 6.0267 | 6.7127 | 7.4796 | 8.337 | 9.2958 | 10.3683 | 11.5682 | 12.9107 | 14.4133 | 16.0952 | 17.9781 | 20.0864 | 22.4475 | 25.0919 | 28.0543 | 31.3731 | 35.0919 | 39.2594 | 43.9301 | 49.1656 | 55.0347 | 61.615 | 66.2296 | 66.2296 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8637 | 2.304 | 2.7958 | 3.3452 | 3.959 | 4.645 | 5.4119 | 6.2693 | 7.2281 | 8.3006 | 9.5005 | 10.843 | 12.3456 | 14.0275 | 15.9104 | 18.0187 | 20.3798 | 22.617 | 24.7736 | 26.9865 | 29.1802 | 31.2362 | 32.9728 | 34.1173 | 34.2656 | 32.8243 | 26.1644 | 10.2838 | -12.1274 | -43.8084 |  | 151.1188 | 168.0457 | 186.9496 | 208.0666 | 231.6614 | 258.0309 | 287.5078 | 320.4654 | 357.3223 | 398.5481 | 444.6695 | 496.2772 | 554.0341 | 618.6841 | 691.0617 | 772.1034 | 862.8601 | 964.5114 | 1078.3813 | 1205.9556 | 1348.9026 | 1509.0947 | 1688.6343 | 1889.8814 | 2115.4861 | 2368.4236 | 2545.8048 | 2545.8048 | 2545.8048 | 2545.8048 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 151.0774 | 168.0043 | 186.9082 | 208.0252 | 231.62 | 257.9894 | 287.4663 | 320.424 | 357.2809 | 398.5067 | 444.628 | 496.2357 | 553.9927 | 618.6427 | 691.0203 | 772.0619 | 862.8187 | 964.4618 | 1078.3155 | 1205.8678 | 1348.7842 | 1508.934 | 1688.4148 | 1889.58 | 2115.07 | 2367.8469 | 2545.0023 | 2544.6842 | 2544.2353 | 2543.6007 |  | 1003.5563 | 1120.9073 | 1251.9641 | 1398.3638 | 1561.9417 | 1744.7557 | 1949.113 | 2177.6015 | 2433.1231 | 2718.933 | 3038.6827 | 3396.4683 | 3796.8856 | 4245.0907 | 4746.8695 | 5308.7147 | 5937.9124 | 6633.9515 | 7406.1956 | 8267.0429 | 9225.524 | 10291.0501 | 11473.1538 | 12781.069 | 14223.0719 | 15805.4767 | 16794.6553 | 16455.8053 | 15977.611 | 15301.6217
| TRUE | 3723 | 22004161 | SA | Blank | 66 | TRANS TR NO.3 | OVERCURRENT | Blank | English Electric | CDG11_521 | CDG11 521 | CDG11 | Electromechanical |  | 0.066046 | 2190 |  | 9.9 | 0.0088019 | 0.0015349 | 0.007267 | 94.0312 | 675.3447 | 769.3759 | 33.699 | 3.537 | 135.9582 |  | 14.6263 | 0.025802 | 0.0044993 | 0.021302 | 275.6434 | 1979.7072 | 2255.3506 | 98.7852 | 10.3683 | 398.5481 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.041417 |  | 942.57 | 2763.0522 | 71.2511 | 2691.8011 |  | 0.039029 |  | 10.294 | 10.7037 | 11.1297 | 11.5727 | 12.0333 | 12.5122 | 13.0102 | 13.528 | 14.0664 | 14.6263 | 15.2084 | 15.8137 | 16.4431 | 17.0975 | 17.778 | 18.4856 | 19.2213 | 19.9863 | 20.7818 | 21.6089 | 22.4689 | 23.3632 | 24.2931 | 25.2599 | 26.2653 | 27.3106 | 28 | 28 | 28 | 28 |  | 0.0097834 | 0.010879 | 0.012103 | 0.01347 | 0.014998 | 0.016705 | 0.018613 | 0.020747 | 0.023133 | 0.025802 | 0.028788 | 0.032129 | 0.035868 | 0.040053 | 0.044739 | 0.049986 | 0.055861 | 0.062442 | 0.069814 | 0.078073 | 0.087327 | 0.097698 | 0.10932 | 0.12235 | 0.13696 | 0.15333 | 0.16481 | 0.16481 | 0.16481 | 0.16481 |  | 0.001706 | 0.0018971 | 0.0021105 | 0.0023489 | 0.0026153 | 0.002913 | 0.0032458 | 0.0036178 | 0.0040339 | 0.0044993 | 0.00502 | 0.0056026 | 0.0062547 | 0.0069845 | 0.0078016 | 0.0087165 | 0.0097411 | 0.010889 | 0.012174 | 0.013614 | 0.015228 | 0.017037 | 0.019064 | 0.021335 | 0.023882 | 0.026738 | 0.02874 | 0.02874 | 0.02874 | 0.02874 | 1047.6755 | 1165.0265 | 1296.0833 | 1442.483 | 1606.0609 | 1788.8749 | 1993.2322 | 2221.7206 | 2477.2423 | 2763.0522 | 3082.8019 | 3440.5875 | 3841.0048 | 4289.2099 | 4790.9887 | 5352.8339 | 5982.0316 | 6686.7594 | 7476.1956 | 8360.6424 | 9351.6643 | 10462.2435 | 11706.9543 | 13102.1593 | 14666.2299 | 16419.7939 | 17649.5414 | 17649.5414 | 17649.5414 | 17649.5414 |  | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 44.1219 | 52.8111 | 70.0043 | 93.6052 | 126.148 | 171.2039 | 233.8148 | 321.11 | 443.1852 | 614.3548 | 854.9384 | 1193.8092 | 1672.0328 | 2348.0635 |  | 104.5166 | 116.2236 | 129.2979 | 143.9028 | 160.2214 | 178.459 | 198.8458 | 221.6399 | 247.1308 | 275.6434 | 307.5417 | 343.2346 | 383.1804 | 427.8935 | 477.9512 | 534.0012 | 596.7702 | 667.0742 | 745.8287 | 834.0615 | 932.9263 | 1043.7182 | 1167.8911 | 1307.0774 | 1463.1098 | 1638.0462 | 1760.7263 | 1760.7263 | 1760.7263 | 1760.7263 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 77.3847 | 89.0917 | 102.166 | 116.7709 | 133.0895 | 151.3271 | 171.7139 | 194.508 | 219.9989 | 248.5114 | 280.4098 | 316.1027 | 356.0485 | 400.7616 | 450.8193 | 506.8692 | 569.6383 | 634.599 | 702.7809 | 776.5008 | 855.354 | 938.4397 | 1024.1112 | 1109.617 | 1190.5816 | 1260.2605 | 1234.9984 | 1026.6163 | 732.5419 | 316.8298 |  | 750.652 | 834.7332 | 928.6344 | 1033.5288 | 1150.7312 | 1281.7161 | 1428.1367 | 1591.847 | 1774.9264 | 1979.7072 | 2208.8056 | 2465.1565 | 2752.0526 | 3073.1883 | 3432.7093 | 3835.2673 | 4286.083 | 4791.0154 | 5356.6409 | 5990.3407 | 6700.4009 | 7496.123 | 8387.9493 | 9387.6038 | 10508.2493 | 11764.6654 | 12645.7707 | 12645.7707 | 12645.7707 | 12645.7707 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 750.4463 | 834.5274 | 928.4287 | 1033.3231 | 1150.5255 | 1281.5104 | 1427.931 | 1591.6413 | 1774.7207 | 1979.5015 | 2208.5999 | 2464.9507 | 2751.8468 | 3072.9826 | 3432.5036 | 3835.0616 | 4285.8773 | 4790.7692 | 5356.3144 | 5989.9042 | 6699.8127 | 7495.3247 | 8386.8591 | 9386.1065 | 10506.1828 | 11761.8008 | 12641.7843 | 12640.2043 | 12637.9744 | 12634.8223 |  | 827.831 | 923.6191 | 1030.5947 | 1150.0939 | 1283.615 | 1432.8374 | 1599.6448 | 1786.1492 | 1994.7196 | 2228.0129 | 2489.0097 | 2781.0534 | 3107.8953 | 3473.7442 | 3883.3229 | 4341.9308 | 4855.5156 | 5425.3682 | 6059.0953 | 6766.405 | 7555.1667 | 8433.7643 | 9410.9703 | 10495.7235 | 11696.7644 | 13022.0612 | 13876.7827 | 13666.8206 | 13370.5163 | 12951.6521 |  | 37.4567 | 41.6523 | 46.3378 | 51.5719 | 57.4202 | 63.9562 | 71.2624 | 79.4314 | 88.5669 | 98.7852 | 110.217 | 123.0086 | 137.3244 | 153.3487 | 171.2884 | 191.3756 | 213.8708 | 239.0664 | 267.2905 | 298.9114 | 334.3426 | 374.0483 | 418.5494 | 468.4311 | 524.3501 | 587.0438 | 631.01 | 631.01 | 631.01 | 631.01 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 22.7843 | 26.9798 | 31.6654 | 36.8995 | 42.7478 | 49.2838 | 56.59 | 64.759 | 73.8944 | 84.1128 | 95.5445 | 108.3362 | 122.652 | 138.6763 | 156.616 | 176.7032 | 199.1984 | 221.5044 | 244.011 | 267.7836 | 292.3929 | 317.1156 | 340.7959 | 361.6481 | 376.9718 | 382.7443 | 346.706 | 234.0168 | 74.9867 | -149.8228 |  | 3.9314 | 4.3717 | 4.8635 | 5.4129 | 6.0267 | 6.7127 | 7.4796 | 8.337 | 9.2958 | 10.3683 | 11.5682 | 12.9107 | 14.4133 | 16.0952 | 17.9781 | 20.0864 | 22.4475 | 25.0919 | 28.0543 | 31.3731 | 35.0919 | 39.2594 | 43.9301 | 49.1656 | 55.0347 | 61.615 | 66.2296 | 66.2296 | 66.2296 | 66.2296 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 1.8637 | 2.304 | 2.7958 | 3.3452 | 3.959 | 4.645 | 5.4119 | 6.2693 | 7.2281 | 8.3006 | 9.5005 | 10.843 | 12.3456 | 14.0275 | 15.9104 | 18.0187 | 20.3798 | 22.617 | 24.7736 | 26.9865 | 29.1802 | 31.2362 | 32.9728 | 34.1173 | 34.2656 | 32.8243 | 26.1644 | 10.2838 | -12.1274 | -43.8084 |  | 151.1188 | 168.0457 | 186.9496 | 208.0666 | 231.6614 | 258.0309 | 287.5078 | 320.4654 | 357.3223 | 398.5481 | 444.6695 | 496.2772 | 554.0341 | 618.6841 | 691.0617 | 772.1034 | 862.8601 | 964.5114 | 1078.3813 | 1205.9556 | 1348.9026 | 1509.0947 | 1688.6343 | 1889.8814 | 2115.4861 | 2368.4236 | 2545.8048 | 2545.8048 | 2545.8048 | 2545.8048 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 151.0774 | 168.0043 | 186.9082 | 208.0252 | 231.62 | 257.9894 | 287.4663 | 320.424 | 357.2809 | 398.5067 | 444.628 | 496.2357 | 553.9927 | 618.6427 | 691.0203 | 772.0619 | 862.8187 | 964.4618 | 1078.3155 | 1205.8678 | 1348.7842 | 1508.934 | 1688.4148 | 1889.58 | 2115.07 | 2367.8469 | 2545.0023 | 2544.6842 | 2544.2353 | 2543.6007 |  | 1003.5563 | 1120.9073 | 1251.9641 | 1398.3638 | 1561.9417 | 1744.7557 | 1949.113 | 2177.6015 | 2433.1231 | 2718.933 | 3038.6827 | 3396.4683 | 3796.8856 | 4245.0907 | 4746.8695 | 5308.7147 | 5937.9124 | 6633.9515 | 7406.1956 | 8267.0429 | 9225.524 | 10291.0501 | 11473.1538 | 12781.069 | 14223.0719 | 15805.4767 | 16794.6553 | 16455.8053 | 15977.611 | 15301.6217
| TRUE | 3724 | 22004158 | SA | Blank | 66 | TRANS TR NO.3 | DIFFERENTIAL | X | Brown Boveri | D202_3102 | D202 3102 | D202 | Electromechanical |  | 0.066046 | 2190 |  | 3.8384 | 0.00090442 | 0.00015771 | 0.00074671 | 6.0388 | 26.0228 | 32.0615 | 3.4627 | 0.36344 | 13.9702 |  | 6.1709 | 0.0025548 | 0.0004455 | 0.0021093 | 17.058 | 73.5077 | 90.5657 | 9.7812 | 1.0266 | 39.4622 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 33.9149 | 0.077148 | 33.992 | 14.6724 | 2.0677 | 0.041417 |  | 49.8578 | 140.8357 | 50.7736 | 90.0621 |  | 0.047478 |  | 4.0251 | 4.2208 | 4.426 | 4.6412 | 4.8669 | 5.1035 | 5.3517 | 5.6119 | 5.8848 | 6.1709 | 6.4709 | 6.7856 | 7.1155 | 7.4615 | 7.8243 | 8.2047 | 8.6037 | 9.022 | 9.4607 | 9.9207 | 10.4031 | 10.9089 | 11.4394 | 11.9956 | 12.5788 | 13.1905 | 13.8318 | 14.5044 | 15.2096 | 15.9492 |  | 0.00091728 | 0.0010221 | 0.0011406 | 0.0012748 | 0.0014268 | 0.001599 | 0.0017945 | 0.0020163 | 0.0022683 | 0.0025548 | 0.0028806 | 0.0032514 | 0.0036736 | 0.0041547 | 0.0047032 | 0.0053287 | 0.0060425 | 0.0068574 | 0.0077882 | 0.0088517 | 0.010067 | 0.011458 | 0.013048 | 0.014868 | 0.016952 | 0.019338 | 0.022072 | 0.025204 | 0.028794 | 0.03291 |  | 0.00015996 | 0.00017823 | 0.0001989 | 0.0002223 | 0.0002488 | 0.00027884 | 0.00031292 | 0.0003516 | 0.00039555 | 0.0004455 | 0.00050232 | 0.00056698 | 0.00064061 | 0.00072451 | 0.00082014 | 0.00092923 | 0.0010537 | 0.0011958 | 0.0013581 | 0.0015436 | 0.0017556 | 0.001998 | 0.0022754 | 0.0025928 | 0.0029561 | 0.0033722 | 0.0038489 | 0.0043951 | 0.0050211 | 0.0057389 | 50.5668 | 56.345 | 62.8795 | 70.2756 | 78.6532 | 88.1499 | 98.9229 | 111.1523 | 125.0445 | 140.8357 | 158.7968 | 179.238 | 202.5154 | 229.0371 | 259.2711 | 293.7549 | 333.1048 | 378.0284 | 429.3384 | 487.9675 | 554.9874 | 631.629 | 719.3065 | 819.645 | 934.5123 | 1066.0553 | 1216.7422 | 1389.4107 | 1587.3241 | 1814.2355 |  | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 43.9913 | 52.6548 | 69.7971 | 93.3281 | 125.7746 | 170.6971 | 233.1227 | 320.1595 | 441.8733 | 612.5363 | 852.4077 | 1190.2754 | 1667.0834 | 2341.1129 |  | 6.1246 | 6.8245 | 7.616 | 8.5118 | 9.5265 | 10.6767 | 11.9815 | 13.4628 | 15.1454 | 17.058 | 19.2334 | 21.7093 | 24.5286 | 27.7409 | 31.4029 | 35.5795 | 40.3456 | 45.7867 | 52.0014 | 59.1025 | 67.22 | 76.5028 | 87.1223 | 99.2753 | 113.188 | 129.1205 | 147.3716 | 168.2852 | 192.2564 | 219.7399 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | -21.0073 | -20.3074 | -19.516 | -18.6201 | -17.6054 | -16.4552 | -15.1504 | -13.6692 | -11.9865 | -10.0739 | -7.8985 | -5.4226 | -2.6033 | 0.60902 | 4.271 | 8.4476 | 13.2137 | 13.3115 | 8.9536 | 1.5418 | -10.3523 | -28.7758 | -56.6576 | -98.1851 | -159.3402 | -248.6652 | -378.3563 | -565.8248 | -835.928 | -1224.1566 |  | 26.3928 | 29.4086 | 32.8193 | 36.6796 | 41.0522 | 46.0089 | 51.6317 | 58.0148 | 65.2656 | 73.5077 | 82.8823 | 93.5514 | 105.7007 | 119.5434 | 135.3238 | 153.3222 | 173.8605 | 197.3079 | 224.0886 | 254.6894 | 289.6697 | 329.672 | 375.4343 | 427.8049 | 487.7587 | 556.4162 | 635.0655 | 725.188 | 828.4868 | 946.9208 |  | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.077148 | 0.092342 | 0.1224 | 0.16367 | 0.22057 | 0.29936 | 0.40883 | 0.56147 | 0.77492 | 1.0742 | 1.4949 | 2.0874 | 2.9236 | 4.1057 |  | 26.3157 | 29.3315 | 32.7421 | 36.6024 | 40.975 | 45.9317 | 51.5546 | 57.9376 | 65.1885 | 73.4306 | 82.8051 | 93.4742 | 105.6236 | 119.4663 | 135.2466 | 153.2451 | 173.7833 | 197.2155 | 223.9662 | 254.5257 | 289.4492 | 329.3726 | 375.0255 | 427.2435 | 486.9838 | 555.3419 | 633.5706 | 723.1006 | 825.5632 | 942.8151 |  | 5.3084 | 9.0241 | 13.2262 | 17.9823 | 23.3696 | 29.4765 | 36.4042 | 44.2685 | 53.202 | 63.3566 | 74.9067 | 88.0516 | 103.0203 | 120.0753 | 139.5176 | 161.6927 | 186.997 | 210.5271 | 232.9198 | 256.0676 | 279.0968 | 300.5969 | 318.3679 | 329.0583 | 327.6435 | 306.6767 | 255.2143 | 157.2758 | -10.3648 | -281.3415 |  | 3.5119 | 3.9132 | 4.3671 | 4.8807 | 5.4626 | 6.1221 | 6.8703 | 7.7197 | 8.6845 | 9.7812 | 11.0286 | 12.4483 | 14.0649 | 15.9069 | 18.0067 | 20.4016 | 23.1345 | 26.2545 | 29.8181 | 33.8899 | 38.5445 | 43.8674 | 49.9567 | 56.9253 | 64.903 | 74.0388 | 84.5042 | 96.4962 | 110.2415 | 126.0008 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | -11.1605 | -10.7592 | -10.3054 | -9.7917 | -9.2099 | -8.5503 | -7.8021 | -6.9528 | -5.9879 | -4.8912 | -3.6438 | -2.2241 | -0.6075 | 1.2345 | 3.3342 | 5.7292 | 8.4621 | 8.6925 | 6.5386 | 2.7621 | -3.4051 | -13.0653 | -27.7969 | -49.8577 | -82.4753 | -130.2608 | -199.7999 | -300.4971 | -445.7818 | -654.832 |  | 0.3686 | 0.41072 | 0.45836 | 0.51227 | 0.57334 | 0.64256 | 0.72109 | 0.81024 | 0.91151 | 1.0266 | 1.1575 | 1.3065 | 1.4762 | 1.6696 | 1.8899 | 2.1413 | 2.4282 | 2.7556 | 3.1296 | 3.557 | 4.0456 | 4.6042 | 5.2434 | 5.9748 | 6.8121 | 7.771 | 8.8694 | 10.1281 | 11.5707 | 13.2248 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | -1.6991 | -1.657 | -1.6093 | -1.5554 | -1.4944 | -1.4251 | -1.3466 | -1.2575 | -1.1562 | -1.0411 | -0.91015 | -0.76115 | -0.59147 | -0.39814 | -0.17775 | 0.073618 | 0.36046 | 0.28072 | -0.15099 | -0.82963 | -1.8662 | -3.4189 | -5.714 | -9.0735 | -13.957 | -21.0197 | -31.1958 | -45.8177 | -66.7862 | -96.8131 |  | 14.1688 | 15.7879 | 17.6189 | 19.6912 | 22.0386 | 24.6996 | 27.7182 | 31.1449 | 35.0375 | 39.4622 | 44.4949 | 50.2225 | 56.7449 | 64.1762 | 72.6478 | 82.3102 | 93.336 | 105.9237 | 120.3007 | 136.7286 | 155.5076 | 176.9826 | 201.5499 | 229.6647 | 261.8506 | 298.709 | 340.9315 | 389.3132 | 444.7686 | 508.3492 |  | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.041417 | 0.049573 | 0.065712 | 0.087866 | 0.11841 | 0.16071 | 0.21948 | 0.30142 | 0.41601 | 0.57669 | 0.80252 | 1.1206 | 1.5695 | 2.2041 |  | 14.1274 | 15.7465 | 17.5774 | 19.6498 | 21.9972 | 24.6582 | 27.6768 | 31.1035 | 34.9961 | 39.4208 | 44.4535 | 50.1811 | 56.7035 | 64.1348 | 72.6064 | 82.2688 | 93.2946 | 105.8741 | 120.235 | 136.6408 | 155.3892 | 176.8219 | 201.3304 | 229.3633 | 261.4346 | 298.1323 | 340.1289 | 388.1926 | 443.1991 | 506.1451 |  | 6.5762 | 12.3544 | 18.8889 | 26.285 | 34.6626 | 44.1593 | 54.9323 | 67.1617 | 81.0539 | 96.8451 | 114.8062 | 135.2474 | 158.5248 | 185.0464 | 215.2805 | 249.7643 | 289.1142 | 325.3744 | 359.5424 | 394.6408 | 429.2147 | 460.9345 | 486.1874 | 499.4905 | 492.6458 | 453.5285 | 364.3476 | 199.1536 | -79.7337 | -526.8415
| FALSE | 3797 | 22011635 | SHL | Blank | 22 | BUS ALL | POWER QUALITY | I | Schneider | ION_7650 | ION 7650 | ION 7000s | Digital |  | 0.033587 | 1 |  | 2.5292 | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.25924 |  | 8.8804 | 0.037562 | 1.7282e-06 | 0.037561 | 103.2973 | 0.12098 | 103.4183 | 106.6353 | 15.0288 | 1.8843 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.25924 |  | 31.2266 | 226.9666 | 31.2266 | 195.74 |  | 0.12559 |  | 2.8677 | 3.2514 | 3.6865 | 4.1799 | 4.7392 | 5.3734 | 6.0925 | 6.9078 | 7.8322 | 8.8804 | 10.0687 | 11.4161 | 12.9438 | 14.676 | 16.64 | 18.8667 | 21.3915 | 24.2541 | 27.4998 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0057115 | 0.0076532 | 0.010356 | 0.014137 | 0.019449 | 0.026946 | 0.037562 | 0.052647 | 0.074144 | 0.10486 | 0.14884 | 0.21196 | 0.3027 | 0.43337 | 0.62179 | 0.89383 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.3778e-07 | 2.3778e-07 | 2.3778e-07 | 2.6278e-07 | 3.5213e-07 | 4.7647e-07 | 6.5042e-07 | 8.9486e-07 | 1.2398e-06 | 1.7282e-06 | 2.4223e-06 | 3.4114e-06 | 4.8245e-06 | 6.8482e-06 | 9.7523e-06 | 1.3927e-05 | 1.9939e-05 | 2.8608e-05 | 4.1125e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 31.2266 | 31.2266 | 31.2266 | 34.5108 | 46.2437 | 62.5742 | 85.4184 | 117.5204 | 162.8169 | 226.9666 | 318.1154 | 448.0063 | 633.5899 | 899.3599 | 1280.7463 | 1829.0423 | 2618.5657 | 3757.0689 | 5400.8767 | 5690.4675 | 5690.4675 | 5690.4675 | 5690.4675 | 5690.4675 | 5690.4675 | 5690.4675 | 5690.4675 | 5690.4675 | 5690.4675 | 5690.4675 |  | 31.2266 | 31.2266 | 31.2266 | 31.2266 | 31.2266 | 31.2266 | 31.2266 | 31.2266 | 31.2266 | 31.2266 | 31.2266 | 31.2266 | 31.2266 | 31.2266 | 31.2266 | 31.2266 | 31.2266 | 37.3763 | 49.5445 | 66.2477 | 89.2794 | 121.167 | 165.4789 | 227.2608 | 313.6577 | 434.8004 | 605.0698 | 844.9005 | 1183.3561 | 1661.8067 |  | 14.2119 | 14.2119 | 14.2119 | 15.7066 | 21.0465 | 28.4788 | 38.8757 | 53.486 | 74.1014 | 103.2973 | 144.781 | 203.8971 | 288.3601 | 409.3177 | 582.8947 | 832.4358 | 1191.7646 | 1709.9215 | 2458.0532 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 0 | 0 | 0 | 1.4947 | 6.8346 | 14.2669 | 24.6638 | 39.2741 | 59.8895 | 89.0854 | 130.5691 | 189.6853 | 274.1483 | 395.1058 | 568.6828 | 818.2239 | 1177.5527 | 1692.9108 | 2435.5045 | 2559.7014 | 2549.2192 | 2534.7064 | 2514.5392 | 2486.4209 | 2447.0999 | 2391.9652 | 2314.472 | 2205.32 | 2051.2817 | 1833.5287 |  | 0.016644 | 0.016644 | 0.016644 | 0.018395 | 0.024649 | 0.033353 | 0.04553 | 0.06264 | 0.086784 | 0.12098 | 0.16956 | 0.2388 | 0.33771 | 0.47938 | 0.68266 | 0.97491 | 1.3957 | 2.0026 | 2.8788 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019922 | 0.026408 | 0.035311 | 0.047588 | 0.064584 | 0.088203 | 0.12113 | 0.16719 | 0.23176 | 0.32251 | 0.45035 | 0.63075 | 0.88577 |  | 0 | 0 | 0 | 0.0017505 | 0.0080044 | 0.016709 | 0.028885 | 0.045996 | 0.07014 | 0.10433 | 0.15292 | 0.22215 | 0.32107 | 0.46273 | 0.66602 | 0.95827 | 1.3791 | 1.9827 | 2.8524 | 2.9978 | 2.9855 | 2.9685 | 2.9449 | 2.912 | 2.8659 | 2.8014 | 2.7106 | 2.5828 | 2.4024 | 2.1473 |  | 0 | 0 | 0 | 1.4965 | 6.8426 | 14.2837 | 24.6927 | 39.3201 | 59.9597 | 89.1898 | 130.7221 | 189.9074 | 274.4693 | 395.5686 | 569.3489 | 819.1822 | 1178.9318 | 1694.8934 | 2438.3568 | 2562.6992 | 2552.2047 | 2537.675 | 2517.4841 | 2489.3329 | 2449.9658 | 2394.7666 | 2317.1826 | 2207.9028 | 2053.6841 | 1835.6761 |  | 14.6711 | 14.6711 | 14.6711 | 16.2142 | 21.7266 | 29.3991 | 40.132 | 55.2144 | 76.496 | 106.6353 | 149.4595 | 210.4859 | 297.6783 | 422.5445 | 601.7305 | 859.3353 | 1230.2756 | 1765.1763 | 2537.4834 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 0 | 0 | 0 | 1.543 | 7.0555 | 14.728 | 25.4608 | 40.5432 | 61.8248 | 91.9642 | 134.7884 | 195.8148 | 283.0071 | 407.8734 | 587.0594 | 844.6642 | 1215.6045 | 1747.6159 | 2514.206 | 2642.4162 | 2631.5953 | 2616.6136 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 2.0677 | 2.0677 | 2.0677 | 2.2852 | 3.0621 | 4.1434 | 5.656 | 7.7817 | 10.781 | 15.0288 | 21.0643 | 29.6651 | 41.9536 | 59.5518 | 84.8056 | 121.1114 | 173.3903 | 248.7772 | 357.6232 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0 | 0 | 0 | 0.21747 | 0.99437 | 2.0757 | 3.5884 | 5.714 | 8.7134 | 12.9611 | 18.9966 | 27.5974 | 39.8859 | 57.4841 | 82.7379 | 119.0437 | 171.3226 | 246.3023 | 354.3425 | 372.412 | 370.8869 | 368.7755 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 0.25924 | 0.25924 | 0.25924 | 0.28651 | 0.38392 | 0.51949 | 0.70915 | 0.97566 | 1.3517 | 1.8843 | 2.641 | 3.7194 | 5.2601 | 7.4665 | 10.6328 | 15.1848 | 21.7394 | 31.1913 | 44.8382 | 47.2424 | 47.2424 | 47.2424 | 47.2424 | 47.2424 | 47.2424 | 47.2424 | 47.2424 | 47.2424 | 47.2424 | 47.2424 |  | 0.25924 | 0.25924 | 0.25924 | 0.25924 | 0.25924 | 0.25924 | 0.25924 | 0.25924 | 0.25924 | 0.25924 | 0.25924 | 0.25924 | 0.25924 | 0.25924 | 0.25924 | 0.25924 | 0.25924 | 0.3103 | 0.41132 | 0.54999 | 0.7412 | 1.0059 | 1.3738 | 1.8867 | 2.604 | 3.6097 | 5.0233 | 7.0144 | 9.8243 | 13.7964 |  | 0 | 0 | 0 | 0.027266 | 0.12467 | 0.26025 | 0.4499 | 0.71641 | 1.0925 | 1.625 | 2.3818 | 3.4601 | 5.0008 | 7.2073 | 10.3735 | 14.9255 | 21.4801 | 30.881 | 44.4269 | 46.6924 | 46.5012 | 46.2365 | 45.8686 | 45.3557 | 44.6384 | 43.6327 | 42.2191 | 40.228 | 37.4181 | 33.446 |  | 0 | 0 | 0 | 3.2842 | 15.0171 | 31.3476 | 54.1918 | 86.2938 | 131.5903 | 195.74 | 286.8887 | 416.7797 | 602.3633 | 868.1333 | 1249.5197 | 1797.8156 | 2587.339 | 3719.6926 | 5351.3322 | 5624.2198 | 5601.1881 | 5569.3005 | 5524.9886 | 5463.2067 | 5376.8098 | 5255.6671 | 5085.3976 | 4845.5669 | 4507.1114 | 4028.6608
| FALSE | 3798 | 22002542 | SHL | Blank | 22 | BUS VRR 2 | VOLTAGE REGULATION | C | RMS | 2V162 | 2V162 | 2V162 | Electronic |  | 0 | 2190 |  | 2.5292 | 0.004397 | 0 | 0.004397 | 12.0918 | 0 | 12.0918 | 12.4815 | 1.7593 | 0 |  | 8.8804 | 0.031959 | 0 | 0.031959 | 87.8881 | 0 | 87.8881 | 90.7202 | 12.7869 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 26.3326 | 191.3952 | 30.9493 | 160.4459 |  | 0.12559 |  | 2.8677 | 3.2514 | 3.6865 | 4.1799 | 4.7392 | 5.3734 | 6.0925 | 6.9078 | 7.8322 | 8.8804 | 10.0687 | 11.4161 | 12.9438 | 14.676 | 16.64 | 18.8667 | 21.3915 | 24.2541 | 27.4998 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.004397 | 0.004397 | 0.004397 | 0.0048595 | 0.0065116 | 0.0088111 | 0.012028 | 0.016548 | 0.022926 | 0.031959 | 0.044794 | 0.063084 | 0.089216 | 0.12664 | 0.18034 | 0.25755 | 0.36872 | 0.52903 | 0.7605 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.3326 | 26.3326 | 26.3326 | 29.1021 | 38.9962 | 52.7672 | 72.0312 | 99.1019 | 137.2994 | 191.3952 | 268.2586 | 377.7923 | 534.2902 | 758.4073 | 1080.0207 | 1542.3847 | 2208.1696 | 3168.2404 | 4554.4215 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 12.0918 | 12.0918 | 12.0918 | 13.3636 | 17.9069 | 24.2305 | 33.0765 | 45.5073 | 63.0474 | 87.8881 | 123.1835 | 173.4811 | 245.3444 | 348.2583 | 495.9422 | 708.2583 | 1013.9847 | 1454.8462 | 2091.3764 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | -2.12 | -2.12 | -2.12 | -0.84823 | 3.6951 | 10.0187 | 18.8647 | 31.2955 | 48.8356 | 73.6763 | 108.9717 | 159.2692 | 231.1326 | 334.0465 | 481.7304 | 694.0465 | 999.7729 | 1437.8356 | 2068.8277 | 2173.3638 | 2162.8816 | 2148.3689 | 2128.2017 | 2100.0836 | 2060.7628 | 2005.6284 | 1928.1355 | 1818.984 | 1664.9464 | 1447.1944 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -2.12 | -2.12 | -2.12 | -0.84823 | 3.6951 | 10.0187 | 18.8647 | 31.2955 | 48.8356 | 73.6763 | 108.9717 | 159.2692 | 231.1326 | 334.0465 | 481.7304 | 694.0465 | 999.7729 | 1437.8356 | 2068.8277 | 2173.3638 | 2162.8816 | 2148.3689 | 2128.2017 | 2100.0836 | 2060.7628 | 2005.6284 | 1928.1355 | 1818.984 | 1664.9464 | 1447.1944 |  | 12.4815 | 12.4815 | 12.4815 | 13.7942 | 18.4839 | 25.0113 | 34.1423 | 46.9737 | 65.0791 | 90.7202 | 127.153 | 179.0713 | 253.2504 | 359.4806 | 511.9234 | 731.0812 | 1046.6594 | 1501.7272 | 2158.7689 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | -2.1883 | -2.1883 | -2.1883 | -0.87556 | 3.8142 | 10.3416 | 19.4726 | 32.3039 | 50.4093 | 76.0504 | 112.4832 | 164.4015 | 238.5806 | 344.8108 | 497.2536 | 716.4114 | 1031.9896 | 1484.1684 | 2135.4937 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 1.7593 | 1.7593 | 1.7593 | 1.9443 | 2.6053 | 3.5253 | 4.8123 | 6.6209 | 9.1728 | 12.7869 | 17.9221 | 25.2399 | 35.6954 | 50.6684 | 72.1551 | 103.0451 | 147.5256 | 211.6669 | 304.2763 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | -0.30844 | -0.30844 | -0.30844 | -0.12341 | 0.5376 | 1.4576 | 2.7446 | 4.5532 | 7.1051 | 10.7192 | 15.8544 | 23.1722 | 33.6277 | 48.6007 | 70.0874 | 100.9775 | 145.4579 | 209.192 | 300.9956 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -4.6167 | -4.6167 | -4.6167 | -1.8472 | 8.0469 | 21.8179 | 41.0819 | 68.1526 | 106.3501 | 160.4459 | 237.3093 | 346.843 | 503.3409 | 727.458 | 1049.0714 | 1511.4354 | 2177.2203 | 3131.196 | 4505.317 | 4732.9667 | 4710.1395 | 4678.5351 | 4634.6167 | 4573.3835 | 4487.7538 | 4367.6869 | 4198.9295 | 3961.2286 | 3625.7787 | 3151.5769
| FALSE | 3799 | 22011624 | SHL | Blank | 22 | CAP NO.1 | NEUTRAL BALANCE MOD 1 | X | Siemens | 7SR11 | 7SR11 | SIEMENS 7SR11 | Digital |  | 0.2894 | 1 |  | 2.1077 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.2337 |  | 6.8646 | 0.019138 | 7.587e-06 | 0.019131 | 52.6319 | 0.53109 | 53.163 | 54.3688 | 7.6572 | 8.272 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.2337 |  | 33.3387 | 123.4611 | 33.3387 | 90.1224 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.006032 | 0.0079547 | 0.01058 | 0.01418 | 0.019138 | 0.02599 | 0.035489 | 0.0487 | 0.06712 | 0.092864 | 0.12892 | 0.17952 | 0.25064 | 0.35077 | 0.49191 | 0.69112 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.3913e-06 | 3.1535e-06 | 4.1942e-06 | 5.6216e-06 | 7.587e-06 | 1.0303e-05 | 1.4069e-05 | 1.9306e-05 | 2.6609e-05 | 3.6814e-05 | 5.1109e-05 | 7.1167e-05 | 9.9363e-05 | 0.00013906 | 0.00019501 | 0.00027398 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 38.9129 | 51.3159 | 68.2516 | 91.4783 | 123.4611 | 167.6609 | 228.9448 | 314.1673 | 432.9939 | 599.069 | 831.6742 | 1158.0817 | 1616.8972 | 2262.81 | 3173.3439 | 4458.455 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 |  | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 39.9043 | 52.8955 | 70.7284 | 95.3179 | 129.3623 | 176.6712 | 242.6318 | 334.8722 | 464.2086 | 645.9944 | 902.0463 | 1263.3937 | 1774.2048 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 16.5887 | 21.8762 | 29.0959 | 38.9975 | 52.6319 | 71.4744 | 97.6 | 133.9306 | 184.5868 | 255.3853 | 354.5457 | 493.6944 | 689.2891 | 964.644 | 1352.8079 | 1900.6553 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 0 | 0 | 0 | 0 | 0 | 2.3763 | 7.6638 | 14.8835 | 24.7851 | 38.4195 | 57.262 | 83.3876 | 119.7183 | 170.3744 | 241.1729 | 340.3333 | 479.482 | 672.2777 | 942.0945 | 1322.6561 | 1860.021 | 2534.7953 | 2514.6273 | 2486.5081 | 2447.1856 | 2392.0491 | 2314.5531 | 2205.3973 | 2051.3536 | 1833.593 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.16739 | 0.22075 | 0.2936 | 0.39351 | 0.53109 | 0.72123 | 0.98485 | 1.3515 | 1.8626 | 2.577 | 3.5776 | 4.9817 | 6.9554 | 9.7339 | 13.6508 | 19.1789 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 |  | 0 | 0 | 0 | 0 | 0 | 0.023979 | 0.077333 | 0.15018 | 0.2501 | 0.38768 | 0.57781 | 0.84144 | 1.208 | 1.7192 | 2.4336 | 3.4342 | 4.8383 | 6.7837 | 9.5064 | 13.3465 | 18.7689 | 25.5778 | 25.3743 | 25.0906 | 24.6938 | 24.1374 | 23.3554 | 22.254 | 20.6996 | 18.5022 |  | 0 | 0 | 0 | 0 | 0 | 2.4003 | 7.7411 | 15.0337 | 25.0352 | 38.8072 | 57.8398 | 84.229 | 120.9263 | 172.0936 | 243.6065 | 343.7675 | 484.3203 | 679.0615 | 951.6009 | 1336.0026 | 1878.7899 | 2560.3731 | 2540.0016 | 2511.5986 | 2471.8794 | 2416.1865 | 2337.9086 | 2227.6513 | 2072.0532 | 1852.0952 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.1362 | 22.5981 | 30.0561 | 40.2845 | 54.3688 | 73.8332 | 100.8209 | 138.3506 | 190.6785 | 263.8133 | 366.2462 | 509.987 | 712.0366 | 996.4787 | 1397.4525 | 1963.3798 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 0 | 0 | 0 | 0 | 0 | 2.4547 | 7.9167 | 15.3747 | 25.6031 | 39.6874 | 59.1518 | 86.1395 | 123.6691 | 175.9971 | 249.1319 | 351.5648 | 495.3056 | 694.4639 | 973.185 | 1366.3057 | 1921.4044 | 2618.4473 | 2597.6137 | 2568.5665 | 2527.9464 | 2470.9902 | 2390.9368 | 2278.1786 | 2119.0513 | 1894.1043 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4134 | 3.1827 | 4.2331 | 5.6736 | 7.6572 | 10.3986 | 14.1995 | 19.4851 | 26.8549 | 37.1551 | 51.5816 | 71.8259 | 100.2823 | 140.3428 | 196.8154 | 276.5199 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0 | 0 | 0 | 0 | 0 | 0.34572 | 1.115 | 2.1653 | 3.6059 | 5.5895 | 8.3309 | 12.1318 | 17.4174 | 24.7872 | 35.0874 | 49.5139 | 69.7582 | 97.8074 | 137.0621 | 192.4287 | 270.6081 | 368.7787 | 365.8445 | 361.7536 | 356.0327 | 348.011 | 336.7364 | 320.8557 | 298.4444 | 266.7632 |  | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.6072 | 3.4382 | 4.5729 | 6.1291 | 8.272 | 11.2335 | 15.3395 | 21.0495 | 29.011 | 40.1382 | 55.723 | 77.5927 | 108.3338 | 151.6106 | 212.6173 | 298.7211 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 |  | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.6736 | 3.5441 | 4.7389 | 6.3864 | 8.6674 | 11.8372 | 16.2566 | 22.4368 | 31.1025 | 43.2823 | 60.438 | 84.6487 | 118.8736 |  | 0 | 0 | 0 | 0 | 0 | 0.37348 | 1.2045 | 2.3392 | 3.8954 | 6.0383 | 8.9997 | 13.1058 | 18.8158 | 26.7773 | 37.9045 | 53.4893 | 75.359 | 105.6602 | 148.0666 | 207.8785 | 292.3347 | 398.3873 | 395.2175 | 390.7981 | 384.6179 | 375.9522 | 363.7724 | 346.6166 | 322.406 | 288.1811 |  | 0 | 0 | 0 | 0 | 0 | 5.5742 | 17.9773 | 34.9129 | 58.1397 | 90.1224 | 134.3222 | 195.6061 | 280.8286 | 399.6552 | 565.7303 | 798.3356 | 1124.743 | 1576.9929 | 2209.9145 | 3102.6154 | 4363.1372 | 5945.9863 | 5898.6773 | 5832.7168 | 5740.4763 | 5611.14 | 5429.3542 | 5173.3022 | 4811.9549 | 4301.1437
| FALSE | 3800 | 22011627 | SHL | Blank | 22 | CAP NO.1 | NEUTRAL BALANCE MOD 4 | X | Siemens | 7SR11 | 7SR11 | SIEMENS 7SR11 | Digital |  | 0.2894 | 1 |  | 2.1077 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.2337 |  | 6.8646 | 0.019138 | 7.587e-06 | 0.019131 | 52.6319 | 0.53109 | 53.163 | 54.3688 | 7.6572 | 8.272 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.2337 |  | 33.3387 | 123.4611 | 33.3387 | 90.1224 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.006032 | 0.0079547 | 0.01058 | 0.01418 | 0.019138 | 0.02599 | 0.035489 | 0.0487 | 0.06712 | 0.092864 | 0.12892 | 0.17952 | 0.25064 | 0.35077 | 0.49191 | 0.69112 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.3913e-06 | 3.1535e-06 | 4.1942e-06 | 5.6216e-06 | 7.587e-06 | 1.0303e-05 | 1.4069e-05 | 1.9306e-05 | 2.6609e-05 | 3.6814e-05 | 5.1109e-05 | 7.1167e-05 | 9.9363e-05 | 0.00013906 | 0.00019501 | 0.00027398 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 38.9129 | 51.3159 | 68.2516 | 91.4783 | 123.4611 | 167.6609 | 228.9448 | 314.1673 | 432.9939 | 599.069 | 831.6742 | 1158.0817 | 1616.8972 | 2262.81 | 3173.3439 | 4458.455 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 |  | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 39.9043 | 52.8955 | 70.7284 | 95.3179 | 129.3623 | 176.6712 | 242.6318 | 334.8722 | 464.2086 | 645.9944 | 902.0463 | 1263.3937 | 1774.2048 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 16.5887 | 21.8762 | 29.0959 | 38.9975 | 52.6319 | 71.4744 | 97.6 | 133.9306 | 184.5868 | 255.3853 | 354.5457 | 493.6944 | 689.2891 | 964.644 | 1352.8079 | 1900.6553 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 0 | 0 | 0 | 0 | 0 | 2.3763 | 7.6638 | 14.8835 | 24.7851 | 38.4195 | 57.262 | 83.3876 | 119.7183 | 170.3744 | 241.1729 | 340.3333 | 479.482 | 672.2777 | 942.0945 | 1322.6561 | 1860.021 | 2534.7953 | 2514.6273 | 2486.5081 | 2447.1856 | 2392.0491 | 2314.5531 | 2205.3973 | 2051.3536 | 1833.593 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.16739 | 0.22075 | 0.2936 | 0.39351 | 0.53109 | 0.72123 | 0.98485 | 1.3515 | 1.8626 | 2.577 | 3.5776 | 4.9817 | 6.9554 | 9.7339 | 13.6508 | 19.1789 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 |  | 0 | 0 | 0 | 0 | 0 | 0.023979 | 0.077333 | 0.15018 | 0.2501 | 0.38768 | 0.57781 | 0.84144 | 1.208 | 1.7192 | 2.4336 | 3.4342 | 4.8383 | 6.7837 | 9.5064 | 13.3465 | 18.7689 | 25.5778 | 25.3743 | 25.0906 | 24.6938 | 24.1374 | 23.3554 | 22.254 | 20.6996 | 18.5022 |  | 0 | 0 | 0 | 0 | 0 | 2.4003 | 7.7411 | 15.0337 | 25.0352 | 38.8072 | 57.8398 | 84.229 | 120.9263 | 172.0936 | 243.6065 | 343.7675 | 484.3203 | 679.0615 | 951.6009 | 1336.0026 | 1878.7899 | 2560.3731 | 2540.0016 | 2511.5986 | 2471.8794 | 2416.1865 | 2337.9086 | 2227.6513 | 2072.0532 | 1852.0952 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.1362 | 22.5981 | 30.0561 | 40.2845 | 54.3688 | 73.8332 | 100.8209 | 138.3506 | 190.6785 | 263.8133 | 366.2462 | 509.987 | 712.0366 | 996.4787 | 1397.4525 | 1963.3798 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 0 | 0 | 0 | 0 | 0 | 2.4547 | 7.9167 | 15.3747 | 25.6031 | 39.6874 | 59.1518 | 86.1395 | 123.6691 | 175.9971 | 249.1319 | 351.5648 | 495.3056 | 694.4639 | 973.185 | 1366.3057 | 1921.4044 | 2618.4473 | 2597.6137 | 2568.5665 | 2527.9464 | 2470.9902 | 2390.9368 | 2278.1786 | 2119.0513 | 1894.1043 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4134 | 3.1827 | 4.2331 | 5.6736 | 7.6572 | 10.3986 | 14.1995 | 19.4851 | 26.8549 | 37.1551 | 51.5816 | 71.8259 | 100.2823 | 140.3428 | 196.8154 | 276.5199 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0 | 0 | 0 | 0 | 0 | 0.34572 | 1.115 | 2.1653 | 3.6059 | 5.5895 | 8.3309 | 12.1318 | 17.4174 | 24.7872 | 35.0874 | 49.5139 | 69.7582 | 97.8074 | 137.0621 | 192.4287 | 270.6081 | 368.7787 | 365.8445 | 361.7536 | 356.0327 | 348.011 | 336.7364 | 320.8557 | 298.4444 | 266.7632 |  | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.6072 | 3.4382 | 4.5729 | 6.1291 | 8.272 | 11.2335 | 15.3395 | 21.0495 | 29.011 | 40.1382 | 55.723 | 77.5927 | 108.3338 | 151.6106 | 212.6173 | 298.7211 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 |  | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.6736 | 3.5441 | 4.7389 | 6.3864 | 8.6674 | 11.8372 | 16.2566 | 22.4368 | 31.1025 | 43.2823 | 60.438 | 84.6487 | 118.8736 |  | 0 | 0 | 0 | 0 | 0 | 0.37348 | 1.2045 | 2.3392 | 3.8954 | 6.0383 | 8.9997 | 13.1058 | 18.8158 | 26.7773 | 37.9045 | 53.4893 | 75.359 | 105.6602 | 148.0666 | 207.8785 | 292.3347 | 398.3873 | 395.2175 | 390.7981 | 384.6179 | 375.9522 | 363.7724 | 346.6166 | 322.406 | 288.1811 |  | 0 | 0 | 0 | 0 | 0 | 5.5742 | 17.9773 | 34.9129 | 58.1397 | 90.1224 | 134.3222 | 195.6061 | 280.8286 | 399.6552 | 565.7303 | 798.3356 | 1124.743 | 1576.9929 | 2209.9145 | 3102.6154 | 4363.1372 | 5945.9863 | 5898.6773 | 5832.7168 | 5740.4763 | 5611.14 | 5429.3542 | 5173.3022 | 4811.9549 | 4301.1437
| FALSE | 3801 | 22011626 | SHL | Blank | 22 | CAP NO.1 | NEUTRAL BALANCE MOD 3 | X | Siemens | 7SR11 | 7SR11 | SIEMENS 7SR11 | Digital |  | 0.2894 | 1 |  | 2.1077 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.2337 |  | 6.8646 | 0.019138 | 7.587e-06 | 0.019131 | 52.6319 | 0.53109 | 53.163 | 54.3688 | 7.6572 | 8.272 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.2337 |  | 33.3387 | 123.4611 | 33.3387 | 90.1224 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.006032 | 0.0079547 | 0.01058 | 0.01418 | 0.019138 | 0.02599 | 0.035489 | 0.0487 | 0.06712 | 0.092864 | 0.12892 | 0.17952 | 0.25064 | 0.35077 | 0.49191 | 0.69112 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.3913e-06 | 3.1535e-06 | 4.1942e-06 | 5.6216e-06 | 7.587e-06 | 1.0303e-05 | 1.4069e-05 | 1.9306e-05 | 2.6609e-05 | 3.6814e-05 | 5.1109e-05 | 7.1167e-05 | 9.9363e-05 | 0.00013906 | 0.00019501 | 0.00027398 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 38.9129 | 51.3159 | 68.2516 | 91.4783 | 123.4611 | 167.6609 | 228.9448 | 314.1673 | 432.9939 | 599.069 | 831.6742 | 1158.0817 | 1616.8972 | 2262.81 | 3173.3439 | 4458.455 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 |  | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 39.9043 | 52.8955 | 70.7284 | 95.3179 | 129.3623 | 176.6712 | 242.6318 | 334.8722 | 464.2086 | 645.9944 | 902.0463 | 1263.3937 | 1774.2048 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 16.5887 | 21.8762 | 29.0959 | 38.9975 | 52.6319 | 71.4744 | 97.6 | 133.9306 | 184.5868 | 255.3853 | 354.5457 | 493.6944 | 689.2891 | 964.644 | 1352.8079 | 1900.6553 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 0 | 0 | 0 | 0 | 0 | 2.3763 | 7.6638 | 14.8835 | 24.7851 | 38.4195 | 57.262 | 83.3876 | 119.7183 | 170.3744 | 241.1729 | 340.3333 | 479.482 | 672.2777 | 942.0945 | 1322.6561 | 1860.021 | 2534.7953 | 2514.6273 | 2486.5081 | 2447.1856 | 2392.0491 | 2314.5531 | 2205.3973 | 2051.3536 | 1833.593 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.16739 | 0.22075 | 0.2936 | 0.39351 | 0.53109 | 0.72123 | 0.98485 | 1.3515 | 1.8626 | 2.577 | 3.5776 | 4.9817 | 6.9554 | 9.7339 | 13.6508 | 19.1789 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 |  | 0 | 0 | 0 | 0 | 0 | 0.023979 | 0.077333 | 0.15018 | 0.2501 | 0.38768 | 0.57781 | 0.84144 | 1.208 | 1.7192 | 2.4336 | 3.4342 | 4.8383 | 6.7837 | 9.5064 | 13.3465 | 18.7689 | 25.5778 | 25.3743 | 25.0906 | 24.6938 | 24.1374 | 23.3554 | 22.254 | 20.6996 | 18.5022 |  | 0 | 0 | 0 | 0 | 0 | 2.4003 | 7.7411 | 15.0337 | 25.0352 | 38.8072 | 57.8398 | 84.229 | 120.9263 | 172.0936 | 243.6065 | 343.7675 | 484.3203 | 679.0615 | 951.6009 | 1336.0026 | 1878.7899 | 2560.3731 | 2540.0016 | 2511.5986 | 2471.8794 | 2416.1865 | 2337.9086 | 2227.6513 | 2072.0532 | 1852.0952 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.1362 | 22.5981 | 30.0561 | 40.2845 | 54.3688 | 73.8332 | 100.8209 | 138.3506 | 190.6785 | 263.8133 | 366.2462 | 509.987 | 712.0366 | 996.4787 | 1397.4525 | 1963.3798 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 0 | 0 | 0 | 0 | 0 | 2.4547 | 7.9167 | 15.3747 | 25.6031 | 39.6874 | 59.1518 | 86.1395 | 123.6691 | 175.9971 | 249.1319 | 351.5648 | 495.3056 | 694.4639 | 973.185 | 1366.3057 | 1921.4044 | 2618.4473 | 2597.6137 | 2568.5665 | 2527.9464 | 2470.9902 | 2390.9368 | 2278.1786 | 2119.0513 | 1894.1043 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4134 | 3.1827 | 4.2331 | 5.6736 | 7.6572 | 10.3986 | 14.1995 | 19.4851 | 26.8549 | 37.1551 | 51.5816 | 71.8259 | 100.2823 | 140.3428 | 196.8154 | 276.5199 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0 | 0 | 0 | 0 | 0 | 0.34572 | 1.115 | 2.1653 | 3.6059 | 5.5895 | 8.3309 | 12.1318 | 17.4174 | 24.7872 | 35.0874 | 49.5139 | 69.7582 | 97.8074 | 137.0621 | 192.4287 | 270.6081 | 368.7787 | 365.8445 | 361.7536 | 356.0327 | 348.011 | 336.7364 | 320.8557 | 298.4444 | 266.7632 |  | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.6072 | 3.4382 | 4.5729 | 6.1291 | 8.272 | 11.2335 | 15.3395 | 21.0495 | 29.011 | 40.1382 | 55.723 | 77.5927 | 108.3338 | 151.6106 | 212.6173 | 298.7211 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 |  | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.6736 | 3.5441 | 4.7389 | 6.3864 | 8.6674 | 11.8372 | 16.2566 | 22.4368 | 31.1025 | 43.2823 | 60.438 | 84.6487 | 118.8736 |  | 0 | 0 | 0 | 0 | 0 | 0.37348 | 1.2045 | 2.3392 | 3.8954 | 6.0383 | 8.9997 | 13.1058 | 18.8158 | 26.7773 | 37.9045 | 53.4893 | 75.359 | 105.6602 | 148.0666 | 207.8785 | 292.3347 | 398.3873 | 395.2175 | 390.7981 | 384.6179 | 375.9522 | 363.7724 | 346.6166 | 322.406 | 288.1811 |  | 0 | 0 | 0 | 0 | 0 | 5.5742 | 17.9773 | 34.9129 | 58.1397 | 90.1224 | 134.3222 | 195.6061 | 280.8286 | 399.6552 | 565.7303 | 798.3356 | 1124.743 | 1576.9929 | 2209.9145 | 3102.6154 | 4363.1372 | 5945.9863 | 5898.6773 | 5832.7168 | 5740.4763 | 5611.14 | 5429.3542 | 5173.3022 | 4811.9549 | 4301.1437
| FALSE | 3802 | 22011625 | SHL | Blank | 22 | CAP NO.1 | NEUTRAL BALANCE MOD 2 | X | Siemens | 7SR11 | 7SR11 | SIEMENS 7SR11 | Digital |  | 0.2894 | 1 |  | 2.1077 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.2337 |  | 6.8646 | 0.019138 | 7.587e-06 | 0.019131 | 52.6319 | 0.53109 | 53.163 | 54.3688 | 7.6572 | 8.272 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.2337 |  | 33.3387 | 123.4611 | 33.3387 | 90.1224 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.006032 | 0.0079547 | 0.01058 | 0.01418 | 0.019138 | 0.02599 | 0.035489 | 0.0487 | 0.06712 | 0.092864 | 0.12892 | 0.17952 | 0.25064 | 0.35077 | 0.49191 | 0.69112 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.3913e-06 | 3.1535e-06 | 4.1942e-06 | 5.6216e-06 | 7.587e-06 | 1.0303e-05 | 1.4069e-05 | 1.9306e-05 | 2.6609e-05 | 3.6814e-05 | 5.1109e-05 | 7.1167e-05 | 9.9363e-05 | 0.00013906 | 0.00019501 | 0.00027398 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 38.9129 | 51.3159 | 68.2516 | 91.4783 | 123.4611 | 167.6609 | 228.9448 | 314.1673 | 432.9939 | 599.069 | 831.6742 | 1158.0817 | 1616.8972 | 2262.81 | 3173.3439 | 4458.455 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 |  | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 39.9043 | 52.8955 | 70.7284 | 95.3179 | 129.3623 | 176.6712 | 242.6318 | 334.8722 | 464.2086 | 645.9944 | 902.0463 | 1263.3937 | 1774.2048 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 16.5887 | 21.8762 | 29.0959 | 38.9975 | 52.6319 | 71.4744 | 97.6 | 133.9306 | 184.5868 | 255.3853 | 354.5457 | 493.6944 | 689.2891 | 964.644 | 1352.8079 | 1900.6553 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 0 | 0 | 0 | 0 | 0 | 2.3763 | 7.6638 | 14.8835 | 24.7851 | 38.4195 | 57.262 | 83.3876 | 119.7183 | 170.3744 | 241.1729 | 340.3333 | 479.482 | 672.2777 | 942.0945 | 1322.6561 | 1860.021 | 2534.7953 | 2514.6273 | 2486.5081 | 2447.1856 | 2392.0491 | 2314.5531 | 2205.3973 | 2051.3536 | 1833.593 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.16739 | 0.22075 | 0.2936 | 0.39351 | 0.53109 | 0.72123 | 0.98485 | 1.3515 | 1.8626 | 2.577 | 3.5776 | 4.9817 | 6.9554 | 9.7339 | 13.6508 | 19.1789 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 |  | 0 | 0 | 0 | 0 | 0 | 0.023979 | 0.077333 | 0.15018 | 0.2501 | 0.38768 | 0.57781 | 0.84144 | 1.208 | 1.7192 | 2.4336 | 3.4342 | 4.8383 | 6.7837 | 9.5064 | 13.3465 | 18.7689 | 25.5778 | 25.3743 | 25.0906 | 24.6938 | 24.1374 | 23.3554 | 22.254 | 20.6996 | 18.5022 |  | 0 | 0 | 0 | 0 | 0 | 2.4003 | 7.7411 | 15.0337 | 25.0352 | 38.8072 | 57.8398 | 84.229 | 120.9263 | 172.0936 | 243.6065 | 343.7675 | 484.3203 | 679.0615 | 951.6009 | 1336.0026 | 1878.7899 | 2560.3731 | 2540.0016 | 2511.5986 | 2471.8794 | 2416.1865 | 2337.9086 | 2227.6513 | 2072.0532 | 1852.0952 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.1362 | 22.5981 | 30.0561 | 40.2845 | 54.3688 | 73.8332 | 100.8209 | 138.3506 | 190.6785 | 263.8133 | 366.2462 | 509.987 | 712.0366 | 996.4787 | 1397.4525 | 1963.3798 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 0 | 0 | 0 | 0 | 0 | 2.4547 | 7.9167 | 15.3747 | 25.6031 | 39.6874 | 59.1518 | 86.1395 | 123.6691 | 175.9971 | 249.1319 | 351.5648 | 495.3056 | 694.4639 | 973.185 | 1366.3057 | 1921.4044 | 2618.4473 | 2597.6137 | 2568.5665 | 2527.9464 | 2470.9902 | 2390.9368 | 2278.1786 | 2119.0513 | 1894.1043 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4134 | 3.1827 | 4.2331 | 5.6736 | 7.6572 | 10.3986 | 14.1995 | 19.4851 | 26.8549 | 37.1551 | 51.5816 | 71.8259 | 100.2823 | 140.3428 | 196.8154 | 276.5199 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0 | 0 | 0 | 0 | 0 | 0.34572 | 1.115 | 2.1653 | 3.6059 | 5.5895 | 8.3309 | 12.1318 | 17.4174 | 24.7872 | 35.0874 | 49.5139 | 69.7582 | 97.8074 | 137.0621 | 192.4287 | 270.6081 | 368.7787 | 365.8445 | 361.7536 | 356.0327 | 348.011 | 336.7364 | 320.8557 | 298.4444 | 266.7632 |  | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.6072 | 3.4382 | 4.5729 | 6.1291 | 8.272 | 11.2335 | 15.3395 | 21.0495 | 29.011 | 40.1382 | 55.723 | 77.5927 | 108.3338 | 151.6106 | 212.6173 | 298.7211 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 |  | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.6736 | 3.5441 | 4.7389 | 6.3864 | 8.6674 | 11.8372 | 16.2566 | 22.4368 | 31.1025 | 43.2823 | 60.438 | 84.6487 | 118.8736 |  | 0 | 0 | 0 | 0 | 0 | 0.37348 | 1.2045 | 2.3392 | 3.8954 | 6.0383 | 8.9997 | 13.1058 | 18.8158 | 26.7773 | 37.9045 | 53.4893 | 75.359 | 105.6602 | 148.0666 | 207.8785 | 292.3347 | 398.3873 | 395.2175 | 390.7981 | 384.6179 | 375.9522 | 363.7724 | 346.6166 | 322.406 | 288.1811 |  | 0 | 0 | 0 | 0 | 0 | 5.5742 | 17.9773 | 34.9129 | 58.1397 | 90.1224 | 134.3222 | 195.6061 | 280.8286 | 399.6552 | 565.7303 | 798.3356 | 1124.743 | 1576.9929 | 2209.9145 | 3102.6154 | 4363.1372 | 5945.9863 | 5898.6773 | 5832.7168 | 5740.4763 | 5611.14 | 5429.3542 | 5173.3022 | 4811.9549 | 4301.1437
| FALSE | 3803 | 22011629 | SHL | Blank | 22 | CAP NO.1 | METER (DIGITAL MULTI FN.) | I | Schneider | ION_6200 | ION 6200 | ION 6000s | Digital |  | 0 | 1 |  | 2.1077 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 6.8646 | 0.019138 | 0 | 0.019138 | 52.6298 | 0 | 52.6298 | 54.3258 | 7.6572 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 114.6128 | 30.9493 | 83.6635 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.006032 | 0.0079547 | 0.01058 | 0.01418 | 0.019138 | 0.02599 | 0.035489 | 0.0487 | 0.06712 | 0.092864 | 0.12892 | 0.17952 | 0.25064 | 0.35077 | 0.49191 | 0.69112 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 36.124 | 47.6382 | 63.36 | 84.9222 | 114.6128 | 155.6447 | 212.5365 | 291.6512 | 401.9616 | 556.1342 | 772.0688 | 1075.083 | 1501.0156 | 2100.6364 | 2945.9131 | 4138.9214 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 16.588 | 21.8753 | 29.0947 | 38.996 | 52.6298 | 71.4716 | 97.5961 | 133.9253 | 184.5795 | 255.3751 | 354.5316 | 493.6748 | 689.2617 | 964.6058 | 1352.7542 | 1900.58 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 2.3762 | 7.6635 | 14.8829 | 24.7842 | 38.418 | 57.2598 | 83.3843 | 119.7135 | 170.3677 | 241.1633 | 340.3198 | 479.463 | 672.2511 | 942.0571 | 1322.6036 | 1859.9473 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2.3762 | 7.6635 | 14.8829 | 24.7842 | 38.418 | 57.2598 | 83.3843 | 119.7135 | 170.3677 | 241.1633 | 340.3198 | 479.463 | 672.2511 | 942.0571 | 1322.6036 | 1859.9473 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.1226 | 22.5802 | 30.0323 | 40.2526 | 54.3258 | 73.7747 | 100.741 | 138.2409 | 190.5274 | 263.6043 | 365.9561 | 509.583 | 711.4725 | 995.6892 | 1396.3454 | 1961.8243 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 2.4528 | 7.9104 | 15.3625 | 25.5828 | 39.656 | 59.1049 | 86.0713 | 123.5712 | 175.8576 | 248.9346 | 351.2863 | 494.9132 | 693.9137 | 972.414 | 1365.2232 | 1919.8822 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4134 | 3.1827 | 4.233 | 5.6736 | 7.6572 | 10.3985 | 14.1993 | 19.4849 | 26.8546 | 37.1548 | 51.5811 | 71.8252 | 100.2813 | 140.3414 | 196.8134 | 276.5171 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0.34572 | 1.115 | 2.1653 | 3.6059 | 5.5895 | 8.3308 | 12.1317 | 17.4172 | 24.787 | 35.0871 | 49.5134 | 69.7575 | 97.8064 | 137.0607 | 192.4268 | 270.6054 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 5.1747 | 16.6889 | 32.4107 | 53.9728 | 83.6635 | 124.6954 | 181.5872 | 260.7019 | 371.0123 | 525.1849 | 741.1195 | 1044.1337 | 1463.9712 | 2051.5319 | 2880.2537 | 4050.4349 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 3804 | 22011623 | SHL | Blank | 22 | CAP NO.1 | OC & EF & CB MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.2894 | 1 |  | 2.5292 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.2337 |  | 8.8804 | 0.037562 | 1.4891e-05 | 0.037548 | 103.3009 | 1.0424 | 104.3433 | 106.71 | 15.0289 | 16.2355 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 2.2337 |  | 33.3387 | 242.3178 | 33.3387 | 208.9791 |  | 0.12559 |  | 2.8677 | 3.2514 | 3.6865 | 4.1799 | 4.7392 | 5.3734 | 6.0925 | 6.9078 | 7.8322 | 8.8804 | 10.0687 | 11.4161 | 12.9438 | 14.676 | 16.64 | 18.8667 | 21.3915 | 24.2541 | 27.4998 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0057115 | 0.0076532 | 0.010356 | 0.014137 | 0.019449 | 0.026946 | 0.037562 | 0.052647 | 0.074144 | 0.10486 | 0.14884 | 0.21196 | 0.3027 | 0.43337 | 0.62179 | 0.89383 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.0488e-06 | 2.0488e-06 | 2.0488e-06 | 2.2642e-06 | 3.034e-06 | 4.1054e-06 | 5.6042e-06 | 7.7104e-06 | 1.0682e-05 | 1.4891e-05 | 2.0871e-05 | 2.9393e-05 | 4.1569e-05 | 5.9006e-05 | 8.4029e-05 | 0.00012 | 0.0001718 | 0.0002465 | 0.00035435 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 33.3387 | 33.3387 | 33.3387 | 36.845 | 49.3715 | 66.8065 | 91.1958 | 125.469 | 173.8292 | 242.3178 | 339.6314 | 478.3077 | 676.4434 | 960.1892 | 1367.371 | 1952.7516 | 2795.6753 | 4011.1824 | 5766.171 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 | 6075.3486 |  | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 33.3387 | 39.9043 | 52.8955 | 70.7284 | 95.3179 | 129.3623 | 176.6712 | 242.6318 | 334.8722 | 464.2086 | 645.9944 | 902.0463 | 1263.3937 | 1774.2048 |  | 14.2124 | 14.2124 | 14.2124 | 15.7072 | 21.0472 | 28.4798 | 38.8771 | 53.4879 | 74.104 | 103.3009 | 144.7861 | 203.9043 | 288.3703 | 409.3321 | 582.9152 | 832.465 | 1191.8064 | 1709.9814 | 2458.1394 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 0 | 0 | 0 | 1.4948 | 6.8349 | 14.2674 | 24.6647 | 39.2755 | 59.8916 | 89.0885 | 130.5737 | 189.6919 | 274.1579 | 395.1197 | 568.7028 | 818.2526 | 1177.594 | 1692.9701 | 2435.5898 | 2559.7911 | 2549.3085 | 2534.7953 | 2514.6273 | 2486.5081 | 2447.1856 | 2392.0491 | 2314.5531 | 2205.3973 | 2051.3536 | 1833.593 |  | 0.14341 | 0.14341 | 0.14341 | 0.1585 | 0.21238 | 0.28738 | 0.3923 | 0.53973 | 0.74776 | 1.0424 | 1.461 | 2.0575 | 2.9099 | 4.1304 | 5.882 | 8.4001 | 12.0261 | 17.2549 | 24.8043 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 |  | 0 | 0 | 0 | 0.015083 | 0.068968 | 0.14397 | 0.24888 | 0.39632 | 0.60435 | 0.89896 | 1.3176 | 1.9141 | 2.7664 | 3.987 | 5.7386 | 8.2567 | 11.8827 | 17.0832 | 24.5768 | 25.83 | 25.7243 | 25.5778 | 25.3743 | 25.0906 | 24.6938 | 24.1374 | 23.3554 | 22.254 | 20.6996 | 18.5022 |  | 0 | 0 | 0 | 1.5099 | 6.9038 | 14.4114 | 24.9136 | 39.6718 | 60.496 | 89.9875 | 131.8913 | 191.606 | 276.9243 | 399.1067 | 574.4414 | 826.5093 | 1189.4767 | 1710.0533 | 2460.1666 | 2585.6211 | 2575.0328 | 2560.3731 | 2540.0016 | 2511.5986 | 2471.8794 | 2416.1865 | 2337.9086 | 2227.6513 | 2072.0532 | 1852.0952 |  | 14.6814 | 14.6814 | 14.6814 | 16.2255 | 21.7418 | 29.4197 | 40.1601 | 55.2531 | 76.5496 | 106.71 | 149.5643 | 210.6334 | 297.8869 | 422.8406 | 602.1522 | 859.9376 | 1231.1377 | 1766.4134 | 2539.2616 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 0 | 0 | 0 | 1.5441 | 7.0604 | 14.7383 | 25.4787 | 40.5716 | 61.8682 | 92.0286 | 134.8828 | 195.952 | 283.2055 | 408.1592 | 587.4708 | 845.2561 | 1216.4563 | 1748.8406 | 2515.9679 | 2644.268 | 2633.4395 | 2618.4473 | 2597.6137 | 2568.5665 | 2527.9464 | 2470.9902 | 2390.9368 | 2278.1786 | 2119.0513 | 1894.1043 |  | 2.0677 | 2.0677 | 2.0677 | 2.2852 | 3.0621 | 4.1434 | 5.6561 | 7.7818 | 10.7811 | 15.0289 | 21.0644 | 29.6653 | 41.954 | 59.5523 | 84.8063 | 121.1125 | 173.3918 | 248.7794 | 357.6263 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0 | 0 | 0 | 0.21747 | 0.99438 | 2.0757 | 3.5884 | 5.7141 | 8.7134 | 12.9612 | 18.9967 | 27.5976 | 39.8863 | 57.4846 | 82.7386 | 119.0448 | 171.3241 | 246.3044 | 354.3456 | 372.4153 | 370.8902 | 368.7787 | 365.8445 | 361.7536 | 356.0327 | 348.011 | 336.7364 | 320.8557 | 298.4444 | 266.7632 |  | 2.2337 | 2.2337 | 2.2337 | 2.4687 | 3.3079 | 4.4761 | 6.1102 | 8.4066 | 11.6467 | 16.2355 | 22.7557 | 32.0471 | 45.3224 | 64.3337 | 91.6153 | 130.8364 | 187.3132 | 268.7534 | 386.3395 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 | 407.0547 |  | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.2337 | 2.6736 | 3.5441 | 4.7389 | 6.3864 | 8.6674 | 11.8372 | 16.2566 | 22.4368 | 31.1025 | 43.2823 | 60.438 | 84.6487 | 118.8736 |  | 0 | 0 | 0 | 0.23493 | 1.0742 | 2.2424 | 3.8765 | 6.1728 | 9.413 | 14.0018 | 20.5219 | 29.8134 | 43.0887 | 62.0999 | 89.3816 | 128.6027 | 185.0794 | 266.0798 | 382.7954 | 402.3158 | 400.6683 | 398.3873 | 395.2175 | 390.7981 | 384.6179 | 375.9522 | 363.7724 | 346.6166 | 322.406 | 288.1811 |  | 0 | 0 | 0 | 3.5063 | 16.0328 | 33.4678 | 57.8571 | 92.1303 | 140.4906 | 208.9791 | 306.2928 | 444.9691 | 643.1048 | 926.8505 | 1334.0324 | 1919.4129 | 2762.3366 | 3971.2782 | 5713.2755 | 6004.6202 | 5980.0307 | 5945.9863 | 5898.6773 | 5832.7168 | 5740.4763 | 5611.14 | 5429.3542 | 5173.3022 | 4811.9549 | 4301.1437
| FALSE | 3805 | 22011628 | SHL | Blank | 22 | CAP NO.1 | CAP CONTROL | C | Schweitzer | SEL_2411 | SEL 2411 | SEL 2000s | Digital |  | 0 | 1 |  | 2.1077 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 6.8646 | 0.019138 | 0 | 0.019138 | 52.6298 | 0 | 52.6298 | 54.3258 | 7.6572 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 114.6128 | 30.9493 | 83.6635 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.006032 | 0.0079547 | 0.01058 | 0.01418 | 0.019138 | 0.02599 | 0.035489 | 0.0487 | 0.06712 | 0.092864 | 0.12892 | 0.17952 | 0.25064 | 0.35077 | 0.49191 | 0.69112 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 36.124 | 47.6382 | 63.36 | 84.9222 | 114.6128 | 155.6447 | 212.5365 | 291.6512 | 401.9616 | 556.1342 | 772.0688 | 1075.083 | 1501.0156 | 2100.6364 | 2945.9131 | 4138.9214 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 16.588 | 21.8753 | 29.0947 | 38.996 | 52.6298 | 71.4716 | 97.5961 | 133.9253 | 184.5795 | 255.3751 | 354.5316 | 493.6748 | 689.2617 | 964.6058 | 1352.7542 | 1900.58 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 2.3762 | 7.6635 | 14.8829 | 24.7842 | 38.418 | 57.2598 | 83.3843 | 119.7135 | 170.3677 | 241.1633 | 340.3198 | 479.463 | 672.2511 | 942.0571 | 1322.6036 | 1859.9473 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2.3762 | 7.6635 | 14.8829 | 24.7842 | 38.418 | 57.2598 | 83.3843 | 119.7135 | 170.3677 | 241.1633 | 340.3198 | 479.463 | 672.2511 | 942.0571 | 1322.6036 | 1859.9473 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.1226 | 22.5802 | 30.0323 | 40.2526 | 54.3258 | 73.7747 | 100.741 | 138.2409 | 190.5274 | 263.6043 | 365.9561 | 509.583 | 711.4725 | 995.6892 | 1396.3454 | 1961.8243 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 2.4528 | 7.9104 | 15.3625 | 25.5828 | 39.656 | 59.1049 | 86.0713 | 123.5712 | 175.8576 | 248.9346 | 351.2863 | 494.9132 | 693.9137 | 972.414 | 1365.2232 | 1919.8822 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4134 | 3.1827 | 4.233 | 5.6736 | 7.6572 | 10.3985 | 14.1993 | 19.4849 | 26.8546 | 37.1548 | 51.5811 | 71.8252 | 100.2813 | 140.3414 | 196.8134 | 276.5171 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0.34572 | 1.115 | 2.1653 | 3.6059 | 5.5895 | 8.3308 | 12.1317 | 17.4172 | 24.787 | 35.0871 | 49.5134 | 69.7575 | 97.8064 | 137.0607 | 192.4268 | 270.6054 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 5.1747 | 16.6889 | 32.4107 | 53.9728 | 83.6635 | 124.6954 | 181.5872 | 260.7019 | 371.0123 | 525.1849 | 741.1195 | 1044.1337 | 1463.9712 | 2051.5319 | 2880.2537 | 4050.4349 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| FALSE | 3806 | 22015967 | SHL | Blank | 22 | CB NER CB | CLOSE NER BYPASS CB | BU | RMS | 2T105 | 2T105 | RMS 2T1XX | Electronic |  | 0.016937 | 2190 |  | 2.1077 | 0.004397 | 0.00021604 | 0.004181 | 12.1513 | 15.1231 | 27.2743 | 13.708 | 1.7614 | 235.5492 |  | 6.8646 | 0.016283 | 0.00080006 | 0.015483 | 44.9991 | 56.0044 | 101.0034 | 50.7641 | 6.5229 | 872.2958 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 14.2119 | 0.0083933 | 14.2203 | 14.6705 | 2.0677 | 0.13073 |  | 278.293 | 1030.5863 | 31.0891 | 999.4972 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.0051322 | 0.0067681 | 0.0090017 | 0.012065 | 0.016283 | 0.022113 | 0.030196 | 0.041436 | 0.057108 | 0.079011 | 0.10969 | 0.15274 | 0.21325 | 0.29844 | 0.41853 | 0.58803 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00021604 | 0.00021604 | 0.00021604 | 0.00021604 | 0.00021604 | 0.00025217 | 0.00033254 | 0.00044229 | 0.00059281 | 0.00080006 | 0.0010865 | 0.0014836 | 0.0020359 | 0.0028059 | 0.0038821 | 0.0053895 | 0.0075047 | 0.010478 | 0.014664 | 0.020564 | 0.028892 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 278.293 | 278.293 | 278.293 | 278.293 | 278.293 | 324.8237 | 428.3575 | 569.727 | 763.6114 | 1030.5863 | 1399.5418 | 1911.1067 | 2622.4982 | 3614.3979 | 5000.703 | 6942.3653 | 9667.0379 | 13496.981 | 18888.7109 | 26489.3536 | 37216.7645 | 50713.715 | 50713.715 | 50713.715 | 50713.715 | 50713.715 | 50713.715 | 50713.715 | 50713.715 | 50713.715 |  | 31.0891 | 31.0891 | 31.0891 | 31.0891 | 31.0891 | 31.0891 | 31.0891 | 31.0891 | 31.0891 | 31.0891 | 31.0891 | 31.0891 | 31.0891 | 31.0891 | 31.0891 | 31.0891 | 31.0891 | 37.2117 | 49.3264 | 65.9561 | 88.8863 | 120.6336 | 164.7504 | 226.2603 | 312.2768 | 432.8863 | 602.4061 | 841.181 | 1178.1466 | 1654.4909 |  | 12.1513 | 12.1513 | 12.1513 | 12.1513 | 12.1513 | 14.183 | 18.7036 | 24.8763 | 33.342 | 44.9991 | 61.109 | 83.4457 | 114.5076 | 157.8175 | 218.3485 | 303.1283 | 422.0972 | 589.3262 | 824.7483 | 1156.6193 | 1625.0162 | 2214.3411 | 2214.3411 | 2214.3411 | 2214.3411 | 2214.3411 | 2214.3411 | 2214.3411 | 2214.3411 | 2214.3411 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6328 | 55.1455 | 75.3128 | 103.4309 | 142.7519 | 197.8864 | 275.3795 | 384.5312 | 538.5692 | 756.3216 |  | -2.0606 | -2.0606 | -2.0606 | -2.0606 | -2.0606 | -0.028899 | 4.4918 | 10.6644 | 19.1301 | 30.7872 | 46.8971 | 69.2339 | 100.2957 | 143.6056 | 204.1366 | 288.9165 | 407.8854 | 572.3155 | 802.1996 | 1126.4687 | 1584.3834 | 2159.1955 | 2139.0283 | 2110.9101 | 2071.5892 | 2016.4547 | 1938.9616 | 1829.8098 | 1675.7719 | 1458.0194 |  | 15.1231 | 15.1231 | 15.1231 | 15.1231 | 15.1231 | 17.6516 | 23.2779 | 30.9602 | 41.4964 | 56.0044 | 76.0542 | 103.8538 | 142.5124 | 196.4145 | 271.7494 | 377.2637 | 525.3285 | 733.4562 | 1026.4549 | 1439.4908 | 2022.4424 | 2755.8969 | 2755.8969 | 2755.8969 | 2755.8969 | 2755.8969 | 2755.8969 | 2755.8969 | 2755.8969 | 2755.8969 |  | 0.0083933 | 0.0083933 | 0.0083933 | 0.0083933 | 0.0083933 | 0.0083933 | 0.0083933 | 0.0083933 | 0.0083933 | 0.0083933 | 0.0083933 | 0.0083933 | 0.0083933 | 0.0083933 | 0.0083933 | 0.0083933 | 0.0083933 | 0.010046 | 0.013317 | 0.017806 | 0.023997 | 0.032568 | 0.044478 | 0.061084 | 0.084307 | 0.11687 | 0.16263 | 0.2271 | 0.31807 | 0.44667 |  | 15.1147 | 15.1147 | 15.1147 | 15.1147 | 15.1147 | 17.6433 | 23.2695 | 30.9518 | 41.488 | 55.996 | 76.0458 | 103.8454 | 142.504 | 196.4061 | 271.741 | 377.2553 | 525.3201 | 733.4461 | 1026.4416 | 1439.473 | 2022.4184 | 2755.8643 | 2755.8524 | 2755.8358 | 2755.8126 | 2755.78 | 2755.7343 | 2755.6698 | 2755.5788 | 2755.4502 |  | 13.0541 | 13.0541 | 13.0541 | 13.0541 | 13.0541 | 17.6144 | 27.7613 | 41.6163 | 60.6181 | 86.7832 | 122.943 | 173.0793 | 242.7998 | 340.0117 | 475.8776 | 666.1718 | 933.2055 | 1305.7616 | 1828.6411 | 2565.9417 | 3606.8018 | 4915.0599 | 4894.8807 | 4866.7459 | 4827.4018 | 4772.2347 | 4694.6959 | 4585.4796 | 4431.3507 | 4213.4697 |  | 13.708 | 13.708 | 13.708 | 13.708 | 13.708 | 16 | 21.0998 | 28.0633 | 37.6136 | 50.7641 | 68.938 | 94.1364 | 129.1778 | 178.0363 | 246.3223 | 341.9638 | 476.1745 | 664.8281 | 930.4114 | 1304.8004 | 1833.2062 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | -0.96244 | -0.96244 | -0.96244 | -0.96244 | -0.96244 | 1.3295 | 6.4294 | 13.3929 | 22.9432 | 36.0937 | 54.2675 | 79.4659 | 114.5073 | 163.3659 | 231.6519 | 327.2934 | 461.504 | 647.2684 | 907.1351 | 1273.6768 | 1791.2622 | 2441.1077 | 2420.2897 | 2391.2642 | 2350.6743 | 2293.7607 | 2213.767 | 2101.0929 | 1942.0842 | 1717.305 |  | 1.7614 | 1.7614 | 1.7614 | 1.7614 | 1.7614 | 2.0559 | 2.7112 | 3.606 | 4.8332 | 6.5229 | 8.8582 | 12.0961 | 16.5987 | 22.8768 | 31.6512 | 43.9407 | 61.1861 | 85.4272 | 119.5533 | 167.6605 | 235.558 | 320.985 | 320.985 | 320.985 | 320.985 | 320.985 | 320.985 | 320.985 | 320.985 | 320.985 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | -0.30628 | -0.30628 | -0.30628 | -0.30628 | -0.30628 | -0.011768 | 0.64353 | 1.5383 | 2.7655 | 4.4553 | 6.7905 | 10.0284 | 14.531 | 20.8091 | 29.5835 | 41.873 | 59.1184 | 82.9523 | 116.2727 | 163.2738 | 229.6463 | 312.9618 | 310.0277 | 305.9368 | 300.2159 | 292.1944 | 280.9199 | 265.0393 | 242.6282 | 210.9473 |  | 235.5492 | 235.5492 | 235.5492 | 235.5492 | 235.5492 | 274.9332 | 362.5649 | 482.2211 | 646.3263 | 872.2958 | 1184.5825 | 1617.5747 | 2219.7017 | 3059.2528 | 4232.6316 | 5876.0687 | 8182.2516 | 11423.9434 | 15987.543 | 22420.7826 | 31500.5416 | 42924.4592 | 42924.4592 | 42924.4592 | 42924.4592 | 42924.4592 | 42924.4592 | 42924.4592 | 42924.4592 | 42924.4592 |  | 0.13073 | 0.13073 | 0.13073 | 0.13073 | 0.13073 | 0.13073 | 0.13073 | 0.13073 | 0.13073 | 0.13073 | 0.13073 | 0.13073 | 0.13073 | 0.13073 | 0.13073 | 0.13073 | 0.13073 | 0.15647 | 0.20742 | 0.27734 | 0.37376 | 0.50726 | 0.69277 | 0.95142 | 1.3131 | 1.8203 | 2.5331 | 3.5371 | 4.9541 | 6.9571 |  | 235.4185 | 235.4185 | 235.4185 | 235.4185 | 235.4185 | 274.8024 | 362.4342 | 482.0903 | 646.1956 | 872.1651 | 1184.4517 | 1617.444 | 2219.5709 | 3059.1221 | 4232.5009 | 5875.938 | 8182.1208 | 11423.7869 | 15987.3356 | 22420.5053 | 31500.1679 | 42923.952 | 42923.7664 | 42923.5078 | 42923.1461 | 42922.6389 | 42921.9261 | 42920.9221 | 42919.5051 | 42917.5021 |  | 247.2039 | 247.2039 | 247.2039 | 247.2039 | 247.2039 | 293.7346 | 397.2684 | 538.6378 | 732.5223 | 999.4972 | 1368.4527 | 1880.0176 | 2591.4091 | 3583.3088 | 4969.6139 | 6911.2761 | 9635.9487 | 13459.7693 | 18839.3845 | 26423.3976 | 37127.8782 | 50593.0814 | 50548.9646 | 50487.4547 | 50401.4381 | 50280.8287 | 50111.3088 | 49872.5339 | 49535.5683 | 49059.224
| FALSE | 3807 | 22011630 | SHL | Blank | 22 | ALL FEEDERS | MASTER EARTH FAULT | X | RMS | 2C138 | 2C138 | RMS 2C13X | Electronic |  | 0.81881 | 2190 |  | 2.5292 | 0.004397 | 0.0035096 | 0.00088747 | 13.057 | 245.6698 | 258.7268 | 32.4061 | 1.7943 | 3826.4296 |  | 8.8804 | 0.031959 | 0.025509 | 0.0064504 | 94.903 | 1785.6202 | 1880.5232 | 235.5399 | 13.042 | 27811.9184 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 6.32 |  | 4119.3569 | 29941.0234 | 37.7096 | 29903.3138 |  | 0.12559 |  | 2.8677 | 3.2514 | 3.6865 | 4.1799 | 4.7392 | 5.3734 | 6.0925 | 6.9078 | 7.8322 | 8.8804 | 10.0687 | 11.4161 | 12.9438 | 14.676 | 16.64 | 18.8667 | 21.3915 | 24.2541 | 27.4998 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.004397 | 0.004397 | 0.004397 | 0.0048595 | 0.0065116 | 0.0088111 | 0.012028 | 0.016548 | 0.022926 | 0.031959 | 0.044794 | 0.063084 | 0.089216 | 0.12664 | 0.18034 | 0.25755 | 0.36872 | 0.52903 | 0.7605 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0035096 | 0.0035096 | 0.0035096 | 0.0038787 | 0.0051973 | 0.0070327 | 0.0096002 | 0.013208 | 0.018299 | 0.025509 | 0.035753 | 0.050352 | 0.071209 | 0.10108 | 0.14394 | 0.20557 | 0.2943 | 0.42226 | 0.60701 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 4119.3569 | 4119.3569 | 4119.3569 | 4552.605 | 6100.3887 | 8254.6712 | 11268.2406 | 15503.0715 | 21478.512 | 29941.0234 | 41965.1966 | 59100.1727 | 83582.0163 | 118641.9205 | 168953.7124 | 241283.9121 | 345436.3963 | 495625.6645 | 712473.7863 | 750676.0723 | 750676.0723 | 750676.0723 | 750676.0723 | 750676.0723 | 750676.0723 | 750676.0723 | 750676.0723 | 750676.0723 | 750676.0723 | 750676.0723 |  | 37.7096 | 37.7096 | 37.7096 | 37.7096 | 37.7096 | 37.7096 | 37.7096 | 37.7096 | 37.7096 | 37.7096 | 37.7096 | 37.7096 | 37.7096 | 37.7096 | 37.7096 | 37.7096 | 37.7096 | 45.1361 | 59.8305 | 80.0015 | 107.8149 | 146.3228 | 199.8344 | 274.4429 | 378.7769 | 525.0704 | 730.6898 | 1020.3124 | 1429.0355 | 2006.8184 |  | 13.057 | 13.057 | 13.057 | 14.4302 | 19.3362 | 26.1645 | 35.7165 | 49.1395 | 68.0797 | 94.903 | 133.0156 | 187.3277 | 264.927 | 376.0551 | 535.5267 | 764.7891 | 1094.9176 | 1570.9673 | 2258.3031 | 2379.3916 | 2379.3916 | 2379.3916 | 2379.3916 | 2379.3916 | 2379.3916 | 2379.3916 | 2379.3916 | 2379.3916 | 2379.3916 | 2379.3916 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | -1.1564 | -1.1564 | -1.1564 | 0.21681 | 5.1228 | 11.9511 | 21.5031 | 34.9261 | 53.8663 | 80.6896 | 118.8022 | 173.1143 | 250.7136 | 361.8417 | 521.3132 | 750.5757 | 1080.7042 | 1553.9547 | 2235.752 | 2349.2376 | 2338.7543 | 2324.24 | 2304.0705 | 2275.9493 | 2236.624 | 2181.4834 | 2103.9819 | 1994.8181 | 1840.7633 | 1622.9869 |  | 245.6698 | 245.6698 | 245.6698 | 271.5079 | 363.8145 | 492.2914 | 672.0144 | 924.5708 | 1280.9336 | 1785.6202 | 2502.7167 | 3524.611 | 4984.657 | 7075.5565 | 10076.0468 | 14389.669 | 20601.1058 | 29558.0803 | 42490.4497 | 44768.7543 | 44768.7543 | 44768.7543 | 44768.7543 | 44768.7543 | 44768.7543 | 44768.7543 | 44768.7543 | 44768.7543 | 44768.7543 | 44768.7543 |  | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.48568 | 0.64379 | 0.86084 | 1.1601 | 1.5745 | 2.1503 | 2.9531 | 4.0757 | 5.6499 | 7.8624 | 10.9788 | 15.3768 | 21.5939 |  | 245.2641 | 245.2641 | 245.2641 | 271.1021 | 363.4087 | 491.8856 | 671.6086 | 924.1651 | 1280.5279 | 1785.2144 | 2502.311 | 3524.2052 | 4984.2513 | 7075.1508 | 10075.641 | 14389.2632 | 20600.7 | 29557.5946 | 42489.8059 | 44767.8935 | 44767.5942 | 44767.1799 | 44766.6041 | 44765.8013 | 44764.6786 | 44763.1044 | 44760.8919 | 44757.7755 | 44753.3775 | 44747.1604 |  | 244.1076 | 244.1076 | 244.1076 | 271.3189 | 368.5315 | 503.8367 | 693.1117 | 959.0912 | 1334.3941 | 1865.904 | 2621.1132 | 3697.3195 | 5234.9648 | 7436.9925 | 10596.9543 | 15139.8389 | 21681.4042 | 31111.5493 | 44725.5579 | 47117.1311 | 47106.3485 | 47091.4199 | 47070.6746 | 47041.7505 | 47001.3026 | 46944.5879 | 46864.8738 | 46752.5936 | 46594.1408 | 46370.1473 |  | 32.4061 | 32.4061 | 32.4061 | 35.8144 | 47.9905 | 64.9378 | 88.6449 | 121.9595 | 168.9671 | 235.5399 | 330.1316 | 464.9289 | 657.5226 | 933.3317 | 1329.1242 | 1898.1311 | 2717.4773 | 3898.9855 | 5604.8852 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 17.7034 | 17.7034 | 17.7034 | 21.1117 | 33.2878 | 50.2351 | 73.9422 | 107.2568 | 154.2644 | 220.8372 | 315.4289 | 450.2262 | 642.8199 | 918.629 | 1314.4215 | 1883.4284 | 2702.7746 | 3881.3873 | 5581.5578 | 5874.2228 | 5863.3786 | 5848.3647 | 5827.5009 | 5798.4116 | 5757.7326 | 5700.6939 | 5620.5245 | 5507.6029 | 5348.2449 | 5122.9719 |  | 1.7943 | 1.7943 | 1.7943 | 1.9831 | 2.6573 | 3.5957 | 4.9083 | 6.753 | 9.3558 | 13.042 | 18.2796 | 25.7434 | 36.4075 | 51.6792 | 73.5945 | 105.1008 | 150.4686 | 215.8895 | 310.3463 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | -0.2734 | -0.2734 | -0.2734 | -0.084681 | 0.58952 | 1.5279 | 2.8406 | 4.6852 | 7.2881 | 10.9743 | 16.2119 | 23.6757 | 34.3397 | 49.6115 | 71.5268 | 103.0331 | 148.4008 | 213.4145 | 307.0656 | 322.6001 | 321.075 | 318.9635 | 316.0292 | 311.9382 | 306.2172 | 298.1954 | 286.9206 | 271.0396 | 248.6279 | 216.9461 |  | 3826.4296 | 3826.4296 | 3826.4296 | 4228.8694 | 5666.5903 | 7667.6818 | 10466.9564 | 14400.6487 | 19951.1758 | 27811.9184 | 38981.053 | 54897.5616 | 77638.5023 | 110205.2979 | 156939.4202 | 224126.2221 | 320872.427 | 460381.742 | 661809.8018 | 697295.5247 | 697295.5247 | 697295.5247 | 697295.5247 | 697295.5247 | 697295.5247 | 697295.5247 | 697295.5247 | 697295.5247 | 697295.5247 | 697295.5247 |  | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 6.32 | 7.5647 | 10.0274 | 13.408 | 18.0694 | 24.5232 | 33.4916 | 45.9957 | 63.4817 | 88 | 122.4612 | 171.001 | 239.5016 | 336.3361 |  | 3820.1096 | 3820.1096 | 3820.1096 | 4222.5494 | 5660.2703 | 7661.3618 | 10460.6364 | 14394.3287 | 19944.8558 | 27805.5984 | 38974.733 | 54891.2416 | 77632.1822 | 110198.9779 | 156933.1002 | 224119.902 | 320866.107 | 460374.1773 | 661799.7744 | 697282.1167 | 697277.4553 | 697271.0015 | 697262.0332 | 697249.529 | 697232.043 | 697207.5247 | 697173.0635 | 697124.5238 | 697056.0231 | 696959.1887 |  | 4081.6473 | 4081.6473 | 4081.6473 | 4514.8953 | 6062.6791 | 8216.9615 | 11230.5309 | 15465.3619 | 21440.8024 | 29903.3138 | 41927.4869 | 59062.463 | 83544.3067 | 118604.2108 | 168916.0027 | 241246.2024 | 345398.6866 | 495580.5284 | 712413.9557 | 750596.0707 | 750568.2574 | 750529.7495 | 750476.2379 | 750401.6294 | 750297.2954 | 750151.0019 | 749945.3824 | 749655.7599 | 749247.0368 | 748669.2539
| FALSE | 3808 | 22011640 | SHL | SHL001 | 22 | SHL1 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 2.5292 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 1.8102 |  | 8.8804 | 0.037562 | 2.9553e-05 | 0.037533 | 103.305 | 2.0687 | 105.3737 | 106.7933 | 15.029 | 13.157 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 1.8102 |  | 33.0683 | 240.353 | 33.0683 | 207.2846 |  | 0.12559 |  | 2.8677 | 3.2514 | 3.6865 | 4.1799 | 4.7392 | 5.3734 | 6.0925 | 6.9078 | 7.8322 | 8.8804 | 10.0687 | 11.4161 | 12.9438 | 14.676 | 16.64 | 18.8667 | 21.3915 | 24.2541 | 27.4998 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0057115 | 0.0076532 | 0.010356 | 0.014137 | 0.019449 | 0.026946 | 0.037562 | 0.052647 | 0.074144 | 0.10486 | 0.14884 | 0.21196 | 0.3027 | 0.43337 | 0.62179 | 0.89383 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.4936e-06 | 6.0213e-06 | 8.1476e-06 | 1.1122e-05 | 1.5302e-05 | 2.12e-05 | 2.9553e-05 | 4.1421e-05 | 5.8334e-05 | 8.2498e-05 | 0.0001171 | 0.00016676 | 0.00023816 | 0.00034096 | 0.0004892 | 0.00070323 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 33.0683 | 33.0683 | 33.0683 | 36.5462 | 48.9712 | 66.2648 | 90.4563 | 124.4516 | 172.4198 | 240.353 | 336.8776 | 474.4294 | 670.9585 | 952.4035 | 1356.2838 | 1936.9178 | 2773.0067 | 3978.6581 | 5719.4164 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 |  | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 39.5807 | 52.4666 | 70.1549 | 94.545 | 128.3133 | 175.2387 | 240.6644 | 332.157 | 460.4446 | 640.7564 | 894.7322 | 1253.1496 | 1759.8188 |  | 14.2129 | 14.2129 | 14.2129 | 15.7078 | 21.0481 | 28.4809 | 38.8786 | 53.49 | 74.1069 | 103.305 | 144.7918 | 203.9122 | 288.3815 | 409.3481 | 582.9379 | 832.4975 | 1191.8529 | 1710.0482 | 2458.2353 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 1.4948 | 6.8351 | 14.268 | 24.6657 | 39.277 | 59.894 | 89.092 | 130.5788 | 189.6993 | 274.1686 | 395.1351 | 568.725 | 818.2845 | 1177.64 | 1693.0362 | 2435.6849 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.31455 | 0.42149 | 0.57033 | 0.77855 | 1.0711 | 1.484 | 2.0687 | 2.8995 | 4.0834 | 5.7749 | 8.1972 | 11.6734 | 16.6709 | 23.867 | 34.2439 | 49.2264 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0.029934 | 0.13687 | 0.28572 | 0.49393 | 0.78653 | 1.1994 | 1.7841 | 2.6149 | 3.7987 | 5.4903 | 7.9126 | 11.3888 | 16.3862 | 23.5824 | 33.9032 | 48.7749 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 1.5248 | 6.972 | 14.5537 | 25.1596 | 40.0635 | 61.0934 | 90.8761 | 133.1937 | 193.4981 | 279.6588 | 403.0477 | 580.1137 | 834.6708 | 1201.2223 | 1726.9394 | 2484.4597 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 16.2382 | 21.7588 | 29.4427 | 40.1914 | 55.2962 | 76.6093 | 106.7933 | 149.6809 | 210.7977 | 298.1193 | 423.1705 | 602.6219 | 860.6083 | 1232.0981 | 1767.7912 | 2541.2423 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 1.5453 | 7.0659 | 14.7498 | 25.4985 | 40.6033 | 61.9164 | 92.1004 | 134.9881 | 196.1049 | 283.4264 | 408.4776 | 587.9291 | 845.9155 | 1217.4052 | 1750.2048 | 2517.9304 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.2852 | 3.0621 | 4.1435 | 5.6561 | 7.7818 | 10.7812 | 15.029 | 21.0646 | 29.6656 | 41.9544 | 59.5529 | 84.8072 | 121.1137 | 173.3935 | 248.7818 | 357.6298 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0.21747 | 0.99439 | 2.0757 | 3.5884 | 5.7141 | 8.7135 | 12.9613 | 18.9969 | 27.5979 | 39.8867 | 57.4852 | 82.7394 | 119.0459 | 171.3258 | 246.3068 | 354.3491 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 1.8102 | 1.8102 | 1.8102 | 2.0006 | 2.6807 | 3.6274 | 4.9516 | 6.8125 | 9.4383 | 13.157 | 18.4408 | 25.9704 | 36.7285 | 52.1349 | 74.2434 | 106.0275 | 151.7952 | 217.793 | 313.0826 | 329.8699 | 329.8699 | 329.8699 | 329.8699 | 329.8699 | 329.8699 | 329.8699 | 329.8699 | 329.8699 | 329.8699 | 329.8699 |  | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 2.1667 | 2.872 | 3.8403 | 5.1754 | 7.0239 | 9.5926 | 13.174 | 18.1824 | 25.2049 | 35.0752 | 48.9779 | 68.5978 | 96.333 |  | 0 | 0 | 0 | 0.19038 | 0.87053 | 1.8172 | 3.1414 | 5.0024 | 7.6281 | 11.3468 | 16.6306 | 24.1602 | 34.9183 | 50.3247 | 72.4332 | 104.2173 | 149.9851 | 215.6263 | 310.2106 | 326.0296 | 324.6944 | 322.846 | 320.2772 | 316.6958 | 311.6875 | 304.665 | 294.7947 | 280.892 | 261.2721 | 233.5368 |  | 0 | 0 | 0 | 3.4779 | 15.9028 | 33.1964 | 57.388 | 91.3833 | 139.3514 | 207.2846 | 303.8092 | 441.3611 | 637.8902 | 919.3352 | 1323.2155 | 1903.8495 | 2739.9384 | 3939.0773 | 5666.9499 | 5955.9321 | 5931.5421 | 5897.7737 | 5850.8484 | 5785.4226 | 5693.9301 | 5565.6424 | 5385.3307 | 5131.3549 | 4772.9375 | 4266.2682
| FALSE | 3809 | 22011641 | SHL | SHL002 | 22 | SHL2 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 2.5292 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 2.6229 |  | 8.8804 | 0.037562 | 2.9553e-05 | 0.037533 | 103.305 | 2.0687 | 105.3737 | 106.7933 | 15.029 | 19.0639 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 2.6229 |  | 33.881 | 246.2599 | 33.881 | 212.3789 |  | 0.12559 |  | 2.8677 | 3.2514 | 3.6865 | 4.1799 | 4.7392 | 5.3734 | 6.0925 | 6.9078 | 7.8322 | 8.8804 | 10.0687 | 11.4161 | 12.9438 | 14.676 | 16.64 | 18.8667 | 21.3915 | 24.2541 | 27.4998 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0057115 | 0.0076532 | 0.010356 | 0.014137 | 0.019449 | 0.026946 | 0.037562 | 0.052647 | 0.074144 | 0.10486 | 0.14884 | 0.21196 | 0.3027 | 0.43337 | 0.62179 | 0.89383 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.4936e-06 | 6.0213e-06 | 8.1476e-06 | 1.1122e-05 | 1.5302e-05 | 2.12e-05 | 2.9553e-05 | 4.1421e-05 | 5.8334e-05 | 8.2498e-05 | 0.0001171 | 0.00016676 | 0.00023816 | 0.00034096 | 0.0004892 | 0.00070323 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 33.881 | 33.881 | 33.881 | 37.4444 | 50.1747 | 67.8933 | 92.6794 | 127.5102 | 176.6572 | 246.2599 | 345.1567 | 486.089 | 687.4481 | 975.8099 | 1389.6159 | 1984.5197 | 2841.1564 | 4076.4379 | 5859.9773 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 |  | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 40.5535 | 53.756 | 71.8791 | 96.8685 | 131.4668 | 179.5454 | 246.579 | 340.3201 | 471.7606 | 656.5037 | 916.7212 | 1283.9471 | 1803.0683 |  | 14.2129 | 14.2129 | 14.2129 | 15.7078 | 21.0481 | 28.4809 | 38.8786 | 53.49 | 74.1069 | 103.305 | 144.7918 | 203.9122 | 288.3815 | 409.3481 | 582.9379 | 832.4975 | 1191.8529 | 1710.0482 | 2458.2353 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 1.4948 | 6.8351 | 14.268 | 24.6657 | 39.277 | 59.894 | 89.092 | 130.5788 | 189.6993 | 274.1686 | 395.1351 | 568.725 | 818.2845 | 1177.64 | 1693.0362 | 2435.6849 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.31455 | 0.42149 | 0.57033 | 0.77855 | 1.0711 | 1.484 | 2.0687 | 2.8995 | 4.0834 | 5.7749 | 8.1972 | 11.6734 | 16.6709 | 23.867 | 34.2439 | 49.2264 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0.029934 | 0.13687 | 0.28572 | 0.49393 | 0.78653 | 1.1994 | 1.7841 | 2.6149 | 3.7987 | 5.4903 | 7.9126 | 11.3888 | 16.3862 | 23.5824 | 33.9032 | 48.7749 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 1.5248 | 6.972 | 14.5537 | 25.1596 | 40.0635 | 61.0934 | 90.8761 | 133.1937 | 193.4981 | 279.6588 | 403.0477 | 580.1137 | 834.6708 | 1201.2223 | 1726.9394 | 2484.4597 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 16.2382 | 21.7588 | 29.4427 | 40.1914 | 55.2962 | 76.6093 | 106.7933 | 149.6809 | 210.7977 | 298.1193 | 423.1705 | 602.6219 | 860.6083 | 1232.0981 | 1767.7912 | 2541.2423 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 1.5453 | 7.0659 | 14.7498 | 25.4985 | 40.6033 | 61.9164 | 92.1004 | 134.9881 | 196.1049 | 283.4264 | 408.4776 | 587.9291 | 845.9155 | 1217.4052 | 1750.2048 | 2517.9304 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.2852 | 3.0621 | 4.1435 | 5.6561 | 7.7818 | 10.7812 | 15.029 | 21.0646 | 29.6656 | 41.9544 | 59.5529 | 84.8072 | 121.1137 | 173.3935 | 248.7818 | 357.6298 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0.21747 | 0.99439 | 2.0757 | 3.5884 | 5.7141 | 8.7135 | 12.9613 | 18.9969 | 27.5979 | 39.8867 | 57.4852 | 82.7394 | 119.0459 | 171.3258 | 246.3068 | 354.3491 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 2.6229 | 2.6229 | 2.6229 | 2.8987 | 3.8842 | 5.2559 | 7.1747 | 9.8711 | 13.6757 | 19.0639 | 26.7199 | 37.63 | 53.218 | 75.5412 | 107.5755 | 153.6293 | 219.9449 | 315.5728 | 453.6435 | 477.9675 | 477.9675 | 477.9675 | 477.9675 | 477.9675 | 477.9675 | 477.9675 | 477.9675 | 477.9675 | 477.9675 | 477.9675 |  | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 3.1394 | 4.1615 | 5.5644 | 7.499 | 10.1774 | 13.8993 | 19.0886 | 26.3455 | 36.5208 | 50.8225 | 70.9669 | 99.3953 | 139.5825 |  | 0 | 0 | 0 | 0.27586 | 1.2614 | 2.633 | 4.5518 | 7.2482 | 11.0529 | 16.4411 | 24.0971 | 35.0072 | 50.5951 | 72.9183 | 104.9527 | 151.0065 | 217.322 | 312.4334 | 449.482 | 472.403 | 470.4685 | 467.7901 | 464.0682 | 458.8788 | 451.622 | 441.4467 | 427.145 | 407.0005 | 378.5722 | 338.385 |  | 0 | 0 | 0 | 3.5634 | 16.2937 | 34.0123 | 58.7984 | 93.6291 | 142.7761 | 212.3789 | 311.2757 | 452.208 | 653.567 | 941.9289 | 1355.7349 | 1950.6387 | 2807.2753 | 4035.8844 | 5806.2213 | 6102.3056 | 6077.3161 | 6042.7179 | 5994.6393 | 5927.6056 | 5833.8646 | 5702.4241 | 5517.681 | 5257.4635 | 4890.2376 | 4371.1164
| FALSE | 3810 | 22011642 | SHL | SHL004 | 22 | SHL4 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 2.5292 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.2457 |  | 8.8804 | 0.037562 | 2.9553e-05 | 0.037533 | 103.305 | 2.0687 | 105.3737 | 106.7933 | 15.029 | 38.1279 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.2457 |  | 36.5039 | 265.3238 | 36.5039 | 228.8199 |  | 0.12559 |  | 2.8677 | 3.2514 | 3.6865 | 4.1799 | 4.7392 | 5.3734 | 6.0925 | 6.9078 | 7.8322 | 8.8804 | 10.0687 | 11.4161 | 12.9438 | 14.676 | 16.64 | 18.8667 | 21.3915 | 24.2541 | 27.4998 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0057115 | 0.0076532 | 0.010356 | 0.014137 | 0.019449 | 0.026946 | 0.037562 | 0.052647 | 0.074144 | 0.10486 | 0.14884 | 0.21196 | 0.3027 | 0.43337 | 0.62179 | 0.89383 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.4936e-06 | 6.0213e-06 | 8.1476e-06 | 1.1122e-05 | 1.5302e-05 | 2.12e-05 | 2.9553e-05 | 4.1421e-05 | 5.8334e-05 | 8.2498e-05 | 0.0001171 | 0.00016676 | 0.00023816 | 0.00034096 | 0.0004892 | 0.00070323 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 36.5039 | 36.5039 | 36.5039 | 40.3431 | 54.0589 | 73.1492 | 99.8541 | 137.3812 | 190.3329 | 265.3238 | 371.8766 | 523.719 | 740.6661 | 1051.3511 | 1497.1915 | 2138.149 | 3061.1013 | 4392.0107 | 6313.6207 | 6652.1521 | 6652.1521 | 6652.1521 | 6652.1521 | 6652.1521 | 6652.1521 | 6652.1521 | 6652.1521 | 6652.1521 | 6652.1521 | 6652.1521 |  | 36.5039 | 36.5039 | 36.5039 | 36.5039 | 36.5039 | 36.5039 | 36.5039 | 36.5039 | 36.5039 | 36.5039 | 36.5039 | 36.5039 | 36.5039 | 36.5039 | 36.5039 | 36.5039 | 36.5039 | 43.6929 | 57.9175 | 77.4435 | 104.3675 | 141.6441 | 193.4447 | 265.6677 | 366.6656 | 508.2814 | 707.3262 | 987.6881 | 1383.3424 | 1942.6508 |  | 14.2129 | 14.2129 | 14.2129 | 15.7078 | 21.0481 | 28.4809 | 38.8786 | 53.49 | 74.1069 | 103.305 | 144.7918 | 203.9122 | 288.3815 | 409.3481 | 582.9379 | 832.4975 | 1191.8529 | 1710.0482 | 2458.2353 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 1.4948 | 6.8351 | 14.268 | 24.6657 | 39.277 | 59.894 | 89.092 | 130.5788 | 189.6993 | 274.1686 | 395.1351 | 568.725 | 818.2845 | 1177.64 | 1693.0362 | 2435.6849 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.31455 | 0.42149 | 0.57033 | 0.77855 | 1.0711 | 1.484 | 2.0687 | 2.8995 | 4.0834 | 5.7749 | 8.1972 | 11.6734 | 16.6709 | 23.867 | 34.2439 | 49.2264 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0.029934 | 0.13687 | 0.28572 | 0.49393 | 0.78653 | 1.1994 | 1.7841 | 2.6149 | 3.7987 | 5.4903 | 7.9126 | 11.3888 | 16.3862 | 23.5824 | 33.9032 | 48.7749 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 1.5248 | 6.972 | 14.5537 | 25.1596 | 40.0635 | 61.0934 | 90.8761 | 133.1937 | 193.4981 | 279.6588 | 403.0477 | 580.1137 | 834.6708 | 1201.2223 | 1726.9394 | 2484.4597 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 16.2382 | 21.7588 | 29.4427 | 40.1914 | 55.2962 | 76.6093 | 106.7933 | 149.6809 | 210.7977 | 298.1193 | 423.1705 | 602.6219 | 860.6083 | 1232.0981 | 1767.7912 | 2541.2423 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 1.5453 | 7.0659 | 14.7498 | 25.4985 | 40.6033 | 61.9164 | 92.1004 | 134.9881 | 196.1049 | 283.4264 | 408.4776 | 587.9291 | 845.9155 | 1217.4052 | 1750.2048 | 2517.9304 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.2852 | 3.0621 | 4.1435 | 5.6561 | 7.7818 | 10.7812 | 15.029 | 21.0646 | 29.6656 | 41.9544 | 59.5529 | 84.8072 | 121.1137 | 173.3935 | 248.7818 | 357.6298 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0.21747 | 0.99439 | 2.0757 | 3.5884 | 5.7141 | 8.7135 | 12.9613 | 18.9969 | 27.5979 | 39.8867 | 57.4852 | 82.7394 | 119.0459 | 171.3258 | 246.3068 | 354.3491 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 5.2457 | 5.2457 | 5.2457 | 5.7974 | 7.7684 | 10.5118 | 14.3493 | 19.7421 | 27.3514 | 38.1279 | 53.4398 | 75.2601 | 106.436 | 151.0824 | 215.1511 | 307.2587 | 439.8898 | 631.1456 | 907.2869 | 955.9349 | 955.9349 | 955.9349 | 955.9349 | 955.9349 | 955.9349 | 955.9349 | 955.9349 | 955.9349 | 955.9349 | 955.9349 |  | 5.2457 | 5.2457 | 5.2457 | 5.2457 | 5.2457 | 5.2457 | 5.2457 | 5.2457 | 5.2457 | 5.2457 | 5.2457 | 5.2457 | 5.2457 | 5.2457 | 5.2457 | 5.2457 | 5.2457 | 6.2788 | 8.3229 | 11.1289 | 14.9979 | 20.3547 | 27.7986 | 38.1773 | 52.691 | 73.0416 | 101.645 | 141.9338 | 198.7906 | 279.165 |  | 0 | 0 | 0 | 0.55171 | 2.5227 | 5.266 | 9.1036 | 14.4964 | 22.1057 | 32.8821 | 48.1941 | 70.0143 | 101.1903 | 145.8367 | 209.9053 | 302.0129 | 434.644 | 624.8668 | 898.964 | 944.8061 | 940.937 | 935.5802 | 928.1363 | 917.7577 | 903.244 | 882.8933 | 854.29 | 814.0011 | 757.1443 | 676.77 |  | 0 | 0 | 0 | 3.8392 | 17.555 | 36.6453 | 63.3502 | 100.8773 | 153.829 | 228.8199 | 335.3727 | 487.2151 | 704.1622 | 1014.8472 | 1460.6876 | 2101.6451 | 3024.5974 | 4348.3178 | 6255.7033 | 6574.7086 | 6547.7846 | 6510.508 | 6458.7074 | 6386.4845 | 6285.4866 | 6143.8708 | 5944.826 | 5664.464 | 5268.8097 | 4709.5014
| FALSE | 3811 | 22011644 | SHL | SHL005 | 22 | SHL5 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 2.5292 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 1.8102 |  | 8.8804 | 0.037562 | 2.9553e-05 | 0.037533 | 103.305 | 2.0687 | 105.3737 | 106.7933 | 15.029 | 13.157 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 1.8102 |  | 33.0683 | 240.353 | 33.0683 | 207.2846 |  | 0.12559 |  | 2.8677 | 3.2514 | 3.6865 | 4.1799 | 4.7392 | 5.3734 | 6.0925 | 6.9078 | 7.8322 | 8.8804 | 10.0687 | 11.4161 | 12.9438 | 14.676 | 16.64 | 18.8667 | 21.3915 | 24.2541 | 27.4998 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0057115 | 0.0076532 | 0.010356 | 0.014137 | 0.019449 | 0.026946 | 0.037562 | 0.052647 | 0.074144 | 0.10486 | 0.14884 | 0.21196 | 0.3027 | 0.43337 | 0.62179 | 0.89383 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.4936e-06 | 6.0213e-06 | 8.1476e-06 | 1.1122e-05 | 1.5302e-05 | 2.12e-05 | 2.9553e-05 | 4.1421e-05 | 5.8334e-05 | 8.2498e-05 | 0.0001171 | 0.00016676 | 0.00023816 | 0.00034096 | 0.0004892 | 0.00070323 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 33.0683 | 33.0683 | 33.0683 | 36.5462 | 48.9712 | 66.2648 | 90.4563 | 124.4516 | 172.4198 | 240.353 | 336.8776 | 474.4294 | 670.9585 | 952.4035 | 1356.2838 | 1936.9178 | 2773.0067 | 3978.6581 | 5719.4164 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 | 6026.0871 |  | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 33.0683 | 39.5807 | 52.4666 | 70.1549 | 94.545 | 128.3133 | 175.2387 | 240.6644 | 332.157 | 460.4446 | 640.7564 | 894.7322 | 1253.1496 | 1759.8188 |  | 14.2129 | 14.2129 | 14.2129 | 15.7078 | 21.0481 | 28.4809 | 38.8786 | 53.49 | 74.1069 | 103.305 | 144.7918 | 203.9122 | 288.3815 | 409.3481 | 582.9379 | 832.4975 | 1191.8529 | 1710.0482 | 2458.2353 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 1.4948 | 6.8351 | 14.268 | 24.6657 | 39.277 | 59.894 | 89.092 | 130.5788 | 189.6993 | 274.1686 | 395.1351 | 568.725 | 818.2845 | 1177.64 | 1693.0362 | 2435.6849 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.31455 | 0.42149 | 0.57033 | 0.77855 | 1.0711 | 1.484 | 2.0687 | 2.8995 | 4.0834 | 5.7749 | 8.1972 | 11.6734 | 16.6709 | 23.867 | 34.2439 | 49.2264 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0.029934 | 0.13687 | 0.28572 | 0.49393 | 0.78653 | 1.1994 | 1.7841 | 2.6149 | 3.7987 | 5.4903 | 7.9126 | 11.3888 | 16.3862 | 23.5824 | 33.9032 | 48.7749 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 1.5248 | 6.972 | 14.5537 | 25.1596 | 40.0635 | 61.0934 | 90.8761 | 133.1937 | 193.4981 | 279.6588 | 403.0477 | 580.1137 | 834.6708 | 1201.2223 | 1726.9394 | 2484.4597 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 16.2382 | 21.7588 | 29.4427 | 40.1914 | 55.2962 | 76.6093 | 106.7933 | 149.6809 | 210.7977 | 298.1193 | 423.1705 | 602.6219 | 860.6083 | 1232.0981 | 1767.7912 | 2541.2423 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 1.5453 | 7.0659 | 14.7498 | 25.4985 | 40.6033 | 61.9164 | 92.1004 | 134.9881 | 196.1049 | 283.4264 | 408.4776 | 587.9291 | 845.9155 | 1217.4052 | 1750.2048 | 2517.9304 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.2852 | 3.0621 | 4.1435 | 5.6561 | 7.7818 | 10.7812 | 15.029 | 21.0646 | 29.6656 | 41.9544 | 59.5529 | 84.8072 | 121.1137 | 173.3935 | 248.7818 | 357.6298 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0.21747 | 0.99439 | 2.0757 | 3.5884 | 5.7141 | 8.7135 | 12.9613 | 18.9969 | 27.5979 | 39.8867 | 57.4852 | 82.7394 | 119.0459 | 171.3258 | 246.3068 | 354.3491 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 1.8102 | 1.8102 | 1.8102 | 2.0006 | 2.6807 | 3.6274 | 4.9516 | 6.8125 | 9.4383 | 13.157 | 18.4408 | 25.9704 | 36.7285 | 52.1349 | 74.2434 | 106.0275 | 151.7952 | 217.793 | 313.0826 | 329.8699 | 329.8699 | 329.8699 | 329.8699 | 329.8699 | 329.8699 | 329.8699 | 329.8699 | 329.8699 | 329.8699 | 329.8699 |  | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 1.8102 | 2.1667 | 2.872 | 3.8403 | 5.1754 | 7.0239 | 9.5926 | 13.174 | 18.1824 | 25.2049 | 35.0752 | 48.9779 | 68.5978 | 96.333 |  | 0 | 0 | 0 | 0.19038 | 0.87053 | 1.8172 | 3.1414 | 5.0024 | 7.6281 | 11.3468 | 16.6306 | 24.1602 | 34.9183 | 50.3247 | 72.4332 | 104.2173 | 149.9851 | 215.6263 | 310.2106 | 326.0296 | 324.6944 | 322.846 | 320.2772 | 316.6958 | 311.6875 | 304.665 | 294.7947 | 280.892 | 261.2721 | 233.5368 |  | 0 | 0 | 0 | 3.4779 | 15.9028 | 33.1964 | 57.388 | 91.3833 | 139.3514 | 207.2846 | 303.8092 | 441.3611 | 637.8902 | 919.3352 | 1323.2155 | 1903.8495 | 2739.9384 | 3939.0773 | 5666.9499 | 5955.9321 | 5931.5421 | 5897.7737 | 5850.8484 | 5785.4226 | 5693.9301 | 5565.6424 | 5385.3307 | 5131.3549 | 4772.9375 | 4266.2682
| FALSE | 3812 | 22011645 | SHL | SHL007 | 22 | SHL7 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 2.5292 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 3.6203 |  | 8.8804 | 0.037562 | 2.9553e-05 | 0.037533 | 103.305 | 2.0687 | 105.3737 | 106.7933 | 15.029 | 26.314 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 3.6203 |  | 34.8785 | 253.51 | 34.8785 | 218.6315 |  | 0.12559 |  | 2.8677 | 3.2514 | 3.6865 | 4.1799 | 4.7392 | 5.3734 | 6.0925 | 6.9078 | 7.8322 | 8.8804 | 10.0687 | 11.4161 | 12.9438 | 14.676 | 16.64 | 18.8667 | 21.3915 | 24.2541 | 27.4998 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0057115 | 0.0076532 | 0.010356 | 0.014137 | 0.019449 | 0.026946 | 0.037562 | 0.052647 | 0.074144 | 0.10486 | 0.14884 | 0.21196 | 0.3027 | 0.43337 | 0.62179 | 0.89383 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.4936e-06 | 6.0213e-06 | 8.1476e-06 | 1.1122e-05 | 1.5302e-05 | 2.12e-05 | 2.9553e-05 | 4.1421e-05 | 5.8334e-05 | 8.2498e-05 | 0.0001171 | 0.00016676 | 0.00023816 | 0.00034096 | 0.0004892 | 0.00070323 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 34.8785 | 34.8785 | 34.8785 | 38.5468 | 51.6519 | 69.8921 | 95.4079 | 131.2641 | 181.8581 | 253.51 | 355.3183 | 500.3998 | 707.687 | 1004.5384 | 1430.5272 | 2042.9453 | 2924.802 | 4196.451 | 6032.4991 | 6355.9569 | 6355.9569 | 6355.9569 | 6355.9569 | 6355.9569 | 6355.9569 | 6355.9569 | 6355.9569 | 6355.9569 | 6355.9569 | 6355.9569 |  | 34.8785 | 34.8785 | 34.8785 | 34.8785 | 34.8785 | 34.8785 | 34.8785 | 34.8785 | 34.8785 | 34.8785 | 34.8785 | 34.8785 | 34.8785 | 34.8785 | 34.8785 | 34.8785 | 34.8785 | 41.7474 | 55.3386 | 73.9952 | 99.7204 | 135.3373 | 184.8313 | 253.8385 | 350.3393 | 485.6495 | 675.8316 | 943.7101 | 1321.7474 | 1856.1519 |  | 14.2129 | 14.2129 | 14.2129 | 15.7078 | 21.0481 | 28.4809 | 38.8786 | 53.49 | 74.1069 | 103.305 | 144.7918 | 203.9122 | 288.3815 | 409.3481 | 582.9379 | 832.4975 | 1191.8529 | 1710.0482 | 2458.2353 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 1.4948 | 6.8351 | 14.268 | 24.6657 | 39.277 | 59.894 | 89.092 | 130.5788 | 189.6993 | 274.1686 | 395.1351 | 568.725 | 818.2845 | 1177.64 | 1693.0362 | 2435.6849 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.31455 | 0.42149 | 0.57033 | 0.77855 | 1.0711 | 1.484 | 2.0687 | 2.8995 | 4.0834 | 5.7749 | 8.1972 | 11.6734 | 16.6709 | 23.867 | 34.2439 | 49.2264 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0.029934 | 0.13687 | 0.28572 | 0.49393 | 0.78653 | 1.1994 | 1.7841 | 2.6149 | 3.7987 | 5.4903 | 7.9126 | 11.3888 | 16.3862 | 23.5824 | 33.9032 | 48.7749 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 1.5248 | 6.972 | 14.5537 | 25.1596 | 40.0635 | 61.0934 | 90.8761 | 133.1937 | 193.4981 | 279.6588 | 403.0477 | 580.1137 | 834.6708 | 1201.2223 | 1726.9394 | 2484.4597 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 16.2382 | 21.7588 | 29.4427 | 40.1914 | 55.2962 | 76.6093 | 106.7933 | 149.6809 | 210.7977 | 298.1193 | 423.1705 | 602.6219 | 860.6083 | 1232.0981 | 1767.7912 | 2541.2423 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 1.5453 | 7.0659 | 14.7498 | 25.4985 | 40.6033 | 61.9164 | 92.1004 | 134.9881 | 196.1049 | 283.4264 | 408.4776 | 587.9291 | 845.9155 | 1217.4052 | 1750.2048 | 2517.9304 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.2852 | 3.0621 | 4.1435 | 5.6561 | 7.7818 | 10.7812 | 15.029 | 21.0646 | 29.6656 | 41.9544 | 59.5529 | 84.8072 | 121.1137 | 173.3935 | 248.7818 | 357.6298 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0.21747 | 0.99439 | 2.0757 | 3.5884 | 5.7141 | 8.7135 | 12.9613 | 18.9969 | 27.5979 | 39.8867 | 57.4852 | 82.7394 | 119.0459 | 171.3258 | 246.3068 | 354.3491 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 3.6203 | 3.6203 | 3.6203 | 4.0011 | 5.3614 | 7.2547 | 9.9032 | 13.625 | 18.8766 | 26.314 | 36.8816 | 51.9408 | 73.457 | 104.2697 | 148.4868 | 212.055 | 303.5905 | 435.5859 | 626.1653 | 659.7397 | 659.7397 | 659.7397 | 659.7397 | 659.7397 | 659.7397 | 659.7397 | 659.7397 | 659.7397 | 659.7397 | 659.7397 |  | 3.6203 | 3.6203 | 3.6203 | 3.6203 | 3.6203 | 3.6203 | 3.6203 | 3.6203 | 3.6203 | 3.6203 | 3.6203 | 3.6203 | 3.6203 | 3.6203 | 3.6203 | 3.6203 | 3.6203 | 4.3333 | 5.7441 | 7.6806 | 10.3508 | 14.0478 | 19.1852 | 26.3481 | 36.3647 | 50.4098 | 70.1504 | 97.9558 | 137.1956 | 192.6661 |  | 0 | 0 | 0 | 0.38076 | 1.7411 | 3.6344 | 6.2829 | 10.0047 | 15.2563 | 22.6936 | 33.2612 | 48.3205 | 69.8366 | 100.6494 | 144.8664 | 208.4346 | 299.9702 | 431.2526 | 620.4212 | 652.0591 | 649.3889 | 645.6919 | 640.5545 | 633.3916 | 623.375 | 609.33 | 589.5893 | 561.7839 | 522.5441 | 467.0737 |  | 0 | 0 | 0 | 3.6683 | 16.7734 | 35.0136 | 60.5294 | 96.3856 | 146.9796 | 218.6315 | 320.4398 | 465.5213 | 672.8085 | 969.6599 | 1395.6487 | 2008.0668 | 2889.9235 | 4154.7037 | 5977.1604 | 6281.9617 | 6256.2365 | 6220.6197 | 6171.1256 | 6102.1185 | 6005.6176 | 5870.3074 | 5680.1253 | 5412.2469 | 5034.2096 | 4499.8051
| FALSE | 3813 | 22011643 | SHL | SHL008 | 22 | SHL8 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 2.5292 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 2.6229 |  | 8.8804 | 0.037562 | 2.9553e-05 | 0.037533 | 103.305 | 2.0687 | 105.3737 | 106.7933 | 15.029 | 19.0639 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 2.6229 |  | 33.881 | 246.2599 | 33.881 | 212.3789 |  | 0.12559 |  | 2.8677 | 3.2514 | 3.6865 | 4.1799 | 4.7392 | 5.3734 | 6.0925 | 6.9078 | 7.8322 | 8.8804 | 10.0687 | 11.4161 | 12.9438 | 14.676 | 16.64 | 18.8667 | 21.3915 | 24.2541 | 27.4998 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0057115 | 0.0076532 | 0.010356 | 0.014137 | 0.019449 | 0.026946 | 0.037562 | 0.052647 | 0.074144 | 0.10486 | 0.14884 | 0.21196 | 0.3027 | 0.43337 | 0.62179 | 0.89383 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.4936e-06 | 6.0213e-06 | 8.1476e-06 | 1.1122e-05 | 1.5302e-05 | 2.12e-05 | 2.9553e-05 | 4.1421e-05 | 5.8334e-05 | 8.2498e-05 | 0.0001171 | 0.00016676 | 0.00023816 | 0.00034096 | 0.0004892 | 0.00070323 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 33.881 | 33.881 | 33.881 | 37.4444 | 50.1747 | 67.8933 | 92.6794 | 127.5102 | 176.6572 | 246.2599 | 345.1567 | 486.089 | 687.4481 | 975.8099 | 1389.6159 | 1984.5197 | 2841.1564 | 4076.4379 | 5859.9773 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 | 6174.1847 |  | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 33.881 | 40.5535 | 53.756 | 71.8791 | 96.8685 | 131.4668 | 179.5454 | 246.579 | 340.3201 | 471.7606 | 656.5037 | 916.7212 | 1283.9471 | 1803.0683 |  | 14.2129 | 14.2129 | 14.2129 | 15.7078 | 21.0481 | 28.4809 | 38.8786 | 53.49 | 74.1069 | 103.305 | 144.7918 | 203.9122 | 288.3815 | 409.3481 | 582.9379 | 832.4975 | 1191.8529 | 1710.0482 | 2458.2353 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 1.4948 | 6.8351 | 14.268 | 24.6657 | 39.277 | 59.894 | 89.092 | 130.5788 | 189.6993 | 274.1686 | 395.1351 | 568.725 | 818.2845 | 1177.64 | 1693.0362 | 2435.6849 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.31455 | 0.42149 | 0.57033 | 0.77855 | 1.0711 | 1.484 | 2.0687 | 2.8995 | 4.0834 | 5.7749 | 8.1972 | 11.6734 | 16.6709 | 23.867 | 34.2439 | 49.2264 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0.029934 | 0.13687 | 0.28572 | 0.49393 | 0.78653 | 1.1994 | 1.7841 | 2.6149 | 3.7987 | 5.4903 | 7.9126 | 11.3888 | 16.3862 | 23.5824 | 33.9032 | 48.7749 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 1.5248 | 6.972 | 14.5537 | 25.1596 | 40.0635 | 61.0934 | 90.8761 | 133.1937 | 193.4981 | 279.6588 | 403.0477 | 580.1137 | 834.6708 | 1201.2223 | 1726.9394 | 2484.4597 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 16.2382 | 21.7588 | 29.4427 | 40.1914 | 55.2962 | 76.6093 | 106.7933 | 149.6809 | 210.7977 | 298.1193 | 423.1705 | 602.6219 | 860.6083 | 1232.0981 | 1767.7912 | 2541.2423 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 1.5453 | 7.0659 | 14.7498 | 25.4985 | 40.6033 | 61.9164 | 92.1004 | 134.9881 | 196.1049 | 283.4264 | 408.4776 | 587.9291 | 845.9155 | 1217.4052 | 1750.2048 | 2517.9304 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.2852 | 3.0621 | 4.1435 | 5.6561 | 7.7818 | 10.7812 | 15.029 | 21.0646 | 29.6656 | 41.9544 | 59.5529 | 84.8072 | 121.1137 | 173.3935 | 248.7818 | 357.6298 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0.21747 | 0.99439 | 2.0757 | 3.5884 | 5.7141 | 8.7135 | 12.9613 | 18.9969 | 27.5979 | 39.8867 | 57.4852 | 82.7394 | 119.0459 | 171.3258 | 246.3068 | 354.3491 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 2.6229 | 2.6229 | 2.6229 | 2.8987 | 3.8842 | 5.2559 | 7.1747 | 9.8711 | 13.6757 | 19.0639 | 26.7199 | 37.63 | 53.218 | 75.5412 | 107.5755 | 153.6293 | 219.9449 | 315.5728 | 453.6435 | 477.9675 | 477.9675 | 477.9675 | 477.9675 | 477.9675 | 477.9675 | 477.9675 | 477.9675 | 477.9675 | 477.9675 | 477.9675 |  | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 2.6229 | 3.1394 | 4.1615 | 5.5644 | 7.499 | 10.1774 | 13.8993 | 19.0886 | 26.3455 | 36.5208 | 50.8225 | 70.9669 | 99.3953 | 139.5825 |  | 0 | 0 | 0 | 0.27586 | 1.2614 | 2.633 | 4.5518 | 7.2482 | 11.0529 | 16.4411 | 24.0971 | 35.0072 | 50.5951 | 72.9183 | 104.9527 | 151.0065 | 217.322 | 312.4334 | 449.482 | 472.403 | 470.4685 | 467.7901 | 464.0682 | 458.8788 | 451.622 | 441.4467 | 427.145 | 407.0005 | 378.5722 | 338.385 |  | 0 | 0 | 0 | 3.5634 | 16.2937 | 34.0123 | 58.7984 | 93.6291 | 142.7761 | 212.3789 | 311.2757 | 452.208 | 653.567 | 941.9289 | 1355.7349 | 1950.6387 | 2807.2753 | 4035.8844 | 5806.2213 | 6102.3056 | 6077.3161 | 6042.7179 | 5994.6393 | 5927.6056 | 5833.8646 | 5702.4241 | 5517.681 | 5257.4635 | 4890.2376 | 4371.1164
| FALSE | 3814 | 22002546 | SHL | Blank | 22 | STN 120V BATTERY | DC SUPPLY SYSTEM UV | X | RMS | 2V731 | 2V731 | 2V73X | Electronic |  | 0 | 2190 |  | 2.1077 | 0.004397 | 0 | 0.004397 | 12.0918 | 0 | 12.0918 | 12.4815 | 1.7593 | 0 |  | 6.8646 | 0.016283 | 0 | 0.016283 | 44.779 | 0 | 44.779 | 46.222 | 6.5149 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 26.3326 | 97.516 | 30.9493 | 66.5667 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.0051322 | 0.0067681 | 0.0090017 | 0.012065 | 0.016283 | 0.022113 | 0.030196 | 0.041436 | 0.057108 | 0.079011 | 0.10969 | 0.15274 | 0.21325 | 0.29844 | 0.41853 | 0.58803 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.3326 | 26.3326 | 26.3326 | 26.3326 | 26.3326 | 30.7354 | 40.532 | 53.9086 | 72.2543 | 97.516 | 132.4273 | 180.8325 | 248.1457 | 342.0011 | 473.1758 | 656.8995 | 914.7131 | 1277.1095 | 1787.285 | 2506.4719 | 3521.5195 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 12.0918 | 12.0918 | 12.0918 | 12.0918 | 12.0918 | 14.1136 | 18.6122 | 24.7547 | 33.179 | 44.779 | 60.8102 | 83.0377 | 113.9477 | 157.0458 | 217.2809 | 301.6462 | 420.0334 | 586.4447 | 820.7158 | 1150.9642 | 1617.0709 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | -2.12 | -2.12 | -2.12 | -2.12 | -2.12 | -0.098212 | 4.4003 | 10.5429 | 18.9671 | 30.5672 | 46.5984 | 68.8259 | 99.7359 | 142.834 | 203.0691 | 287.4344 | 405.8216 | 569.4341 | 798.1671 | 1120.8136 | 1576.4382 | 2148.3689 | 2128.2017 | 2100.0836 | 2060.7628 | 2005.6284 | 1928.1355 | 1818.984 | 1664.9464 | 1447.1944 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -2.12 | -2.12 | -2.12 | -2.12 | -2.12 | -0.098212 | 4.4003 | 10.5429 | 18.9671 | 30.5672 | 46.5984 | 68.8259 | 99.7359 | 142.834 | 203.0691 | 287.4344 | 405.8216 | 569.4341 | 798.1671 | 1120.8136 | 1576.4382 | 2148.3689 | 2128.2017 | 2100.0836 | 2060.7628 | 2005.6284 | 1928.1355 | 1818.984 | 1664.9464 | 1447.1944 |  | 12.4815 | 12.4815 | 12.4815 | 12.4815 | 12.4815 | 14.5684 | 19.2119 | 25.5524 | 34.2481 | 46.222 | 62.7697 | 85.7135 | 117.6196 | 162.1065 | 224.2825 | 311.3665 | 433.5686 | 605.3423 | 847.1625 | 1188.0529 | 1669.1794 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | -2.1883 | -2.1883 | -2.1883 | -2.1883 | -2.1883 | -0.10138 | 4.5421 | 10.8826 | 19.5783 | 31.5522 | 48.1 | 71.0437 | 102.9498 | 147.4367 | 209.6128 | 296.6967 | 418.8988 | 587.7835 | 823.8873 | 1156.9307 | 1627.2373 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 1.7593 | 1.7593 | 1.7593 | 1.7593 | 1.7593 | 2.0534 | 2.7079 | 3.6016 | 4.8272 | 6.5149 | 8.8473 | 12.0812 | 16.5784 | 22.8487 | 31.6124 | 43.8868 | 61.111 | 85.3224 | 119.4067 | 167.4548 | 235.2691 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | -0.30844 | -0.30844 | -0.30844 | -0.30844 | -0.30844 | -0.014289 | 0.64021 | 1.5339 | 2.7595 | 4.4473 | 6.7796 | 10.0135 | 14.5107 | 20.781 | 29.5447 | 41.8191 | 59.0434 | 82.8475 | 116.1261 | 163.0682 | 229.3574 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -4.6167 | -4.6167 | -4.6167 | -4.6167 | -4.6167 | -0.21388 | 9.5827 | 22.9593 | 41.305 | 66.5667 | 101.478 | 149.8832 | 217.1964 | 311.0518 | 442.2265 | 625.9502 | 883.7638 | 1240.0651 | 1738.1805 | 2440.8125 | 3433.033 | 4678.5351 | 4634.6167 | 4573.3835 | 4487.7538 | 4367.6869 | 4198.9295 | 3961.2286 | 3625.7787 | 3151.5769
| FALSE | 3815 | 22011634 | SHL | Blank | 22 | STN 120V BATTERY | DC SUPPLY SYSTEM UV | Y | RMS | 2V731 | 2V731 | 2V73X | Electronic |  | 0 | 2190 |  | 2.1077 | 0.004397 | 0 | 0.004397 | 12.0918 | 0 | 12.0918 | 12.4815 | 1.7593 | 0 |  | 6.8646 | 0.016283 | 0 | 0.016283 | 44.779 | 0 | 44.779 | 46.222 | 6.5149 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 26.3326 | 97.516 | 30.9493 | 66.5667 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.0051322 | 0.0067681 | 0.0090017 | 0.012065 | 0.016283 | 0.022113 | 0.030196 | 0.041436 | 0.057108 | 0.079011 | 0.10969 | 0.15274 | 0.21325 | 0.29844 | 0.41853 | 0.58803 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.3326 | 26.3326 | 26.3326 | 26.3326 | 26.3326 | 30.7354 | 40.532 | 53.9086 | 72.2543 | 97.516 | 132.4273 | 180.8325 | 248.1457 | 342.0011 | 473.1758 | 656.8995 | 914.7131 | 1277.1095 | 1787.285 | 2506.4719 | 3521.5195 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 12.0918 | 12.0918 | 12.0918 | 12.0918 | 12.0918 | 14.1136 | 18.6122 | 24.7547 | 33.179 | 44.779 | 60.8102 | 83.0377 | 113.9477 | 157.0458 | 217.2809 | 301.6462 | 420.0334 | 586.4447 | 820.7158 | 1150.9642 | 1617.0709 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | -2.12 | -2.12 | -2.12 | -2.12 | -2.12 | -0.098212 | 4.4003 | 10.5429 | 18.9671 | 30.5672 | 46.5984 | 68.8259 | 99.7359 | 142.834 | 203.0691 | 287.4344 | 405.8216 | 569.4341 | 798.1671 | 1120.8136 | 1576.4382 | 2148.3689 | 2128.2017 | 2100.0836 | 2060.7628 | 2005.6284 | 1928.1355 | 1818.984 | 1664.9464 | 1447.1944 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -2.12 | -2.12 | -2.12 | -2.12 | -2.12 | -0.098212 | 4.4003 | 10.5429 | 18.9671 | 30.5672 | 46.5984 | 68.8259 | 99.7359 | 142.834 | 203.0691 | 287.4344 | 405.8216 | 569.4341 | 798.1671 | 1120.8136 | 1576.4382 | 2148.3689 | 2128.2017 | 2100.0836 | 2060.7628 | 2005.6284 | 1928.1355 | 1818.984 | 1664.9464 | 1447.1944 |  | 12.4815 | 12.4815 | 12.4815 | 12.4815 | 12.4815 | 14.5684 | 19.2119 | 25.5524 | 34.2481 | 46.222 | 62.7697 | 85.7135 | 117.6196 | 162.1065 | 224.2825 | 311.3665 | 433.5686 | 605.3423 | 847.1625 | 1188.0529 | 1669.1794 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | -2.1883 | -2.1883 | -2.1883 | -2.1883 | -2.1883 | -0.10138 | 4.5421 | 10.8826 | 19.5783 | 31.5522 | 48.1 | 71.0437 | 102.9498 | 147.4367 | 209.6128 | 296.6967 | 418.8988 | 587.7835 | 823.8873 | 1156.9307 | 1627.2373 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 1.7593 | 1.7593 | 1.7593 | 1.7593 | 1.7593 | 2.0534 | 2.7079 | 3.6016 | 4.8272 | 6.5149 | 8.8473 | 12.0812 | 16.5784 | 22.8487 | 31.6124 | 43.8868 | 61.111 | 85.3224 | 119.4067 | 167.4548 | 235.2691 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | -0.30844 | -0.30844 | -0.30844 | -0.30844 | -0.30844 | -0.014289 | 0.64021 | 1.5339 | 2.7595 | 4.4473 | 6.7796 | 10.0135 | 14.5107 | 20.781 | 29.5447 | 41.8191 | 59.0434 | 82.8475 | 116.1261 | 163.0682 | 229.3574 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -4.6167 | -4.6167 | -4.6167 | -4.6167 | -4.6167 | -0.21388 | 9.5827 | 22.9593 | 41.305 | 66.5667 | 101.478 | 149.8832 | 217.1964 | 311.0518 | 442.2265 | 625.9502 | 883.7638 | 1240.0651 | 1738.1805 | 2440.8125 | 3433.033 | 4678.5351 | 4634.6167 | 4573.3835 | 4487.7538 | 4367.6869 | 4198.9295 | 3961.2286 | 3625.7787 | 3151.5769
| FALSE | 3816 | 22002545 | SHL | Blank | 22 | STN 24V BATTERY | 24 V BATT U/V RELAY | C | RMS | 2V731 | 2V731 | 2V73X | Electronic |  | 0 | 2190 |  | 2.1077 | 0.004397 | 0 | 0.004397 | 12.0918 | 0 | 12.0918 | 12.4815 | 1.7593 | 0 |  | 6.8646 | 0.016283 | 0 | 0.016283 | 44.779 | 0 | 44.779 | 46.222 | 6.5149 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 26.3326 | 97.516 | 30.9493 | 66.5667 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.0051322 | 0.0067681 | 0.0090017 | 0.012065 | 0.016283 | 0.022113 | 0.030196 | 0.041436 | 0.057108 | 0.079011 | 0.10969 | 0.15274 | 0.21325 | 0.29844 | 0.41853 | 0.58803 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.3326 | 26.3326 | 26.3326 | 26.3326 | 26.3326 | 30.7354 | 40.532 | 53.9086 | 72.2543 | 97.516 | 132.4273 | 180.8325 | 248.1457 | 342.0011 | 473.1758 | 656.8995 | 914.7131 | 1277.1095 | 1787.285 | 2506.4719 | 3521.5195 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 | 4798.6261 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 12.0918 | 12.0918 | 12.0918 | 12.0918 | 12.0918 | 14.1136 | 18.6122 | 24.7547 | 33.179 | 44.779 | 60.8102 | 83.0377 | 113.9477 | 157.0458 | 217.2809 | 301.6462 | 420.0334 | 586.4447 | 820.7158 | 1150.9642 | 1617.0709 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 | 2203.5143 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | -2.12 | -2.12 | -2.12 | -2.12 | -2.12 | -0.098212 | 4.4003 | 10.5429 | 18.9671 | 30.5672 | 46.5984 | 68.8259 | 99.7359 | 142.834 | 203.0691 | 287.4344 | 405.8216 | 569.4341 | 798.1671 | 1120.8136 | 1576.4382 | 2148.3689 | 2128.2017 | 2100.0836 | 2060.7628 | 2005.6284 | 1928.1355 | 1818.984 | 1664.9464 | 1447.1944 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -2.12 | -2.12 | -2.12 | -2.12 | -2.12 | -0.098212 | 4.4003 | 10.5429 | 18.9671 | 30.5672 | 46.5984 | 68.8259 | 99.7359 | 142.834 | 203.0691 | 287.4344 | 405.8216 | 569.4341 | 798.1671 | 1120.8136 | 1576.4382 | 2148.3689 | 2128.2017 | 2100.0836 | 2060.7628 | 2005.6284 | 1928.1355 | 1818.984 | 1664.9464 | 1447.1944 |  | 12.4815 | 12.4815 | 12.4815 | 12.4815 | 12.4815 | 14.5684 | 19.2119 | 25.5524 | 34.2481 | 46.222 | 62.7697 | 85.7135 | 117.6196 | 162.1065 | 224.2825 | 311.3665 | 433.5686 | 605.3423 | 847.1625 | 1188.0529 | 1669.1794 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | -2.1883 | -2.1883 | -2.1883 | -2.1883 | -2.1883 | -0.10138 | 4.5421 | 10.8826 | 19.5783 | 31.5522 | 48.1 | 71.0437 | 102.9498 | 147.4367 | 209.6128 | 296.6967 | 418.8988 | 587.7835 | 823.8873 | 1156.9307 | 1627.2373 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 1.7593 | 1.7593 | 1.7593 | 1.7593 | 1.7593 | 2.0534 | 2.7079 | 3.6016 | 4.8272 | 6.5149 | 8.8473 | 12.0812 | 16.5784 | 22.8487 | 31.6124 | 43.8868 | 61.111 | 85.3224 | 119.4067 | 167.4548 | 235.2691 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | -0.30844 | -0.30844 | -0.30844 | -0.30844 | -0.30844 | -0.014289 | 0.64021 | 1.5339 | 2.7595 | 4.4473 | 6.7796 | 10.0135 | 14.5107 | 20.781 | 29.5447 | 41.8191 | 59.0434 | 82.8475 | 116.1261 | 163.0682 | 229.3574 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -4.6167 | -4.6167 | -4.6167 | -4.6167 | -4.6167 | -0.21388 | 9.5827 | 22.9593 | 41.305 | 66.5667 | 101.478 | 149.8832 | 217.1964 | 311.0518 | 442.2265 | 625.9502 | 883.7638 | 1240.0651 | 1738.1805 | 2440.8125 | 3433.033 | 4678.5351 | 4634.6167 | 4573.3835 | 4487.7538 | 4367.6869 | 4198.9295 | 3961.2286 | 3625.7787 | 3151.5769
| FALSE | 3817 | 22011636 | SHL | Blank | 22 | TRANS NO.1 | METER (DIGITAL MULTI FN.) | I | Schneider | ION_6200 | ION 6200 | ION 6000s | Digital |  | 0 | 1 |  | 2.1077 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 6.8646 | 0.019138 | 0 | 0.019138 | 100.4751 | 0 | 100.4751 | 54.3258 | 7.6572 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 162.458 | 43.8691 | 118.5889 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.006032 | 0.0079547 | 0.01058 | 0.01418 | 0.019138 | 0.02599 | 0.035489 | 0.0487 | 0.06712 | 0.092864 | 0.12892 | 0.17952 | 0.25064 | 0.35077 | 0.49191 | 0.69112 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 51.2041 | 67.5248 | 89.8098 | 120.3731 | 162.458 | 220.6189 | 301.2602 | 413.4015 | 569.7611 | 788.2935 | 1094.3703 | 1523.8783 | 2127.6172 | 2977.5507 | 4175.6897 | 5866.7214 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 31.6681 | 41.7619 | 55.5445 | 74.4469 | 100.4751 | 136.4458 | 186.3198 | 255.6756 | 352.3791 | 487.5343 | 676.8331 | 942.4701 | 1315.8633 | 1841.5201 | 2582.5308 | 3628.38 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 4.5364 | 14.6303 | 28.4128 | 47.3152 | 73.3435 | 109.3141 | 159.1882 | 228.544 | 325.2474 | 460.4027 | 649.7015 | 915.3384 | 1283.3884 | 1798.4727 | 2524.9706 | 3550.8084 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 4.5364 | 14.6303 | 28.4128 | 47.3152 | 73.3435 | 109.3141 | 159.1882 | 228.544 | 325.2474 | 460.4027 | 649.7015 | 915.3384 | 1283.3884 | 1798.4727 | 2524.9706 | 3550.8084 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.1226 | 22.5802 | 30.0323 | 40.2526 | 54.3258 | 73.7747 | 100.741 | 138.2409 | 190.5274 | 263.6043 | 365.9561 | 509.583 | 711.4725 | 995.6892 | 1396.3454 | 1961.8243 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 2.4528 | 7.9104 | 15.3625 | 25.5828 | 39.656 | 59.1049 | 86.0713 | 123.5712 | 175.8576 | 248.9346 | 351.2863 | 494.9132 | 693.9137 | 972.414 | 1365.2232 | 1919.8822 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4134 | 3.1827 | 4.233 | 5.6736 | 7.6572 | 10.3985 | 14.1993 | 19.4849 | 26.8546 | 37.1548 | 51.5811 | 71.8252 | 100.2813 | 140.3414 | 196.8134 | 276.5171 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0.34572 | 1.115 | 2.1653 | 3.6059 | 5.5895 | 8.3308 | 12.1317 | 17.4172 | 24.787 | 35.0871 | 49.5134 | 69.7575 | 97.8064 | 137.0607 | 192.4268 | 270.6054 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 7.3349 | 23.6556 | 45.9406 | 76.5039 | 118.5889 | 176.7498 | 257.3911 | 369.5324 | 525.892 | 744.4243 | 1050.5012 | 1480.0091 | 2075.1086 | 2907.9475 | 4082.6206 | 5741.296 | 7824.1106 | 7761.8584 | 7675.0633 | 7553.6874 | 7383.4983 | 7144.2929 | 6807.3633 | 6331.8792 | 5659.7211
| FALSE | 3818 | 22011637 | SHL | Blank | 22 | TRANS NO.2 | METER (DIGITAL MULTI FN.) | I | Schneider | ION_6200 | ION 6200 | ION 6000s | Digital |  | 0 | 1 |  | 2.1077 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 6.8646 | 0.019138 | 0 | 0.019138 | 100.4751 | 0 | 100.4751 | 54.3258 | 7.6572 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 162.458 | 43.8691 | 118.5889 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.006032 | 0.0079547 | 0.01058 | 0.01418 | 0.019138 | 0.02599 | 0.035489 | 0.0487 | 0.06712 | 0.092864 | 0.12892 | 0.17952 | 0.25064 | 0.35077 | 0.49191 | 0.69112 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 51.2041 | 67.5248 | 89.8098 | 120.3731 | 162.458 | 220.6189 | 301.2602 | 413.4015 | 569.7611 | 788.2935 | 1094.3703 | 1523.8783 | 2127.6172 | 2977.5507 | 4175.6897 | 5866.7214 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 31.6681 | 41.7619 | 55.5445 | 74.4469 | 100.4751 | 136.4458 | 186.3198 | 255.6756 | 352.3791 | 487.5343 | 676.8331 | 942.4701 | 1315.8633 | 1841.5201 | 2582.5308 | 3628.38 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 4.5364 | 14.6303 | 28.4128 | 47.3152 | 73.3435 | 109.3141 | 159.1882 | 228.544 | 325.2474 | 460.4027 | 649.7015 | 915.3384 | 1283.3884 | 1798.4727 | 2524.9706 | 3550.8084 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 4.5364 | 14.6303 | 28.4128 | 47.3152 | 73.3435 | 109.3141 | 159.1882 | 228.544 | 325.2474 | 460.4027 | 649.7015 | 915.3384 | 1283.3884 | 1798.4727 | 2524.9706 | 3550.8084 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.1226 | 22.5802 | 30.0323 | 40.2526 | 54.3258 | 73.7747 | 100.741 | 138.2409 | 190.5274 | 263.6043 | 365.9561 | 509.583 | 711.4725 | 995.6892 | 1396.3454 | 1961.8243 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 2.4528 | 7.9104 | 15.3625 | 25.5828 | 39.656 | 59.1049 | 86.0713 | 123.5712 | 175.8576 | 248.9346 | 351.2863 | 494.9132 | 693.9137 | 972.414 | 1365.2232 | 1919.8822 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4134 | 3.1827 | 4.233 | 5.6736 | 7.6572 | 10.3985 | 14.1993 | 19.4849 | 26.8546 | 37.1548 | 51.5811 | 71.8252 | 100.2813 | 140.3414 | 196.8134 | 276.5171 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0.34572 | 1.115 | 2.1653 | 3.6059 | 5.5895 | 8.3308 | 12.1317 | 17.4172 | 24.787 | 35.0871 | 49.5134 | 69.7575 | 97.8064 | 137.0607 | 192.4268 | 270.6054 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 7.3349 | 23.6556 | 45.9406 | 76.5039 | 118.5889 | 176.7498 | 257.3911 | 369.5324 | 525.892 | 744.4243 | 1050.5012 | 1480.0091 | 2075.1086 | 2907.9475 | 4082.6206 | 5741.296 | 7824.1106 | 7761.8584 | 7675.0633 | 7553.6874 | 7383.4983 | 7144.2929 | 6807.3633 | 6331.8792 | 5659.7211
| FALSE | 3819 | 22011646 | SHL | Blank | 22 | TRANS NO.2 | WTI | C | Schweitzer | SEL_2414 | SEL 2414 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 2.1077 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.18876 |  | 6.8646 | 0.019138 | 1.7315e-06 | 0.019136 | 100.476 | 0.19047 | 100.6665 | 54.3356 | 7.6572 | 0.69901 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.18876 |  | 44.1122 | 163.3583 | 44.1122 | 119.246 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.006032 | 0.0079547 | 0.01058 | 0.01418 | 0.019138 | 0.02599 | 0.035489 | 0.0487 | 0.06712 | 0.092864 | 0.12892 | 0.17952 | 0.25064 | 0.35077 | 0.49191 | 0.69112 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.4574e-07 | 7.1969e-07 | 9.5721e-07 | 1.283e-06 | 1.7315e-06 | 2.3514e-06 | 3.2109e-06 | 4.4061e-06 | 6.0726e-06 | 8.4018e-06 | 1.1664e-05 | 1.6242e-05 | 2.2677e-05 | 3.1735e-05 | 4.4505e-05 | 6.2529e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 51.4878 | 67.899 | 90.3074 | 121.0401 | 163.3583 | 221.8414 | 302.9296 | 415.6923 | 572.9184 | 792.6617 | 1100.4346 | 1532.3226 | 2139.4071 | 2994.0504 | 4198.8286 | 5899.231 | 8038.6332 | 8038.6332 | 8038.6332 | 8038.6332 | 8038.6332 | 8038.6332 | 8038.6332 | 8038.6332 | 8038.6332 |  | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 52.7996 | 69.989 | 93.5847 | 126.1204 | 171.1664 | 233.7636 | 321.0397 | 443.0882 | 614.2204 | 854.7513 | 1193.5479 | 1671.6668 | 2347.5496 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 31.6684 | 41.7623 | 55.545 | 74.4476 | 100.476 | 136.447 | 186.3215 | 255.678 | 352.3823 | 487.5388 | 676.8393 | 942.4786 | 1315.8752 | 1841.5368 | 2582.5542 | 3628.4128 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 4.5365 | 14.6304 | 28.4131 | 47.3157 | 73.3441 | 109.3151 | 159.1896 | 228.546 | 325.2504 | 460.4068 | 649.7073 | 915.3467 | 1283.4 | 1798.489 | 2524.9934 | 3550.8405 | 4839.0065 | 4800.5052 | 4746.8247 | 4671.7569 | 4566.4994 | 4418.5572 | 4210.1751 | 3916.1007 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.060032 | 0.079166 | 0.10529 | 0.14113 | 0.19047 | 0.25865 | 0.3532 | 0.48467 | 0.66799 | 0.9242 | 1.283 | 1.7866 | 2.4944 | 3.4909 | 4.8956 | 6.8782 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0.0085995 | 0.027734 | 0.053861 | 0.089693 | 0.13903 | 0.20722 | 0.30177 | 0.43324 | 0.61656 | 0.87277 | 1.2316 | 1.7352 | 2.4329 | 3.4093 | 4.7865 | 6.7311 | 9.173 | 9.1 | 8.9983 | 8.856 | 8.6564 | 8.376 | 7.981 | 7.4235 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 4.5451 | 14.6581 | 28.4669 | 47.4053 | 73.4832 | 109.5223 | 159.4914 | 228.9793 | 325.8669 | 461.2796 | 650.939 | 917.0819 | 1285.8329 | 1801.8983 | 2529.7799 | 3557.5717 | 4848.1796 | 4809.6052 | 4755.823 | 4680.6129 | 4575.1558 | 4426.9331 | 4218.1561 | 3923.5242 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.1257 | 22.5843 | 30.0377 | 40.2599 | 54.3356 | 73.788 | 100.7593 | 138.266 | 190.5619 | 263.652 | 366.0223 | 509.6752 | 711.6013 | 995.8694 | 1396.5981 | 1962.1793 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 2.4532 | 7.9119 | 15.3653 | 25.5874 | 39.6632 | 59.1156 | 86.0868 | 123.5935 | 175.8894 | 248.9796 | 351.3499 | 495.0028 | 694.0393 | 972.59 | 1365.4703 | 1920.2296 | 2616.8462 | 2596.0254 | 2566.996 | 2526.4007 | 2469.4794 | 2389.4749 | 2276.7857 | 2117.7556 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4134 | 3.1827 | 4.233 | 5.6736 | 7.6572 | 10.3985 | 14.1994 | 19.485 | 26.8547 | 37.1548 | 51.5812 | 71.8254 | 100.2815 | 140.3417 | 196.8139 | 276.5177 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0.34572 | 1.115 | 2.1653 | 3.6059 | 5.5895 | 8.3308 | 12.1317 | 17.4173 | 24.787 | 35.0871 | 49.5136 | 69.7577 | 97.8066 | 137.0611 | 192.4272 | 270.606 | 368.7759 | 365.8417 | 361.7508 | 356.03 | 348.0084 | 336.7339 | 320.8533 | 298.4421 | 266.7611 |  | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.22032 | 0.29054 | 0.38643 | 0.51793 | 0.69901 | 0.94927 | 1.2962 | 1.7788 | 2.4515 | 3.3918 | 4.7088 | 6.5568 | 9.1546 | 12.8116 | 17.9669 | 25.243 | 34.3975 | 34.3975 | 34.3975 | 34.3975 | 34.3975 | 34.3975 | 34.3975 | 34.3975 | 34.3975 |  | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.22593 | 0.29948 | 0.40045 | 0.53967 | 0.73243 | 1.0003 | 1.3737 | 1.896 | 2.6283 | 3.6575 | 5.1072 | 7.1531 | 10.0452 |  | 0 | 0 | 0 | 0 | 0 | 0.03156 | 0.10178 | 0.19767 | 0.32918 | 0.51026 | 0.76051 | 1.1075 | 1.59 | 2.2628 | 3.2031 | 4.52 | 6.3681 | 8.9286 | 12.5121 | 17.5664 | 24.7033 | 33.6651 | 33.3972 | 33.0238 | 32.5015 | 31.7693 | 30.74 | 29.2903 | 27.2444 | 24.3523 |  | 0 | 0 | 0 | 0 | 0 | 7.3756 | 23.7867 | 46.1952 | 76.9278 | 119.246 | 177.7292 | 258.8174 | 371.5801 | 528.8061 | 748.5494 | 1056.3224 | 1488.2104 | 2086.6075 | 2924.0614 | 4105.2439 | 5773.1106 | 7867.4668 | 7804.8696 | 7717.5935 | 7595.545 | 7424.4128 | 7183.8819 | 6845.0853 | 6366.9664 | 5691.0837
| FALSE | 3820 | 22011638 | SHL | Blank | 22 | TRANS NO.3 | METER (DIGITAL MULTI FN.) | I | Schneider | ION_6200 | ION 6200 | ION 6000s | Digital |  | 0 | 1 |  | 2.1077 | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 6.8646 | 0.019138 | 0 | 0.019138 | 100.4751 | 0 | 100.4751 | 54.3258 | 7.6572 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 43.8691 | 162.458 | 43.8691 | 118.5889 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.006032 | 0.0079547 | 0.01058 | 0.01418 | 0.019138 | 0.02599 | 0.035489 | 0.0487 | 0.06712 | 0.092864 | 0.12892 | 0.17952 | 0.25064 | 0.35077 | 0.49191 | 0.69112 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 51.2041 | 67.5248 | 89.8098 | 120.3731 | 162.458 | 220.6189 | 301.2602 | 413.4015 | 569.7611 | 788.2935 | 1094.3703 | 1523.8783 | 2127.6172 | 2977.5507 | 4175.6897 | 5866.7214 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 31.6681 | 41.7619 | 55.5445 | 74.4469 | 100.4751 | 136.4458 | 186.3198 | 255.6756 | 352.3791 | 487.5343 | 676.8331 | 942.4701 | 1315.8633 | 1841.5201 | 2582.5308 | 3628.38 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 0 | 0 | 0 | 0 | 0 | 4.5364 | 14.6303 | 28.4128 | 47.3152 | 73.3435 | 109.3141 | 159.1882 | 228.544 | 325.2474 | 460.4027 | 649.7015 | 915.3384 | 1283.3884 | 1798.4727 | 2524.9706 | 3550.8084 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 4.5364 | 14.6303 | 28.4128 | 47.3152 | 73.3435 | 109.3141 | 159.1882 | 228.544 | 325.2474 | 460.4027 | 649.7015 | 915.3384 | 1283.3884 | 1798.4727 | 2524.9706 | 3550.8084 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.1226 | 22.5802 | 30.0323 | 40.2526 | 54.3258 | 73.7747 | 100.741 | 138.2409 | 190.5274 | 263.6043 | 365.9561 | 509.583 | 711.4725 | 995.6892 | 1396.3454 | 1961.8243 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 2.4528 | 7.9104 | 15.3625 | 25.5828 | 39.656 | 59.1049 | 86.0713 | 123.5712 | 175.8576 | 248.9346 | 351.2863 | 494.9132 | 693.9137 | 972.414 | 1365.2232 | 1919.8822 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4134 | 3.1827 | 4.233 | 5.6736 | 7.6572 | 10.3985 | 14.1993 | 19.4849 | 26.8546 | 37.1548 | 51.5811 | 71.8252 | 100.2813 | 140.3414 | 196.8134 | 276.5171 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0.34572 | 1.115 | 2.1653 | 3.6059 | 5.5895 | 8.3308 | 12.1317 | 17.4172 | 24.787 | 35.0871 | 49.5134 | 69.7575 | 97.8064 | 137.0607 | 192.4268 | 270.6054 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 7.3349 | 23.6556 | 45.9406 | 76.5039 | 118.5889 | 176.7498 | 257.3911 | 369.5324 | 525.892 | 744.4243 | 1050.5012 | 1480.0091 | 2075.1086 | 2907.9475 | 4082.6206 | 5741.296 | 7824.1106 | 7761.8584 | 7675.0633 | 7553.6874 | 7383.4983 | 7144.2929 | 6807.3633 | 6331.8792 | 5659.7211
| FALSE | 3821 | 22011647 | SHL | Blank | 22 | TRANS NO.3 | WTI | C | Schweitzer | SEL_2414 | SEL 2414 | SEL 2000s | Digital |  | 0.066046 | 1 |  | 2.1077 | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.18876 |  | 6.8646 | 0.019138 | 1.7315e-06 | 0.019136 | 100.476 | 0.19047 | 100.6665 | 54.3356 | 7.6572 | 0.69901 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 27.1319 | 0.051432 | 27.1833 | 14.6724 | 2.0677 | 0.18876 |  | 44.1122 | 163.3583 | 44.1122 | 119.246 |  | 0.11808 |  | 2.3718 | 2.6691 | 3.0036 | 3.3801 | 3.8037 | 4.2805 | 4.8169 | 5.4207 | 6.1 | 6.8646 | 7.7249 | 8.6931 | 9.7826 | 11.0087 | 12.3884 | 13.9411 | 15.6884 | 17.6547 | 19.8674 | 22.3574 | 25.1595 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.006032 | 0.0079547 | 0.01058 | 0.01418 | 0.019138 | 0.02599 | 0.035489 | 0.0487 | 0.06712 | 0.092864 | 0.12892 | 0.17952 | 0.25064 | 0.35077 | 0.49191 | 0.69112 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 4.6757e-07 | 5.4574e-07 | 7.1969e-07 | 9.5721e-07 | 1.283e-06 | 1.7315e-06 | 2.3514e-06 | 3.2109e-06 | 4.4061e-06 | 6.0726e-06 | 8.4018e-06 | 1.1664e-05 | 1.6242e-05 | 2.2677e-05 | 3.1735e-05 | 4.4505e-05 | 6.2529e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 8.5205e-05 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 51.4878 | 67.899 | 90.3074 | 121.0401 | 163.3583 | 221.8414 | 302.9296 | 415.6923 | 572.9184 | 792.6617 | 1100.4346 | 1532.3226 | 2139.4071 | 2994.0504 | 4198.8286 | 5899.231 | 8038.6332 | 8038.6332 | 8038.6332 | 8038.6332 | 8038.6332 | 8038.6332 | 8038.6332 | 8038.6332 | 8038.6332 |  | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 44.1122 | 52.7996 | 69.989 | 93.5847 | 126.1204 | 171.1664 | 233.7636 | 321.0397 | 443.0882 | 614.2204 | 854.7513 | 1193.5479 | 1671.6668 | 2347.5496 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 31.6684 | 41.7623 | 55.545 | 74.4476 | 100.476 | 136.447 | 186.3215 | 255.678 | 352.3823 | 487.5388 | 676.8393 | 942.4786 | 1315.8752 | 1841.5368 | 2582.5542 | 3628.4128 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 | 4944.2851 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 0 | 0 | 0 | 0 | 0 | 4.5365 | 14.6304 | 28.4131 | 47.3157 | 73.3441 | 109.3151 | 159.1896 | 228.546 | 325.2504 | 460.4068 | 649.7073 | 915.3467 | 1283.4 | 1798.489 | 2524.9934 | 3550.8405 | 4839.0065 | 4800.5052 | 4746.8247 | 4671.7569 | 4566.4994 | 4418.5572 | 4210.1751 | 3916.1007 | 3500.3886 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.060032 | 0.079166 | 0.10529 | 0.14113 | 0.19047 | 0.25865 | 0.3532 | 0.48467 | 0.66799 | 0.9242 | 1.283 | 1.7866 | 2.4944 | 3.4909 | 4.8956 | 6.8782 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 | 9.3726 |  | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.051432 | 0.061561 | 0.081603 | 0.10911 | 0.14705 | 0.19957 | 0.27255 | 0.37431 | 0.51662 | 0.71615 | 0.99659 | 1.3916 | 1.9491 | 2.7371 |  | 0 | 0 | 0 | 0 | 0 | 0.0085995 | 0.027734 | 0.053861 | 0.089693 | 0.13903 | 0.20722 | 0.30177 | 0.43324 | 0.61656 | 0.87277 | 1.2316 | 1.7352 | 2.4329 | 3.4093 | 4.7865 | 6.7311 | 9.173 | 9.1 | 8.9983 | 8.856 | 8.6564 | 8.376 | 7.981 | 7.4235 | 6.6355 |  | 0 | 0 | 0 | 0 | 0 | 4.5451 | 14.6581 | 28.4669 | 47.4053 | 73.4832 | 109.5223 | 159.4914 | 228.9793 | 325.8669 | 461.2796 | 650.939 | 917.0819 | 1285.8329 | 1801.8983 | 2529.7799 | 3557.5717 | 4848.1796 | 4809.6052 | 4755.823 | 4680.6129 | 4575.1558 | 4426.9331 | 4218.1561 | 3923.5242 | 3507.0241 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.1257 | 22.5843 | 30.0377 | 40.2599 | 54.3356 | 73.788 | 100.7593 | 138.266 | 190.5619 | 263.652 | 366.0223 | 509.6752 | 711.6013 | 995.8694 | 1396.5981 | 1962.1793 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 | 2673.779 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 0 | 0 | 0 | 0 | 0 | 2.4532 | 7.9119 | 15.3653 | 25.5874 | 39.6632 | 59.1156 | 86.0868 | 123.5935 | 175.8894 | 248.9796 | 351.3499 | 495.0028 | 694.0393 | 972.59 | 1365.4703 | 1920.2296 | 2616.8462 | 2596.0254 | 2566.996 | 2526.4007 | 2469.4794 | 2389.4749 | 2276.7857 | 2117.7556 | 1892.9461 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4134 | 3.1827 | 4.233 | 5.6736 | 7.6572 | 10.3985 | 14.1994 | 19.485 | 26.8547 | 37.1548 | 51.5812 | 71.8254 | 100.2815 | 140.3417 | 196.8139 | 276.5177 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 | 376.7991 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 0 | 0 | 0 | 0 | 0 | 0.34572 | 1.115 | 2.1653 | 3.6059 | 5.5895 | 8.3308 | 12.1317 | 17.4173 | 24.787 | 35.0871 | 49.5136 | 69.7577 | 97.8066 | 137.0611 | 192.4272 | 270.606 | 368.7759 | 365.8417 | 361.7508 | 356.03 | 348.0084 | 336.7339 | 320.8533 | 298.4421 | 266.7611 |  | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.22032 | 0.29054 | 0.38643 | 0.51793 | 0.69901 | 0.94927 | 1.2962 | 1.7788 | 2.4515 | 3.3918 | 4.7088 | 6.5568 | 9.1546 | 12.8116 | 17.9669 | 25.243 | 34.3975 | 34.3975 | 34.3975 | 34.3975 | 34.3975 | 34.3975 | 34.3975 | 34.3975 | 34.3975 |  | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.22593 | 0.29948 | 0.40045 | 0.53967 | 0.73243 | 1.0003 | 1.3737 | 1.896 | 2.6283 | 3.6575 | 5.1072 | 7.1531 | 10.0452 |  | 0 | 0 | 0 | 0 | 0 | 0.03156 | 0.10178 | 0.19767 | 0.32918 | 0.51026 | 0.76051 | 1.1075 | 1.59 | 2.2628 | 3.2031 | 4.52 | 6.3681 | 8.9286 | 12.5121 | 17.5664 | 24.7033 | 33.6651 | 33.3972 | 33.0238 | 32.5015 | 31.7693 | 30.74 | 29.2903 | 27.2444 | 24.3523 |  | 0 | 0 | 0 | 0 | 0 | 7.3756 | 23.7867 | 46.1952 | 76.9278 | 119.246 | 177.7292 | 258.8174 | 371.5801 | 528.8061 | 748.5494 | 1056.3224 | 1488.2104 | 2086.6075 | 2924.0614 | 4105.2439 | 5773.1106 | 7867.4668 | 7804.8696 | 7717.5935 | 7595.545 | 7424.4128 | 7183.8819 | 6845.0853 | 6366.9664 | 5691.0837
| TRUE | 3822 | 22008205 | SHL | Blank | 66 | BUS ALL | TWO ZONE BUS DIST | X | Schweitzer | SEL_311B | SEL 311B | SEL 300s | Digital |  | 0.033587 | 1 |  | 6.6 | 0.017308 | 7.9633e-07 | 0.017307 | 90.8667 | 0.087597 | 90.9543 | 49.1349 | 6.9249 | 0.32148 |  | 15.598 | 0.17662 | 8.1263e-06 | 0.17661 | 927.2653 | 0.8939 | 928.1592 | 501.4057 | 70.6662 | 3.2806 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 27.1318 | 0.026155 | 27.1579 | 14.6711 | 2.0677 | 0.095991 |  | 147.3355 | 1503.5117 | 43.9928 | 1459.5189 |  | 0.086007 |  | 7.1928 | 7.8388 | 8.5428 | 9.3101 | 10.1463 | 11.0575 | 12.0507 | 13.133 | 14.3125 | 15.598 | 16.9989 | 18.5257 | 20.1895 | 22.0028 | 23.979 | 26.1326 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021585 | 0.027005 | 0.033883 | 0.042625 | 0.053753 | 0.067937 | 0.086039 | 0.10917 | 0.13875 | 0.17662 | 0.22515 | 0.28739 | 0.36726 | 0.46984 | 0.60168 | 0.7712 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 9.9315e-07 | 1.2425e-06 | 1.5589e-06 | 1.9612e-06 | 2.4732e-06 | 3.1258e-06 | 3.9587e-06 | 5.0228e-06 | 6.3838e-06 | 8.1263e-06 | 1.0359e-05 | 1.3223e-05 | 1.6898e-05 | 2.1618e-05 | 2.7683e-05 | 3.5483e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 183.7492 | 229.8832 | 288.4311 | 362.8501 | 457.5797 | 578.3249 | 732.4212 | 929.3051 | 1181.1221 | 1503.5117 | 1916.6208 | 2446.4125 | 3126.3574 | 3999.6182 | 5121.8733 | 6564.9656 | 8016.8618 | 8016.8618 | 8016.8618 | 8016.8618 | 8016.8618 | 8016.8618 | 8016.8618 | 8016.8618 | 8016.8618 | 8016.8618 | 8016.8618 | 8016.8618 | 8016.8618 | 8016.8618 |  | 43.9928 | 43.9928 | 43.9928 | 43.9928 | 43.9928 | 43.9928 | 43.9928 | 43.9928 | 43.9928 | 43.9928 | 43.9928 | 43.9928 | 43.9928 | 43.9928 | 43.9928 | 43.9928 | 43.9928 | 52.6566 | 69.7994 | 93.3313 | 125.7788 | 170.7029 | 233.1305 | 320.1702 | 441.8882 | 612.5569 | 852.4363 | 1190.3154 | 1667.1394 | 2341.1916 |  | 113.3242 | 141.7765 | 177.885 | 223.7816 | 282.2045 | 356.6721 | 451.7083 | 573.1331 | 728.4369 | 927.2653 | 1182.0433 | 1508.7833 | 1928.1277 | 2466.6965 | 3158.8282 | 4048.8308 | 4944.2631 | 4944.2631 | 4944.2631 | 4944.2631 | 4944.2631 | 4944.2631 | 4944.2631 | 4944.2631 | 4944.2631 | 4944.2631 | 4944.2631 | 4944.2631 | 4944.2631 | 4944.2631 |  | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 27.1318 | 32.4751 | 43.0476 | 57.5605 | 77.572 | 105.2781 | 143.7793 | 197.4595 | 272.527 | 377.784 | 525.7256 | 734.1068 | 1028.1799 | 1443.8901 |  | 86.1924 | 114.6448 | 150.7532 | 196.6498 | 255.0727 | 329.5403 | 424.5765 | 546.0013 | 701.3051 | 900.1335 | 1154.9115 | 1481.6515 | 1900.9959 | 2439.5647 | 3131.6964 | 4021.6991 | 4917.1313 | 4911.7881 | 4901.2155 | 4886.7026 | 4866.6912 | 4838.985 | 4800.4839 | 4746.8036 | 4671.7361 | 4566.4791 | 4418.5375 | 4210.1564 | 3916.0833 | 3500.373 |  | 0.10925 | 0.13667 | 0.17148 | 0.21573 | 0.27205 | 0.34384 | 0.43545 | 0.55251 | 0.70222 | 0.8939 | 1.1395 | 1.4545 | 1.8587 | 2.3779 | 3.0452 | 3.9031 | 4.7663 | 4.7663 | 4.7663 | 4.7663 | 4.7663 | 4.7663 | 4.7663 | 4.7663 | 4.7663 | 4.7663 | 4.7663 | 4.7663 | 4.7663 | 4.7663 |  | 0.026155 | 0.026155 | 0.026155 | 0.026155 | 0.026155 | 0.026155 | 0.026155 | 0.026155 | 0.026155 | 0.026155 | 0.026155 | 0.026155 | 0.026155 | 0.026155 | 0.026155 | 0.026155 | 0.026155 | 0.031306 | 0.041498 | 0.055489 | 0.07478 | 0.10149 | 0.13861 | 0.19035 | 0.26272 | 0.36419 | 0.50681 | 0.70769 | 0.99118 | 1.3919 |  | 0.083091 | 0.11052 | 0.14533 | 0.18957 | 0.24589 | 0.31768 | 0.4093 | 0.52635 | 0.67607 | 0.86774 | 1.1134 | 1.4283 | 1.8326 | 2.3518 | 3.019 | 3.877 | 4.7402 | 4.735 | 4.7248 | 4.7108 | 4.6916 | 4.6648 | 4.6277 | 4.576 | 4.5036 | 4.4021 | 4.2595 | 4.0586 | 3.7752 | 3.3744 |  | 86.2755 | 114.7553 | 150.8985 | 196.8394 | 255.3186 | 329.858 | 424.9858 | 546.5276 | 701.9812 | 901.0012 | 1156.0248 | 1483.0798 | 1902.8285 | 2441.9165 | 3134.7154 | 4025.576 | 4921.8715 | 4916.5231 | 4905.9404 | 4891.4135 | 4871.3827 | 4843.6499 | 4805.1116 | 4751.3796 | 4676.2397 | 4570.8812 | 4422.797 | 4214.215 | 3919.8584 | 3503.7474 |  | 61.2785 | 76.6637 | 96.1888 | 121.0068 | 152.5981 | 192.8654 | 244.255 | 309.9137 | 393.8921 | 501.4057 | 639.1734 | 815.8535 | 1042.6081 | 1333.8317 | 1708.0922 | 2189.3487 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 46.6074 | 61.9926 | 81.5177 | 106.3356 | 137.927 | 178.1943 | 229.5838 | 295.2426 | 379.221 | 486.7346 | 624.5022 | 801.1824 | 1027.937 | 1319.1605 | 1693.4211 | 2174.6776 | 2658.8701 | 2655.9808 | 2650.2638 | 2642.4162 | 2631.5953 | 2616.6136 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 8.6364 | 10.8047 | 13.5565 | 17.0542 | 21.5066 | 27.1817 | 34.4244 | 43.678 | 55.5136 | 70.6662 | 90.0826 | 114.9833 | 146.9412 | 187.9851 | 240.732 | 308.5584 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 6.5687 | 8.737 | 11.4888 | 14.9865 | 19.4389 | 25.114 | 32.3567 | 41.6104 | 53.4459 | 68.5985 | 88.0149 | 112.9156 | 144.8735 | 185.9174 | 238.6643 | 306.4907 | 374.7309 | 374.3237 | 373.518 | 372.412 | 370.8869 | 368.7755 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 0.40093 | 0.5016 | 0.62935 | 0.79173 | 0.99842 | 1.2619 | 1.5981 | 2.0277 | 2.5772 | 3.2806 | 4.182 | 5.338 | 6.8216 | 8.727 | 11.1758 | 14.3245 | 17.4925 | 17.4925 | 17.4925 | 17.4925 | 17.4925 | 17.4925 | 17.4925 | 17.4925 | 17.4925 | 17.4925 | 17.4925 | 17.4925 | 17.4925 | 17.4925 |  | 0.095991 | 0.095991 | 0.095991 | 0.095991 | 0.095991 | 0.095991 | 0.095991 | 0.095991 | 0.095991 | 0.095991 | 0.095991 | 0.095991 | 0.095991 | 0.095991 | 0.095991 | 0.095991 | 0.095991 | 0.11489 | 0.1523 | 0.20365 | 0.27445 | 0.37247 | 0.50868 | 0.6986 | 0.96419 | 1.3366 | 1.86 | 2.5972 | 3.6376 | 5.1084 |  | 0.30494 | 0.40561 | 0.53336 | 0.69574 | 0.90243 | 1.1659 | 1.5021 | 1.9317 | 2.4812 | 3.1846 | 4.086 | 5.242 | 6.7256 | 8.631 | 11.0798 | 14.2285 | 17.3965 | 17.3776 | 17.3402 | 17.2889 | 17.2181 | 17.1201 | 16.9838 | 16.7939 | 16.5283 | 16.1559 | 15.6325 | 14.8953 | 13.8549 | 12.3841 |  | 139.7565 | 185.8904 | 244.4384 | 318.8573 | 413.5869 | 534.3322 | 688.4285 | 885.3123 | 1137.1293 | 1459.5189 | 1872.628 | 2402.4198 | 3082.3646 | 3955.6254 | 5077.8806 | 6520.9729 | 7972.8691 | 7964.2053 | 7947.0624 | 7923.5306 | 7891.083 | 7846.159 | 7783.7313 | 7696.6916 | 7574.9737 | 7404.305 | 7164.4255 | 6826.5465 | 6349.7224 | 5675.6702
| FALSE | 3823 | 22012934 | SHL | Blank | 66 | CB A | CB MGMT & DIR EF | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.15703 | 1 |  | 1.7651 | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.44878 |  | 7.1689 | 0.021401 | 4.6035e-06 | 0.021396 | 112.3566 | 0.50638 | 112.863 | 60.7748 | 8.5625 | 1.8584 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.44878 |  | 44.4471 | 184.0587 | 44.4471 | 139.6116 |  | 0.14015 |  | 2.0307 | 2.3362 | 2.6877 | 3.0921 | 3.5573 | 4.0924 | 4.7082 | 5.4165 | 6.2314 | 7.1689 | 8.2475 | 9.4883 | 10.9158 | 12.5581 | 14.4475 | 16.6211 | 19.1217 | 21.9985 | 25.3082 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054426 | 0.0075349 | 0.01056 | 0.014961 | 0.021401 | 0.030869 | 0.044852 | 0.065583 | 0.096424 | 0.14244 | 0.21128 | 0.3145 | 0.46958 | 0.70298 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1707e-06 | 1.6208e-06 | 2.2715e-06 | 3.2183e-06 | 4.6035e-06 | 6.6402e-06 | 9.648e-06 | 1.4107e-05 | 2.0741e-05 | 3.064e-05 | 4.5448e-05 | 6.7651e-05 | 0.00010101 | 0.00015122 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 46.809 | 64.8042 | 90.8222 | 128.6759 | 184.0587 | 265.4915 | 385.7547 | 564.0542 | 829.2991 | 1225.0678 | 1817.1357 | 2704.8923 | 4038.6672 | 6046.0335 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 |  | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 53.2004 | 70.5203 | 94.2952 | 127.0778 | 172.4658 | 235.5382 | 323.4768 | 446.4518 | 618.8831 | 861.24 | 1202.6086 | 1684.3571 | 2365.3706 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 28.574 | 39.559 | 55.4414 | 78.5488 | 112.3566 | 162.0663 | 235.4797 | 344.3207 | 506.2365 | 747.8292 | 1109.2505 | 1651.1717 | 2465.36 | 3690.7347 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 0 | 0 | 0 | 0 | 0 | 1.4418 | 12.4268 | 28.3091 | 51.4166 | 85.2244 | 134.9341 | 208.3475 | 317.1884 | 479.1043 | 720.6969 | 1082.1182 | 1624.0395 | 2432.8844 | 3647.6863 | 4886.7853 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12878 | 0.17829 | 0.24987 | 0.35401 | 0.50638 | 0.73042 | 1.0613 | 1.5518 | 2.2816 | 3.3704 | 4.9993 | 7.4417 | 11.1111 | 16.6338 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0 | 0 | 0 | 0 | 0 | 0.0064981 | 0.056006 | 0.12759 | 0.23173 | 0.3841 | 0.60813 | 0.939 | 1.4295 | 2.1593 | 3.2481 | 4.877 | 7.3194 | 10.9648 | 16.4398 | 22.0242 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 0 | 0 | 0 | 0 | 0 | 1.4483 | 12.4828 | 28.4367 | 51.6483 | 85.6085 | 135.5422 | 209.2865 | 318.618 | 481.2635 | 723.945 | 1086.9952 | 1631.3589 | 2443.8492 | 3664.1261 | 4908.8095 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 15.456 | 21.3979 | 29.9888 | 42.4878 | 60.7748 | 87.6633 | 127.3733 | 186.2464 | 273.8283 | 404.5081 | 600.0044 | 893.1349 | 1333.5372 | 1996.3543 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0 | 0 | 0 | 0 | 0.77989 | 6.7218 | 15.3127 | 27.8117 | 46.0987 | 72.9872 | 112.6972 | 171.5703 | 259.1522 | 389.832 | 585.3283 | 878.4588 | 1315.9709 | 1973.0691 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1776 | 3.0147 | 4.2251 | 5.9861 | 8.5625 | 12.3508 | 17.9455 | 26.2401 | 38.5794 | 56.9908 | 84.5341 | 125.833 | 187.8809 | 281.2646 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0 | 0 | 0 | 0 | 0.10988 | 0.94702 | 2.1574 | 3.9184 | 6.4948 | 10.2831 | 15.8778 | 24.1724 | 36.5117 | 54.9231 | 82.4664 | 123.7653 | 185.406 | 277.984 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.47263 | 0.65432 | 0.91702 | 1.2992 | 1.8584 | 2.6806 | 3.8949 | 5.6952 | 8.3733 | 12.3694 | 18.3474 | 27.311 | 40.778 | 61.0462 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 |  | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.53716 | 0.71204 | 0.95209 | 1.2831 | 1.7414 | 2.3782 | 3.2661 | 4.5078 | 6.2488 | 8.6959 | 12.1426 | 17.0068 | 23.8829 |  | 0 | 0 | 0 | 0 | 0 | 0.023848 | 0.20554 | 0.46824 | 0.85045 | 1.4096 | 2.2319 | 3.4461 | 5.2464 | 7.9246 | 11.9206 | 17.8987 | 26.8622 | 40.2408 | 60.3341 | 80.8293 | 80.4983 | 80.04 | 79.4032 | 78.5153 | 77.2736 | 75.5326 | 73.0855 | 69.6388 | 64.7746 | 57.8985 |  | 0 | 0 | 0 | 0 | 0 | 2.3619 | 20.3571 | 46.375 | 84.2288 | 139.6116 | 221.0443 | 341.3076 | 519.6071 | 784.852 | 1180.6207 | 1772.6886 | 2660.4451 | 3985.4668 | 5975.5132 | 8005.3622 | 7972.5795 | 7927.1915 | 7864.1191 | 7776.1805 | 7653.2055 | 7480.7742 | 7238.4173 | 6897.0488 | 6415.3003 | 5734.2867
| FALSE | 3824 | 22014926 | SHL | Blank | 66 | CB B | CB MGMT & DIR EF | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.15703 | 1 |  | 1.7651 | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.44878 |  | 7.1689 | 0.021401 | 4.6035e-06 | 0.021396 | 112.3566 | 0.50638 | 112.863 | 60.7748 | 8.5625 | 1.8584 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.44878 |  | 44.4471 | 184.0587 | 44.4471 | 139.6116 |  | 0.14015 |  | 2.0307 | 2.3362 | 2.6877 | 3.0921 | 3.5573 | 4.0924 | 4.7082 | 5.4165 | 6.2314 | 7.1689 | 8.2475 | 9.4883 | 10.9158 | 12.5581 | 14.4475 | 16.6211 | 19.1217 | 21.9985 | 25.3082 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0054426 | 0.0075349 | 0.01056 | 0.014961 | 0.021401 | 0.030869 | 0.044852 | 0.065583 | 0.096424 | 0.14244 | 0.21128 | 0.3145 | 0.46958 | 0.70298 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1707e-06 | 1.6208e-06 | 2.2715e-06 | 3.2183e-06 | 4.6035e-06 | 6.6402e-06 | 9.648e-06 | 1.4107e-05 | 2.0741e-05 | 3.064e-05 | 4.5448e-05 | 6.7651e-05 | 0.00010101 | 0.00015122 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 46.809 | 64.8042 | 90.8222 | 128.6759 | 184.0587 | 265.4915 | 385.7547 | 564.0542 | 829.2991 | 1225.0678 | 1817.1357 | 2704.8923 | 4038.6672 | 6046.0335 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 |  | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 53.2004 | 70.5203 | 94.2952 | 127.0778 | 172.4658 | 235.5382 | 323.4768 | 446.4518 | 618.8831 | 861.24 | 1202.6086 | 1684.3571 | 2365.3706 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 28.574 | 39.559 | 55.4414 | 78.5488 | 112.3566 | 162.0663 | 235.4797 | 344.3207 | 506.2365 | 747.8292 | 1109.2505 | 1651.1717 | 2465.36 | 3690.7347 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 0 | 0 | 0 | 0 | 0 | 1.4418 | 12.4268 | 28.3091 | 51.4166 | 85.2244 | 134.9341 | 208.3475 | 317.1884 | 479.1043 | 720.6969 | 1082.1182 | 1624.0395 | 2432.8844 | 3647.6863 | 4886.7853 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12878 | 0.17829 | 0.24987 | 0.35401 | 0.50638 | 0.73042 | 1.0613 | 1.5518 | 2.2816 | 3.3704 | 4.9993 | 7.4417 | 11.1111 | 16.6338 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0 | 0 | 0 | 0 | 0 | 0.0064981 | 0.056006 | 0.12759 | 0.23173 | 0.3841 | 0.60813 | 0.939 | 1.4295 | 2.1593 | 3.2481 | 4.877 | 7.3194 | 10.9648 | 16.4398 | 22.0242 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 0 | 0 | 0 | 0 | 0 | 1.4483 | 12.4828 | 28.4367 | 51.6483 | 85.6085 | 135.5422 | 209.2865 | 318.618 | 481.2635 | 723.945 | 1086.9952 | 1631.3589 | 2443.8492 | 3664.1261 | 4908.8095 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 15.456 | 21.3979 | 29.9888 | 42.4878 | 60.7748 | 87.6633 | 127.3733 | 186.2464 | 273.8283 | 404.5081 | 600.0044 | 893.1349 | 1333.5372 | 1996.3543 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0 | 0 | 0 | 0 | 0.77989 | 6.7218 | 15.3127 | 27.8117 | 46.0987 | 72.9872 | 112.6972 | 171.5703 | 259.1522 | 389.832 | 585.3283 | 878.4588 | 1315.9709 | 1973.0691 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.1776 | 3.0147 | 4.2251 | 5.9861 | 8.5625 | 12.3508 | 17.9455 | 26.2401 | 38.5794 | 56.9908 | 84.5341 | 125.833 | 187.8809 | 281.2646 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0 | 0 | 0 | 0 | 0.10988 | 0.94702 | 2.1574 | 3.9184 | 6.4948 | 10.2831 | 15.8778 | 24.1724 | 36.5117 | 54.9231 | 82.4664 | 123.7653 | 185.406 | 277.984 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.47263 | 0.65432 | 0.91702 | 1.2992 | 1.8584 | 2.6806 | 3.8949 | 5.6952 | 8.3733 | 12.3694 | 18.3474 | 27.311 | 40.778 | 61.0462 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 |  | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.53716 | 0.71204 | 0.95209 | 1.2831 | 1.7414 | 2.3782 | 3.2661 | 4.5078 | 6.2488 | 8.6959 | 12.1426 | 17.0068 | 23.8829 |  | 0 | 0 | 0 | 0 | 0 | 0.023848 | 0.20554 | 0.46824 | 0.85045 | 1.4096 | 2.2319 | 3.4461 | 5.2464 | 7.9246 | 11.9206 | 17.8987 | 26.8622 | 40.2408 | 60.3341 | 80.8293 | 80.4983 | 80.04 | 79.4032 | 78.5153 | 77.2736 | 75.5326 | 73.0855 | 69.6388 | 64.7746 | 57.8985 |  | 0 | 0 | 0 | 0 | 0 | 2.3619 | 20.3571 | 46.375 | 84.2288 | 139.6116 | 221.0443 | 341.3076 | 519.6071 | 784.852 | 1180.6207 | 1772.6886 | 2660.4451 | 3985.4668 | 5975.5132 | 8005.3622 | 7972.5795 | 7927.1915 | 7864.1191 | 7776.1805 | 7653.2055 | 7480.7742 | 7238.4173 | 6897.0488 | 6415.3003 | 5734.2867
| FALSE | 3825 | 22014924 | SHL | SHL-GSF | 66 | GSF LINE | DISTANCE & DIR EF | X | Schweitzer | SEL_311C_1 | SEL 311C | SEL 300s | Digital |  | 0.15703 | 1 |  | 1.99 | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.44878 |  | 7.92 | 0.027745 | 5.9682e-06 | 0.027739 | 145.6653 | 0.6565 | 146.3218 | 78.7918 | 11.1009 | 2.4094 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.44878 |  | 44.4471 | 238.6239 | 44.4471 | 194.1768 |  | 0.13813 |  | 2.2847 | 2.6231 | 3.0117 | 3.4578 | 3.97 | 4.558 | 5.2331 | 6.0083 | 6.8982 | 7.92 | 9.0931 | 10.44 | 11.9864 | 13.7618 | 15.8003 | 18.1406 | 20.8276 | 23.9126 | 27.4546 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0069809 | 0.0097093 | 0.013652 | 0.01938 | 0.027745 | 0.040015 | 0.058083 | 0.08478 | 0.12435 | 0.18315 | 0.27073 | 0.40144 | 0.59689 | 0.88958 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.5016e-06 | 2.0885e-06 | 2.9365e-06 | 4.1688e-06 | 5.9682e-06 | 8.6075e-06 | 1.2494e-05 | 1.8237e-05 | 2.6748e-05 | 3.9396e-05 | 5.8235e-05 | 8.6353e-05 | 0.0001284 | 0.00019136 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 60.0394 | 83.5049 | 117.4112 | 166.6785 | 238.6239 | 344.1519 | 499.5446 | 729.1543 | 1069.4569 | 1575.1591 | 2328.4028 | 3452.6481 | 5133.6181 | 7650.914 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 |  | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 53.2004 | 70.5203 | 94.2952 | 127.0778 | 172.4658 | 235.5382 | 323.4768 | 446.4518 | 618.8831 | 861.24 | 1202.6086 | 1684.3571 | 2365.3706 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 36.6504 | 50.9747 | 71.6724 | 101.7471 | 145.6653 | 210.0837 | 304.9415 | 445.1042 | 652.8382 | 961.5385 | 1421.3479 | 2107.6311 | 3133.7607 | 4670.4163 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 0 | 0 | 0 | 0 | 0 | 9.5182 | 23.8424 | 44.5401 | 74.6148 | 118.5331 | 182.9515 | 277.8093 | 417.972 | 625.706 | 934.4063 | 1394.2156 | 2080.4988 | 3101.2851 | 4627.368 | 4886.7853 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.16518 | 0.22974 | 0.32302 | 0.45856 | 0.6565 | 0.94683 | 1.3743 | 2.006 | 2.9423 | 4.3336 | 6.4059 | 9.4989 | 14.1235 | 21.0491 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0 | 0 | 0 | 0 | 0 | 0.042897 | 0.10746 | 0.20074 | 0.33628 | 0.53422 | 0.82454 | 1.2521 | 1.8838 | 2.82 | 4.2113 | 6.2836 | 9.3766 | 13.9772 | 20.8551 | 22.0242 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 0 | 0 | 0 | 0 | 0 | 9.5611 | 23.9499 | 44.7409 | 74.9511 | 119.0673 | 183.776 | 279.0613 | 419.8557 | 628.526 | 938.6175 | 1400.4992 | 2089.8754 | 3115.2623 | 4648.2231 | 4908.8095 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 19.8246 | 27.5727 | 38.7683 | 55.036 | 78.7918 | 113.6363 | 164.9458 | 240.7612 | 353.1266 | 520.1056 | 768.8209 | 1140.0382 | 1695.0817 | 2526.2737 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0 | 0 | 0 | 0 | 5.1485 | 12.8966 | 24.0922 | 40.3599 | 64.1157 | 98.9602 | 150.2697 | 226.0851 | 338.4505 | 505.4295 | 754.1448 | 1125.3621 | 1677.5153 | 2502.9884 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.7931 | 3.8847 | 5.462 | 7.754 | 11.1009 | 16.0101 | 23.2391 | 33.9206 | 49.7517 | 73.2772 | 108.3185 | 160.619 | 238.8186 | 355.9245 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0 | 0 | 0 | 0 | 0.72536 | 1.817 | 3.3943 | 5.6863 | 9.0332 | 13.9424 | 21.1714 | 31.8529 | 47.684 | 71.2095 | 106.2508 | 158.5513 | 236.3436 | 352.6438 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.60621 | 0.84314 | 1.1855 | 1.6829 | 2.4094 | 3.4749 | 5.0438 | 7.3622 | 10.7982 | 15.9042 | 23.5096 | 34.861 | 51.8336 | 77.2505 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 |  | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.53716 | 0.71204 | 0.95209 | 1.2831 | 1.7414 | 2.3782 | 3.2661 | 4.5078 | 6.2488 | 8.6959 | 12.1426 | 17.0068 | 23.8829 |  | 0 | 0 | 0 | 0 | 0 | 0.15743 | 0.39436 | 0.73671 | 1.2342 | 1.9606 | 3.0261 | 4.5951 | 6.9134 | 10.3494 | 15.4554 | 23.0609 | 34.4122 | 51.2964 | 76.5384 | 80.8293 | 80.4983 | 80.04 | 79.4032 | 78.5153 | 77.2736 | 75.5326 | 73.0855 | 69.6388 | 64.7746 | 57.8985 |  | 0 | 0 | 0 | 0 | 0 | 15.5923 | 39.0578 | 72.9641 | 122.2314 | 194.1768 | 299.7048 | 455.0975 | 684.7072 | 1025.0098 | 1530.7119 | 2283.9557 | 3408.201 | 5080.4177 | 7580.3938 | 8005.3622 | 7972.5795 | 7927.1915 | 7864.1191 | 7776.1805 | 7653.2055 | 7480.7742 | 7238.4173 | 6897.0488 | 6415.3003 | 5734.2867
| FALSE | 3826 | 22014925 | SHL | SHL-KGTS | 66 | KGTS LINE | DISTANCE & DIR EF | X | Schweitzer | SEL_311C | SEL 311C | SEL 300s | Digital |  | 0.15703 | 1 |  | 1.99 | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.44878 |  | 7.92 | 0.027745 | 5.9682e-06 | 0.027739 | 145.6653 | 0.6565 | 146.3218 | 78.7918 | 11.1009 | 2.4094 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.44878 |  | 44.4471 | 238.6239 | 44.4471 | 194.1768 |  | 0.13813 |  | 2.2847 | 2.6231 | 3.0117 | 3.4578 | 3.97 | 4.558 | 5.2331 | 6.0083 | 6.8982 | 7.92 | 9.0931 | 10.44 | 11.9864 | 13.7618 | 15.8003 | 18.1406 | 20.8276 | 23.9126 | 27.4546 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0069809 | 0.0097093 | 0.013652 | 0.01938 | 0.027745 | 0.040015 | 0.058083 | 0.08478 | 0.12435 | 0.18315 | 0.27073 | 0.40144 | 0.59689 | 0.88958 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.5016e-06 | 2.0885e-06 | 2.9365e-06 | 4.1688e-06 | 5.9682e-06 | 8.6075e-06 | 1.2494e-05 | 1.8237e-05 | 2.6748e-05 | 3.9396e-05 | 5.8235e-05 | 8.6353e-05 | 0.0001284 | 0.00019136 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 60.0394 | 83.5049 | 117.4112 | 166.6785 | 238.6239 | 344.1519 | 499.5446 | 729.1543 | 1069.4569 | 1575.1591 | 2328.4028 | 3452.6481 | 5133.6181 | 7650.914 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 | 8099.6573 |  | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 44.4471 | 53.2004 | 70.5203 | 94.2952 | 127.0778 | 172.4658 | 235.5382 | 323.4768 | 446.4518 | 618.8831 | 861.24 | 1202.6086 | 1684.3571 | 2365.3706 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 36.6504 | 50.9747 | 71.6724 | 101.7471 | 145.6653 | 210.0837 | 304.9415 | 445.1042 | 652.8382 | 961.5385 | 1421.3479 | 2107.6311 | 3133.7607 | 4670.4163 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 0 | 0 | 0 | 0 | 0 | 9.5182 | 23.8424 | 44.5401 | 74.6148 | 118.5331 | 182.9515 | 277.8093 | 417.972 | 625.706 | 934.4063 | 1394.2156 | 2080.4988 | 3101.2851 | 4627.368 | 4886.7853 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.16518 | 0.22974 | 0.32302 | 0.45856 | 0.6565 | 0.94683 | 1.3743 | 2.006 | 2.9423 | 4.3336 | 6.4059 | 9.4989 | 14.1235 | 21.0491 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0 | 0 | 0 | 0 | 0 | 0.042897 | 0.10746 | 0.20074 | 0.33628 | 0.53422 | 0.82454 | 1.2521 | 1.8838 | 2.82 | 4.2113 | 6.2836 | 9.3766 | 13.9772 | 20.8551 | 22.0242 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 0 | 0 | 0 | 0 | 0 | 9.5611 | 23.9499 | 44.7409 | 74.9511 | 119.0673 | 183.776 | 279.0613 | 419.8557 | 628.526 | 938.6175 | 1400.4992 | 2089.8754 | 3115.2623 | 4648.2231 | 4908.8095 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 19.8246 | 27.5727 | 38.7683 | 55.036 | 78.7918 | 113.6363 | 164.9458 | 240.7612 | 353.1266 | 520.1056 | 768.8209 | 1140.0382 | 1695.0817 | 2526.2737 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0 | 0 | 0 | 0 | 5.1485 | 12.8966 | 24.0922 | 40.3599 | 64.1157 | 98.9602 | 150.2697 | 226.0851 | 338.4505 | 505.4295 | 754.1448 | 1125.3621 | 1677.5153 | 2502.9884 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.7931 | 3.8847 | 5.462 | 7.754 | 11.1009 | 16.0101 | 23.2391 | 33.9206 | 49.7517 | 73.2772 | 108.3185 | 160.619 | 238.8186 | 355.9245 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0 | 0 | 0 | 0 | 0.72536 | 1.817 | 3.3943 | 5.6863 | 9.0332 | 13.9424 | 21.1714 | 31.8529 | 47.684 | 71.2095 | 106.2508 | 158.5513 | 236.3436 | 352.6438 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.60621 | 0.84314 | 1.1855 | 1.6829 | 2.4094 | 3.4749 | 5.0438 | 7.3622 | 10.7982 | 15.9042 | 23.5096 | 34.861 | 51.8336 | 77.2505 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 | 81.7814 |  | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.44878 | 0.53716 | 0.71204 | 0.95209 | 1.2831 | 1.7414 | 2.3782 | 3.2661 | 4.5078 | 6.2488 | 8.6959 | 12.1426 | 17.0068 | 23.8829 |  | 0 | 0 | 0 | 0 | 0 | 0.15743 | 0.39436 | 0.73671 | 1.2342 | 1.9606 | 3.0261 | 4.5951 | 6.9134 | 10.3494 | 15.4554 | 23.0609 | 34.4122 | 51.2964 | 76.5384 | 80.8293 | 80.4983 | 80.04 | 79.4032 | 78.5153 | 77.2736 | 75.5326 | 73.0855 | 69.6388 | 64.7746 | 57.8985 |  | 0 | 0 | 0 | 0 | 0 | 15.5923 | 39.0578 | 72.9641 | 122.2314 | 194.1768 | 299.7048 | 455.0975 | 684.7072 | 1025.0098 | 1530.7119 | 2283.9557 | 3408.201 | 5080.4177 | 7580.3938 | 8005.3622 | 7972.5795 | 7927.1915 | 7864.1191 | 7776.1805 | 7653.2055 | 7480.7742 | 7238.4173 | 6897.0488 | 6415.3003 | 5734.2867
| TRUE | 3827 | 22002530 | SHL | Blank | 66 | TRANS ALL | DIFFERENTIAL | X | Reyrolle | DUOBIAS_959 | DUOBIAS 979 | DUOBIAS | Electronic |  | 0.066046 | 2190 |  | 6.6 | 0.014726 | 0.0025679 | 0.012158 | 157.3198 | 1129.892 | 1287.2118 | 56.3804 | 5.9176 | 1036.6799 |  | 9.8464 | 0.042169 | 0.0073534 | 0.034815 | 450.4919 | 3235.493 | 3685.9849 | 161.4475 | 16.9452 | 2968.5764 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.18876 |  | 2386.1896 | 6832.9541 | 71.3984 | 6761.5557 |  | 0.040003 |  | 6.8694 | 7.1497 | 7.4416 | 7.7453 | 8.0614 | 8.3904 | 8.7329 | 9.0893 | 9.4603 | 9.8464 | 10.2482 | 10.6665 | 11.1019 | 11.555 | 12.0266 | 12.5174 | 13.0283 | 13.5601 | 14.1135 | 14.6896 | 15.2891 | 15.9131 | 16.5626 | 17.2386 | 17.9422 | 18.6745 | 19.4366 | 20.2299 | 21.0556 | 21.915 |  | 0.016313 | 0.018083 | 0.020059 | 0.022266 | 0.024731 | 0.027485 | 0.030564 | 0.034008 | 0.037859 | 0.042169 | 0.046992 | 0.052392 | 0.058439 | 0.065213 | 0.072802 | 0.081308 | 0.090842 | 0.10153 | 0.11352 | 0.12697 | 0.14205 | 0.15898 | 0.17798 | 0.19931 | 0.22326 | 0.25015 | 0.28035 | 0.31427 | 0.35238 | 0.3952 |  | 0.0028446 | 0.0031533 | 0.0034979 | 0.0038827 | 0.0043125 | 0.0047929 | 0.0053298 | 0.0059303 | 0.0066019 | 0.0073534 | 0.0081945 | 0.0091361 | 0.010191 | 0.011372 | 0.012695 | 0.014178 | 0.015841 | 0.017705 | 0.019796 | 0.022141 | 0.024771 | 0.027724 | 0.031037 | 0.034756 | 0.038932 | 0.043621 | 0.048887 | 0.054802 | 0.061448 | 0.068914 | 2643.2675 | 2930.1211 | 3250.3236 | 3607.8868 | 4007.3146 | 4453.6652 | 4952.6193 | 5510.5584 | 6134.6515 | 6832.9541 | 7614.5186 | 8489.5189 | 9469.3911 | 10566.991 | 11796.7727 | 13174.9884 | 14719.9144 | 16452.1052 | 18394.6797 | 20573.6432 | 23018.2512 | 25761.4177 | 28840.1759 | 32296.1978 | 36176.3776 | 40533.4914 | 45426.9381 | 50923.5756 | 57098.6626 | 64036.9191 |  | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 52.9875 | 70.2381 | 93.9178 | 126.5693 | 171.7756 | 234.5956 | 322.1823 | 444.6652 | 616.4064 | 857.7934 | 1197.7958 | 1677.6164 | 2355.9046 |  | 174.2688 | 193.1809 | 214.2916 | 237.8655 | 264.1995 | 293.6271 | 326.5228 | 363.3073 | 404.4533 | 450.4919 | 502.0199 | 559.7081 | 624.3104 | 696.6744 | 777.7531 | 868.6179 | 970.4738 | 1084.6759 | 1212.7485 | 1356.4061 | 1517.5774 | 1698.4324 | 1901.4129 | 2129.266 | 2385.0836 | 2672.3451 | 2994.9666 | 3357.3561 | 3764.4753 | 4221.9098 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 147.1369 | 166.0489 | 187.1597 | 210.7336 | 237.0676 | 266.4952 | 299.3909 | 336.1754 | 377.3214 | 423.36 | 474.888 | 532.5762 | 597.1785 | 669.5425 | 750.6212 | 841.486 | 943.3419 | 1052.2007 | 1169.7007 | 1298.8453 | 1440.0051 | 1593.1539 | 1757.633 | 1931.8056 | 2112.5553 | 2294.5594 | 2469.2387 | 2623.2461 | 2736.2909 | 2778.0133 |  | 1251.6217 | 1387.4506 | 1539.0707 | 1708.3815 | 1897.5158 | 2108.8686 | 2345.1299 | 2609.3214 | 2904.8376 | 3235.493 | 3605.574 | 4019.8981 | 4483.8803 | 5003.6082 | 5585.9259 | 6238.529 | 6970.0717 | 7790.2867 | 8710.121 | 9741.8887 | 10899.4425 | 12198.3677 | 13656.1999 | 15292.6714 | 17129.9872 | 19193.1375 | 21510.2484 | 24112.9781 | 27036.9624 | 30322.3174 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 1251.416 | 1387.2449 | 1538.865 | 1708.1758 | 1897.3101 | 2108.6629 | 2344.9242 | 2609.1156 | 2904.6319 | 3235.2873 | 3605.3683 | 4019.6924 | 4483.6746 | 5003.4025 | 5585.7202 | 6238.3233 | 6969.866 | 7790.0404 | 8709.7946 | 9741.4523 | 10898.8543 | 12197.5694 | 13655.1097 | 15291.1741 | 17127.9208 | 19190.2729 | 21506.262 | 24107.4116 | 27029.1661 | 30311.369 |  | 1398.5529 | 1553.2938 | 1726.0246 | 1918.9093 | 2134.3777 | 2375.1581 | 2644.3151 | 2945.291 | 3281.9533 | 3658.6473 | 4080.2563 | 4552.2686 | 5080.8531 | 5672.945 | 6336.3413 | 7079.8093 | 7913.2078 | 8842.2411 | 9879.4953 | 11040.2976 | 12338.8594 | 13790.7233 | 15412.7427 | 17222.9797 | 19240.4761 | 21484.8323 | 23975.5007 | 26730.6577 | 29765.457 | 33089.3823 |  | 62.4545 | 69.2323 | 76.7979 | 85.2464 | 94.6839 | 105.2302 | 117.0194 | 130.2023 | 144.9482 | 161.4475 | 179.9142 | 200.5885 | 223.7407 | 249.6745 | 278.7316 | 311.2957 | 347.7989 | 388.7267 | 434.6254 | 486.1095 | 543.8702 | 608.6851 | 681.4293 | 763.0875 | 854.7675 | 957.7164 | 1073.3377 | 1203.2111 | 1349.1147 | 1513.0503 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 47.7821 | 54.5598 | 62.1255 | 70.5739 | 80.0115 | 90.5578 | 102.347 | 115.5298 | 130.2758 | 146.7751 | 165.2417 | 185.916 | 209.0683 | 235.0021 | 264.0591 | 296.6233 | 333.1265 | 371.1647 | 411.346 | 454.9817 | 501.9205 | 551.7524 | 603.6758 | 656.3045 | 707.3892 | 753.4168 | 789.0337 | 806.2178 | 793.0913 | 732.2174 |  | 6.5551 | 7.2665 | 8.0606 | 8.9473 | 9.9378 | 11.0448 | 12.2821 | 13.6658 | 15.2135 | 16.9452 | 18.8834 | 21.0534 | 23.4834 | 26.2053 | 29.2551 | 32.673 | 36.5043 | 40.8 | 45.6174 | 51.0211 | 57.0835 | 63.8864 | 71.5215 | 80.0921 | 89.7147 | 100.52 | 112.6554 | 126.2866 | 141.6004 | 158.8067 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 4.4874 | 5.1988 | 5.9929 | 6.8796 | 7.8701 | 8.9771 | 10.2144 | 11.5981 | 13.1458 | 14.8775 | 16.8157 | 18.9857 | 21.4157 | 24.1376 | 27.1874 | 30.6053 | 34.4366 | 38.3251 | 42.3368 | 46.6344 | 51.1718 | 55.8632 | 60.5641 | 65.0439 | 68.9456 | 71.7293 | 72.5902 | 70.3408 | 63.2435 | 48.7688 |  | 1148.3674 | 1272.9909 | 1412.1029 | 1567.4462 | 1740.9776 | 1934.8945 | 2151.6651 | 2394.0617 | 2665.1989 | 2968.5764 | 3308.1271 | 3688.2709 | 4113.9763 | 4590.8285 | 5125.107 | 5723.8727 | 6395.0657 | 7147.6159 | 7991.5672 | 8938.2178 | 10000.2776 | 11192.046 | 12529.6124 | 14031.0808 | 15716.8247 | 17609.7724 | 19735.73 | 22123.7437 | 24806.5098 | 27820.8349 |  | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.22593 | 0.29948 | 0.40045 | 0.53967 | 0.73243 | 1.0003 | 1.3737 | 1.896 | 2.6283 | 3.6575 | 5.1072 | 7.1531 | 10.0452 |  | 1148.1786 | 1272.8021 | 1411.9141 | 1567.2574 | 1740.7888 | 1934.7058 | 2151.4764 | 2393.8729 | 2665.0101 | 2968.3877 | 3307.9383 | 3688.0821 | 4113.7875 | 4590.6397 | 5124.9183 | 5723.684 | 6394.877 | 7147.39 | 7991.2678 | 8937.8174 | 9999.7379 | 11191.3136 | 12528.6121 | 14029.7071 | 15714.9287 | 17607.1441 | 19732.0725 | 22118.6365 | 24799.3567 | 27810.7897 |  | 2599.001 | 2885.8545 | 3206.0571 | 3563.6203 | 3963.0481 | 4409.3987 | 4908.3528 | 5466.2918 | 6090.385 | 6788.6876 | 7570.2521 | 8445.2524 | 9425.1246 | 10522.7245 | 11752.5061 | 13130.7218 | 14675.6479 | 16399.121 | 18324.4459 | 20479.7311 | 22891.6897 | 25589.6525 | 28605.5947 | 31974.0351 | 35731.7396 | 39917.1226 | 44569.197 | 49725.8529 | 55421.1486 | 61681.1582
| TRUE | 3828 | 22002531 | SHL | Blank | 66 | TRANS ALL | DIFFERENTIAL | X | Reyrolle | DUOBIAS_959 | DUOBIAS 979 | DUOBIAS | Electronic |  | 0.066046 | 2190 |  | 6.6 | 0.014726 | 0.0025679 | 0.012158 | 157.3198 | 1129.892 | 1287.2118 | 56.3804 | 5.9176 | 1036.6799 |  | 9.8464 | 0.042169 | 0.0073534 | 0.034815 | 450.4919 | 3235.493 | 3685.9849 | 161.4475 | 16.9452 | 2968.5764 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.18876 |  | 2386.1896 | 6832.9541 | 71.3984 | 6761.5557 |  | 0.040003 |  | 6.8694 | 7.1497 | 7.4416 | 7.7453 | 8.0614 | 8.3904 | 8.7329 | 9.0893 | 9.4603 | 9.8464 | 10.2482 | 10.6665 | 11.1019 | 11.555 | 12.0266 | 12.5174 | 13.0283 | 13.5601 | 14.1135 | 14.6896 | 15.2891 | 15.9131 | 16.5626 | 17.2386 | 17.9422 | 18.6745 | 19.4366 | 20.2299 | 21.0556 | 21.915 |  | 0.016313 | 0.018083 | 0.020059 | 0.022266 | 0.024731 | 0.027485 | 0.030564 | 0.034008 | 0.037859 | 0.042169 | 0.046992 | 0.052392 | 0.058439 | 0.065213 | 0.072802 | 0.081308 | 0.090842 | 0.10153 | 0.11352 | 0.12697 | 0.14205 | 0.15898 | 0.17798 | 0.19931 | 0.22326 | 0.25015 | 0.28035 | 0.31427 | 0.35238 | 0.3952 |  | 0.0028446 | 0.0031533 | 0.0034979 | 0.0038827 | 0.0043125 | 0.0047929 | 0.0053298 | 0.0059303 | 0.0066019 | 0.0073534 | 0.0081945 | 0.0091361 | 0.010191 | 0.011372 | 0.012695 | 0.014178 | 0.015841 | 0.017705 | 0.019796 | 0.022141 | 0.024771 | 0.027724 | 0.031037 | 0.034756 | 0.038932 | 0.043621 | 0.048887 | 0.054802 | 0.061448 | 0.068914 | 2643.2675 | 2930.1211 | 3250.3236 | 3607.8868 | 4007.3146 | 4453.6652 | 4952.6193 | 5510.5584 | 6134.6515 | 6832.9541 | 7614.5186 | 8489.5189 | 9469.3911 | 10566.991 | 11796.7727 | 13174.9884 | 14719.9144 | 16452.1052 | 18394.6797 | 20573.6432 | 23018.2512 | 25761.4177 | 28840.1759 | 32296.1978 | 36176.3776 | 40533.4914 | 45426.9381 | 50923.5756 | 57098.6626 | 64036.9191 |  | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 52.9875 | 70.2381 | 93.9178 | 126.5693 | 171.7756 | 234.5956 | 322.1823 | 444.6652 | 616.4064 | 857.7934 | 1197.7958 | 1677.6164 | 2355.9046 |  | 174.2688 | 193.1809 | 214.2916 | 237.8655 | 264.1995 | 293.6271 | 326.5228 | 363.3073 | 404.4533 | 450.4919 | 502.0199 | 559.7081 | 624.3104 | 696.6744 | 777.7531 | 868.6179 | 970.4738 | 1084.6759 | 1212.7485 | 1356.4061 | 1517.5774 | 1698.4324 | 1901.4129 | 2129.266 | 2385.0836 | 2672.3451 | 2994.9666 | 3357.3561 | 3764.4753 | 4221.9098 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 147.1369 | 166.0489 | 187.1597 | 210.7336 | 237.0676 | 266.4952 | 299.3909 | 336.1754 | 377.3214 | 423.36 | 474.888 | 532.5762 | 597.1785 | 669.5425 | 750.6212 | 841.486 | 943.3419 | 1052.2007 | 1169.7007 | 1298.8453 | 1440.0051 | 1593.1539 | 1757.633 | 1931.8056 | 2112.5553 | 2294.5594 | 2469.2387 | 2623.2461 | 2736.2909 | 2778.0133 |  | 1251.6217 | 1387.4506 | 1539.0707 | 1708.3815 | 1897.5158 | 2108.8686 | 2345.1299 | 2609.3214 | 2904.8376 | 3235.493 | 3605.574 | 4019.8981 | 4483.8803 | 5003.6082 | 5585.9259 | 6238.529 | 6970.0717 | 7790.2867 | 8710.121 | 9741.8887 | 10899.4425 | 12198.3677 | 13656.1999 | 15292.6714 | 17129.9872 | 19193.1375 | 21510.2484 | 24112.9781 | 27036.9624 | 30322.3174 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 1251.416 | 1387.2449 | 1538.865 | 1708.1758 | 1897.3101 | 2108.6629 | 2344.9242 | 2609.1156 | 2904.6319 | 3235.2873 | 3605.3683 | 4019.6924 | 4483.6746 | 5003.4025 | 5585.7202 | 6238.3233 | 6969.866 | 7790.0404 | 8709.7946 | 9741.4523 | 10898.8543 | 12197.5694 | 13655.1097 | 15291.1741 | 17127.9208 | 19190.2729 | 21506.262 | 24107.4116 | 27029.1661 | 30311.369 |  | 1398.5529 | 1553.2938 | 1726.0246 | 1918.9093 | 2134.3777 | 2375.1581 | 2644.3151 | 2945.291 | 3281.9533 | 3658.6473 | 4080.2563 | 4552.2686 | 5080.8531 | 5672.945 | 6336.3413 | 7079.8093 | 7913.2078 | 8842.2411 | 9879.4953 | 11040.2976 | 12338.8594 | 13790.7233 | 15412.7427 | 17222.9797 | 19240.4761 | 21484.8323 | 23975.5007 | 26730.6577 | 29765.457 | 33089.3823 |  | 62.4545 | 69.2323 | 76.7979 | 85.2464 | 94.6839 | 105.2302 | 117.0194 | 130.2023 | 144.9482 | 161.4475 | 179.9142 | 200.5885 | 223.7407 | 249.6745 | 278.7316 | 311.2957 | 347.7989 | 388.7267 | 434.6254 | 486.1095 | 543.8702 | 608.6851 | 681.4293 | 763.0875 | 854.7675 | 957.7164 | 1073.3377 | 1203.2111 | 1349.1147 | 1513.0503 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 47.7821 | 54.5598 | 62.1255 | 70.5739 | 80.0115 | 90.5578 | 102.347 | 115.5298 | 130.2758 | 146.7751 | 165.2417 | 185.916 | 209.0683 | 235.0021 | 264.0591 | 296.6233 | 333.1265 | 371.1647 | 411.346 | 454.9817 | 501.9205 | 551.7524 | 603.6758 | 656.3045 | 707.3892 | 753.4168 | 789.0337 | 806.2178 | 793.0913 | 732.2174 |  | 6.5551 | 7.2665 | 8.0606 | 8.9473 | 9.9378 | 11.0448 | 12.2821 | 13.6658 | 15.2135 | 16.9452 | 18.8834 | 21.0534 | 23.4834 | 26.2053 | 29.2551 | 32.673 | 36.5043 | 40.8 | 45.6174 | 51.0211 | 57.0835 | 63.8864 | 71.5215 | 80.0921 | 89.7147 | 100.52 | 112.6554 | 126.2866 | 141.6004 | 158.8067 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 4.4874 | 5.1988 | 5.9929 | 6.8796 | 7.8701 | 8.9771 | 10.2144 | 11.5981 | 13.1458 | 14.8775 | 16.8157 | 18.9857 | 21.4157 | 24.1376 | 27.1874 | 30.6053 | 34.4366 | 38.3251 | 42.3368 | 46.6344 | 51.1718 | 55.8632 | 60.5641 | 65.0439 | 68.9456 | 71.7293 | 72.5902 | 70.3408 | 63.2435 | 48.7688 |  | 1148.3674 | 1272.9909 | 1412.1029 | 1567.4462 | 1740.9776 | 1934.8945 | 2151.6651 | 2394.0617 | 2665.1989 | 2968.5764 | 3308.1271 | 3688.2709 | 4113.9763 | 4590.8285 | 5125.107 | 5723.8727 | 6395.0657 | 7147.6159 | 7991.5672 | 8938.2178 | 10000.2776 | 11192.046 | 12529.6124 | 14031.0808 | 15716.8247 | 17609.7724 | 19735.73 | 22123.7437 | 24806.5098 | 27820.8349 |  | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.22593 | 0.29948 | 0.40045 | 0.53967 | 0.73243 | 1.0003 | 1.3737 | 1.896 | 2.6283 | 3.6575 | 5.1072 | 7.1531 | 10.0452 |  | 1148.1786 | 1272.8021 | 1411.9141 | 1567.2574 | 1740.7888 | 1934.7058 | 2151.4764 | 2393.8729 | 2665.0101 | 2968.3877 | 3307.9383 | 3688.0821 | 4113.7875 | 4590.6397 | 5124.9183 | 5723.684 | 6394.877 | 7147.39 | 7991.2678 | 8937.8174 | 9999.7379 | 11191.3136 | 12528.6121 | 14029.7071 | 15714.9287 | 17607.1441 | 19732.0725 | 22118.6365 | 24799.3567 | 27810.7897 |  | 2599.001 | 2885.8545 | 3206.0571 | 3563.6203 | 3963.0481 | 4409.3987 | 4908.3528 | 5466.2918 | 6090.385 | 6788.6876 | 7570.2521 | 8445.2524 | 9425.1246 | 10522.7245 | 11752.5061 | 13130.7218 | 14675.6479 | 16399.121 | 18324.4459 | 20479.7311 | 22891.6897 | 25589.6525 | 28605.5947 | 31974.0351 | 35731.7396 | 39917.1226 | 44569.197 | 49725.8529 | 55421.1486 | 61681.1582
| TRUE | 3829 | 22002532 | SHL | Blank | 66 | TRANS ALL | DIFFERENTIAL | X | Reyrolle | DUOBIAS_959 | DUOBIAS 979 | DUOBIAS | Electronic |  | 0.066046 | 2190 |  | 6.6 | 0.014726 | 0.0025679 | 0.012158 | 157.3198 | 1129.892 | 1287.2118 | 56.3804 | 5.9176 | 1036.6799 |  | 9.8464 | 0.042169 | 0.0073534 | 0.034815 | 450.4919 | 3235.493 | 3685.9849 | 161.4475 | 16.9452 | 2968.5764 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.18876 |  | 2386.1896 | 6832.9541 | 71.3984 | 6761.5557 |  | 0.040003 |  | 6.8694 | 7.1497 | 7.4416 | 7.7453 | 8.0614 | 8.3904 | 8.7329 | 9.0893 | 9.4603 | 9.8464 | 10.2482 | 10.6665 | 11.1019 | 11.555 | 12.0266 | 12.5174 | 13.0283 | 13.5601 | 14.1135 | 14.6896 | 15.2891 | 15.9131 | 16.5626 | 17.2386 | 17.9422 | 18.6745 | 19.4366 | 20.2299 | 21.0556 | 21.915 |  | 0.016313 | 0.018083 | 0.020059 | 0.022266 | 0.024731 | 0.027485 | 0.030564 | 0.034008 | 0.037859 | 0.042169 | 0.046992 | 0.052392 | 0.058439 | 0.065213 | 0.072802 | 0.081308 | 0.090842 | 0.10153 | 0.11352 | 0.12697 | 0.14205 | 0.15898 | 0.17798 | 0.19931 | 0.22326 | 0.25015 | 0.28035 | 0.31427 | 0.35238 | 0.3952 |  | 0.0028446 | 0.0031533 | 0.0034979 | 0.0038827 | 0.0043125 | 0.0047929 | 0.0053298 | 0.0059303 | 0.0066019 | 0.0073534 | 0.0081945 | 0.0091361 | 0.010191 | 0.011372 | 0.012695 | 0.014178 | 0.015841 | 0.017705 | 0.019796 | 0.022141 | 0.024771 | 0.027724 | 0.031037 | 0.034756 | 0.038932 | 0.043621 | 0.048887 | 0.054802 | 0.061448 | 0.068914 | 2643.2675 | 2930.1211 | 3250.3236 | 3607.8868 | 4007.3146 | 4453.6652 | 4952.6193 | 5510.5584 | 6134.6515 | 6832.9541 | 7614.5186 | 8489.5189 | 9469.3911 | 10566.991 | 11796.7727 | 13174.9884 | 14719.9144 | 16452.1052 | 18394.6797 | 20573.6432 | 23018.2512 | 25761.4177 | 28840.1759 | 32296.1978 | 36176.3776 | 40533.4914 | 45426.9381 | 50923.5756 | 57098.6626 | 64036.9191 |  | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 44.2692 | 52.9875 | 70.2381 | 93.9178 | 126.5693 | 171.7756 | 234.5956 | 322.1823 | 444.6652 | 616.4064 | 857.7934 | 1197.7958 | 1677.6164 | 2355.9046 |  | 174.2688 | 193.1809 | 214.2916 | 237.8655 | 264.1995 | 293.6271 | 326.5228 | 363.3073 | 404.4533 | 450.4919 | 502.0199 | 559.7081 | 624.3104 | 696.6744 | 777.7531 | 868.6179 | 970.4738 | 1084.6759 | 1212.7485 | 1356.4061 | 1517.5774 | 1698.4324 | 1901.4129 | 2129.266 | 2385.0836 | 2672.3451 | 2994.9666 | 3357.3561 | 3764.4753 | 4221.9098 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 147.1369 | 166.0489 | 187.1597 | 210.7336 | 237.0676 | 266.4952 | 299.3909 | 336.1754 | 377.3214 | 423.36 | 474.888 | 532.5762 | 597.1785 | 669.5425 | 750.6212 | 841.486 | 943.3419 | 1052.2007 | 1169.7007 | 1298.8453 | 1440.0051 | 1593.1539 | 1757.633 | 1931.8056 | 2112.5553 | 2294.5594 | 2469.2387 | 2623.2461 | 2736.2909 | 2778.0133 |  | 1251.6217 | 1387.4506 | 1539.0707 | 1708.3815 | 1897.5158 | 2108.8686 | 2345.1299 | 2609.3214 | 2904.8376 | 3235.493 | 3605.574 | 4019.8981 | 4483.8803 | 5003.6082 | 5585.9259 | 6238.529 | 6970.0717 | 7790.2867 | 8710.121 | 9741.8887 | 10899.4425 | 12198.3677 | 13656.1999 | 15292.6714 | 17129.9872 | 19193.1375 | 21510.2484 | 24112.9781 | 27036.9624 | 30322.3174 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 1251.416 | 1387.2449 | 1538.865 | 1708.1758 | 1897.3101 | 2108.6629 | 2344.9242 | 2609.1156 | 2904.6319 | 3235.2873 | 3605.3683 | 4019.6924 | 4483.6746 | 5003.4025 | 5585.7202 | 6238.3233 | 6969.866 | 7790.0404 | 8709.7946 | 9741.4523 | 10898.8543 | 12197.5694 | 13655.1097 | 15291.1741 | 17127.9208 | 19190.2729 | 21506.262 | 24107.4116 | 27029.1661 | 30311.369 |  | 1398.5529 | 1553.2938 | 1726.0246 | 1918.9093 | 2134.3777 | 2375.1581 | 2644.3151 | 2945.291 | 3281.9533 | 3658.6473 | 4080.2563 | 4552.2686 | 5080.8531 | 5672.945 | 6336.3413 | 7079.8093 | 7913.2078 | 8842.2411 | 9879.4953 | 11040.2976 | 12338.8594 | 13790.7233 | 15412.7427 | 17222.9797 | 19240.4761 | 21484.8323 | 23975.5007 | 26730.6577 | 29765.457 | 33089.3823 |  | 62.4545 | 69.2323 | 76.7979 | 85.2464 | 94.6839 | 105.2302 | 117.0194 | 130.2023 | 144.9482 | 161.4475 | 179.9142 | 200.5885 | 223.7407 | 249.6745 | 278.7316 | 311.2957 | 347.7989 | 388.7267 | 434.6254 | 486.1095 | 543.8702 | 608.6851 | 681.4293 | 763.0875 | 854.7675 | 957.7164 | 1073.3377 | 1203.2111 | 1349.1147 | 1513.0503 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 47.7821 | 54.5598 | 62.1255 | 70.5739 | 80.0115 | 90.5578 | 102.347 | 115.5298 | 130.2758 | 146.7751 | 165.2417 | 185.916 | 209.0683 | 235.0021 | 264.0591 | 296.6233 | 333.1265 | 371.1647 | 411.346 | 454.9817 | 501.9205 | 551.7524 | 603.6758 | 656.3045 | 707.3892 | 753.4168 | 789.0337 | 806.2178 | 793.0913 | 732.2174 |  | 6.5551 | 7.2665 | 8.0606 | 8.9473 | 9.9378 | 11.0448 | 12.2821 | 13.6658 | 15.2135 | 16.9452 | 18.8834 | 21.0534 | 23.4834 | 26.2053 | 29.2551 | 32.673 | 36.5043 | 40.8 | 45.6174 | 51.0211 | 57.0835 | 63.8864 | 71.5215 | 80.0921 | 89.7147 | 100.52 | 112.6554 | 126.2866 | 141.6004 | 158.8067 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 4.4874 | 5.1988 | 5.9929 | 6.8796 | 7.8701 | 8.9771 | 10.2144 | 11.5981 | 13.1458 | 14.8775 | 16.8157 | 18.9857 | 21.4157 | 24.1376 | 27.1874 | 30.6053 | 34.4366 | 38.3251 | 42.3368 | 46.6344 | 51.1718 | 55.8632 | 60.5641 | 65.0439 | 68.9456 | 71.7293 | 72.5902 | 70.3408 | 63.2435 | 48.7688 |  | 1148.3674 | 1272.9909 | 1412.1029 | 1567.4462 | 1740.9776 | 1934.8945 | 2151.6651 | 2394.0617 | 2665.1989 | 2968.5764 | 3308.1271 | 3688.2709 | 4113.9763 | 4590.8285 | 5125.107 | 5723.8727 | 6395.0657 | 7147.6159 | 7991.5672 | 8938.2178 | 10000.2776 | 11192.046 | 12529.6124 | 14031.0808 | 15716.8247 | 17609.7724 | 19735.73 | 22123.7437 | 24806.5098 | 27820.8349 |  | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.22593 | 0.29948 | 0.40045 | 0.53967 | 0.73243 | 1.0003 | 1.3737 | 1.896 | 2.6283 | 3.6575 | 5.1072 | 7.1531 | 10.0452 |  | 1148.1786 | 1272.8021 | 1411.9141 | 1567.2574 | 1740.7888 | 1934.7058 | 2151.4764 | 2393.8729 | 2665.0101 | 2968.3877 | 3307.9383 | 3688.0821 | 4113.7875 | 4590.6397 | 5124.9183 | 5723.684 | 6394.877 | 7147.39 | 7991.2678 | 8937.8174 | 9999.7379 | 11191.3136 | 12528.6121 | 14029.7071 | 15714.9287 | 17607.1441 | 19732.0725 | 22118.6365 | 24799.3567 | 27810.7897 |  | 2599.001 | 2885.8545 | 3206.0571 | 3563.6203 | 3963.0481 | 4409.3987 | 4908.3528 | 5466.2918 | 6090.385 | 6788.6876 | 7570.2521 | 8445.2524 | 9425.1246 | 10522.7245 | 11752.5061 | 13130.7218 | 14675.6479 | 16399.121 | 18324.4459 | 20479.7311 | 22891.6897 | 25589.6525 | 28605.5947 | 31974.0351 | 35731.7396 | 39917.1226 | 44569.197 | 49725.8529 | 55421.1486 | 61681.1582
| TRUE | 3830 | 22002971 | SHN | Blank | 22 | BUS ALL | VRR NO. 2 | C | RMS | 2V161_2203 | 2V161 2203 | 2V161 | Electronic |  | 0 | 2190 |  | 6.6 | 0.014726 | 0 | 0.014726 | 80.9933 | 0 | 80.9933 | 41.8016 | 5.8919 | 0 |  | 10.0404 | 0.044454 | 0 | 0.044454 | 244.4947 | 0 | 244.4947 | 126.1867 | 17.7859 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 128.6867 | 388.4672 | 45.1611 | 343.3061 |  | 0.041955 |  | 6.8828 | 7.1777 | 7.4852 | 7.806 | 8.1404 | 8.4892 | 8.853 | 9.2323 | 9.6279 | 10.0404 | 10.4706 | 10.9192 | 11.3871 | 11.875 | 12.3838 | 12.9144 | 13.4678 | 14.0448 | 14.6466 | 15.2742 | 15.9286 | 16.6111 | 17.3229 | 18.0651 | 18.8392 | 19.6464 | 20.4882 | 21.366 | 22.2815 | 23.2362 |  | 0.016394 | 0.018266 | 0.020367 | 0.022725 | 0.025374 | 0.028351 | 0.031697 | 0.03546 | 0.039692 | 0.044454 | 0.049814 | 0.055848 | 0.062645 | 0.070302 | 0.07893 | 0.088655 | 0.099619 | 0.11198 | 0.12593 | 0.14167 | 0.15942 | 0.17946 | 0.20209 | 0.22763 | 0.25648 | 0.28906 | 0.32587 | 0.36747 | 0.41447 | 0.46759 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143.2668 | 159.6231 | 177.9799 | 198.5904 | 221.7404 | 247.7527 | 276.9921 | 309.8706 | 346.8536 | 388.4672 | 435.3061 | 488.0424 | 547.4359 | 614.3458 | 689.7437 | 774.7284 | 870.5428 | 978.5927 | 1100.4687 | 1237.9704 | 1393.134 | 1568.264 | 1765.9684 | 1989.1988 | 2241.2965 | 2526.0439 | 2847.7229 | 3211.1816 | 3621.9093 | 4086.1216 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 90.1697 | 100.4641 | 112.0176 | 124.9894 | 139.5596 | 155.9314 | 174.3342 | 195.0273 | 218.3038 | 244.4947 | 273.9743 | 307.1656 | 344.5469 | 386.6589 | 434.113 | 487.601 | 547.9049 | 615.9097 | 692.6164 | 779.1576 | 876.815 | 987.0389 | 1111.4706 | 1251.968 | 1410.6341 | 1589.8493 | 1792.3086 | 2021.0634 | 2279.5684 | 2571.7358 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 75.9579 | 86.2523 | 97.8057 | 110.7776 | 125.3478 | 141.7196 | 160.1223 | 180.8155 | 204.092 | 230.2829 | 259.7625 | 292.9538 | 330.3351 | 372.447 | 419.9012 | 473.3891 | 533.6931 | 598.899 | 670.0677 | 749.007 | 836.1822 | 931.8934 | 1036.158 | 1148.5373 | 1267.8825 | 1391.9633 | 1516.9298 | 1636.5331 | 1741.0005 | 1815.4159 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 75.9579 | 86.2523 | 97.8057 | 110.7776 | 125.3478 | 141.7196 | 160.1223 | 180.8155 | 204.092 | 230.2829 | 259.7625 | 292.9538 | 330.3351 | 372.447 | 419.9012 | 473.3891 | 533.6931 | 598.899 | 670.0677 | 749.007 | 836.1822 | 931.8934 | 1036.158 | 1148.5373 | 1267.8825 | 1391.9633 | 1516.9298 | 1636.5331 | 1741.0005 | 1815.4159 |  | 46.5377 | 51.8507 | 57.8136 | 64.5085 | 72.0284 | 80.4781 | 89.976 | 100.6559 | 112.6692 | 126.1867 | 141.4014 | 158.5319 | 177.8248 | 199.5593 | 224.0509 | 251.6567 | 282.7803 | 317.8784 | 357.4676 | 402.1326 | 452.5347 | 509.4226 | 573.6433 | 646.1557 | 728.0452 | 820.5403 | 925.032 | 1043.0951 | 1176.5126 | 1327.3037 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 31.8679 | 37.1809 | 43.1438 | 49.8388 | 57.3586 | 65.8083 | 75.3062 | 85.9861 | 97.9994 | 111.5169 | 126.7316 | 143.8621 | 163.155 | 184.8895 | 209.3812 | 236.9869 | 268.1105 | 300.3196 | 334.1924 | 371.0104 | 410.5927 | 452.5002 | 495.9038 | 539.3921 | 580.6936 | 616.2777 | 640.7794 | 646.1736 | 620.5899 | 546.6122 |  | 6.5594 | 7.3083 | 8.1488 | 9.0924 | 10.1523 | 11.3433 | 12.682 | 14.1873 | 15.8806 | 17.7859 | 19.9304 | 22.3449 | 25.0642 | 28.1277 | 31.5797 | 35.4708 | 39.8576 | 44.8046 | 50.3847 | 56.6802 | 63.7843 | 71.8026 | 80.8544 | 91.075 | 102.6172 | 115.6543 | 130.3823 | 147.0232 | 165.8282 | 187.0821 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 4.4917 | 5.2406 | 6.0811 | 7.0247 | 8.0846 | 9.2756 | 10.6143 | 12.1197 | 13.8129 | 15.7182 | 17.8627 | 20.2772 | 22.9965 | 26.06 | 29.5121 | 33.4031 | 37.7899 | 42.3297 | 47.1041 | 52.2935 | 57.8726 | 63.7794 | 69.8971 | 76.0268 | 81.8482 | 86.8637 | 90.3172 | 91.0775 | 87.4715 | 77.0444 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 112.3175 | 128.6738 | 147.0306 | 167.6411 | 190.7911 | 216.8034 | 246.0428 | 278.9213 | 315.9043 | 357.5179 | 404.3568 | 457.0931 | 516.4866 | 583.3965 | 658.7944 | 743.7791 | 839.5935 | 941.5483 | 1051.3642 | 1172.311 | 1304.6475 | 1448.1731 | 1601.959 | 1763.9562 | 1930.4242 | 2095.1047 | 2248.0264 | 2373.7842 | 2449.0619 | 2439.0725
| TRUE | 3831 | 22002972 | SHN | Blank | 22 | BUS ALL | OV-UV SUPERVISION | C | RPL | GROUP_2506 | GROUP 2506 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 498.1313 | 0 | 498.1313 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 791.4596 | 45.1611 | 746.2985 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.1882 | 292.6741 | 330.7184 | 373.9588 | 423.1235 | 479.0446 | 542.6727 | 615.0939 | 697.5498 | 791.4596 | 898.4455 | 1020.3625 | 1159.3315 | 1317.7785 | 1498.4776 | 1704.6026 | 1939.7838 | 2208.1751 | 2514.5289 | 2864.2839 | 3263.6638 | 3719.792 | 4240.8213 | 4836.0847 | 5516.2655 | 6293.5949 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 163.1287 | 184.2041 | 208.1485 | 235.3633 | 266.3068 | 301.5026 | 341.549 | 387.1297 | 439.0261 | 498.1313 | 565.4664 | 642.1989 | 729.6637 | 829.3875 | 943.1165 | 1072.848 | 1220.8671 | 1389.788 | 1582.602 | 1802.7318 | 2054.0948 | 2341.1741 | 2669.1012 | 3043.7499 | 3471.8442 | 3961.0821 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 228.2389 | 261.7248 | 299.7691 | 343.0095 | 392.1742 | 448.0953 | 511.7234 | 584.1446 | 666.6005 | 760.5103 | 867.4962 | 989.4132 | 1128.3822 | 1286.8292 | 1467.5283 | 1673.6533 | 1908.8345 | 2171.1307 | 2465.4244 | 2798.6245 | 3175.1773 | 3599.701 | 4076.812 | 4610.8421 | 5205.3933 | 5862.6557 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 3832 | 22002956 | SHN | Blank | 22 | BUS NO.1 | SINGLE ZONE BUS DIST | X | ASEA | GROUP_3075 | GROUP 3075 | GROUP 3000s | Electronic |  | 0.033587 | 2190 |  | 9.9 | 0.042792 | 0.0040364 | 0.038756 | 237.5764 | 1130.1807 | 1367.7571 | 144.3856 | 17.1615 | 2650.8732 |  | 16.087 | 0.16393 | 0.015463 | 0.14847 | 910.1185 | 4329.5472 | 5239.6658 | 553.119 | 65.743 | 10155.0849 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.15616 |  | 4180.1774 | 16013.6127 | 45.3853 | 15968.2273 |  | 0.048548 |  | 10.3925 | 10.9095 | 11.4522 | 12.0218 | 12.6199 | 13.2477 | 13.9067 | 14.5985 | 15.3247 | 16.087 | 16.8873 | 17.7273 | 18.6092 | 19.5349 | 20.5067 | 21.5268 | 22.5976 | 23.7218 | 24.9018 | 26.1406 | 27.4409 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.04881 | 0.055712 | 0.063632 | 0.072723 | 0.083163 | 0.095155 | 0.10893 | 0.12477 | 0.14298 | 0.16393 | 0.18803 | 0.21575 | 0.24767 | 0.28441 | 0.32672 | 0.37545 | 0.43158 | 0.49627 | 0.57081 | 0.65674 | 0.75579 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.004604 | 0.005255 | 0.0060021 | 0.0068596 | 0.0078443 | 0.0089755 | 0.010275 | 0.011769 | 0.013487 | 0.015463 | 0.017735 | 0.020351 | 0.023361 | 0.026827 | 0.030817 | 0.035414 | 0.040709 | 0.04681 | 0.053842 | 0.061947 | 0.07129 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 4767.9997 | 5442.2415 | 6215.9114 | 7104.0051 | 8123.8109 | 9295.2638 | 10641.354 | 12188.5988 | 13967.5877 | 16013.6127 | 18367.3955 | 21075.9293 | 24193.45 | 27782.5594 | 31915.5231 | 36675.7702 | 42159.6269 | 48478.32 | 55760.293 | 64153.8825 | 73830.4127 | 78273.4573 | 78273.4573 | 78273.4573 | 78273.4573 | 78273.4573 | 78273.4573 | 78273.4573 | 78273.4573 | 78273.4573 |  | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 37.3135 | 49.4613 | 66.1365 | 89.1295 | 120.9636 | 165.201 | 226.8792 | 313.131 | 434.0704 | 604.0539 | 843.4819 | 1181.3692 | 1659.0164 |  | 270.9848 | 309.3047 | 353.2755 | 403.7494 | 461.7091 | 528.2875 | 604.7913 | 692.7275 | 793.8346 | 910.1185 | 1043.8936 | 1197.8305 | 1375.0119 | 1578.9955 | 1813.8886 | 2084.4327 | 2396.1025 | 2755.2195 | 3169.0835 | 3646.1253 | 4196.0817 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 256.7729 | 295.0928 | 339.0636 | 389.5375 | 447.4972 | 514.0756 | 590.5794 | 678.5156 | 779.6228 | 895.9066 | 1029.6817 | 1183.6186 | 1360.8 | 1564.7836 | 1799.6767 | 2070.2208 | 2381.8906 | 2738.2087 | 3146.5348 | 3615.9745 | 4155.4488 | 4393.4523 | 4373.285 | 4345.1668 | 4305.8457 | 4250.7111 | 4173.2179 | 4064.0658 | 3910.0276 | 3692.2746 |  | 1289.1082 | 1471.4007 | 1680.5753 | 1920.6863 | 2196.4078 | 2513.1296 | 2877.0675 | 3295.391 | 3776.3703 | 4329.5472 | 4965.9317 | 5698.229 | 6541.1027 | 7511.4783 | 8628.8939 | 9915.9061 | 11398.5582 | 13106.9223 | 15075.7251 | 17345.072 | 19961.2834 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 1289.0417 | 1471.3342 | 1680.5087 | 1920.6197 | 2196.3412 | 2513.063 | 2877.001 | 3295.3244 | 3776.3037 | 4329.4807 | 4965.8651 | 5698.1624 | 6541.0361 | 7511.4117 | 8628.8274 | 9915.8395 | 11398.4917 | 13106.8426 | 15075.6195 | 17344.9308 | 19961.093 | 21162.2762 | 21162.1818 | 21162.05 | 21161.8658 | 21161.6076 | 21161.2445 | 21160.7332 | 21160.0116 | 21158.9915 |  | 1545.8145 | 1766.4269 | 2019.5723 | 2310.1572 | 2643.8384 | 3027.1387 | 3467.5804 | 3973.84 | 4555.9265 | 5225.3873 | 5995.5468 | 6881.781 | 7901.8361 | 9076.1953 | 10428.5041 | 11986.0604 | 13780.3823 | 15845.0514 | 18222.1543 | 20960.9053 | 24116.5418 | 25555.7285 | 25535.4668 | 25507.2168 | 25467.7116 | 25412.3186 | 25334.4624 | 25224.799 | 25070.0391 | 24851.2661 |  | 164.6893 | 187.978 | 214.701 | 245.3762 | 280.6009 | 321.0635 | 367.5582 | 421.0009 | 482.4482 | 553.119 | 634.42 | 727.9742 | 835.6551 | 959.6249 | 1102.3797 | 1266.8013 | 1456.2167 | 1674.4679 | 1925.9912 | 2215.9104 | 2550.1431 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 150.0182 | 173.3069 | 200.0299 | 230.7051 | 265.9298 | 306.3924 | 352.8871 | 406.3298 | 467.777 | 538.4479 | 619.7488 | 713.3031 | 820.984 | 944.9538 | 1087.7086 | 1252.1302 | 1441.5456 | 1656.9074 | 1902.7138 | 2184.7854 | 2508.1972 | 2646.6807 | 2625.8617 | 2596.8349 | 2556.2432 | 2499.3269 | 2419.3296 | 2306.6504 | 2147.6344 | 1922.8449 |  | 19.5747 | 22.3428 | 25.5191 | 29.1651 | 33.3518 | 38.1612 | 43.6875 | 50.0396 | 57.3431 | 65.743 | 75.4063 | 86.526 | 99.3248 | 114.0597 | 131.0273 | 150.5702 | 173.0839 | 199.0249 | 228.9206 | 263.38 | 303.1064 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 17.5071 | 20.2751 | 23.4514 | 27.0974 | 31.2841 | 36.0935 | 41.6198 | 47.9719 | 55.2754 | 63.6753 | 73.3386 | 84.4583 | 97.2571 | 111.992 | 128.9596 | 148.5025 | 171.0162 | 196.55 | 225.64 | 258.9934 | 297.1947 | 313.3239 | 310.3898 | 306.2989 | 300.578 | 292.5565 | 281.2819 | 265.4014 | 242.9903 | 211.3093 |  | 3023.6427 | 3451.2153 | 3941.8406 | 4505.0281 | 5151.7413 | 5894.622 | 6748.2495 | 7729.4399 | 8857.5915 | 10155.0849 | 11647.744 | 13365.3696 | 15342.3556 | 17618.4011 | 20239.3335 | 23258.0598 | 26735.6655 | 30742.6854 | 35360.5724 | 40683.3947 | 46819.7981 | 49637.3694 | 49637.3694 | 49637.3694 | 49637.3694 | 49637.3694 | 49637.3694 | 49637.3694 | 49637.3694 | 49637.3694 |  | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.18691 | 0.24776 | 0.33129 | 0.44647 | 0.60594 | 0.82753 | 1.1365 | 1.5686 | 2.1744 | 3.0259 | 4.2252 | 5.9178 | 8.3104 |  | 3023.4865 | 3451.0591 | 3941.6844 | 4504.8719 | 5151.5851 | 5894.4658 | 6748.0934 | 7729.2837 | 8857.4354 | 10154.9288 | 11647.5879 | 13365.2134 | 15342.1994 | 17618.2449 | 20239.1774 | 23257.9036 | 26735.5093 | 30742.4985 | 35360.3247 | 40683.0634 | 46819.3516 | 49636.7634 | 49636.5418 | 49636.2329 | 49635.8008 | 49635.195 | 49634.3435 | 49633.1442 | 49631.4516 | 49629.0589 |  | 4736.8263 | 5411.068 | 6184.738 | 7072.8316 | 8092.6374 | 9264.0903 | 10610.1806 | 12157.4254 | 13936.4143 | 15982.4392 | 18336.222 | 21044.7559 | 24162.2765 | 27751.386 | 31884.3497 | 36644.5967 | 42128.4534 | 48441.0073 | 55710.8328 | 64087.7475 | 73741.2853 | 78152.4966 | 78108.2601 | 78046.5834 | 77960.3336 | 77839.397 | 77669.4174 | 77429.9949 | 77092.1154 | 76614.4793
| TRUE | 3833 | 22002954 | SHN | Blank | 22 | BUS NO.1 | HIBP | X | ABB | RADHA_2524 | RADHA 2524 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 81.7572 | 388.9293 | 470.6866 | 49.6875 | 5.9058 | 912.2456 |  | 10.0404 | 0.044454 | 0.0041931 | 0.040261 | 246.8009 | 1174.0627 | 1420.8636 | 149.9917 | 17.8278 | 2753.7997 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.15616 |  | 1438.5254 | 4342.4828 | 45.3853 | 4297.0975 |  | 0.041955 |  | 6.8828 | 7.1777 | 7.4852 | 7.806 | 8.1404 | 8.4892 | 8.853 | 9.2323 | 9.6279 | 10.0404 | 10.4706 | 10.9192 | 11.3871 | 11.875 | 12.3838 | 12.9144 | 13.4678 | 14.0448 | 14.6466 | 15.2742 | 15.9286 | 16.6111 | 17.3229 | 18.0651 | 18.8392 | 19.6464 | 20.4882 | 21.366 | 22.2815 | 23.2362 |  | 0.016394 | 0.018266 | 0.020367 | 0.022725 | 0.025374 | 0.028351 | 0.031697 | 0.03546 | 0.039692 | 0.044454 | 0.049814 | 0.055848 | 0.062645 | 0.070302 | 0.07893 | 0.088655 | 0.099619 | 0.11198 | 0.12593 | 0.14167 | 0.15942 | 0.17946 | 0.20209 | 0.22763 | 0.25648 | 0.28906 | 0.32587 | 0.36747 | 0.41447 | 0.46759 |  | 0.0015464 | 0.001723 | 0.0019211 | 0.0021436 | 0.0023934 | 0.0026742 | 0.0029898 | 0.0033447 | 0.0037439 | 0.0041931 | 0.0046987 | 0.0052679 | 0.005909 | 0.0066312 | 0.007445 | 0.0083623 | 0.0093966 | 0.010563 | 0.011878 | 0.013363 | 0.015037 | 0.016928 | 0.019062 | 0.021471 | 0.024192 | 0.027266 | 0.030738 | 0.034661 | 0.039095 | 0.044105 | 1601.5087 | 1784.3478 | 1989.5495 | 2219.9436 | 2478.7258 | 2769.505 | 3096.3577 | 3463.8896 | 3877.3044 | 4342.4828 | 4866.0716 | 5455.5842 | 6119.5147 | 6867.4674 | 7710.3033 | 8660.3052 | 9731.3664 | 10939.2028 | 12301.5942 | 13838.6574 | 15573.155 | 17530.8465 | 19740.885 | 22236.2671 | 25054.3427 | 28237.3926 | 31833.2832 | 35896.2082 | 40487.5292 | 45676.7284 |  | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 37.3135 | 49.4613 | 66.1365 | 89.1295 | 120.9636 | 165.201 | 226.8792 | 313.131 | 434.0704 | 604.0539 | 843.4819 | 1181.3692 | 1659.0164 |  | 91.0202 | 101.4117 | 113.0742 | 126.1684 | 140.876 | 157.4022 | 175.9786 | 196.8669 | 220.3629 | 246.8009 | 276.5586 | 310.063 | 347.7968 | 390.306 | 438.2078 | 492.2003 | 553.073 | 621.7192 | 699.1495 | 786.507 | 885.0855 | 996.3491 | 1121.9545 | 1263.7772 | 1423.9399 | 1604.8455 | 1809.2146 | 2040.1271 | 2301.0704 | 2595.9937 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 76.8083 | 87.1998 | 98.8623 | 111.9565 | 126.6641 | 143.1903 | 161.7667 | 182.655 | 206.151 | 232.589 | 262.3467 | 295.8511 | 333.5849 | 376.0941 | 423.9959 | 477.9884 | 538.8611 | 604.7085 | 676.6007 | 756.3563 | 844.4526 | 941.2034 | 1046.6416 | 1160.346 | 1281.1876 | 1406.9586 | 1533.8345 | 1655.5949 | 1762.5 | 1839.6703 |  | 432.9946 | 482.4282 | 537.9079 | 600.1988 | 670.1649 | 748.7819 | 837.152 | 936.5203 | 1048.2939 | 1174.0627 | 1315.6236 | 1475.0082 | 1654.5128 | 1856.7344 | 2084.6091 | 2341.4579 | 2631.0372 | 2957.5959 | 3325.9412 | 3741.5118 | 4210.4622 | 4739.7567 | 5337.2775 | 6011.9457 | 6773.8594 | 7634.45 | 8606.659 | 9705.1385 | 10946.4787 | 12349.4653 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 432.928 | 482.3616 | 537.8413 | 600.1322 | 670.0983 | 748.7153 | 837.0854 | 936.4537 | 1048.2273 | 1173.9961 | 1315.557 | 1474.9416 | 1654.4463 | 1856.6678 | 2084.5425 | 2341.3914 | 2630.9706 | 2957.5162 | 3325.8355 | 3741.3706 | 4210.2718 | 4739.4984 | 5336.9247 | 6011.4611 | 6773.1906 | 7633.523 | 8605.3689 | 9703.3371 | 10943.9557 | 12345.9222 |  | 509.7363 | 569.5614 | 636.7036 | 712.0887 | 796.7624 | 891.9056 | 998.852 | 1119.1087 | 1254.3784 | 1406.5851 | 1577.9037 | 1770.7927 | 1988.0312 | 2232.7619 | 2508.5384 | 2819.3797 | 3169.8317 | 3562.2247 | 4002.4363 | 4497.7269 | 5054.7244 | 5680.7018 | 6383.5663 | 7171.8072 | 8054.3783 | 9040.4816 | 10139.2034 | 11358.9321 | 12706.4558 | 14185.5925 |  | 55.317 | 61.6324 | 68.7201 | 76.6781 | 85.6166 | 95.6602 | 106.9499 | 119.6447 | 133.9242 | 149.9917 | 168.0768 | 188.4389 | 211.3714 | 237.2061 | 266.3181 | 299.1317 | 336.1268 | 377.8461 | 424.9038 | 477.9948 | 537.9054 | 605.5251 | 681.861 | 768.0529 | 865.3908 | 975.3351 | 1099.5391 | 1239.8748 | 1398.4616 | 1577.6994 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 40.6459 | 46.9612 | 54.049 | 62.0069 | 70.9454 | 80.9891 | 92.2788 | 104.9735 | 119.2531 | 135.3206 | 153.4057 | 173.7677 | 196.7003 | 222.535 | 251.647 | 284.4606 | 321.4556 | 360.2857 | 401.6265 | 446.8698 | 495.9594 | 548.5974 | 604.1144 | 661.2794 | 718.0256 | 771.0537 | 815.2604 | 842.9168 | 842.4877 | 796.936 |  | 6.5749 | 7.3255 | 8.168 | 9.1138 | 10.1763 | 11.37 | 12.7119 | 14.2208 | 15.918 | 17.8278 | 19.9774 | 22.3976 | 25.1233 | 28.194 | 31.6542 | 35.5544 | 39.9516 | 44.9103 | 50.5035 | 56.8138 | 63.9347 | 71.9719 | 81.0451 | 91.2897 | 102.8591 | 115.927 | 130.6897 | 147.3698 | 166.2192 | 187.5231 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 4.5072 | 5.2578 | 6.1003 | 7.0462 | 8.1086 | 9.3023 | 10.6442 | 12.1531 | 13.8504 | 15.7601 | 17.9097 | 20.3299 | 23.0556 | 26.1263 | 29.5865 | 33.4867 | 37.8839 | 42.4354 | 47.2229 | 52.4272 | 58.023 | 63.9487 | 70.0877 | 76.2415 | 82.0901 | 87.1363 | 90.6245 | 91.4241 | 87.8624 | 77.4853 |  | 1015.602 | 1131.55 | 1261.6793 | 1407.7845 | 1571.8921 | 1756.2906 | 1963.5654 | 2196.6369 | 2458.8053 | 2753.7997 | 3085.8353 | 3459.6766 | 3880.7103 | 4355.027 | 4889.5141 | 5491.9609 | 6171.1779 | 6937.1313 | 7801.0963 | 8775.8299 | 9875.7673 | 11117.2438 | 12518.7469 | 14101.2016 | 15888.2935 | 17906.835 | 20187.1808 | 22763.698 | 25675.2993 | 28966.047 |  | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.18691 | 0.24776 | 0.33129 | 0.44647 | 0.60594 | 0.82753 | 1.1365 | 1.5686 | 2.1744 | 3.0259 | 4.2252 | 5.9178 | 8.3104 |  | 1015.4458 | 1131.3938 | 1261.5232 | 1407.6284 | 1571.7359 | 1756.1345 | 1963.4092 | 2196.4808 | 2458.6491 | 2753.6435 | 3085.6791 | 3459.5204 | 3880.5541 | 4354.8708 | 4889.3579 | 5491.8048 | 6171.0217 | 6936.9444 | 7800.8485 | 8775.4986 | 9875.3208 | 11116.6378 | 12517.9194 | 14100.0651 | 15886.7249 | 17904.6606 | 20184.1549 | 22759.4728 | 25669.3815 | 28957.7365 |  | 1570.3352 | 1753.1744 | 1958.376 | 2188.7702 | 2447.5523 | 2738.3315 | 3065.1843 | 3432.7161 | 3846.1309 | 4311.3094 | 4834.8982 | 5424.4107 | 6088.3412 | 6836.294 | 7679.1298 | 8629.1317 | 9700.1929 | 10901.8901 | 12252.1341 | 13772.5224 | 15484.0276 | 17409.8858 | 19575.6878 | 22009.3932 | 24741.2189 | 27803.3322 | 31229.2432 | 35052.7458 | 39306.1873 | 44017.7504
| TRUE | 3834 | 22002957 | SHN | Blank | 22 | BUS NO.2 | SINGLE ZONE BUS DIST | X | ASEA | GROUP_3075 | GROUP 3075 | GROUP 3000s | Electronic |  | 0.033587 | 2190 |  | 9.9 | 0.042792 | 0.0040364 | 0.038756 | 237.5764 | 1130.1807 | 1367.7571 | 144.3856 | 17.1615 | 2650.8732 |  | 16.087 | 0.16393 | 0.015463 | 0.14847 | 910.1185 | 4329.5472 | 5239.6658 | 553.119 | 65.743 | 10155.0849 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.15616 |  | 4180.1774 | 16013.6127 | 45.3853 | 15968.2273 |  | 0.048548 |  | 10.3925 | 10.9095 | 11.4522 | 12.0218 | 12.6199 | 13.2477 | 13.9067 | 14.5985 | 15.3247 | 16.087 | 16.8873 | 17.7273 | 18.6092 | 19.5349 | 20.5067 | 21.5268 | 22.5976 | 23.7218 | 24.9018 | 26.1406 | 27.4409 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.04881 | 0.055712 | 0.063632 | 0.072723 | 0.083163 | 0.095155 | 0.10893 | 0.12477 | 0.14298 | 0.16393 | 0.18803 | 0.21575 | 0.24767 | 0.28441 | 0.32672 | 0.37545 | 0.43158 | 0.49627 | 0.57081 | 0.65674 | 0.75579 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.004604 | 0.005255 | 0.0060021 | 0.0068596 | 0.0078443 | 0.0089755 | 0.010275 | 0.011769 | 0.013487 | 0.015463 | 0.017735 | 0.020351 | 0.023361 | 0.026827 | 0.030817 | 0.035414 | 0.040709 | 0.04681 | 0.053842 | 0.061947 | 0.07129 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 4767.9997 | 5442.2415 | 6215.9114 | 7104.0051 | 8123.8109 | 9295.2638 | 10641.354 | 12188.5988 | 13967.5877 | 16013.6127 | 18367.3955 | 21075.9293 | 24193.45 | 27782.5594 | 31915.5231 | 36675.7702 | 42159.6269 | 48478.32 | 55760.293 | 64153.8825 | 73830.4127 | 78273.4573 | 78273.4573 | 78273.4573 | 78273.4573 | 78273.4573 | 78273.4573 | 78273.4573 | 78273.4573 | 78273.4573 |  | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 37.3135 | 49.4613 | 66.1365 | 89.1295 | 120.9636 | 165.201 | 226.8792 | 313.131 | 434.0704 | 604.0539 | 843.4819 | 1181.3692 | 1659.0164 |  | 270.9848 | 309.3047 | 353.2755 | 403.7494 | 461.7091 | 528.2875 | 604.7913 | 692.7275 | 793.8346 | 910.1185 | 1043.8936 | 1197.8305 | 1375.0119 | 1578.9955 | 1813.8886 | 2084.4327 | 2396.1025 | 2755.2195 | 3169.0835 | 3646.1253 | 4196.0817 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 256.7729 | 295.0928 | 339.0636 | 389.5375 | 447.4972 | 514.0756 | 590.5794 | 678.5156 | 779.6228 | 895.9066 | 1029.6817 | 1183.6186 | 1360.8 | 1564.7836 | 1799.6767 | 2070.2208 | 2381.8906 | 2738.2087 | 3146.5348 | 3615.9745 | 4155.4488 | 4393.4523 | 4373.285 | 4345.1668 | 4305.8457 | 4250.7111 | 4173.2179 | 4064.0658 | 3910.0276 | 3692.2746 |  | 1289.1082 | 1471.4007 | 1680.5753 | 1920.6863 | 2196.4078 | 2513.1296 | 2877.0675 | 3295.391 | 3776.3703 | 4329.5472 | 4965.9317 | 5698.229 | 6541.1027 | 7511.4783 | 8628.8939 | 9915.9061 | 11398.5582 | 13106.9223 | 15075.7251 | 17345.072 | 19961.2834 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 1289.0417 | 1471.3342 | 1680.5087 | 1920.6197 | 2196.3412 | 2513.063 | 2877.001 | 3295.3244 | 3776.3037 | 4329.4807 | 4965.8651 | 5698.1624 | 6541.0361 | 7511.4117 | 8628.8274 | 9915.8395 | 11398.4917 | 13106.8426 | 15075.6195 | 17344.9308 | 19961.093 | 21162.2762 | 21162.1818 | 21162.05 | 21161.8658 | 21161.6076 | 21161.2445 | 21160.7332 | 21160.0116 | 21158.9915 |  | 1545.8145 | 1766.4269 | 2019.5723 | 2310.1572 | 2643.8384 | 3027.1387 | 3467.5804 | 3973.84 | 4555.9265 | 5225.3873 | 5995.5468 | 6881.781 | 7901.8361 | 9076.1953 | 10428.5041 | 11986.0604 | 13780.3823 | 15845.0514 | 18222.1543 | 20960.9053 | 24116.5418 | 25555.7285 | 25535.4668 | 25507.2168 | 25467.7116 | 25412.3186 | 25334.4624 | 25224.799 | 25070.0391 | 24851.2661 |  | 164.6893 | 187.978 | 214.701 | 245.3762 | 280.6009 | 321.0635 | 367.5582 | 421.0009 | 482.4482 | 553.119 | 634.42 | 727.9742 | 835.6551 | 959.6249 | 1102.3797 | 1266.8013 | 1456.2167 | 1674.4679 | 1925.9912 | 2215.9104 | 2550.1431 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 150.0182 | 173.3069 | 200.0299 | 230.7051 | 265.9298 | 306.3924 | 352.8871 | 406.3298 | 467.777 | 538.4479 | 619.7488 | 713.3031 | 820.984 | 944.9538 | 1087.7086 | 1252.1302 | 1441.5456 | 1656.9074 | 1902.7138 | 2184.7854 | 2508.1972 | 2646.6807 | 2625.8617 | 2596.8349 | 2556.2432 | 2499.3269 | 2419.3296 | 2306.6504 | 2147.6344 | 1922.8449 |  | 19.5747 | 22.3428 | 25.5191 | 29.1651 | 33.3518 | 38.1612 | 43.6875 | 50.0396 | 57.3431 | 65.743 | 75.4063 | 86.526 | 99.3248 | 114.0597 | 131.0273 | 150.5702 | 173.0839 | 199.0249 | 228.9206 | 263.38 | 303.1064 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 17.5071 | 20.2751 | 23.4514 | 27.0974 | 31.2841 | 36.0935 | 41.6198 | 47.9719 | 55.2754 | 63.6753 | 73.3386 | 84.4583 | 97.2571 | 111.992 | 128.9596 | 148.5025 | 171.0162 | 196.55 | 225.64 | 258.9934 | 297.1947 | 313.3239 | 310.3898 | 306.2989 | 300.578 | 292.5565 | 281.2819 | 265.4014 | 242.9903 | 211.3093 |  | 3023.6427 | 3451.2153 | 3941.8406 | 4505.0281 | 5151.7413 | 5894.622 | 6748.2495 | 7729.4399 | 8857.5915 | 10155.0849 | 11647.744 | 13365.3696 | 15342.3556 | 17618.4011 | 20239.3335 | 23258.0598 | 26735.6655 | 30742.6854 | 35360.5724 | 40683.3947 | 46819.7981 | 49637.3694 | 49637.3694 | 49637.3694 | 49637.3694 | 49637.3694 | 49637.3694 | 49637.3694 | 49637.3694 | 49637.3694 |  | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.18691 | 0.24776 | 0.33129 | 0.44647 | 0.60594 | 0.82753 | 1.1365 | 1.5686 | 2.1744 | 3.0259 | 4.2252 | 5.9178 | 8.3104 |  | 3023.4865 | 3451.0591 | 3941.6844 | 4504.8719 | 5151.5851 | 5894.4658 | 6748.0934 | 7729.2837 | 8857.4354 | 10154.9288 | 11647.5879 | 13365.2134 | 15342.1994 | 17618.2449 | 20239.1774 | 23257.9036 | 26735.5093 | 30742.4985 | 35360.3247 | 40683.0634 | 46819.3516 | 49636.7634 | 49636.5418 | 49636.2329 | 49635.8008 | 49635.195 | 49634.3435 | 49633.1442 | 49631.4516 | 49629.0589 |  | 4736.8263 | 5411.068 | 6184.738 | 7072.8316 | 8092.6374 | 9264.0903 | 10610.1806 | 12157.4254 | 13936.4143 | 15982.4392 | 18336.222 | 21044.7559 | 24162.2765 | 27751.386 | 31884.3497 | 36644.5967 | 42128.4534 | 48441.0073 | 55710.8328 | 64087.7475 | 73741.2853 | 78152.4966 | 78108.2601 | 78046.5834 | 77960.3336 | 77839.397 | 77669.4174 | 77429.9949 | 77092.1154 | 76614.4793
| TRUE | 3835 | 22002955 | SHN | Blank | 22 | BUS NO.2 | HIBP | X | ABB | RADHA_2524 | RADHA 2524 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 81.7572 | 388.9293 | 470.6866 | 49.6875 | 5.9058 | 912.2456 |  | 10.0404 | 0.044454 | 0.0041931 | 0.040261 | 246.8009 | 1174.0627 | 1420.8636 | 149.9917 | 17.8278 | 2753.7997 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.15616 |  | 1438.5254 | 4342.4828 | 45.3853 | 4297.0975 |  | 0.041955 |  | 6.8828 | 7.1777 | 7.4852 | 7.806 | 8.1404 | 8.4892 | 8.853 | 9.2323 | 9.6279 | 10.0404 | 10.4706 | 10.9192 | 11.3871 | 11.875 | 12.3838 | 12.9144 | 13.4678 | 14.0448 | 14.6466 | 15.2742 | 15.9286 | 16.6111 | 17.3229 | 18.0651 | 18.8392 | 19.6464 | 20.4882 | 21.366 | 22.2815 | 23.2362 |  | 0.016394 | 0.018266 | 0.020367 | 0.022725 | 0.025374 | 0.028351 | 0.031697 | 0.03546 | 0.039692 | 0.044454 | 0.049814 | 0.055848 | 0.062645 | 0.070302 | 0.07893 | 0.088655 | 0.099619 | 0.11198 | 0.12593 | 0.14167 | 0.15942 | 0.17946 | 0.20209 | 0.22763 | 0.25648 | 0.28906 | 0.32587 | 0.36747 | 0.41447 | 0.46759 |  | 0.0015464 | 0.001723 | 0.0019211 | 0.0021436 | 0.0023934 | 0.0026742 | 0.0029898 | 0.0033447 | 0.0037439 | 0.0041931 | 0.0046987 | 0.0052679 | 0.005909 | 0.0066312 | 0.007445 | 0.0083623 | 0.0093966 | 0.010563 | 0.011878 | 0.013363 | 0.015037 | 0.016928 | 0.019062 | 0.021471 | 0.024192 | 0.027266 | 0.030738 | 0.034661 | 0.039095 | 0.044105 | 1601.5087 | 1784.3478 | 1989.5495 | 2219.9436 | 2478.7258 | 2769.505 | 3096.3577 | 3463.8896 | 3877.3044 | 4342.4828 | 4866.0716 | 5455.5842 | 6119.5147 | 6867.4674 | 7710.3033 | 8660.3052 | 9731.3664 | 10939.2028 | 12301.5942 | 13838.6574 | 15573.155 | 17530.8465 | 19740.885 | 22236.2671 | 25054.3427 | 28237.3926 | 31833.2832 | 35896.2082 | 40487.5292 | 45676.7284 |  | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 31.1742 | 37.3135 | 49.4613 | 66.1365 | 89.1295 | 120.9636 | 165.201 | 226.8792 | 313.131 | 434.0704 | 604.0539 | 843.4819 | 1181.3692 | 1659.0164 |  | 91.0202 | 101.4117 | 113.0742 | 126.1684 | 140.876 | 157.4022 | 175.9786 | 196.8669 | 220.3629 | 246.8009 | 276.5586 | 310.063 | 347.7968 | 390.306 | 438.2078 | 492.2003 | 553.073 | 621.7192 | 699.1495 | 786.507 | 885.0855 | 996.3491 | 1121.9545 | 1263.7772 | 1423.9399 | 1604.8455 | 1809.2146 | 2040.1271 | 2301.0704 | 2595.9937 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 76.8083 | 87.1998 | 98.8623 | 111.9565 | 126.6641 | 143.1903 | 161.7667 | 182.655 | 206.151 | 232.589 | 262.3467 | 295.8511 | 333.5849 | 376.0941 | 423.9959 | 477.9884 | 538.8611 | 604.7085 | 676.6007 | 756.3563 | 844.4526 | 941.2034 | 1046.6416 | 1160.346 | 1281.1876 | 1406.9586 | 1533.8345 | 1655.5949 | 1762.5 | 1839.6703 |  | 432.9946 | 482.4282 | 537.9079 | 600.1988 | 670.1649 | 748.7819 | 837.152 | 936.5203 | 1048.2939 | 1174.0627 | 1315.6236 | 1475.0082 | 1654.5128 | 1856.7344 | 2084.6091 | 2341.4579 | 2631.0372 | 2957.5959 | 3325.9412 | 3741.5118 | 4210.4622 | 4739.7567 | 5337.2775 | 6011.9457 | 6773.8594 | 7634.45 | 8606.659 | 9705.1385 | 10946.4787 | 12349.4653 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 432.928 | 482.3616 | 537.8413 | 600.1322 | 670.0983 | 748.7153 | 837.0854 | 936.4537 | 1048.2273 | 1173.9961 | 1315.557 | 1474.9416 | 1654.4463 | 1856.6678 | 2084.5425 | 2341.3914 | 2630.9706 | 2957.5162 | 3325.8355 | 3741.3706 | 4210.2718 | 4739.4984 | 5336.9247 | 6011.4611 | 6773.1906 | 7633.523 | 8605.3689 | 9703.3371 | 10943.9557 | 12345.9222 |  | 509.7363 | 569.5614 | 636.7036 | 712.0887 | 796.7624 | 891.9056 | 998.852 | 1119.1087 | 1254.3784 | 1406.5851 | 1577.9037 | 1770.7927 | 1988.0312 | 2232.7619 | 2508.5384 | 2819.3797 | 3169.8317 | 3562.2247 | 4002.4363 | 4497.7269 | 5054.7244 | 5680.7018 | 6383.5663 | 7171.8072 | 8054.3783 | 9040.4816 | 10139.2034 | 11358.9321 | 12706.4558 | 14185.5925 |  | 55.317 | 61.6324 | 68.7201 | 76.6781 | 85.6166 | 95.6602 | 106.9499 | 119.6447 | 133.9242 | 149.9917 | 168.0768 | 188.4389 | 211.3714 | 237.2061 | 266.3181 | 299.1317 | 336.1268 | 377.8461 | 424.9038 | 477.9948 | 537.9054 | 605.5251 | 681.861 | 768.0529 | 865.3908 | 975.3351 | 1099.5391 | 1239.8748 | 1398.4616 | 1577.6994 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 40.6459 | 46.9612 | 54.049 | 62.0069 | 70.9454 | 80.9891 | 92.2788 | 104.9735 | 119.2531 | 135.3206 | 153.4057 | 173.7677 | 196.7003 | 222.535 | 251.647 | 284.4606 | 321.4556 | 360.2857 | 401.6265 | 446.8698 | 495.9594 | 548.5974 | 604.1144 | 661.2794 | 718.0256 | 771.0537 | 815.2604 | 842.9168 | 842.4877 | 796.936 |  | 6.5749 | 7.3255 | 8.168 | 9.1138 | 10.1763 | 11.37 | 12.7119 | 14.2208 | 15.918 | 17.8278 | 19.9774 | 22.3976 | 25.1233 | 28.194 | 31.6542 | 35.5544 | 39.9516 | 44.9103 | 50.5035 | 56.8138 | 63.9347 | 71.9719 | 81.0451 | 91.2897 | 102.8591 | 115.927 | 130.6897 | 147.3698 | 166.2192 | 187.5231 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 4.5072 | 5.2578 | 6.1003 | 7.0462 | 8.1086 | 9.3023 | 10.6442 | 12.1531 | 13.8504 | 15.7601 | 17.9097 | 20.3299 | 23.0556 | 26.1263 | 29.5865 | 33.4867 | 37.8839 | 42.4354 | 47.2229 | 52.4272 | 58.023 | 63.9487 | 70.0877 | 76.2415 | 82.0901 | 87.1363 | 90.6245 | 91.4241 | 87.8624 | 77.4853 |  | 1015.602 | 1131.55 | 1261.6793 | 1407.7845 | 1571.8921 | 1756.2906 | 1963.5654 | 2196.6369 | 2458.8053 | 2753.7997 | 3085.8353 | 3459.6766 | 3880.7103 | 4355.027 | 4889.5141 | 5491.9609 | 6171.1779 | 6937.1313 | 7801.0963 | 8775.8299 | 9875.7673 | 11117.2438 | 12518.7469 | 14101.2016 | 15888.2935 | 17906.835 | 20187.1808 | 22763.698 | 25675.2993 | 28966.047 |  | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.15616 | 0.18691 | 0.24776 | 0.33129 | 0.44647 | 0.60594 | 0.82753 | 1.1365 | 1.5686 | 2.1744 | 3.0259 | 4.2252 | 5.9178 | 8.3104 |  | 1015.4458 | 1131.3938 | 1261.5232 | 1407.6284 | 1571.7359 | 1756.1345 | 1963.4092 | 2196.4808 | 2458.6491 | 2753.6435 | 3085.6791 | 3459.5204 | 3880.5541 | 4354.8708 | 4889.3579 | 5491.8048 | 6171.0217 | 6936.9444 | 7800.8485 | 8775.4986 | 9875.3208 | 11116.6378 | 12517.9194 | 14100.0651 | 15886.7249 | 17904.6606 | 20184.1549 | 22759.4728 | 25669.3815 | 28957.7365 |  | 1570.3352 | 1753.1744 | 1958.376 | 2188.7702 | 2447.5523 | 2738.3315 | 3065.1843 | 3432.7161 | 3846.1309 | 4311.3094 | 4834.8982 | 5424.4107 | 6088.3412 | 6836.294 | 7679.1298 | 8629.1317 | 9700.1929 | 10901.8901 | 12252.1341 | 13772.5224 | 15484.0276 | 17409.8858 | 19575.6878 | 22009.3932 | 24741.2189 | 27803.3322 | 31229.2432 | 35052.7458 | 39306.1873 | 44017.7504
| TRUE | 3836 | 22002966 | SHN | Blank | 22 | CAP NO.1 | CAP CONTROL | C | Siemens | DED_760 | DED 760 | DED | Electronic |  | 0 | 2190 |  | 6.6 | 0.014726 | 0 | 0.014726 | 80.9933 | 0 | 80.9933 | 41.8016 | 5.8919 | 0 |  | 10.0404 | 0.044454 | 0 | 0.044454 | 244.4947 | 0 | 244.4947 | 126.1867 | 17.7859 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 128.6867 | 388.4672 | 45.1611 | 343.3061 |  | 0.041955 |  | 6.8828 | 7.1777 | 7.4852 | 7.806 | 8.1404 | 8.4892 | 8.853 | 9.2323 | 9.6279 | 10.0404 | 10.4706 | 10.9192 | 11.3871 | 11.875 | 12.3838 | 12.9144 | 13.4678 | 14.0448 | 14.6466 | 15.2742 | 15.9286 | 16.6111 | 17.3229 | 18.0651 | 18.8392 | 19.6464 | 20.4882 | 21.366 | 22.2815 | 23.2362 |  | 0.016394 | 0.018266 | 0.020367 | 0.022725 | 0.025374 | 0.028351 | 0.031697 | 0.03546 | 0.039692 | 0.044454 | 0.049814 | 0.055848 | 0.062645 | 0.070302 | 0.07893 | 0.088655 | 0.099619 | 0.11198 | 0.12593 | 0.14167 | 0.15942 | 0.17946 | 0.20209 | 0.22763 | 0.25648 | 0.28906 | 0.32587 | 0.36747 | 0.41447 | 0.46759 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143.2668 | 159.6231 | 177.9799 | 198.5904 | 221.7404 | 247.7527 | 276.9921 | 309.8706 | 346.8536 | 388.4672 | 435.3061 | 488.0424 | 547.4359 | 614.3458 | 689.7437 | 774.7284 | 870.5428 | 978.5927 | 1100.4687 | 1237.9704 | 1393.134 | 1568.264 | 1765.9684 | 1989.1988 | 2241.2965 | 2526.0439 | 2847.7229 | 3211.1816 | 3621.9093 | 4086.1216 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 90.1697 | 100.4641 | 112.0176 | 124.9894 | 139.5596 | 155.9314 | 174.3342 | 195.0273 | 218.3038 | 244.4947 | 273.9743 | 307.1656 | 344.5469 | 386.6589 | 434.113 | 487.601 | 547.9049 | 615.9097 | 692.6164 | 779.1576 | 876.815 | 987.0389 | 1111.4706 | 1251.968 | 1410.6341 | 1589.8493 | 1792.3086 | 2021.0634 | 2279.5684 | 2571.7358 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 75.9579 | 86.2523 | 97.8057 | 110.7776 | 125.3478 | 141.7196 | 160.1223 | 180.8155 | 204.092 | 230.2829 | 259.7625 | 292.9538 | 330.3351 | 372.447 | 419.9012 | 473.3891 | 533.6931 | 598.899 | 670.0677 | 749.007 | 836.1822 | 931.8934 | 1036.158 | 1148.5373 | 1267.8825 | 1391.9633 | 1516.9298 | 1636.5331 | 1741.0005 | 1815.4159 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 75.9579 | 86.2523 | 97.8057 | 110.7776 | 125.3478 | 141.7196 | 160.1223 | 180.8155 | 204.092 | 230.2829 | 259.7625 | 292.9538 | 330.3351 | 372.447 | 419.9012 | 473.3891 | 533.6931 | 598.899 | 670.0677 | 749.007 | 836.1822 | 931.8934 | 1036.158 | 1148.5373 | 1267.8825 | 1391.9633 | 1516.9298 | 1636.5331 | 1741.0005 | 1815.4159 |  | 46.5377 | 51.8507 | 57.8136 | 64.5085 | 72.0284 | 80.4781 | 89.976 | 100.6559 | 112.6692 | 126.1867 | 141.4014 | 158.5319 | 177.8248 | 199.5593 | 224.0509 | 251.6567 | 282.7803 | 317.8784 | 357.4676 | 402.1326 | 452.5347 | 509.4226 | 573.6433 | 646.1557 | 728.0452 | 820.5403 | 925.032 | 1043.0951 | 1176.5126 | 1327.3037 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 31.8679 | 37.1809 | 43.1438 | 49.8388 | 57.3586 | 65.8083 | 75.3062 | 85.9861 | 97.9994 | 111.5169 | 126.7316 | 143.8621 | 163.155 | 184.8895 | 209.3812 | 236.9869 | 268.1105 | 300.3196 | 334.1924 | 371.0104 | 410.5927 | 452.5002 | 495.9038 | 539.3921 | 580.6936 | 616.2777 | 640.7794 | 646.1736 | 620.5899 | 546.6122 |  | 6.5594 | 7.3083 | 8.1488 | 9.0924 | 10.1523 | 11.3433 | 12.682 | 14.1873 | 15.8806 | 17.7859 | 19.9304 | 22.3449 | 25.0642 | 28.1277 | 31.5797 | 35.4708 | 39.8576 | 44.8046 | 50.3847 | 56.6802 | 63.7843 | 71.8026 | 80.8544 | 91.075 | 102.6172 | 115.6543 | 130.3823 | 147.0232 | 165.8282 | 187.0821 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 4.4917 | 5.2406 | 6.0811 | 7.0247 | 8.0846 | 9.2756 | 10.6143 | 12.1197 | 13.8129 | 15.7182 | 17.8627 | 20.2772 | 22.9965 | 26.06 | 29.5121 | 33.4031 | 37.7899 | 42.3297 | 47.1041 | 52.2935 | 57.8726 | 63.7794 | 69.8971 | 76.0268 | 81.8482 | 86.8637 | 90.3172 | 91.0775 | 87.4715 | 77.0444 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 112.3175 | 128.6738 | 147.0306 | 167.6411 | 190.7911 | 216.8034 | 246.0428 | 278.9213 | 315.9043 | 357.5179 | 404.3568 | 457.0931 | 516.4866 | 583.3965 | 658.7944 | 743.7791 | 839.5935 | 941.5483 | 1051.3642 | 1172.311 | 1304.6475 | 1448.1731 | 1601.959 | 1763.9562 | 1930.4242 | 2095.1047 | 2248.0264 | 2373.7842 | 2449.0619 | 2439.0725
| TRUE | 3837 | 22002965 | SHN | Blank | 22 | CAP NO.1 | NEUTRAL BALANCE | X | ASEA | GROUP_2945 | GROUP 2945 | GROUP 2000s | Electronic |  | 0.2894 | 2190 |  | 8.25 | 0.026286 | 0.013817 | 0.012468 | 152.1704 | 3868.8382 | 4021.0086 | 153.0587 | 10.655 | 9074.4779 |  | 13.0142 | 0.090569 | 0.047609 | 0.042961 | 524.316 | 13330.4101 | 13854.7262 | 527.3766 | 36.7129 | 31266.883 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.57365 | 28.9984 | 14.6814 | 2.0677 | 1.3455 |  | 13259.2003 | 45685.6987 | 47.0931 | 45638.6056 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.015591 | 0.017605 | 0.019894 | 0.022495 | 0.025452 | 0.028816 | 0.032643 | 0.037 | 0.04196 | 0.047609 | 0.054044 | 0.061378 | 0.069737 | 0.079268 | 0.090138 | 0.10254 | 0.11668 | 0.13283 | 0.15126 | 0.1723 | 0.19632 | 0.22376 | 0.2551 | 0.2909 | 0.33182 | 0.37858 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 14961.2126 | 16894.1271 | 19090.1721 | 21586.1527 | 24424.1074 | 27652.0608 | 31324.8839 | 35505.2802 | 40264.9132 | 45685.6987 | 51861.2835 | 58898.739 | 66920.5004 | 76066.5875 | 86497.148 | 98395.3705 | 111970.8203 | 127463.261 | 145147.0319 | 165336.061 | 188389.6098 | 214718.8523 | 244794.4137 | 279155.0063 | 318417.324 | 363287.3792 | 404186.9991 | 404186.9991 | 404186.9991 | 404186.9991 |  | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 39.3635 | 52.1787 | 69.77 | 94.0262 | 127.6093 | 174.2772 | 239.3439 | 330.3344 | 457.9181 | 637.2405 | 889.8227 | 1246.2734 | 1750.1625 |  | 171.7037 | 193.887 | 219.0901 | 247.7354 | 280.3055 | 317.3513 | 359.5028 | 407.4795 | 462.1039 | 524.316 | 595.1907 | 675.9566 | 768.0191 | 872.985 | 992.6923 | 1129.2433 | 1285.0431 | 1462.8435 | 1665.7929 | 1897.4941 | 2162.0702 | 2464.2401 | 2809.405 | 3203.7474 | 3654.3449 | 4169.3001 | 4638.6883 | 4638.6883 | 4638.6883 | 4638.6883 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 157.4913 | 179.6746 | 204.8777 | 233.523 | 266.0931 | 303.139 | 345.2904 | 393.2671 | 447.8915 | 510.1036 | 580.9783 | 661.7443 | 753.8067 | 858.7726 | 978.4799 | 1115.0309 | 1270.8307 | 1445.8322 | 1643.2434 | 1867.3423 | 2121.4359 | 2409.0925 | 2734.0894 | 3100.3126 | 3511.5877 | 3971.4063 | 4363.2985 | 4254.1427 | 4100.099 | 3882.3384 |  | 4365.4602 | 4929.456 | 5570.2295 | 6298.5196 | 7126.5928 | 8068.4617 | 9140.1371 | 10359.9148 | 11748.7052 | 13330.4101 | 15132.3543 | 17185.7796 | 19526.4107 | 22195.1035 | 25238.5866 | 28710.3116 | 32671.4268 | 37191.8915 | 42351.7539 | 48242.6136 | 54969.2976 | 62651.7806 | 71427.3839 | 81453.2958 | 92909.4586 | 106001.8761 | 117935.7793 | 117935.7793 | 117935.7793 | 117935.7793 |  | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.68662 | 0.91016 | 1.217 | 1.6401 | 2.2259 | 3.0399 | 4.1749 | 5.7621 | 7.9875 | 11.1155 | 15.5213 | 21.7389 | 30.5284 |  | 4364.8866 | 4928.8824 | 5569.6558 | 6297.946 | 7126.0191 | 8067.8881 | 9139.5635 | 10359.3412 | 11748.1316 | 13329.8365 | 15131.7807 | 17185.2059 | 19525.8371 | 22194.5298 | 25238.0129 | 28709.738 | 32670.8531 | 37191.2049 | 42350.8437 | 48241.3966 | 54967.6575 | 62649.5547 | 71424.344 | 81449.1209 | 92903.6965 | 105993.8885 | 117924.6638 | 117920.258 | 117914.0404 | 117905.251 |  | 4522.3779 | 5108.557 | 5774.5335 | 6531.469 | 7392.1122 | 8371.027 | 9484.8539 | 10752.6083 | 12196.0231 | 13839.9401 | 15712.7589 | 17846.9502 | 20279.6438 | 23053.3025 | 26216.4928 | 29824.7689 | 33941.6839 | 38637.0371 | 43994.0871 | 50108.7389 | 57089.0934 | 65058.6472 | 74158.4334 | 84549.4335 | 96415.2842 | 109965.2948 | 122287.9623 | 122174.4007 | 122014.1394 | 121787.5893 |  | 172.706 | 195.0188 | 220.369 | 249.1815 | 281.9417 | 319.2039 | 361.6014 | 409.8581 | 464.8014 | 527.3766 | 598.665 | 679.9025 | 772.5023 | 878.0809 | 998.487 | 1135.8351 | 1292.5444 | 1471.3827 | 1675.5168 | 1908.5705 | 2174.691 | 2478.6248 | 2825.8046 | 3222.4489 | 3675.6767 | 4193.6379 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 158.0246 | 180.3373 | 205.6876 | 234.5001 | 267.2603 | 304.5224 | 346.92 | 395.1767 | 450.1199 | 512.6952 | 583.9836 | 665.221 | 757.8209 | 863.3995 | 983.8056 | 1121.1537 | 1277.863 | 1453.81 | 1652.2231 | 1877.4237 | 2132.7157 | 2421.6573 | 2748.0035 | 3115.6006 | 3528.2083 | 3989.2133 | 4381.2881 | 4268.5299 | 4109.4026 | 3884.4555 |  | 12.0228 | 13.5761 | 15.3408 | 17.3466 | 19.6271 | 22.2211 | 25.1726 | 28.5319 | 32.3567 | 36.7129 | 41.6756 | 47.3308 | 53.7771 | 61.1269 | 69.5088 | 79.0702 | 89.9794 | 102.429 | 116.6397 | 132.8635 | 151.3892 | 172.5473 | 196.716 | 224.328 | 255.8791 | 291.9365 | 324.8033 | 324.8033 | 324.8033 | 324.8033 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 9.9551 | 11.5084 | 13.2731 | 15.2788 | 17.5594 | 20.1534 | 23.1049 | 26.4642 | 30.289 | 34.6452 | 39.6078 | 45.2631 | 51.7094 | 59.0591 | 67.4411 | 77.0025 | 87.9117 | 99.9541 | 113.359 | 128.4768 | 145.4775 | 164.5241 | 185.7586 | 209.2796 | 235.1098 | 263.1456 | 284.7378 | 268.8571 | 246.4458 | 214.7645 |  | 10239.3199 | 11562.1893 | 13065.1428 | 14773.3696 | 16715.6403 | 18924.8227 | 21438.47 | 24299.4958 | 27556.9459 | 31266.883 | 35493.3979 | 40309.7694 | 45799.7911 | 52059.2912 | 59197.8734 | 67340.9103 | 76631.8265 | 87234.7143 | 99337.3286 | 113154.5194 | 128932.1617 | 146951.6594 | 167535.1043 | 191051.1861 | 217921.9647 | 248630.6286 | 276621.9622 | 276621.9622 | 276621.9622 | 276621.9622 |  | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.6105 | 2.1348 | 2.8545 | 3.8469 | 5.2209 | 7.1303 | 9.7924 | 13.5151 | 18.735 | 26.0717 | 36.4057 | 50.9893 | 71.6052 |  | 10237.9744 | 11560.8438 | 13063.7973 | 14772.024 | 16714.2948 | 18923.4772 | 21437.1245 | 24298.1502 | 27555.6004 | 31265.5375 | 35492.0524 | 40308.4239 | 45798.4456 | 52057.9457 | 59196.5279 | 67339.5648 | 76630.481 | 87233.1038 | 99335.1938 | 113151.6648 | 128928.3147 | 146946.4385 | 167527.974 | 191041.3937 | 217908.4496 | 248611.8936 | 276595.8904 | 276585.5564 | 276570.9728 | 276550.357 |  | 14928.3319 | 16861.2464 | 19057.2915 | 21553.272 | 24391.2267 | 27619.1801 | 31292.0032 | 35472.3995 | 40232.0325 | 45652.818 | 51828.4028 | 58865.8583 | 66887.6197 | 76033.7068 | 86464.2674 | 98362.4898 | 111937.9396 | 127423.9049 | 145094.863 | 165266.3042 | 188295.6013 | 214591.2671 | 244620.1694 | 278915.7075 | 318087.0519 | 362829.5474 | 403549.8786 | 403297.3441 | 402940.9605 | 402437.1664
| TRUE | 3838 | 22002964 | SHN | Blank | 22 | CAP NO.1 | OC & EF | Blank | GEC | M1AM_3238 | M1AM 3238 | M1AM | Electronic |  | 0.2894 | 2190 |  | 5.5 | 0.0093284 | 0.0049035 | 0.0044248 | 54.003 | 1372.9933 | 1426.9963 | 54.3183 | 3.7813 | 3220.3976 |  | 8.1226 | 0.025228 | 0.013261 | 0.011967 | 146.0489 | 3713.202 | 3859.2508 | 146.9014 | 10.2264 | 8709.4283 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 28.4248 | 0.57365 | 28.9984 | 14.6814 | 2.0677 | 1.3455 |  | 4705.4934 | 12725.807 | 47.0931 | 12678.7139 |  | 0.03899 |  | 5.7187 | 5.9461 | 6.1825 | 6.4283 | 6.6839 | 6.9496 | 7.226 | 7.5133 | 7.812 | 8.1226 | 8.4456 | 8.7813 | 9.1305 | 9.4935 | 9.871 | 10.2635 | 10.6715 | 11.0958 | 11.537 | 11.9957 | 12.4727 | 12.9686 | 13.4842 | 14.0204 | 14.5778 | 15.1575 | 15.7601 | 16.3867 | 17.0383 | 17.7157 |  | 0.01027 | 0.011317 | 0.012479 | 0.013771 | 0.015208 | 0.016807 | 0.018586 | 0.020566 | 0.022771 | 0.025228 | 0.027966 | 0.031018 | 0.034422 | 0.038218 | 0.042454 | 0.047182 | 0.052459 | 0.058352 | 0.064935 | 0.072288 | 0.080506 | 0.089691 | 0.099958 | 0.11144 | 0.12428 | 0.13864 | 0.15471 | 0.1727 | 0.19282 | 0.21535 |  | 0.0053988 | 0.0059487 | 0.0065598 | 0.0072391 | 0.0079944 | 0.0088346 | 0.0097697 | 0.010811 | 0.01197 | 0.013261 | 0.014701 | 0.016305 | 0.018094 | 0.02009 | 0.022316 | 0.024801 | 0.027576 | 0.030673 | 0.034134 | 0.037999 | 0.042319 | 0.047147 | 0.052544 | 0.058579 | 0.065329 | 0.072879 | 0.081327 | 0.09078 | 0.10136 | 0.1132 | 5180.7069 | 5708.4795 | 6294.8777 | 6946.6866 | 7671.4961 | 8477.798 | 9375.0948 | 10374.0216 | 11486.483 | 12725.807 | 14106.9169 | 15646.525 | 17363.3496 | 19278.3584 | 21415.0418 | 23799.7202 | 26461.8875 | 29434.5984 | 32754.9022 | 36464.3297 | 40609.4402 | 45242.4356 | 50421.8501 | 56213.3238 | 62690.4724 | 69935.8631 | 78042.111 | 87113.1097 | 97265.4141 | 108629.793 |  | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 32.8869 | 39.3635 | 52.1787 | 69.77 | 94.0262 | 127.6093 | 174.2772 | 239.3439 | 330.3344 | 457.9181 | 637.2405 | 889.8227 | 1246.2734 | 1750.1625 |  | 59.4568 | 65.5139 | 72.2437 | 79.7243 | 88.0426 | 97.2962 | 107.5941 | 119.0584 | 131.8256 | 146.0489 | 161.8993 | 179.5687 | 199.272 | 221.2498 | 245.7716 | 273.1396 | 303.6922 | 337.8088 | 375.9146 | 418.4861 | 466.0579 | 519.2289 | 578.6709 | 645.1372 | 719.4728 | 802.6252 | 895.6573 | 999.7614 | 1116.2752 | 1246.6995 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 45.2445 | 51.3015 | 58.0313 | 65.5119 | 73.8302 | 83.0838 | 93.3817 | 104.846 | 117.6133 | 131.8365 | 147.6869 | 165.3564 | 185.0596 | 207.0374 | 231.5593 | 258.9272 | 289.4798 | 320.7975 | 353.365 | 388.3344 | 425.4235 | 464.0813 | 503.3553 | 541.7024 | 576.7156 | 604.7314 | 620.2675 | 615.2158 | 577.686 | 490.3497 |  | 1511.6535 | 1665.6498 | 1836.7521 | 2026.9402 | 2238.4289 | 2473.6959 | 2735.5138 | 3026.9858 | 3351.5856 | 3713.202 | 4116.1894 | 4565.4242 | 5066.3682 | 5625.1394 | 6248.592 | 6944.4058 | 7721.1868 | 8588.5798 | 9557.3953 | 10639.7513 | 11849.2331 | 13201.0726 | 14712.349 | 16402.2152 | 18292.1512 | 20406.2489 | 22771.532 | 25418.315 | 28380.6071 | 31696.5645 |  | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.57365 | 0.68662 | 0.91016 | 1.217 | 1.6401 | 2.2259 | 3.0399 | 4.1749 | 5.7621 | 7.9875 | 11.1155 | 15.5213 | 21.7389 | 30.5284 |  | 1511.0799 | 1665.0761 | 1836.1784 | 2026.3666 | 2237.8553 | 2473.1222 | 2734.9401 | 3026.4122 | 3351.0119 | 3712.6283 | 4115.6157 | 4564.8506 | 5065.7946 | 5624.5658 | 6248.0183 | 6943.8322 | 7720.6131 | 8587.8932 | 9556.4851 | 10638.5343 | 11847.593 | 13198.8466 | 14709.309 | 16398.0403 | 18286.3892 | 20398.2614 | 22760.4165 | 25402.7937 | 28358.8681 | 31666.0362 |  | 1556.3244 | 1716.3776 | 1894.2098 | 2091.8785 | 2311.6855 | 2556.2061 | 2828.3219 | 3131.2582 | 3468.6252 | 3844.4648 | 4263.3026 | 4730.2069 | 5250.8542 | 5831.6032 | 6479.5776 | 7202.7594 | 8010.093 | 8908.6907 | 9909.8502 | 11026.8686 | 12273.0165 | 13662.9279 | 15212.6643 | 16939.7427 | 18863.1047 | 21002.9928 | 23380.684 | 26018.0095 | 28936.5541 | 32156.3858 |  | 59.8039 | 65.8963 | 72.6654 | 80.1897 | 88.5565 | 97.8642 | 108.2222 | 119.7534 | 132.5952 | 146.9014 | 162.8444 | 180.617 | 200.4353 | 222.5413 | 247.2063 | 274.734 | 305.465 | 339.7807 | 378.1089 | 420.929 | 468.7784 | 522.2598 | 582.0488 | 648.9032 | 723.6727 | 807.3104 | 900.8856 | 1005.5974 | 1122.7914 | 1253.977 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 45.1225 | 51.2149 | 57.984 | 65.5082 | 73.8751 | 83.1827 | 93.5408 | 105.072 | 117.9137 | 132.22 | 148.1629 | 165.9355 | 185.7538 | 207.8599 | 232.5249 | 260.0526 | 290.7836 | 322.208 | 354.8152 | 389.7822 | 426.8031 | 465.2922 | 504.2477 | 542.0548 | 576.2042 | 602.8858 | 616.4076 | 608.3612 | 566.4278 | 472.6665 |  | 4.1632 | 4.5873 | 5.0585 | 5.5823 | 6.1648 | 6.8127 | 7.5338 | 8.3365 | 9.2305 | 10.2264 | 11.3363 | 12.5735 | 13.9531 | 15.492 | 17.2091 | 19.1254 | 21.2647 | 23.6535 | 26.3217 | 29.3026 | 32.6336 | 36.3567 | 40.5188 | 45.1728 | 50.3779 | 56.2002 | 62.7144 | 70.0038 | 78.1622 | 87.2945 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 2.0955 | 2.5196 | 2.9908 | 3.5146 | 4.0971 | 4.745 | 5.4661 | 6.2688 | 7.1628 | 8.1587 | 9.2686 | 10.5058 | 11.8854 | 13.4243 | 15.1413 | 17.0577 | 19.197 | 21.1786 | 23.0411 | 24.9159 | 26.7219 | 28.3334 | 29.5614 | 30.1245 | 29.6086 | 27.4093 | 22.6489 | 14.0576 | -0.19536 | -22.7442 |  | 3545.6294 | 3906.8322 | 4308.1579 | 4754.2501 | 5250.3032 | 5802.129 | 6416.2309 | 7099.8874 | 7861.2461 | 8709.4283 | 9654.6475 | 10708.3416 | 11883.3209 | 13193.9358 | 14656.2628 | 16288.3153 | 18110.2788 | 20144.7755 | 22417.1617 | 24955.8607 | 27792.7371 | 30963.5177 | 34508.2626 | 38471.8953 | 42904.7978 | 47863.4783 | 53411.3218 | 59619.432 | 66567.5783 | 74345.2574 |  | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.3455 | 1.6105 | 2.1348 | 2.8545 | 3.8469 | 5.2209 | 7.1303 | 9.7924 | 13.5151 | 18.735 | 26.0717 | 36.4057 | 50.9893 | 71.6052 |  | 3544.2839 | 3905.4867 | 4306.8124 | 4752.9046 | 5248.9577 | 5800.7835 | 6414.8854 | 7098.5419 | 7859.9006 | 8708.0828 | 9653.302 | 10706.9961 | 11881.9754 | 13192.5903 | 14654.9173 | 16286.9698 | 18108.9333 | 20143.165 | 22415.0269 | 24953.0061 | 27788.8902 | 30958.2968 | 34501.1323 | 38462.1029 | 42891.2827 | 47844.7433 | 53385.2501 | 59583.0263 | 66516.5889 | 74273.6522 |  | 5147.8263 | 5675.5988 | 6261.997 | 6913.8059 | 7638.6154 | 8444.9173 | 9342.2141 | 10341.1409 | 11453.6023 | 12692.9263 | 14074.0362 | 15613.6443 | 17330.4689 | 19245.4777 | 21382.1612 | 23766.8395 | 26429.0068 | 29395.2423 | 32702.7334 | 36394.5728 | 40515.4316 | 45114.8504 | 50247.6057 | 55974.025 | 62360.2002 | 69478.0313 | 77404.9905 | 86223.4547 | 96019.3755 | 106879.9602
| TRUE | 3839 | 22002961 | SHN | Blank | 22 | CB BT1-2 | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 498.1313 | 0 | 498.1313 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 791.4596 | 45.1611 | 746.2985 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.1882 | 292.6741 | 330.7184 | 373.9588 | 423.1235 | 479.0446 | 542.6727 | 615.0939 | 697.5498 | 791.4596 | 898.4455 | 1020.3625 | 1159.3315 | 1317.7785 | 1498.4776 | 1704.6026 | 1939.7838 | 2208.1751 | 2514.5289 | 2864.2839 | 3263.6638 | 3719.792 | 4240.8213 | 4836.0847 | 5516.2655 | 6293.5949 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 163.1287 | 184.2041 | 208.1485 | 235.3633 | 266.3068 | 301.5026 | 341.549 | 387.1297 | 439.0261 | 498.1313 | 565.4664 | 642.1989 | 729.6637 | 829.3875 | 943.1165 | 1072.848 | 1220.8671 | 1389.788 | 1582.602 | 1802.7318 | 2054.0948 | 2341.1741 | 2669.1012 | 3043.7499 | 3471.8442 | 3961.0821 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 228.2389 | 261.7248 | 299.7691 | 343.0095 | 392.1742 | 448.0953 | 511.7234 | 584.1446 | 666.6005 | 760.5103 | 867.4962 | 989.4132 | 1128.3822 | 1286.8292 | 1467.5283 | 1673.6533 | 1908.8345 | 2171.1307 | 2465.4244 | 2798.6245 | 3175.1773 | 3599.701 | 4076.812 | 4610.8421 | 5205.3933 | 5862.6557 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 3840 | 22015969 | SHN | Blank | 22 | CB TR NO.1 | SUPP FOR CB FAIL | X | ABB | CUB_3166 | CUB 3166 | CUB 3000s | Electronic |  | 0 | 2190 |  | 5.5 | 0.0093284 | 0 | 0.0093284 | 51.3061 | 0 | 51.3061 | 26.4797 | 3.7323 | 0 |  | 8.1226 | 0.025228 | 0 | 0.025228 | 138.7551 | 0 | 138.7551 | 71.6132 | 10.0938 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 81.518 | 220.462 | 45.1611 | 175.3009 |  | 0.03899 |  | 5.7187 | 5.9461 | 6.1825 | 6.4283 | 6.6839 | 6.9496 | 7.226 | 7.5133 | 7.812 | 8.1226 | 8.4456 | 8.7813 | 9.1305 | 9.4935 | 9.871 | 10.2635 | 10.6715 | 11.0958 | 11.537 | 11.9957 | 12.4727 | 12.9686 | 13.4842 | 14.0204 | 14.5778 | 15.1575 | 15.7601 | 16.3867 | 17.0383 | 17.7157 |  | 0.01027 | 0.011317 | 0.012479 | 0.013771 | 0.015208 | 0.016807 | 0.018586 | 0.020566 | 0.022771 | 0.025228 | 0.027966 | 0.031018 | 0.034422 | 0.038218 | 0.042454 | 0.047182 | 0.052459 | 0.058352 | 0.064935 | 0.072288 | 0.080506 | 0.089691 | 0.099958 | 0.11144 | 0.12428 | 0.13864 | 0.15471 | 0.1727 | 0.19282 | 0.21535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7506 | 98.8938 | 109.0525 | 120.3445 | 132.9011 | 146.8695 | 162.4143 | 179.7197 | 198.992 | 220.462 | 244.3884 | 271.0606 | 300.8029 | 333.9785 | 370.9944 | 412.3066 | 458.4261 | 509.9253 | 567.4463 | 631.7085 | 703.5184 | 783.7805 | 873.5087 | 973.8403 | 1086.0505 | 1211.5697 | 1352.0025 | 1509.1486 | 1685.0272 | 1881.9038 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 56.4875 | 62.2421 | 68.6358 | 75.7428 | 83.6457 | 92.4372 | 102.2208 | 113.1125 | 125.2422 | 138.7551 | 153.8139 | 170.6009 | 189.3202 | 210.2004 | 233.4976 | 259.4988 | 288.5256 | 320.9384 | 357.1411 | 397.5866 | 442.7826 | 493.2982 | 549.7716 | 612.9186 | 683.5418 | 762.5415 | 850.9275 | 949.8326 | 1060.5276 | 1184.4384 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 42.2757 | 48.0302 | 54.424 | 61.531 | 69.4339 | 78.2253 | 88.009 | 98.9007 | 111.0304 | 124.5432 | 139.6021 | 156.3891 | 175.1084 | 195.9886 | 219.2858 | 245.287 | 274.3138 | 303.9277 | 334.5925 | 367.436 | 402.1499 | 438.1528 | 474.459 | 509.4879 | 540.7902 | 564.6555 | 575.5487 | 565.3022 | 521.9597 | 428.1185 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.2757 | 48.0302 | 54.424 | 61.531 | 69.4339 | 78.2253 | 88.009 | 98.9007 | 111.0304 | 124.5432 | 139.6021 | 156.3891 | 175.1084 | 195.9886 | 219.2858 | 245.287 | 274.3138 | 303.9277 | 334.5925 | 367.436 | 402.1499 | 438.1528 | 474.459 | 509.4879 | 540.7902 | 564.6555 | 575.5487 | 565.3022 | 521.9597 | 428.1185 |  | 29.1539 | 32.1239 | 35.4238 | 39.0918 | 43.1705 | 47.7079 | 52.7574 | 58.3787 | 64.639 | 71.6132 | 79.3852 | 88.0492 | 97.7104 | 108.487 | 120.5109 | 133.9305 | 148.9115 | 165.6401 | 184.3248 | 205.1992 | 228.5254 | 254.5971 | 283.7437 | 316.3346 | 352.7841 | 393.5568 | 439.1739 | 490.22 | 547.351 | 611.3029 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 14.4841 | 17.4541 | 20.754 | 24.422 | 28.5008 | 33.0381 | 38.0876 | 43.7089 | 49.9692 | 56.9434 | 64.7154 | 73.3794 | 83.0407 | 93.8172 | 105.8411 | 119.2607 | 134.2417 | 148.0813 | 161.0496 | 174.0771 | 186.5833 | 197.6747 | 206.0043 | 209.571 | 205.4325 | 189.2942 | 154.9213 | 93.2985 | -8.5717 | -169.3887 |  | 4.1092 | 4.5278 | 4.9929 | 5.5099 | 6.0848 | 6.7244 | 7.4361 | 8.2284 | 9.1108 | 10.0938 | 11.1893 | 12.4104 | 13.7722 | 15.2911 | 16.9859 | 18.8774 | 20.9889 | 23.3468 | 25.9804 | 28.9226 | 32.2104 | 35.8852 | 39.9934 | 44.587 | 49.7246 | 55.4714 | 61.9011 | 69.096 | 77.1486 | 86.1625 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 2.0415 | 2.4601 | 2.9253 | 3.4423 | 4.0172 | 4.6567 | 5.3684 | 6.1607 | 7.0431 | 8.0261 | 9.1216 | 10.3428 | 11.7045 | 13.2234 | 14.9182 | 16.8097 | 18.9212 | 20.8719 | 22.6998 | 24.536 | 26.2987 | 27.862 | 29.0361 | 29.5388 | 28.9555 | 26.6808 | 21.836 | 13.1503 | -1.2082 | -23.8752 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 58.8013 | 67.9445 | 78.1032 | 89.3952 | 101.9518 | 115.9202 | 131.465 | 148.7704 | 168.0427 | 189.5127 | 213.4391 | 240.1113 | 269.8536 | 303.0292 | 340.0451 | 381.3573 | 427.4768 | 472.881 | 518.3418 | 566.0491 | 615.0319 | 663.6895 | 709.4994 | 748.5977 | 775.1782 | 780.6305 | 752.3059 | 671.7511 | 512.1798 | 234.8547
| TRUE | 3841 | 22002962 | SHN | Blank | 22 | CB TR NO.1 | CB FAIL | Y | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 498.1313 | 0 | 498.1313 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 791.4596 | 45.1611 | 746.2985 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.1882 | 292.6741 | 330.7184 | 373.9588 | 423.1235 | 479.0446 | 542.6727 | 615.0939 | 697.5498 | 791.4596 | 898.4455 | 1020.3625 | 1159.3315 | 1317.7785 | 1498.4776 | 1704.6026 | 1939.7838 | 2208.1751 | 2514.5289 | 2864.2839 | 3263.6638 | 3719.792 | 4240.8213 | 4836.0847 | 5516.2655 | 6293.5949 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 163.1287 | 184.2041 | 208.1485 | 235.3633 | 266.3068 | 301.5026 | 341.549 | 387.1297 | 439.0261 | 498.1313 | 565.4664 | 642.1989 | 729.6637 | 829.3875 | 943.1165 | 1072.848 | 1220.8671 | 1389.788 | 1582.602 | 1802.7318 | 2054.0948 | 2341.1741 | 2669.1012 | 3043.7499 | 3471.8442 | 3961.0821 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 228.2389 | 261.7248 | 299.7691 | 343.0095 | 392.1742 | 448.0953 | 511.7234 | 584.1446 | 666.6005 | 760.5103 | 867.4962 | 989.4132 | 1128.3822 | 1286.8292 | 1467.5283 | 1673.6533 | 1908.8345 | 2171.1307 | 2465.4244 | 2798.6245 | 3175.1773 | 3599.701 | 4076.812 | 4610.8421 | 5205.3933 | 5862.6557 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 3842 | 22002959 | SHN | Blank | 22 | CB TR NO.1 | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 498.1313 | 0 | 498.1313 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 791.4596 | 45.1611 | 746.2985 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.1882 | 292.6741 | 330.7184 | 373.9588 | 423.1235 | 479.0446 | 542.6727 | 615.0939 | 697.5498 | 791.4596 | 898.4455 | 1020.3625 | 1159.3315 | 1317.7785 | 1498.4776 | 1704.6026 | 1939.7838 | 2208.1751 | 2514.5289 | 2864.2839 | 3263.6638 | 3719.792 | 4240.8213 | 4836.0847 | 5516.2655 | 6293.5949 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 163.1287 | 184.2041 | 208.1485 | 235.3633 | 266.3068 | 301.5026 | 341.549 | 387.1297 | 439.0261 | 498.1313 | 565.4664 | 642.1989 | 729.6637 | 829.3875 | 943.1165 | 1072.848 | 1220.8671 | 1389.788 | 1582.602 | 1802.7318 | 2054.0948 | 2341.1741 | 2669.1012 | 3043.7499 | 3471.8442 | 3961.0821 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 228.2389 | 261.7248 | 299.7691 | 343.0095 | 392.1742 | 448.0953 | 511.7234 | 584.1446 | 666.6005 | 760.5103 | 867.4962 | 989.4132 | 1128.3822 | 1286.8292 | 1467.5283 | 1673.6533 | 1908.8345 | 2171.1307 | 2465.4244 | 2798.6245 | 3175.1773 | 3599.701 | 4076.812 | 4610.8421 | 5205.3933 | 5862.6557 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 3843 | 22015968 | SHN | Blank | 22 | CB TR NO.2 | SUPP FOR CB FAIL | X | ABB | CUB_3166 | CUB 3166 | CUB 3000s | Electronic |  | 0 | 2190 |  | 5.5 | 0.0093284 | 0 | 0.0093284 | 51.3061 | 0 | 51.3061 | 26.4797 | 3.7323 | 0 |  | 8.1226 | 0.025228 | 0 | 0.025228 | 138.7551 | 0 | 138.7551 | 71.6132 | 10.0938 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 81.518 | 220.462 | 45.1611 | 175.3009 |  | 0.03899 |  | 5.7187 | 5.9461 | 6.1825 | 6.4283 | 6.6839 | 6.9496 | 7.226 | 7.5133 | 7.812 | 8.1226 | 8.4456 | 8.7813 | 9.1305 | 9.4935 | 9.871 | 10.2635 | 10.6715 | 11.0958 | 11.537 | 11.9957 | 12.4727 | 12.9686 | 13.4842 | 14.0204 | 14.5778 | 15.1575 | 15.7601 | 16.3867 | 17.0383 | 17.7157 |  | 0.01027 | 0.011317 | 0.012479 | 0.013771 | 0.015208 | 0.016807 | 0.018586 | 0.020566 | 0.022771 | 0.025228 | 0.027966 | 0.031018 | 0.034422 | 0.038218 | 0.042454 | 0.047182 | 0.052459 | 0.058352 | 0.064935 | 0.072288 | 0.080506 | 0.089691 | 0.099958 | 0.11144 | 0.12428 | 0.13864 | 0.15471 | 0.1727 | 0.19282 | 0.21535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7506 | 98.8938 | 109.0525 | 120.3445 | 132.9011 | 146.8695 | 162.4143 | 179.7197 | 198.992 | 220.462 | 244.3884 | 271.0606 | 300.8029 | 333.9785 | 370.9944 | 412.3066 | 458.4261 | 509.9253 | 567.4463 | 631.7085 | 703.5184 | 783.7805 | 873.5087 | 973.8403 | 1086.0505 | 1211.5697 | 1352.0025 | 1509.1486 | 1685.0272 | 1881.9038 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 56.4875 | 62.2421 | 68.6358 | 75.7428 | 83.6457 | 92.4372 | 102.2208 | 113.1125 | 125.2422 | 138.7551 | 153.8139 | 170.6009 | 189.3202 | 210.2004 | 233.4976 | 259.4988 | 288.5256 | 320.9384 | 357.1411 | 397.5866 | 442.7826 | 493.2982 | 549.7716 | 612.9186 | 683.5418 | 762.5415 | 850.9275 | 949.8326 | 1060.5276 | 1184.4384 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 42.2757 | 48.0302 | 54.424 | 61.531 | 69.4339 | 78.2253 | 88.009 | 98.9007 | 111.0304 | 124.5432 | 139.6021 | 156.3891 | 175.1084 | 195.9886 | 219.2858 | 245.287 | 274.3138 | 303.9277 | 334.5925 | 367.436 | 402.1499 | 438.1528 | 474.459 | 509.4879 | 540.7902 | 564.6555 | 575.5487 | 565.3022 | 521.9597 | 428.1185 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.2757 | 48.0302 | 54.424 | 61.531 | 69.4339 | 78.2253 | 88.009 | 98.9007 | 111.0304 | 124.5432 | 139.6021 | 156.3891 | 175.1084 | 195.9886 | 219.2858 | 245.287 | 274.3138 | 303.9277 | 334.5925 | 367.436 | 402.1499 | 438.1528 | 474.459 | 509.4879 | 540.7902 | 564.6555 | 575.5487 | 565.3022 | 521.9597 | 428.1185 |  | 29.1539 | 32.1239 | 35.4238 | 39.0918 | 43.1705 | 47.7079 | 52.7574 | 58.3787 | 64.639 | 71.6132 | 79.3852 | 88.0492 | 97.7104 | 108.487 | 120.5109 | 133.9305 | 148.9115 | 165.6401 | 184.3248 | 205.1992 | 228.5254 | 254.5971 | 283.7437 | 316.3346 | 352.7841 | 393.5568 | 439.1739 | 490.22 | 547.351 | 611.3029 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 14.4841 | 17.4541 | 20.754 | 24.422 | 28.5008 | 33.0381 | 38.0876 | 43.7089 | 49.9692 | 56.9434 | 64.7154 | 73.3794 | 83.0407 | 93.8172 | 105.8411 | 119.2607 | 134.2417 | 148.0813 | 161.0496 | 174.0771 | 186.5833 | 197.6747 | 206.0043 | 209.571 | 205.4325 | 189.2942 | 154.9213 | 93.2985 | -8.5717 | -169.3887 |  | 4.1092 | 4.5278 | 4.9929 | 5.5099 | 6.0848 | 6.7244 | 7.4361 | 8.2284 | 9.1108 | 10.0938 | 11.1893 | 12.4104 | 13.7722 | 15.2911 | 16.9859 | 18.8774 | 20.9889 | 23.3468 | 25.9804 | 28.9226 | 32.2104 | 35.8852 | 39.9934 | 44.587 | 49.7246 | 55.4714 | 61.9011 | 69.096 | 77.1486 | 86.1625 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 2.0415 | 2.4601 | 2.9253 | 3.4423 | 4.0172 | 4.6567 | 5.3684 | 6.1607 | 7.0431 | 8.0261 | 9.1216 | 10.3428 | 11.7045 | 13.2234 | 14.9182 | 16.8097 | 18.9212 | 20.8719 | 22.6998 | 24.536 | 26.2987 | 27.862 | 29.0361 | 29.5388 | 28.9555 | 26.6808 | 21.836 | 13.1503 | -1.2082 | -23.8752 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 58.8013 | 67.9445 | 78.1032 | 89.3952 | 101.9518 | 115.9202 | 131.465 | 148.7704 | 168.0427 | 189.5127 | 213.4391 | 240.1113 | 269.8536 | 303.0292 | 340.0451 | 381.3573 | 427.4768 | 472.881 | 518.3418 | 566.0491 | 615.0319 | 663.6895 | 709.4994 | 748.5977 | 775.1782 | 780.6305 | 752.3059 | 671.7511 | 512.1798 | 234.8547
| TRUE | 3844 | 22002963 | SHN | Blank | 22 | CB TR NO.2 | CB FAIL | Y | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 498.1313 | 0 | 498.1313 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 791.4596 | 45.1611 | 746.2985 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.1882 | 292.6741 | 330.7184 | 373.9588 | 423.1235 | 479.0446 | 542.6727 | 615.0939 | 697.5498 | 791.4596 | 898.4455 | 1020.3625 | 1159.3315 | 1317.7785 | 1498.4776 | 1704.6026 | 1939.7838 | 2208.1751 | 2514.5289 | 2864.2839 | 3263.6638 | 3719.792 | 4240.8213 | 4836.0847 | 5516.2655 | 6293.5949 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 163.1287 | 184.2041 | 208.1485 | 235.3633 | 266.3068 | 301.5026 | 341.549 | 387.1297 | 439.0261 | 498.1313 | 565.4664 | 642.1989 | 729.6637 | 829.3875 | 943.1165 | 1072.848 | 1220.8671 | 1389.788 | 1582.602 | 1802.7318 | 2054.0948 | 2341.1741 | 2669.1012 | 3043.7499 | 3471.8442 | 3961.0821 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 228.2389 | 261.7248 | 299.7691 | 343.0095 | 392.1742 | 448.0953 | 511.7234 | 584.1446 | 666.6005 | 760.5103 | 867.4962 | 989.4132 | 1128.3822 | 1286.8292 | 1467.5283 | 1673.6533 | 1908.8345 | 2171.1307 | 2465.4244 | 2798.6245 | 3175.1773 | 3599.701 | 4076.812 | 4610.8421 | 5205.3933 | 5862.6557 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 3845 | 22002960 | SHN | Blank | 22 | CB TR NO.2 | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 144.5709 | 0 | 144.5709 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 498.1313 | 0 | 498.1313 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 229.7025 | 791.4596 | 45.1611 | 746.2985 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.1882 | 292.6741 | 330.7184 | 373.9588 | 423.1235 | 479.0446 | 542.6727 | 615.0939 | 697.5498 | 791.4596 | 898.4455 | 1020.3625 | 1159.3315 | 1317.7785 | 1498.4776 | 1704.6026 | 1939.7838 | 2208.1751 | 2514.5289 | 2864.2839 | 3263.6638 | 3719.792 | 4240.8213 | 4836.0847 | 5516.2655 | 6293.5949 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 163.1287 | 184.2041 | 208.1485 | 235.3633 | 266.3068 | 301.5026 | 341.549 | 387.1297 | 439.0261 | 498.1313 | 565.4664 | 642.1989 | 729.6637 | 829.3875 | 943.1165 | 1072.848 | 1220.8671 | 1389.788 | 1582.602 | 1802.7318 | 2054.0948 | 2341.1741 | 2669.1012 | 3043.7499 | 3471.8442 | 3961.0821 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148.9169 | 169.9923 | 193.9367 | 221.1515 | 252.095 | 287.2908 | 327.3372 | 372.9179 | 424.8142 | 483.9194 | 551.2546 | 627.987 | 715.4518 | 815.1756 | 928.9046 | 1058.6362 | 1206.6553 | 1372.7774 | 1560.0533 | 1772.5812 | 2013.4621 | 2286.0287 | 2593.7886 | 2940.3192 | 3329.0926 | 3763.1962 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 228.2389 | 261.7248 | 299.7691 | 343.0095 | 392.1742 | 448.0953 | 511.7234 | 584.1446 | 666.6005 | 760.5103 | 867.4962 | 989.4132 | 1128.3822 | 1286.8292 | 1467.5283 | 1673.6533 | 1908.8345 | 2171.1307 | 2465.4244 | 2798.6245 | 3175.1773 | 3599.701 | 4076.812 | 4610.8421 | 5205.3933 | 5862.6557 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 3846 | 22002969 | SHN | Blank | 22 | ALL FEEDERS | MASTER EARTH FAULT | Blank | ASEA | GROUP_2650 | GROUP 2650 | GROUP 2000s | Electronic |  | 0.81881 | 2190 |  | 8.25 | 0.026286 | 0.02098 | 0.0053053 | 156.1101 | 5874.4876 | 6030.5977 | 193.7249 | 10.7267 | 13778.7896 |  | 15.3818 | 0.14449 | 0.11533 | 0.029162 | 858.11 | 32291.0401 | 33149.1501 | 1064.8721 | 58.9627 | 75739.618 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 28.4268 | 1.6231 | 30.0499 | 14.7027 | 2.0677 | 3.8069 |  | 20013.8389 | 110012.6028 | 50.6273 | 109961.9755 |  | 0.062297 |  | 8.7803 | 9.3447 | 9.9453 | 10.5846 | 11.265 | 11.9891 | 12.7597 | 13.5799 | 14.4528 | 15.3818 | 16.3705 | 17.4227 | 18.5426 | 19.7345 | 21.003 | 22.3531 | 23.7899 | 25.3191 | 26.9465 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.031008 | 0.036629 | 0.043324 | 0.051303 | 0.06082 | 0.072178 | 0.08574 | 0.10195 | 0.12132 | 0.14449 | 0.17221 | 0.2054 | 0.24516 | 0.29278 | 0.34986 | 0.4183 | 0.50038 | 0.59886 | 0.71704 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.02475 | 0.029236 | 0.03458 | 0.040949 | 0.048544 | 0.05761 | 0.068435 | 0.081369 | 0.096832 | 0.11533 | 0.13745 | 0.16395 | 0.19567 | 0.23369 | 0.27925 | 0.33387 | 0.39939 | 0.47799 | 0.57231 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 23609.7918 | 27889.5032 | 32986.8131 | 39062.2218 | 46308.2601 | 54955.9471 | 65282.5604 | 77620.9838 | 92370.9551 | 110012.6028 | 131122.7363 | 156394.4554 | 186660.7536 | 222922.9345 | 266384.8236 | 318493.9603 | 380991.1998 | 455970.4436 | 545950.573 | 610092.1092 | 610092.1092 | 610092.1092 | 610092.1092 | 610092.1092 | 610092.1092 | 610092.1092 | 610092.1092 | 610092.1092 | 610092.1092 | 610092.1092 |  | 36.4314 | 36.4314 | 36.4314 | 36.4314 | 36.4314 | 36.4314 | 36.4314 | 36.4314 | 36.4314 | 36.4314 | 36.4314 | 36.4314 | 36.4314 | 36.4314 | 36.4314 | 36.4314 | 36.4314 | 43.6061 | 57.8025 | 77.2898 | 104.1603 | 141.3629 | 193.0607 | 265.1402 | 365.9376 | 507.2723 | 705.9219 | 985.7273 | 1380.5961 | 1938.7941 |  | 184.1589 | 217.5411 | 257.3006 | 304.6895 | 361.2093 | 428.6622 | 509.2109 | 605.4519 | 720.5033 | 858.11 | 1022.7713 | 1219.8933 | 1455.9737 | 1738.8225 | 2077.8299 | 2484.2867 | 2971.7718 | 3556.6178 | 4258.4724 | 4758.7832 | 4758.7832 | 4758.7832 | 4758.7832 | 4758.7832 | 4758.7832 | 4758.7832 | 4758.7832 | 4758.7832 | 4758.7832 | 4758.7832 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | 169.9455 | 203.3277 | 243.0872 | 290.4761 | 346.9959 | 414.4488 | 494.9975 | 591.2385 | 706.2898 | 843.8966 | 1008.5578 | 1205.6799 | 1441.7603 | 1724.6091 | 2063.6165 | 2470.0733 | 2957.5584 | 3539.6053 | 4235.9212 | 4728.6292 | 4718.1459 | 4703.6316 | 4683.4621 | 4655.3409 | 4616.0156 | 4560.875 | 4483.3735 | 4374.2097 | 4220.1549 | 4002.3785 |  | 6929.9763 | 8186.1627 | 9682.3316 | 11465.5934 | 13592.4598 | 16130.74 | 19161.8208 | 22783.4106 | 27112.8411 | 32291.0401 | 38487.3135 | 45905.1009 | 54788.9035 | 65432.6253 | 78189.6146 | 93484.7552 | 111829.025 | 133837.0287 | 160248.1115 | 179075.0174 | 179075.0174 | 179075.0174 | 179075.0174 | 179075.0174 | 179075.0174 | 179075.0174 | 179075.0174 | 179075.0174 | 179075.0174 | 179075.0174 |  | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.6231 | 1.9427 | 2.5752 | 3.4434 | 4.6405 | 6.2979 | 8.6011 | 11.8123 | 16.303 | 22.5996 | 31.4497 | 43.9154 | 61.5073 | 86.3757 |  | 6928.3533 | 8184.5396 | 9680.7086 | 11463.9703 | 13590.8367 | 16129.1169 | 19160.1977 | 22781.7875 | 27111.218 | 32289.417 | 38485.6905 | 45903.4778 | 54787.2804 | 65431.0022 | 78187.9916 | 93483.1321 | 111827.4019 | 133835.086 | 160245.5363 | 179071.574 | 179070.3769 | 179068.7195 | 179066.4163 | 179063.205 | 179058.7144 | 179052.4177 | 179043.5677 | 179031.102 | 179013.5101 | 178988.6417 |  | 7098.2987 | 8387.8673 | 9923.7958 | 11754.4464 | 13937.8327 | 16543.5657 | 19655.1952 | 23373.026 | 27817.5078 | 33133.3136 | 39494.2483 | 47109.1577 | 56229.0407 | 67155.6113 | 80251.608 | 95953.2054 | 114784.9603 | 137374.6912 | 164481.4576 | 183800.2032 | 183788.5228 | 183772.3511 | 183749.8784 | 183718.5459 | 183674.73 | 183613.2928 | 183526.9411 | 183405.3117 | 183233.6649 | 182991.0201 |  | 228.5321 | 269.9577 | 319.2974 | 378.1046 | 448.2429 | 531.9486 | 631.9056 | 751.3359 | 894.1089 | 1064.8721 | 1269.2086 | 1513.8274 | 1806.7914 | 2157.7929 | 2578.4842 | 3082.877 | 3687.8219 | 4413.587 | 5284.5538 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 213.8294 | 255.255 | 304.5947 | 363.4019 | 433.5403 | 517.2459 | 617.2029 | 736.6332 | 879.4062 | 1050.1694 | 1254.5059 | 1499.1247 | 1792.0887 | 2143.0902 | 2563.7815 | 3068.1743 | 3673.1192 | 4395.9888 | 5261.2264 | 5874.2228 | 5863.3786 | 5848.3647 | 5827.5009 | 5798.4116 | 5757.7326 | 5700.6939 | 5620.5245 | 5507.6029 | 5348.2449 | 5122.9719 |  | 12.654 | 14.9477 | 17.6797 | 20.9359 | 24.8195 | 29.4544 | 34.989 | 41.602 | 49.5074 | 58.9627 | 70.2769 | 83.8217 | 100.0433 | 119.4785 | 142.7724 | 170.701 | 204.1972 | 244.3833 | 292.6093 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | 10.5862 | 12.88 | 15.612 | 18.8682 | 22.7518 | 27.3866 | 32.9213 | 39.5342 | 47.4397 | 56.8949 | 68.2092 | 81.7539 | 97.9755 | 117.4107 | 140.7047 | 168.6333 | 202.1295 | 241.9084 | 289.3286 | 322.6001 | 321.075 | 318.9635 | 316.0292 | 311.9382 | 306.2172 | 298.1954 | 286.9206 | 271.0396 | 248.6279 | 216.9461 |  | 16254.4705 | 19200.8939 | 22710.2037 | 26892.8985 | 31881.5285 | 37835.1419 | 44944.6342 | 53439.1834 | 63593.9945 | 75739.618 | 90273.166 | 107671.8122 | 128509.0417 | 153474.2154 | 183396.1224 | 219271.3404 | 262298.3839 | 313918.8268 | 375866.8259 | 420025.907 | 420025.907 | 420025.907 | 420025.907 | 420025.907 | 420025.907 | 420025.907 | 420025.907 | 420025.907 | 420025.907 | 420025.907 |  | 3.8069 | 3.8069 | 3.8069 | 3.8069 | 3.8069 | 3.8069 | 3.8069 | 3.8069 | 3.8069 | 3.8069 | 3.8069 | 3.8069 | 3.8069 | 3.8069 | 3.8069 | 3.8069 | 3.8069 | 4.5567 | 6.0401 | 8.0765 | 10.8844 | 14.7719 | 20.1741 | 27.7062 | 38.2391 | 53.0081 | 73.7662 | 103.0049 | 144.2672 | 202.5968 |  | 16250.6636 | 19197.087 | 22706.3968 | 26889.0915 | 31877.7215 | 37831.335 | 44940.8272 | 53435.3765 | 63590.1875 | 75735.811 | 90269.3591 | 107668.0052 | 128505.2348 | 153470.4084 | 183392.3155 | 219267.5335 | 262294.5769 | 313914.2701 | 375860.7858 | 420017.8305 | 420015.0226 | 420011.1351 | 420005.7329 | 419998.2008 | 419987.6679 | 419972.8989 | 419952.1408 | 419922.9021 | 419881.6398 | 419823.3102 |  | 23573.3779 | 27853.0893 | 32950.3992 | 39025.8079 | 46271.8462 | 54919.5332 | 65246.1466 | 77584.5699 | 92334.5413 | 109976.1889 | 131086.3225 | 156358.0415 | 186624.3397 | 222886.5206 | 266348.4097 | 318457.5464 | 380954.7859 | 455926.8585 | 545892.7983 | 610014.8566 | 609987.999 | 609950.8143 | 609899.1414 | 609827.0966 | 609726.3477 | 609585.0811 | 609386.527 | 609106.8564 | 608712.1776 | 608154.2483
| TRUE | 3847 | 22008296 | SHN | SHN011 | 22 | SHN11 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 11.6684 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 116.1374 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 4.713 |  | 89.057 | 886.3994 | 35.9712 | 850.4282 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 110.6216 | 137.896 | 172.4575 | 216.33 | 272.1126 | 343.1454 | 433.7236 | 549.3738 | 697.2109 | 886.3994 | 1128.7494 | 1439.4867 | 1838.249 | 2350.3727 | 3008.5587 | 3855.0254 | 4944.2951 | 6346.7974 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 |  | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 43.0552 | 57.0722 | 76.3133 | 102.8444 | 139.577 | 190.6216 | 261.7906 | 361.3146 | 500.8636 | 697.0037 | 973.2741 | 1363.1543 | 1914.3003 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 14.4938 | 18.0673 | 22.5956 | 28.3439 | 35.6526 | 44.9594 | 56.8271 | 71.9798 | 91.3496 | 116.1374 | 147.8904 | 188.6037 | 240.8501 | 307.9493 | 394.1858 | 505.0912 | 647.8089 | 831.5668 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 |  | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 5.6412 | 7.4777 | 9.9987 | 13.4748 | 18.2876 | 24.9755 | 34.3002 | 47.34 | 65.6239 | 91.3225 | 127.5198 | 178.6025 | 250.8145 |  | 9.7808 | 13.3543 | 17.8826 | 23.6309 | 30.9396 | 40.2464 | 52.1141 | 67.2668 | 86.6366 | 111.4244 | 143.1774 | 183.8907 | 236.1371 | 303.2363 | 389.4728 | 500.3782 | 643.0959 | 825.9257 | 851.3777 | 848.8567 | 845.3805 | 840.5678 | 833.8798 | 824.5552 | 811.5154 | 793.2315 | 767.5329 | 731.3355 | 680.2529 | 608.0409 |  | 74.6504 | 101.9248 | 136.4863 | 180.3588 | 236.1414 | 307.1743 | 397.7525 | 513.4026 | 661.2397 | 850.4282 | 1092.7782 | 1403.5156 | 1802.2778 | 2314.4015 | 2972.5875 | 3819.0543 | 4908.3239 | 6303.7421 | 6498.0003 | 6478.7592 | 6452.2282 | 6415.4955 | 6364.4509 | 6293.282 | 6193.758 | 6054.2089 | 5858.0689 | 5581.7985 | 5191.9183 | 4640.7723
| TRUE | 3848 | 22008297 | SHN | SHN012 | 22 | SHN12 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 5.8342 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 58.0687 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 2.3565 |  | 83.2228 | 828.3307 | 33.6147 | 794.716 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 103.3747 | 128.8623 | 161.1597 | 202.158 | 254.2863 | 320.6657 | 405.3101 | 513.3839 | 651.5361 | 828.3307 | 1054.8041 | 1345.1849 | 1717.8239 | 2196.398 | 2811.4658 | 3602.4799 | 4620.3906 | 5931.0139 | 6125.6449 | 6125.6449 | 6125.6449 | 6125.6449 | 6125.6449 | 6125.6449 | 6125.6449 | 6125.6449 | 6125.6449 | 6125.6449 | 6125.6449 | 6125.6449 |  | 33.6147 | 33.6147 | 33.6147 | 33.6147 | 33.6147 | 33.6147 | 33.6147 | 33.6147 | 33.6147 | 33.6147 | 33.6147 | 33.6147 | 33.6147 | 33.6147 | 33.6147 | 33.6147 | 33.6147 | 40.2346 | 53.3334 | 71.314 | 96.107 | 130.4332 | 178.1339 | 244.6405 | 337.6446 | 468.0517 | 651.3424 | 909.5142 | 1273.853 | 1788.893 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 7.2469 | 9.0337 | 11.2978 | 14.1719 | 17.8263 | 22.4797 | 28.4136 | 35.9899 | 45.6748 | 58.0687 | 73.9452 | 94.3018 | 120.4251 | 153.9747 | 197.0929 | 252.5456 | 323.9044 | 415.7834 | 429.4277 | 429.4277 | 429.4277 | 429.4277 | 429.4277 | 429.4277 | 429.4277 | 429.4277 | 429.4277 | 429.4277 | 429.4277 | 429.4277 |  | 2.3565 | 2.3565 | 2.3565 | 2.3565 | 2.3565 | 2.3565 | 2.3565 | 2.3565 | 2.3565 | 2.3565 | 2.3565 | 2.3565 | 2.3565 | 2.3565 | 2.3565 | 2.3565 | 2.3565 | 2.8206 | 3.7388 | 4.9993 | 6.7374 | 9.1438 | 12.4878 | 17.1501 | 23.67 | 32.812 | 45.6612 | 63.7599 | 89.3013 | 125.4072 |  | 4.8904 | 6.6772 | 8.9413 | 11.8154 | 15.4698 | 20.1232 | 26.0571 | 33.6334 | 43.3183 | 55.7122 | 71.5887 | 91.9453 | 118.0686 | 151.6182 | 194.7364 | 250.1891 | 321.548 | 412.9628 | 425.6888 | 424.4283 | 422.6903 | 420.2839 | 416.9399 | 412.2776 | 405.7577 | 396.6157 | 383.7664 | 365.6678 | 340.1264 | 304.0204 |  | 69.76 | 95.2477 | 127.545 | 168.5434 | 220.6716 | 287.0511 | 371.6954 | 479.7693 | 617.9214 | 794.716 | 1021.1895 | 1311.5702 | 1684.2093 | 2162.7834 | 2777.8511 | 3568.8652 | 4586.776 | 5890.7793 | 6072.3115 | 6054.3309 | 6029.5379 | 5995.2117 | 5947.511 | 5881.0044 | 5788.0003 | 5657.5932 | 5474.3024 | 5216.1307 | 4851.7918 | 4336.7518
| TRUE | 3849 | 22008298 | SHN | SHN014 | 22 | SHN14 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 11.6684 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 116.1374 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 4.713 |  | 89.057 | 886.3994 | 35.9712 | 850.4282 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 110.6216 | 137.896 | 172.4575 | 216.33 | 272.1126 | 343.1454 | 433.7236 | 549.3738 | 697.2109 | 886.3994 | 1128.7494 | 1439.4867 | 1838.249 | 2350.3727 | 3008.5587 | 3855.0254 | 4944.2951 | 6346.7974 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 | 6555.0726 |  | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 35.9712 | 43.0552 | 57.0722 | 76.3133 | 102.8444 | 139.577 | 190.6216 | 261.7906 | 361.3146 | 500.8636 | 697.0037 | 973.2741 | 1363.1543 | 1914.3003 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 14.4938 | 18.0673 | 22.5956 | 28.3439 | 35.6526 | 44.9594 | 56.8271 | 71.9798 | 91.3496 | 116.1374 | 147.8904 | 188.6037 | 240.8501 | 307.9493 | 394.1858 | 505.0912 | 647.8089 | 831.5668 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 | 858.8554 |  | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 4.713 | 5.6412 | 7.4777 | 9.9987 | 13.4748 | 18.2876 | 24.9755 | 34.3002 | 47.34 | 65.6239 | 91.3225 | 127.5198 | 178.6025 | 250.8145 |  | 9.7808 | 13.3543 | 17.8826 | 23.6309 | 30.9396 | 40.2464 | 52.1141 | 67.2668 | 86.6366 | 111.4244 | 143.1774 | 183.8907 | 236.1371 | 303.2363 | 389.4728 | 500.3782 | 643.0959 | 825.9257 | 851.3777 | 848.8567 | 845.3805 | 840.5678 | 833.8798 | 824.5552 | 811.5154 | 793.2315 | 767.5329 | 731.3355 | 680.2529 | 608.0409 |  | 74.6504 | 101.9248 | 136.4863 | 180.3588 | 236.1414 | 307.1743 | 397.7525 | 513.4026 | 661.2397 | 850.4282 | 1092.7782 | 1403.5156 | 1802.2778 | 2314.4015 | 2972.5875 | 3819.0543 | 4908.3239 | 6303.7421 | 6498.0003 | 6478.7592 | 6452.2282 | 6415.4955 | 6364.4509 | 6293.282 | 6193.758 | 6054.2089 | 5858.0689 | 5581.7985 | 5191.9183 | 4640.7723
| TRUE | 3850 | 22008299 | SHN | SHN021 | 22 | SHN21 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 2.8514 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.9682 |  | 9.4101 | 0.043865 | 3.4512e-05 | 0.043831 | 120.6389 | 2.4158 | 123.0547 | 124.7125 | 17.5508 | 50.6579 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.9682 |  | 37.2264 | 315.976 | 37.2264 | 278.7496 |  | 0.1194 |  | 3.213 | 3.6205 | 4.0796 | 4.597 | 5.1799 | 5.8369 | 6.5771 | 7.4112 | 8.351 | 9.4101 | 10.6034 | 11.9482 | 13.4634 | 15.1708 | 17.0947 | 19.2626 | 21.7055 | 24.4581 | 27.5598 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0054038 | 0.0071219 | 0.0094715 | 0.0127 | 0.017155 | 0.023326 | 0.031904 | 0.043865 | 0.060591 | 0.084037 | 0.11698 | 0.16335 | 0.22876 | 0.32115 | 0.45186 | 0.63698 | 0.8995 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.2515e-06 | 5.6032e-06 | 7.4518e-06 | 9.9919e-06 | 1.3497e-05 | 1.8352e-05 | 2.5101e-05 | 3.4512e-05 | 4.767e-05 | 6.6117e-05 | 9.2034e-05 | 0.00012852 | 0.00017998 | 0.00025267 | 0.0003555 | 0.00050116 | 0.00070769 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 37.2264 | 37.2264 | 38.9254 | 51.3011 | 68.2265 | 91.4827 | 123.5735 | 168.026 | 229.8163 | 315.976 | 436.4539 | 605.344 | 842.6336 | 1176.6955 | 1647.8399 | 2313.3821 | 3254.8714 | 4588.4095 | 6479.3802 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 |  | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 44.5576 | 59.0638 | 78.9763 | 106.4331 | 144.4475 | 197.2734 | 270.9257 | 373.9226 | 518.3412 | 721.3255 | 1007.2364 | 1410.7214 | 1981.0996 |  | 14.2129 | 14.2129 | 14.8616 | 19.5866 | 26.0487 | 34.9279 | 47.1801 | 64.152 | 87.7434 | 120.6389 | 166.6371 | 231.119 | 321.7156 | 449.2597 | 629.1416 | 883.2441 | 1242.7026 | 1751.8445 | 2473.8129 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0.64867 | 5.3737 | 11.8358 | 20.7149 | 32.9672 | 49.939 | 73.5304 | 106.426 | 152.4242 | 216.906 | 307.5027 | 435.0468 | 614.9286 | 869.0312 | 1228.4897 | 1734.8325 | 2451.2625 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.29761 | 0.39222 | 0.52163 | 0.69943 | 0.94479 | 1.2846 | 1.7571 | 2.4158 | 3.3369 | 4.6282 | 6.4424 | 8.9965 | 12.5986 | 17.6871 | 24.8853 | 35.0809 | 49.5384 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0.01299 | 0.10761 | 0.23701 | 0.41482 | 0.66017 | 1 | 1.4725 | 2.1312 | 3.0523 | 4.3436 | 6.1578 | 8.7119 | 12.314 | 17.4024 | 24.6006 | 34.7402 | 49.0868 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0.66166 | 5.4813 | 12.0728 | 21.1298 | 33.6273 | 50.939 | 75.0029 | 108.5572 | 155.4765 | 221.2496 | 313.6605 | 443.7586 | 627.2427 | 886.4336 | 1253.0903 | 1769.5727 | 2500.3493 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 15.3634 | 20.248 | 26.9283 | 36.1073 | 48.7732 | 66.3182 | 90.7062 | 124.7125 | 172.2639 | 238.9231 | 332.579 | 464.4298 | 650.3857 | 913.0685 | 1284.6648 | 1810.9989 | 2557.3459 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0.67057 | 5.5552 | 12.2355 | 21.4144 | 34.0804 | 51.6253 | 76.0133 | 110.0197 | 157.5711 | 224.2303 | 317.8861 | 449.7369 | 635.6929 | 898.3757 | 1269.972 | 1793.4124 | 2534.034 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.1621 | 2.8495 | 3.7896 | 5.0814 | 6.8639 | 9.333 | 12.7651 | 17.5508 | 24.2428 | 33.6237 | 46.8039 | 65.3593 | 91.529 | 128.4964 | 180.7913 | 254.8624 | 359.896 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0.09437 | 0.78178 | 1.7219 | 3.0137 | 4.7961 | 7.2652 | 10.6974 | 15.4831 | 22.175 | 31.556 | 44.7362 | 63.2916 | 89.4612 | 126.4287 | 178.7235 | 252.3875 | 356.6154 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 5.9682 | 5.9682 | 6.2406 | 8.2247 | 10.9382 | 14.6667 | 19.8116 | 26.9383 | 36.8446 | 50.6579 | 69.9731 | 97.0499 | 135.0927 | 188.6501 | 264.1849 | 370.886 | 521.8274 | 735.6229 | 1038.787 | 1087.594 | 1087.594 | 1087.594 | 1087.594 | 1087.594 | 1087.594 | 1087.594 | 1087.594 | 1087.594 | 1087.594 | 1087.594 |  | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 7.1436 | 9.4692 | 12.6616 | 17.0636 | 23.1581 | 31.6273 | 43.4354 | 59.948 | 83.1015 | 115.6443 | 161.4821 | 226.1697 | 317.6138 |  | 0 | 0 | 0.27239 | 2.2565 | 4.97 | 8.6985 | 13.8433 | 20.9701 | 30.8764 | 44.6897 | 64.0049 | 91.0817 | 129.1245 | 182.6819 | 258.2167 | 364.9178 | 515.8592 | 728.4793 | 1029.3178 | 1074.9324 | 1070.5305 | 1064.4359 | 1055.9668 | 1044.1587 | 1027.646 | 1004.4925 | 971.9497 | 926.1119 | 861.4244 | 769.9802 |  | 0 | 0 | 1.699 | 14.0747 | 31.0002 | 54.2563 | 86.3472 | 130.7996 | 192.59 | 278.7496 | 399.2275 | 568.1176 | 805.4073 | 1139.4691 | 1610.6135 | 2276.1557 | 3217.6451 | 4543.8519 | 6420.3165 | 6704.835 | 6677.3781 | 6639.3637 | 6586.5379 | 6512.8855 | 6409.8886 | 6265.47 | 6062.4857 | 5776.5749 | 5373.0898 | 4802.7116
| TRUE | 3851 | 22008300 | SHN | SHN022 | 22 | SHN22 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 14.776 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 147.0682 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 5.9682 |  | 92.1646 | 917.3302 | 37.2264 | 880.1038 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 114.4817 | 142.7079 | 178.4754 | 223.8788 | 281.6079 | 355.1194 | 448.8584 | 568.5441 | 721.54 | 917.3302 | 1168.137 | 1489.7175 | 1902.3945 | 2432.3887 | 3113.5421 | 3989.5462 | 5116.8258 | 6568.2683 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 | 6783.8112 |  | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 37.2264 | 44.5576 | 59.0638 | 78.9763 | 106.4331 | 144.4475 | 197.2734 | 270.9257 | 373.9226 | 518.3412 | 721.3255 | 1007.2364 | 1410.7214 | 1981.0996 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 18.3539 | 22.8792 | 28.6135 | 35.8927 | 45.1479 | 56.9335 | 71.9619 | 91.1501 | 115.6787 | 147.0682 | 187.278 | 238.8345 | 304.9957 | 389.9654 | 499.1692 | 639.6119 | 820.3396 | 1053.0378 | 1087.594 | 1087.594 | 1087.594 | 1087.594 | 1087.594 | 1087.594 | 1087.594 | 1087.594 | 1087.594 | 1087.594 | 1087.594 | 1087.594 |  | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 5.9682 | 7.1436 | 9.4692 | 12.6616 | 17.0636 | 23.1581 | 31.6273 | 43.4354 | 59.948 | 83.1015 | 115.6443 | 161.4821 | 226.1697 | 317.6138 |  | 12.3857 | 16.911 | 22.6453 | 29.9245 | 39.1797 | 50.9652 | 65.9937 | 85.1819 | 109.7105 | 141.1 | 181.3098 | 232.8663 | 299.0274 | 383.9972 | 493.201 | 633.6437 | 814.3714 | 1045.8942 | 1078.1248 | 1074.9324 | 1070.5305 | 1064.4359 | 1055.9668 | 1044.1587 | 1027.646 | 1004.4925 | 971.9497 | 926.1119 | 861.4244 | 769.9802 |  | 77.2553 | 105.4815 | 141.249 | 186.6524 | 244.3816 | 317.8931 | 411.632 | 531.3178 | 684.3136 | 880.1038 | 1130.9106 | 1452.4911 | 1865.1682 | 2395.1624 | 3076.3157 | 3952.3199 | 5079.5995 | 6523.7107 | 6724.7475 | 6704.835 | 6677.3781 | 6639.3637 | 6586.5379 | 6512.8855 | 6409.8886 | 6265.47 | 6062.4857 | 5776.5749 | 5373.0898 | 4802.7116
| TRUE | 3852 | 22008301 | SHN | SHN023 | 22 | SHN23 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 5.8543 | 0.012795 | 1.0066e-05 | 0.012785 | 35.1883 | 0.70465 | 35.8929 | 36.3765 | 5.1193 | 7.388 |  | 13.88 | 0.12735 | 0.00010019 | 0.12725 | 350.2346 | 7.0135 | 357.2481 | 362.061 | 50.9529 | 73.5341 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 2.9841 |  | 84.7766 | 843.7961 | 34.2423 | 809.5538 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.2504e-05 | 1.5587e-05 | 1.9493e-05 | 2.4452e-05 | 3.0758e-05 | 3.8787e-05 | 4.9025e-05 | 6.2098e-05 | 7.8808e-05 | 0.00010019 | 0.00012759 | 0.00016271 | 0.00020778 | 0.00026567 | 0.00034007 | 0.00043575 | 0.00055887 | 0.0007174 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 105.3047 | 131.2683 | 164.1686 | 205.9324 | 259.034 | 326.6527 | 412.8775 | 522.9691 | 663.7006 | 843.7961 | 1074.498 | 1370.3003 | 1749.8967 | 2237.4061 | 2863.9575 | 3669.7402 | 4706.656 | 6041.7494 | 6240.0142 | 6240.0142 | 6240.0142 | 6240.0142 | 6240.0142 | 6240.0142 | 6240.0142 | 6240.0142 | 6240.0142 | 6240.0142 | 6240.0142 | 6240.0142 |  | 34.2423 | 34.2423 | 34.2423 | 34.2423 | 34.2423 | 34.2423 | 34.2423 | 34.2423 | 34.2423 | 34.2423 | 34.2423 | 34.2423 | 34.2423 | 34.2423 | 34.2423 | 34.2423 | 34.2423 | 40.9858 | 54.3292 | 72.6454 | 97.9014 | 132.8685 | 181.4597 | 249.2081 | 343.9486 | 476.7905 | 663.5034 | 926.4953 | 1297.6366 | 1822.2927 |  | 43.7089 | 54.4855 | 68.1415 | 85.4764 | 107.5173 | 135.5838 | 171.3731 | 217.0689 | 275.4823 | 350.2346 | 445.9921 | 568.7708 | 726.33 | 928.6806 | 1188.7434 | 1523.1998 | 1953.5927 | 2507.7501 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 29.4959 | 40.2726 | 53.9286 | 71.2635 | 93.3043 | 121.3709 | 157.1602 | 202.8559 | 261.2694 | 336.0217 | 431.7791 | 554.5579 | 712.117 | 914.4676 | 1174.5305 | 1508.9869 | 1939.3797 | 2490.7381 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.87527 | 1.0911 | 1.3645 | 1.7117 | 2.153 | 2.7151 | 3.4318 | 4.3468 | 5.5166 | 7.0135 | 8.931 | 11.3897 | 14.5448 | 18.5969 | 23.8047 | 30.5022 | 39.1209 | 50.218 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.59066 | 0.80646 | 1.0799 | 1.4271 | 1.8684 | 2.4305 | 3.1472 | 4.0622 | 5.2319 | 6.7289 | 8.6464 | 11.1051 | 14.2602 | 18.3123 | 23.5201 | 30.2176 | 38.8363 | 49.8773 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 30.0866 | 41.0791 | 55.0085 | 72.6905 | 95.1728 | 123.8013 | 160.3073 | 206.9182 | 266.5014 | 342.7505 | 440.4256 | 565.6629 | 726.3773 | 932.78 | 1198.0506 | 1539.2045 | 1978.216 | 2540.6154 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 45.1848 | 56.3253 | 70.4424 | 88.3627 | 111.1478 | 140.1621 | 177.1599 | 224.3986 | 284.7845 | 362.061 | 461.0519 | 587.9764 | 750.8559 | 960.0393 | 1228.8836 | 1574.6336 | 2019.5594 | 2592.4291 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 30.4919 | 41.6325 | 55.7496 | 73.6698 | 96.4549 | 125.4692 | 162.467 | 209.7058 | 270.0917 | 347.3681 | 446.359 | 573.2836 | 736.163 | 945.3464 | 1214.1907 | 1559.9407 | 2004.8666 | 2574.8427 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 6.3589 | 7.9267 | 9.9134 | 12.4353 | 15.6419 | 19.725 | 24.9318 | 31.5797 | 40.0778 | 50.9529 | 64.884 | 82.7461 | 105.6682 | 135.1066 | 172.9412 | 221.5986 | 284.2132 | 364.8333 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 4.2911 | 5.859 | 7.8457 | 10.3676 | 13.5741 | 17.6573 | 22.864 | 29.512 | 38.0101 | 48.8852 | 62.8162 | 80.6784 | 103.6004 | 133.0389 | 170.8734 | 219.5309 | 282.1455 | 362.3584 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 9.177 | 11.4396 | 14.3068 | 17.9463 | 22.574 | 28.4667 | 35.9809 | 45.5751 | 57.8394 | 73.5341 | 93.639 | 119.4172 | 152.4978 | 194.9827 | 249.5846 | 319.806 | 410.1698 | 526.5189 | 543.797 | 543.797 | 543.797 | 543.797 | 543.797 | 543.797 | 543.797 | 543.797 | 543.797 | 543.797 | 543.797 | 543.797 |  | 2.9841 | 2.9841 | 2.9841 | 2.9841 | 2.9841 | 2.9841 | 2.9841 | 2.9841 | 2.9841 | 2.9841 | 2.9841 | 2.9841 | 2.9841 | 2.9841 | 2.9841 | 2.9841 | 2.9841 | 3.5718 | 4.7346 | 6.3308 | 8.5318 | 11.5791 | 15.8136 | 21.7177 | 29.974 | 41.5507 | 57.8222 | 80.7411 | 113.0848 | 158.8069 |  | 6.1929 | 8.4555 | 11.3227 | 14.9622 | 19.5899 | 25.4826 | 32.9968 | 42.591 | 54.8553 | 70.55 | 90.6549 | 116.4331 | 149.5137 | 191.9986 | 246.6005 | 316.8219 | 407.1857 | 522.9471 | 539.0624 | 537.4662 | 535.2652 | 532.218 | 527.9834 | 522.0793 | 513.823 | 502.2463 | 485.9748 | 463.056 | 430.7122 | 384.9901 |  | 71.0625 | 97.026 | 129.9263 | 171.6902 | 224.7917 | 292.4105 | 378.6352 | 488.7268 | 629.4584 | 809.5538 | 1040.2557 | 1336.058 | 1715.6544 | 2203.1638 | 2829.7152 | 3635.498 | 4672.4138 | 6000.7636 | 6185.6851 | 6167.3688 | 6142.1129 | 6107.1457 | 6058.5545 | 5990.8062 | 5896.0656 | 5763.2237 | 5576.5108 | 5313.5189 | 4942.3776 | 4417.7215
| TRUE | 3853 | 22008302 | SHN | SHN024 | 22 | SHN24 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.99892 | 1 |  | 5.8543 | 0.012795 | 1.7508e-05 | 0.012777 | 35.1903 | 1.2256 | 36.4159 | 36.4187 | 5.1193 | 12.8497 |  | 13.88 | 0.12735 | 0.00017426 | 0.12717 | 350.255 | 12.1983 | 362.4533 | 362.4815 | 50.9537 | 127.8951 |  | 0.0051679 | 7.0717e-06 | 0.0051609 | 14.2138 | 0.49502 | 14.7088 | 14.7099 | 2.0678 | 5.1901 |  | 90.8036 | 903.7835 | 36.6766 | 867.1069 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.1748e-05 | 2.711e-05 | 3.3904e-05 | 4.2529e-05 | 5.3496e-05 | 6.7461e-05 | 8.5268e-05 | 0.000108 | 0.00013707 | 0.00017426 | 0.00022191 | 0.000283 | 0.00036139 | 0.00046207 | 0.00059147 | 0.00075788 | 0.00097202 | 0.0012477 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 0.0012887 | 112.7911 | 140.6004 | 175.8397 | 220.5727 | 277.4493 | 349.8752 | 442.2299 | 560.1482 | 710.8846 | 903.7835 | 1150.8865 | 1467.7181 | 1874.3009 | 2396.4684 | 3067.5628 | 3930.6305 | 5041.263 | 6471.2712 | 6683.6312 | 6683.6312 | 6683.6312 | 6683.6312 | 6683.6312 | 6683.6312 | 6683.6312 | 6683.6312 | 6683.6312 | 6683.6312 | 6683.6312 | 6683.6312 |  | 36.6766 | 36.6766 | 36.6766 | 36.6766 | 36.6766 | 36.6766 | 36.6766 | 36.6766 | 36.6766 | 36.6766 | 36.6766 | 36.6766 | 36.6766 | 36.6766 | 36.6766 | 36.6766 | 36.6766 | 43.8996 | 58.1915 | 77.81 | 104.8614 | 142.3144 | 194.3601 | 266.9248 | 368.4007 | 510.6866 | 710.6734 | 992.362 | 1389.8886 | 1951.8437 |  | 43.7114 | 54.4887 | 68.1455 | 85.4814 | 107.5235 | 135.5917 | 171.3831 | 217.0815 | 275.4984 | 350.255 | 446.018 | 568.8039 | 726.3722 | 928.7346 | 1188.8125 | 1523.2884 | 1953.7063 | 2507.896 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 | 2590.1946 |  | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 14.2138 | 17.013 | 22.5517 | 30.1547 | 40.6383 | 55.153 | 75.3229 | 103.4449 | 142.7711 | 197.913 | 275.4165 | 384.583 | 538.6416 | 756.4234 |  | 29.4976 | 40.2749 | 53.9317 | 71.2676 | 93.3098 | 121.3779 | 157.1693 | 202.8677 | 261.2846 | 336.0412 | 431.8042 | 554.5901 | 712.1584 | 914.5208 | 1174.5988 | 1509.0746 | 1939.4925 | 2490.883 | 2567.6429 | 2560.0399 | 2549.5563 | 2535.0416 | 2514.8717 | 2486.7497 | 2447.4235 | 2392.2815 | 2314.7781 | 2205.6116 | 2051.553 | 1833.7712 |  | 1.5223 | 1.8977 | 2.3733 | 2.9771 | 3.7447 | 4.7222 | 5.9687 | 7.5603 | 9.5948 | 12.1983 | 15.5334 | 19.8097 | 25.2973 | 32.3449 | 41.4026 | 53.0514 | 68.0415 | 87.3422 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 | 90.2084 |  | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.49502 | 0.59251 | 0.78541 | 1.0502 | 1.4153 | 1.9208 | 2.6233 | 3.6027 | 4.9723 | 6.8927 | 9.5919 | 13.3938 | 18.7592 | 26.3439 |  | 1.0273 | 1.4027 | 1.8783 | 2.482 | 3.2497 | 4.2272 | 5.4737 | 7.0653 | 9.0997 | 11.7033 | 15.0384 | 19.3147 | 24.8023 | 31.8499 | 40.9076 | 52.5564 | 67.5465 | 86.7497 | 89.423 | 89.1582 | 88.7931 | 88.2876 | 87.5852 | 86.6058 | 85.2362 | 83.3157 | 80.6165 | 76.8146 | 71.4492 | 63.8646 |  | 30.5249 | 41.6776 | 55.81 | 73.7497 | 96.5595 | 125.6051 | 162.643 | 209.933 | 270.3843 | 347.7445 | 446.8427 | 573.9048 | 736.9607 | 946.3707 | 1215.5064 | 1561.631 | 2007.039 | 2577.6327 | 2657.0659 | 2649.1981 | 2638.3494 | 2623.3293 | 2602.4568 | 2573.3555 | 2532.6596 | 2475.5973 | 2395.3946 | 2282.4262 | 2123.0022 | 1897.6358 |  | 45.2372 | 56.3908 | 70.5242 | 88.4653 | 111.2769 | 140.3248 | 177.3656 | 224.6592 | 285.1153 | 362.4815 | 461.5873 | 588.6593 | 751.7279 | 961.1543 | 1230.3108 | 1576.4624 | 2021.905 | 2595.44 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 | 2680.6114 |  | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 14.7099 | 17.6069 | 23.3389 | 31.2073 | 42.0569 | 57.0782 | 77.9522 | 107.0558 | 147.7549 | 204.8217 | 285.0306 | 398.0077 | 557.4442 | 782.8281 |  | 30.5273 | 41.6808 | 55.8143 | 73.7554 | 96.567 | 125.6149 | 162.6557 | 209.9493 | 270.4054 | 347.7715 | 446.8774 | 573.9494 | 737.018 | 946.4443 | 1215.6009 | 1561.7524 | 2007.1951 | 2577.8331 | 2657.2725 | 2649.4041 | 2638.5545 | 2623.5332 | 2602.6592 | 2573.5556 | 2532.8566 | 2475.7898 | 2395.5809 | 2282.6037 | 2123.1673 | 1897.7833 |  | 6.359 | 7.9268 | 9.9135 | 12.4355 | 15.6421 | 19.7253 | 24.9321 | 31.5801 | 40.0784 | 50.9537 | 64.8849 | 82.7473 | 105.6697 | 135.1086 | 172.9437 | 221.6019 | 284.2173 | 364.8386 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 | 376.8111 |  | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.0678 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9577 | 15.0487 | 20.7698 | 28.7916 | 40.0665 | 55.9476 | 78.3594 | 110.0414 |  | 4.2912 | 5.859 | 7.8458 | 10.3677 | 13.5743 | 17.6576 | 22.8644 | 29.5124 | 38.0106 | 48.8859 | 62.8171 | 80.6795 | 103.6019 | 133.0408 | 170.8759 | 219.5341 | 282.1496 | 362.3636 | 373.5304 | 372.4243 | 370.8992 | 368.7877 | 365.8534 | 361.7623 | 356.0413 | 348.0195 | 336.7446 | 320.8635 | 298.4517 | 266.7697 |  | 15.9612 | 19.8965 | 24.8832 | 31.2134 | 39.2621 | 49.5111 | 62.5803 | 79.267 | 100.5978 | 127.8951 | 162.8628 | 207.6979 | 265.2337 | 339.126 | 434.0931 | 556.2264 | 713.3929 | 915.7544 | 945.8056 | 945.8056 | 945.8056 | 945.8056 | 945.8056 | 945.8056 | 945.8056 | 945.8056 | 945.8056 | 945.8056 | 945.8056 | 945.8056 |  | 5.1901 | 5.1901 | 5.1901 | 5.1901 | 5.1901 | 5.1901 | 5.1901 | 5.1901 | 5.1901 | 5.1901 | 5.1901 | 5.1901 | 5.1901 | 5.1901 | 5.1901 | 5.1901 | 5.1901 | 6.2123 | 8.2347 | 11.0109 | 14.839 | 20.139 | 27.504 | 37.7727 | 52.1327 | 72.2676 | 100.5679 | 140.4299 | 196.6842 | 276.2069 |  | 10.771 | 14.7063 | 19.6931 | 26.0233 | 34.0719 | 44.321 | 57.3901 | 74.0768 | 95.4077 | 122.7049 | 157.6727 | 202.5077 | 260.0436 | 333.9359 | 428.903 | 551.0363 | 708.2027 | 909.5421 | 937.5709 | 934.7947 | 930.9666 | 925.6666 | 918.3016 | 908.0329 | 893.673 | 873.538 | 845.2377 | 805.3757 | 749.1215 | 669.5988 |  | 76.1145 | 103.9238 | 139.1631 | 183.896 | 240.7727 | 313.1986 | 405.5532 | 523.4715 | 674.208 | 867.1069 | 1114.2099 | 1431.0414 | 1837.6242 | 2359.7918 | 3030.8861 | 3893.9539 | 5004.5864 | 6427.3716 | 6625.4396 | 6605.8212 | 6578.7698 | 6541.3167 | 6489.271 | 6416.7063 | 6315.2305 | 6172.9445 | 5972.9578 | 5691.2692 | 5293.7426 | 4731.7875
| TRUE | 3854 | 22002950 | SHN | Blank | 22 | TRANS NO.1 | DIFFERENTIAL | X | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.066046 | 2190 |  | 8.25 | 0.026286 | 0.0045837 | 0.021702 | 280.8119 | 2016.8282 | 2297.64 | 100.6375 | 10.5627 | 486.0379 |  | 13.0142 | 0.090569 | 0.015794 | 0.074776 | 967.5611 | 6949.1524 | 7916.7135 | 346.7551 | 36.3947 | 1674.6846 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.049579 |  | 2894.8781 | 9974.5479 | 71.2593 | 9903.2886 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0051721 | 0.0058403 | 0.0065995 | 0.0074623 | 0.0084434 | 0.0095593 | 0.010829 | 0.012274 | 0.01392 | 0.015794 | 0.017928 | 0.020361 | 0.023134 | 0.026296 | 0.029902 | 0.034015 | 0.038708 | 0.044064 | 0.050177 | 0.057157 | 0.065126 | 0.074228 | 0.084625 | 0.096504 | 0.11008 | 0.12559 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 3266.4781 | 3688.4908 | 4167.9528 | 4712.8997 | 5332.5097 | 6037.268 | 6839.1546 | 7751.8595 | 8791.0291 | 9974.5479 | 11322.8619 | 12859.3479 | 14610.7372 | 16607.6003 | 18884.9021 | 21482.6382 | 24446.563 | 27829.024 | 31689.9175 | 36097.7836 | 41131.0595 | 46879.5168 | 53445.9071 | 60947.8473 | 69519.9799 | 79316.4486 | 88246.053 | 88246.053 | 88246.053 | 88246.053 |  | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 52.8209 | 70.0172 | 93.6225 | 126.1714 | 171.2356 | 233.858 | 321.1694 | 443.2672 | 614.4685 | 855.0966 | 1194.03 | 1672.3421 | 2348.4978 |  | 316.8582 | 357.7947 | 404.3039 | 457.1654 | 517.2694 | 585.6331 | 663.4185 | 751.9536 | 852.7562 | 967.5611 | 1098.3516 | 1247.3954 | 1417.2854 | 1610.9871 | 1831.8922 | 2083.8804 | 2371.39 | 2699.4989 | 3074.0171 | 3501.5934 | 3989.8362 | 4547.4539 | 5184.4134 | 5912.1241 | 6743.6467 | 7693.9336 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 289.7263 | 330.6628 | 377.172 | 430.0335 | 490.1375 | 558.5012 | 636.2866 | 724.8217 | 825.6243 | 940.4292 | 1071.2197 | 1220.2634 | 1390.1535 | 1583.8552 | 1804.7603 | 2056.7485 | 2344.2581 | 2667.0237 | 3030.9693 | 3444.0326 | 3912.2639 | 4442.1753 | 5040.6335 | 5714.6637 | 6471.1185 | 7316.1479 | 8034.4041 | 7826.022 | 7531.9476 | 7116.2356 |  | 2275.7176 | 2569.729 | 2903.7646 | 3283.4228 | 3715.0979 | 4206.0949 | 4764.7601 | 5400.6311 | 6124.6085 | 6949.1524 | 7888.5072 | 8958.9593 | 10179.132 | 11570.3234 | 13156.8933 | 14966.7061 | 17031.6383 | 19388.1598 | 22077.9998 | 25148.9092 | 28655.5344 | 32660.4183 | 37235.1466 | 42461.6617 | 48433.7676 | 55258.8543 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 2275.5118 | 2569.5233 | 2903.5589 | 3283.2171 | 3714.8922 | 4205.8892 | 4764.5543 | 5400.4253 | 6124.4028 | 6948.9467 | 7888.3015 | 8958.7535 | 10178.9262 | 11570.1177 | 13156.6876 | 14966.5004 | 17031.4326 | 19387.9136 | 22077.6734 | 25148.4727 | 28654.9462 | 32659.62 | 37234.0564 | 42460.1645 | 48431.7012 | 55255.9897 | 61476.0203 | 61474.4402 | 61472.2104 | 61469.0582 |  | 2565.2381 | 2900.186 | 3280.7309 | 3713.2506 | 4205.0297 | 4764.3904 | 5400.8409 | 6125.2471 | 6950.0271 | 7889.3759 | 8959.5212 | 10179.017 | 11569.0797 | 13153.9729 | 14961.4479 | 17023.2489 | 19375.6907 | 22054.9372 | 25108.6427 | 28592.5053 | 32567.2101 | 37101.7953 | 42274.6899 | 48174.8282 | 54902.8197 | 62572.1376 | 69510.4244 | 69300.4622 | 69004.158 | 68585.2938 |  | 113.5558 | 128.2266 | 144.8947 | 163.8392 | 185.3793 | 209.8795 | 237.7563 | 269.4855 | 305.6112 | 346.7551 | 393.6278 | 447.0422 | 507.9275 | 577.3464 | 656.5145 | 746.8222 | 849.86 | 967.4478 | 1101.6679 | 1254.9029 | 1429.8796 | 1629.7189 | 1857.9928 | 2118.7902 | 2416.7917 | 2757.356 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 98.8834 | 113.5542 | 130.2222 | 149.1667 | 170.7069 | 195.2071 | 223.0838 | 254.8131 | 290.9388 | 332.0826 | 378.9554 | 432.3698 | 493.255 | 562.674 | 641.8421 | 732.1497 | 835.1876 | 949.8858 | 1078.3884 | 1223.7751 | 1387.9299 | 1572.7862 | 1780.2393 | 2012.0072 | 2269.4134 | 2553.0564 | 2783.4806 | 2670.7914 | 2511.7613 | 2286.9518 |  | 11.9186 | 13.4584 | 15.2079 | 17.1962 | 19.457 | 22.0285 | 24.9544 | 28.2847 | 32.0763 | 36.3947 | 41.3144 | 46.9207 | 53.3111 | 60.5971 | 68.9065 | 78.385 | 89.1996 | 101.5414 | 115.6289 | 131.7121 | 150.0773 | 171.0521 | 195.0112 | 222.384 | 253.6617 | 289.4066 | 321.9886 | 321.9886 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 9.8509 | 11.3907 | 13.1402 | 15.1285 | 17.3893 | 19.9608 | 22.8867 | 26.217 | 30.0087 | 34.327 | 39.2467 | 44.853 | 51.2434 | 58.5294 | 66.8388 | 76.3173 | 87.1319 | 99.0665 | 112.3482 | 127.3255 | 144.1656 | 163.0289 | 184.0539 | 207.3357 | 232.8925 | 260.6159 | 281.9234 | 266.0428 | 243.6317 | 211.9507 |  | 548.4279 | 619.2821 | 699.7817 | 791.276 | 895.3059 | 1013.6319 | 1148.2653 | 1301.5046 | 1475.9768 | 1674.6846 | 1901.0609 | 2159.0304 | 2453.0813 | 2788.3462 | 3170.6956 | 3606.8446 | 4104.4751 | 4672.3761 | 5320.6039 | 6060.666 | 6905.7319 | 7870.8737 | 8973.343 | 10232.8872 | 11672.1122 | 13316.8981 | 14816.1411 | 14816.1411 | 14816.1411 | 14816.1411 |  | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.059343 | 0.078663 | 0.10518 | 0.14175 | 0.19238 | 0.26273 | 0.36083 | 0.498 | 0.69034 | 0.96068 | 1.3415 | 1.8788 | 2.6385 |  | 548.3783 | 619.2325 | 699.7322 | 791.2265 | 895.2564 | 1013.5823 | 1148.2157 | 1301.455 | 1475.9272 | 1674.6351 | 1901.0113 | 2158.9808 | 2453.0317 | 2788.2967 | 3170.6461 | 3606.795 | 4104.4255 | 4672.3167 | 5320.5252 | 6060.5608 | 6905.5901 | 7870.6813 | 8973.0803 | 10232.5264 | 11671.6142 | 13316.2078 | 14815.1805 | 14814.7997 | 14814.2623 | 14813.5027 |  | 3222.3507 | 3644.3635 | 4123.8255 | 4668.7723 | 5288.3823 | 5993.1406 | 6795.0272 | 7707.7322 | 8746.9017 | 9930.4206 | 11278.7345 | 12815.2206 | 14566.6099 | 16563.4729 | 18840.7748 | 21438.5109 | 24402.4357 | 27776.2063 | 31619.9046 | 36004.1667 | 41004.8958 | 46708.2917 | 53212.0634 | 60626.6975 | 69076.7399 | 78702.0177 | 87391.0088 | 87052.0961 | 86573.8133 | 85897.6989
| TRUE | 3855 | 22002951 | SHN | Blank | 22 | TRANS NO.1 | DIFFERENTIAL | Y | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.0068096 | 2190 |  | 8.25 | 0.026286 | 0.00052975 | 0.025756 | 276.5552 | 233.0884 | 509.6437 | 77.6223 | 10.5222 | 56.1723 |  | 13.0142 | 0.090569 | 0.0018253 | 0.088744 | 952.8944 | 803.126 | 1756.0204 | 267.4541 | 36.255 | 193.5463 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.0051117 |  | 653.9604 | 2253.2759 | 71.0275 | 2182.2484 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00059775 | 0.00067497 | 0.00076271 | 0.00086243 | 0.00097582 | 0.0011048 | 0.0012515 | 0.0014185 | 0.0016087 | 0.0018253 | 0.002072 | 0.0023532 | 0.0026737 | 0.0030391 | 0.0034558 | 0.0039312 | 0.0044736 | 0.0050926 | 0.0057991 | 0.0066057 | 0.0075268 | 0.0085787 | 0.0097803 | 0.011153 | 0.012722 | 0.014514 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 737.9057 | 833.2395 | 941.5512 | 1064.6561 | 1204.6276 | 1363.8343 | 1544.9825 | 1751.1649 | 1985.9159 | 2253.2759 | 2557.8634 | 2904.9595 | 3300.6029 | 3751.6993 | 4266.1476 | 4852.9829 | 5522.541 | 6286.6476 | 7158.8333 | 8154.5815 | 9291.6114 | 10590.2026 | 12073.5669 | 13768.2744 | 15704.741 | 17917.7883 | 19935.0088 | 19935.0088 | 19935.0088 | 19935.0088 |  | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 52.5408 | 69.646 | 93.1261 | 125.5023 | 170.3276 | 232.6179 | 319.4663 | 440.9166 | 611.2101 | 850.5622 | 1187.6983 | 1663.474 | 2336.0443 |  | 312.0551 | 352.3711 | 398.1753 | 450.2355 | 509.4285 | 576.7559 | 653.3622 | 740.5552 | 839.8298 | 952.8944 | 1081.7024 | 1228.4869 | 1395.8016 | 1586.5671 | 1804.1237 | 2052.2922 | 2335.4436 | 2658.5789 | 3027.42 | 3448.5149 | 3929.3568 | 4478.5218 | 5105.8261 | 5822.5059 | 6641.424 | 7577.3061 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 284.9234 | 325.2394 | 371.0437 | 423.1038 | 482.2968 | 549.6242 | 626.2305 | 713.4236 | 812.6981 | 925.7627 | 1054.5707 | 1201.3552 | 1368.6699 | 1559.4354 | 1776.992 | 2025.1605 | 2308.3119 | 2626.1039 | 2984.3726 | 3390.9546 | 3851.7851 | 4373.2441 | 4962.0474 | 5625.0471 | 6368.898 | 7199.5234 | 7904.6507 | 7696.2703 | 7402.1983 | 6986.4896 |  | 263.0087 | 296.9882 | 335.5933 | 379.471 | 429.3605 | 486.1059 | 550.6718 | 624.1606 | 707.832 | 803.126 | 911.6889 | 1035.4029 | 1176.4205 | 1337.203 | 1520.5657 | 1729.729 | 1968.3769 | 2240.7243 | 2551.5939 | 2906.5044 | 3311.7714 | 3774.623 | 4303.3325 | 4907.3702 | 5597.5772 | 6386.3646 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 262.9875 | 296.967 | 335.5721 | 379.4498 | 429.3393 | 486.0847 | 550.6506 | 624.1394 | 707.8107 | 803.1048 | 911.6677 | 1035.3817 | 1176.3993 | 1337.1818 | 1520.5445 | 1729.7078 | 1968.3557 | 2240.6989 | 2551.5603 | 2906.4594 | 3311.7107 | 3774.5407 | 4303.2201 | 4907.2158 | 5597.3641 | 6386.0693 | 7104.9433 | 7104.7804 | 7104.5505 | 7104.2255 |  | 547.911 | 622.2064 | 706.6157 | 802.5537 | 911.6361 | 1035.7089 | 1176.8811 | 1337.5629 | 1520.5089 | 1728.8675 | 1966.2384 | 2236.7369 | 2545.0692 | 2896.6172 | 3297.5365 | 3754.8683 | 4276.6676 | 4866.8028 | 5535.9329 | 6297.4141 | 7163.4959 | 8147.7848 | 9265.2675 | 10532.263 | 11966.2621 | 13585.5927 | 15009.594 | 14801.0507 | 14506.7488 | 14090.7151 |  | 87.5862 | 98.9019 | 111.7581 | 126.3701 | 142.9841 | 161.8812 | 183.3827 | 207.8557 | 235.7196 | 267.4541 | 303.6073 | 344.8061 | 391.7673 | 445.3105 | 506.3733 | 576.0281 | 655.5017 | 746.1979 | 849.7226 | 967.9136 | 1102.8741 | 1257.0113 | 1433.0802 | 1634.2347 | 1864.0849 | 2126.764 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 72.9162 | 84.2319 | 97.088 | 111.7 | 128.314 | 147.2112 | 168.7127 | 193.1856 | 221.0496 | 252.784 | 288.9373 | 330.1361 | 377.0972 | 430.6404 | 491.7032 | 561.358 | 640.8317 | 728.6388 | 826.4469 | 936.7908 | 1060.9312 | 1200.0878 | 1355.3393 | 1527.469 | 1716.7305 | 1922.4976 | 2081.9414 | 1969.2705 | 1810.2663 | 1585.4933 |  | 11.8728 | 13.4068 | 15.1495 | 17.1302 | 19.3824 | 21.944 | 24.8587 | 28.1761 | 31.9532 | 36.255 | 41.1558 | 46.7406 | 53.1065 | 60.3646 | 68.642 | 78.0841 | 88.8573 | 101.1517 | 115.1851 | 131.2066 | 149.5013 | 170.3956 | 194.2628 | 221.5305 | 252.6881 | 288.2959 | 320.7528 | 320.7528 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 9.8052 | 11.3391 | 13.0818 | 15.0625 | 17.3147 | 19.8763 | 22.791 | 26.1084 | 29.8855 | 34.1873 | 39.0881 | 44.6729 | 51.0388 | 58.2969 | 66.5743 | 76.0164 | 86.7896 | 98.6768 | 111.9045 | 126.82 | 143.5896 | 162.3724 | 183.3055 | 206.4823 | 231.919 | 259.5053 | 280.6877 | 264.8071 | 242.396 | 210.7151 |  | 63.3828 | 71.5715 | 80.875 | 91.4492 | 103.4721 | 117.1473 | 132.7071 | 150.4172 | 170.5813 | 193.5463 | 219.709 | 249.523 | 283.507 | 322.2542 | 366.443 | 416.8495 | 474.3615 | 539.9949 | 614.9117 | 700.442 | 798.1078 | 909.651 | 1037.0653 | 1182.6331 | 1348.9669 | 1539.0577 | 1712.3279 | 1712.3279 | 1712.3279 | 1712.3279 |  | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0061184 | 0.0081103 | 0.010845 | 0.014615 | 0.019835 | 0.027089 | 0.037202 | 0.051345 | 0.071176 | 0.099049 | 0.13831 | 0.19371 | 0.27203 |  | 63.3777 | 71.5664 | 80.8699 | 91.4441 | 103.467 | 117.1421 | 132.702 | 150.4121 | 170.5762 | 193.5412 | 219.7039 | 249.5179 | 283.5019 | 322.2491 | 366.4379 | 416.8444 | 474.3564 | 539.9887 | 614.9036 | 700.4312 | 798.0932 | 909.6311 | 1037.0382 | 1182.5959 | 1348.9155 | 1538.9866 | 1712.2289 | 1712.1896 | 1712.1342 | 1712.0559 |  | 694.01 | 789.3437 | 897.6554 | 1020.7603 | 1160.7318 | 1319.9385 | 1501.0867 | 1707.2691 | 1942.0202 | 2209.3801 | 2513.9677 | 2861.0638 | 3256.7071 | 3707.8036 | 4222.2519 | 4809.0871 | 5478.6453 | 6234.1071 | 7089.1878 | 8061.456 | 9166.1099 | 10419.8761 | 11840.9505 | 13448.8101 | 15263.8272 | 17306.5821 | 19084.452 | 18747.318 | 18271.5453 | 17598.9794
| TRUE | 3856 | 22002953 | SHN | Blank | 22 | TRANS NO.2 | DIFFERENTIAL | Y | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.0068096 | 2190 |  | 8.25 | 0.026286 | 0.00052975 | 0.025756 | 276.5552 | 233.0884 | 509.6437 | 77.6223 | 10.5222 | 56.1723 |  | 13.0142 | 0.090569 | 0.0018253 | 0.088744 | 952.8944 | 803.126 | 1756.0204 | 267.4541 | 36.255 | 193.5463 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.0051117 |  | 653.9604 | 2253.2759 | 71.0275 | 2182.2484 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00059775 | 0.00067497 | 0.00076271 | 0.00086243 | 0.00097582 | 0.0011048 | 0.0012515 | 0.0014185 | 0.0016087 | 0.0018253 | 0.002072 | 0.0023532 | 0.0026737 | 0.0030391 | 0.0034558 | 0.0039312 | 0.0044736 | 0.0050926 | 0.0057991 | 0.0066057 | 0.0075268 | 0.0085787 | 0.0097803 | 0.011153 | 0.012722 | 0.014514 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 737.9057 | 833.2395 | 941.5512 | 1064.6561 | 1204.6276 | 1363.8343 | 1544.9825 | 1751.1649 | 1985.9159 | 2253.2759 | 2557.8634 | 2904.9595 | 3300.6029 | 3751.6993 | 4266.1476 | 4852.9829 | 5522.541 | 6286.6476 | 7158.8333 | 8154.5815 | 9291.6114 | 10590.2026 | 12073.5669 | 13768.2744 | 15704.741 | 17917.7883 | 19935.0088 | 19935.0088 | 19935.0088 | 19935.0088 |  | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 43.896 | 52.5408 | 69.646 | 93.1261 | 125.5023 | 170.3276 | 232.6179 | 319.4663 | 440.9166 | 611.2101 | 850.5622 | 1187.6983 | 1663.474 | 2336.0443 |  | 312.0551 | 352.3711 | 398.1753 | 450.2355 | 509.4285 | 576.7559 | 653.3622 | 740.5552 | 839.8298 | 952.8944 | 1081.7024 | 1228.4869 | 1395.8016 | 1586.5671 | 1804.1237 | 2052.2922 | 2335.4436 | 2658.5789 | 3027.42 | 3448.5149 | 3929.3568 | 4478.5218 | 5105.8261 | 5822.5059 | 6641.424 | 7577.3061 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 284.9234 | 325.2394 | 371.0437 | 423.1038 | 482.2968 | 549.6242 | 626.2305 | 713.4236 | 812.6981 | 925.7627 | 1054.5707 | 1201.3552 | 1368.6699 | 1559.4354 | 1776.992 | 2025.1605 | 2308.3119 | 2626.1039 | 2984.3726 | 3390.9546 | 3851.7851 | 4373.2441 | 4962.0474 | 5625.0471 | 6368.898 | 7199.5234 | 7904.6507 | 7696.2703 | 7402.1983 | 6986.4896 |  | 263.0087 | 296.9882 | 335.5933 | 379.471 | 429.3605 | 486.1059 | 550.6718 | 624.1606 | 707.832 | 803.126 | 911.6889 | 1035.4029 | 1176.4205 | 1337.203 | 1520.5657 | 1729.729 | 1968.3769 | 2240.7243 | 2551.5939 | 2906.5044 | 3311.7714 | 3774.623 | 4303.3325 | 4907.3702 | 5597.5772 | 6386.3646 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 262.9875 | 296.967 | 335.5721 | 379.4498 | 429.3393 | 486.0847 | 550.6506 | 624.1394 | 707.8107 | 803.1048 | 911.6677 | 1035.3817 | 1176.3993 | 1337.1818 | 1520.5445 | 1729.7078 | 1968.3557 | 2240.6989 | 2551.5603 | 2906.4594 | 3311.7107 | 3774.5407 | 4303.2201 | 4907.2158 | 5597.3641 | 6386.0693 | 7104.9433 | 7104.7804 | 7104.5505 | 7104.2255 |  | 547.911 | 622.2064 | 706.6157 | 802.5537 | 911.6361 | 1035.7089 | 1176.8811 | 1337.5629 | 1520.5089 | 1728.8675 | 1966.2384 | 2236.7369 | 2545.0692 | 2896.6172 | 3297.5365 | 3754.8683 | 4276.6676 | 4866.8028 | 5535.9329 | 6297.4141 | 7163.4959 | 8147.7848 | 9265.2675 | 10532.263 | 11966.2621 | 13585.5927 | 15009.594 | 14801.0507 | 14506.7488 | 14090.7151 |  | 87.5862 | 98.9019 | 111.7581 | 126.3701 | 142.9841 | 161.8812 | 183.3827 | 207.8557 | 235.7196 | 267.4541 | 303.6073 | 344.8061 | 391.7673 | 445.3105 | 506.3733 | 576.0281 | 655.5017 | 746.1979 | 849.7226 | 967.9136 | 1102.8741 | 1257.0113 | 1433.0802 | 1634.2347 | 1864.0849 | 2126.764 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 72.9162 | 84.2319 | 97.088 | 111.7 | 128.314 | 147.2112 | 168.7127 | 193.1856 | 221.0496 | 252.784 | 288.9373 | 330.1361 | 377.0972 | 430.6404 | 491.7032 | 561.358 | 640.8317 | 728.6388 | 826.4469 | 936.7908 | 1060.9312 | 1200.0878 | 1355.3393 | 1527.469 | 1716.7305 | 1922.4976 | 2081.9414 | 1969.2705 | 1810.2663 | 1585.4933 |  | 11.8728 | 13.4068 | 15.1495 | 17.1302 | 19.3824 | 21.944 | 24.8587 | 28.1761 | 31.9532 | 36.255 | 41.1558 | 46.7406 | 53.1065 | 60.3646 | 68.642 | 78.0841 | 88.8573 | 101.1517 | 115.1851 | 131.2066 | 149.5013 | 170.3956 | 194.2628 | 221.5305 | 252.6881 | 288.2959 | 320.7528 | 320.7528 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 9.8052 | 11.3391 | 13.0818 | 15.0625 | 17.3147 | 19.8763 | 22.791 | 26.1084 | 29.8855 | 34.1873 | 39.0881 | 44.6729 | 51.0388 | 58.2969 | 66.5743 | 76.0164 | 86.7896 | 98.6768 | 111.9045 | 126.82 | 143.5896 | 162.3724 | 183.3055 | 206.4823 | 231.919 | 259.5053 | 280.6877 | 264.8071 | 242.396 | 210.7151 |  | 63.3828 | 71.5715 | 80.875 | 91.4492 | 103.4721 | 117.1473 | 132.7071 | 150.4172 | 170.5813 | 193.5463 | 219.709 | 249.523 | 283.507 | 322.2542 | 366.443 | 416.8495 | 474.3615 | 539.9949 | 614.9117 | 700.442 | 798.1078 | 909.651 | 1037.0653 | 1182.6331 | 1348.9669 | 1539.0577 | 1712.3279 | 1712.3279 | 1712.3279 | 1712.3279 |  | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0051117 | 0.0061184 | 0.0081103 | 0.010845 | 0.014615 | 0.019835 | 0.027089 | 0.037202 | 0.051345 | 0.071176 | 0.099049 | 0.13831 | 0.19371 | 0.27203 |  | 63.3777 | 71.5664 | 80.8699 | 91.4441 | 103.467 | 117.1421 | 132.702 | 150.4121 | 170.5762 | 193.5412 | 219.7039 | 249.5179 | 283.5019 | 322.2491 | 366.4379 | 416.8444 | 474.3564 | 539.9887 | 614.9036 | 700.4312 | 798.0932 | 909.6311 | 1037.0382 | 1182.5959 | 1348.9155 | 1538.9866 | 1712.2289 | 1712.1896 | 1712.1342 | 1712.0559 |  | 694.01 | 789.3437 | 897.6554 | 1020.7603 | 1160.7318 | 1319.9385 | 1501.0867 | 1707.2691 | 1942.0202 | 2209.3801 | 2513.9677 | 2861.0638 | 3256.7071 | 3707.8036 | 4222.2519 | 4809.0871 | 5478.6453 | 6234.1071 | 7089.1878 | 8061.456 | 9166.1099 | 10419.8761 | 11840.9505 | 13448.8101 | 15263.8272 | 17306.5821 | 19084.452 | 18747.318 | 18271.5453 | 17598.9794
| TRUE | 3857 | 22002952 | SHN | Blank | 22 | TRANS NO.2 | DIFFERENTIAL | X | ASEA | GROUP_2819 | GROUP 2819 | GROUP 2000s | Electronic |  | 0.066046 | 2190 |  | 8.25 | 0.026286 | 0.0045837 | 0.021702 | 280.8119 | 2016.8282 | 2297.64 | 100.6375 | 10.5627 | 486.0379 |  | 13.0142 | 0.090569 | 0.015794 | 0.074776 | 967.5611 | 6949.1524 | 7916.7135 | 346.7551 | 36.3947 | 1674.6846 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.049579 |  | 2894.8781 | 9974.5479 | 71.2593 | 9903.2886 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0051721 | 0.0058403 | 0.0065995 | 0.0074623 | 0.0084434 | 0.0095593 | 0.010829 | 0.012274 | 0.01392 | 0.015794 | 0.017928 | 0.020361 | 0.023134 | 0.026296 | 0.029902 | 0.034015 | 0.038708 | 0.044064 | 0.050177 | 0.057157 | 0.065126 | 0.074228 | 0.084625 | 0.096504 | 0.11008 | 0.12559 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 3266.4781 | 3688.4908 | 4167.9528 | 4712.8997 | 5332.5097 | 6037.268 | 6839.1546 | 7751.8595 | 8791.0291 | 9974.5479 | 11322.8619 | 12859.3479 | 14610.7372 | 16607.6003 | 18884.9021 | 21482.6382 | 24446.563 | 27829.024 | 31689.9175 | 36097.7836 | 41131.0595 | 46879.5168 | 53445.9071 | 60947.8473 | 69519.9799 | 79316.4486 | 88246.053 | 88246.053 | 88246.053 | 88246.053 |  | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 44.1301 | 52.8209 | 70.0172 | 93.6225 | 126.1714 | 171.2356 | 233.858 | 321.1694 | 443.2672 | 614.4685 | 855.0966 | 1194.03 | 1672.3421 | 2348.4978 |  | 316.8582 | 357.7947 | 404.3039 | 457.1654 | 517.2694 | 585.6331 | 663.4185 | 751.9536 | 852.7562 | 967.5611 | 1098.3516 | 1247.3954 | 1417.2854 | 1610.9871 | 1831.8922 | 2083.8804 | 2371.39 | 2699.4989 | 3074.0171 | 3501.5934 | 3989.8362 | 4547.4539 | 5184.4134 | 5912.1241 | 6743.6467 | 7693.9336 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 289.7263 | 330.6628 | 377.172 | 430.0335 | 490.1375 | 558.5012 | 636.2866 | 724.8217 | 825.6243 | 940.4292 | 1071.2197 | 1220.2634 | 1390.1535 | 1583.8552 | 1804.7603 | 2056.7485 | 2344.2581 | 2667.0237 | 3030.9693 | 3444.0326 | 3912.2639 | 4442.1753 | 5040.6335 | 5714.6637 | 6471.1185 | 7316.1479 | 8034.4041 | 7826.022 | 7531.9476 | 7116.2356 |  | 2275.7176 | 2569.729 | 2903.7646 | 3283.4228 | 3715.0979 | 4206.0949 | 4764.7601 | 5400.6311 | 6124.6085 | 6949.1524 | 7888.5072 | 8958.9593 | 10179.132 | 11570.3234 | 13156.8933 | 14966.7061 | 17031.6383 | 19388.1598 | 22077.9998 | 25148.9092 | 28655.5344 | 32660.4183 | 37235.1466 | 42461.6617 | 48433.7676 | 55258.8543 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 2275.5118 | 2569.5233 | 2903.5589 | 3283.2171 | 3714.8922 | 4205.8892 | 4764.5543 | 5400.4253 | 6124.4028 | 6948.9467 | 7888.3015 | 8958.7535 | 10178.9262 | 11570.1177 | 13156.6876 | 14966.5004 | 17031.4326 | 19387.9136 | 22077.6734 | 25148.4727 | 28654.9462 | 32659.62 | 37234.0564 | 42460.1645 | 48431.7012 | 55255.9897 | 61476.0203 | 61474.4402 | 61472.2104 | 61469.0582 |  | 2565.2381 | 2900.186 | 3280.7309 | 3713.2506 | 4205.0297 | 4764.3904 | 5400.8409 | 6125.2471 | 6950.0271 | 7889.3759 | 8959.5212 | 10179.017 | 11569.0797 | 13153.9729 | 14961.4479 | 17023.2489 | 19375.6907 | 22054.9372 | 25108.6427 | 28592.5053 | 32567.2101 | 37101.7953 | 42274.6899 | 48174.8282 | 54902.8197 | 62572.1376 | 69510.4244 | 69300.4622 | 69004.158 | 68585.2938 |  | 113.5558 | 128.2266 | 144.8947 | 163.8392 | 185.3793 | 209.8795 | 237.7563 | 269.4855 | 305.6112 | 346.7551 | 393.6278 | 447.0422 | 507.9275 | 577.3464 | 656.5145 | 746.8222 | 849.86 | 967.4478 | 1101.6679 | 1254.9029 | 1429.8796 | 1629.7189 | 1857.9928 | 2118.7902 | 2416.7917 | 2757.356 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 98.8834 | 113.5542 | 130.2222 | 149.1667 | 170.7069 | 195.2071 | 223.0838 | 254.8131 | 290.9388 | 332.0826 | 378.9554 | 432.3698 | 493.255 | 562.674 | 641.8421 | 732.1497 | 835.1876 | 949.8858 | 1078.3884 | 1223.7751 | 1387.9299 | 1572.7862 | 1780.2393 | 2012.0072 | 2269.4134 | 2553.0564 | 2783.4806 | 2670.7914 | 2511.7613 | 2286.9518 |  | 11.9186 | 13.4584 | 15.2079 | 17.1962 | 19.457 | 22.0285 | 24.9544 | 28.2847 | 32.0763 | 36.3947 | 41.3144 | 46.9207 | 53.3111 | 60.5971 | 68.9065 | 78.385 | 89.1996 | 101.5414 | 115.6289 | 131.7121 | 150.0773 | 171.0521 | 195.0112 | 222.384 | 253.6617 | 289.4066 | 321.9886 | 321.9886 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 9.8509 | 11.3907 | 13.1402 | 15.1285 | 17.3893 | 19.9608 | 22.8867 | 26.217 | 30.0087 | 34.327 | 39.2467 | 44.853 | 51.2434 | 58.5294 | 66.8388 | 76.3173 | 87.1319 | 99.0665 | 112.3482 | 127.3255 | 144.1656 | 163.0289 | 184.0539 | 207.3357 | 232.8925 | 260.6159 | 281.9234 | 266.0428 | 243.6317 | 211.9507 |  | 548.4279 | 619.2821 | 699.7817 | 791.276 | 895.3059 | 1013.6319 | 1148.2653 | 1301.5046 | 1475.9768 | 1674.6846 | 1901.0609 | 2159.0304 | 2453.0813 | 2788.3462 | 3170.6956 | 3606.8446 | 4104.4751 | 4672.3761 | 5320.6039 | 6060.666 | 6905.7319 | 7870.8737 | 8973.343 | 10232.8872 | 11672.1122 | 13316.8981 | 14816.1411 | 14816.1411 | 14816.1411 | 14816.1411 |  | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.049579 | 0.059343 | 0.078663 | 0.10518 | 0.14175 | 0.19238 | 0.26273 | 0.36083 | 0.498 | 0.69034 | 0.96068 | 1.3415 | 1.8788 | 2.6385 |  | 548.3783 | 619.2325 | 699.7322 | 791.2265 | 895.2564 | 1013.5823 | 1148.2157 | 1301.455 | 1475.9272 | 1674.6351 | 1901.0113 | 2158.9808 | 2453.0317 | 2788.2967 | 3170.6461 | 3606.795 | 4104.4255 | 4672.3167 | 5320.5252 | 6060.5608 | 6905.5901 | 7870.6813 | 8973.0803 | 10232.5264 | 11671.6142 | 13316.2078 | 14815.1805 | 14814.7997 | 14814.2623 | 14813.5027 |  | 3222.3507 | 3644.3635 | 4123.8255 | 4668.7723 | 5288.3823 | 5993.1406 | 6795.0272 | 7707.7322 | 8746.9017 | 9930.4206 | 11278.7345 | 12815.2206 | 14566.6099 | 16563.4729 | 18840.7748 | 21438.5109 | 24402.4357 | 27776.2063 | 31619.9046 | 36004.1667 | 41004.8958 | 46708.2917 | 53212.0634 | 60626.6975 | 69076.7399 | 78702.0177 | 87391.0088 | 87052.0961 | 86573.8133 | 85897.6989
| TRUE | 3858 | 22015970 | SHN | Blank | 66 | CB A | SUPP FOR CB FAIL | X | ABB | CUB_3166 | CUB 3166 | CUB 3000s | Electronic |  | 0 | 2190 |  | 5.5 | 0.0093284 | 0 | 0.0093284 | 97.9479 | 0 | 97.9479 | 26.4797 | 3.7323 | 0 |  | 8.1226 | 0.025228 | 0 | 0.025228 | 264.896 | 0 | 264.896 | 71.6132 | 10.0938 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 128.1599 | 346.603 | 71.0008 | 275.6022 |  | 0.03899 |  | 5.7187 | 5.9461 | 6.1825 | 6.4283 | 6.6839 | 6.9496 | 7.226 | 7.5133 | 7.812 | 8.1226 | 8.4456 | 8.7813 | 9.1305 | 9.4935 | 9.871 | 10.2635 | 10.6715 | 11.0958 | 11.537 | 11.9957 | 12.4727 | 12.9686 | 13.4842 | 14.0204 | 14.5778 | 15.1575 | 15.7601 | 16.3867 | 17.0383 | 17.7157 |  | 0.01027 | 0.011317 | 0.012479 | 0.013771 | 0.015208 | 0.016807 | 0.018586 | 0.020566 | 0.022771 | 0.025228 | 0.027966 | 0.031018 | 0.034422 | 0.038218 | 0.042454 | 0.047182 | 0.052459 | 0.058352 | 0.064935 | 0.072288 | 0.080506 | 0.089691 | 0.099958 | 0.11144 | 0.12428 | 0.13864 | 0.15471 | 0.1727 | 0.19282 | 0.21535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.1029 | 155.4775 | 171.4487 | 189.2016 | 208.9426 | 230.9033 | 255.3422 | 282.5492 | 312.8485 | 346.603 | 384.2192 | 426.1524 | 472.9122 | 525.0698 | 583.265 | 648.2147 | 720.7221 | 801.6875 | 892.1201 | 993.1509 | 1106.0481 | 1232.2334 | 1373.3011 | 1531.039 | 1707.4521 | 1904.7893 | 2125.5729 | 2372.6327 | 2649.1432 | 2958.666 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 107.8398 | 118.8258 | 131.032 | 144.5999 | 159.6872 | 176.4709 | 195.1488 | 215.9421 | 239.0987 | 264.896 | 293.6448 | 325.6927 | 361.4295 | 401.2917 | 445.7682 | 495.4068 | 550.8216 | 612.7005 | 681.8148 | 759.029 | 845.3122 | 941.7511 | 1049.564 | 1170.1173 | 1304.9434 | 1455.761 | 1624.4979 | 1813.3167 | 2024.6436 | 2261.2006 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 80.7082 | 91.6941 | 103.9004 | 117.4682 | 132.5556 | 149.3393 | 168.0171 | 188.8104 | 211.967 | 237.7644 | 266.5131 | 298.5611 | 334.2979 | 374.1601 | 418.6365 | 468.2752 | 523.6899 | 580.2256 | 638.7674 | 701.4688 | 767.7406 | 836.4735 | 905.7854 | 972.6587 | 1032.4177 | 1077.9787 | 1098.7747 | 1079.2133 | 996.4685 | 817.3172 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 80.7082 | 91.6941 | 103.9004 | 117.4682 | 132.5556 | 149.3393 | 168.0171 | 188.8104 | 211.967 | 237.7644 | 266.5131 | 298.5611 | 334.2979 | 374.1601 | 418.6365 | 468.2752 | 523.6899 | 580.2256 | 638.7674 | 701.4688 | 767.7406 | 836.4735 | 905.7854 | 972.6587 | 1032.4177 | 1077.9787 | 1098.7747 | 1079.2133 | 996.4685 | 817.3172 |  | 29.1539 | 32.1239 | 35.4238 | 39.0918 | 43.1705 | 47.7079 | 52.7574 | 58.3787 | 64.639 | 71.6132 | 79.3852 | 88.0492 | 97.7104 | 108.487 | 120.5109 | 133.9305 | 148.9115 | 165.6401 | 184.3248 | 205.1992 | 228.5254 | 254.5971 | 283.7437 | 316.3346 | 352.7841 | 393.5568 | 439.1739 | 490.22 | 547.351 | 611.3029 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 14.4841 | 17.4541 | 20.754 | 24.422 | 28.5008 | 33.0381 | 38.0876 | 43.7089 | 49.9692 | 56.9434 | 64.7154 | 73.3794 | 83.0407 | 93.8172 | 105.8411 | 119.2607 | 134.2417 | 148.0813 | 161.0496 | 174.0771 | 186.5833 | 197.6747 | 206.0043 | 209.571 | 205.4325 | 189.2942 | 154.9213 | 93.2985 | -8.5717 | -169.3887 |  | 4.1092 | 4.5278 | 4.9929 | 5.5099 | 6.0848 | 6.7244 | 7.4361 | 8.2284 | 9.1108 | 10.0938 | 11.1893 | 12.4104 | 13.7722 | 15.2911 | 16.9859 | 18.8774 | 20.9889 | 23.3468 | 25.9804 | 28.9226 | 32.2104 | 35.8852 | 39.9934 | 44.587 | 49.7246 | 55.4714 | 61.9011 | 69.096 | 77.1486 | 86.1625 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 2.0415 | 2.4601 | 2.9253 | 3.4423 | 4.0172 | 4.6567 | 5.3684 | 6.1607 | 7.0431 | 8.0261 | 9.1216 | 10.3428 | 11.7045 | 13.2234 | 14.9182 | 16.8097 | 18.9212 | 20.8719 | 22.6998 | 24.536 | 26.2987 | 27.862 | 29.0361 | 29.5388 | 28.9555 | 26.6808 | 21.836 | 13.1503 | -1.2082 | -23.8752 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 97.2338 | 111.6083 | 127.5796 | 145.3324 | 165.0735 | 187.0341 | 211.4731 | 238.6801 | 268.9794 | 302.7339 | 340.3501 | 382.2832 | 429.043 | 481.2007 | 539.3959 | 604.3455 | 676.8529 | 749.1789 | 822.5168 | 900.0819 | 980.6227 | 1062.0102 | 1140.8257 | 1211.7685 | 1266.8057 | 1293.9537 | 1275.532 | 1185.6622 | 986.6886 | 624.0534
| TRUE | 3859 | 22002958 | SHN | Blank | 66 | CB A | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 275.999 | 0 | 275.999 | 74.6148 | 10.5169 | 0 |  | 13.0142 | 0.090569 | 0 | 0.090569 | 950.9779 | 0 | 950.9779 | 257.0915 | 36.2368 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 361.1306 | 1244.3062 | 71.0008 | 1173.3054 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407.487 | 460.1323 | 519.9443 | 587.9254 | 665.2206 | 753.1379 | 853.1717 | 967.03 | 1096.6644 | 1244.3062 | 1412.5058 | 1604.1796 | 1822.6621 | 2071.7671 | 2355.8562 | 2679.919 | 3049.663 | 3471.6187 | 3953.258 | 4503.131 | 5131.0228 | 5848.1321 | 6667.277 | 7603.13 | 8672.4875 | 9894.5787 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 311.4275 | 351.6624 | 397.3745 | 449.33 | 508.4039 | 575.5958 | 652.0481 | 739.0658 | 838.1407 | 950.9779 | 1079.5267 | 1226.016 | 1392.9943 | 1583.3761 | 1800.4951 | 2048.1644 | 2330.7463 | 2653.2317 | 3021.331 | 3441.5789 | 3921.4537 | 4469.5142 | 5095.5568 | 5810.7952 | 6628.0662 | 7562.0659 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 284.2958 | 324.5307 | 370.2428 | 422.1983 | 481.2722 | 548.4642 | 624.9164 | 711.9341 | 811.009 | 923.8462 | 1052.3951 | 1198.8844 | 1365.8626 | 1556.2444 | 1773.3634 | 2021.0327 | 2303.6147 | 2620.7568 | 2978.2836 | 3384.0187 | 3843.8821 | 4364.2366 | 4951.7782 | 5613.3366 | 6355.5404 | 7184.2836 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 284.2958 | 324.5307 | 370.2428 | 422.1983 | 481.2722 | 548.4642 | 624.9164 | 711.9341 | 811.009 | 923.8462 | 1052.3951 | 1198.8844 | 1365.8626 | 1556.2444 | 1773.3634 | 2021.0327 | 2303.6147 | 2620.7568 | 2978.2836 | 3384.0187 | 3843.8821 | 4364.2366 | 4951.7782 | 5613.3366 | 6355.5404 | 7184.2836 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 84.1927 | 95.0699 | 107.428 | 121.4738 | 137.4441 | 155.6091 | 176.2775 | 199.8023 | 226.5866 | 257.0915 | 291.844 | 331.4465 | 376.5882 | 428.0568 | 486.7537 | 553.7097 | 630.1042 | 717.2863 | 816.7999 | 930.4115 | 1060.143 | 1208.3081 | 1377.5552 | 1570.9158 | 1791.8605 | 2044.362 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 69.5229 | 80.4002 | 92.7582 | 106.804 | 122.7743 | 140.9393 | 161.6077 | 185.1325 | 211.9168 | 242.4217 | 277.1742 | 316.7768 | 361.9184 | 413.387 | 472.0839 | 539.04 | 615.4344 | 699.7275 | 793.5246 | 899.2894 | 1018.2009 | 1151.3856 | 1299.8157 | 1464.1522 | 1644.5088 | 1840.0994 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 11.8669 | 13.4 | 15.1419 | 17.1216 | 19.3726 | 21.9329 | 24.8461 | 28.1619 | 31.9372 | 36.2368 | 41.1351 | 46.717 | 53.0797 | 60.3342 | 68.6074 | 78.0448 | 88.8125 | 101.1008 | 115.1271 | 131.1405 | 149.4261 | 170.3098 | 194.165 | 221.419 | 252.5609 | 288.1507 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 9.7992 | 11.3323 | 13.0742 | 15.0539 | 17.3049 | 19.8653 | 22.7784 | 26.0942 | 29.8695 | 34.1691 | 39.0674 | 44.6494 | 51.012 | 58.2665 | 66.5397 | 75.9771 | 86.7448 | 98.6259 | 111.8465 | 126.7539 | 143.5144 | 162.2866 | 183.2077 | 206.3707 | 231.7918 | 259.3601 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 363.6179 | 416.2632 | 476.0752 | 544.0563 | 621.3515 | 709.2687 | 809.3026 | 923.1608 | 1052.7953 | 1200.4371 | 1368.6367 | 1560.3105 | 1778.793 | 2027.8979 | 2311.9871 | 2636.0498 | 3005.7939 | 3419.1101 | 3883.6547 | 4410.062 | 5005.5974 | 5677.9089 | 6434.8016 | 7283.8595 | 8231.8411 | 9283.7431 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| TRUE | 3860 | 22002943 | SHN | SHN-ALL | 66 | ALL LINE | EARTH FAULT | X | ASEA | GROUP_2890 | GROUP 2890 | GROUP 2000s | Electronic |  | 0.15703 | 2190 |  | 8.25 | 0.026286 | 0.0092625 | 0.017023 | 285.7247 | 4075.5196 | 4361.2443 | 127.2004 | 10.6095 | 196.4329 |  | 13.0142 | 0.090569 | 0.031915 | 0.058654 | 984.4885 | 14042.5484 | 15027.0369 | 438.2797 | 36.5559 | 676.8261 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.023575 |  | 4695.4871 | 16178.6987 | 71.521 | 16107.1777 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.010452 | 0.011802 | 0.013336 | 0.01508 | 0.017062 | 0.019317 | 0.021883 | 0.024803 | 0.028128 | 0.031915 | 0.036229 | 0.041145 | 0.046749 | 0.053138 | 0.060425 | 0.068737 | 0.07822 | 0.089043 | 0.1014 | 0.1155 | 0.1316 | 0.15 | 0.17101 | 0.19501 | 0.22244 | 0.25378 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 5298.2215 | 5982.7255 | 6760.412 | 7644.3148 | 8649.321 | 9792.4377 | 11093.0964 | 12573.5022 | 14259.0333 | 16178.6987 | 18365.6616 | 20857.8391 | 23698.5894 | 26937.4977 | 30631.2771 | 34844.8005 | 39652.2811 | 45138.6267 | 51400.9891 | 58550.5398 | 66714.5042 | 76038.4917 | 86689.1649 | 98857.2983 | 112761.282 | 128651.1365 | 143134.9388 | 143134.9388 | 143134.9388 | 143134.9388 |  | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 53.1382 | 70.4379 | 94.185 | 126.9293 | 172.2643 | 235.263 | 323.0988 | 445.9302 | 618.16 | 860.2337 | 1201.2033 | 1682.3889 | 2362.6067 |  | 322.4016 | 364.0543 | 411.3772 | 465.1635 | 526.319 | 595.8787 | 675.025 | 765.109 | 867.6751 | 984.4885 | 1117.5672 | 1269.2185 | 1442.0807 | 1639.1712 | 1863.941 | 2120.3378 | 2412.8773 | 2746.7264 | 3127.7969 | 3562.8535 | 4059.6382 | 4627.0113 | 5275.1144 | 6015.5564 | 6861.6264 | 7828.5385 | 8709.891 | 8709.891 | 8709.891 | 8709.891 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 295.2693 | 336.922 | 384.245 | 438.0312 | 499.1868 | 568.7465 | 647.8927 | 737.9768 | 840.5429 | 957.3563 | 1090.4349 | 1242.0862 | 1414.9484 | 1612.039 | 1836.8088 | 2093.2055 | 2385.7451 | 2714.2508 | 3084.7485 | 3505.2921 | 3982.0649 | 4521.7314 | 5131.3327 | 5818.0935 | 6589.0948 | 7450.7481 | 8184.1565 | 7975.7719 | 7681.6938 | 7265.9765 |  | 4598.6722 | 5192.7978 | 5867.8027 | 6634.9996 | 7507.3102 | 8499.4957 | 9628.4223 | 10913.363 | 12376.3455 | 14042.5484 | 15940.7562 | 18103.8797 | 20569.5522 | 23380.8121 | 26586.8844 | 30244.0762 | 34416.8024 | 39178.7597 | 44614.2727 | 50819.8344 | 57905.8719 | 65998.7691 | 75243.1834 | 85804.7004 | 97872.8752 | 111664.7168 | 124236.154 | 124236.154 | 124236.154 | 124236.154 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 4598.1831 | 5192.3087 | 5867.3136 | 6634.5105 | 7506.821 | 8499.0066 | 9627.9331 | 10912.8739 | 12375.8564 | 14042.0593 | 15940.267 | 18103.3906 | 20569.0631 | 23380.323 | 26586.3952 | 30243.5871 | 34416.3132 | 39178.1743 | 44613.4967 | 50818.7967 | 57904.4734 | 65996.8711 | 75240.5913 | 85801.1406 | 97867.9621 | 111657.9062 | 124226.6763 | 124222.9196 | 124217.6181 | 124210.1237 |  | 4893.4524 | 5529.2307 | 6251.5585 | 7072.5417 | 8006.0078 | 9067.7531 | 10275.8259 | 11650.8507 | 13216.3993 | 14999.4155 | 17030.702 | 19345.4768 | 21984.0116 | 24992.3619 | 28423.204 | 32336.7926 | 36802.0583 | 41892.4251 | 47698.2452 | 54324.0887 | 61886.5383 | 70518.6025 | 80371.9241 | 91619.2341 | 104457.0569 | 119108.6543 | 132410.8328 | 132198.6915 | 131899.3119 | 131476.1003 |  | 143.5284 | 162.0716 | 183.139 | 207.0839 | 234.3095 | 265.2764 | 300.5111 | 340.6152 | 386.2761 | 438.2797 | 497.5244 | 565.0373 | 641.993 | 729.7348 | 829.799 | 943.943 | 1074.1773 | 1222.802 | 1392.4489 | 1586.1297 | 1807.2909 | 2059.877 | 2348.4029 | 2678.0367 | 3054.6946 | 3485.1496 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 128.8523 | 147.3955 | 168.463 | 192.4078 | 219.6334 | 250.6003 | 285.835 | 325.9391 | 371.6 | 423.6036 | 482.8483 | 550.3612 | 627.3169 | 715.0587 | 815.1229 | 929.2669 | 1059.5012 | 1205.2356 | 1369.1636 | 1554.9941 | 1765.3307 | 2002.9301 | 2270.63 | 2571.2271 | 2907.2796 | 3280.799 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 11.9714 | 13.518 | 15.2752 | 17.2724 | 19.5432 | 22.1261 | 25.065 | 28.41 | 32.2184 | 36.5559 | 41.4974 | 47.1285 | 53.5472 | 60.8656 | 69.2117 | 78.7322 | 89.5947 | 101.9912 | 116.1411 | 132.2955 | 150.7421 | 171.8097 | 195.8751 | 223.3691 | 254.7853 | 290.6886 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 9.9037 | 11.4503 | 13.2075 | 15.2047 | 17.4755 | 20.0584 | 22.9973 | 26.3423 | 30.1507 | 34.4882 | 39.4297 | 45.0608 | 51.4795 | 58.7978 | 67.144 | 76.6645 | 87.527 | 99.5163 | 112.8604 | 127.9089 | 144.8304 | 163.7865 | 184.9177 | 208.3208 | 234.0161 | 261.8978 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 221.6479 | 250.2837 | 282.8178 | 319.7953 | 361.8392 | 409.6608 | 464.073 | 526.0049 | 596.5181 | 676.8261 | 768.3164 | 872.5752 | 991.4163 | 1126.914 | 1281.4411 | 1457.7113 | 1658.8294 | 1888.3473 | 2150.3295 | 2449.4267 | 2790.9612 | 3181.0246 | 3626.5891 | 4135.6357 | 4717.3005 | 5382.043 | 5987.9642 | 5987.9642 | 5987.9642 | 5987.9642 |  | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.028218 | 0.037405 | 0.050015 | 0.067403 | 0.091478 | 0.12493 | 0.17158 | 0.2368 | 0.32826 | 0.45681 | 0.63788 | 0.8934 | 1.2546 |  | 221.6243 | 250.2602 | 282.7942 | 319.7717 | 361.8156 | 409.6372 | 464.0495 | 525.9813 | 596.4945 | 676.8026 | 768.2928 | 872.5516 | 991.3927 | 1126.8905 | 1281.4175 | 1457.6877 | 1658.8058 | 1888.3191 | 2150.2921 | 2449.3767 | 2790.8938 | 3180.9332 | 3626.4642 | 4135.4641 | 4717.0637 | 5381.7148 | 5987.5074 | 5987.3263 | 5987.0708 | 5986.7096 |  | 5253.8328 | 5938.3367 | 6716.0232 | 7599.926 | 8604.9323 | 9748.049 | 11048.7076 | 12529.1134 | 14214.6446 | 16134.31 | 18321.2728 | 20813.4504 | 23654.2006 | 26893.1089 | 30586.8884 | 34800.4117 | 39607.8923 | 45085.4961 | 51330.5614 | 58456.3684 | 66587.5932 | 75866.2523 | 86453.936 | 98534.2462 | 112315.4163 | 128033.0659 | 142274.8295 | 141933.9092 | 141452.7932 | 140772.6737
| FALSE | 3861 | 22002939 | SHN | SHN-SHTS NO.1 | 66 | SHTS NO.1 LINE | PILOT WIRE | X | English Electric | DSF7_1490 | DSF7 1490 | DSF7 | Electromechanical |  | 0.15703 | 2190 |  | 5.5 | 0.0019187 | 0.00067613 | 0.0012426 | 20.8568 | 297.4968 | 318.3535 | 9.2851 | 0.77445 | 14.3388 |  | 8.1226 | 0.0051892 | 0.0018286 | 0.0033606 | 56.4062 | 804.5673 | 860.9735 | 25.1112 | 2.0945 | 38.7787 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.023575 |  | 342.7519 | 926.958 | 71.521 | 855.437 |  | 0.03899 |  | 5.7187 | 5.9461 | 6.1825 | 6.4283 | 6.6839 | 6.9496 | 7.226 | 7.5133 | 7.812 | 8.1226 | 8.4456 | 8.7813 | 9.1305 | 9.4935 | 9.871 | 10.2635 | 10.6715 | 11.0958 | 11.537 | 11.9957 | 12.4727 | 12.9686 | 13.4842 | 14.0204 | 14.5778 | 15.1575 | 15.7601 | 16.3867 | 17.0383 | 17.7157 |  | 0.0021125 | 0.0023277 | 0.0025668 | 0.0028326 | 0.0031282 | 0.003457 | 0.0038229 | 0.0042302 | 0.0046838 | 0.0051892 | 0.0057523 | 0.0063801 | 0.0070802 | 0.0078611 | 0.0087324 | 0.0097047 | 0.01079 | 0.012002 | 0.013356 | 0.014869 | 0.016559 | 0.018448 | 0.02056 | 0.022922 | 0.025563 | 0.028518 | 0.031823 | 0.035522 | 0.039662 | 0.044296 |  | 0.00074441 | 0.00082025 | 0.00090451 | 0.00099816 | 0.0011023 | 0.0012182 | 0.0013471 | 0.0014906 | 0.0016505 | 0.0018286 | 0.002027 | 0.0022482 | 0.0024949 | 0.0027701 | 0.0030771 | 0.0034198 | 0.0038023 | 0.0042294 | 0.0047065 | 0.0052395 | 0.0058351 | 0.0065009 | 0.0072451 | 0.0080773 | 0.0090079 | 0.010049 | 0.011214 | 0.012517 | 0.013976 | 0.015609 | 377.3668 | 415.8102 | 458.5239 | 506.0022 | 558.7979 | 617.5296 | 682.8894 | 755.652 | 836.6846 | 926.958 | 1027.5591 | 1139.7054 | 1264.7603 | 1404.2511 | 1559.8888 | 1733.5907 | 1927.5051 | 2144.0397 | 2385.8933 | 2656.091 | 2958.0241 | 3295.4952 | 3672.7679 | 4094.6235 | 4566.4242 | 5094.1843 | 5684.6499 | 6345.3887 | 7084.8907 | 7912.6811 |  | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 53.1382 | 70.4379 | 94.185 | 126.9293 | 172.2643 | 235.263 | 323.0988 | 445.9302 | 618.16 | 860.2337 | 1201.2033 | 1682.3889 | 2362.6067 |  | 22.9631 | 25.3024 | 27.9016 | 30.7907 | 34.0034 | 37.5772 | 41.5544 | 45.9821 | 50.913 | 56.4062 | 62.5279 | 69.3521 | 76.9618 | 85.45 | 94.9207 | 105.4906 | 117.2904 | 130.4668 | 145.1838 | 161.6255 | 179.9985 | 200.5339 | 223.4913 | 249.1616 | 277.8711 | 309.9857 | 345.9161 | 386.1227 | 431.122 | 481.4938 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | -4.1691 | -1.8298 | 0.76935 | 3.6584 | 6.8711 | 10.445 | 14.4222 | 18.8499 | 23.7808 | 29.274 | 35.3957 | 42.2199 | 49.8296 | 58.3177 | 67.7884 | 78.3583 | 90.1582 | 97.9912 | 102.1354 | 104.0641 | 102.4252 | 95.254 | 79.7096 | 51.6987 | 5.3395 | -67.8047 | -179.8184 | -347.9965 | -597.0752 | -962.4207 |  | 327.5413 | 360.9088 | 397.9828 | 439.1923 | 485.0172 | 535.9942 | 592.7243 | 655.8797 | 726.2132 | 804.5673 | 891.8856 | 989.2247 | 1097.768 | 1218.8411 | 1353.9293 | 1504.6965 | 1673.0074 | 1860.952 | 2070.8725 | 2305.3947 | 2567.4622 | 2860.3754 | 3187.835 | 3553.991 | 3963.4976 | 4421.575 | 4934.0786 | 5507.5769 | 6149.439 | 6867.9323 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 327.0522 | 360.4197 | 397.4937 | 438.7032 | 484.5281 | 535.5051 | 592.2352 | 655.3906 | 725.7241 | 804.0782 | 891.3965 | 988.7356 | 1097.2789 | 1218.352 | 1353.4402 | 1504.2074 | 1672.5183 | 1860.3665 | 2070.0964 | 2304.357 | 2566.0637 | 2858.4774 | 3185.2429 | 3550.4312 | 3958.5845 | 4414.7643 | 4924.6009 | 5494.3425 | 6130.903 | 6841.902 |  | 322.883 | 358.5899 | 398.2631 | 442.3617 | 491.3992 | 545.9501 | 606.6574 | 674.2405 | 749.5048 | 833.3522 | 926.7921 | 1030.9554 | 1147.1084 | 1276.6697 | 1421.2286 | 1582.5657 | 1762.6765 | 1958.3577 | 2172.2319 | 2408.4211 | 2668.4889 | 2953.7315 | 3264.9525 | 3602.1299 | 3963.9239 | 4346.9597 | 4744.7825 | 5146.346 | 5533.8278 | 5879.4814 |  | 10.2228 | 11.2643 | 12.4214 | 13.7076 | 15.1378 | 16.7288 | 18.4994 | 20.4706 | 22.6657 | 25.1112 | 27.8365 | 30.8745 | 34.2623 | 38.0411 | 42.2573 | 46.9628 | 52.216 | 58.0819 | 64.6337 | 71.9533 | 80.1327 | 89.2747 | 99.495 | 110.923 | 123.7041 | 138.0011 | 153.9967 | 171.8961 | 191.9292 | 214.3539 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | -4.4533 | -3.4118 | -2.2547 | -0.96854 | 0.4617 | 2.0527 | 3.8233 | 5.7945 | 7.9896 | 10.4351 | 13.1604 | 16.1984 | 19.5862 | 23.365 | 27.5812 | 32.2867 | 37.5399 | 40.5155 | 41.3484 | 40.8178 | 38.1725 | 32.3278 | 21.7221 | 4.1135 | -23.7109 | -66.3494 | -130.3782 | -225.1961 | -364.2327 | -566.6735 |  | 0.85266 | 0.93953 | 1.036 | 1.1433 | 1.2626 | 1.3953 | 1.543 | 1.7074 | 1.8905 | 2.0945 | 2.3218 | 2.5752 | 2.8577 | 3.1729 | 3.5246 | 3.9171 | 4.3552 | 4.8445 | 5.391 | 6.0015 | 6.6837 | 7.4462 | 8.2987 | 9.2518 | 10.3179 | 11.5104 | 12.8445 | 14.3375 | 16.0084 | 17.8788 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | -1.215 | -1.1282 | -1.0317 | -0.92439 | -0.80509 | -0.67239 | -0.52471 | -0.3603 | -0.1772 | 0.026769 | 0.25408 | 0.50747 | 0.79004 | 1.1052 | 1.4569 | 1.8494 | 2.2875 | 2.3696 | 2.1103 | 1.6148 | 0.77196 | -0.57699 | -2.6587 | -5.7965 | -10.4513 | -17.2804 | -27.2208 | -41.6085 | -62.3488 | -92.1595 |  | 15.7869 | 17.3952 | 19.1821 | 21.1683 | 23.377 | 25.834 | 28.5683 | 31.6122 | 35.0022 | 38.7787 | 42.9873 | 47.6789 | 52.9105 | 58.746 | 65.257 | 72.5237 | 80.636 | 89.6946 | 99.8124 | 111.116 | 123.7472 | 137.8651 | 153.648 | 171.2961 | 191.0336 | 213.1121 | 237.8139 | 265.4555 | 296.3921 | 331.0223 |  | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.028218 | 0.037405 | 0.050015 | 0.067403 | 0.091478 | 0.12493 | 0.17158 | 0.2368 | 0.32826 | 0.45681 | 0.63788 | 0.8934 | 1.2546 |  | 15.7633 | 17.3716 | 19.1585 | 21.1447 | 23.3534 | 25.8104 | 28.5447 | 31.5887 | 34.9786 | 38.7552 | 42.9637 | 47.6553 | 52.8869 | 58.7224 | 65.2334 | 72.5001 | 80.6124 | 89.6664 | 99.775 | 111.066 | 123.6798 | 137.7736 | 153.5231 | 171.1245 | 190.7968 | 212.7839 | 237.3571 | 264.8176 | 295.4987 | 329.7676 |  | 332.9781 | 371.4215 | 414.1352 | 461.6135 | 514.4092 | 573.1408 | 638.5007 | 711.2633 | 792.2959 | 882.5692 | 983.1704 | 1095.3167 | 1220.3715 | 1359.8623 | 1515.5001 | 1689.2019 | 1883.1163 | 2090.9092 | 2315.4656 | 2561.9196 | 2831.1132 | 3123.2559 | 3437.539 | 3771.5714 | 4120.5586 | 4476.1137 | 4824.5406 | 5144.3591 | 5402.7451 | 5550.416
| FALSE | 3862 | 22008294 | SHN | SHN-SHTS NO.1 | 66 | SHTS NO.1 LINE | Y DIR OC & AUTO RECLOSE | Y | Schweitzer | SEL_351A | SEL 351 | SEL 300s | Digital |  | 0.016937 | 1 |  | 5.8543 | 0.012795 | 2.9686e-07 | 0.012794 | 67.1724 | 0.032654 | 67.2051 | 36.321 | 5.1192 | 0.0062955 |  | 13.88 | 0.12735 | 2.9547e-06 | 0.12735 | 668.5787 | 0.32501 | 668.9037 | 361.5089 | 50.952 | 0.06266 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.0025428 |  | 108.6516 | 1081.4272 | 43.8856 | 1037.5416 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 3.6874e-07 | 4.5965e-07 | 5.7486e-07 | 7.211e-07 | 9.0704e-07 | 1.1438e-06 | 1.4457e-06 | 1.8312e-06 | 2.324e-06 | 2.9547e-06 | 3.7625e-06 | 4.7983e-06 | 6.1275e-06 | 7.8346e-06 | 1.0029e-05 | 1.285e-05 | 1.6481e-05 | 2.1156e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 134.9608 | 168.2362 | 210.402 | 263.9275 | 331.9835 | 418.6452 | 529.1526 | 670.2484 | 850.613 | 1081.4272 | 1377.0997 | 1756.2063 | 2242.7052 | 2867.5077 | 3670.5095 | 4703.218 | 6032.1516 | 7743.236 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 |  | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 52.5283 | 69.6294 | 93.104 | 125.4725 | 170.2871 | 232.5627 | 319.3904 | 440.8119 | 611.065 | 850.3602 | 1187.4163 | 1663.079 | 2335.4895 |  | 83.4378 | 104.0099 | 130.0784 | 163.1698 | 205.2446 | 258.8221 | 327.1419 | 414.3726 | 525.8807 | 668.5787 | 851.3744 | 1085.7523 | 1386.5241 | 1772.8003 | 2269.2459 | 2907.7049 | 3729.3012 | 4787.1575 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 56.3061 | 76.8782 | 102.9467 | 136.0381 | 178.1129 | 231.6903 | 300.0102 | 387.2409 | 498.749 | 641.4469 | 824.2427 | 1058.6206 | 1359.3923 | 1745.6686 | 2242.1142 | 2880.5732 | 3702.1695 | 4754.6825 | 4901.2043 | 4886.6915 | 4866.6801 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.040561 | 0.050562 | 0.063234 | 0.079321 | 0.099774 | 0.12582 | 0.15903 | 0.20144 | 0.25564 | 0.32501 | 0.41387 | 0.52781 | 0.67402 | 0.8618 | 1.1031 | 1.4135 | 1.8129 | 2.3272 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015787 | 0.020926 | 0.027982 | 0.03771 | 0.051178 | 0.069894 | 0.09599 | 0.13248 | 0.18365 | 0.25557 | 0.35687 | 0.49982 | 0.70191 |  | 0.027372 | 0.037372 | 0.050045 | 0.066131 | 0.086585 | 0.11263 | 0.14584 | 0.18825 | 0.24245 | 0.31182 | 0.40068 | 0.51462 | 0.66083 | 0.84861 | 1.0899 | 1.4003 | 1.7997 | 2.3114 | 2.3826 | 2.3755 | 2.3658 | 2.3523 | 2.3336 | 2.3075 | 2.271 | 2.2199 | 2.148 | 2.0467 | 1.9037 | 1.7016 |  | 56.3335 | 76.9156 | 102.9967 | 136.1042 | 178.1994 | 231.803 | 300.156 | 387.4291 | 498.9914 | 641.7588 | 824.6434 | 1059.1352 | 1360.0532 | 1746.5172 | 2243.2042 | 2881.9735 | 3703.9692 | 4756.9939 | 4903.5869 | 4889.067 | 4869.0459 | 4841.3263 | 4802.8065 | 4749.1003 | 4673.9965 | 4568.6886 | 4420.6754 | 4212.1934 | 3917.978 | 3502.0667 |  | 45.1159 | 56.2395 | 70.335 | 88.228 | 110.9783 | 139.9483 | 176.8897 | 224.0565 | 284.3503 | 361.5089 | 460.3489 | 587.0799 | 749.711 | 958.5755 | 1227.0099 | 1572.2327 | 2016.4802 | 2588.4764 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 30.4454 | 41.569 | 55.6646 | 73.5575 | 96.3079 | 125.2779 | 162.2193 | 209.386 | 269.6798 | 346.8384 | 445.6784 | 572.4095 | 735.0406 | 943.905 | 1212.3394 | 1557.5622 | 2001.8097 | 2570.9167 | 2650.1429 | 2642.2957 | 2631.4752 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 6.3587 | 7.9265 | 9.9132 | 12.4351 | 15.6416 | 19.7247 | 24.9313 | 31.5791 | 40.077 | 50.952 | 64.8827 | 82.7445 | 105.6662 | 135.104 | 172.9379 | 221.5944 | 284.2078 | 364.8264 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 4.2911 | 5.8588 | 7.8455 | 10.3674 | 13.5739 | 17.657 | 22.8636 | 29.5114 | 38.0094 | 48.8843 | 62.815 | 80.6768 | 103.5985 | 133.0363 | 170.8702 | 219.5267 | 282.1401 | 362.3515 | 373.5178 | 372.4118 | 370.8867 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.0078199 | 0.009748 | 0.012191 | 0.015293 | 0.019236 | 0.024257 | 0.03066 | 0.038836 | 0.049286 | 0.06266 | 0.079792 | 0.10176 | 0.12995 | 0.16615 | 0.21268 | 0.27251 | 0.34952 | 0.44866 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 |  | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0030436 | 0.0040345 | 0.0053946 | 0.0072701 | 0.0098668 | 0.013475 | 0.018506 | 0.025542 | 0.035406 | 0.049272 | 0.068801 | 0.096362 | 0.13532 |  | 0.0052771 | 0.0072051 | 0.0096483 | 0.01275 | 0.016693 | 0.021714 | 0.028117 | 0.036293 | 0.046743 | 0.060117 | 0.077249 | 0.099215 | 0.1274 | 0.16361 | 0.21013 | 0.26997 | 0.34697 | 0.44562 | 0.45935 | 0.45799 | 0.45611 | 0.45352 | 0.44991 | 0.44488 | 0.43784 | 0.42798 | 0.41411 | 0.39458 | 0.36702 | 0.32806 |  | 91.0752 | 124.3506 | 166.5164 | 220.0418 | 288.0979 | 374.7595 | 485.267 | 626.3628 | 806.7274 | 1037.5416 | 1333.2141 | 1712.3207 | 2198.8196 | 2823.6221 | 3626.6239 | 4659.3324 | 5988.266 | 7690.7077 | 7927.707 | 7904.2325 | 7871.8639 | 7827.0493 | 7764.7738 | 7677.946 | 7556.5245 | 7386.2715 | 7146.9762 | 6809.9201 | 6334.2574 | 5661.8469
| FALSE | 3863 | 22002940 | SHN | SHN-SHTS NO.2 | 66 | SHTS NO.2 LINE | PILOT WIRE | X | English Electric | DSF7_1490 | DSF7 1490 | DSF7 | Electromechanical |  | 0.15703 | 2190 |  | 5.5 | 0.0019187 | 0.00067613 | 0.0012426 | 20.8568 | 297.4968 | 318.3535 | 9.2851 | 0.77445 | 14.3388 |  | 8.1226 | 0.0051892 | 0.0018286 | 0.0033606 | 56.4062 | 804.5673 | 860.9735 | 25.1112 | 2.0945 | 38.7787 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.023575 |  | 342.7519 | 926.958 | 71.521 | 855.437 |  | 0.03899 |  | 5.7187 | 5.9461 | 6.1825 | 6.4283 | 6.6839 | 6.9496 | 7.226 | 7.5133 | 7.812 | 8.1226 | 8.4456 | 8.7813 | 9.1305 | 9.4935 | 9.871 | 10.2635 | 10.6715 | 11.0958 | 11.537 | 11.9957 | 12.4727 | 12.9686 | 13.4842 | 14.0204 | 14.5778 | 15.1575 | 15.7601 | 16.3867 | 17.0383 | 17.7157 |  | 0.0021125 | 0.0023277 | 0.0025668 | 0.0028326 | 0.0031282 | 0.003457 | 0.0038229 | 0.0042302 | 0.0046838 | 0.0051892 | 0.0057523 | 0.0063801 | 0.0070802 | 0.0078611 | 0.0087324 | 0.0097047 | 0.01079 | 0.012002 | 0.013356 | 0.014869 | 0.016559 | 0.018448 | 0.02056 | 0.022922 | 0.025563 | 0.028518 | 0.031823 | 0.035522 | 0.039662 | 0.044296 |  | 0.00074441 | 0.00082025 | 0.00090451 | 0.00099816 | 0.0011023 | 0.0012182 | 0.0013471 | 0.0014906 | 0.0016505 | 0.0018286 | 0.002027 | 0.0022482 | 0.0024949 | 0.0027701 | 0.0030771 | 0.0034198 | 0.0038023 | 0.0042294 | 0.0047065 | 0.0052395 | 0.0058351 | 0.0065009 | 0.0072451 | 0.0080773 | 0.0090079 | 0.010049 | 0.011214 | 0.012517 | 0.013976 | 0.015609 | 377.3668 | 415.8102 | 458.5239 | 506.0022 | 558.7979 | 617.5296 | 682.8894 | 755.652 | 836.6846 | 926.958 | 1027.5591 | 1139.7054 | 1264.7603 | 1404.2511 | 1559.8888 | 1733.5907 | 1927.5051 | 2144.0397 | 2385.8933 | 2656.091 | 2958.0241 | 3295.4952 | 3672.7679 | 4094.6235 | 4566.4242 | 5094.1843 | 5684.6499 | 6345.3887 | 7084.8907 | 7912.6811 |  | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 44.3952 | 53.1382 | 70.4379 | 94.185 | 126.9293 | 172.2643 | 235.263 | 323.0988 | 445.9302 | 618.16 | 860.2337 | 1201.2033 | 1682.3889 | 2362.6067 |  | 22.9631 | 25.3024 | 27.9016 | 30.7907 | 34.0034 | 37.5772 | 41.5544 | 45.9821 | 50.913 | 56.4062 | 62.5279 | 69.3521 | 76.9618 | 85.45 | 94.9207 | 105.4906 | 117.2904 | 130.4668 | 145.1838 | 161.6255 | 179.9985 | 200.5339 | 223.4913 | 249.1616 | 277.8711 | 309.9857 | 345.9161 | 386.1227 | 431.122 | 481.4938 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | -4.1691 | -1.8298 | 0.76935 | 3.6584 | 6.8711 | 10.445 | 14.4222 | 18.8499 | 23.7808 | 29.274 | 35.3957 | 42.2199 | 49.8296 | 58.3177 | 67.7884 | 78.3583 | 90.1582 | 97.9912 | 102.1354 | 104.0641 | 102.4252 | 95.254 | 79.7096 | 51.6987 | 5.3395 | -67.8047 | -179.8184 | -347.9965 | -597.0752 | -962.4207 |  | 327.5413 | 360.9088 | 397.9828 | 439.1923 | 485.0172 | 535.9942 | 592.7243 | 655.8797 | 726.2132 | 804.5673 | 891.8856 | 989.2247 | 1097.768 | 1218.8411 | 1353.9293 | 1504.6965 | 1673.0074 | 1860.952 | 2070.8725 | 2305.3947 | 2567.4622 | 2860.3754 | 3187.835 | 3553.991 | 3963.4976 | 4421.575 | 4934.0786 | 5507.5769 | 6149.439 | 6867.9323 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 327.0522 | 360.4197 | 397.4937 | 438.7032 | 484.5281 | 535.5051 | 592.2352 | 655.3906 | 725.7241 | 804.0782 | 891.3965 | 988.7356 | 1097.2789 | 1218.352 | 1353.4402 | 1504.2074 | 1672.5183 | 1860.3665 | 2070.0964 | 2304.357 | 2566.0637 | 2858.4774 | 3185.2429 | 3550.4312 | 3958.5845 | 4414.7643 | 4924.6009 | 5494.3425 | 6130.903 | 6841.902 |  | 322.883 | 358.5899 | 398.2631 | 442.3617 | 491.3992 | 545.9501 | 606.6574 | 674.2405 | 749.5048 | 833.3522 | 926.7921 | 1030.9554 | 1147.1084 | 1276.6697 | 1421.2286 | 1582.5657 | 1762.6765 | 1958.3577 | 2172.2319 | 2408.4211 | 2668.4889 | 2953.7315 | 3264.9525 | 3602.1299 | 3963.9239 | 4346.9597 | 4744.7825 | 5146.346 | 5533.8278 | 5879.4814 |  | 10.2228 | 11.2643 | 12.4214 | 13.7076 | 15.1378 | 16.7288 | 18.4994 | 20.4706 | 22.6657 | 25.1112 | 27.8365 | 30.8745 | 34.2623 | 38.0411 | 42.2573 | 46.9628 | 52.216 | 58.0819 | 64.6337 | 71.9533 | 80.1327 | 89.2747 | 99.495 | 110.923 | 123.7041 | 138.0011 | 153.9967 | 171.8961 | 191.9292 | 214.3539 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | -4.4533 | -3.4118 | -2.2547 | -0.96854 | 0.4617 | 2.0527 | 3.8233 | 5.7945 | 7.9896 | 10.4351 | 13.1604 | 16.1984 | 19.5862 | 23.365 | 27.5812 | 32.2867 | 37.5399 | 40.5155 | 41.3484 | 40.8178 | 38.1725 | 32.3278 | 21.7221 | 4.1135 | -23.7109 | -66.3494 | -130.3782 | -225.1961 | -364.2327 | -566.6735 |  | 0.85266 | 0.93953 | 1.036 | 1.1433 | 1.2626 | 1.3953 | 1.543 | 1.7074 | 1.8905 | 2.0945 | 2.3218 | 2.5752 | 2.8577 | 3.1729 | 3.5246 | 3.9171 | 4.3552 | 4.8445 | 5.391 | 6.0015 | 6.6837 | 7.4462 | 8.2987 | 9.2518 | 10.3179 | 11.5104 | 12.8445 | 14.3375 | 16.0084 | 17.8788 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | -1.215 | -1.1282 | -1.0317 | -0.92439 | -0.80509 | -0.67239 | -0.52471 | -0.3603 | -0.1772 | 0.026769 | 0.25408 | 0.50747 | 0.79004 | 1.1052 | 1.4569 | 1.8494 | 2.2875 | 2.3696 | 2.1103 | 1.6148 | 0.77196 | -0.57699 | -2.6587 | -5.7965 | -10.4513 | -17.2804 | -27.2208 | -41.6085 | -62.3488 | -92.1595 |  | 15.7869 | 17.3952 | 19.1821 | 21.1683 | 23.377 | 25.834 | 28.5683 | 31.6122 | 35.0022 | 38.7787 | 42.9873 | 47.6789 | 52.9105 | 58.746 | 65.257 | 72.5237 | 80.636 | 89.6946 | 99.8124 | 111.116 | 123.7472 | 137.8651 | 153.648 | 171.2961 | 191.0336 | 213.1121 | 237.8139 | 265.4555 | 296.3921 | 331.0223 |  | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.023575 | 0.028218 | 0.037405 | 0.050015 | 0.067403 | 0.091478 | 0.12493 | 0.17158 | 0.2368 | 0.32826 | 0.45681 | 0.63788 | 0.8934 | 1.2546 |  | 15.7633 | 17.3716 | 19.1585 | 21.1447 | 23.3534 | 25.8104 | 28.5447 | 31.5887 | 34.9786 | 38.7552 | 42.9637 | 47.6553 | 52.8869 | 58.7224 | 65.2334 | 72.5001 | 80.6124 | 89.6664 | 99.775 | 111.066 | 123.6798 | 137.7736 | 153.5231 | 171.1245 | 190.7968 | 212.7839 | 237.3571 | 264.8176 | 295.4987 | 329.7676 |  | 332.9781 | 371.4215 | 414.1352 | 461.6135 | 514.4092 | 573.1408 | 638.5007 | 711.2633 | 792.2959 | 882.5692 | 983.1704 | 1095.3167 | 1220.3715 | 1359.8623 | 1515.5001 | 1689.2019 | 1883.1163 | 2090.9092 | 2315.4656 | 2561.9196 | 2831.1132 | 3123.2559 | 3437.539 | 3771.5714 | 4120.5586 | 4476.1137 | 4824.5406 | 5144.3591 | 5402.7451 | 5550.416
| FALSE | 3864 | 22008295 | SHN | SHN-SHTS NO.2 | 66 | SHTS NO.2 LINE | Y DIR OC & AUTO RECLOSE | Y | Schweitzer | SEL_351A | SEL 351 | SEL 300s | Digital |  | 0.016937 | 1 |  | 5.8543 | 0.012795 | 2.9686e-07 | 0.012794 | 67.1724 | 0.032654 | 67.2051 | 36.321 | 5.1192 | 0.0062955 |  | 13.88 | 0.12735 | 2.9547e-06 | 0.12735 | 668.5787 | 0.32501 | 668.9037 | 361.5089 | 50.952 | 0.06266 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.0025428 |  | 108.6516 | 1081.4272 | 43.8856 | 1037.5416 |  | 0.086327 |  | 6.3821 | 6.9576 | 7.5849 | 8.2687 | 9.0143 | 9.827 | 10.7131 | 11.679 | 12.732 | 13.88 | 15.1314 | 16.4957 | 17.983 | 19.6044 | 21.372 | 23.299 | 25.3997 | 27.6898 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.015893 | 0.019811 | 0.024777 | 0.03108 | 0.039094 | 0.049299 | 0.062313 | 0.078928 | 0.10017 | 0.12735 | 0.16217 | 0.20681 | 0.2641 | 0.33768 | 0.43224 | 0.55385 | 0.71034 | 0.91184 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 3.6874e-07 | 4.5965e-07 | 5.7486e-07 | 7.211e-07 | 9.0704e-07 | 1.1438e-06 | 1.4457e-06 | 1.8312e-06 | 2.324e-06 | 2.9547e-06 | 3.7625e-06 | 4.7983e-06 | 6.1275e-06 | 7.8346e-06 | 1.0029e-05 | 1.285e-05 | 1.6481e-05 | 2.1156e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 134.9608 | 168.2362 | 210.402 | 263.9275 | 331.9835 | 418.6452 | 529.1526 | 670.2484 | 850.613 | 1081.4272 | 1377.0997 | 1756.2063 | 2242.7052 | 2867.5077 | 3670.5095 | 4703.218 | 6032.1516 | 7743.236 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 | 7997.3364 |  | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 43.8856 | 52.5283 | 69.6294 | 93.104 | 125.4725 | 170.2871 | 232.5627 | 319.3904 | 440.8119 | 611.065 | 850.3602 | 1187.4163 | 1663.079 | 2335.4895 |  | 83.4378 | 104.0099 | 130.0784 | 163.1698 | 205.2446 | 258.8221 | 327.1419 | 414.3726 | 525.8807 | 668.5787 | 851.3744 | 1085.7523 | 1386.5241 | 1772.8003 | 2269.2459 | 2907.7049 | 3729.3012 | 4787.1575 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 56.3061 | 76.8782 | 102.9467 | 136.0381 | 178.1129 | 231.6903 | 300.0102 | 387.2409 | 498.749 | 641.4469 | 824.2427 | 1058.6206 | 1359.3923 | 1745.6686 | 2242.1142 | 2880.5732 | 3702.1695 | 4754.6825 | 4901.2043 | 4886.6915 | 4866.6801 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.040561 | 0.050562 | 0.063234 | 0.079321 | 0.099774 | 0.12582 | 0.15903 | 0.20144 | 0.25564 | 0.32501 | 0.41387 | 0.52781 | 0.67402 | 0.8618 | 1.1031 | 1.4135 | 1.8129 | 2.3272 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015787 | 0.020926 | 0.027982 | 0.03771 | 0.051178 | 0.069894 | 0.09599 | 0.13248 | 0.18365 | 0.25557 | 0.35687 | 0.49982 | 0.70191 |  | 0.027372 | 0.037372 | 0.050045 | 0.066131 | 0.086585 | 0.11263 | 0.14584 | 0.18825 | 0.24245 | 0.31182 | 0.40068 | 0.51462 | 0.66083 | 0.84861 | 1.0899 | 1.4003 | 1.7997 | 2.3114 | 2.3826 | 2.3755 | 2.3658 | 2.3523 | 2.3336 | 2.3075 | 2.271 | 2.2199 | 2.148 | 2.0467 | 1.9037 | 1.7016 |  | 56.3335 | 76.9156 | 102.9967 | 136.1042 | 178.1994 | 231.803 | 300.156 | 387.4291 | 498.9914 | 641.7588 | 824.6434 | 1059.1352 | 1360.0532 | 1746.5172 | 2243.2042 | 2881.9735 | 3703.9692 | 4756.9939 | 4903.5869 | 4889.067 | 4869.0459 | 4841.3263 | 4802.8065 | 4749.1003 | 4673.9965 | 4568.6886 | 4420.6754 | 4212.1934 | 3917.978 | 3502.0667 |  | 45.1159 | 56.2395 | 70.335 | 88.228 | 110.9783 | 139.9483 | 176.8897 | 224.0565 | 284.3503 | 361.5089 | 460.3489 | 587.0799 | 749.711 | 958.5755 | 1227.0099 | 1572.2327 | 2016.4802 | 2588.4764 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 30.4454 | 41.569 | 55.6646 | 73.5575 | 96.3079 | 125.2779 | 162.2193 | 209.386 | 269.6798 | 346.8384 | 445.6784 | 572.4095 | 735.0406 | 943.905 | 1212.3394 | 1557.5622 | 2001.8097 | 2570.9167 | 2650.1429 | 2642.2957 | 2631.4752 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 6.3587 | 7.9265 | 9.9132 | 12.4351 | 15.6416 | 19.7247 | 24.9313 | 31.5791 | 40.077 | 50.952 | 64.8827 | 82.7445 | 105.6662 | 135.104 | 172.9379 | 221.5944 | 284.2078 | 364.8264 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 4.2911 | 5.8588 | 7.8455 | 10.3674 | 13.5739 | 17.657 | 22.8636 | 29.5114 | 38.0094 | 48.8843 | 62.815 | 80.6768 | 103.5985 | 133.0363 | 170.8702 | 219.5267 | 282.1401 | 362.3515 | 373.5178 | 372.4118 | 370.8867 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.0078199 | 0.009748 | 0.012191 | 0.015293 | 0.019236 | 0.024257 | 0.03066 | 0.038836 | 0.049286 | 0.06266 | 0.079792 | 0.10176 | 0.12995 | 0.16615 | 0.21268 | 0.27251 | 0.34952 | 0.44866 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 | 0.46338 |  | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0025428 | 0.0030436 | 0.0040345 | 0.0053946 | 0.0072701 | 0.0098668 | 0.013475 | 0.018506 | 0.025542 | 0.035406 | 0.049272 | 0.068801 | 0.096362 | 0.13532 |  | 0.0052771 | 0.0072051 | 0.0096483 | 0.01275 | 0.016693 | 0.021714 | 0.028117 | 0.036293 | 0.046743 | 0.060117 | 0.077249 | 0.099215 | 0.1274 | 0.16361 | 0.21013 | 0.26997 | 0.34697 | 0.44562 | 0.45935 | 0.45799 | 0.45611 | 0.45352 | 0.44991 | 0.44488 | 0.43784 | 0.42798 | 0.41411 | 0.39458 | 0.36702 | 0.32806 |  | 91.0752 | 124.3506 | 166.5164 | 220.0418 | 288.0979 | 374.7595 | 485.267 | 626.3628 | 806.7274 | 1037.5416 | 1333.2141 | 1712.3207 | 2198.8196 | 2823.6221 | 3626.6239 | 4659.3324 | 5988.266 | 7690.7077 | 7927.707 | 7904.2325 | 7871.8639 | 7827.0493 | 7764.7738 | 7677.946 | 7556.5245 | 7386.2715 | 7146.9762 | 6809.9201 | 6334.2574 | 5661.8469
| FALSE | 3865 | 22002944 | SHN | Blank | 66 | TRANS NO.1 | NEUTRAL DISPLACEMENT | X | ASEA | GROUP_2605 | GROUP 2605 | GROUP 2000s | Electronic |  | 0.066046 | 2190 |  | 8.25 | 0.026286 | 0.0045837 | 0.021702 | 280.8119 | 2016.8282 | 2297.64 | 100.6375 | 10.5627 | 97.2076 |  | 13.0142 | 0.090569 | 0.015794 | 0.074776 | 967.5611 | 6949.1524 | 7916.7135 | 346.7551 | 36.3947 | 334.9369 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.0099158 |  | 2506.0478 | 8634.8002 | 71.2196 | 8563.5806 |  | 0.045583 |  | 8.6348 | 9.0375 | 9.459 | 9.9001 | 10.3618 | 10.8451 | 11.3509 | 11.8803 | 12.4343 | 13.0142 | 13.6212 | 14.2565 | 14.9214 | 15.6173 | 16.3456 | 17.1079 | 17.9058 | 18.7409 | 19.6149 | 20.5298 | 21.4872 | 22.4893 | 23.5382 | 24.636 | 25.7849 | 26.9875 | 28 | 28 | 28 | 28 |  | 0.02966 | 0.033492 | 0.037845 | 0.042793 | 0.048419 | 0.054819 | 0.0621 | 0.070387 | 0.079823 | 0.090569 | 0.10281 | 0.11676 | 0.13267 | 0.1508 | 0.17148 | 0.19506 | 0.22198 | 0.25269 | 0.28775 | 0.32777 | 0.37347 | 0.42567 | 0.48529 | 0.55341 | 0.63124 | 0.7202 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0051721 | 0.0058403 | 0.0065995 | 0.0074623 | 0.0084434 | 0.0095593 | 0.010829 | 0.012274 | 0.01392 | 0.015794 | 0.017928 | 0.020361 | 0.023134 | 0.026296 | 0.029902 | 0.034015 | 0.038708 | 0.044064 | 0.050177 | 0.057157 | 0.065126 | 0.074228 | 0.084625 | 0.096504 | 0.11008 | 0.12559 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 2827.7357 | 3193.0651 | 3608.1274 | 4079.8788 | 4616.2649 | 5226.3624 | 5920.5424 | 6710.6558 | 7610.2476 | 8634.8002 | 9802.0132 | 11132.1236 | 12648.2721 | 14376.9233 | 16348.3456 | 18597.1626 | 21162.9829 | 24091.1231 | 27433.4344 | 31249.2507 | 35606.474 | 40582.8179 | 46267.2327 | 52761.5375 | 60182.2901 | 68662.9301 | 76393.1401 | 76393.1401 | 76393.1401 | 76393.1401 |  | 44.0904 | 44.0904 | 44.0904 | 44.0904 | 44.0904 | 44.0904 | 44.0904 | 44.0904 | 44.0904 | 44.0904 | 44.0904 | 44.0904 | 44.0904 | 44.0904 | 44.0904 | 44.0904 | 44.0904 | 52.7734 | 69.9543 | 93.5384 | 126.058 | 171.0817 | 233.6478 | 320.8807 | 442.8688 | 613.9162 | 854.328 | 1192.9569 | 1670.839 | 2346.3871 |  | 316.8582 | 357.7947 | 404.3039 | 457.1654 | 517.2694 | 585.6331 | 663.4185 | 751.9536 | 852.7562 | 967.5611 | 1098.3516 | 1247.3954 | 1417.2854 | 1610.9871 | 1831.8922 | 2083.8804 | 2371.39 | 2699.4989 | 3074.0171 | 3501.5934 | 3989.8362 | 4547.4539 | 5184.4134 | 5912.1241 | 6743.6467 | 7693.9336 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 289.7263 | 330.6628 | 377.172 | 430.0335 | 490.1375 | 558.5012 | 636.2866 | 724.8217 | 825.6243 | 940.4292 | 1071.2197 | 1220.2634 | 1390.1535 | 1583.8552 | 1804.7603 | 2056.7485 | 2344.2581 | 2667.0237 | 3030.9693 | 3444.0326 | 3912.2639 | 4442.1753 | 5040.6335 | 5714.6637 | 6471.1185 | 7316.1479 | 8034.4041 | 7826.022 | 7531.9476 | 7116.2356 |  | 2275.7176 | 2569.729 | 2903.7646 | 3283.4228 | 3715.0979 | 4206.0949 | 4764.7601 | 5400.6311 | 6124.6085 | 6949.1524 | 7888.5072 | 8958.9593 | 10179.132 | 11570.3234 | 13156.8933 | 14966.7061 | 17031.6383 | 19388.1598 | 22077.9998 | 25148.9092 | 28655.5344 | 32660.4183 | 37235.1466 | 42461.6617 | 48433.7676 | 55258.8543 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 2275.5118 | 2569.5233 | 2903.5589 | 3283.2171 | 3714.8922 | 4205.8892 | 4764.5543 | 5400.4253 | 6124.4028 | 6948.9467 | 7888.3015 | 8958.7535 | 10178.9262 | 11570.1177 | 13156.6876 | 14966.5004 | 17031.4326 | 19387.9136 | 22077.6734 | 25148.4727 | 28654.9462 | 32659.62 | 37234.0564 | 42460.1645 | 48431.7012 | 55255.9897 | 61476.0203 | 61474.4402 | 61472.2104 | 61469.0582 |  | 2565.2381 | 2900.186 | 3280.7309 | 3713.2506 | 4205.0297 | 4764.3904 | 5400.8409 | 6125.2471 | 6950.0271 | 7889.3759 | 8959.5212 | 10179.017 | 11569.0797 | 13153.9729 | 14961.4479 | 17023.2489 | 19375.6907 | 22054.9372 | 25108.6427 | 28592.5053 | 32567.2101 | 37101.7953 | 42274.6899 | 48174.8282 | 54902.8197 | 62572.1376 | 69510.4244 | 69300.4622 | 69004.158 | 68585.2938 |  | 113.5558 | 128.2266 | 144.8947 | 163.8392 | 185.3793 | 209.8795 | 237.7563 | 269.4855 | 305.6112 | 346.7551 | 393.6278 | 447.0422 | 507.9275 | 577.3464 | 656.5145 | 746.8222 | 849.86 | 967.4478 | 1101.6679 | 1254.9029 | 1429.8796 | 1629.7189 | 1857.9928 | 2118.7902 | 2416.7917 | 2757.356 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 98.8834 | 113.5542 | 130.2222 | 149.1667 | 170.7069 | 195.2071 | 223.0838 | 254.8131 | 290.9388 | 332.0826 | 378.9554 | 432.3698 | 493.255 | 562.674 | 641.8421 | 732.1497 | 835.1876 | 949.8858 | 1078.3884 | 1223.7751 | 1387.9299 | 1572.7862 | 1780.2393 | 2012.0072 | 2269.4134 | 2553.0564 | 2783.4806 | 2670.7914 | 2511.7613 | 2286.9518 |  | 11.9186 | 13.4584 | 15.2079 | 17.1962 | 19.457 | 22.0285 | 24.9544 | 28.2847 | 32.0763 | 36.3947 | 41.3144 | 46.9207 | 53.3111 | 60.5971 | 68.9065 | 78.385 | 89.1996 | 101.5414 | 115.6289 | 131.7121 | 150.0773 | 171.0521 | 195.0112 | 222.384 | 253.6617 | 289.4066 | 321.9886 | 321.9886 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 9.8509 | 11.3907 | 13.1402 | 15.1285 | 17.3893 | 19.9608 | 22.8867 | 26.217 | 30.0087 | 34.327 | 39.2467 | 44.853 | 51.2434 | 58.5294 | 66.8388 | 76.3173 | 87.1319 | 99.0665 | 112.3482 | 127.3255 | 144.1656 | 163.0289 | 184.0539 | 207.3357 | 232.8925 | 260.6159 | 281.9234 | 266.0428 | 243.6317 | 211.9507 |  | 109.6856 | 123.8564 | 139.9563 | 158.2552 | 179.0612 | 202.7264 | 229.6531 | 260.3009 | 295.1954 | 334.9369 | 380.2122 | 431.8061 | 490.6163 | 557.6692 | 634.1391 | 721.3689 | 820.895 | 934.4752 | 1064.1208 | 1212.1332 | 1381.1464 | 1574.1747 | 1794.6686 | 2046.5774 | 2334.4224 | 2663.3796 | 2963.2282 | 2963.2282 | 2963.2282 | 2963.2282 |  | 0.0099158 | 0.0099158 | 0.0099158 | 0.0099158 | 0.0099158 | 0.0099158 | 0.0099158 | 0.0099158 | 0.0099158 | 0.0099158 | 0.0099158 | 0.0099158 | 0.0099158 | 0.0099158 | 0.0099158 | 0.0099158 | 0.0099158 | 0.011869 | 0.015733 | 0.021036 | 0.02835 | 0.038476 | 0.052547 | 0.072165 | 0.0996 | 0.13807 | 0.19214 | 0.26829 | 0.37577 | 0.5277 |  | 109.6757 | 123.8465 | 139.9464 | 158.2453 | 179.0513 | 202.7165 | 229.6431 | 260.291 | 295.1854 | 334.927 | 380.2023 | 431.7962 | 490.6063 | 557.6593 | 634.1292 | 721.359 | 820.8851 | 934.4633 | 1064.105 | 1212.1122 | 1381.118 | 1574.1363 | 1794.6161 | 2046.5053 | 2334.3228 | 2663.2416 | 2963.0361 | 2962.9599 | 2962.8525 | 2962.7005 |  | 2783.648 | 3148.9775 | 3564.0397 | 4035.7912 | 4572.1772 | 5182.2748 | 5876.4547 | 6666.5681 | 7566.1599 | 8590.7125 | 9757.9255 | 11088.0359 | 12604.1845 | 14332.8356 | 16304.2579 | 18553.0749 | 21118.8952 | 24038.3529 | 27363.4844 | 31155.7181 | 35480.4237 | 40411.7467 | 46033.5992 | 52440.6764 | 59739.4485 | 68049.0515 | 75538.8644 | 75200.2563 | 74722.4034 | 74046.8968
| TRUE | 4360 | 22004360 | TYA | Blank | 66 | CB A | CB FAIL | X | EMAIL | GROUP_3183 | GROUP 3183 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 449.3168 | 0 | 449.3168 | 121.4703 | 17.1211 | 0 |  | 17.778 | 0.21751 | 0 | 0.21751 | 2283.8323 | 0 | 2283.8323 | 617.4212 | 87.0249 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 587.9082 | 2988.2784 | 71.0008 | 2917.2776 |  | 0.058543 |  | 10.4969 | 11.1297 | 11.8008 | 12.5122 | 13.2666 | 14.0664 | 14.9145 | 15.8137 | 16.7671 | 17.778 | 18.8499 | 19.9863 | 21.1913 | 22.4689 | 23.8236 | 25.2599 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.050154 | 0.058841 | 0.069098 | 0.081214 | 0.095533 | 0.11247 | 0.1325 | 0.1562 | 0.18427 | 0.21751 | 0.25689 | 0.30357 | 0.35892 | 0.42456 | 0.50243 | 0.59483 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 689.0539 | 808.4047 | 949.3165 | 1115.7731 | 1312.5044 | 1545.1277 | 1820.3153 | 2145.9941 | 2531.5835 | 2988.2784 | 3529.3857 | 4170.7255 | 4931.1083 | 5832.9039 | 6902.7174 | 8172.1962 | 9678.9889 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 526.6188 | 617.8342 | 725.528 | 852.7447 | 1003.0993 | 1180.8848 | 1391.2006 | 1640.1051 | 1934.797 | 2283.8323 | 2697.3809 | 3187.5335 | 3768.6664 | 4457.8759 | 5275.4954 | 6245.7117 | 7397.2985 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 499.4871 | 590.7026 | 698.3963 | 825.613 | 975.9676 | 1153.7532 | 1364.069 | 1612.9734 | 1907.6654 | 2256.7006 | 2670.2492 | 3160.4018 | 3741.5347 | 4430.7442 | 5248.3637 | 6218.5801 | 7370.1668 | 8380.9435 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 499.4871 | 590.7026 | 698.3963 | 825.613 | 975.9676 | 1153.7532 | 1364.069 | 1612.9734 | 1907.6654 | 2256.7006 | 2670.2492 | 3160.4018 | 3741.5347 | 4430.7442 | 5248.3637 | 6218.5801 | 7370.1668 | 8380.9435 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 142.3684 | 167.028 | 196.1424 | 230.5347 | 271.1823 | 319.2456 | 376.1033 | 443.3932 | 523.0615 | 617.4212 | 729.2218 | 861.7318 | 1018.8378 | 1205.1617 | 1426.2005 | 1688.4931 | 1999.8181 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 127.6987 | 152.3582 | 181.4726 | 215.865 | 256.5125 | 304.5758 | 361.4335 | 428.7234 | 508.3917 | 602.7514 | 714.552 | 847.062 | 1004.168 | 1190.4919 | 1411.5308 | 1673.8233 | 1985.1483 | 2256.9616 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 20.0667 | 23.5424 | 27.6461 | 32.4936 | 38.2229 | 44.9973 | 53.0114 | 62.4958 | 73.725 | 87.0249 | 102.7831 | 121.4602 | 143.6041 | 169.8663 | 201.0215 | 237.9914 | 281.8723 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 17.999 | 21.4747 | 25.5784 | 30.4259 | 36.1552 | 42.9296 | 50.9437 | 60.4281 | 71.6573 | 84.9572 | 100.7154 | 119.3925 | 141.5364 | 167.7986 | 198.9538 | 235.9237 | 279.8046 | 318.1164 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 645.1848 | 764.5355 | 905.4473 | 1071.9039 | 1268.6353 | 1501.2586 | 1776.4462 | 2102.1249 | 2487.7144 | 2944.4093 | 3485.5166 | 4126.8563 | 4887.2392 | 5789.0347 | 6858.8483 | 8128.327 | 9635.1197 | 10956.0215 | 10938.9268 | 10915.4611 | 10883.1047 | 10838.3069 | 10776.0547 | 10689.2596 | 10567.8837 | 10397.6946 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| TRUE | 4361 | 22004361 | TYA | Blank | 66 | CB B | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 275.999 | 0 | 275.999 | 74.6148 | 10.5169 | 0 |  | 14.2947 | 0.11764 | 0 | 0.11764 | 1235.2445 | 0 | 1235.2445 | 333.9414 | 47.0687 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 361.1306 | 1616.2545 | 71.0008 | 1545.2537 |  | 0.054968 |  | 8.7162 | 9.2087 | 9.7291 | 10.2788 | 10.8596 | 11.4733 | 12.1216 | 12.8065 | 13.5302 | 14.2947 | 15.1025 | 15.9559 | 16.8575 | 17.8101 | 18.8164 | 19.8797 | 21.003 | 22.1898 | 23.4437 | 24.7684 | 26.168 | 27.6467 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.030409 | 0.035217 | 0.040826 | 0.047373 | 0.05502 | 0.063954 | 0.074399 | 0.086616 | 0.10091 | 0.11764 | 0.13724 | 0.16019 | 0.18709 | 0.21862 | 0.2556 | 0.29897 | 0.34986 | 0.40959 | 0.47971 | 0.56204 | 0.65873 | 0.77233 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417.7845 | 483.8387 | 560.8985 | 650.848 | 755.8993 | 878.6501 | 1022.1517 | 1189.9885 | 1386.3727 | 1616.2545 | 1885.453 | 2200.8092 | 2570.3674 | 3003.5881 | 3511.5987 | 4107.4891 | 4806.66 | 5627.2328 | 6590.533 | 7721.659 | 9050.1535 | 10610.7932 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 319.2975 | 369.7803 | 428.6743 | 497.4194 | 577.7063 | 671.5203 | 781.1933 | 909.4649 | 1059.5541 | 1235.2445 | 1440.983 | 1681.9983 | 1964.4382 | 2295.533 | 2683.7869 | 3139.2043 | 3673.5551 | 4300.689 | 5036.9042 | 5901.3826 | 6916.7026 | 8109.4426 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 292.1658 | 342.6487 | 401.5426 | 470.2877 | 550.5746 | 644.3886 | 754.0616 | 882.3332 | 1032.4225 | 1208.1128 | 1413.8513 | 1654.8666 | 1937.3065 | 2268.4013 | 2656.6553 | 3112.0726 | 3646.4234 | 4268.2141 | 4993.8568 | 5843.8224 | 6839.131 | 8004.165 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 292.1658 | 342.6487 | 401.5426 | 470.2877 | 550.5746 | 644.3886 | 754.0616 | 882.3332 | 1032.4225 | 1208.1128 | 1413.8513 | 1654.8666 | 1937.3065 | 2268.4013 | 2656.6553 | 3112.0726 | 3646.4234 | 4268.2141 | 4993.8568 | 5843.8224 | 6839.131 | 8004.165 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 86.3203 | 99.968 | 115.8897 | 134.4745 | 156.1796 | 181.5417 | 211.1912 | 245.8687 | 286.4445 | 333.9414 | 389.5617 | 454.7188 | 531.0748 | 620.5844 | 725.5467 | 848.6662 | 993.125 | 1162.6671 | 1361.6988 | 1595.4056 | 1869.8917 | 2192.3423 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 71.6505 | 85.2982 | 101.2199 | 119.8048 | 141.5099 | 166.8719 | 196.5214 | 231.1989 | 271.7747 | 319.2716 | 374.8919 | 440.049 | 516.405 | 605.9147 | 710.8769 | 833.9965 | 978.4552 | 1145.1083 | 1338.4235 | 1564.2835 | 1827.9496 | 2135.4198 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 12.1668 | 14.0904 | 16.3345 | 18.954 | 22.0134 | 25.5881 | 29.7672 | 34.6549 | 40.3741 | 47.0687 | 54.9083 | 64.0921 | 74.8544 | 87.4707 | 102.2651 | 119.6186 | 139.9799 | 163.8767 | 191.93 | 224.8708 | 263.5593 | 309.0084 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 10.0991 | 12.0227 | 14.2668 | 16.8864 | 19.9457 | 23.5204 | 27.6995 | 32.5873 | 38.3064 | 45.001 | 52.8406 | 62.0245 | 72.7868 | 85.403 | 100.1974 | 117.5509 | 137.9123 | 161.4018 | 188.6494 | 220.4841 | 257.6476 | 300.9852 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 373.9154 | 439.9696 | 517.0294 | 606.9788 | 712.0302 | 834.781 | 978.2825 | 1146.1194 | 1342.5036 | 1572.3854 | 1841.5838 | 2156.94 | 2526.4983 | 2959.719 | 3467.7296 | 4063.62 | 4762.7909 | 5574.7242 | 6520.9297 | 7628.59 | 8924.7282 | 10440.57 | 10776.0547 | 10689.2596 | 10567.8837 | 10397.6946 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| TRUE | 4362 | 22004362 | TYA | Blank | 66 | CB C | CB FAIL | X | ASEA | GROUP_2753 | GROUP 2753 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 275.999 | 0 | 275.999 | 74.6148 | 10.5169 | 0 |  | 14.2947 | 0.11764 | 0 | 0.11764 | 1235.2445 | 0 | 1235.2445 | 333.9414 | 47.0687 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 361.1306 | 1616.2545 | 71.0008 | 1545.2537 |  | 0.054968 |  | 8.7162 | 9.2087 | 9.7291 | 10.2788 | 10.8596 | 11.4733 | 12.1216 | 12.8065 | 13.5302 | 14.2947 | 15.1025 | 15.9559 | 16.8575 | 17.8101 | 18.8164 | 19.8797 | 21.003 | 22.1898 | 23.4437 | 24.7684 | 26.168 | 27.6467 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.030409 | 0.035217 | 0.040826 | 0.047373 | 0.05502 | 0.063954 | 0.074399 | 0.086616 | 0.10091 | 0.11764 | 0.13724 | 0.16019 | 0.18709 | 0.21862 | 0.2556 | 0.29897 | 0.34986 | 0.40959 | 0.47971 | 0.56204 | 0.65873 | 0.77233 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417.7845 | 483.8387 | 560.8985 | 650.848 | 755.8993 | 878.6501 | 1022.1517 | 1189.9885 | 1386.3727 | 1616.2545 | 1885.453 | 2200.8092 | 2570.3674 | 3003.5881 | 3511.5987 | 4107.4891 | 4806.66 | 5627.2328 | 6590.533 | 7721.659 | 9050.1535 | 10610.7932 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 319.2975 | 369.7803 | 428.6743 | 497.4194 | 577.7063 | 671.5203 | 781.1933 | 909.4649 | 1059.5541 | 1235.2445 | 1440.983 | 1681.9983 | 1964.4382 | 2295.533 | 2683.7869 | 3139.2043 | 3673.5551 | 4300.689 | 5036.9042 | 5901.3826 | 6916.7026 | 8109.4426 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 292.1658 | 342.6487 | 401.5426 | 470.2877 | 550.5746 | 644.3886 | 754.0616 | 882.3332 | 1032.4225 | 1208.1128 | 1413.8513 | 1654.8666 | 1937.3065 | 2268.4013 | 2656.6553 | 3112.0726 | 3646.4234 | 4268.2141 | 4993.8568 | 5843.8224 | 6839.131 | 8004.165 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 292.1658 | 342.6487 | 401.5426 | 470.2877 | 550.5746 | 644.3886 | 754.0616 | 882.3332 | 1032.4225 | 1208.1128 | 1413.8513 | 1654.8666 | 1937.3065 | 2268.4013 | 2656.6553 | 3112.0726 | 3646.4234 | 4268.2141 | 4993.8568 | 5843.8224 | 6839.131 | 8004.165 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 86.3203 | 99.968 | 115.8897 | 134.4745 | 156.1796 | 181.5417 | 211.1912 | 245.8687 | 286.4445 | 333.9414 | 389.5617 | 454.7188 | 531.0748 | 620.5844 | 725.5467 | 848.6662 | 993.125 | 1162.6671 | 1361.6988 | 1595.4056 | 1869.8917 | 2192.3423 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 71.6505 | 85.2982 | 101.2199 | 119.8048 | 141.5099 | 166.8719 | 196.5214 | 231.1989 | 271.7747 | 319.2716 | 374.8919 | 440.049 | 516.405 | 605.9147 | 710.8769 | 833.9965 | 978.4552 | 1145.1083 | 1338.4235 | 1564.2835 | 1827.9496 | 2135.4198 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 12.1668 | 14.0904 | 16.3345 | 18.954 | 22.0134 | 25.5881 | 29.7672 | 34.6549 | 40.3741 | 47.0687 | 54.9083 | 64.0921 | 74.8544 | 87.4707 | 102.2651 | 119.6186 | 139.9799 | 163.8767 | 191.93 | 224.8708 | 263.5593 | 309.0084 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 10.0991 | 12.0227 | 14.2668 | 16.8864 | 19.9457 | 23.5204 | 27.6995 | 32.5873 | 38.3064 | 45.001 | 52.8406 | 62.0245 | 72.7868 | 85.403 | 100.1974 | 117.5509 | 137.9123 | 161.4018 | 188.6494 | 220.4841 | 257.6476 | 300.9852 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 373.9154 | 439.9696 | 517.0294 | 606.9788 | 712.0302 | 834.781 | 978.2825 | 1146.1194 | 1342.5036 | 1572.3854 | 1841.5838 | 2156.94 | 2526.4983 | 2959.719 | 3467.7296 | 4063.62 | 4762.7909 | 5574.7242 | 6520.9297 | 7628.59 | 8924.7282 | 10440.57 | 10776.0547 | 10689.2596 | 10567.8837 | 10397.6946 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| TRUE | 4363 | 22004350 | TYA | TYA-ATS | 66 | ATS LINE | PILOT WIRE | Y | Brown Boveri | GROUP_2372 | GROUP 2372 | GROUP 2000s | Electronic |  | 0.016937 | 2190 |  | 8.25 | 0.026286 | 0.0012915 | 0.024994 | 277.3551 | 568.2672 | 845.6223 | 81.947 | 10.5298 | 234.9136 |  | 14.2947 | 0.11764 | 0.0057802 | 0.11186 | 1241.3137 | 2543.3026 | 3784.6162 | 366.7571 | 47.1265 | 1051.3654 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 54.2635 | 0.052758 | 54.3162 | 14.6705 | 2.0677 | 0.021809 |  | 1173.0127 | 5249.8653 | 71.0762 | 5178.7891 |  | 0.054968 |  | 8.7162 | 9.2087 | 9.7291 | 10.2788 | 10.8596 | 11.4733 | 12.1216 | 12.8065 | 13.5302 | 14.2947 | 15.1025 | 15.9559 | 16.8575 | 17.8101 | 18.8164 | 19.8797 | 21.003 | 22.1898 | 23.4437 | 24.7684 | 26.168 | 27.6467 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.030409 | 0.035217 | 0.040826 | 0.047373 | 0.05502 | 0.063954 | 0.074399 | 0.086616 | 0.10091 | 0.11764 | 0.13724 | 0.16019 | 0.18709 | 0.21862 | 0.2556 | 0.29897 | 0.34986 | 0.40959 | 0.47971 | 0.56204 | 0.65873 | 0.77233 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0014941 | 0.0017304 | 0.0020059 | 0.0023276 | 0.0027033 | 0.0031423 | 0.0036555 | 0.0042558 | 0.0049581 | 0.0057802 | 0.006743 | 0.0078708 | 0.0091924 | 0.010742 | 0.012559 | 0.01469 | 0.01719 | 0.020125 | 0.02357 | 0.027615 | 0.032366 | 0.037948 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 0.03937 | 1357.0341 | 1571.5892 | 1821.8922 | 2114.0632 | 2455.2874 | 2854.0027 | 3320.1197 | 3865.2818 | 4503.1706 | 5249.8653 | 6124.2668 | 7148.5965 | 8348.9835 | 9756.1569 | 11406.2603 | 13341.8121 | 15612.8362 | 18278.194 | 21407.1541 | 25081.2408 | 29396.4133 | 34465.6321 | 35757.5481 | 35757.5481 | 35757.5481 | 35757.5481 | 35757.5481 | 35757.5481 | 35757.5481 | 35757.5481 |  | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 52.5996 | 69.7239 | 93.2303 | 125.6427 | 170.5181 | 232.8781 | 319.8236 | 441.4098 | 611.8938 | 851.5136 | 1189.0269 | 1665.3348 | 2338.6574 |  | 320.8663 | 371.5972 | 430.7805 | 499.8634 | 580.5448 | 674.8197 | 785.0316 | 913.9334 | 1064.7601 | 1241.3137 | 1448.0631 | 1690.2626 | 1974.0902 | 2306.8118 | 2696.9734 | 3154.6284 | 3691.6047 | 4321.82 | 5061.6525 | 5930.3784 | 6950.687 | 8149.2875 | 8454.7569 | 8454.7569 | 8454.7569 | 8454.7569 | 8454.7569 | 8454.7569 | 8454.7569 | 8454.7569 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 293.7346 | 344.4655 | 403.6488 | 472.7317 | 553.4131 | 647.688 | 757.8999 | 886.8017 | 1037.6284 | 1214.182 | 1420.9314 | 1663.1308 | 1946.9585 | 2279.6801 | 2669.8417 | 3127.4967 | 3664.473 | 4289.345 | 5018.605 | 5872.8181 | 6873.1153 | 8044.0096 | 8310.9779 | 8257.2978 | 8182.2305 | 8076.9737 | 7929.0324 | 7720.6518 | 7426.5793 | 7010.8701 |  | 657.4165 | 761.358 | 882.6175 | 1024.1601 | 1189.4665 | 1382.6245 | 1608.4354 | 1872.5397 | 2181.5656 | 2543.3026 | 2966.9073 | 3463.1448 | 4044.6736 | 4726.3801 | 5525.7744 | 6463.4544 | 7563.6543 | 8854.8896 | 10370.7175 | 12150.6326 | 14241.1222 | 16696.9104 | 17322.7805 | 17322.7805 | 17322.7805 | 17322.7805 | 17322.7805 | 17322.7805 | 17322.7805 | 17322.7805 |  | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.063148 | 0.083706 | 0.11193 | 0.15084 | 0.20471 | 0.27958 | 0.38396 | 0.52993 | 0.7346 | 1.0223 | 1.4275 | 1.9993 | 2.8076 |  | 657.3638 | 761.3052 | 882.5648 | 1024.1073 | 1189.4137 | 1382.5717 | 1608.3826 | 1872.487 | 2181.5128 | 2543.2498 | 2966.8545 | 3463.0921 | 4044.6208 | 4726.3274 | 5525.7216 | 6463.4016 | 7563.6016 | 8854.8265 | 10370.6338 | 12150.5206 | 14240.9714 | 16696.7057 | 17322.5009 | 17322.3965 | 17322.2505 | 17322.0459 | 17321.7582 | 17321.353 | 17320.7812 | 17319.9728 |  | 951.0984 | 1105.7707 | 1286.2136 | 1496.839 | 1742.8268 | 2030.2597 | 2366.2825 | 2759.2886 | 3219.1412 | 3757.4318 | 4387.7859 | 5126.2229 | 5991.5793 | 7006.0074 | 8195.5633 | 9590.8983 | 11228.0746 | 13144.1715 | 15389.2388 | 18023.3387 | 21114.0867 | 24740.7154 | 25633.4788 | 25579.6943 | 25504.481 | 25399.0196 | 25250.7906 | 25042.0048 | 24747.3605 | 24330.8429 |  | 94.8028 | 109.7917 | 127.2779 | 147.6891 | 171.5271 | 199.3815 | 231.9445 | 270.0297 | 314.5928 | 366.7571 | 427.8431 | 499.403 | 583.2624 | 681.568 | 796.8447 | 932.0629 | 1090.7173 | 1276.92 | 1495.5101 | 1752.1828 | 2053.642 | 2407.7791 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 | 2498.0328 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 80.1323 | 95.1212 | 112.6075 | 133.0186 | 156.8566 | 184.711 | 217.2741 | 255.3593 | 299.9223 | 352.0867 | 413.1726 | 484.7326 | 568.592 | 666.8975 | 782.1742 | 917.3924 | 1076.0468 | 1259.3604 | 1472.2337 | 1721.0592 | 2011.698 | 2350.8541 | 2420.2897 | 2391.2642 | 2350.6743 | 2293.7607 | 2213.767 | 2101.0929 | 1942.0842 | 1717.305 |  | 12.1817 | 14.1077 | 16.3546 | 18.9773 | 22.0404 | 25.6195 | 29.8037 | 34.6975 | 40.4236 | 47.1265 | 54.9757 | 64.1709 | 74.9464 | 87.5782 | 102.3906 | 119.7655 | 140.1518 | 164.078 | 192.1657 | 225.1469 | 263.883 | 309.3879 | 320.985 | 320.985 | 320.985 | 320.985 | 320.985 | 320.985 | 320.985 | 320.985 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 10.114 | 12.04 | 14.2869 | 16.9096 | 19.9727 | 23.5519 | 27.736 | 32.6298 | 38.3559 | 45.0588 | 52.9081 | 62.1032 | 72.8787 | 85.5105 | 100.323 | 117.6978 | 138.0842 | 161.6031 | 188.8851 | 220.7603 | 257.9713 | 301.3647 | 310.0277 | 305.9368 | 300.2159 | 292.1944 | 280.9199 | 265.0393 | 242.6282 | 210.9473 |  | 271.7667 | 314.7346 | 364.8616 | 423.3733 | 491.7087 | 571.5575 | 664.9045 | 774.0815 | 901.8284 | 1051.3654 | 1226.4776 | 1431.6152 | 1672.011 | 1953.8188 | 2284.2771 | 2671.9008 | 3126.708 | 3660.4864 | 4287.1083 | 5022.9 | 5887.079 | 6902.2671 | 7160.993 | 7160.993 | 7160.993 | 7160.993 | 7160.993 | 7160.993 | 7160.993 | 7160.993 |  | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.026104 | 0.034603 | 0.046269 | 0.062354 | 0.084625 | 0.11557 | 0.15872 | 0.21906 | 0.30367 | 0.42259 | 0.59009 | 0.82648 | 1.1606 |  | 271.7449 | 314.7128 | 364.8398 | 423.3515 | 491.6868 | 571.5356 | 664.8827 | 774.0597 | 901.8066 | 1051.3436 | 1226.4558 | 1431.5934 | 1671.9892 | 1953.797 | 2284.2553 | 2671.879 | 3126.6861 | 3660.4603 | 4287.0737 | 5022.8538 | 5887.0166 | 6902.1825 | 7160.8774 | 7160.8343 | 7160.7739 | 7160.6893 | 7160.5704 | 7160.4029 | 7160.1665 | 7159.8324 |  | 1313.0896 | 1527.6447 | 1777.9477 | 2070.1187 | 2411.343 | 2810.0582 | 3276.1752 | 3821.3374 | 4459.2261 | 5205.9208 | 6080.3223 | 7104.652 | 8305.0391 | 9712.2124 | 11362.3158 | 13297.8676 | 15568.8917 | 18225.5952 | 21337.4313 | 24988.012 | 29270.7726 | 34295.1167 | 35524.6736 | 35437.7295 | 35316.1452 | 35145.6639 | 34906.0479 | 34568.5399 | 34092.2395 | 33418.9275
| TRUE | 4364 | 22015998 | TYA | TYA-ATS | 66 | ATS LINE | NEUTRAL DISPLACEMENT | X | EMAIL | GROUP_3242 | GROUP 3242 | GROUP 3000s | Electronic |  | 0.15703 | 2190 |  | 9.9 | 0.042792 | 0.015079 | 0.027713 | 465.1499 | 6634.8055 | 7099.9554 | 207.0778 | 17.2719 | 2742.735 |  | 17.778 | 0.21751 | 0.076646 | 0.14086 | 2364.3101 | 33724.0498 | 36088.3599 | 1052.5559 | 87.7913 | 13941.0463 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.2022 |  | 10067.0401 | 51169.7534 | 71.6996 | 51098.0538 |  | 0.058543 |  | 10.4969 | 11.1297 | 11.8008 | 12.5122 | 13.2666 | 14.0664 | 14.9145 | 15.8137 | 16.7671 | 17.778 | 18.8499 | 19.9863 | 21.1913 | 22.4689 | 23.8236 | 25.2599 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.050154 | 0.058841 | 0.069098 | 0.081214 | 0.095533 | 0.11247 | 0.1325 | 0.1562 | 0.18427 | 0.21751 | 0.25689 | 0.30357 | 0.35892 | 0.42456 | 0.50243 | 0.59483 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.017673 | 0.020735 | 0.024349 | 0.028618 | 0.033664 | 0.039631 | 0.046689 | 0.055042 | 0.064932 | 0.076646 | 0.090524 | 0.10697 | 0.12648 | 0.14961 | 0.17705 | 0.20961 | 0.24825 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 11799.0075 | 13842.7088 | 16255.6105 | 19105.928 | 22474.6552 | 26457.9782 | 31170.1495 | 36746.9067 | 43349.5434 | 51169.7534 | 60435.3982 | 71417.3728 | 84437.7807 | 99879.667 | 118198.6082 | 139936.5139 | 165738.0625 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 |  | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 53.352 | 70.7213 | 94.5639 | 127.44 | 172.9574 | 236.2095 | 324.3988 | 447.7244 | 620.6472 | 863.6948 | 1206.0364 | 1689.158 | 2372.1127 |  | 545.1758 | 639.6055 | 751.0942 | 882.7938 | 1038.4466 | 1222.4969 | 1440.2239 | 1697.8992 | 2002.9756 | 2364.3101 | 2792.4314 | 3299.856 | 3901.4669 | 4614.9628 | 5461.3937 | 6465.7986 | 7657.965 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 518.0436 | 612.4733 | 723.9619 | 855.6615 | 1011.3143 | 1195.3647 | 1413.0916 | 1670.767 | 1975.8433 | 2337.1779 | 2765.2991 | 3272.7238 | 3874.3347 | 4587.8306 | 5434.2614 | 6438.6663 | 7630.8328 | 8677.4154 | 8666.8427 | 8652.3296 | 8632.3178 | 8604.6112 | 8566.1093 | 8512.4282 | 8437.3594 | 8332.1006 | 8184.1565 | 7975.7719 | 7681.6938 | 7265.9765 |  | 7776.2797 | 9123.206 | 10713.4582 | 12591.9948 | 14812.1955 | 17437.4531 | 20543.067 | 24218.4968 | 28570.0451 | 33724.0498 | 39830.6859 | 47068.4901 | 55649.7487 | 65826.9121 | 77900.2336 | 92226.8653 | 109231.6905 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 7775.7906 | 9122.7169 | 10712.9691 | 12591.5057 | 14811.7063 | 17436.9639 | 20542.5778 | 24218.0077 | 28569.5559 | 33723.5607 | 39830.1968 | 47068.001 | 55649.2596 | 65826.423 | 77899.7445 | 92226.3762 | 109231.2014 | 124235.5686 | 124235.378 | 124235.1163 | 124234.7556 | 124234.2561 | 124233.562 | 124232.5942 | 124231.2409 | 124229.3434 | 124226.6763 | 124222.9196 | 124217.6181 | 124210.1237 |  | 8293.8342 | 9735.1901 | 11436.9311 | 13447.1672 | 15823.0207 | 18632.3286 | 21955.6695 | 25888.7747 | 30545.3992 | 36060.7386 | 42595.4959 | 50340.7248 | 59523.5943 | 70414.2535 | 83334.0059 | 98665.0425 | 116862.0341 | 132912.984 | 132902.2207 | 132887.4459 | 132867.0733 | 132838.8672 | 132799.6713 | 132745.0224 | 132668.6004 | 132561.444 | 132410.8328 | 132198.6915 | 131899.3119 | 131476.1003 |  | 242.7042 | 284.7429 | 334.376 | 393.0067 | 462.3011 | 544.2375 | 641.1664 | 755.8796 | 891.6951 | 1052.5559 | 1243.1491 | 1469.0471 | 1736.8754 | 2054.5132 | 2431.3317 | 2878.4779 | 3409.2128 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 228.0281 | 270.0668 | 319.6999 | 378.3306 | 447.625 | 529.5615 | 626.4903 | 741.2035 | 877.019 | 1037.8798 | 1228.473 | 1454.371 | 1722.1993 | 2039.8371 | 2416.6556 | 2863.8018 | 3394.5367 | 3859.9483 | 3854.2294 | 3846.3791 | 3835.5545 | 3820.5678 | 3799.7417 | 3770.7051 | 3730.0997 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 20.2434 | 23.7498 | 27.8896 | 32.7798 | 38.5595 | 45.3936 | 53.4783 | 63.0462 | 74.3743 | 87.7913 | 103.6883 | 122.5299 | 144.8689 | 171.3624 | 202.792 | 240.0874 | 284.3548 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 18.1757 | 21.6821 | 25.8219 | 30.7121 | 36.4918 | 43.3259 | 51.4106 | 60.9785 | 72.3066 | 85.7236 | 101.6206 | 120.4622 | 142.8012 | 169.2947 | 200.7243 | 238.0197 | 282.2871 | 320.9399 | 320.1342 | 319.0282 | 317.5031 | 315.3917 | 312.4575 | 308.3665 | 302.6457 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 3214.6043 | 3771.4046 | 4428.7925 | 5205.3529 | 6123.1526 | 7208.397 | 8492.214 | 10011.5848 | 11810.4534 | 13941.0463 | 16465.4435 | 19457.4496 | 23004.8208 | 27211.9165 | 32202.8572 | 38125.2846 | 45154.8394 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 |  | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.24202 | 0.32081 | 0.42897 | 0.5781 | 0.78458 | 1.0715 | 1.4716 | 2.031 | 2.8154 | 3.918 | 5.4709 | 7.6625 | 10.7606 |  | 3214.4021 | 3771.2024 | 4428.5903 | 5205.1507 | 6122.9504 | 7208.1948 | 8492.0118 | 10011.3826 | 11810.2512 | 13940.8441 | 16465.2413 | 19457.2474 | 23004.6186 | 27211.7143 | 32202.655 | 38125.0824 | 45154.6372 | 51357.2308 | 51357.152 | 51357.0439 | 51356.8948 | 51356.6883 | 51356.4013 | 51356.0013 | 51355.4419 | 51354.6574 | 51353.5549 | 51352.0019 | 51349.8104 | 51346.7123 |  | 11754.4401 | 13798.1414 | 16211.0431 | 19061.3607 | 22430.0878 | 26413.4108 | 31125.5821 | 36702.3393 | 43304.9761 | 51125.1861 | 60390.8308 | 71372.8054 | 84393.2133 | 99835.0996 | 118154.0408 | 139891.9465 | 165693.4951 | 188451.1031 | 188433.7363 | 188409.8971 | 188377.0257 | 188331.5149 | 188268.2719 | 188180.0953 | 188056.7876 | 187883.8897 | 187640.877 | 187298.5848 | 186815.5327 | 186132.6764
| TRUE | 4365 | 22004349 | TYA | TYA-ATS | 66 | ATS LINE | PILOT WIRE | X | SEC | GROUP_3385 | GROUP 3385 | GROUP 3000s | Electronic |  | 0.15703 | 2190 |  | 9.9 | 0.042792 | 0.015079 | 0.027713 | 465.1499 | 6634.8055 | 7099.9554 | 207.0778 | 17.2719 | 2742.735 |  | 17.778 | 0.21751 | 0.076646 | 0.14086 | 2364.3101 | 33724.0498 | 36088.3599 | 1052.5559 | 87.7913 | 13941.0463 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.2022 |  | 10067.0401 | 51169.7534 | 71.6996 | 51098.0538 |  | 0.058543 |  | 10.4969 | 11.1297 | 11.8008 | 12.5122 | 13.2666 | 14.0664 | 14.9145 | 15.8137 | 16.7671 | 17.778 | 18.8499 | 19.9863 | 21.1913 | 22.4689 | 23.8236 | 25.2599 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.050154 | 0.058841 | 0.069098 | 0.081214 | 0.095533 | 0.11247 | 0.1325 | 0.1562 | 0.18427 | 0.21751 | 0.25689 | 0.30357 | 0.35892 | 0.42456 | 0.50243 | 0.59483 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.017673 | 0.020735 | 0.024349 | 0.028618 | 0.033664 | 0.039631 | 0.046689 | 0.055042 | 0.064932 | 0.076646 | 0.090524 | 0.10697 | 0.12648 | 0.14961 | 0.17705 | 0.20961 | 0.24825 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 11799.0075 | 13842.7088 | 16255.6105 | 19105.928 | 22474.6552 | 26457.9782 | 31170.1495 | 36746.9067 | 43349.5434 | 51169.7534 | 60435.3982 | 71417.3728 | 84437.7807 | 99879.667 | 118198.6082 | 139936.5139 | 165738.0625 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 |  | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 53.352 | 70.7213 | 94.5639 | 127.44 | 172.9574 | 236.2095 | 324.3988 | 447.7244 | 620.6472 | 863.6948 | 1206.0364 | 1689.158 | 2372.1127 |  | 545.1758 | 639.6055 | 751.0942 | 882.7938 | 1038.4466 | 1222.4969 | 1440.2239 | 1697.8992 | 2002.9756 | 2364.3101 | 2792.4314 | 3299.856 | 3901.4669 | 4614.9628 | 5461.3937 | 6465.7986 | 7657.965 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 518.0436 | 612.4733 | 723.9619 | 855.6615 | 1011.3143 | 1195.3647 | 1413.0916 | 1670.767 | 1975.8433 | 2337.1779 | 2765.2991 | 3272.7238 | 3874.3347 | 4587.8306 | 5434.2614 | 6438.6663 | 7630.8328 | 8677.4154 | 8666.8427 | 8652.3296 | 8632.3178 | 8604.6112 | 8566.1093 | 8512.4282 | 8437.3594 | 8332.1006 | 8184.1565 | 7975.7719 | 7681.6938 | 7265.9765 |  | 7776.2797 | 9123.206 | 10713.4582 | 12591.9948 | 14812.1955 | 17437.4531 | 20543.067 | 24218.4968 | 28570.0451 | 33724.0498 | 39830.6859 | 47068.4901 | 55649.7487 | 65826.9121 | 77900.2336 | 92226.8653 | 109231.6905 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 7775.7906 | 9122.7169 | 10712.9691 | 12591.5057 | 14811.7063 | 17436.9639 | 20542.5778 | 24218.0077 | 28569.5559 | 33723.5607 | 39830.1968 | 47068.001 | 55649.2596 | 65826.423 | 77899.7445 | 92226.3762 | 109231.2014 | 124235.5686 | 124235.378 | 124235.1163 | 124234.7556 | 124234.2561 | 124233.562 | 124232.5942 | 124231.2409 | 124229.3434 | 124226.6763 | 124222.9196 | 124217.6181 | 124210.1237 |  | 8293.8342 | 9735.1901 | 11436.9311 | 13447.1672 | 15823.0207 | 18632.3286 | 21955.6695 | 25888.7747 | 30545.3992 | 36060.7386 | 42595.4959 | 50340.7248 | 59523.5943 | 70414.2535 | 83334.0059 | 98665.0425 | 116862.0341 | 132912.984 | 132902.2207 | 132887.4459 | 132867.0733 | 132838.8672 | 132799.6713 | 132745.0224 | 132668.6004 | 132561.444 | 132410.8328 | 132198.6915 | 131899.3119 | 131476.1003 |  | 242.7042 | 284.7429 | 334.376 | 393.0067 | 462.3011 | 544.2375 | 641.1664 | 755.8796 | 891.6951 | 1052.5559 | 1243.1491 | 1469.0471 | 1736.8754 | 2054.5132 | 2431.3317 | 2878.4779 | 3409.2128 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 228.0281 | 270.0668 | 319.6999 | 378.3306 | 447.625 | 529.5615 | 626.4903 | 741.2035 | 877.019 | 1037.8798 | 1228.473 | 1454.371 | 1722.1993 | 2039.8371 | 2416.6556 | 2863.8018 | 3394.5367 | 3859.9483 | 3854.2294 | 3846.3791 | 3835.5545 | 3820.5678 | 3799.7417 | 3770.7051 | 3730.0997 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 20.2434 | 23.7498 | 27.8896 | 32.7798 | 38.5595 | 45.3936 | 53.4783 | 63.0462 | 74.3743 | 87.7913 | 103.6883 | 122.5299 | 144.8689 | 171.3624 | 202.792 | 240.0874 | 284.3548 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 18.1757 | 21.6821 | 25.8219 | 30.7121 | 36.4918 | 43.3259 | 51.4106 | 60.9785 | 72.3066 | 85.7236 | 101.6206 | 120.4622 | 142.8012 | 169.2947 | 200.7243 | 238.0197 | 282.2871 | 320.9399 | 320.1342 | 319.0282 | 317.5031 | 315.3917 | 312.4575 | 308.3665 | 302.6457 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 3214.6043 | 3771.4046 | 4428.7925 | 5205.3529 | 6123.1526 | 7208.397 | 8492.214 | 10011.5848 | 11810.4534 | 13941.0463 | 16465.4435 | 19457.4496 | 23004.8208 | 27211.9165 | 32202.8572 | 38125.2846 | 45154.8394 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 |  | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.24202 | 0.32081 | 0.42897 | 0.5781 | 0.78458 | 1.0715 | 1.4716 | 2.031 | 2.8154 | 3.918 | 5.4709 | 7.6625 | 10.7606 |  | 3214.4021 | 3771.2024 | 4428.5903 | 5205.1507 | 6122.9504 | 7208.1948 | 8492.0118 | 10011.3826 | 11810.2512 | 13940.8441 | 16465.2413 | 19457.2474 | 23004.6186 | 27211.7143 | 32202.655 | 38125.0824 | 45154.6372 | 51357.2308 | 51357.152 | 51357.0439 | 51356.8948 | 51356.6883 | 51356.4013 | 51356.0013 | 51355.4419 | 51354.6574 | 51353.5549 | 51352.0019 | 51349.8104 | 51346.7123 |  | 11754.4401 | 13798.1414 | 16211.0431 | 19061.3607 | 22430.0878 | 26413.4108 | 31125.5821 | 36702.3393 | 43304.9761 | 51125.1861 | 60390.8308 | 71372.8054 | 84393.2133 | 99835.0996 | 118154.0408 | 139891.9465 | 165693.4951 | 188451.1031 | 188433.7363 | 188409.8971 | 188377.0257 | 188331.5149 | 188268.2719 | 188180.0953 | 188056.7876 | 187883.8897 | 187640.877 | 187298.5848 | 186815.5327 | 186132.6764
| TRUE | 4366 | 22004357 | TYA | TYA-ATS | 66 | ATS LINE | AUTO RECLOSE | Blank | LOCUS | LAR_3156 | LAR 3156 | LAR | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 101.3994 | 1446.3414 | 1547.7409 | 45.1415 | 3.7652 | 597.8971 |  | 8.8015 | 0.031208 | 0.010997 | 0.020211 | 339.2359 | 4838.7928 | 5178.0286 | 151.0228 | 12.5965 | 2000.2887 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.2022 |  | 2194.5447 | 7341.9366 | 71.6996 | 7270.2369 |  | 0.047018 |  | 5.7648 | 6.0423 | 6.3332 | 6.6381 | 6.9576 | 7.2926 | 7.6436 | 8.0116 | 8.3973 | 8.8015 | 9.2252 | 9.6693 | 10.1348 | 10.6227 | 11.1341 | 11.6701 | 12.2319 | 12.8207 | 13.4379 | 14.0848 | 14.7629 | 15.4736 | 16.2185 | 16.9993 | 17.8176 | 18.6754 | 19.5744 | 20.5167 | 21.5044 | 22.5396 |  | 0.010477 | 0.011781 | 0.013261 | 0.014944 | 0.016856 | 0.019033 | 0.02151 | 0.024331 | 0.027545 | 0.031208 | 0.035387 | 0.040154 | 0.045595 | 0.051808 | 0.058904 | 0.067014 | 0.076283 | 0.086882 | 0.099006 | 0.11288 | 0.12875 | 0.14693 | 0.16774 | 0.19158 | 0.21889 | 0.25018 | 0.28605 | 0.32717 | 0.37433 | 0.42841 |  | 0.0036919 | 0.0041513 | 0.004673 | 0.0052658 | 0.0059399 | 0.0067067 | 0.0075796 | 0.0085736 | 0.0097062 | 0.010997 | 0.01247 | 0.014149 | 0.016067 | 0.018256 | 0.020757 | 0.023614 | 0.026881 | 0.030616 | 0.034888 | 0.039776 | 0.04537 | 0.051774 | 0.059108 | 0.067507 | 0.077131 | 0.088159 | 0.1008 | 0.11529 | 0.13191 | 0.15096 | 2464.7586 | 2771.4441 | 3119.7405 | 3515.5305 | 3965.549 | 4477.5089 | 5060.2449 | 5723.8791 | 6480.011 | 7341.9366 | 8324.8985 | 9446.3753 | 10726.4129 | 12188.0052 | 13857.5332 | 15765.2679 | 17945.9497 | 20439.454 | 23291.5573 | 26554.8169 | 30289.5836 | 34565.1662 | 39461.17 | 45069.0375 | 51493.8197 | 58856.2141 | 67294.9085 | 76969.2784 | 88062.4889 | 100785.0643 |  | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 53.352 | 70.7213 | 94.5639 | 127.44 | 172.9574 | 236.2095 | 324.3988 | 447.7244 | 620.6472 | 863.6948 | 1206.0364 | 1689.158 | 2372.1127 |  | 113.8847 | 128.0552 | 144.1483 | 162.4359 | 183.2291 | 206.8843 | 233.8098 | 264.4731 | 299.4104 | 339.2359 | 384.6538 | 436.4719 | 495.6164 | 563.1496 | 640.2905 | 728.4378 | 829.1967 | 944.4096 | 1076.1917 | 1226.9714 | 1399.5371 | 1597.0914 | 1823.3124 | 2082.4252 | 2379.2837 | 2719.4648 | 3109.3766 | 3556.3831 | 4068.9474 | 4656.7969 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 86.7525 | 100.923 | 117.0161 | 135.3036 | 156.0969 | 179.7521 | 206.6775 | 237.3409 | 272.2781 | 312.1036 | 357.5216 | 409.3397 | 468.4841 | 536.0173 | 613.1582 | 701.3056 | 802.0645 | 911.934 | 1033.1434 | 1169.4099 | 1321.9639 | 1491.8115 | 1679.5307 | 1884.9623 | 2106.7521 | 2341.6744 | 2583.6421 | 2822.2639 | 3040.7502 | 3212.8824 |  | 1624.4292 | 1826.554 | 2056.103 | 2316.9532 | 2613.5434 | 2950.9568 | 3335.0161 | 3772.3923 | 4270.7303 | 4838.7928 | 5486.6258 | 6225.7488 | 7069.3732 | 8032.6534 | 9132.9762 | 10390.292 | 11827.4969 | 13470.8713 | 15350.5848 | 17501.2758 | 19962.7193 | 22780.5941 | 26007.3651 | 29703.2986 | 33937.6296 | 38789.9053 | 44351.5298 | 50727.5412 | 58038.6568 | 66423.6252 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 1623.9401 | 1826.0649 | 2055.6139 | 2316.4641 | 2613.0543 | 2950.4677 | 3334.527 | 3771.9031 | 4270.2411 | 4838.3037 | 5486.1367 | 6225.2597 | 7068.884 | 8032.1643 | 9132.4871 | 10389.8029 | 11827.0078 | 13470.2859 | 15349.8087 | 17500.2381 | 19961.3209 | 22778.6962 | 26004.7731 | 29699.7388 | 33932.7165 | 38783.0947 | 44342.0521 | 50714.3068 | 58020.1209 | 66397.5949 |  | 1710.6926 | 1926.9878 | 2172.6299 | 2451.7677 | 2769.1511 | 3130.2198 | 3541.2045 | 4009.244 | 4542.5193 | 5150.4073 | 5843.6583 | 6634.5994 | 7537.3681 | 8568.1816 | 9745.6453 | 11091.1084 | 12629.0722 | 14382.2199 | 16382.9521 | 18669.648 | 21283.2847 | 24270.5077 | 27684.3038 | 31584.7011 | 36039.4686 | 41124.7691 | 46925.6942 | 53536.5707 | 61060.8711 | 69610.4773 |  | 50.6998 | 57.0083 | 64.1727 | 72.3141 | 81.5709 | 92.1018 | 104.0887 | 117.7395 | 133.2931 | 151.0228 | 171.2422 | 194.3108 | 220.6411 | 250.7059 | 285.0479 | 324.2897 | 369.1461 | 420.4372 | 479.1046 | 546.2295 | 623.0532 | 711.0015 | 811.7117 | 927.0649 | 1059.2219 | 1210.6655 | 1384.2485 | 1583.2491 | 1811.4352 | 2073.1371 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 36.0237 | 42.3322 | 49.4966 | 57.638 | 66.8948 | 77.4257 | 89.4126 | 103.0634 | 118.617 | 136.3467 | 156.5661 | 179.6348 | 205.965 | 236.0298 | 270.3718 | 309.6136 | 354.47 | 402.8708 | 455.8194 | 515.094 | 581.0931 | 654.0546 | 733.9388 | 820.2553 | 911.8069 | 1006.315 | 1099.8736 | 1186.1569 | 1255.2733 | 1292.1097 |  | 4.2288 | 4.7549 | 5.3525 | 6.0316 | 6.8036 | 7.682 | 8.6818 | 9.8204 | 11.1177 | 12.5965 | 14.2829 | 16.207 | 18.4032 | 20.9108 | 23.7752 | 27.0483 | 30.7897 | 35.0677 | 39.961 | 45.5598 | 51.9675 | 59.303 | 67.7031 | 77.3244 | 88.3473 | 100.9789 | 115.4571 | 132.0553 | 151.0878 | 172.9157 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 2.1611 | 2.6872 | 3.2848 | 3.9639 | 4.7359 | 5.6143 | 6.6141 | 7.7527 | 9.05 | 10.5288 | 12.2152 | 14.1393 | 16.3355 | 18.8431 | 21.7075 | 24.9806 | 28.722 | 32.5928 | 36.6804 | 41.1731 | 46.0558 | 51.2798 | 56.7457 | 62.2761 | 67.5782 | 72.1881 | 75.3918 | 76.1093 | 72.7306 | 62.8775 |  | 671.5161 | 755.0716 | 849.964 | 957.7958 | 1080.402 | 1219.8839 | 1378.6486 | 1559.4537 | 1765.4596 | 2000.2887 | 2268.0937 | 2573.6367 | 2922.3791 | 3320.5856 | 3775.4435 | 4295.2001 | 4889.3203 | 5568.6681 | 6345.7151 | 7234.7804 | 8252.3065 | 9417.1761 | 10751.0777 | 12278.9245 | 14029.3372 | 16035.1995 | 18334.2965 | 20970.0497 | 23992.3617 | 27458.5893 |  | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.24202 | 0.32081 | 0.42897 | 0.5781 | 0.78458 | 1.0715 | 1.4716 | 2.031 | 2.8154 | 3.918 | 5.4709 | 7.6625 | 10.7606 |  | 671.3139 | 754.8694 | 849.7618 | 957.5936 | 1080.1998 | 1219.6817 | 1378.4464 | 1559.2515 | 1765.2574 | 2000.0865 | 2267.8915 | 2573.4345 | 2922.1769 | 3320.3834 | 3775.2413 | 4294.9979 | 4889.1181 | 5568.4261 | 6345.3943 | 7234.3515 | 8251.7284 | 9416.3916 | 10750.0062 | 12277.4529 | 14027.3062 | 16032.384 | 18330.3786 | 20964.5788 | 23984.6992 | 27447.8287 |  | 2420.1912 | 2726.8767 | 3075.1731 | 3470.9631 | 3920.9816 | 4432.9416 | 5015.6775 | 5679.3117 | 6435.4437 | 7297.3692 | 8280.3311 | 9401.808 | 10681.8455 | 12143.4379 | 13812.9659 | 15720.7005 | 17901.3823 | 20386.1097 | 23220.8462 | 26460.2666 | 30162.162 | 34392.2337 | 39224.9945 | 44744.6854 | 51046.1598 | 58235.6563 | 66431.3381 | 75763.4157 | 86373.5742 | 98413.2933
| TRUE | 4367 | 22004348 | TYA | TYA-ATS | 66 | ATS LINE | PILOT WIRE | X | GEC | MBCI_3342 | MBCI 3342 | MBCI | Electronic |  | 0.15703 | 2190 |  | 6.6 | 0.014726 | 0.0051892 | 0.0095369 | 160.0721 | 2283.2371 | 2443.3092 | 71.2617 | 5.9438 | 943.858 |  | 10.9462 | 0.056226 | 0.019813 | 0.036413 | 611.1777 | 8717.7177 | 9328.8955 | 272.0873 | 22.6942 | 3603.7815 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.2022 |  | 3464.3727 | 13227.4584 | 71.6996 | 13155.7588 |  | 0.050592 |  | 6.9425 | 7.3028 | 7.6817 | 8.0804 | 8.4997 | 8.9408 | 9.4048 | 9.8928 | 10.4062 | 10.9462 | 11.5143 | 12.1118 | 12.7403 | 13.4015 | 14.0969 | 14.8285 | 15.598 | 16.4074 | 17.2589 | 18.1545 | 19.0966 | 20.0876 | 21.1301 | 22.2266 | 23.38 | 24.5933 | 25.8696 | 27.212 | 28 | 28 |  | 0.016762 | 0.019102 | 0.021791 | 0.024884 | 0.028444 | 0.032543 | 0.037265 | 0.042708 | 0.048985 | 0.056226 | 0.064584 | 0.074234 | 0.08538 | 0.09826 | 0.11315 | 0.13036 | 0.15027 | 0.17331 | 0.19998 | 0.23085 | 0.26659 | 0.30799 | 0.35596 | 0.41154 | 0.47596 | 0.55065 | 0.63725 | 0.73768 | 0.80128 | 0.80128 |  | 0.0059068 | 0.0067311 | 0.0076788 | 0.0087687 | 0.010023 | 0.011468 | 0.013132 | 0.01505 | 0.017261 | 0.019813 | 0.022758 | 0.026158 | 0.030086 | 0.034625 | 0.039871 | 0.045937 | 0.052954 | 0.061072 | 0.070468 | 0.081345 | 0.093941 | 0.10853 | 0.12543 | 0.14502 | 0.16772 | 0.19404 | 0.22455 | 0.25994 | 0.28235 | 0.28235 | 3943.4413 | 4493.8054 | 5126.4638 | 5854.1493 | 6691.6055 | 7655.9087 | 8766.8417 | 10047.3275 | 11523.9339 | 13227.4584 | 15193.6093 | 17463.7958 | 20086.0468 | 23116.0782 | 26618.5337 | 30668.4267 | 35352.8161 | 40772.7548 | 47045.554 | 54307.4166 | 62716.498 | 72456.465 | 83740.6343 | 96816.7843 | 111972.7507 | 129542.9336 | 149915.8649 | 173543.0093 | 188504.4474 | 188504.4474 |  | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 53.352 | 70.7213 | 94.5639 | 127.44 | 172.9574 | 236.2095 | 324.3988 | 447.7244 | 620.6472 | 863.6948 | 1206.0364 | 1689.158 | 2372.1127 |  | 182.2076 | 207.6373 | 236.8694 | 270.4923 | 309.1872 | 353.743 | 405.0739 | 464.2391 | 532.466 | 611.1777 | 702.0242 | 806.9187 | 928.0804 | 1068.0837 | 1229.9154 | 1417.0417 | 1633.4849 | 1883.9144 | 2173.7506 | 2509.2866 | 2897.8301 | 3347.8675 | 3869.2551 | 4473.4416 | 5173.7265 | 5985.5608 | 6926.8968 | 8018.5944 | 8709.891 | 8709.891 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 155.0754 | 180.5051 | 209.7372 | 243.3601 | 282.0549 | 326.6108 | 377.9417 | 437.1068 | 505.3337 | 584.0455 | 674.8919 | 779.7864 | 900.9481 | 1040.9514 | 1202.7832 | 1389.9094 | 1606.3527 | 1851.4388 | 2130.7022 | 2451.7251 | 2820.2568 | 3242.5876 | 3725.4734 | 4275.9788 | 4901.1949 | 5607.7704 | 6401.1623 | 7284.4752 | 7681.6938 | 7265.9765 |  | 2598.973 | 2961.6972 | 3378.6585 | 3858.2485 | 4410.1842 | 5045.7199 | 5777.8939 | 6621.8137 | 7594.9891 | 8717.7177 | 10013.5334 | 11509.7275 | 13237.954 | 15234.9331 | 17543.2691 | 20212.4005 | 23299.7044 | 26871.7811 | 31005.9459 | 35791.965 | 41334.0725 | 47753.3165 | 55190.2859 | 63808.2819 | 73797.0063 | 85376.8496 | 98803.8783 | 114375.6359 | 124236.154 | 124236.154 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 2598.4839 | 2961.2081 | 3378.1693 | 3857.7593 | 4409.695 | 5045.2308 | 5777.4047 | 6621.3246 | 7594.5 | 8717.2286 | 10013.0443 | 11509.2384 | 13237.4649 | 15234.444 | 17542.78 | 20211.9114 | 23299.2153 | 26871.1956 | 31005.1698 | 35790.9273 | 41332.6741 | 47751.4186 | 55187.6938 | 63804.7221 | 73792.0932 | 85370.0389 | 98794.4006 | 114362.4014 | 124217.6181 | 124210.1237 |  | 2753.5593 | 3141.7131 | 3587.9065 | 4101.1194 | 4691.7499 | 5371.8416 | 6155.3464 | 7058.4314 | 8099.8337 | 9301.2741 | 10687.9363 | 12289.0248 | 14138.413 | 16275.3954 | 18745.5632 | 21601.8208 | 24905.568 | 28722.6345 | 33135.872 | 38242.6524 | 44152.9309 | 50994.0062 | 58913.1673 | 68080.7009 | 78693.2882 | 90977.8093 | 105195.5628 | 121646.8767 | 131899.3119 | 131476.1003 |  | 81.1161 | 92.4371 | 105.4508 | 120.4192 | 137.6456 | 157.4812 | 180.3329 | 206.6724 | 237.046 | 272.0873 | 312.5308 | 359.2283 | 413.1677 | 475.4951 | 547.5402 | 630.846 | 727.2033 | 838.6908 | 967.7216 | 1117.0973 | 1290.0711 | 1490.4211 | 1722.5352 | 1991.51 | 2303.2665 | 2664.6832 | 3083.752 | 3569.7596 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 66.44 | 77.761 | 90.7747 | 105.7431 | 122.9695 | 142.8051 | 165.6568 | 191.9963 | 222.3699 | 257.4112 | 297.8547 | 344.5522 | 398.4916 | 460.819 | 532.8641 | 616.1699 | 712.5272 | 821.1245 | 944.4363 | 1085.9617 | 1248.111 | 1433.4742 | 1644.7622 | 1884.7005 | 2155.8515 | 2460.3326 | 2799.3771 | 3172.6674 | 3321.3528 | 3096.4873 |  | 6.7657 | 7.71 | 8.7954 | 10.0439 | 11.4807 | 13.1352 | 15.0412 | 17.2381 | 19.7715 | 22.6942 | 26.0675 | 29.9624 | 34.4614 | 39.66 | 45.6691 | 52.6175 | 60.6544 | 69.9533 | 80.7155 | 93.1746 | 107.602 | 124.3127 | 143.6728 | 166.1074 | 192.1103 | 222.2553 | 257.2089 | 297.7457 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 4.698 | 5.6423 | 6.7277 | 7.9762 | 9.413 | 11.0674 | 12.9735 | 15.1704 | 17.7038 | 20.6265 | 23.9998 | 27.8947 | 32.3937 | 37.5923 | 43.6014 | 50.5498 | 58.5867 | 67.4784 | 77.4349 | 88.7879 | 101.6902 | 116.2895 | 132.7155 | 151.0591 | 171.3412 | 193.4645 | 217.1435 | 241.7997 | 245.0577 | 213.3766 |  | 1074.3788 | 1224.3238 | 1396.6897 | 1594.9455 | 1823.1079 | 2085.8294 | 2388.4998 | 2737.3643 | 3139.6613 | 3603.7815 | 4139.4534 | 4757.9589 | 5472.3834 | 6297.9064 | 7252.1399 | 8355.5211 | 9631.769 | 11108.4151 | 12817.4205 | 14795.8932 | 17086.9223 | 19740.5472 | 22814.8853 | 26377.4433 | 30506.641 | 35293.5848 | 40844.129 | 47281.2738 | 51357.4729 | 51357.4729 |  | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.24202 | 0.32081 | 0.42897 | 0.5781 | 0.78458 | 1.0715 | 1.4716 | 2.031 | 2.8154 | 3.918 | 5.4709 | 7.6625 | 10.7606 |  | 1074.1766 | 1224.1216 | 1396.4875 | 1594.7433 | 1822.9057 | 2085.6272 | 2388.2976 | 2737.1621 | 3139.4591 | 3603.5793 | 4139.2512 | 4757.7567 | 5472.1812 | 6297.7042 | 7251.9377 | 8355.3189 | 9631.5668 | 11108.1731 | 12817.0997 | 14795.4643 | 17086.3442 | 19739.7626 | 22813.8138 | 26375.9717 | 30504.61 | 35290.7693 | 40840.211 | 47275.8029 | 51349.8104 | 51346.7123 |  | 3898.8739 | 4449.238 | 5081.8965 | 5809.5819 | 6647.0381 | 7611.3413 | 8722.2743 | 10002.7602 | 11479.3665 | 13182.891 | 15149.0419 | 17419.2285 | 20041.4794 | 23071.5108 | 26573.9664 | 30623.8593 | 35308.2488 | 40719.4104 | 46974.8429 | 54212.8663 | 62589.0763 | 72283.5325 | 83504.4588 | 96492.4322 | 111525.0908 | 128922.3758 | 149052.2945 | 172337.1467 | 186815.5327 | 186132.6764
| TRUE | 4368 | 22015999 | TYA | TYA-BLTS | 66 | BLTS LINE | NEUTRAL DISPLACEMENT | X | EMAIL | GROUP_3242 | GROUP 3242 | GROUP 3000s | Electronic |  | 0.15703 | 2190 |  | 9.9 | 0.042792 | 0.015079 | 0.027713 | 465.1499 | 6634.8055 | 7099.9554 | 207.0778 | 17.2719 | 2742.735 |  | 17.778 | 0.21751 | 0.076646 | 0.14086 | 2364.3101 | 33724.0498 | 36088.3599 | 1052.5559 | 87.7913 | 13941.0463 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.2022 |  | 10067.0401 | 51169.7534 | 71.6996 | 51098.0538 |  | 0.058543 |  | 10.4969 | 11.1297 | 11.8008 | 12.5122 | 13.2666 | 14.0664 | 14.9145 | 15.8137 | 16.7671 | 17.778 | 18.8499 | 19.9863 | 21.1913 | 22.4689 | 23.8236 | 25.2599 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.050154 | 0.058841 | 0.069098 | 0.081214 | 0.095533 | 0.11247 | 0.1325 | 0.1562 | 0.18427 | 0.21751 | 0.25689 | 0.30357 | 0.35892 | 0.42456 | 0.50243 | 0.59483 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.017673 | 0.020735 | 0.024349 | 0.028618 | 0.033664 | 0.039631 | 0.046689 | 0.055042 | 0.064932 | 0.076646 | 0.090524 | 0.10697 | 0.12648 | 0.14961 | 0.17705 | 0.20961 | 0.24825 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 11799.0075 | 13842.7088 | 16255.6105 | 19105.928 | 22474.6552 | 26457.9782 | 31170.1495 | 36746.9067 | 43349.5434 | 51169.7534 | 60435.3982 | 71417.3728 | 84437.7807 | 99879.667 | 118198.6082 | 139936.5139 | 165738.0625 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 |  | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 53.352 | 70.7213 | 94.5639 | 127.44 | 172.9574 | 236.2095 | 324.3988 | 447.7244 | 620.6472 | 863.6948 | 1206.0364 | 1689.158 | 2372.1127 |  | 545.1758 | 639.6055 | 751.0942 | 882.7938 | 1038.4466 | 1222.4969 | 1440.2239 | 1697.8992 | 2002.9756 | 2364.3101 | 2792.4314 | 3299.856 | 3901.4669 | 4614.9628 | 5461.3937 | 6465.7986 | 7657.965 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 518.0436 | 612.4733 | 723.9619 | 855.6615 | 1011.3143 | 1195.3647 | 1413.0916 | 1670.767 | 1975.8433 | 2337.1779 | 2765.2991 | 3272.7238 | 3874.3347 | 4587.8306 | 5434.2614 | 6438.6663 | 7630.8328 | 8677.4154 | 8666.8427 | 8652.3296 | 8632.3178 | 8604.6112 | 8566.1093 | 8512.4282 | 8437.3594 | 8332.1006 | 8184.1565 | 7975.7719 | 7681.6938 | 7265.9765 |  | 7776.2797 | 9123.206 | 10713.4582 | 12591.9948 | 14812.1955 | 17437.4531 | 20543.067 | 24218.4968 | 28570.0451 | 33724.0498 | 39830.6859 | 47068.4901 | 55649.7487 | 65826.9121 | 77900.2336 | 92226.8653 | 109231.6905 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 7775.7906 | 9122.7169 | 10712.9691 | 12591.5057 | 14811.7063 | 17436.9639 | 20542.5778 | 24218.0077 | 28569.5559 | 33723.5607 | 39830.1968 | 47068.001 | 55649.2596 | 65826.423 | 77899.7445 | 92226.3762 | 109231.2014 | 124235.5686 | 124235.378 | 124235.1163 | 124234.7556 | 124234.2561 | 124233.562 | 124232.5942 | 124231.2409 | 124229.3434 | 124226.6763 | 124222.9196 | 124217.6181 | 124210.1237 |  | 8293.8342 | 9735.1901 | 11436.9311 | 13447.1672 | 15823.0207 | 18632.3286 | 21955.6695 | 25888.7747 | 30545.3992 | 36060.7386 | 42595.4959 | 50340.7248 | 59523.5943 | 70414.2535 | 83334.0059 | 98665.0425 | 116862.0341 | 132912.984 | 132902.2207 | 132887.4459 | 132867.0733 | 132838.8672 | 132799.6713 | 132745.0224 | 132668.6004 | 132561.444 | 132410.8328 | 132198.6915 | 131899.3119 | 131476.1003 |  | 242.7042 | 284.7429 | 334.376 | 393.0067 | 462.3011 | 544.2375 | 641.1664 | 755.8796 | 891.6951 | 1052.5559 | 1243.1491 | 1469.0471 | 1736.8754 | 2054.5132 | 2431.3317 | 2878.4779 | 3409.2128 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 228.0281 | 270.0668 | 319.6999 | 378.3306 | 447.625 | 529.5615 | 626.4903 | 741.2035 | 877.019 | 1037.8798 | 1228.473 | 1454.371 | 1722.1993 | 2039.8371 | 2416.6556 | 2863.8018 | 3394.5367 | 3859.9483 | 3854.2294 | 3846.3791 | 3835.5545 | 3820.5678 | 3799.7417 | 3770.7051 | 3730.0997 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 20.2434 | 23.7498 | 27.8896 | 32.7798 | 38.5595 | 45.3936 | 53.4783 | 63.0462 | 74.3743 | 87.7913 | 103.6883 | 122.5299 | 144.8689 | 171.3624 | 202.792 | 240.0874 | 284.3548 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 18.1757 | 21.6821 | 25.8219 | 30.7121 | 36.4918 | 43.3259 | 51.4106 | 60.9785 | 72.3066 | 85.7236 | 101.6206 | 120.4622 | 142.8012 | 169.2947 | 200.7243 | 238.0197 | 282.2871 | 320.9399 | 320.1342 | 319.0282 | 317.5031 | 315.3917 | 312.4575 | 308.3665 | 302.6457 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 3214.6043 | 3771.4046 | 4428.7925 | 5205.3529 | 6123.1526 | 7208.397 | 8492.214 | 10011.5848 | 11810.4534 | 13941.0463 | 16465.4435 | 19457.4496 | 23004.8208 | 27211.9165 | 32202.8572 | 38125.2846 | 45154.8394 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 |  | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.24202 | 0.32081 | 0.42897 | 0.5781 | 0.78458 | 1.0715 | 1.4716 | 2.031 | 2.8154 | 3.918 | 5.4709 | 7.6625 | 10.7606 |  | 3214.4021 | 3771.2024 | 4428.5903 | 5205.1507 | 6122.9504 | 7208.1948 | 8492.0118 | 10011.3826 | 11810.2512 | 13940.8441 | 16465.2413 | 19457.2474 | 23004.6186 | 27211.7143 | 32202.655 | 38125.0824 | 45154.6372 | 51357.2308 | 51357.152 | 51357.0439 | 51356.8948 | 51356.6883 | 51356.4013 | 51356.0013 | 51355.4419 | 51354.6574 | 51353.5549 | 51352.0019 | 51349.8104 | 51346.7123 |  | 11754.4401 | 13798.1414 | 16211.0431 | 19061.3607 | 22430.0878 | 26413.4108 | 31125.5821 | 36702.3393 | 43304.9761 | 51125.1861 | 60390.8308 | 71372.8054 | 84393.2133 | 99835.0996 | 118154.0408 | 139891.9465 | 165693.4951 | 188451.1031 | 188433.7363 | 188409.8971 | 188377.0257 | 188331.5149 | 188268.2719 | 188180.0953 | 188056.7876 | 187883.8897 | 187640.877 | 187298.5848 | 186815.5327 | 186132.6764
| TRUE | 4369 | 22004354 | TYA | TYA-BLTS | 66 | BLTS LINE | PILOT WIRE | X | SEC | GROUP_3385 | GROUP 3385 | GROUP 3000s | Electronic |  | 0.15703 | 2190 |  | 9.9 | 0.042792 | 0.015079 | 0.027713 | 465.1499 | 6634.8055 | 7099.9554 | 207.0778 | 17.2719 | 2742.735 |  | 17.778 | 0.21751 | 0.076646 | 0.14086 | 2364.3101 | 33724.0498 | 36088.3599 | 1052.5559 | 87.7913 | 13941.0463 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.2022 |  | 10067.0401 | 51169.7534 | 71.6996 | 51098.0538 |  | 0.058543 |  | 10.4969 | 11.1297 | 11.8008 | 12.5122 | 13.2666 | 14.0664 | 14.9145 | 15.8137 | 16.7671 | 17.778 | 18.8499 | 19.9863 | 21.1913 | 22.4689 | 23.8236 | 25.2599 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.050154 | 0.058841 | 0.069098 | 0.081214 | 0.095533 | 0.11247 | 0.1325 | 0.1562 | 0.18427 | 0.21751 | 0.25689 | 0.30357 | 0.35892 | 0.42456 | 0.50243 | 0.59483 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.017673 | 0.020735 | 0.024349 | 0.028618 | 0.033664 | 0.039631 | 0.046689 | 0.055042 | 0.064932 | 0.076646 | 0.090524 | 0.10697 | 0.12648 | 0.14961 | 0.17705 | 0.20961 | 0.24825 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 0.28235 | 11799.0075 | 13842.7088 | 16255.6105 | 19105.928 | 22474.6552 | 26457.9782 | 31170.1495 | 36746.9067 | 43349.5434 | 51169.7534 | 60435.3982 | 71417.3728 | 84437.7807 | 99879.667 | 118198.6082 | 139936.5139 | 165738.0625 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 | 188504.4474 |  | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 53.352 | 70.7213 | 94.5639 | 127.44 | 172.9574 | 236.2095 | 324.3988 | 447.7244 | 620.6472 | 863.6948 | 1206.0364 | 1689.158 | 2372.1127 |  | 545.1758 | 639.6055 | 751.0942 | 882.7938 | 1038.4466 | 1222.4969 | 1440.2239 | 1697.8992 | 2002.9756 | 2364.3101 | 2792.4314 | 3299.856 | 3901.4669 | 4614.9628 | 5461.3937 | 6465.7986 | 7657.965 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 | 8709.891 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 518.0436 | 612.4733 | 723.9619 | 855.6615 | 1011.3143 | 1195.3647 | 1413.0916 | 1670.767 | 1975.8433 | 2337.1779 | 2765.2991 | 3272.7238 | 3874.3347 | 4587.8306 | 5434.2614 | 6438.6663 | 7630.8328 | 8677.4154 | 8666.8427 | 8652.3296 | 8632.3178 | 8604.6112 | 8566.1093 | 8512.4282 | 8437.3594 | 8332.1006 | 8184.1565 | 7975.7719 | 7681.6938 | 7265.9765 |  | 7776.2797 | 9123.206 | 10713.4582 | 12591.9948 | 14812.1955 | 17437.4531 | 20543.067 | 24218.4968 | 28570.0451 | 33724.0498 | 39830.6859 | 47068.4901 | 55649.7487 | 65826.9121 | 77900.2336 | 92226.8653 | 109231.6905 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 | 124236.154 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 7775.7906 | 9122.7169 | 10712.9691 | 12591.5057 | 14811.7063 | 17436.9639 | 20542.5778 | 24218.0077 | 28569.5559 | 33723.5607 | 39830.1968 | 47068.001 | 55649.2596 | 65826.423 | 77899.7445 | 92226.3762 | 109231.2014 | 124235.5686 | 124235.378 | 124235.1163 | 124234.7556 | 124234.2561 | 124233.562 | 124232.5942 | 124231.2409 | 124229.3434 | 124226.6763 | 124222.9196 | 124217.6181 | 124210.1237 |  | 8293.8342 | 9735.1901 | 11436.9311 | 13447.1672 | 15823.0207 | 18632.3286 | 21955.6695 | 25888.7747 | 30545.3992 | 36060.7386 | 42595.4959 | 50340.7248 | 59523.5943 | 70414.2535 | 83334.0059 | 98665.0425 | 116862.0341 | 132912.984 | 132902.2207 | 132887.4459 | 132867.0733 | 132838.8672 | 132799.6713 | 132745.0224 | 132668.6004 | 132561.444 | 132410.8328 | 132198.6915 | 131899.3119 | 131476.1003 |  | 242.7042 | 284.7429 | 334.376 | 393.0067 | 462.3011 | 544.2375 | 641.1664 | 755.8796 | 891.6951 | 1052.5559 | 1243.1491 | 1469.0471 | 1736.8754 | 2054.5132 | 2431.3317 | 2878.4779 | 3409.2128 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 228.0281 | 270.0668 | 319.6999 | 378.3306 | 447.625 | 529.5615 | 626.4903 | 741.2035 | 877.019 | 1037.8798 | 1228.473 | 1454.371 | 1722.1993 | 2039.8371 | 2416.6556 | 2863.8018 | 3394.5367 | 3859.9483 | 3854.2294 | 3846.3791 | 3835.5545 | 3820.5678 | 3799.7417 | 3770.7051 | 3730.0997 | 3673.1642 | 3593.1398 | 3480.4225 | 3321.3528 | 3096.4873 |  | 20.2434 | 23.7498 | 27.8896 | 32.7798 | 38.5595 | 45.3936 | 53.4783 | 63.0462 | 74.3743 | 87.7913 | 103.6883 | 122.5299 | 144.8689 | 171.3624 | 202.792 | 240.0874 | 284.3548 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 18.1757 | 21.6821 | 25.8219 | 30.7121 | 36.4918 | 43.3259 | 51.4106 | 60.9785 | 72.3066 | 85.7236 | 101.6206 | 120.4622 | 142.8012 | 169.2947 | 200.7243 | 238.0197 | 282.2871 | 320.9399 | 320.1342 | 319.0282 | 317.5031 | 315.3917 | 312.4575 | 308.3665 | 302.6457 | 294.6241 | 283.3495 | 267.4689 | 245.0577 | 213.3766 |  | 3214.6043 | 3771.4046 | 4428.7925 | 5205.3529 | 6123.1526 | 7208.397 | 8492.214 | 10011.5848 | 11810.4534 | 13941.0463 | 16465.4435 | 19457.4496 | 23004.8208 | 27211.9165 | 32202.8572 | 38125.2846 | 45154.8394 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 | 51357.4729 |  | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.24202 | 0.32081 | 0.42897 | 0.5781 | 0.78458 | 1.0715 | 1.4716 | 2.031 | 2.8154 | 3.918 | 5.4709 | 7.6625 | 10.7606 |  | 3214.4021 | 3771.2024 | 4428.5903 | 5205.1507 | 6122.9504 | 7208.1948 | 8492.0118 | 10011.3826 | 11810.2512 | 13940.8441 | 16465.2413 | 19457.2474 | 23004.6186 | 27211.7143 | 32202.655 | 38125.0824 | 45154.6372 | 51357.2308 | 51357.152 | 51357.0439 | 51356.8948 | 51356.6883 | 51356.4013 | 51356.0013 | 51355.4419 | 51354.6574 | 51353.5549 | 51352.0019 | 51349.8104 | 51346.7123 |  | 11754.4401 | 13798.1414 | 16211.0431 | 19061.3607 | 22430.0878 | 26413.4108 | 31125.5821 | 36702.3393 | 43304.9761 | 51125.1861 | 60390.8308 | 71372.8054 | 84393.2133 | 99835.0996 | 118154.0408 | 139891.9465 | 165693.4951 | 188451.1031 | 188433.7363 | 188409.8971 | 188377.0257 | 188331.5149 | 188268.2719 | 188180.0953 | 188056.7876 | 187883.8897 | 187640.877 | 187298.5848 | 186815.5327 | 186132.6764
| TRUE | 4370 | 22004356 | TYA | TYA-BLTS | 66 | BLTS LINE | AUTO RECLOSE | Blank | LOCUS | LAR_3156 | LAR 3156 | LAR | Electronic |  | 0.15703 | 2190 |  | 5.5 | 0.0093284 | 0.0032871 | 0.0060412 | 101.3994 | 1446.3414 | 1547.7409 | 45.1415 | 3.7652 | 597.8971 |  | 8.8015 | 0.031208 | 0.010997 | 0.020211 | 339.2359 | 4838.7928 | 5178.0286 | 151.0228 | 12.5965 | 2000.2887 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.2022 |  | 2194.5447 | 7341.9366 | 71.6996 | 7270.2369 |  | 0.047018 |  | 5.7648 | 6.0423 | 6.3332 | 6.6381 | 6.9576 | 7.2926 | 7.6436 | 8.0116 | 8.3973 | 8.8015 | 9.2252 | 9.6693 | 10.1348 | 10.6227 | 11.1341 | 11.6701 | 12.2319 | 12.8207 | 13.4379 | 14.0848 | 14.7629 | 15.4736 | 16.2185 | 16.9993 | 17.8176 | 18.6754 | 19.5744 | 20.5167 | 21.5044 | 22.5396 |  | 0.010477 | 0.011781 | 0.013261 | 0.014944 | 0.016856 | 0.019033 | 0.02151 | 0.024331 | 0.027545 | 0.031208 | 0.035387 | 0.040154 | 0.045595 | 0.051808 | 0.058904 | 0.067014 | 0.076283 | 0.086882 | 0.099006 | 0.11288 | 0.12875 | 0.14693 | 0.16774 | 0.19158 | 0.21889 | 0.25018 | 0.28605 | 0.32717 | 0.37433 | 0.42841 |  | 0.0036919 | 0.0041513 | 0.004673 | 0.0052658 | 0.0059399 | 0.0067067 | 0.0075796 | 0.0085736 | 0.0097062 | 0.010997 | 0.01247 | 0.014149 | 0.016067 | 0.018256 | 0.020757 | 0.023614 | 0.026881 | 0.030616 | 0.034888 | 0.039776 | 0.04537 | 0.051774 | 0.059108 | 0.067507 | 0.077131 | 0.088159 | 0.1008 | 0.11529 | 0.13191 | 0.15096 | 2464.7586 | 2771.4441 | 3119.7405 | 3515.5305 | 3965.549 | 4477.5089 | 5060.2449 | 5723.8791 | 6480.011 | 7341.9366 | 8324.8985 | 9446.3753 | 10726.4129 | 12188.0052 | 13857.5332 | 15765.2679 | 17945.9497 | 20439.454 | 23291.5573 | 26554.8169 | 30289.5836 | 34565.1662 | 39461.17 | 45069.0375 | 51493.8197 | 58856.2141 | 67294.9085 | 76969.2784 | 88062.4889 | 100785.0643 |  | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 53.352 | 70.7213 | 94.5639 | 127.44 | 172.9574 | 236.2095 | 324.3988 | 447.7244 | 620.6472 | 863.6948 | 1206.0364 | 1689.158 | 2372.1127 |  | 113.8847 | 128.0552 | 144.1483 | 162.4359 | 183.2291 | 206.8843 | 233.8098 | 264.4731 | 299.4104 | 339.2359 | 384.6538 | 436.4719 | 495.6164 | 563.1496 | 640.2905 | 728.4378 | 829.1967 | 944.4096 | 1076.1917 | 1226.9714 | 1399.5371 | 1597.0914 | 1823.3124 | 2082.4252 | 2379.2837 | 2719.4648 | 3109.3766 | 3556.3831 | 4068.9474 | 4656.7969 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 86.7525 | 100.923 | 117.0161 | 135.3036 | 156.0969 | 179.7521 | 206.6775 | 237.3409 | 272.2781 | 312.1036 | 357.5216 | 409.3397 | 468.4841 | 536.0173 | 613.1582 | 701.3056 | 802.0645 | 911.934 | 1033.1434 | 1169.4099 | 1321.9639 | 1491.8115 | 1679.5307 | 1884.9623 | 2106.7521 | 2341.6744 | 2583.6421 | 2822.2639 | 3040.7502 | 3212.8824 |  | 1624.4292 | 1826.554 | 2056.103 | 2316.9532 | 2613.5434 | 2950.9568 | 3335.0161 | 3772.3923 | 4270.7303 | 4838.7928 | 5486.6258 | 6225.7488 | 7069.3732 | 8032.6534 | 9132.9762 | 10390.292 | 11827.4969 | 13470.8713 | 15350.5848 | 17501.2758 | 19962.7193 | 22780.5941 | 26007.3651 | 29703.2986 | 33937.6296 | 38789.9053 | 44351.5298 | 50727.5412 | 58038.6568 | 66423.6252 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 1623.9401 | 1826.0649 | 2055.6139 | 2316.4641 | 2613.0543 | 2950.4677 | 3334.527 | 3771.9031 | 4270.2411 | 4838.3037 | 5486.1367 | 6225.2597 | 7068.884 | 8032.1643 | 9132.4871 | 10389.8029 | 11827.0078 | 13470.2859 | 15349.8087 | 17500.2381 | 19961.3209 | 22778.6962 | 26004.7731 | 29699.7388 | 33932.7165 | 38783.0947 | 44342.0521 | 50714.3068 | 58020.1209 | 66397.5949 |  | 1710.6926 | 1926.9878 | 2172.6299 | 2451.7677 | 2769.1511 | 3130.2198 | 3541.2045 | 4009.244 | 4542.5193 | 5150.4073 | 5843.6583 | 6634.5994 | 7537.3681 | 8568.1816 | 9745.6453 | 11091.1084 | 12629.0722 | 14382.2199 | 16382.9521 | 18669.648 | 21283.2847 | 24270.5077 | 27684.3038 | 31584.7011 | 36039.4686 | 41124.7691 | 46925.6942 | 53536.5707 | 61060.8711 | 69610.4773 |  | 50.6998 | 57.0083 | 64.1727 | 72.3141 | 81.5709 | 92.1018 | 104.0887 | 117.7395 | 133.2931 | 151.0228 | 171.2422 | 194.3108 | 220.6411 | 250.7059 | 285.0479 | 324.2897 | 369.1461 | 420.4372 | 479.1046 | 546.2295 | 623.0532 | 711.0015 | 811.7117 | 927.0649 | 1059.2219 | 1210.6655 | 1384.2485 | 1583.2491 | 1811.4352 | 2073.1371 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 36.0237 | 42.3322 | 49.4966 | 57.638 | 66.8948 | 77.4257 | 89.4126 | 103.0634 | 118.617 | 136.3467 | 156.5661 | 179.6348 | 205.965 | 236.0298 | 270.3718 | 309.6136 | 354.47 | 402.8708 | 455.8194 | 515.094 | 581.0931 | 654.0546 | 733.9388 | 820.2553 | 911.8069 | 1006.315 | 1099.8736 | 1186.1569 | 1255.2733 | 1292.1097 |  | 4.2288 | 4.7549 | 5.3525 | 6.0316 | 6.8036 | 7.682 | 8.6818 | 9.8204 | 11.1177 | 12.5965 | 14.2829 | 16.207 | 18.4032 | 20.9108 | 23.7752 | 27.0483 | 30.7897 | 35.0677 | 39.961 | 45.5598 | 51.9675 | 59.303 | 67.7031 | 77.3244 | 88.3473 | 100.9789 | 115.4571 | 132.0553 | 151.0878 | 172.9157 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 2.1611 | 2.6872 | 3.2848 | 3.9639 | 4.7359 | 5.6143 | 6.6141 | 7.7527 | 9.05 | 10.5288 | 12.2152 | 14.1393 | 16.3355 | 18.8431 | 21.7075 | 24.9806 | 28.722 | 32.5928 | 36.6804 | 41.1731 | 46.0558 | 51.2798 | 56.7457 | 62.2761 | 67.5782 | 72.1881 | 75.3918 | 76.1093 | 72.7306 | 62.8775 |  | 671.5161 | 755.0716 | 849.964 | 957.7958 | 1080.402 | 1219.8839 | 1378.6486 | 1559.4537 | 1765.4596 | 2000.2887 | 2268.0937 | 2573.6367 | 2922.3791 | 3320.5856 | 3775.4435 | 4295.2001 | 4889.3203 | 5568.6681 | 6345.7151 | 7234.7804 | 8252.3065 | 9417.1761 | 10751.0777 | 12278.9245 | 14029.3372 | 16035.1995 | 18334.2965 | 20970.0497 | 23992.3617 | 27458.5893 |  | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.24202 | 0.32081 | 0.42897 | 0.5781 | 0.78458 | 1.0715 | 1.4716 | 2.031 | 2.8154 | 3.918 | 5.4709 | 7.6625 | 10.7606 |  | 671.3139 | 754.8694 | 849.7618 | 957.5936 | 1080.1998 | 1219.6817 | 1378.4464 | 1559.2515 | 1765.2574 | 2000.0865 | 2267.8915 | 2573.4345 | 2922.1769 | 3320.3834 | 3775.2413 | 4294.9979 | 4889.1181 | 5568.4261 | 6345.3943 | 7234.3515 | 8251.7284 | 9416.3916 | 10750.0062 | 12277.4529 | 14027.3062 | 16032.384 | 18330.3786 | 20964.5788 | 23984.6992 | 27447.8287 |  | 2420.1912 | 2726.8767 | 3075.1731 | 3470.9631 | 3920.9816 | 4432.9416 | 5015.6775 | 5679.3117 | 6435.4437 | 7297.3692 | 8280.3311 | 9401.808 | 10681.8455 | 12143.4379 | 13812.9659 | 15720.7005 | 17901.3823 | 20386.1097 | 23220.8462 | 26460.2666 | 30162.162 | 34392.2337 | 39224.9945 | 44744.6854 | 51046.1598 | 58235.6563 | 66431.3381 | 75763.4157 | 86373.5742 | 98413.2933
| TRUE | 4371 | 22004355 | TYA | TYA-BLTS | 66 | BLTS LINE | DISTANCE | Y | Mitsubishi | MDTA2_3204 | MDTA2 3204 | MDTA2 | Electronic |  | 0.016937 | 2190 |  | 5.5 | 0.0093284 | 0.00045834 | 0.00887 | 98.4292 | 201.6696 | 300.0988 | 29.0818 | 3.7369 | 83.3674 |  | 8.8015 | 0.031208 | 0.0015334 | 0.029675 | 329.2988 | 674.6937 | 1003.9925 | 97.2942 | 12.5018 | 278.9088 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 54.2635 | 0.052758 | 54.3162 | 14.6705 | 2.0677 | 0.021809 |  | 416.2848 | 1392.6974 | 71.0762 | 1321.6212 |  | 0.047018 |  | 5.7648 | 6.0423 | 6.3332 | 6.6381 | 6.9576 | 7.2926 | 7.6436 | 8.0116 | 8.3973 | 8.8015 | 9.2252 | 9.6693 | 10.1348 | 10.6227 | 11.1341 | 11.6701 | 12.2319 | 12.8207 | 13.4379 | 14.0848 | 14.7629 | 15.4736 | 16.2185 | 16.9993 | 17.8176 | 18.6754 | 19.5744 | 20.5167 | 21.5044 | 22.5396 |  | 0.010477 | 0.011781 | 0.013261 | 0.014944 | 0.016856 | 0.019033 | 0.02151 | 0.024331 | 0.027545 | 0.031208 | 0.035387 | 0.040154 | 0.045595 | 0.051808 | 0.058904 | 0.067014 | 0.076283 | 0.086882 | 0.099006 | 0.11288 | 0.12875 | 0.14693 | 0.16774 | 0.19158 | 0.21889 | 0.25018 | 0.28605 | 0.32717 | 0.37433 | 0.42841 |  | 0.00051478 | 0.00057883 | 0.00065157 | 0.00073423 | 0.00082822 | 0.00093515 | 0.0010569 | 0.0011955 | 0.0013534 | 0.0015334 | 0.0017387 | 0.0019729 | 0.0022403 | 0.0025455 | 0.0028942 | 0.0032926 | 0.0037481 | 0.0042689 | 0.0048645 | 0.0055461 | 0.0063261 | 0.0072191 | 0.0082416 | 0.0094129 | 0.010755 | 0.012292 | 0.014055 | 0.016075 | 0.018392 | 0.021049 | 467.5419 | 525.7173 | 591.7859 | 666.8636 | 752.2279 | 849.342 | 959.8816 | 1085.7669 | 1229.1981 | 1392.6974 | 1579.1562 | 1791.8899 | 2034.7012 | 2311.9517 | 2628.6457 | 2990.5253 | 3404.1805 | 3877.1752 | 4418.1927 | 5037.2029 | 5745.6535 | 6556.6919 | 7485.4185 | 8549.1791 | 9767.9008 | 11164.4788 | 12765.221 | 14600.3594 | 16704.6387 | 19117.9934 |  | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 43.9451 | 52.5996 | 69.7239 | 93.2303 | 125.6427 | 170.5181 | 232.8781 | 319.8236 | 441.4098 | 611.8938 | 851.5136 | 1189.0269 | 1665.3348 | 2338.6574 |  | 110.5488 | 124.3042 | 139.9259 | 157.6777 | 177.8619 | 200.8242 | 226.9609 | 256.7261 | 290.6399 | 329.2988 | 373.3864 | 423.6866 | 481.0985 | 546.6535 | 621.5348 | 707.1001 | 804.9075 | 916.7456 | 1044.6674 | 1191.0304 | 1358.5412 | 1550.3087 | 1769.9031 | 2021.4258 | 2309.5886 | 2639.805 | 3018.2953 | 3452.2079 | 3949.7579 | 4520.3878 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 83.417 | 97.1724 | 112.7941 | 130.546 | 150.7301 | 173.6924 | 199.8292 | 229.5943 | 263.5082 | 302.1671 | 346.2547 | 396.5549 | 453.9668 | 519.5218 | 594.4031 | 679.9683 | 777.7758 | 884.2706 | 1001.6199 | 1133.47 | 1280.9695 | 1445.0308 | 1626.1241 | 1823.9667 | 2037.0622 | 2262.0218 | 2492.5709 | 2718.1028 | 2921.5804 | 3076.5011 |  | 226.5011 | 254.6843 | 286.6913 | 323.0627 | 364.4176 | 411.4646 | 465.0156 | 526.0009 | 595.4863 | 674.6937 | 765.0238 | 868.0829 | 985.7131 | 1120.0274 | 1273.4501 | 1448.763 | 1649.1587 | 1878.3014 | 2140.398 | 2440.278 | 2783.4877 | 3176.3961 | 3626.3186 | 4141.6585 | 4732.0694 | 5408.6431 | 6184.1243 | 7073.1589 | 8092.5792 | 9261.7313 |  | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.052758 | 0.063148 | 0.083706 | 0.11193 | 0.15084 | 0.20471 | 0.27958 | 0.38396 | 0.52993 | 0.7346 | 1.0223 | 1.4275 | 1.9993 | 2.8076 |  | 226.4484 | 254.6315 | 286.6385 | 323.01 | 364.3648 | 411.4118 | 464.9629 | 525.9481 | 595.4335 | 674.6409 | 764.971 | 868.0301 | 985.6603 | 1119.9746 | 1273.3973 | 1448.7103 | 1649.1059 | 1878.2383 | 2140.3142 | 2440.1661 | 2783.3368 | 3176.1914 | 3626.039 | 4141.2745 | 4731.5395 | 5407.9085 | 6183.102 | 7071.7314 | 8090.5799 | 9258.9237 |  | 309.8654 | 351.8039 | 399.4326 | 453.556 | 515.095 | 585.1043 | 664.792 | 755.5424 | 858.9417 | 976.808 | 1111.2257 | 1264.585 | 1439.6271 | 1639.4964 | 1867.8004 | 2128.6786 | 2426.8817 | 2762.5089 | 3141.9342 | 3573.6361 | 4064.3063 | 4621.2222 | 5252.1631 | 5965.2412 | 6768.6017 | 7669.9303 | 8675.6729 | 9789.8342 | 11012.1603 | 12335.4247 |  | 32.6626 | 36.7268 | 41.3423 | 46.5873 | 52.5509 | 59.3353 | 67.0576 | 75.852 | 85.8721 | 97.2942 | 110.3203 | 125.182 | 142.1448 | 161.5136 | 183.638 | 208.919 | 237.817 | 270.8606 | 308.6562 | 351.9005 | 401.393 | 458.0524 | 522.9335 | 597.2482 | 682.3884 | 779.9538 | 891.7821 | 1019.9854 | 1166.9909 | 1335.5886 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 17.9921 | 22.0563 | 26.6719 | 31.9168 | 37.8804 | 44.6648 | 52.3871 | 61.1815 | 71.2017 | 82.6238 | 95.6498 | 110.5115 | 127.4744 | 146.8432 | 168.9675 | 194.2485 | 223.1466 | 253.301 | 285.3799 | 320.7769 | 359.449 | 401.1274 | 445.1904 | 490.4795 | 535.03 | 575.6816 | 607.5163 | 623.0455 | 611.0424 | 554.8608 |  | 4.197 | 4.7192 | 5.3123 | 5.9862 | 6.7525 | 7.6243 | 8.6166 | 9.7466 | 11.0342 | 12.5018 | 14.1756 | 16.0853 | 18.2649 | 20.7537 | 23.5966 | 26.8451 | 30.5583 | 34.8043 | 39.6608 | 45.2175 | 51.577 | 58.8575 | 67.1944 | 76.7435 | 87.6836 | 100.2202 | 114.5896 | 131.0631 | 149.9526 | 171.6166 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 2.1293 | 2.6515 | 3.2446 | 3.9185 | 4.6848 | 5.5566 | 6.5489 | 7.6789 | 8.9665 | 10.4341 | 12.1079 | 14.0176 | 16.1972 | 18.686 | 21.5289 | 24.7774 | 28.4906 | 32.3294 | 36.3802 | 40.8309 | 45.6653 | 50.8343 | 56.2371 | 61.6952 | 66.9145 | 71.4296 | 74.5245 | 75.1174 | 71.5959 | 61.5789 |  | 93.6324 | 105.2829 | 118.5141 | 133.5496 | 150.6451 | 170.0937 | 192.2309 | 217.4413 | 246.1656 | 278.9088 | 316.25 | 358.8532 | 407.4799 | 463.0035 | 526.4263 | 598.8982 | 681.7389 | 776.4633 | 884.8103 | 1008.7765 | 1150.6545 | 1313.0773 | 1499.0689 | 1712.1032 | 1956.1707 | 2235.8567 | 2556.4297 | 2923.9441 | 3345.358 | 3828.669 |  | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.021809 | 0.026104 | 0.034603 | 0.046269 | 0.062354 | 0.084625 | 0.11557 | 0.15872 | 0.21906 | 0.30367 | 0.42259 | 0.59009 | 0.82648 | 1.1606 |  | 93.6106 | 105.2611 | 118.4923 | 133.5278 | 150.6233 | 170.0718 | 192.2091 | 217.4195 | 246.1438 | 278.887 | 316.2282 | 358.8314 | 407.4581 | 462.9817 | 526.4045 | 598.8764 | 681.7171 | 776.4372 | 884.7757 | 1008.7302 | 1150.5922 | 1312.9927 | 1498.9534 | 1711.9444 | 1955.9517 | 2235.553 | 2556.0071 | 2923.354 | 3344.5315 | 3827.5084 |  | 423.5974 | 481.7728 | 547.8414 | 622.9191 | 708.2835 | 805.3975 | 915.9371 | 1041.8224 | 1185.2536 | 1348.7529 | 1535.2117 | 1747.9455 | 1990.7567 | 2268.0073 | 2584.7013 | 2946.5809 | 3360.236 | 3824.5764 | 4348.47 | 4943.9741 | 5620.0128 | 6386.1765 | 7252.5441 | 8229.3605 | 9326.4979 | 10552.5946 | 11913.7208 | 13411.3512 | 15039.3301 | 16779.3728
| TRUE | 4372 | 22004353 | TYA | TYA-BLTS | 66 | BLTS LINE | DISTANCE | X | ABB | RAZOA_3207 | RAZOA 3207 | RAZOG | Electronic |  | 0.15703 | 2190 |  | 6.6 | 0.014726 | 0.0051892 | 0.0095369 | 160.0721 | 2283.2371 | 2443.3092 | 71.2617 | 5.9438 | 943.858 |  | 10.9462 | 0.056226 | 0.019813 | 0.036413 | 611.1777 | 8717.7177 | 9328.8955 | 272.0873 | 22.6942 | 3603.7815 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 54.2645 | 0.48913 | 54.7536 | 14.6761 | 2.0677 | 0.2022 |  | 3464.3727 | 13227.4584 | 71.6996 | 13155.7588 |  | 0.050592 |  | 6.9425 | 7.3028 | 7.6817 | 8.0804 | 8.4997 | 8.9408 | 9.4048 | 9.8928 | 10.4062 | 10.9462 | 11.5143 | 12.1118 | 12.7403 | 13.4015 | 14.0969 | 14.8285 | 15.598 | 16.4074 | 17.2589 | 18.1545 | 19.0966 | 20.0876 | 21.1301 | 22.2266 | 23.38 | 24.5933 | 25.8696 | 27.212 | 28 | 28 |  | 0.016762 | 0.019102 | 0.021791 | 0.024884 | 0.028444 | 0.032543 | 0.037265 | 0.042708 | 0.048985 | 0.056226 | 0.064584 | 0.074234 | 0.08538 | 0.09826 | 0.11315 | 0.13036 | 0.15027 | 0.17331 | 0.19998 | 0.23085 | 0.26659 | 0.30799 | 0.35596 | 0.41154 | 0.47596 | 0.55065 | 0.63725 | 0.73768 | 0.80128 | 0.80128 |  | 0.0059068 | 0.0067311 | 0.0076788 | 0.0087687 | 0.010023 | 0.011468 | 0.013132 | 0.01505 | 0.017261 | 0.019813 | 0.022758 | 0.026158 | 0.030086 | 0.034625 | 0.039871 | 0.045937 | 0.052954 | 0.061072 | 0.070468 | 0.081345 | 0.093941 | 0.10853 | 0.12543 | 0.14502 | 0.16772 | 0.19404 | 0.22455 | 0.25994 | 0.28235 | 0.28235 | 3943.4413 | 4493.8054 | 5126.4638 | 5854.1493 | 6691.6055 | 7655.9087 | 8766.8417 | 10047.3275 | 11523.9339 | 13227.4584 | 15193.6093 | 17463.7958 | 20086.0468 | 23116.0782 | 26618.5337 | 30668.4267 | 35352.8161 | 40772.7548 | 47045.554 | 54307.4166 | 62716.498 | 72456.465 | 83740.6343 | 96816.7843 | 111972.7507 | 129542.9336 | 149915.8649 | 173543.0093 | 188504.4474 | 188504.4474 |  | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 44.5738 | 53.352 | 70.7213 | 94.5639 | 127.44 | 172.9574 | 236.2095 | 324.3988 | 447.7244 | 620.6472 | 863.6948 | 1206.0364 | 1689.158 | 2372.1127 |  | 182.2076 | 207.6373 | 236.8694 | 270.4923 | 309.1872 | 353.743 | 405.0739 | 464.2391 | 532.466 | 611.1777 | 702.0242 | 806.9187 | 928.0804 | 1068.0837 | 1229.9154 | 1417.0417 | 1633.4849 | 1883.9144 | 2173.7506 | 2509.2866 | 2897.8301 | 3347.8675 | 3869.2551 | 4473.4416 | 5173.7265 | 5985.5608 | 6926.8968 | 8018.5944 | 8709.891 | 8709.891 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 155.0754 | 180.5051 | 209.7372 | 243.3601 | 282.0549 | 326.6108 | 377.9417 | 437.1068 | 505.3337 | 584.0455 | 674.8919 | 779.7864 | 900.9481 | 1040.9514 | 1202.7832 | 1389.9094 | 1606.3527 | 1851.4388 | 2130.7022 | 2451.7251 | 2820.2568 | 3242.5876 | 3725.4734 | 4275.9788 | 4901.1949 | 5607.7704 | 6401.1623 | 7284.4752 | 7681.6938 | 7265.9765 |  | 2598.973 | 2961.6972 | 3378.6585 | 3858.2485 | 4410.1842 | 5045.7199 | 5777.8939 | 6621.8137 | 7594.9891 | 8717.7177 | 10013.5334 | 11509.7275 | 13237.954 | 15234.9331 | 17543.2691 | 20212.4005 | 23299.7044 | 26871.7811 | 31005.9459 | 35791.965 | 41334.0725 | 47753.3165 | 55190.2859 | 63808.2819 | 73797.0063 | 85376.8496 | 98803.8783 | 114375.6359 | 124236.154 | 124236.154 |  | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.48913 | 0.58546 | 0.77606 | 1.0377 | 1.3985 | 1.8979 | 2.592 | 3.5598 | 4.9131 | 6.8107 | 9.4777 | 13.2344 | 18.5359 | 26.0303 |  | 2598.4839 | 2961.2081 | 3378.1693 | 3857.7593 | 4409.695 | 5045.2308 | 5777.4047 | 6621.3246 | 7594.5 | 8717.2286 | 10013.0443 | 11509.2384 | 13237.4649 | 15234.444 | 17542.78 | 20211.9114 | 23299.2153 | 26871.1956 | 31005.1698 | 35790.9273 | 41332.6741 | 47751.4186 | 55187.6938 | 63804.7221 | 73792.0932 | 85370.0389 | 98794.4006 | 114362.4014 | 124217.6181 | 124210.1237 |  | 2753.5593 | 3141.7131 | 3587.9065 | 4101.1194 | 4691.7499 | 5371.8416 | 6155.3464 | 7058.4314 | 8099.8337 | 9301.2741 | 10687.9363 | 12289.0248 | 14138.413 | 16275.3954 | 18745.5632 | 21601.8208 | 24905.568 | 28722.6345 | 33135.872 | 38242.6524 | 44152.9309 | 50994.0062 | 58913.1673 | 68080.7009 | 78693.2882 | 90977.8093 | 105195.5628 | 121646.8767 | 131899.3119 | 131476.1003 |  | 81.1161 | 92.4371 | 105.4508 | 120.4192 | 137.6456 | 157.4812 | 180.3329 | 206.6724 | 237.046 | 272.0873 | 312.5308 | 359.2283 | 413.1677 | 475.4951 | 547.5402 | 630.846 | 727.2033 | 838.6908 | 967.7216 | 1117.0973 | 1290.0711 | 1490.4211 | 1722.5352 | 1991.51 | 2303.2665 | 2664.6832 | 3083.752 | 3569.7596 | 3877.5147 | 3877.5147 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 66.44 | 77.761 | 90.7747 | 105.7431 | 122.9695 | 142.8051 | 165.6568 | 191.9963 | 222.3699 | 257.4112 | 297.8547 | 344.5522 | 398.4916 | 460.819 | 532.8641 | 616.1699 | 712.5272 | 821.1245 | 944.4363 | 1085.9617 | 1248.111 | 1433.4742 | 1644.7622 | 1884.7005 | 2155.8515 | 2460.3326 | 2799.3771 | 3172.6674 | 3321.3528 | 3096.4873 |  | 6.7657 | 7.71 | 8.7954 | 10.0439 | 11.4807 | 13.1352 | 15.0412 | 17.2381 | 19.7715 | 22.6942 | 26.0675 | 29.9624 | 34.4614 | 39.66 | 45.6691 | 52.6175 | 60.6544 | 69.9533 | 80.7155 | 93.1746 | 107.602 | 124.3127 | 143.6728 | 166.1074 | 192.1103 | 222.2553 | 257.2089 | 297.7457 | 323.4149 | 323.4149 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 4.698 | 5.6423 | 6.7277 | 7.9762 | 9.413 | 11.0674 | 12.9735 | 15.1704 | 17.7038 | 20.6265 | 23.9998 | 27.8947 | 32.3937 | 37.5923 | 43.6014 | 50.5498 | 58.5867 | 67.4784 | 77.4349 | 88.7879 | 101.6902 | 116.2895 | 132.7155 | 151.0591 | 171.3412 | 193.4645 | 217.1435 | 241.7997 | 245.0577 | 213.3766 |  | 1074.3788 | 1224.3238 | 1396.6897 | 1594.9455 | 1823.1079 | 2085.8294 | 2388.4998 | 2737.3643 | 3139.6613 | 3603.7815 | 4139.4534 | 4757.9589 | 5472.3834 | 6297.9064 | 7252.1399 | 8355.5211 | 9631.769 | 11108.4151 | 12817.4205 | 14795.8932 | 17086.9223 | 19740.5472 | 22814.8853 | 26377.4433 | 30506.641 | 35293.5848 | 40844.129 | 47281.2738 | 51357.4729 | 51357.4729 |  | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.2022 | 0.24202 | 0.32081 | 0.42897 | 0.5781 | 0.78458 | 1.0715 | 1.4716 | 2.031 | 2.8154 | 3.918 | 5.4709 | 7.6625 | 10.7606 |  | 1074.1766 | 1224.1216 | 1396.4875 | 1594.7433 | 1822.9057 | 2085.6272 | 2388.2976 | 2737.1621 | 3139.4591 | 3603.5793 | 4139.2512 | 4757.7567 | 5472.1812 | 6297.7042 | 7251.9377 | 8355.3189 | 9631.5668 | 11108.1731 | 12817.0997 | 14795.4643 | 17086.3442 | 19739.7626 | 22813.8138 | 26375.9717 | 30504.61 | 35290.7693 | 40840.211 | 47275.8029 | 51349.8104 | 51346.7123 |  | 3898.8739 | 4449.238 | 5081.8965 | 5809.5819 | 6647.0381 | 7611.3413 | 8722.2743 | 10002.7602 | 11479.3665 | 13182.891 | 15149.0419 | 17419.2285 | 20041.4794 | 23071.5108 | 26573.9664 | 30623.8593 | 35308.2488 | 40719.4104 | 46974.8429 | 54212.8663 | 62589.0763 | 72283.5325 | 83504.4588 | 96492.4322 | 111525.0908 | 128922.3758 | 149052.2945 | 172337.1467 | 186815.5327 | 186132.6764
| TRUE | 4373 | 22004365 | TYA | Blank | 66 | STN STN | 66KV/110V VT AUTO C/O | Blank | EMAIL | GROUP_2630 | GROUP 2630 | GROUP 2000s | Electronic |  | 0 | 2190 |  | 8.25 | 0.026286 | 0 | 0.026286 | 275.999 | 0 | 275.999 | 74.6148 | 10.5169 | 0 |  | 14.2947 | 0.11764 | 0 | 0.11764 | 1235.2445 | 0 | 1235.2445 | 333.9414 | 47.0687 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 361.1306 | 1616.2545 | 71.0008 | 1545.2537 |  | 0.054968 |  | 8.7162 | 9.2087 | 9.7291 | 10.2788 | 10.8596 | 11.4733 | 12.1216 | 12.8065 | 13.5302 | 14.2947 | 15.1025 | 15.9559 | 16.8575 | 17.8101 | 18.8164 | 19.8797 | 21.003 | 22.1898 | 23.4437 | 24.7684 | 26.168 | 27.6467 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.030409 | 0.035217 | 0.040826 | 0.047373 | 0.05502 | 0.063954 | 0.074399 | 0.086616 | 0.10091 | 0.11764 | 0.13724 | 0.16019 | 0.18709 | 0.21862 | 0.2556 | 0.29897 | 0.34986 | 0.40959 | 0.47971 | 0.56204 | 0.65873 | 0.77233 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417.7845 | 483.8387 | 560.8985 | 650.848 | 755.8993 | 878.6501 | 1022.1517 | 1189.9885 | 1386.3727 | 1616.2545 | 1885.453 | 2200.8092 | 2570.3674 | 3003.5881 | 3511.5987 | 4107.4891 | 4806.66 | 5627.2328 | 6590.533 | 7721.659 | 9050.1535 | 10610.7932 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 319.2975 | 369.7803 | 428.6743 | 497.4194 | 577.7063 | 671.5203 | 781.1933 | 909.4649 | 1059.5541 | 1235.2445 | 1440.983 | 1681.9983 | 1964.4382 | 2295.533 | 2683.7869 | 3139.2043 | 3673.5551 | 4300.689 | 5036.9042 | 5901.3826 | 6916.7026 | 8109.4426 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 292.1658 | 342.6487 | 401.5426 | 470.2877 | 550.5746 | 644.3886 | 754.0616 | 882.3332 | 1032.4225 | 1208.1128 | 1413.8513 | 1654.8666 | 1937.3065 | 2268.4013 | 2656.6553 | 3112.0726 | 3646.4234 | 4268.2141 | 4993.8568 | 5843.8224 | 6839.131 | 8004.165 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 292.1658 | 342.6487 | 401.5426 | 470.2877 | 550.5746 | 644.3886 | 754.0616 | 882.3332 | 1032.4225 | 1208.1128 | 1413.8513 | 1654.8666 | 1937.3065 | 2268.4013 | 2656.6553 | 3112.0726 | 3646.4234 | 4268.2141 | 4993.8568 | 5843.8224 | 6839.131 | 8004.165 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 86.3203 | 99.968 | 115.8897 | 134.4745 | 156.1796 | 181.5417 | 211.1912 | 245.8687 | 286.4445 | 333.9414 | 389.5617 | 454.7188 | 531.0748 | 620.5844 | 725.5467 | 848.6662 | 993.125 | 1162.6671 | 1361.6988 | 1595.4056 | 1869.8917 | 2192.3423 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 71.6505 | 85.2982 | 101.2199 | 119.8048 | 141.5099 | 166.8719 | 196.5214 | 231.1989 | 271.7747 | 319.2716 | 374.8919 | 440.049 | 516.405 | 605.9147 | 710.8769 | 833.9965 | 978.4552 | 1145.1083 | 1338.4235 | 1564.2835 | 1827.9496 | 2135.4198 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 12.1668 | 14.0904 | 16.3345 | 18.954 | 22.0134 | 25.5881 | 29.7672 | 34.6549 | 40.3741 | 47.0687 | 54.9083 | 64.0921 | 74.8544 | 87.4707 | 102.2651 | 119.6186 | 139.9799 | 163.8767 | 191.93 | 224.8708 | 263.5593 | 309.0084 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 10.0991 | 12.0227 | 14.2668 | 16.8864 | 19.9457 | 23.5204 | 27.6995 | 32.5873 | 38.3064 | 45.001 | 52.8406 | 62.0245 | 72.7868 | 85.403 | 100.1974 | 117.5509 | 137.9123 | 161.4018 | 188.6494 | 220.4841 | 257.6476 | 300.9852 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 373.9154 | 439.9696 | 517.0294 | 606.9788 | 712.0302 | 834.781 | 978.2825 | 1146.1194 | 1342.5036 | 1572.3854 | 1841.5838 | 2156.94 | 2526.4983 | 2959.719 | 3467.7296 | 4063.62 | 4762.7909 | 5574.7242 | 6520.9297 | 7628.59 | 8924.7282 | 10440.57 | 10776.0547 | 10689.2596 | 10567.8837 | 10397.6946 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| TRUE | 4374 | 22004358 | TYA | Blank | 66 | TRANS NO.1 | OVERCURRENT | Y | ASEA | GROUP_2602 | GROUP 2602 | GROUP 2000s | Electronic |  | 0.0068096 | 2190 |  | 8.25 | 0.026286 | 0.00052975 | 0.025756 | 276.5552 | 233.0884 | 509.6437 | 77.6223 | 10.5222 | 96.3555 |  | 14.2947 | 0.11764 | 0.0023709 | 0.11527 | 1237.7339 | 1043.1966 | 2280.9305 | 347.4016 | 47.0924 | 431.2428 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.0087684 |  | 694.1436 | 3106.6672 | 71.0311 | 3035.6361 |  | 0.054968 |  | 8.7162 | 9.2087 | 9.7291 | 10.2788 | 10.8596 | 11.4733 | 12.1216 | 12.8065 | 13.5302 | 14.2947 | 15.1025 | 15.9559 | 16.8575 | 17.8101 | 18.8164 | 19.8797 | 21.003 | 22.1898 | 23.4437 | 24.7684 | 26.168 | 27.6467 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.030409 | 0.035217 | 0.040826 | 0.047373 | 0.05502 | 0.063954 | 0.074399 | 0.086616 | 0.10091 | 0.11764 | 0.13724 | 0.16019 | 0.18709 | 0.21862 | 0.2556 | 0.29897 | 0.34986 | 0.40959 | 0.47971 | 0.56204 | 0.65873 | 0.77233 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00061285 | 0.00070975 | 0.00082279 | 0.00095474 | 0.0011088 | 0.0012889 | 0.0014994 | 0.0017456 | 0.0020337 | 0.0023709 | 0.0027658 | 0.0032284 | 0.0037705 | 0.004406 | 0.0051512 | 0.0060253 | 0.0070509 | 0.0082546 | 0.0096677 | 0.011327 | 0.013276 | 0.015565 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 803.0403 | 930.0057 | 1078.1253 | 1251.0208 | 1452.9441 | 1688.8884 | 1964.7184 | 2287.3243 | 2664.8022 | 3106.6672 | 3624.1042 | 4230.2629 | 4940.6056 | 5773.3163 | 6749.7837 | 7895.1684 | 9239.0726 | 10816.3283 | 12667.9259 | 14842.1083 | 17395.6605 | 20395.4281 | 21159.9341 | 21159.9341 | 21159.9341 | 21159.9341 | 21159.9341 | 21159.9341 | 21159.9341 | 21159.9341 |  | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 52.5452 | 69.6518 | 93.1338 | 125.5127 | 170.3418 | 232.6373 | 319.4929 | 440.9533 | 611.261 | 850.633 | 1187.7973 | 1663.6126 | 2336.2389 |  | 319.941 | 370.5255 | 429.5382 | 498.4219 | 578.8706 | 672.8736 | 782.7677 | 911.2977 | 1061.6895 | 1237.7339 | 1443.8871 | 1685.3881 | 1968.3972 | 2300.1592 | 2689.1957 | 3145.5308 | 3680.9586 | 4309.3564 | 5047.0553 | 5913.276 | 6930.6421 | 8125.7859 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 292.8093 | 343.3939 | 402.4065 | 471.2902 | 551.7389 | 645.7419 | 755.636 | 884.1661 | 1034.5578 | 1210.6022 | 1416.7554 | 1658.2564 | 1941.2655 | 2273.0276 | 2662.064 | 3118.3992 | 3653.8269 | 4276.8814 | 5004.0079 | 5855.7157 | 6853.0704 | 8020.5082 | 8286.5956 | 8232.9156 | 8157.8484 | 8052.5917 | 7904.6507 | 7696.2703 | 7402.1983 | 6986.4896 |  | 269.6552 | 312.2893 | 362.0268 | 420.0838 | 487.8882 | 567.1166 | 659.7384 | 768.0671 | 894.8215 | 1043.1966 | 1216.9483 | 1420.492 | 1659.02 | 1938.6383 | 2266.529 | 2651.141 | 3102.4144 | 3632.0456 | 4253.7988 | 4983.8737 | 5841.3382 | 6848.6387 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 269.634 | 312.268 | 362.0056 | 420.0626 | 487.867 | 567.0954 | 659.7172 | 768.0459 | 894.8003 | 1043.1754 | 1216.927 | 1420.4708 | 1658.9988 | 1938.6171 | 2266.5078 | 2651.1198 | 3102.3932 | 3632.0202 | 4253.7651 | 4983.8287 | 5841.2776 | 6848.5564 | 7105.2419 | 7105.2 | 7105.1413 | 7105.059 | 7104.9433 | 7104.7804 | 7104.5505 | 7104.2255 |  | 562.4433 | 655.6619 | 764.4121 | 891.3528 | 1039.6059 | 1212.8373 | 1415.3531 | 1652.212 | 1929.3581 | 2253.7776 | 2633.6824 | 3078.7272 | 3600.2643 | 4211.6446 | 4928.5718 | 5769.519 | 6756.2201 | 7908.9017 | 9257.773 | 10839.5444 | 12694.348 | 14869.0646 | 15391.8376 | 15338.1155 | 15262.9896 | 15157.6507 | 15009.594 | 14801.0507 | 14506.7488 | 14090.7151 |  | 89.7996 | 103.9974 | 120.5608 | 139.8948 | 162.4748 | 188.8591 | 219.7037 | 255.7789 | 297.9902 | 347.4016 | 405.2637 | 473.0471 | 552.4808 | 645.5983 | 754.7913 | 882.8734 | 1033.1548 | 1209.5307 | 1416.5847 | 1659.7116 | 1945.2613 | 2280.7089 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 75.1295 | 89.3274 | 105.8908 | 125.2247 | 147.8047 | 174.1891 | 205.0336 | 241.1089 | 283.3202 | 332.7315 | 390.5936 | 458.377 | 537.8108 | 630.9282 | 740.1212 | 868.2033 | 1018.4848 | 1191.9715 | 1393.309 | 1628.5888 | 1903.3184 | 2223.7854 | 2288.4584 | 2259.4337 | 2218.845 | 2161.9329 | 2081.9414 | 1969.2705 | 1810.2663 | 1585.4933 |  | 12.1729 | 14.0975 | 16.3428 | 18.9636 | 22.0244 | 25.601 | 29.7822 | 34.6724 | 40.3944 | 47.0924 | 54.936 | 64.1244 | 74.8922 | 87.5148 | 102.3166 | 119.6789 | 140.0505 | 163.9593 | 192.0267 | 224.984 | 263.6921 | 309.164 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 10.1052 | 12.0298 | 14.2751 | 16.8959 | 19.9568 | 23.5333 | 27.7145 | 32.6047 | 38.3267 | 45.0247 | 52.8683 | 62.0567 | 72.8245 | 85.4471 | 100.2489 | 117.6112 | 137.9828 | 161.4844 | 188.7461 | 220.5974 | 257.7804 | 301.1409 | 309.7955 | 305.7046 | 299.9837 | 291.9622 | 280.6877 | 264.8071 | 242.396 | 210.7151 |  | 111.4716 | 129.096 | 149.6568 | 173.6567 | 201.6861 | 234.438 | 272.7265 | 317.5081 | 369.9066 | 431.2428 | 503.0692 | 587.2113 | 685.8154 | 801.4057 | 936.9511 | 1095.9443 | 1282.4943 | 1501.4364 | 1758.4604 | 2060.2631 | 2414.7268 | 2831.1306 | 2937.2532 | 2937.2532 | 2937.2532 | 2937.2532 | 2937.2532 | 2937.2532 | 2937.2532 | 2937.2532 |  | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.010495 | 0.013912 | 0.018602 | 0.02507 | 0.034024 | 0.046466 | 0.063815 | 0.088075 | 0.12209 | 0.1699 | 0.23725 | 0.33229 | 0.46664 |  | 111.4629 | 129.0872 | 149.648 | 173.648 | 201.6773 | 234.4292 | 272.7178 | 317.4993 | 369.8978 | 431.234 | 503.0605 | 587.2026 | 685.8067 | 801.3969 | 936.9423 | 1095.9355 | 1282.4856 | 1501.4259 | 1758.4465 | 2060.2444 | 2414.7017 | 2831.0966 | 2937.2067 | 2937.1894 | 2937.1651 | 2937.1311 | 2937.0833 | 2937.016 | 2936.9209 | 2936.7866 |  | 759.1409 | 886.1063 | 1034.2259 | 1207.1214 | 1409.0447 | 1644.989 | 1920.819 | 2243.4249 | 2620.9028 | 3062.7678 | 3580.2048 | 4186.3635 | 4896.7062 | 5729.4169 | 6705.8843 | 7851.269 | 9195.1732 | 10763.7835 | 12598.2746 | 14748.9751 | 17270.1485 | 20225.0875 | 20927.2982 | 20840.4432 | 20718.9835 | 20548.6769 | 20309.3064 | 19972.1443 | 19496.332 | 18823.71
| TRUE | 4375 | 22004359 | TYA | Blank | 66 | TRANS NO.2 | OVERCURRENT | Y | ASEA | GROUP_2602 | GROUP 2602 | GROUP 2000s | Electronic |  | 0.0068096 | 2190 |  | 8.25 | 0.026286 | 0.00052975 | 0.025756 | 276.5552 | 233.0884 | 509.6437 | 77.6223 | 10.5222 | 96.3555 |  | 14.2947 | 0.11764 | 0.0023709 | 0.11527 | 1237.7339 | 1043.1966 | 2280.9305 | 347.4016 | 47.0924 | 431.2428 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.0087684 |  | 694.1436 | 3106.6672 | 71.0311 | 3035.6361 |  | 0.054968 |  | 8.7162 | 9.2087 | 9.7291 | 10.2788 | 10.8596 | 11.4733 | 12.1216 | 12.8065 | 13.5302 | 14.2947 | 15.1025 | 15.9559 | 16.8575 | 17.8101 | 18.8164 | 19.8797 | 21.003 | 22.1898 | 23.4437 | 24.7684 | 26.168 | 27.6467 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.030409 | 0.035217 | 0.040826 | 0.047373 | 0.05502 | 0.063954 | 0.074399 | 0.086616 | 0.10091 | 0.11764 | 0.13724 | 0.16019 | 0.18709 | 0.21862 | 0.2556 | 0.29897 | 0.34986 | 0.40959 | 0.47971 | 0.56204 | 0.65873 | 0.77233 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00061285 | 0.00070975 | 0.00082279 | 0.00095474 | 0.0011088 | 0.0012889 | 0.0014994 | 0.0017456 | 0.0020337 | 0.0023709 | 0.0027658 | 0.0032284 | 0.0037705 | 0.004406 | 0.0051512 | 0.0060253 | 0.0070509 | 0.0082546 | 0.0096677 | 0.011327 | 0.013276 | 0.015565 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 803.0403 | 930.0057 | 1078.1253 | 1251.0208 | 1452.9441 | 1688.8884 | 1964.7184 | 2287.3243 | 2664.8022 | 3106.6672 | 3624.1042 | 4230.2629 | 4940.6056 | 5773.3163 | 6749.7837 | 7895.1684 | 9239.0726 | 10816.3283 | 12667.9259 | 14842.1083 | 17395.6605 | 20395.4281 | 21159.9341 | 21159.9341 | 21159.9341 | 21159.9341 | 21159.9341 | 21159.9341 | 21159.9341 | 21159.9341 |  | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 43.8997 | 52.5452 | 69.6518 | 93.1338 | 125.5127 | 170.3418 | 232.6373 | 319.4929 | 440.9533 | 611.261 | 850.633 | 1187.7973 | 1663.6126 | 2336.2389 |  | 319.941 | 370.5255 | 429.5382 | 498.4219 | 578.8706 | 672.8736 | 782.7677 | 911.2977 | 1061.6895 | 1237.7339 | 1443.8871 | 1685.3881 | 1968.3972 | 2300.1592 | 2689.1957 | 3145.5308 | 3680.9586 | 4309.3564 | 5047.0553 | 5913.276 | 6930.6421 | 8125.7859 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 292.8093 | 343.3939 | 402.4065 | 471.2902 | 551.7389 | 645.7419 | 755.636 | 884.1661 | 1034.5578 | 1210.6022 | 1416.7554 | 1658.2564 | 1941.2655 | 2273.0276 | 2662.064 | 3118.3992 | 3653.8269 | 4276.8814 | 5004.0079 | 5855.7157 | 6853.0704 | 8020.5082 | 8286.5956 | 8232.9156 | 8157.8484 | 8052.5917 | 7904.6507 | 7696.2703 | 7402.1983 | 6986.4896 |  | 269.6552 | 312.2893 | 362.0268 | 420.0838 | 487.8882 | 567.1166 | 659.7384 | 768.0671 | 894.8215 | 1043.1966 | 1216.9483 | 1420.492 | 1659.02 | 1938.6383 | 2266.529 | 2651.141 | 3102.4144 | 3632.0456 | 4253.7988 | 4983.8737 | 5841.3382 | 6848.6387 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 269.634 | 312.268 | 362.0056 | 420.0626 | 487.867 | 567.0954 | 659.7172 | 768.0459 | 894.8003 | 1043.1754 | 1216.927 | 1420.4708 | 1658.9988 | 1938.6171 | 2266.5078 | 2651.1198 | 3102.3932 | 3632.0202 | 4253.7651 | 4983.8287 | 5841.2776 | 6848.5564 | 7105.2419 | 7105.2 | 7105.1413 | 7105.059 | 7104.9433 | 7104.7804 | 7104.5505 | 7104.2255 |  | 562.4433 | 655.6619 | 764.4121 | 891.3528 | 1039.6059 | 1212.8373 | 1415.3531 | 1652.212 | 1929.3581 | 2253.7776 | 2633.6824 | 3078.7272 | 3600.2643 | 4211.6446 | 4928.5718 | 5769.519 | 6756.2201 | 7908.9017 | 9257.773 | 10839.5444 | 12694.348 | 14869.0646 | 15391.8376 | 15338.1155 | 15262.9896 | 15157.6507 | 15009.594 | 14801.0507 | 14506.7488 | 14090.7151 |  | 89.7996 | 103.9974 | 120.5608 | 139.8948 | 162.4748 | 188.8591 | 219.7037 | 255.7789 | 297.9902 | 347.4016 | 405.2637 | 473.0471 | 552.4808 | 645.5983 | 754.7913 | 882.8734 | 1033.1548 | 1209.5307 | 1416.5847 | 1659.7116 | 1945.2613 | 2280.7089 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 75.1295 | 89.3274 | 105.8908 | 125.2247 | 147.8047 | 174.1891 | 205.0336 | 241.1089 | 283.3202 | 332.7315 | 390.5936 | 458.377 | 537.8108 | 630.9282 | 740.1212 | 868.2033 | 1018.4848 | 1191.9715 | 1393.309 | 1628.5888 | 1903.3184 | 2223.7854 | 2288.4584 | 2259.4337 | 2218.845 | 2161.9329 | 2081.9414 | 1969.2705 | 1810.2663 | 1585.4933 |  | 12.1729 | 14.0975 | 16.3428 | 18.9636 | 22.0244 | 25.601 | 29.7822 | 34.6724 | 40.3944 | 47.0924 | 54.936 | 64.1244 | 74.8922 | 87.5148 | 102.3166 | 119.6789 | 140.0505 | 163.9593 | 192.0267 | 224.984 | 263.6921 | 309.164 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 10.1052 | 12.0298 | 14.2751 | 16.8959 | 19.9568 | 23.5333 | 27.7145 | 32.6047 | 38.3267 | 45.0247 | 52.8683 | 62.0567 | 72.8245 | 85.4471 | 100.2489 | 117.6112 | 137.9828 | 161.4844 | 188.7461 | 220.5974 | 257.7804 | 301.1409 | 309.7955 | 305.7046 | 299.9837 | 291.9622 | 280.6877 | 264.8071 | 242.396 | 210.7151 |  | 111.4716 | 129.096 | 149.6568 | 173.6567 | 201.6861 | 234.438 | 272.7265 | 317.5081 | 369.9066 | 431.2428 | 503.0692 | 587.2113 | 685.8154 | 801.4057 | 936.9511 | 1095.9443 | 1282.4943 | 1501.4364 | 1758.4604 | 2060.2631 | 2414.7268 | 2831.1306 | 2937.2532 | 2937.2532 | 2937.2532 | 2937.2532 | 2937.2532 | 2937.2532 | 2937.2532 | 2937.2532 |  | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.0087684 | 0.010495 | 0.013912 | 0.018602 | 0.02507 | 0.034024 | 0.046466 | 0.063815 | 0.088075 | 0.12209 | 0.1699 | 0.23725 | 0.33229 | 0.46664 |  | 111.4629 | 129.0872 | 149.648 | 173.648 | 201.6773 | 234.4292 | 272.7178 | 317.4993 | 369.8978 | 431.234 | 503.0605 | 587.2026 | 685.8067 | 801.3969 | 936.9423 | 1095.9355 | 1282.4856 | 1501.4259 | 1758.4465 | 2060.2444 | 2414.7017 | 2831.0966 | 2937.2067 | 2937.1894 | 2937.1651 | 2937.1311 | 2937.0833 | 2937.016 | 2936.9209 | 2936.7866 |  | 759.1409 | 886.1063 | 1034.2259 | 1207.1214 | 1409.0447 | 1644.989 | 1920.819 | 2243.4249 | 2620.9028 | 3062.7678 | 3580.2048 | 4186.3635 | 4896.7062 | 5729.4169 | 6705.8843 | 7851.269 | 9195.1732 | 10763.7835 | 12598.2746 | 14748.9751 | 17270.1485 | 20225.0875 | 20927.2982 | 20840.4432 | 20718.9835 | 20548.6769 | 20309.3064 | 19972.1443 | 19496.332 | 18823.71
| FALSE | 4637 | 22014285 | WBE | Blank | 22 | BUS ALL | VOLTAGE REGULATION | C | RMS | 2V164S | 2V164 S | 2V164S | Digital |  | 0 | 1 |  | 1.1573 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 3.8384 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 30.9493 | 30.9493 | 0 |  | 0.11989 |  | 1.3047 | 1.4709 | 1.6583 | 1.8695 | 2.1077 | 2.3762 | 2.6788 | 3.0201 | 3.4047 | 3.8384 | 4.3274 | 4.8786 | 5.5 | 6.2006 | 6.9904 | 7.8808 | 8.8847 | 10.0164 | 11.2923 | 12.7306 | 14.3522 | 16.1804 | 18.2414 | 20.565 | 23.1845 | 26.1377 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0061857 | 0.0081995 | 0.010964 | 0.014776 | 0.020053 | 0.027386 | 0.037611 | 0.05191 | 0.071959 | 0.10014 | 0.13983 | 0.19584 | 0.27503 | 0.38713 | 0.54606 | 0.77164 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 125.7409 | 175.3373 | 245.2282 | 343.8976 | 483.4225 | 681.0073 | 961.1761 | 1358.9071 | 1924.1147 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7988 | 8.3368 | 15.9388 | 26.4209 | 40.9336 | 61.1008 | 89.2189 | 125.7409 | 175.3373 | 245.2282 | 343.8976 | 483.4225 | 681.0073 | 961.1761 | 1358.9071 | 1924.1147 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.889 | 8.6055 | 16.4524 | 27.2723 | 42.2526 | 63.0697 | 92.0939 | 129.7928 | 180.9874 | 253.1305 | 354.9794 | 499.0003 | 702.9521 | 992.149 | 1402.6966 | 1986.1174 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40721 | 1.2129 | 2.3189 | 3.844 | 5.9555 | 8.8896 | 12.9805 | 18.2942 | 25.51 | 35.6785 | 50.034 | 70.3336 | 99.0804 | 139.8424 | 197.7086 | 279.9412 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0951 | 18.1552 | 34.7101 | 57.5372 | 89.1417 | 133.0601 | 194.2933 | 273.8279 | 381.8347 | 534.0372 | 748.9109 | 1052.7564 | 1483.0397 | 2093.1675 | 2959.3123 | 4190.1734 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 4638 | 22004396 | WBE | Blank | 22 | BUS ALL | OV-UV SUPERVISION | Blank | EMAIL | GROUP_3066 | GROUP 3066 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 235.3564 | 0 | 235.3564 | 121.4703 | 17.1211 | 0 |  | 20.1542 | 0.31092 | 0 | 0.31092 | 1710.0365 | 0 | 1710.0365 | 882.5704 | 124.3974 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 373.9478 | 2717.0043 | 45.1611 | 2671.8431 |  | 0.071088 |  | 10.6294 | 11.4125 | 12.2533 | 13.1561 | 14.1254 | 15.1661 | 16.2834 | 17.4831 | 18.7712 | 20.1542 | 21.639 | 23.2333 | 24.945 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.051896 | 0.063029 | 0.076653 | 0.093338 | 0.11379 | 0.13887 | 0.16964 | 0.20743 | 0.25385 | 0.31092 | 0.38109 | 0.46742 | 0.57368 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.5085 | 550.7932 | 669.8476 | 815.6541 | 994.3516 | 1213.5054 | 1482.442 | 1812.6618 | 2218.3493 | 2717.0043 | 3330.2204 | 4084.6492 | 5013.1908 | 6156.4658 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 285.4306 | 346.6599 | 421.5907 | 513.3589 | 625.8281 | 763.7598 | 933.0239 | 1140.8586 | 1396.1915 | 1710.0365 | 2095.9844 | 2570.8091 | 3155.2174 | 3874.7754 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 271.2187 | 332.4481 | 407.3789 | 499.1471 | 611.6162 | 749.548 | 918.8121 | 1126.6468 | 1381.9797 | 1695.8247 | 2081.7725 | 2556.5973 | 3141.0056 | 3860.5636 | 4392.8169 | 4392.8169 | 4392.8169 | 4390.018 | 4384.48 | 4376.8781 | 4366.3959 | 4351.8833 | 4331.7161 | 4303.598 | 4264.2771 | 4209.1427 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 271.2187 | 332.4481 | 407.3789 | 499.1471 | 611.6162 | 749.548 | 918.8121 | 1126.6468 | 1381.9797 | 1695.8247 | 2081.7725 | 2556.5973 | 3141.0056 | 3860.5636 | 4392.8169 | 4392.8169 | 4392.8169 | 4390.018 | 4384.48 | 4376.8781 | 4366.3959 | 4351.8833 | 4331.7161 | 4303.598 | 4264.2771 | 4209.1427 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 147.3141 | 178.9154 | 217.588 | 264.9507 | 322.9974 | 394.1856 | 481.5448 | 588.8108 | 720.5912 | 882.5704 | 1081.7627 | 1326.8254 | 1628.4456 | 1999.8181 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 132.6444 | 164.2456 | 202.9183 | 250.2809 | 308.3276 | 379.5158 | 466.8751 | 574.1411 | 705.9214 | 867.9006 | 1067.0929 | 1312.1557 | 1613.7758 | 1985.1483 | 2259.8506 | 2259.8506 | 2259.8506 | 2256.9616 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 20.7638 | 25.2179 | 30.6688 | 37.3445 | 45.5261 | 55.5601 | 67.8732 | 82.9923 | 101.5666 | 124.3974 | 152.4733 | 187.0147 | 229.5277 | 281.8723 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 18.6961 | 23.1502 | 28.6011 | 35.2768 | 43.4585 | 53.4924 | 65.8056 | 80.9246 | 99.4989 | 122.3297 | 150.4056 | 184.947 | 227.46 | 279.8046 | 318.5236 | 318.5236 | 318.5236 | 318.1164 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 422.5592 | 519.8439 | 638.8983 | 784.7048 | 963.4023 | 1182.5561 | 1451.4927 | 1781.7125 | 2187.4 | 2686.055 | 3299.2711 | 4053.6999 | 4982.2415 | 6125.5165 | 6971.1911 | 6971.1911 | 6971.1911 | 6965.096 | 6953.0359 | 6936.481 | 6913.6539 | 6882.0494 | 6838.131 | 6776.8978 | 6691.2682 | 6571.2012 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| FALSE | 4639 | 22010142 | WBE | Blank | 22 | BUS ALL | POWER QUALITY | I | Schneider | ION_7650 | ION 7650 | ION 7000s | Digital |  | 0.033587 | 1 |  | 2.8514 | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.4961 |  | 9.4101 | 0.043865 | 2.0182e-06 | 0.043863 | 120.63 | 0.14128 | 120.7713 | 124.5281 | 17.5505 | 4.2109 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 14.2119 | 0.016644 | 14.2285 | 14.6711 | 2.0677 | 0.4961 |  | 31.4635 | 267.0607 | 31.4635 | 235.5972 |  | 0.1194 |  | 3.213 | 3.6205 | 4.0796 | 4.597 | 5.1799 | 5.8369 | 6.5771 | 7.4112 | 8.351 | 9.4101 | 10.6034 | 11.9482 | 13.4634 | 15.1708 | 17.0947 | 19.2626 | 21.7055 | 24.4581 | 27.5598 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0054038 | 0.0071219 | 0.0094715 | 0.0127 | 0.017155 | 0.023326 | 0.031904 | 0.043865 | 0.060591 | 0.084037 | 0.11698 | 0.16335 | 0.22876 | 0.32115 | 0.45186 | 0.63698 | 0.8995 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.3778e-07 | 2.3778e-07 | 2.4863e-07 | 3.2768e-07 | 4.3578e-07 | 5.8433e-07 | 7.893e-07 | 1.0732e-06 | 1.4679e-06 | 2.0182e-06 | 2.7878e-06 | 3.8665e-06 | 5.3822e-06 | 7.5159e-06 | 1.0525e-05 | 1.4776e-05 | 2.079e-05 | 2.9308e-05 | 4.1386e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 4.333e-05 | 31.4635 | 31.4635 | 32.8994 | 43.3593 | 57.6646 | 77.3205 | 104.4435 | 142.0144 | 194.2392 | 267.0607 | 368.8878 | 511.6325 | 712.1881 | 994.5348 | 1392.7428 | 1955.2544 | 2750.9947 | 3878.0918 | 5476.3271 | 5733.6301 | 5733.6301 | 5733.6301 | 5733.6301 | 5733.6301 | 5733.6301 | 5733.6301 | 5733.6301 | 5733.6301 | 5733.6301 | 5733.6301 |  | 31.4635 | 31.4635 | 31.4635 | 31.4635 | 31.4635 | 31.4635 | 31.4635 | 31.4635 | 31.4635 | 31.4635 | 31.4635 | 31.4635 | 31.4635 | 31.4635 | 31.4635 | 31.4635 | 31.4635 | 37.6598 | 49.9203 | 66.7502 | 89.9566 | 122.0861 | 166.7341 | 228.9846 | 316.0368 | 438.0984 | 609.6593 | 851.3092 | 1192.332 | 1674.4116 |  | 14.2119 | 14.2119 | 14.8605 | 19.5852 | 26.0468 | 34.9253 | 47.1766 | 64.1472 | 87.7369 | 120.63 | 166.6248 | 231.1019 | 321.6918 | 449.2264 | 629.095 | 883.1787 | 1242.6106 | 1751.7147 | 2473.6296 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 | 2589.8521 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 0 | 0 | 0.64862 | 5.3733 | 11.8349 | 20.7134 | 32.9647 | 49.9353 | 73.525 | 106.4181 | 152.4129 | 216.89 | 307.4799 | 435.0145 | 614.8831 | 868.9668 | 1228.3987 | 1734.704 | 2451.0809 | 2559.7014 | 2549.2192 | 2534.7064 | 2514.5392 | 2486.4209 | 2447.0999 | 2391.9652 | 2314.472 | 2205.32 | 2051.2817 | 1833.5287 |  | 0.016644 | 0.016644 | 0.017404 | 0.022937 | 0.030505 | 0.040903 | 0.055251 | 0.075126 | 0.10275 | 0.14128 | 0.19514 | 0.27066 | 0.37675 | 0.52611 | 0.73677 | 1.0343 | 1.4553 | 2.0515 | 2.897 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 | 3.0331 |  | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.016644 | 0.019922 | 0.026408 | 0.035311 | 0.047588 | 0.064584 | 0.088203 | 0.12113 | 0.16719 | 0.23176 | 0.32251 | 0.45035 | 0.63075 | 0.88577 |  | 0 | 0 | 0.00075964 | 0.006293 | 0.013861 | 0.024259 | 0.038607 | 0.058482 | 0.086109 | 0.12463 | 0.1785 | 0.25401 | 0.36011 | 0.50947 | 0.72012 | 1.0177 | 1.4386 | 2.0316 | 2.8706 | 2.9978 | 2.9855 | 2.9685 | 2.9449 | 2.912 | 2.8659 | 2.8014 | 2.7106 | 2.5828 | 2.4024 | 2.1473 |  | 0 | 0 | 0.64938 | 5.3796 | 11.8488 | 20.7377 | 33.0033 | 49.9938 | 73.6111 | 106.5427 | 152.5914 | 217.144 | 307.84 | 435.524 | 615.6032 | 869.9845 | 1229.8373 | 1736.7356 | 2453.9515 | 2562.6992 | 2552.2047 | 2537.675 | 2517.4841 | 2489.3329 | 2449.9658 | 2394.7666 | 2317.1826 | 2207.9028 | 2053.6841 | 1835.6761 |  | 14.6711 | 14.6711 | 15.3407 | 20.2181 | 26.8885 | 36.0539 | 48.7011 | 66.2201 | 90.572 | 124.5281 | 172.0091 | 238.5697 | 332.087 | 463.7428 | 649.4237 | 911.7179 | 1282.7646 | 1808.3201 | 2553.5631 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 | 2673.5412 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 0 | 0 | 0.66958 | 5.5469 | 12.2174 | 21.3827 | 34.0299 | 51.5489 | 75.9009 | 109.8569 | 157.338 | 223.8986 | 317.4159 | 449.0717 | 634.7526 | 897.0468 | 1268.0935 | 1790.7596 | 2530.2857 | 2642.4162 | 2631.5953 | 2616.6136 | 2595.7946 | 2566.7677 | 2526.1761 | 2469.2598 | 2389.2624 | 2276.5832 | 2117.5673 | 1892.7778 |  | 2.0677 | 2.0677 | 2.1621 | 2.8495 | 3.7896 | 5.0813 | 6.8637 | 9.3328 | 12.7649 | 17.5505 | 24.2423 | 33.6231 | 46.8031 | 65.3581 | 91.5273 | 128.494 | 180.7879 | 254.8577 | 359.8894 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 | 376.7986 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 0 | 0 | 0.094368 | 0.78176 | 1.7219 | 3.0136 | 4.796 | 7.2651 | 10.6972 | 15.4828 | 22.1746 | 31.5554 | 44.7354 | 63.2904 | 89.4596 | 126.4263 | 178.7202 | 252.3828 | 356.6088 | 372.412 | 370.8869 | 368.7755 | 365.8413 | 361.7504 | 356.0296 | 348.008 | 336.7335 | 320.8529 | 298.4418 | 266.7608 |  | 0.4961 | 0.4961 | 0.51874 | 0.68367 | 0.90923 | 1.2192 | 1.6468 | 2.2392 | 3.0627 | 4.2109 | 5.8164 | 8.0672 | 11.2294 | 15.6813 | 21.9601 | 30.8295 | 43.3763 | 61.1478 | 86.348 | 90.405 | 90.405 | 90.405 | 90.405 | 90.405 | 90.405 | 90.405 | 90.405 | 90.405 | 90.405 | 90.405 |  | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.5938 | 0.78712 | 1.0525 | 1.4184 | 1.925 | 2.629 | 3.6105 | 4.9831 | 6.9077 | 9.6128 | 13.423 | 18.8001 | 26.4013 |  | 0 | 0 | 0.022642 | 0.18757 | 0.41313 | 0.72305 | 1.1507 | 1.7431 | 2.5666 | 3.7148 | 5.3203 | 7.5711 | 10.7333 | 15.1852 | 21.464 | 30.3334 | 42.8802 | 60.554 | 85.5609 | 89.3525 | 88.9866 | 88.48 | 87.776 | 86.7945 | 85.4219 | 83.4973 | 80.7922 | 76.982 | 71.6049 | 64.0037 |  | 0 | 0 | 1.436 | 11.8959 | 26.2011 | 45.8571 | 72.98 | 110.5509 | 162.7757 | 235.5972 | 337.4243 | 480.169 | 680.7246 | 963.0714 | 1361.2794 | 1923.791 | 2719.5312 | 3840.432 | 5426.4068 | 5666.8799 | 5643.6735 | 5611.544 | 5566.896 | 5504.6455 | 5417.5933 | 5295.5317 | 5123.9708 | 4882.3209 | 4541.2981 | 4059.2185
| TRUE | 4640 | 22009476 | WBE | Blank | 22 | BUS NO.1 | BUEF STAGE 2 | BU | RMS | 2C137 | RMS - 2C137 | RMS 2C13X | Electronic |  | 0.0034106 | 2190 |  | 6.6 | 0.014726 | 0.00014965 | 0.014576 | 60.8067 | 20.9513 | 81.758 | 42.6512 | 5.8934 | 312.2361 |  | 14.9721 | 0.13394 | 0.0013611 | 0.13257 | 553.0441 | 190.5544 | 743.5985 | 387.9178 | 53.6011 | 2839.8247 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 21.3177 | 0.0033803 | 21.3211 | 14.6699 | 2.0677 | 0.050376 |  | 442.5386 | 4024.9422 | 38.1091 | 3986.833 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.018172 | 0.022489 | 0.027904 | 0.034708 | 0.043268 | 0.05405 | 0.067647 | 0.084812 | 0.1065 | 0.13394 | 0.16866 | 0.21265 | 0.26843 | 0.33918 | 0.42899 | 0.54305 | 0.688 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00018467 | 0.00022854 | 0.00028358 | 0.00035272 | 0.00043971 | 0.00054928 | 0.00068746 | 0.00086189 | 0.0010823 | 0.0013611 | 0.001714 | 0.0021611 | 0.0027279 | 0.0034469 | 0.0043595 | 0.0055187 | 0.0069917 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 546.0972 | 675.819 | 838.565 | 1043.0358 | 1300.2716 | 1624.2894 | 2032.8949 | 2548.7181 | 3200.5331 | 4024.9422 | 5068.5231 | 6390.5702 | 8066.5906 | 10192.7674 | 12891.6566 | 16319.4595 | 20675.3082 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 |  | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 37.1089 | 49.1901 | 65.7738 | 88.6407 | 120.3003 | 164.2952 | 225.6351 | 311.414 | 431.6902 | 600.7417 | 838.8568 | 1174.8914 | 1649.9195 |  | 75.0361 | 92.8604 | 115.2224 | 143.3175 | 178.6628 | 223.1842 | 279.3284 | 350.2046 | 439.7668 | 553.0441 | 696.4365 | 878.0914 | 1108.3837 | 1400.5293 | 1771.3681 | 2242.3627 | 2840.8748 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 60.8242 | 78.6486 | 101.0105 | 129.1057 | 164.451 | 208.9724 | 265.1165 | 335.9928 | 425.555 | 538.8322 | 682.2247 | 863.8795 | 1094.1718 | 1386.3175 | 1757.1563 | 2228.1509 | 2826.6629 | 3291.6198 | 3286.0818 | 3278.4799 | 3267.9977 | 3253.485 | 3233.3178 | 3205.1997 | 3165.8788 | 3110.7444 | 3033.2515 | 2924.0999 | 2770.0623 | 2552.3102 |  | 25.8541 | 31.9956 | 39.7005 | 49.3809 | 61.5593 | 76.8994 | 96.2442 | 120.665 | 151.5241 | 190.5544 | 239.9611 | 302.5513 | 381.8998 | 482.5603 | 610.3349 | 772.6187 | 978.8394 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 |  | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.004046 | 0.0053632 | 0.0071713 | 0.0096645 | 0.013116 | 0.017913 | 0.024601 | 0.033953 | 0.047067 | 0.065499 | 0.09146 | 0.1281 | 0.17989 |  | 25.8507 | 31.9922 | 39.6971 | 49.3775 | 61.5559 | 76.896 | 96.2408 | 120.6616 | 151.5207 | 190.5511 | 239.9577 | 302.5479 | 381.8964 | 482.5569 | 610.3315 | 772.6153 | 978.836 | 1140.0032 | 1140.0019 | 1140.0001 | 1139.9976 | 1139.9941 | 1139.9893 | 1139.9826 | 1139.9733 | 1139.9602 | 1139.9417 | 1139.9158 | 1139.8791 | 1139.8273 |  | 86.675 | 110.6407 | 140.7077 | 178.4832 | 226.0069 | 285.8684 | 361.3573 | 456.6544 | 577.0757 | 729.3833 | 922.1824 | 1166.4275 | 1476.0683 | 1868.8744 | 2367.4878 | 3000.7662 | 3805.4989 | 4431.623 | 4426.0837 | 4418.4799 | 4407.9953 | 4393.4791 | 4373.3072 | 4345.1823 | 4305.8521 | 4250.7046 | 4173.1933 | 4064.0157 | 3909.9414 | 3692.1376 |  | 52.632 | 65.1344 | 80.8196 | 100.5262 | 125.3182 | 156.5466 | 195.9273 | 245.6416 | 308.4625 | 387.9178 | 488.4966 | 615.9135 | 777.4458 | 982.3635 | 1242.4784 | 1572.8449 | 1992.655 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 37.9621 | 50.4645 | 66.1497 | 85.8563 | 110.6483 | 141.8766 | 181.2574 | 230.9717 | 293.7926 | 373.2479 | 473.8267 | 601.2436 | 762.7759 | 967.6936 | 1227.8085 | 1558.1749 | 1977.9851 | 2303.1906 | 2297.4741 | 2289.6271 | 2278.8071 | 2263.8266 | 2243.0094 | 2213.9849 | 2173.3966 | 2116.485 | 2036.4943 | 1923.8244 | 1764.8217 | 1540.0507 |  | 7.2725 | 9 | 11.1674 | 13.8903 | 17.316 | 21.631 | 27.0725 | 33.9419 | 42.6222 | 53.6011 | 67.4987 | 85.1047 | 107.4246 | 135.7394 | 171.6811 | 217.33 | 275.3378 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 5.2048 | 6.9323 | 9.0997 | 11.8227 | 15.2483 | 19.5633 | 25.0048 | 31.8742 | 40.5545 | 51.5334 | 65.431 | 83.037 | 105.3569 | 133.6717 | 169.6135 | 215.2623 | 273.2701 | 318.1978 | 317.3921 | 316.2861 | 314.761 | 312.6496 | 309.7154 | 305.6245 | 299.9037 | 291.8821 | 280.6076 | 264.7271 | 242.316 | 210.6351 |  | 385.3025 | 476.8286 | 591.6551 | 735.9208 | 917.4153 | 1146.0282 | 1434.3226 | 1798.265 | 2258.1575 | 2839.8247 | 3576.1302 | 4508.9093 | 5691.4367 | 7191.5748 | 9095.7941 | 11514.3033 | 14587.6013 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 |  | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.060297 | 0.079927 | 0.10687 | 0.14403 | 0.19547 | 0.26696 | 0.36663 | 0.50601 | 0.70144 | 0.97613 | 1.363 | 1.909 | 2.6809 |  | 385.2521 | 476.7782 | 591.6047 | 735.8705 | 917.3649 | 1145.9778 | 1434.2722 | 1798.2147 | 2258.1071 | 2839.7743 | 3576.0799 | 4508.859 | 5691.3863 | 7191.5245 | 9095.7437 | 11514.2529 | 14587.5509 | 16989.4186 | 16989.399 | 16989.372 | 16989.3349 | 16989.2834 | 16989.2119 | 16989.1123 | 16988.9729 | 16988.7775 | 16988.5028 | 16988.1159 | 16987.5698 | 16986.798 |  | 515.094 | 644.8158 | 807.5618 | 1012.0326 | 1269.2684 | 1593.2862 | 2001.8917 | 2517.7149 | 3169.5299 | 3993.939 | 5037.5199 | 6359.567 | 8035.5874 | 10161.7642 | 12860.6534 | 16288.4563 | 20644.305 | 24042.43 | 24030.3489 | 24013.7652 | 23990.8983 | 23959.2388 | 23915.2439 | 23853.904 | 23768.1253 | 23647.8492 | 23478.798 | 23240.6831 | 22904.6489 | 22429.6213
| TRUE | 4641 | 22009477 | WBE | Blank | 22 | BUS NO.1 | BUEF STAGE 3 | BU | RMS | 2T105 | 2T105 | RMS 2T1XX | Electronic |  | 0.0034106 | 2190 |  | 5.5 | 0.0093284 | 9.4799e-05 | 0.0092336 | 38.5187 | 13.2718 | 51.7905 | 27.0179 | 3.7332 | 197.7893 |  | 11.7751 | 0.068685 | 0.000698 | 0.067987 | 283.6131 | 97.7205 | 381.3336 | 198.9328 | 27.4878 | 1456.3243 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 21.3177 | 0.0033803 | 21.3211 | 14.6699 | 2.0677 | 0.050376 |  | 280.3309 | 2064.0785 | 38.1091 | 2025.9694 |  | 0.076124 |  | 5.935 | 6.4045 | 6.911 | 7.4577 | 8.0475 | 8.6841 | 9.3709 | 10.1121 | 10.912 | 11.7751 | 12.7064 | 13.7115 | 14.796 | 15.9663 | 17.2292 | 18.5919 | 20.0625 | 21.6493 | 23.3617 | 25.2095 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.011264 | 0.013642 | 0.016568 | 0.020172 | 0.024619 | 0.030112 | 0.036906 | 0.045319 | 0.055747 | 0.068685 | 0.084752 | 0.10472 | 0.12956 | 0.16048 | 0.199 | 0.24701 | 0.30689 | 0.38161 | 0.47489 | 0.59141 | 0.73701 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00011447 | 0.00013864 | 0.00016837 | 0.000205 | 0.00025019 | 0.00030601 | 0.00037506 | 0.00046055 | 0.00056652 | 0.000698 | 0.00086129 | 0.0010642 | 0.0013167 | 0.0016309 | 0.0020223 | 0.0025102 | 0.0031187 | 0.003878 | 0.004826 | 0.0060101 | 0.0074898 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 338.5106 | 409.9724 | 497.8866 | 606.2007 | 739.8325 | 904.9129 | 1109.0889 | 1361.9036 | 1675.2722 | 2064.0785 | 2546.9218 | 3147.0542 | 3893.5544 | 4822.8007 | 5980.3177 | 7423.0919 | 9222.4782 | 11467.8442 | 14271.1445 | 17772.6595 | 22148.1986 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 |  | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 37.1089 | 49.1901 | 65.7738 | 88.6407 | 120.3003 | 164.2952 | 225.6351 | 311.414 | 431.6902 | 600.7417 | 838.8568 | 1174.8914 | 1649.9195 |  | 46.5128 | 56.3319 | 68.4117 | 83.2945 | 101.6561 | 124.3389 | 152.3935 | 187.1313 | 230.1895 | 283.6131 | 349.9578 | 432.4186 | 534.9908 | 662.6732 | 821.7209 | 1019.9642 | 1267.2075 | 1575.7303 | 1960.9156 | 2442.0386 | 3043.2561 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 32.301 | 42.1201 | 54.1999 | 69.0827 | 87.4443 | 110.127 | 138.1817 | 172.9195 | 215.9777 | 269.4013 | 335.746 | 418.2067 | 520.779 | 648.4614 | 807.5091 | 1005.7524 | 1252.9957 | 1558.7196 | 1938.3669 | 2411.888 | 3002.6234 | 3253.485 | 3233.3178 | 3205.1997 | 3165.8788 | 3110.7444 | 3033.2515 | 2924.0999 | 2770.0623 | 2552.3102 |  | 16.0262 | 19.4095 | 23.5716 | 28.6996 | 35.0262 | 42.8417 | 52.508 | 64.4771 | 79.3131 | 97.7205 | 120.5799 | 148.9922 | 184.3341 | 228.3278 | 283.1286 | 351.4344 | 436.6235 | 542.9267 | 675.6445 | 841.4181 | 1048.571 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 |  | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.004046 | 0.0053632 | 0.0071713 | 0.0096645 | 0.013116 | 0.017913 | 0.024601 | 0.033953 | 0.047067 | 0.065499 | 0.09146 | 0.1281 | 0.17989 |  | 16.0229 | 19.4061 | 23.5683 | 28.6962 | 35.0228 | 42.8383 | 52.5047 | 64.4738 | 79.3097 | 97.7171 | 120.5766 | 148.9889 | 184.3307 | 228.3244 | 283.1252 | 351.431 | 436.6201 | 542.9227 | 675.6391 | 841.411 | 1048.5614 | 1139.9941 | 1139.9893 | 1139.9826 | 1139.9733 | 1139.9602 | 1139.9417 | 1139.9158 | 1139.8791 | 1139.8273 |  | 48.3238 | 61.5262 | 77.7682 | 97.7789 | 122.4671 | 152.9653 | 190.6863 | 237.3932 | 295.2874 | 367.1184 | 456.3226 | 567.1956 | 705.1097 | 876.7858 | 1090.6343 | 1357.1834 | 1689.6158 | 2101.6423 | 2614.0061 | 3253.2989 | 4051.1847 | 4393.4791 | 4373.3072 | 4345.1823 | 4305.8521 | 4250.7046 | 4173.1933 | 4064.0157 | 3909.9414 | 3692.1376 |  | 32.6251 | 39.5125 | 47.9856 | 58.4247 | 71.3039 | 87.2141 | 106.8923 | 131.2582 | 161.4602 | 198.9328 | 245.4685 | 303.3083 | 375.2549 | 464.8143 | 576.374 | 715.4264 | 888.8485 | 1105.2535 | 1375.4313 | 1712.9021 | 2134.6099 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 17.9552 | 24.8426 | 33.3156 | 43.7548 | 56.634 | 72.5442 | 92.2224 | 116.5883 | 146.7903 | 184.2628 | 230.7986 | 288.6384 | 360.585 | 450.1443 | 561.7041 | 700.7565 | 874.1786 | 1087.6945 | 1352.1559 | 1681.7796 | 2092.6674 | 2263.8266 | 2243.0094 | 2213.9849 | 2173.3966 | 2116.485 | 2036.4943 | 1923.8244 | 1764.8217 | 1540.0507 |  | 4.508 | 5.4597 | 6.6305 | 8.0729 | 9.8525 | 12.0509 | 14.77 | 18.1368 | 22.31 | 27.4878 | 33.9179 | 41.91 | 51.8514 | 64.2263 | 79.6413 | 98.855 | 122.8179 | 152.7199 | 190.0521 | 236.6826 | 294.9526 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 2.4403 | 3.392 | 4.5628 | 6.0052 | 7.7848 | 9.9832 | 12.7023 | 16.0691 | 20.2423 | 25.4201 | 31.8502 | 39.8423 | 49.7837 | 62.1587 | 77.5736 | 96.7873 | 120.7502 | 150.245 | 186.7715 | 232.2959 | 289.0409 | 312.6496 | 309.7154 | 305.6245 | 299.9037 | 291.8821 | 280.6076 | 264.7271 | 242.316 | 210.6351 |  | 238.8384 | 289.2588 | 351.2872 | 427.7089 | 521.9938 | 638.4673 | 782.525 | 960.9001 | 1181.9994 | 1456.3243 | 1796.9976 | 2220.425 | 2747.1232 | 3402.7592 | 4219.4529 | 5237.4119 | 6506.9808 | 8091.2138 | 10069.1009 | 12539.6182 | 15626.8089 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 |  | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.060297 | 0.079927 | 0.10687 | 0.14403 | 0.19547 | 0.26696 | 0.36663 | 0.50601 | 0.70144 | 0.97613 | 1.363 | 1.909 | 2.6809 |  | 238.7881 | 289.2084 | 351.2369 | 427.6586 | 521.9434 | 638.417 | 782.4747 | 960.8497 | 1181.9491 | 1456.2739 | 1796.9473 | 2220.3746 | 2747.0728 | 3402.7088 | 4219.4025 | 5237.3615 | 6506.9305 | 8091.1535 | 10069.021 | 12539.5113 | 15626.6648 | 16989.2834 | 16989.2119 | 16989.1123 | 16988.9729 | 16988.7775 | 16988.5028 | 16988.1159 | 16987.5698 | 16986.798 |  | 307.5074 | 378.9692 | 466.8834 | 575.1975 | 708.8293 | 873.9097 | 1078.0857 | 1330.9004 | 1644.269 | 2033.0753 | 2515.9186 | 3116.051 | 3862.5512 | 4791.7975 | 5949.3145 | 7392.0887 | 9191.475 | 11430.7353 | 14221.9544 | 17706.8858 | 22059.5579 | 23959.2388 | 23915.2439 | 23853.904 | 23768.1253 | 23647.8492 | 23478.798 | 23240.6831 | 22904.6489 | 22429.6213
| TRUE | 4642 | 22009473 | WBE | Blank | 22 | BUS NO.1 | HIBP | X | ABB | RADHA_3110 | RADHA 3110 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 81.7572 | 388.9293 | 470.6866 | 49.6875 | 5.9058 | 2898.0985 |  | 12.1996 | 0.075729 | 0.0071431 | 0.068586 | 420.4389 | 2000.0803 | 2420.5193 | 255.5192 | 30.3707 | 14903.5557 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.4961 |  | 3424.3783 | 17609.9648 | 45.7253 | 17564.2395 |  | 0.061434 |  | 7.0182 | 7.4628 | 7.9357 | 8.4385 | 8.9732 | 9.5417 | 10.1463 | 10.7891 | 11.4727 | 12.1996 | 12.9726 | 13.7946 | 14.6686 | 15.598 | 16.5863 | 17.6372 | 18.7547 | 19.943 | 21.2066 | 22.5502 | 23.979 | 25.4983 | 27.1139 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.017237 | 0.020209 | 0.023729 | 0.027904 | 0.032859 | 0.038742 | 0.045735 | 0.05405 | 0.063946 | 0.075729 | 0.089768 | 0.1065 | 0.12646 | 0.15027 | 0.1787 | 0.21265 | 0.25322 | 0.3017 | 0.35966 | 0.42899 | 0.51193 | 0.61118 | 0.73 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0016259 | 0.0019062 | 0.0022383 | 0.0026321 | 0.0030994 | 0.0036544 | 0.0043139 | 0.0050983 | 0.0060317 | 0.0071431 | 0.0084673 | 0.010046 | 0.011928 | 0.014175 | 0.016856 | 0.020059 | 0.023885 | 0.028458 | 0.033925 | 0.040464 | 0.048287 | 0.05765 | 0.068857 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 4008.2108 | 4699.2836 | 5518.0256 | 6488.8432 | 7640.9053 | 9009.0846 | 10635.0868 | 12568.8046 | 14869.9422 | 17609.9648 | 20874.437 | 24765.8302 | 29406.891 | 34944.6859 | 41555.4551 | 49450.4415 | 58882.8884 | 70156.4431 | 83635.248 | 99756.0604 | 119042.808 | 142124.0731 | 169754.094 | 186328.2599 | 186328.2599 | 186328.2599 | 186328.2599 | 186328.2599 | 186328.2599 | 186328.2599 |  | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 37.7204 | 50.0007 | 66.8576 | 90.1014 | 122.2826 | 167.0025 | 229.3532 | 316.5456 | 438.8037 | 610.6408 | 852.6797 | 1194.2515 | 1677.1072 |  | 95.6963 | 112.1957 | 131.7432 | 154.9215 | 182.4271 | 215.0924 | 253.9133 | 300.0809 | 355.0207 | 420.4389 | 498.3784 | 591.2856 | 702.0912 | 834.3064 | 992.1389 | 1180.6321 | 1405.8324 | 1674.9891 | 1996.7964 | 2381.6817 | 2842.1539 | 3393.2204 | 4052.8888 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 81.4844 | 97.9838 | 117.5313 | 140.7096 | 168.2152 | 200.8805 | 239.7014 | 285.869 | 340.8088 | 406.227 | 484.1665 | 577.0737 | 687.8793 | 820.0945 | 977.927 | 1166.4203 | 1391.6205 | 1657.9784 | 1974.2476 | 2351.531 | 2801.521 | 3338.0748 | 3977.5758 | 4345.1668 | 4305.8457 | 4250.7111 | 4173.2179 | 4064.0658 | 3910.0276 | 3692.2746 |  | 455.239 | 533.7288 | 626.7187 | 736.9809 | 867.8282 | 1023.2214 | 1207.8972 | 1427.5224 | 1688.8778 | 2000.0803 | 2370.8481 | 2812.8194 | 3339.9354 | 3968.8994 | 4719.7283 | 5616.4142 | 6687.7196 | 7968.1319 | 9499.0091 | 11329.9565 | 13520.4802 | 16141.9723 | 19280.0968 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 455.1725 | 533.6622 | 626.6521 | 736.9143 | 867.7616 | 1023.1548 | 1207.8307 | 1427.4558 | 1688.8113 | 2000.0138 | 2370.7815 | 2812.7528 | 3339.8688 | 3968.8329 | 4719.6617 | 5616.3476 | 6687.6531 | 7968.0522 | 9498.9034 | 11329.8153 | 13520.2898 | 16141.714 | 19279.744 | 21162.05 | 21161.8658 | 21161.6076 | 21161.2445 | 21160.7332 | 21160.0116 | 21158.9915 |  | 536.6568 | 631.646 | 744.1834 | 877.6239 | 1035.9768 | 1224.0354 | 1447.5321 | 1713.3249 | 2029.6201 | 2406.2408 | 2854.948 | 3389.8265 | 4027.7481 | 4788.9274 | 5697.5887 | 6782.7678 | 8079.2735 | 9626.0306 | 11473.1511 | 13681.3462 | 16321.8108 | 19479.7888 | 23257.3198 | 25507.2168 | 25467.7116 | 25412.3186 | 25334.4624 | 25224.799 | 25070.0391 | 24851.2661 |  | 58.1588 | 68.1862 | 80.0661 | 94.1526 | 110.8689 | 130.7211 | 154.3143 | 182.3724 | 215.7617 | 255.5192 | 302.8864 | 359.3502 | 426.6917 | 507.0446 | 602.9664 | 717.522 | 854.3861 | 1017.9644 | 1213.5408 | 1447.4526 | 1727.3017 | 2062.2091 | 2463.1185 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 43.4877 | 53.5151 | 65.395 | 79.4815 | 96.1978 | 116.05 | 139.6431 | 167.7012 | 201.0906 | 240.8481 | 288.2153 | 344.6791 | 412.0205 | 492.3735 | 588.2952 | 702.8509 | 839.7149 | 1000.404 | 1190.2635 | 1416.3275 | 1685.3558 | 2005.2814 | 2385.3719 | 2596.8349 | 2556.2432 | 2499.3269 | 2419.3296 | 2306.6504 | 2147.6344 | 1922.8449 |  | 6.9127 | 8.1045 | 9.5165 | 11.1908 | 13.1777 | 15.5373 | 18.3416 | 21.6765 | 25.6451 | 30.3707 | 36.0007 | 42.7119 | 50.716 | 60.2666 | 71.6677 | 85.2837 | 101.5511 | 120.9938 | 144.2398 | 172.0422 | 205.3047 | 245.1113 | 292.7628 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 4.845 | 6.0368 | 7.4489 | 9.1232 | 11.11 | 13.4696 | 16.2739 | 19.6088 | 23.5774 | 28.303 | 33.933 | 40.6442 | 48.6483 | 58.1989 | 69.6 | 83.216 | 99.4834 | 118.5189 | 140.9591 | 167.6555 | 199.393 | 237.0881 | 281.8055 | 306.2989 | 300.578 | 292.5565 | 281.2819 | 265.4014 | 242.9903 | 211.3093 |  | 3392.204 | 3977.0684 | 4669.981 | 5491.5973 | 6466.6033 | 7624.5123 | 9000.6204 | 10637.1524 | 12584.6369 | 14903.5557 | 17666.3235 | 20959.6631 | 24887.4568 | 29574.1689 | 35168.9539 | 41850.5895 | 49833.3992 | 59374.3638 | 70781.662 | 84424.9275 | 100747.5675 | 120281.56 | 143665.2271 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 |  | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.5938 | 0.78712 | 1.0525 | 1.4184 | 1.925 | 2.629 | 3.6105 | 4.9831 | 6.9077 | 9.6128 | 13.423 | 18.8001 | 26.4013 |  | 3391.7079 | 3976.5723 | 4669.4849 | 5491.1012 | 6466.1072 | 7624.0162 | 9000.1243 | 10636.6563 | 12584.1408 | 14903.0596 | 17665.8274 | 20959.167 | 24886.9607 | 29573.6728 | 35168.4578 | 41850.0934 | 49832.9031 | 59373.77 | 70780.8749 | 84423.875 | 100746.1491 | 120279.635 | 143662.5981 | 157688.5614 | 157687.1888 | 157685.2642 | 157682.5591 | 157678.7489 | 157673.3718 | 157665.7706 |  | 3976.6974 | 4667.7702 | 5486.5122 | 6457.3298 | 7609.3919 | 8977.5712 | 10603.5734 | 12537.2912 | 14838.4289 | 17578.4514 | 20842.9236 | 24734.3168 | 29375.3776 | 34913.1725 | 41523.9417 | 49418.9281 | 58851.375 | 70118.7235 | 83585.2485 | 99689.2043 | 118952.7087 | 142001.7933 | 169587.0953 | 186098.9119 | 186011.7215 | 185889.4662 | 185717.633 | 185475.5996 | 185134.0356 | 184651.1909
| TRUE | 4643 | 22009474 | WBE | Blank | 22 | BUS NO.1 | SINGLE ZONE BUS DIST | Y | Schweitzer | SEL_311A | SEL 311A | SEL 300s | Digital |  | 0.0034106 | 1 |  | 6.6 | 0.017308 | 8.0863e-08 | 0.017308 | 59.4958 | 0.0084906 | 59.5043 | 49.1308 | 6.9249 | 0.16871 |  | 14.9721 | 0.15742 | 7.3546e-07 | 0.15742 | 541.1213 | 0.077223 | 541.1986 | 446.8507 | 62.9826 | 1.5345 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 17.7648 | 0.0025352 | 17.7673 | 14.6699 | 2.0677 | 0.050376 |  | 115.7287 | 1052.5663 | 34.5553 | 1018.011 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021358 | 0.026432 | 0.032797 | 0.040794 | 0.050854 | 0.063527 | 0.079507 | 0.099681 | 0.12517 | 0.15742 | 0.19823 | 0.24994 | 0.31549 | 0.39864 | 0.5042 | 0.63826 | 0.80862 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 9.9786e-08 | 1.2349e-07 | 1.5323e-07 | 1.9059e-07 | 2.3759e-07 | 2.968e-07 | 3.7146e-07 | 4.6572e-07 | 5.8482e-07 | 7.3546e-07 | 9.2615e-07 | 1.1677e-06 | 1.474e-06 | 1.8625e-06 | 2.3556e-06 | 2.982e-06 | 3.7779e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 142.8104 | 176.734 | 219.2939 | 272.7652 | 340.0352 | 424.7694 | 531.6242 | 666.5176 | 836.9744 | 1052.5663 | 1325.4741 | 1671.2039 | 2109.5015 | 2665.52 | 3371.3089 | 4267.7168 | 5406.8188 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 |  | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 37.1079 | 49.1887 | 65.772 | 88.6383 | 120.2969 | 164.2906 | 225.6288 | 311.4053 | 431.6782 | 600.7249 | 838.8335 | 1174.8587 | 1649.8736 |  | 73.4184 | 90.8585 | 112.7384 | 140.2278 | 174.8111 | 218.3727 | 273.3065 | 342.6548 | 430.2861 | 541.1213 | 681.4225 | 859.1611 | 1084.4887 | 1370.3362 | 1733.1803 | 2194.021 | 2779.6301 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 59.2066 | 76.6466 | 98.5265 | 126.016 | 160.5993 | 204.1609 | 259.0947 | 328.443 | 416.0743 | 526.9095 | 667.2106 | 844.9493 | 1070.2769 | 1356.1244 | 1718.9685 | 2179.8092 | 2765.4183 | 3220.2911 | 3214.7531 | 3207.1512 | 3196.669 | 3182.1563 | 3161.9891 | 3133.871 | 3094.5501 | 3039.4157 | 2961.9228 | 2852.7712 | 2698.7336 | 2480.9815 |  | 0.010478 | 0.012966 | 0.016089 | 0.020012 | 0.024947 | 0.031164 | 0.039004 | 0.0489 | 0.061406 | 0.077223 | 0.097246 | 0.12261 | 0.15477 | 0.19556 | 0.24734 | 0.31311 | 0.39668 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 |  | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0030345 | 0.0040224 | 0.0053785 | 0.0072484 | 0.0098372 | 0.013435 | 0.018451 | 0.025465 | 0.0353 | 0.049124 | 0.068595 | 0.096074 | 0.13492 |  | 0.0079423 | 0.010431 | 0.013554 | 0.017477 | 0.022412 | 0.028629 | 0.036468 | 0.046365 | 0.058871 | 0.074688 | 0.094711 | 0.12008 | 0.15223 | 0.19303 | 0.24481 | 0.31057 | 0.39415 | 0.45896 | 0.45797 | 0.45662 | 0.45475 | 0.45216 | 0.44856 | 0.44354 | 0.43653 | 0.42669 | 0.41287 | 0.3934 | 0.36592 | 0.32708 |  | 59.2145 | 76.6571 | 98.5401 | 126.0335 | 160.6217 | 204.1895 | 259.1311 | 328.4893 | 416.1332 | 526.9842 | 667.3053 | 845.0694 | 1070.4291 | 1356.3174 | 1719.2133 | 2180.1198 | 2765.8124 | 3220.75 | 3215.2111 | 3207.6078 | 3197.1237 | 3182.6085 | 3162.4377 | 3134.3145 | 3094.9866 | 3039.8424 | 2962.3357 | 2853.1646 | 2699.0995 | 2481.3086 |  | 60.6279 | 75.0297 | 93.0978 | 115.7983 | 144.3567 | 180.3293 | 225.6928 | 282.9597 | 355.3245 | 446.8507 | 562.7095 | 709.4837 | 895.5562 | 1131.6052 | 1431.237 | 1811.793 | 2295.3811 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 45.958 | 60.3598 | 78.4279 | 101.1283 | 129.6868 | 165.6593 | 211.0229 | 268.2898 | 340.6546 | 432.1808 | 548.0396 | 694.8138 | 880.8862 | 1116.9353 | 1416.567 | 1797.1231 | 2280.7112 | 2655.7612 | 2650.0447 | 2642.1978 | 2631.3777 | 2616.3973 | 2595.58 | 2566.5555 | 2525.9672 | 2469.0557 | 2389.0649 | 2276.395 | 2117.3923 | 1892.6214 |  | 8.5454 | 10.5753 | 13.1219 | 16.3215 | 20.3467 | 25.417 | 31.8109 | 39.8825 | 50.0822 | 62.9826 | 79.3126 | 100.0001 | 126.2266 | 159.4971 | 201.7295 | 255.368 | 323.5286 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 6.4777 | 8.5076 | 11.0542 | 14.2538 | 18.279 | 23.3493 | 29.7432 | 37.8148 | 48.0145 | 60.9149 | 77.2449 | 97.9324 | 124.1589 | 157.4294 | 199.6618 | 253.3003 | 321.4609 | 374.3234 | 373.5176 | 372.4116 | 370.8866 | 368.7751 | 365.8409 | 361.75 | 356.0292 | 348.0076 | 336.7331 | 320.8526 | 298.4415 | 266.7606 |  | 0.20819 | 0.25765 | 0.3197 | 0.39765 | 0.49572 | 0.61925 | 0.77502 | 0.97168 | 1.2202 | 1.5345 | 1.9323 | 2.4364 | 3.0753 | 3.8859 | 4.9148 | 6.2217 | 7.8823 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 |  | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.060297 | 0.079927 | 0.10687 | 0.14403 | 0.19547 | 0.26696 | 0.36663 | 0.50601 | 0.70144 | 0.97613 | 1.363 | 1.909 | 2.6809 |  | 0.15782 | 0.20727 | 0.26932 | 0.34727 | 0.44534 | 0.56887 | 0.72465 | 0.9213 | 1.1698 | 1.4841 | 1.882 | 2.386 | 3.0249 | 3.8355 | 4.8645 | 6.1713 | 7.8319 | 9.1198 | 9.1002 | 9.0732 | 9.0361 | 8.9846 | 8.9132 | 8.8135 | 8.6741 | 8.4787 | 8.204 | 7.8171 | 7.2711 | 6.4992 |  | 111.808 | 145.7317 | 188.2915 | 241.7629 | 309.0329 | 393.7671 | 500.6219 | 635.5153 | 805.972 | 1021.564 | 1294.4718 | 1640.2015 | 2078.4991 | 2634.5176 | 3340.3066 | 4236.7145 | 5375.8165 | 6259.9544 | 6247.8736 | 6231.2904 | 6208.4241 | 6176.7655 | 6132.7718 | 6071.4336 | 5985.6572 | 5865.3844 | 5696.3377 | 5458.2293 | 5122.2044 | 4647.1897
| TRUE | 4644 | 22009478 | WBE | Blank | 22 | BUS NO.2 | BUEF STAGE 2 | BU | RMS | 2C137 | RMS - 2C137 | RMS 2C13X | Electronic |  | 0.0034106 | 2190 |  | 6.6 | 0.014726 | 0.00014965 | 0.014576 | 60.8067 | 20.9513 | 81.758 | 42.6512 | 5.8934 | 312.2361 |  | 14.9721 | 0.13394 | 0.0013611 | 0.13257 | 553.0441 | 190.5544 | 743.5985 | 387.9178 | 53.6011 | 2839.8247 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 21.3177 | 0.0033803 | 21.3211 | 14.6699 | 2.0677 | 0.050376 |  | 442.5386 | 4024.9422 | 38.1091 | 3986.833 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.018172 | 0.022489 | 0.027904 | 0.034708 | 0.043268 | 0.05405 | 0.067647 | 0.084812 | 0.1065 | 0.13394 | 0.16866 | 0.21265 | 0.26843 | 0.33918 | 0.42899 | 0.54305 | 0.688 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00018467 | 0.00022854 | 0.00028358 | 0.00035272 | 0.00043971 | 0.00054928 | 0.00068746 | 0.00086189 | 0.0010823 | 0.0013611 | 0.001714 | 0.0021611 | 0.0027279 | 0.0034469 | 0.0043595 | 0.0055187 | 0.0069917 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 546.0972 | 675.819 | 838.565 | 1043.0358 | 1300.2716 | 1624.2894 | 2032.8949 | 2548.7181 | 3200.5331 | 4024.9422 | 5068.5231 | 6390.5702 | 8066.5906 | 10192.7674 | 12891.6566 | 16319.4595 | 20675.3082 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 |  | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 37.1089 | 49.1901 | 65.7738 | 88.6407 | 120.3003 | 164.2952 | 225.6351 | 311.414 | 431.6902 | 600.7417 | 838.8568 | 1174.8914 | 1649.9195 |  | 75.0361 | 92.8604 | 115.2224 | 143.3175 | 178.6628 | 223.1842 | 279.3284 | 350.2046 | 439.7668 | 553.0441 | 696.4365 | 878.0914 | 1108.3837 | 1400.5293 | 1771.3681 | 2242.3627 | 2840.8748 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 60.8242 | 78.6486 | 101.0105 | 129.1057 | 164.451 | 208.9724 | 265.1165 | 335.9928 | 425.555 | 538.8322 | 682.2247 | 863.8795 | 1094.1718 | 1386.3175 | 1757.1563 | 2228.1509 | 2826.6629 | 3291.6198 | 3286.0818 | 3278.4799 | 3267.9977 | 3253.485 | 3233.3178 | 3205.1997 | 3165.8788 | 3110.7444 | 3033.2515 | 2924.0999 | 2770.0623 | 2552.3102 |  | 25.8541 | 31.9956 | 39.7005 | 49.3809 | 61.5593 | 76.8994 | 96.2442 | 120.665 | 151.5241 | 190.5544 | 239.9611 | 302.5513 | 381.8998 | 482.5603 | 610.3349 | 772.6187 | 978.8394 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 |  | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.004046 | 0.0053632 | 0.0071713 | 0.0096645 | 0.013116 | 0.017913 | 0.024601 | 0.033953 | 0.047067 | 0.065499 | 0.09146 | 0.1281 | 0.17989 |  | 25.8507 | 31.9922 | 39.6971 | 49.3775 | 61.5559 | 76.896 | 96.2408 | 120.6616 | 151.5207 | 190.5511 | 239.9577 | 302.5479 | 381.8964 | 482.5569 | 610.3315 | 772.6153 | 978.836 | 1140.0032 | 1140.0019 | 1140.0001 | 1139.9976 | 1139.9941 | 1139.9893 | 1139.9826 | 1139.9733 | 1139.9602 | 1139.9417 | 1139.9158 | 1139.8791 | 1139.8273 |  | 86.675 | 110.6407 | 140.7077 | 178.4832 | 226.0069 | 285.8684 | 361.3573 | 456.6544 | 577.0757 | 729.3833 | 922.1824 | 1166.4275 | 1476.0683 | 1868.8744 | 2367.4878 | 3000.7662 | 3805.4989 | 4431.623 | 4426.0837 | 4418.4799 | 4407.9953 | 4393.4791 | 4373.3072 | 4345.1823 | 4305.8521 | 4250.7046 | 4173.1933 | 4064.0157 | 3909.9414 | 3692.1376 |  | 52.632 | 65.1344 | 80.8196 | 100.5262 | 125.3182 | 156.5466 | 195.9273 | 245.6416 | 308.4625 | 387.9178 | 488.4966 | 615.9135 | 777.4458 | 982.3635 | 1242.4784 | 1572.8449 | 1992.655 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 37.9621 | 50.4645 | 66.1497 | 85.8563 | 110.6483 | 141.8766 | 181.2574 | 230.9717 | 293.7926 | 373.2479 | 473.8267 | 601.2436 | 762.7759 | 967.6936 | 1227.8085 | 1558.1749 | 1977.9851 | 2303.1906 | 2297.4741 | 2289.6271 | 2278.8071 | 2263.8266 | 2243.0094 | 2213.9849 | 2173.3966 | 2116.485 | 2036.4943 | 1923.8244 | 1764.8217 | 1540.0507 |  | 7.2725 | 9 | 11.1674 | 13.8903 | 17.316 | 21.631 | 27.0725 | 33.9419 | 42.6222 | 53.6011 | 67.4987 | 85.1047 | 107.4246 | 135.7394 | 171.6811 | 217.33 | 275.3378 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 5.2048 | 6.9323 | 9.0997 | 11.8227 | 15.2483 | 19.5633 | 25.0048 | 31.8742 | 40.5545 | 51.5334 | 65.431 | 83.037 | 105.3569 | 133.6717 | 169.6135 | 215.2623 | 273.2701 | 318.1978 | 317.3921 | 316.2861 | 314.761 | 312.6496 | 309.7154 | 305.6245 | 299.9037 | 291.8821 | 280.6076 | 264.7271 | 242.316 | 210.6351 |  | 385.3025 | 476.8286 | 591.6551 | 735.9208 | 917.4153 | 1146.0282 | 1434.3226 | 1798.265 | 2258.1575 | 2839.8247 | 3576.1302 | 4508.9093 | 5691.4367 | 7191.5748 | 9095.7941 | 11514.3033 | 14587.6013 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 |  | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.060297 | 0.079927 | 0.10687 | 0.14403 | 0.19547 | 0.26696 | 0.36663 | 0.50601 | 0.70144 | 0.97613 | 1.363 | 1.909 | 2.6809 |  | 385.2521 | 476.7782 | 591.6047 | 735.8705 | 917.3649 | 1145.9778 | 1434.2722 | 1798.2147 | 2258.1071 | 2839.7743 | 3576.0799 | 4508.859 | 5691.3863 | 7191.5245 | 9095.7437 | 11514.2529 | 14587.5509 | 16989.4186 | 16989.399 | 16989.372 | 16989.3349 | 16989.2834 | 16989.2119 | 16989.1123 | 16988.9729 | 16988.7775 | 16988.5028 | 16988.1159 | 16987.5698 | 16986.798 |  | 515.094 | 644.8158 | 807.5618 | 1012.0326 | 1269.2684 | 1593.2862 | 2001.8917 | 2517.7149 | 3169.5299 | 3993.939 | 5037.5199 | 6359.567 | 8035.5874 | 10161.7642 | 12860.6534 | 16288.4563 | 20644.305 | 24042.43 | 24030.3489 | 24013.7652 | 23990.8983 | 23959.2388 | 23915.2439 | 23853.904 | 23768.1253 | 23647.8492 | 23478.798 | 23240.6831 | 22904.6489 | 22429.6213
| TRUE | 4645 | 22009479 | WBE | Blank | 22 | BUS NO.2 | BUEF STAGE 3 | BU | RMS | 2T105 | 2T105 | RMS 2T1XX | Electronic |  | 0.0034106 | 2190 |  | 5.5 | 0.0093284 | 9.4799e-05 | 0.0092336 | 38.5187 | 13.2718 | 51.7905 | 27.0179 | 3.7332 | 197.7893 |  | 11.7751 | 0.068685 | 0.000698 | 0.067987 | 283.6131 | 97.7205 | 381.3336 | 198.9328 | 27.4878 | 1456.3243 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 21.3177 | 0.0033803 | 21.3211 | 14.6699 | 2.0677 | 0.050376 |  | 280.3309 | 2064.0785 | 38.1091 | 2025.9694 |  | 0.076124 |  | 5.935 | 6.4045 | 6.911 | 7.4577 | 8.0475 | 8.6841 | 9.3709 | 10.1121 | 10.912 | 11.7751 | 12.7064 | 13.7115 | 14.796 | 15.9663 | 17.2292 | 18.5919 | 20.0625 | 21.6493 | 23.3617 | 25.2095 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.011264 | 0.013642 | 0.016568 | 0.020172 | 0.024619 | 0.030112 | 0.036906 | 0.045319 | 0.055747 | 0.068685 | 0.084752 | 0.10472 | 0.12956 | 0.16048 | 0.199 | 0.24701 | 0.30689 | 0.38161 | 0.47489 | 0.59141 | 0.73701 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00011447 | 0.00013864 | 0.00016837 | 0.000205 | 0.00025019 | 0.00030601 | 0.00037506 | 0.00046055 | 0.00056652 | 0.000698 | 0.00086129 | 0.0010642 | 0.0013167 | 0.0016309 | 0.0020223 | 0.0025102 | 0.0031187 | 0.003878 | 0.004826 | 0.0060101 | 0.0074898 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 338.5106 | 409.9724 | 497.8866 | 606.2007 | 739.8325 | 904.9129 | 1109.0889 | 1361.9036 | 1675.2722 | 2064.0785 | 2546.9218 | 3147.0542 | 3893.5544 | 4822.8007 | 5980.3177 | 7423.0919 | 9222.4782 | 11467.8442 | 14271.1445 | 17772.6595 | 22148.1986 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 |  | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 37.1089 | 49.1901 | 65.7738 | 88.6407 | 120.3003 | 164.2952 | 225.6351 | 311.414 | 431.6902 | 600.7417 | 838.8568 | 1174.8914 | 1649.9195 |  | 46.5128 | 56.3319 | 68.4117 | 83.2945 | 101.6561 | 124.3389 | 152.3935 | 187.1313 | 230.1895 | 283.6131 | 349.9578 | 432.4186 | 534.9908 | 662.6732 | 821.7209 | 1019.9642 | 1267.2075 | 1575.7303 | 1960.9156 | 2442.0386 | 3043.2561 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 32.301 | 42.1201 | 54.1999 | 69.0827 | 87.4443 | 110.127 | 138.1817 | 172.9195 | 215.9777 | 269.4013 | 335.746 | 418.2067 | 520.779 | 648.4614 | 807.5091 | 1005.7524 | 1252.9957 | 1558.7196 | 1938.3669 | 2411.888 | 3002.6234 | 3253.485 | 3233.3178 | 3205.1997 | 3165.8788 | 3110.7444 | 3033.2515 | 2924.0999 | 2770.0623 | 2552.3102 |  | 16.0262 | 19.4095 | 23.5716 | 28.6996 | 35.0262 | 42.8417 | 52.508 | 64.4771 | 79.3131 | 97.7205 | 120.5799 | 148.9922 | 184.3341 | 228.3278 | 283.1286 | 351.4344 | 436.6235 | 542.9267 | 675.6445 | 841.4181 | 1048.571 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 |  | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.004046 | 0.0053632 | 0.0071713 | 0.0096645 | 0.013116 | 0.017913 | 0.024601 | 0.033953 | 0.047067 | 0.065499 | 0.09146 | 0.1281 | 0.17989 |  | 16.0229 | 19.4061 | 23.5683 | 28.6962 | 35.0228 | 42.8383 | 52.5047 | 64.4738 | 79.3097 | 97.7171 | 120.5766 | 148.9889 | 184.3307 | 228.3244 | 283.1252 | 351.431 | 436.6201 | 542.9227 | 675.6391 | 841.411 | 1048.5614 | 1139.9941 | 1139.9893 | 1139.9826 | 1139.9733 | 1139.9602 | 1139.9417 | 1139.9158 | 1139.8791 | 1139.8273 |  | 48.3238 | 61.5262 | 77.7682 | 97.7789 | 122.4671 | 152.9653 | 190.6863 | 237.3932 | 295.2874 | 367.1184 | 456.3226 | 567.1956 | 705.1097 | 876.7858 | 1090.6343 | 1357.1834 | 1689.6158 | 2101.6423 | 2614.0061 | 3253.2989 | 4051.1847 | 4393.4791 | 4373.3072 | 4345.1823 | 4305.8521 | 4250.7046 | 4173.1933 | 4064.0157 | 3909.9414 | 3692.1376 |  | 32.6251 | 39.5125 | 47.9856 | 58.4247 | 71.3039 | 87.2141 | 106.8923 | 131.2582 | 161.4602 | 198.9328 | 245.4685 | 303.3083 | 375.2549 | 464.8143 | 576.374 | 715.4264 | 888.8485 | 1105.2535 | 1375.4313 | 1712.9021 | 2134.6099 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 17.9552 | 24.8426 | 33.3156 | 43.7548 | 56.634 | 72.5442 | 92.2224 | 116.5883 | 146.7903 | 184.2628 | 230.7986 | 288.6384 | 360.585 | 450.1443 | 561.7041 | 700.7565 | 874.1786 | 1087.6945 | 1352.1559 | 1681.7796 | 2092.6674 | 2263.8266 | 2243.0094 | 2213.9849 | 2173.3966 | 2116.485 | 2036.4943 | 1923.8244 | 1764.8217 | 1540.0507 |  | 4.508 | 5.4597 | 6.6305 | 8.0729 | 9.8525 | 12.0509 | 14.77 | 18.1368 | 22.31 | 27.4878 | 33.9179 | 41.91 | 51.8514 | 64.2263 | 79.6413 | 98.855 | 122.8179 | 152.7199 | 190.0521 | 236.6826 | 294.9526 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 2.4403 | 3.392 | 4.5628 | 6.0052 | 7.7848 | 9.9832 | 12.7023 | 16.0691 | 20.2423 | 25.4201 | 31.8502 | 39.8423 | 49.7837 | 62.1587 | 77.5736 | 96.7873 | 120.7502 | 150.245 | 186.7715 | 232.2959 | 289.0409 | 312.6496 | 309.7154 | 305.6245 | 299.9037 | 291.8821 | 280.6076 | 264.7271 | 242.316 | 210.6351 |  | 238.8384 | 289.2588 | 351.2872 | 427.7089 | 521.9938 | 638.4673 | 782.525 | 960.9001 | 1181.9994 | 1456.3243 | 1796.9976 | 2220.425 | 2747.1232 | 3402.7592 | 4219.4529 | 5237.4119 | 6506.9808 | 8091.2138 | 10069.1009 | 12539.6182 | 15626.8089 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 |  | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.060297 | 0.079927 | 0.10687 | 0.14403 | 0.19547 | 0.26696 | 0.36663 | 0.50601 | 0.70144 | 0.97613 | 1.363 | 1.909 | 2.6809 |  | 238.7881 | 289.2084 | 351.2369 | 427.6586 | 521.9434 | 638.417 | 782.4747 | 960.8497 | 1181.9491 | 1456.2739 | 1796.9473 | 2220.3746 | 2747.0728 | 3402.7088 | 4219.4025 | 5237.3615 | 6506.9305 | 8091.1535 | 10069.021 | 12539.5113 | 15626.6648 | 16989.2834 | 16989.2119 | 16989.1123 | 16988.9729 | 16988.7775 | 16988.5028 | 16988.1159 | 16987.5698 | 16986.798 |  | 307.5074 | 378.9692 | 466.8834 | 575.1975 | 708.8293 | 873.9097 | 1078.0857 | 1330.9004 | 1644.269 | 2033.0753 | 2515.9186 | 3116.051 | 3862.5512 | 4791.7975 | 5949.3145 | 7392.0887 | 9191.475 | 11430.7353 | 14221.9544 | 17706.8858 | 22059.5579 | 23959.2388 | 23915.2439 | 23853.904 | 23768.1253 | 23647.8492 | 23478.798 | 23240.6831 | 22904.6489 | 22429.6213
| TRUE | 4646 | 22008233 | WBE | Blank | 22 | BUS NO.2 | HIBP | X | ABB | RADHA_3110 | RADHA 3110 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 61.3179 | 194.4647 | 255.7826 | 49.6875 | 5.9058 | 2898.0985 |  | 14.9721 | 0.13394 | 0.012633 | 0.1213 | 557.6939 | 1768.6796 | 2326.3735 | 451.9134 | 53.7138 | 26358.5558 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 21.3178 | 0.033289 | 21.3511 | 14.6711 | 2.0677 | 0.4961 |  | 3209.4744 | 29190.5565 | 38.5861 | 29151.9705 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.018172 | 0.022489 | 0.027904 | 0.034708 | 0.043268 | 0.05405 | 0.067647 | 0.084812 | 0.1065 | 0.13394 | 0.16866 | 0.21265 | 0.26843 | 0.33918 | 0.42899 | 0.54305 | 0.688 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0017141 | 0.0021213 | 0.0026321 | 0.0032739 | 0.0040813 | 0.0050983 | 0.0063808 | 0.0079999 | 0.010046 | 0.012633 | 0.015909 | 0.020059 | 0.025319 | 0.031993 | 0.040464 | 0.051223 | 0.064895 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 3960.5244 | 4901.3207 | 6081.6224 | 7564.5298 | 9430.1112 | 11780.0232 | 14743.4007 | 18484.3652 | 23211.5991 | 29190.5565 | 36759.0404 | 46347.0764 | 58502.2738 | 73922.1933 | 93495.6618 | 118355.5161 | 149945.9445 | 174634.8431 | 174634.8431 | 174634.8431 | 174634.8431 | 174634.8431 | 174634.8431 | 174634.8431 | 174634.8431 | 174634.8431 | 174634.8431 | 174634.8431 | 174634.8431 | 174634.8431 |  | 31.4805 | 31.4805 | 31.4805 | 31.4805 | 31.4805 | 31.4805 | 31.4805 | 31.4805 | 31.4805 | 31.4805 | 31.4805 | 31.4805 | 31.4805 | 31.4805 | 31.4805 | 31.4805 | 31.4805 | 37.6801 | 49.9473 | 66.7863 | 90.0052 | 122.152 | 166.8242 | 229.1083 | 316.2076 | 438.3352 | 609.9888 | 851.7693 | 1192.9763 | 1675.3165 |  | 75.6669 | 93.6411 | 116.1911 | 144.5225 | 180.165 | 225.0607 | 281.6769 | 353.1491 | 443.4642 | 557.6939 | 702.2919 | 885.4741 | 1117.7026 | 1412.3046 | 1786.2613 | 2261.2159 | 2864.76 | 3336.4485 | 3336.4485 | 3336.4485 | 3336.4485 | 3336.4485 | 3336.4485 | 3336.4485 | 3336.4485 | 3336.4485 | 3336.4485 | 3336.4485 | 3336.4485 | 3336.4485 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 61.4551 | 79.4292 | 101.9792 | 130.3106 | 165.9531 | 210.8488 | 267.465 | 338.9372 | 429.2523 | 543.482 | 688.0801 | 871.2622 | 1103.4907 | 1398.0927 | 1772.0494 | 2247.004 | 2850.5481 | 3319.4377 | 3313.8997 | 3306.2977 | 3295.8155 | 3281.3028 | 3261.1355 | 3233.0173 | 3193.6962 | 3138.5616 | 3061.0684 | 2951.9164 | 2797.8781 | 2580.1251 |  | 239.9714 | 296.975 | 368.4904 | 458.341 | 571.3781 | 713.7612 | 893.3146 | 1119.9827 | 1406.4097 | 1768.6796 | 2227.2602 | 2808.2071 | 3544.7004 | 4479.0059 | 5664.9782 | 7171.2571 | 9085.3468 | 10581.2673 | 10581.2673 | 10581.2673 | 10581.2673 | 10581.2673 | 10581.2673 | 10581.2673 | 10581.2673 | 10581.2673 | 10581.2673 | 10581.2673 | 10581.2673 | 10581.2673 |  | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.033289 | 0.039844 | 0.052816 | 0.070622 | 0.095175 | 0.12917 | 0.17641 | 0.24227 | 0.33437 | 0.46351 | 0.64503 | 0.90069 | 1.2615 | 1.7715 |  | 239.9381 | 296.9417 | 368.4572 | 458.3077 | 571.3448 | 713.7279 | 893.2814 | 1119.9494 | 1406.3764 | 1768.6463 | 2227.2269 | 2808.1738 | 3544.6671 | 4478.9726 | 5664.945 | 7171.2238 | 9085.3135 | 10581.2274 | 10581.2145 | 10581.1967 | 10581.1721 | 10581.1381 | 10581.0909 | 10581.025 | 10580.9329 | 10580.8038 | 10580.6223 | 10580.3666 | 10580.0058 | 10579.4957 |  | 301.3932 | 376.371 | 470.4364 | 588.6183 | 737.2979 | 924.5767 | 1160.7463 | 1458.8866 | 1835.6287 | 2312.1283 | 2915.3069 | 3679.436 | 4648.1578 | 5877.0653 | 7436.9943 | 9418.2278 | 11935.8617 | 13900.6652 | 13895.1142 | 13887.4944 | 13876.9876 | 13862.4409 | 13842.2264 | 13814.0423 | 13774.6291 | 13719.3654 | 13641.6906 | 13532.2829 | 13377.8839 | 13159.6208 |  | 61.3148 | 75.8798 | 94.1526 | 117.1102 | 145.9922 | 182.3724 | 228.2499 | 286.1656 | 359.3502 | 451.9134 | 569.0849 | 717.522 | 905.7026 | 1144.426 | 1447.4526 | 1832.3203 | 2321.3873 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 46.6437 | 61.2086 | 79.4815 | 102.4391 | 131.3211 | 167.7012 | 213.5787 | 271.4945 | 344.6791 | 437.2423 | 554.4137 | 702.8509 | 891.0315 | 1129.7549 | 1432.7814 | 1817.6491 | 2306.7162 | 2686.0479 | 2680.3309 | 2672.4833 | 2661.6624 | 2646.6807 | 2625.8617 | 2596.8349 | 2556.2432 | 2499.3269 | 2419.3296 | 2306.6504 | 2147.6344 | 1922.8449 |  | 7.2878 | 9.019 | 11.1908 | 13.9196 | 17.3524 | 21.6765 | 27.1295 | 34.0132 | 42.7119 | 53.7138 | 67.6406 | 85.2837 | 107.6505 | 136.0249 | 172.0422 | 217.787 | 275.9169 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 5.2201 | 6.9513 | 9.1232 | 11.8519 | 15.2847 | 19.6088 | 25.0618 | 31.9455 | 40.6442 | 51.6461 | 65.5729 | 83.216 | 105.5829 | 133.9572 | 169.9745 | 215.7193 | 273.8492 | 318.8722 | 318.0665 | 316.9605 | 315.4354 | 313.3239 | 310.3898 | 306.2989 | 300.578 | 292.5565 | 281.2819 | 265.4014 | 242.9903 | 211.3093 |  | 3576.2834 | 4425.8058 | 5491.5973 | 6830.6365 | 8515.2235 | 10637.1524 | 13313.0298 | 16691.0545 | 20959.6631 | 26358.5558 | 33192.7628 | 41850.5895 | 52826.5177 | 66750.432 | 84424.9275 | 106872.9359 | 135398.5335 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 |  | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.5938 | 0.78712 | 1.0525 | 1.4184 | 1.925 | 2.629 | 3.6105 | 4.9831 | 6.9077 | 9.6128 | 13.423 | 18.8001 | 26.4013 |  | 3575.7873 | 4425.3097 | 5491.1012 | 6830.1404 | 8514.7274 | 10636.6563 | 13312.5337 | 16690.5584 | 20959.167 | 26358.0597 | 33192.2667 | 41850.0934 | 52826.0216 | 66749.9359 | 84424.4314 | 106872.4398 | 135398.0374 | 157691.5781 | 157691.3848 | 157691.1194 | 157690.7535 | 157690.2469 | 157689.5429 | 157688.5614 | 157687.1888 | 157685.2642 | 157682.5591 | 157678.7489 | 157673.3718 | 157665.7706 |  | 3929.0443 | 4869.8406 | 6050.1423 | 7533.0497 | 9398.6311 | 11748.5431 | 14711.9205 | 18452.8851 | 23180.119 | 29159.0764 | 36727.5603 | 46315.5963 | 58470.7937 | 73890.7132 | 93464.1816 | 118324.036 | 149914.4644 | 174597.1634 | 174584.8964 | 174568.0576 | 174544.8389 | 174512.6924 | 174468.0208 | 174405.7374 | 174318.6391 | 174196.5129 | 174024.8612 | 173783.0836 | 173441.8804 | 172959.5457
| TRUE | 4647 | 22009475 | WBE | Blank | 22 | BUS NO.2 | SINGLE ZONE BUS DIST | Y | Schweitzer | SEL_311A | SEL 311A | SEL 300s | Digital |  | 0.0034106 | 1 |  | 6.6 | 0.017308 | 8.0863e-08 | 0.017308 | 59.4958 | 0.0084906 | 59.5043 | 49.1308 | 6.9249 | 0.16871 |  | 14.9721 | 0.15742 | 7.3546e-07 | 0.15742 | 541.1213 | 0.077223 | 541.1986 | 446.8507 | 62.9826 | 1.5345 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 17.7648 | 0.0025352 | 17.7673 | 14.6699 | 2.0677 | 0.050376 |  | 115.7287 | 1052.5663 | 34.5553 | 1018.011 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021358 | 0.026432 | 0.032797 | 0.040794 | 0.050854 | 0.063527 | 0.079507 | 0.099681 | 0.12517 | 0.15742 | 0.19823 | 0.24994 | 0.31549 | 0.39864 | 0.5042 | 0.63826 | 0.80862 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 9.9786e-08 | 1.2349e-07 | 1.5323e-07 | 1.9059e-07 | 2.3759e-07 | 2.968e-07 | 3.7146e-07 | 4.6572e-07 | 5.8482e-07 | 7.3546e-07 | 9.2615e-07 | 1.1677e-06 | 1.474e-06 | 1.8625e-06 | 2.3556e-06 | 2.982e-06 | 3.7779e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 4.4e-06 | 142.8104 | 176.734 | 219.2939 | 272.7652 | 340.0352 | 424.7694 | 531.6242 | 666.5176 | 836.9744 | 1052.5663 | 1325.4741 | 1671.2039 | 2109.5015 | 2665.52 | 3371.3089 | 4267.7168 | 5406.8188 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 | 6297.0623 |  | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 31.0024 | 37.1079 | 49.1887 | 65.772 | 88.6383 | 120.2969 | 164.2906 | 225.6288 | 311.4053 | 431.6782 | 600.7249 | 838.8335 | 1174.8587 | 1649.8736 |  | 73.4184 | 90.8585 | 112.7384 | 140.2278 | 174.8111 | 218.3727 | 273.3065 | 342.6548 | 430.2861 | 541.1213 | 681.4225 | 859.1611 | 1084.4887 | 1370.3362 | 1733.1803 | 2194.021 | 2779.6301 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 | 3237.3018 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 59.2066 | 76.6466 | 98.5265 | 126.016 | 160.5993 | 204.1609 | 259.0947 | 328.443 | 416.0743 | 526.9095 | 667.2106 | 844.9493 | 1070.2769 | 1356.1244 | 1718.9685 | 2179.8092 | 2765.4183 | 3220.2911 | 3214.7531 | 3207.1512 | 3196.669 | 3182.1563 | 3161.9891 | 3133.871 | 3094.5501 | 3039.4157 | 2961.9228 | 2852.7712 | 2698.7336 | 2480.9815 |  | 0.010478 | 0.012966 | 0.016089 | 0.020012 | 0.024947 | 0.031164 | 0.039004 | 0.0489 | 0.061406 | 0.077223 | 0.097246 | 0.12261 | 0.15477 | 0.19556 | 0.24734 | 0.31311 | 0.39668 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 | 0.46199 |  | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0025352 | 0.0030345 | 0.0040224 | 0.0053785 | 0.0072484 | 0.0098372 | 0.013435 | 0.018451 | 0.025465 | 0.0353 | 0.049124 | 0.068595 | 0.096074 | 0.13492 |  | 0.0079423 | 0.010431 | 0.013554 | 0.017477 | 0.022412 | 0.028629 | 0.036468 | 0.046365 | 0.058871 | 0.074688 | 0.094711 | 0.12008 | 0.15223 | 0.19303 | 0.24481 | 0.31057 | 0.39415 | 0.45896 | 0.45797 | 0.45662 | 0.45475 | 0.45216 | 0.44856 | 0.44354 | 0.43653 | 0.42669 | 0.41287 | 0.3934 | 0.36592 | 0.32708 |  | 59.2145 | 76.6571 | 98.5401 | 126.0335 | 160.6217 | 204.1895 | 259.1311 | 328.4893 | 416.1332 | 526.9842 | 667.3053 | 845.0694 | 1070.4291 | 1356.3174 | 1719.2133 | 2180.1198 | 2765.8124 | 3220.75 | 3215.2111 | 3207.6078 | 3197.1237 | 3182.6085 | 3162.4377 | 3134.3145 | 3094.9866 | 3039.8424 | 2962.3357 | 2853.1646 | 2699.0995 | 2481.3086 |  | 60.6279 | 75.0297 | 93.0978 | 115.7983 | 144.3567 | 180.3293 | 225.6928 | 282.9597 | 355.3245 | 446.8507 | 562.7095 | 709.4837 | 895.5562 | 1131.6052 | 1431.237 | 1811.793 | 2295.3811 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 | 2673.3202 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 45.958 | 60.3598 | 78.4279 | 101.1283 | 129.6868 | 165.6593 | 211.0229 | 268.2898 | 340.6546 | 432.1808 | 548.0396 | 694.8138 | 880.8862 | 1116.9353 | 1416.567 | 1797.1231 | 2280.7112 | 2655.7612 | 2650.0447 | 2642.1978 | 2631.3777 | 2616.3973 | 2595.58 | 2566.5555 | 2525.9672 | 2469.0557 | 2389.0649 | 2276.395 | 2117.3923 | 1892.6214 |  | 8.5454 | 10.5753 | 13.1219 | 16.3215 | 20.3467 | 25.417 | 31.8109 | 39.8825 | 50.0822 | 62.9826 | 79.3126 | 100.0001 | 126.2266 | 159.4971 | 201.7295 | 255.368 | 323.5286 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 6.4777 | 8.5076 | 11.0542 | 14.2538 | 18.279 | 23.3493 | 29.7432 | 37.8148 | 48.0145 | 60.9149 | 77.2449 | 97.9324 | 124.1589 | 157.4294 | 199.6618 | 253.3003 | 321.4609 | 374.3234 | 373.5176 | 372.4116 | 370.8866 | 368.7751 | 365.8409 | 361.75 | 356.0292 | 348.0076 | 336.7331 | 320.8526 | 298.4415 | 266.7606 |  | 0.20819 | 0.25765 | 0.3197 | 0.39765 | 0.49572 | 0.61925 | 0.77502 | 0.97168 | 1.2202 | 1.5345 | 1.9323 | 2.4364 | 3.0753 | 3.8859 | 4.9148 | 6.2217 | 7.8823 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 | 9.1801 |  | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.060297 | 0.079927 | 0.10687 | 0.14403 | 0.19547 | 0.26696 | 0.36663 | 0.50601 | 0.70144 | 0.97613 | 1.363 | 1.909 | 2.6809 |  | 0.15782 | 0.20727 | 0.26932 | 0.34727 | 0.44534 | 0.56887 | 0.72465 | 0.9213 | 1.1698 | 1.4841 | 1.882 | 2.386 | 3.0249 | 3.8355 | 4.8645 | 6.1713 | 7.8319 | 9.1198 | 9.1002 | 9.0732 | 9.0361 | 8.9846 | 8.9132 | 8.8135 | 8.6741 | 8.4787 | 8.204 | 7.8171 | 7.2711 | 6.4992 |  | 111.808 | 145.7317 | 188.2915 | 241.7629 | 309.0329 | 393.7671 | 500.6219 | 635.5153 | 805.972 | 1021.564 | 1294.4718 | 1640.2015 | 2078.4991 | 2634.5176 | 3340.3066 | 4236.7145 | 5375.8165 | 6259.9544 | 6247.8736 | 6231.2904 | 6208.4241 | 6176.7655 | 6132.7718 | 6071.4336 | 5985.6572 | 5865.3844 | 5696.3377 | 5458.2293 | 5122.2044 | 4647.1897
| TRUE | 4648 | 22008230 | WBE | Blank | 22 | BUS NO.3 | BACKUP EARTH FAULT | BU | RMS | 2C136 | 2C136 | RMS 2C13X | Electronic |  | 0.0034106 | 2190 |  | 6.6 | 0.014726 | 0.00014965 | 0.014576 | 60.8067 | 20.9513 | 81.758 | 42.6512 | 5.8934 | 312.2361 |  | 14.9721 | 0.13394 | 0.0013611 | 0.13257 | 553.0441 | 190.5544 | 743.5985 | 387.9178 | 53.6011 | 2839.8247 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 21.3177 | 0.0033803 | 21.3211 | 14.6699 | 2.0677 | 0.050376 |  | 442.5386 | 4024.9422 | 38.1091 | 3986.833 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.018172 | 0.022489 | 0.027904 | 0.034708 | 0.043268 | 0.05405 | 0.067647 | 0.084812 | 0.1065 | 0.13394 | 0.16866 | 0.21265 | 0.26843 | 0.33918 | 0.42899 | 0.54305 | 0.688 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00018467 | 0.00022854 | 0.00028358 | 0.00035272 | 0.00043971 | 0.00054928 | 0.00068746 | 0.00086189 | 0.0010823 | 0.0013611 | 0.001714 | 0.0021611 | 0.0027279 | 0.0034469 | 0.0043595 | 0.0055187 | 0.0069917 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 546.0972 | 675.819 | 838.565 | 1043.0358 | 1300.2716 | 1624.2894 | 2032.8949 | 2548.7181 | 3200.5331 | 4024.9422 | 5068.5231 | 6390.5702 | 8066.5906 | 10192.7674 | 12891.6566 | 16319.4595 | 20675.3082 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 |  | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 37.1089 | 49.1901 | 65.7738 | 88.6407 | 120.3003 | 164.2952 | 225.6351 | 311.414 | 431.6902 | 600.7417 | 838.8568 | 1174.8914 | 1649.9195 |  | 75.0361 | 92.8604 | 115.2224 | 143.3175 | 178.6628 | 223.1842 | 279.3284 | 350.2046 | 439.7668 | 553.0441 | 696.4365 | 878.0914 | 1108.3837 | 1400.5293 | 1771.3681 | 2242.3627 | 2840.8748 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 60.8242 | 78.6486 | 101.0105 | 129.1057 | 164.451 | 208.9724 | 265.1165 | 335.9928 | 425.555 | 538.8322 | 682.2247 | 863.8795 | 1094.1718 | 1386.3175 | 1757.1563 | 2228.1509 | 2826.6629 | 3291.6198 | 3286.0818 | 3278.4799 | 3267.9977 | 3253.485 | 3233.3178 | 3205.1997 | 3165.8788 | 3110.7444 | 3033.2515 | 2924.0999 | 2770.0623 | 2552.3102 |  | 25.8541 | 31.9956 | 39.7005 | 49.3809 | 61.5593 | 76.8994 | 96.2442 | 120.665 | 151.5241 | 190.5544 | 239.9611 | 302.5513 | 381.8998 | 482.5603 | 610.3349 | 772.6187 | 978.8394 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 |  | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.004046 | 0.0053632 | 0.0071713 | 0.0096645 | 0.013116 | 0.017913 | 0.024601 | 0.033953 | 0.047067 | 0.065499 | 0.09146 | 0.1281 | 0.17989 |  | 25.8507 | 31.9922 | 39.6971 | 49.3775 | 61.5559 | 76.896 | 96.2408 | 120.6616 | 151.5207 | 190.5511 | 239.9577 | 302.5479 | 381.8964 | 482.5569 | 610.3315 | 772.6153 | 978.836 | 1140.0032 | 1140.0019 | 1140.0001 | 1139.9976 | 1139.9941 | 1139.9893 | 1139.9826 | 1139.9733 | 1139.9602 | 1139.9417 | 1139.9158 | 1139.8791 | 1139.8273 |  | 86.675 | 110.6407 | 140.7077 | 178.4832 | 226.0069 | 285.8684 | 361.3573 | 456.6544 | 577.0757 | 729.3833 | 922.1824 | 1166.4275 | 1476.0683 | 1868.8744 | 2367.4878 | 3000.7662 | 3805.4989 | 4431.623 | 4426.0837 | 4418.4799 | 4407.9953 | 4393.4791 | 4373.3072 | 4345.1823 | 4305.8521 | 4250.7046 | 4173.1933 | 4064.0157 | 3909.9414 | 3692.1376 |  | 52.632 | 65.1344 | 80.8196 | 100.5262 | 125.3182 | 156.5466 | 195.9273 | 245.6416 | 308.4625 | 387.9178 | 488.4966 | 615.9135 | 777.4458 | 982.3635 | 1242.4784 | 1572.8449 | 1992.655 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 37.9621 | 50.4645 | 66.1497 | 85.8563 | 110.6483 | 141.8766 | 181.2574 | 230.9717 | 293.7926 | 373.2479 | 473.8267 | 601.2436 | 762.7759 | 967.6936 | 1227.8085 | 1558.1749 | 1977.9851 | 2303.1906 | 2297.4741 | 2289.6271 | 2278.8071 | 2263.8266 | 2243.0094 | 2213.9849 | 2173.3966 | 2116.485 | 2036.4943 | 1923.8244 | 1764.8217 | 1540.0507 |  | 7.2725 | 9 | 11.1674 | 13.8903 | 17.316 | 21.631 | 27.0725 | 33.9419 | 42.6222 | 53.6011 | 67.4987 | 85.1047 | 107.4246 | 135.7394 | 171.6811 | 217.33 | 275.3378 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 5.2048 | 6.9323 | 9.0997 | 11.8227 | 15.2483 | 19.5633 | 25.0048 | 31.8742 | 40.5545 | 51.5334 | 65.431 | 83.037 | 105.3569 | 133.6717 | 169.6135 | 215.2623 | 273.2701 | 318.1978 | 317.3921 | 316.2861 | 314.761 | 312.6496 | 309.7154 | 305.6245 | 299.9037 | 291.8821 | 280.6076 | 264.7271 | 242.316 | 210.6351 |  | 385.3025 | 476.8286 | 591.6551 | 735.9208 | 917.4153 | 1146.0282 | 1434.3226 | 1798.265 | 2258.1575 | 2839.8247 | 3576.1302 | 4508.9093 | 5691.4367 | 7191.5748 | 9095.7941 | 11514.3033 | 14587.6013 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 |  | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.060297 | 0.079927 | 0.10687 | 0.14403 | 0.19547 | 0.26696 | 0.36663 | 0.50601 | 0.70144 | 0.97613 | 1.363 | 1.909 | 2.6809 |  | 385.2521 | 476.7782 | 591.6047 | 735.8705 | 917.3649 | 1145.9778 | 1434.2722 | 1798.2147 | 2258.1071 | 2839.7743 | 3576.0799 | 4508.859 | 5691.3863 | 7191.5245 | 9095.7437 | 11514.2529 | 14587.5509 | 16989.4186 | 16989.399 | 16989.372 | 16989.3349 | 16989.2834 | 16989.2119 | 16989.1123 | 16988.9729 | 16988.7775 | 16988.5028 | 16988.1159 | 16987.5698 | 16986.798 |  | 515.094 | 644.8158 | 807.5618 | 1012.0326 | 1269.2684 | 1593.2862 | 2001.8917 | 2517.7149 | 3169.5299 | 3993.939 | 5037.5199 | 6359.567 | 8035.5874 | 10161.7642 | 12860.6534 | 16288.4563 | 20644.305 | 24042.43 | 24030.3489 | 24013.7652 | 23990.8983 | 23959.2388 | 23915.2439 | 23853.904 | 23768.1253 | 23647.8492 | 23478.798 | 23240.6831 | 22904.6489 | 22429.6213
| TRUE | 4649 | 22008231 | WBE | Blank | 22 | BUS NO.3 | BUEF STAGE 3 | BU | RMS | 2T103 | 2T103 | RMS 2T1XX | Electronic |  | 0.0034106 | 2190 |  | 5.5 | 0.0093284 | 9.4799e-05 | 0.0092336 | 38.5187 | 13.2718 | 51.7905 | 27.0179 | 3.7332 | 197.7893 |  | 11.7751 | 0.068685 | 0.000698 | 0.067987 | 283.6131 | 97.7205 | 381.3336 | 198.9328 | 27.4878 | 1456.3243 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 21.3177 | 0.0033803 | 21.3211 | 14.6699 | 2.0677 | 0.050376 |  | 280.3309 | 2064.0785 | 38.1091 | 2025.9694 |  | 0.076124 |  | 5.935 | 6.4045 | 6.911 | 7.4577 | 8.0475 | 8.6841 | 9.3709 | 10.1121 | 10.912 | 11.7751 | 12.7064 | 13.7115 | 14.796 | 15.9663 | 17.2292 | 18.5919 | 20.0625 | 21.6493 | 23.3617 | 25.2095 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.011264 | 0.013642 | 0.016568 | 0.020172 | 0.024619 | 0.030112 | 0.036906 | 0.045319 | 0.055747 | 0.068685 | 0.084752 | 0.10472 | 0.12956 | 0.16048 | 0.199 | 0.24701 | 0.30689 | 0.38161 | 0.47489 | 0.59141 | 0.73701 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00011447 | 0.00013864 | 0.00016837 | 0.000205 | 0.00025019 | 0.00030601 | 0.00037506 | 0.00046055 | 0.00056652 | 0.000698 | 0.00086129 | 0.0010642 | 0.0013167 | 0.0016309 | 0.0020223 | 0.0025102 | 0.0031187 | 0.003878 | 0.004826 | 0.0060101 | 0.0074898 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 338.5106 | 409.9724 | 497.8866 | 606.2007 | 739.8325 | 904.9129 | 1109.0889 | 1361.9036 | 1675.2722 | 2064.0785 | 2546.9218 | 3147.0542 | 3893.5544 | 4822.8007 | 5980.3177 | 7423.0919 | 9222.4782 | 11467.8442 | 14271.1445 | 17772.6595 | 22148.1986 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 | 24079.5389 |  | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 31.0032 | 37.1089 | 49.1901 | 65.7738 | 88.6407 | 120.3003 | 164.2952 | 225.6351 | 311.414 | 431.6902 | 600.7417 | 838.8568 | 1174.8914 | 1649.9195 |  | 46.5128 | 56.3319 | 68.4117 | 83.2945 | 101.6561 | 124.3389 | 152.3935 | 187.1313 | 230.1895 | 283.6131 | 349.9578 | 432.4186 | 534.9908 | 662.6732 | 821.7209 | 1019.9642 | 1267.2075 | 1575.7303 | 1960.9156 | 2442.0386 | 3043.2561 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 | 3308.6305 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 32.301 | 42.1201 | 54.1999 | 69.0827 | 87.4443 | 110.127 | 138.1817 | 172.9195 | 215.9777 | 269.4013 | 335.746 | 418.2067 | 520.779 | 648.4614 | 807.5091 | 1005.7524 | 1252.9957 | 1558.7196 | 1938.3669 | 2411.888 | 3002.6234 | 3253.485 | 3233.3178 | 3205.1997 | 3165.8788 | 3110.7444 | 3033.2515 | 2924.0999 | 2770.0623 | 2552.3102 |  | 16.0262 | 19.4095 | 23.5716 | 28.6996 | 35.0262 | 42.8417 | 52.508 | 64.4771 | 79.3131 | 97.7205 | 120.5799 | 148.9922 | 184.3341 | 228.3278 | 283.1286 | 351.4344 | 436.6235 | 542.9267 | 675.6445 | 841.4181 | 1048.571 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 | 1140.0072 |  | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.0033803 | 0.004046 | 0.0053632 | 0.0071713 | 0.0096645 | 0.013116 | 0.017913 | 0.024601 | 0.033953 | 0.047067 | 0.065499 | 0.09146 | 0.1281 | 0.17989 |  | 16.0229 | 19.4061 | 23.5683 | 28.6962 | 35.0228 | 42.8383 | 52.5047 | 64.4738 | 79.3097 | 97.7171 | 120.5766 | 148.9889 | 184.3307 | 228.3244 | 283.1252 | 351.431 | 436.6201 | 542.9227 | 675.6391 | 841.411 | 1048.5614 | 1139.9941 | 1139.9893 | 1139.9826 | 1139.9733 | 1139.9602 | 1139.9417 | 1139.9158 | 1139.8791 | 1139.8273 |  | 48.3238 | 61.5262 | 77.7682 | 97.7789 | 122.4671 | 152.9653 | 190.6863 | 237.3932 | 295.2874 | 367.1184 | 456.3226 | 567.1956 | 705.1097 | 876.7858 | 1090.6343 | 1357.1834 | 1689.6158 | 2101.6423 | 2614.0061 | 3253.2989 | 4051.1847 | 4393.4791 | 4373.3072 | 4345.1823 | 4305.8521 | 4250.7046 | 4173.1933 | 4064.0157 | 3909.9414 | 3692.1376 |  | 32.6251 | 39.5125 | 47.9856 | 58.4247 | 71.3039 | 87.2141 | 106.8923 | 131.2582 | 161.4602 | 198.9328 | 245.4685 | 303.3083 | 375.2549 | 464.8143 | 576.374 | 715.4264 | 888.8485 | 1105.2535 | 1375.4313 | 1712.9021 | 2134.6099 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 17.9552 | 24.8426 | 33.3156 | 43.7548 | 56.634 | 72.5442 | 92.2224 | 116.5883 | 146.7903 | 184.2628 | 230.7986 | 288.6384 | 360.585 | 450.1443 | 561.7041 | 700.7565 | 874.1786 | 1087.6945 | 1352.1559 | 1681.7796 | 2092.6674 | 2263.8266 | 2243.0094 | 2213.9849 | 2173.3966 | 2116.485 | 2036.4943 | 1923.8244 | 1764.8217 | 1540.0507 |  | 4.508 | 5.4597 | 6.6305 | 8.0729 | 9.8525 | 12.0509 | 14.77 | 18.1368 | 22.31 | 27.4878 | 33.9179 | 41.91 | 51.8514 | 64.2263 | 79.6413 | 98.855 | 122.8179 | 152.7199 | 190.0521 | 236.6826 | 294.9526 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 2.4403 | 3.392 | 4.5628 | 6.0052 | 7.7848 | 9.9832 | 12.7023 | 16.0691 | 20.2423 | 25.4201 | 31.8502 | 39.8423 | 49.7837 | 62.1587 | 77.5736 | 96.7873 | 120.7502 | 150.245 | 186.7715 | 232.2959 | 289.0409 | 312.6496 | 309.7154 | 305.6245 | 299.9037 | 291.8821 | 280.6076 | 264.7271 | 242.316 | 210.6351 |  | 238.8384 | 289.2588 | 351.2872 | 427.7089 | 521.9938 | 638.4673 | 782.525 | 960.9001 | 1181.9994 | 1456.3243 | 1796.9976 | 2220.425 | 2747.1232 | 3402.7592 | 4219.4529 | 5237.4119 | 6506.9808 | 8091.2138 | 10069.1009 | 12539.6182 | 15626.8089 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 |  | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.060297 | 0.079927 | 0.10687 | 0.14403 | 0.19547 | 0.26696 | 0.36663 | 0.50601 | 0.70144 | 0.97613 | 1.363 | 1.909 | 2.6809 |  | 238.7881 | 289.2084 | 351.2369 | 427.6586 | 521.9434 | 638.417 | 782.4747 | 960.8497 | 1181.9491 | 1456.2739 | 1796.9473 | 2220.3746 | 2747.0728 | 3402.7088 | 4219.4025 | 5237.3615 | 6506.9305 | 8091.1535 | 10069.021 | 12539.5113 | 15626.6648 | 16989.2834 | 16989.2119 | 16989.1123 | 16988.9729 | 16988.7775 | 16988.5028 | 16988.1159 | 16987.5698 | 16986.798 |  | 307.5074 | 378.9692 | 466.8834 | 575.1975 | 708.8293 | 873.9097 | 1078.0857 | 1330.9004 | 1644.269 | 2033.0753 | 2515.9186 | 3116.051 | 3862.5512 | 4791.7975 | 5949.3145 | 7392.0887 | 9191.475 | 11430.7353 | 14221.9544 | 17706.8858 | 22059.5579 | 23959.2388 | 23915.2439 | 23853.904 | 23768.1253 | 23647.8492 | 23478.798 | 23240.6831 | 22904.6489 | 22429.6213
| TRUE | 4650 | 22004392 | WBE | Blank | 22 | BUS NO.3 | SINGLE ZONE BUS DIST | Y | ASEA | GROUP_3075 | GROUP 3075 | GROUP 3000s | Electronic |  | 0.0034106 | 2190 |  | 9.9 | 0.042792 | 0.00043487 | 0.042357 | 235.5956 | 121.7637 | 357.3593 | 123.9391 | 17.1255 | 907.3195 |  | 20.1542 | 0.31092 | 0.0031597 | 0.30776 | 1711.7743 | 884.7022 | 2596.4765 | 900.5084 | 124.429 | 6592.3395 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 28.4237 | 0.0067606 | 28.4304 | 14.6699 | 2.0677 | 0.050376 |  | 1405.7434 | 10213.7534 | 45.2184 | 10168.535 |  | 0.071088 |  | 10.6294 | 11.4125 | 12.2533 | 13.1561 | 14.1254 | 15.1661 | 16.2834 | 17.4831 | 18.7712 | 20.1542 | 21.639 | 23.2333 | 24.945 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.051896 | 0.063029 | 0.076653 | 0.093338 | 0.11379 | 0.13887 | 0.16964 | 0.20743 | 0.25385 | 0.31092 | 0.38109 | 0.46742 | 0.57368 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00052739 | 0.00064053 | 0.00077898 | 0.00094854 | 0.0011563 | 0.0014112 | 0.001724 | 0.002108 | 0.0025798 | 0.0031597 | 0.0038728 | 0.0047501 | 0.0058299 | 0.0071595 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 1704.8276 | 2070.5401 | 2518.0888 | 3066.2043 | 3737.9632 | 4561.8055 | 5572.7911 | 6814.1521 | 8339.2115 | 10213.7534 | 12518.9535 | 15354.9999 | 18845.5702 | 23143.3658 | 26322.423 | 26322.423 | 26322.423 | 26322.423 | 26322.423 | 26322.423 | 26322.423 | 26322.423 | 26322.423 | 26322.423 | 26322.423 | 26322.423 | 26322.423 | 26322.423 | 26322.423 | 26322.423 |  | 31.0067 | 31.0067 | 31.0067 | 31.0067 | 31.0067 | 31.0067 | 31.0067 | 31.0067 | 31.0067 | 31.0067 | 31.0067 | 31.0067 | 31.0067 | 31.0067 | 31.0067 | 31.0067 | 31.0067 | 37.113 | 49.1955 | 65.7811 | 88.6505 | 120.3135 | 164.3133 | 225.66 | 311.4483 | 431.7378 | 600.8079 | 838.9493 | 1175.0209 | 1650.1013 |  | 285.7206 | 347.0122 | 422.0192 | 513.8806 | 626.4641 | 764.5359 | 933.9721 | 1142.018 | 1397.6104 | 1711.7743 | 2098.1144 | 2573.4217 | 3158.4239 | 3878.7131 | 4411.5073 | 4411.5073 | 4411.5073 | 4411.5073 | 4411.5073 | 4411.5073 | 4411.5073 | 4411.5073 | 4411.5073 | 4411.5073 | 4411.5073 | 4411.5073 | 4411.5073 | 4411.5073 | 4411.5073 | 4411.5073 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5487 | 30.1506 | 40.6328 | 55.1454 | 75.3126 | 103.4308 | 142.7516 | 197.8861 | 275.3789 | 384.5305 | 538.5682 | 756.3202 |  | 271.5088 | 332.8004 | 407.8073 | 499.6688 | 612.2522 | 750.3241 | 919.7603 | 1127.8062 | 1383.3986 | 1697.5625 | 2083.9026 | 2559.2098 | 3144.2121 | 3864.5013 | 4397.2955 | 4397.2955 | 4397.2955 | 4394.4966 | 4388.9586 | 4381.3567 | 4370.8745 | 4356.3618 | 4336.1947 | 4308.0765 | 4268.7556 | 4213.6212 | 4136.1283 | 4026.9768 | 3872.9391 | 3655.187 |  | 147.67 | 179.3475 | 218.1136 | 265.5907 | 323.7776 | 395.1377 | 482.708 | 590.2331 | 722.3318 | 884.7022 | 1084.3757 | 1330.0304 | 1632.3791 | 2004.6486 | 2280.0145 | 2280.0145 | 2280.0145 | 2280.0145 | 2280.0145 | 2280.0145 | 2280.0145 | 2280.0145 | 2280.0145 | 2280.0145 | 2280.0145 | 2280.0145 | 2280.0145 | 2280.0145 | 2280.0145 | 2280.0145 |  | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.0067606 | 0.008092 | 0.010726 | 0.014343 | 0.019329 | 0.026233 | 0.035826 | 0.049202 | 0.067907 | 0.094134 | 0.131 | 0.18292 | 0.2562 | 0.35978 |  | 147.6632 | 179.3408 | 218.1069 | 265.5839 | 323.7708 | 395.131 | 482.7012 | 590.2263 | 722.325 | 884.6954 | 1084.3689 | 1330.0236 | 1632.3723 | 2004.6419 | 2280.0077 | 2280.0077 | 2280.0077 | 2280.0064 | 2280.0037 | 2280.0001 | 2279.9951 | 2279.9882 | 2279.9786 | 2279.9653 | 2279.9466 | 2279.9203 | 2279.8835 | 2279.8316 | 2279.7583 | 2279.6547 |  | 419.172 | 512.1412 | 625.9142 | 765.2527 | 936.023 | 1145.4551 | 1402.4615 | 1718.0325 | 2105.7236 | 2582.2579 | 3168.2715 | 3889.2335 | 4776.5844 | 5869.1431 | 6677.3032 | 6677.3032 | 6677.3032 | 6674.503 | 6668.9624 | 6661.3568 | 6650.8697 | 6636.3501 | 6616.1733 | 6588.0418 | 6548.7022 | 6493.5416 | 6416.0118 | 6306.8083 | 6152.6974 | 5934.8417 |  | 150.3083 | 182.5518 | 222.0105 | 270.3358 | 329.5622 | 402.1973 | 491.3321 | 600.7783 | 735.2371 | 900.5084 | 1103.7493 | 1353.7929 | 1661.5434 | 2040.464 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 135.6383 | 167.8819 | 207.3406 | 255.6658 | 314.8923 | 387.5274 | 476.6622 | 586.1084 | 720.5672 | 885.8385 | 1089.0794 | 1339.123 | 1646.8735 | 2025.7941 | 2306.0797 | 2306.0797 | 2306.0797 | 2303.1906 | 2297.4741 | 2289.6271 | 2278.8071 | 2263.8266 | 2243.0094 | 2213.9849 | 2173.3966 | 2116.485 | 2036.4943 | 1923.8244 | 1764.8217 | 1540.0507 |  | 20.7691 | 25.2243 | 30.6766 | 37.354 | 45.5377 | 55.5742 | 67.8905 | 83.0134 | 101.5924 | 124.429 | 152.5121 | 187.0622 | 229.586 | 281.9439 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 18.7014 | 23.1566 | 28.6089 | 35.2863 | 43.47 | 53.5065 | 65.8228 | 80.9457 | 99.5247 | 122.3613 | 150.4444 | 184.9945 | 227.5183 | 279.8762 | 318.605 | 318.605 | 318.605 | 318.1978 | 317.3921 | 316.2861 | 314.761 | 312.6496 | 309.7154 | 305.6245 | 299.9037 | 291.8821 | 280.6076 | 264.7271 | 242.316 | 210.6351 |  | 1100.3597 | 1336.4042 | 1625.269 | 1979.0433 | 2412.6217 | 2944.3604 | 3596.8884 | 4398.1093 | 5382.4398 | 6592.3395 | 8080.2021 | 9910.6927 | 12163.6377 | 14937.5962 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 | 16989.4789 |  | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.050376 | 0.060297 | 0.079927 | 0.10687 | 0.14403 | 0.19547 | 0.26696 | 0.36663 | 0.50601 | 0.70144 | 0.97613 | 1.363 | 1.909 | 2.6809 |  | 1100.3093 | 1336.3538 | 1625.2186 | 1978.9929 | 2412.5713 | 2944.31 | 3596.838 | 4398.0589 | 5382.3894 | 6592.2891 | 8080.1517 | 9910.6424 | 12163.5873 | 14937.5458 | 16989.4285 | 16989.4285 | 16989.4285 | 16989.4186 | 16989.399 | 16989.372 | 16989.3349 | 16989.2834 | 16989.2119 | 16989.1123 | 16988.9729 | 16988.7775 | 16988.5028 | 16988.1159 | 16987.5698 | 16986.798 |  | 1673.821 | 2039.5335 | 2487.0822 | 3035.1977 | 3706.9567 | 4530.799 | 5541.7845 | 6783.1455 | 8308.2049 | 10182.7469 | 12487.9469 | 15323.9933 | 18814.5636 | 23112.3592 | 26291.4164 | 26291.4164 | 26291.4164 | 26285.31 | 26273.2276 | 26256.6421 | 26233.7727 | 26202.1097 | 26158.1101 | 26096.7635 | 26010.9754 | 25890.6862 | 25721.6165 | 25483.4757 | 25147.4049 | 24672.3255
| TRUE | 4651 | 22004391 | WBE | Blank | 22 | BUS NO.3 | HIBP | X | ABB | RADHA_3110 | RADHA 3110 | RADHA | Electronic |  | 0.033587 | 2190 |  | 6.6 | 0.014726 | 0.001389 | 0.013337 | 81.7572 | 388.9293 | 470.6866 | 49.6875 | 5.9058 | 2898.0985 |  | 12.1996 | 0.075729 | 0.0071431 | 0.068586 | 420.4389 | 2000.0803 | 2420.5193 | 255.5192 | 30.3707 | 14903.5557 |  | 0.0051679 | 2.3778e-07 | 0.0051677 | 28.4238 | 0.066577 | 28.4904 | 14.6711 | 2.0677 | 0.4961 |  | 3424.3783 | 17609.9648 | 45.7253 | 17564.2395 |  | 0.061434 |  | 7.0182 | 7.4628 | 7.9357 | 8.4385 | 8.9732 | 9.5417 | 10.1463 | 10.7891 | 11.4727 | 12.1996 | 12.9726 | 13.7946 | 14.6686 | 15.598 | 16.5863 | 17.6372 | 18.7547 | 19.943 | 21.2066 | 22.5502 | 23.979 | 25.4983 | 27.1139 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.017237 | 0.020209 | 0.023729 | 0.027904 | 0.032859 | 0.038742 | 0.045735 | 0.05405 | 0.063946 | 0.075729 | 0.089768 | 0.1065 | 0.12646 | 0.15027 | 0.1787 | 0.21265 | 0.25322 | 0.3017 | 0.35966 | 0.42899 | 0.51193 | 0.61118 | 0.73 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0016259 | 0.0019062 | 0.0022383 | 0.0026321 | 0.0030994 | 0.0036544 | 0.0043139 | 0.0050983 | 0.0060317 | 0.0071431 | 0.0084673 | 0.010046 | 0.011928 | 0.014175 | 0.016856 | 0.020059 | 0.023885 | 0.028458 | 0.033925 | 0.040464 | 0.048287 | 0.05765 | 0.068857 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 0.07558 | 4008.2108 | 4699.2836 | 5518.0256 | 6488.8432 | 7640.9053 | 9009.0846 | 10635.0868 | 12568.8046 | 14869.9422 | 17609.9648 | 20874.437 | 24765.8302 | 29406.891 | 34944.6859 | 41555.4551 | 49450.4415 | 58882.8884 | 70156.4431 | 83635.248 | 99756.0604 | 119042.808 | 142124.0731 | 169754.094 | 186328.2599 | 186328.2599 | 186328.2599 | 186328.2599 | 186328.2599 | 186328.2599 | 186328.2599 |  | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 31.5141 | 37.7204 | 50.0007 | 66.8576 | 90.1014 | 122.2826 | 167.0025 | 229.3532 | 316.5456 | 438.8037 | 610.6408 | 852.6797 | 1194.2515 | 1677.1072 |  | 95.6963 | 112.1957 | 131.7432 | 154.9215 | 182.4271 | 215.0924 | 253.9133 | 300.0809 | 355.0207 | 420.4389 | 498.3784 | 591.2856 | 702.0912 | 834.3064 | 992.1389 | 1180.6321 | 1405.8324 | 1674.9891 | 1996.7964 | 2381.6817 | 2842.1539 | 3393.2204 | 4052.8888 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 | 4448.5979 |  | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 14.2119 | 17.0107 | 22.5487 | 30.1507 | 40.6329 | 55.1457 | 75.3129 | 103.4312 | 142.7522 | 197.8869 | 275.3801 | 384.5321 | 538.5704 | 756.3234 |  | 81.4844 | 97.9838 | 117.5313 | 140.7096 | 168.2152 | 200.8805 | 239.7014 | 285.869 | 340.8088 | 406.227 | 484.1665 | 577.0737 | 687.8793 | 820.0945 | 977.927 | 1166.4203 | 1391.6205 | 1657.9784 | 1974.2476 | 2351.531 | 2801.521 | 3338.0748 | 3977.5758 | 4345.1668 | 4305.8457 | 4250.7111 | 4173.2179 | 4064.0658 | 3910.0276 | 3692.2746 |  | 455.239 | 533.7288 | 626.7187 | 736.9809 | 867.8282 | 1023.2214 | 1207.8972 | 1427.5224 | 1688.8778 | 2000.0803 | 2370.8481 | 2812.8194 | 3339.9354 | 3968.8994 | 4719.7283 | 5616.4142 | 6687.7196 | 7968.1319 | 9499.0091 | 11329.9565 | 13520.4802 | 16141.9723 | 19280.0968 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 | 21162.5346 |  | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.066577 | 0.079689 | 0.10563 | 0.14124 | 0.19035 | 0.25834 | 0.35281 | 0.48454 | 0.66874 | 0.92703 | 1.2901 | 1.8014 | 2.523 | 3.5431 |  | 455.1725 | 533.6622 | 626.6521 | 736.9143 | 867.7616 | 1023.1548 | 1207.8307 | 1427.4558 | 1688.8113 | 2000.0138 | 2370.7815 | 2812.7528 | 3339.8688 | 3968.8329 | 4719.6617 | 5616.3476 | 6687.6531 | 7968.0522 | 9498.9034 | 11329.8153 | 13520.2898 | 16141.714 | 19279.744 | 21162.05 | 21161.8658 | 21161.6076 | 21161.2445 | 21160.7332 | 21160.0116 | 21158.9915 |  | 536.6568 | 631.646 | 744.1834 | 877.6239 | 1035.9768 | 1224.0354 | 1447.5321 | 1713.3249 | 2029.6201 | 2406.2408 | 2854.948 | 3389.8265 | 4027.7481 | 4788.9274 | 5697.5887 | 6782.7678 | 8079.2735 | 9626.0306 | 11473.1511 | 13681.3462 | 16321.8108 | 19479.7888 | 23257.3198 | 25507.2168 | 25467.7116 | 25412.3186 | 25334.4624 | 25224.799 | 25070.0391 | 24851.2661 |  | 58.1588 | 68.1862 | 80.0661 | 94.1526 | 110.8689 | 130.7211 | 154.3143 | 182.3724 | 215.7617 | 255.5192 | 302.8864 | 359.3502 | 426.6917 | 507.0446 | 602.9664 | 717.522 | 854.3861 | 1017.9644 | 1213.5408 | 1447.4526 | 1727.3017 | 2062.2091 | 2463.1185 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 | 2703.6083 |  | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 14.6711 | 17.5604 | 23.2774 | 31.125 | 41.946 | 56.9277 | 77.7466 | 106.7735 | 147.3652 | 204.2814 | 284.2788 | 396.958 | 555.9739 | 780.7634 |  | 43.4877 | 53.5151 | 65.395 | 79.4815 | 96.1978 | 116.05 | 139.6431 | 167.7012 | 201.0906 | 240.8481 | 288.2153 | 344.6791 | 412.0205 | 492.3735 | 588.2952 | 702.8509 | 839.7149 | 1000.404 | 1190.2635 | 1416.3275 | 1685.3558 | 2005.2814 | 2385.3719 | 2596.8349 | 2556.2432 | 2499.3269 | 2419.3296 | 2306.6504 | 2147.6344 | 1922.8449 |  | 6.9127 | 8.1045 | 9.5165 | 11.1908 | 13.1777 | 15.5373 | 18.3416 | 21.6765 | 25.6451 | 30.3707 | 36.0007 | 42.7119 | 50.716 | 60.2666 | 71.6677 | 85.2837 | 101.5511 | 120.9938 | 144.2398 | 172.0422 | 205.3047 | 245.1113 | 292.7628 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 | 321.3471 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0652 | 55.9457 | 78.3568 | 110.0378 |  | 4.845 | 6.0368 | 7.4489 | 9.1232 | 11.11 | 13.4696 | 16.2739 | 19.6088 | 23.5774 | 28.303 | 33.933 | 40.6442 | 48.6483 | 58.1989 | 69.6 | 83.216 | 99.4834 | 118.5189 | 140.9591 | 167.6555 | 199.393 | 237.0881 | 281.8055 | 306.2989 | 300.578 | 292.5565 | 281.2819 | 265.4014 | 242.9903 | 211.3093 |  | 3392.204 | 3977.0684 | 4669.981 | 5491.5973 | 6466.6033 | 7624.5123 | 9000.6204 | 10637.1524 | 12584.6369 | 14903.5557 | 17666.3235 | 20959.6631 | 24887.4568 | 29574.1689 | 35168.9539 | 41850.5895 | 49833.3992 | 59374.3638 | 70781.662 | 84424.9275 | 100747.5675 | 120281.56 | 143665.2271 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 | 157692.1719 |  | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.4961 | 0.5938 | 0.78712 | 1.0525 | 1.4184 | 1.925 | 2.629 | 3.6105 | 4.9831 | 6.9077 | 9.6128 | 13.423 | 18.8001 | 26.4013 |  | 3391.7079 | 3976.5723 | 4669.4849 | 5491.1012 | 6466.1072 | 7624.0162 | 9000.1243 | 10636.6563 | 12584.1408 | 14903.0596 | 17665.8274 | 20959.167 | 24886.9607 | 29573.6728 | 35168.4578 | 41850.0934 | 49832.9031 | 59373.77 | 70780.8749 | 84423.875 | 100746.1491 | 120279.635 | 143662.5981 | 157688.5614 | 157687.1888 | 157685.2642 | 157682.5591 | 157678.7489 | 157673.3718 | 157665.7706 |  | 3976.6974 | 4667.7702 | 5486.5122 | 6457.3298 | 7609.3919 | 8977.5712 | 10603.5734 | 12537.2912 | 14838.4289 | 17578.4514 | 20842.9236 | 24734.3168 | 29375.3776 | 34913.1725 | 41523.9417 | 49418.9281 | 58851.375 | 70118.7235 | 83585.2485 | 99689.2043 | 118952.7087 | 142001.7933 | 169587.0953 | 186098.9119 | 186011.7215 | 185889.4662 | 185717.633 | 185475.5996 | 185134.0356 | 184651.1909
| TRUE | 4652 | 22004378 | WBE | Blank | 22 | CAP NO.3 | NEUTRAL BALANCE | X | RMS | 2C138 | 2C138 | RMS 2C13X | Electronic |  | 0.2894 | 2190 |  | 6.6 | 0.014726 | 0.0077409 | 0.0069852 | 63.9381 | 1083.7238 | 1147.6618 | 85.7484 | 5.9693 | 16150.6887 |  | 14.9721 | 0.13394 | 0.070404 | 0.063531 | 581.5244 | 9856.5984 | 10438.1228 | 779.8919 | 54.2915 | 146892.4627 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 21.3186 | 0.28683 | 21.6054 | 14.6814 | 2.0677 | 4.2745 |  | 17390.0682 | 158164.7689 | 42.6291 | 158122.1398 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.018172 | 0.022489 | 0.027904 | 0.034708 | 0.043268 | 0.05405 | 0.067647 | 0.084812 | 0.1065 | 0.13394 | 0.16866 | 0.21265 | 0.26843 | 0.33918 | 0.42899 | 0.54305 | 0.688 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0095523 | 0.011821 | 0.014668 | 0.018245 | 0.022744 | 0.028412 | 0.035559 | 0.044582 | 0.055984 | 0.070404 | 0.088659 | 0.11178 | 0.1411 | 0.17829 | 0.2255 | 0.28546 | 0.36165 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 0.4212 | 21459.5233 | 26557.0905 | 32952.3829 | 40987.3006 | 51095.6809 | 63828.3358 | 79884.964 | 100154.8341 | 125768.6608 | 158164.7689 | 199173.4938 | 251124.8669 | 316986.0298 | 400536.6123 | 506592.5934 | 641292.0849 | 812460.2093 | 946233.4017 | 946233.4017 | 946233.4017 | 946233.4017 | 946233.4017 | 946233.4017 | 946233.4017 | 946233.4017 | 946233.4017 | 946233.4017 | 946233.4017 | 946233.4017 | 946233.4017 |  | 35.526 | 35.526 | 35.526 | 35.526 | 35.526 | 35.526 | 35.526 | 35.526 | 35.526 | 35.526 | 35.526 | 35.526 | 35.526 | 35.526 | 35.526 | 35.526 | 35.526 | 42.5224 | 56.3659 | 75.3689 | 101.5716 | 137.8497 | 188.2626 | 258.5508 | 356.8431 | 494.6652 | 688.3778 | 961.2292 | 1346.2844 | 1890.6097 |  | 78.9002 | 97.6425 | 121.156 | 150.698 | 187.8635 | 234.6776 | 293.713 | 368.2393 | 462.4136 | 581.5244 | 732.3012 | 923.3108 | 1165.4625 | 1472.6529 | 1862.5889 | 2357.8385 | 2987.1723 | 3479.0162 | 3479.0162 | 3479.0162 | 3479.0162 | 3479.0162 | 3479.0162 | 3479.0162 | 3479.0162 | 3479.0162 | 3479.0162 | 3479.0162 | 3479.0162 | 3479.0162 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 64.6878 | 83.4301 | 106.9436 | 136.4856 | 173.6511 | 220.4652 | 279.5006 | 354.0269 | 448.2012 | 567.312 | 718.0888 | 909.0984 | 1151.2501 | 1458.4405 | 1848.3765 | 2343.6261 | 2972.9599 | 3462.0049 | 3456.4667 | 3448.8644 | 3438.3818 | 3423.8686 | 3403.7006 | 3375.5814 | 3336.2589 | 3281.1224 | 3203.6265 | 3094.4706 | 2940.4269 | 2722.6663 |  | 1337.3263 | 1654.9993 | 2053.5446 | 2554.269 | 3184.2085 | 3977.6891 | 4978.3148 | 6241.5036 | 7837.7201 | 9856.5984 | 12412.2025 | 15649.7365 | 19754.1084 | 24960.8593 | 31570.1138 | 39964.3902 | 50631.3388 | 58967.8897 | 58967.8897 | 58967.8897 | 58967.8897 | 58967.8897 | 58967.8897 | 58967.8897 | 58967.8897 | 58967.8897 | 58967.8897 | 58967.8897 | 58967.8897 | 58967.8897 |  | 0.28683 | 0.28683 | 0.28683 | 0.28683 | 0.28683 | 0.28683 | 0.28683 | 0.28683 | 0.28683 | 0.28683 | 0.28683 | 0.28683 | 0.28683 | 0.28683 | 0.28683 | 0.28683 | 0.28683 | 0.34331 | 0.45508 | 0.6085 | 0.82006 | 1.113 | 1.52 | 2.0875 | 2.881 | 3.9938 | 5.5577 | 7.7607 | 10.8695 | 15.2642 |  | 1337.0395 | 1654.7124 | 2053.2578 | 2553.9821 | 3183.9217 | 3977.4022 | 4978.028 | 6241.2168 | 7837.4332 | 9856.3116 | 12411.9157 | 15649.4497 | 19753.8216 | 24960.5724 | 31569.827 | 39964.1034 | 50631.052 | 58967.5463 | 58967.4346 | 58967.2812 | 58967.0696 | 58966.7767 | 58966.3697 | 58965.8022 | 58965.0086 | 58963.8959 | 58962.3319 | 58960.129 | 58957.0202 | 58952.6255 |  | 1401.7273 | 1738.1425 | 2160.2014 | 2690.4678 | 3357.5728 | 4197.8675 | 5257.5286 | 6595.2437 | 8285.6345 | 10423.6236 | 13130.0045 | 16558.5481 | 20905.0717 | 26419.0129 | 33418.2035 | 42307.7295 | 53604.0119 | 62429.5512 | 62423.9012 | 62416.1456 | 62405.4514 | 62390.6453 | 62370.0703 | 62341.3836 | 62301.2676 | 62245.0183 | 62165.9584 | 62054.5996 | 61897.4471 | 61675.2918 |  | 105.8144 | 130.9499 | 162.4843 | 202.1036 | 251.9468 | 314.73 | 393.9034 | 493.8518 | 620.1505 | 779.8919 | 982.1012 | 1238.2673 | 1563.021 | 1974.9991 | 2497.9487 | 3162.1362 | 4006.1461 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 | 4665.7661 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 91.133 | 116.2685 | 147.8029 | 187.4222 | 237.2654 | 300.0486 | 379.222 | 479.1703 | 605.4691 | 765.2105 | 967.4198 | 1223.5859 | 1548.3396 | 1960.3177 | 2483.2673 | 3147.4547 | 3991.4647 | 4648.1933 | 4642.4724 | 4634.6192 | 4623.7907 | 4608.7985 | 4587.965 | 4558.9178 | 4518.2976 | 4461.3415 | 4381.2881 | 4268.5299 | 4109.4026 | 3884.4555 |  | 7.3662 | 9.116 | 11.3112 | 14.0693 | 17.5391 | 21.9097 | 27.4212 | 34.3791 | 43.1712 | 54.2915 | 68.3681 | 86.2009 | 108.8084 | 137.4879 | 173.8926 | 220.1294 | 278.8844 | 324.8033 | 324.8033 | 324.8033 | 324.8033 | 324.8033 | 324.8033 | 324.8033 | 324.8033 | 324.8033 | 324.8033 | 324.8033 | 324.8033 | 324.8033 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 5.2985 | 7.0483 | 9.2435 | 12.0016 | 15.4713 | 19.842 | 25.3535 | 32.3114 | 41.1035 | 52.2238 | 66.3004 | 84.1332 | 106.7407 | 135.4202 | 171.8248 | 218.0617 | 276.8167 | 322.3284 | 321.5226 | 320.4166 | 318.8915 | 316.7801 | 313.8459 | 309.7549 | 304.034 | 296.0124 | 284.7378 | 268.8571 | 246.4458 | 214.7645 |  | 19930.1162 | 24664.3829 | 30603.8867 | 38066.1608 | 47454.123 | 59279.3294 | 74191.6115 | 93016.8603 | 116805.2054 | 146892.4627 | 184978.5209 | 233227.3514 | 294394.6296 | 371990.6132 | 470488.0495 | 595587.5907 | 754556.6676 | 878795.9265 | 878795.9265 | 878795.9265 | 878795.9265 | 878795.9265 | 878795.9265 | 878795.9265 | 878795.9265 | 878795.9265 | 878795.9265 | 878795.9265 | 878795.9265 | 878795.9265 |  | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 5.1164 | 6.782 | 9.0685 | 12.2213 | 16.5863 | 22.6521 | 31.1093 | 42.936 | 59.519 | 82.8268 | 115.6567 | 161.9873 | 227.4814 |  | 19925.8417 | 24660.1084 | 30599.6122 | 38061.8862 | 47449.8485 | 59275.0548 | 74187.337 | 93012.5858 | 116800.9308 | 146888.1881 | 184974.2463 | 233223.0769 | 294390.355 | 371986.3387 | 470483.7749 | 595583.3161 | 754552.3931 | 878790.8101 | 878789.1444 | 878786.8579 | 878783.7052 | 878779.3401 | 878773.2744 | 878764.8172 | 878752.9905 | 878736.4075 | 878713.0997 | 878680.2697 | 878633.9392 | 878568.4451 |  | 21424.0004 | 26521.5676 | 32916.86 | 40951.7777 | 51060.158 | 63792.8129 | 79849.4411 | 100119.3112 | 125733.1379 | 158129.246 | 199137.9709 | 251089.3441 | 316950.507 | 400501.0895 | 506557.0706 | 641256.562 | 812424.6865 | 946190.883 | 946177.0406 | 946158.0393 | 946131.8389 | 946095.564 | 946045.1555 | 945974.8734 | 945876.5897 | 945738.7796 | 945545.0839 | 945272.2563 | 944887.2346 | 944342.9569
| FALSE | 4653 | 22004377 | WBE | Blank | 22 | CAP NO.3 | OC & EF | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.2894 | 1 |  | 2.8514 | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 4.2745 |  | 9.4101 | 0.043865 | 1.739e-05 | 0.043848 | 120.6342 | 1.2173 | 121.8515 | 124.6153 | 17.5507 | 36.2822 |  | 0.0051679 | 2.0488e-06 | 0.0051659 | 14.2124 | 0.14341 | 14.3558 | 14.6814 | 2.0677 | 4.2745 |  | 35.3795 | 300.2997 | 35.3795 | 264.9202 |  | 0.1194 |  | 3.213 | 3.6205 | 4.0796 | 4.597 | 5.1799 | 5.8369 | 6.5771 | 7.4112 | 8.351 | 9.4101 | 10.6034 | 11.9482 | 13.4634 | 15.1708 | 17.0947 | 19.2626 | 21.7055 | 24.4581 | 27.5598 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0054038 | 0.0071219 | 0.0094715 | 0.0127 | 0.017155 | 0.023326 | 0.031904 | 0.043865 | 0.060591 | 0.084037 | 0.11698 | 0.16335 | 0.22876 | 0.32115 | 0.45186 | 0.63698 | 0.8995 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 2.0488e-06 | 2.0488e-06 | 2.1423e-06 | 2.8234e-06 | 3.7548e-06 | 5.0348e-06 | 6.8009e-06 | 9.2473e-06 | 1.2648e-05 | 1.739e-05 | 2.402e-05 | 3.3315e-05 | 4.6374e-05 | 6.4759e-05 | 9.0689e-05 | 0.00012732 | 0.00017913 | 0.00025252 | 0.00035659 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 0.00037335 | 35.3795 | 35.3795 | 36.9942 | 48.7559 | 64.8417 | 86.944 | 117.4428 | 159.6898 | 218.4146 | 300.2997 | 414.8004 | 575.3114 | 800.8286 | 1118.3169 | 1566.0867 | 2198.6098 | 3093.3897 | 4360.7679 | 6157.9232 | 6447.2506 | 6447.2506 | 6447.2506 | 6447.2506 | 6447.2506 | 6447.2506 | 6447.2506 | 6447.2506 | 6447.2506 | 6447.2506 | 6447.2506 |  | 35.3795 | 35.3795 | 35.3795 | 35.3795 | 35.3795 | 35.3795 | 35.3795 | 35.3795 | 35.3795 | 35.3795 | 35.3795 | 35.3795 | 35.3795 | 35.3795 | 35.3795 | 35.3795 | 35.3795 | 42.347 | 56.1335 | 75.0581 | 101.1528 | 137.2812 | 187.4862 | 257.4845 | 355.3714 | 492.6251 | 685.5389 | 957.265 | 1340.7323 | 1882.8127 |  | 14.2124 | 14.2124 | 14.861 | 19.5859 | 26.0477 | 34.9265 | 47.1783 | 64.1494 | 87.7399 | 120.6342 | 166.6306 | 231.11 | 321.7031 | 449.2422 | 629.117 | 883.2096 | 1242.6541 | 1751.7761 | 2473.7163 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 | 2589.9429 |  | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 14.2124 | 17.0113 | 22.5495 | 30.1518 | 40.6344 | 55.1476 | 75.3156 | 103.4348 | 142.7572 | 197.8938 | 275.3897 | 384.5456 | 538.5893 | 756.3499 |  | 0 | 0 | 0.64865 | 5.3735 | 11.8353 | 20.7141 | 32.9659 | 49.9371 | 73.5276 | 106.4218 | 152.4182 | 216.8976 | 307.4907 | 435.0298 | 614.9046 | 868.9972 | 1228.4417 | 1734.7648 | 2451.1668 | 2559.7911 | 2549.3085 | 2534.7953 | 2514.6273 | 2486.5081 | 2447.1856 | 2392.0491 | 2314.5531 | 2205.3973 | 2051.3536 | 1833.593 |  | 0.14341 | 0.14341 | 0.14996 | 0.19763 | 0.26284 | 0.35243 | 0.47606 | 0.64731 | 0.88536 | 1.2173 | 1.6814 | 2.3321 | 3.2462 | 4.5332 | 6.3482 | 8.9122 | 12.5392 | 17.6766 | 24.9615 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 | 26.1343 |  | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.14341 | 0.17166 | 0.22754 | 0.30425 | 0.41003 | 0.55648 | 0.75999 | 1.0437 | 1.4405 | 1.9969 | 2.7789 | 3.8803 | 5.4347 | 7.6321 |  | 0 | 0 | 0.0065453 | 0.054222 | 0.11943 | 0.20902 | 0.33265 | 0.5039 | 0.74194 | 1.0739 | 1.538 | 2.1886 | 3.1028 | 4.3897 | 6.2048 | 8.7688 | 12.3958 | 17.505 | 24.734 | 25.83 | 25.7243 | 25.5778 | 25.3743 | 25.0906 | 24.6938 | 24.1374 | 23.3554 | 22.254 | 20.6996 | 18.5022 |  | 0 | 0 | 0.65519 | 5.4277 | 11.9548 | 20.9232 | 33.2985 | 50.441 | 74.2695 | 107.4957 | 153.9562 | 219.0862 | 310.5935 | 439.4195 | 621.1095 | 877.766 | 1240.8376 | 1752.2697 | 2475.9007 | 2585.6211 | 2575.0328 | 2560.3731 | 2540.0016 | 2511.5986 | 2471.8794 | 2416.1865 | 2337.9086 | 2227.6513 | 2072.0532 | 1852.0952 |  | 14.6814 | 14.6814 | 15.3515 | 20.2322 | 26.9073 | 36.0792 | 48.7352 | 66.2665 | 90.6355 | 124.6153 | 172.1297 | 238.7369 | 332.3198 | 464.0678 | 649.8788 | 912.3568 | 1283.6635 | 1809.5873 | 2555.3526 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 | 2675.4148 |  | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 14.6814 | 17.5727 | 23.2937 | 31.1468 | 41.9753 | 56.9676 | 77.8011 | 106.8483 | 147.4684 | 204.4246 | 284.478 | 397.2362 | 556.3635 | 781.3105 |  | 0 | 0 | 0.67005 | 5.5508 | 12.2259 | 21.3977 | 34.0538 | 51.5851 | 75.9541 | 109.9339 | 157.4482 | 224.0555 | 317.6383 | 449.3864 | 635.1974 | 897.6754 | 1268.9821 | 1792.0146 | 2532.0589 | 2644.268 | 2633.4395 | 2618.4473 | 2597.6137 | 2568.5665 | 2527.9464 | 2470.9902 | 2390.9368 | 2278.1786 | 2119.0513 | 1894.1043 |  | 2.0677 | 2.0677 | 2.1621 | 2.8495 | 3.7896 | 5.0813 | 6.8638 | 9.3329 | 12.765 | 17.5507 | 24.2425 | 33.6234 | 46.8035 | 65.3587 | 91.5281 | 128.4952 | 180.7895 | 254.8599 | 359.8925 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 | 376.8019 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0232 | 10.9574 | 15.0484 | 20.7693 | 28.7909 | 40.0655 | 55.9462 | 78.3575 | 110.0388 |  | 0 | 0 | 0.094369 | 0.78177 | 1.7219 | 3.0136 | 4.7961 | 7.2652 | 10.6973 | 15.4829 | 22.1748 | 31.5557 | 44.7358 | 63.291 | 89.4604 | 126.4274 | 178.7218 | 252.385 | 356.6119 | 372.4153 | 370.8902 | 368.7787 | 365.8445 | 361.7536 | 356.0327 | 348.011 | 336.7364 | 320.8557 | 298.4444 | 266.7632 |  | 4.2745 | 4.2745 | 4.4696 | 5.8907 | 7.8342 | 10.5046 | 14.1894 | 19.2937 | 26.3888 | 36.2822 | 50.1162 | 69.5091 | 96.7561 | 135.115 | 189.2146 | 265.636 | 373.7433 | 526.8679 | 744.0002 | 778.9567 | 778.9567 | 778.9567 | 778.9567 | 778.9567 | 778.9567 | 778.9567 | 778.9567 | 778.9567 | 778.9567 | 778.9567 |  | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 4.2745 | 5.1164 | 6.782 | 9.0685 | 12.2213 | 16.5863 | 22.6521 | 31.1093 | 42.936 | 59.519 | 82.8268 | 115.6567 | 161.9873 | 227.4814 |  | 0 | 0 | 0.19509 | 1.6161 | 3.5596 | 6.23 | 9.9149 | 15.0192 | 22.1143 | 32.0077 | 45.8416 | 65.2346 | 92.4816 | 130.8405 | 184.94 | 261.3615 | 369.4687 | 521.7515 | 737.2181 | 769.8882 | 766.7354 | 762.3704 | 756.3046 | 747.8474 | 736.0207 | 719.4378 | 696.1299 | 663.3 | 616.9695 | 551.4753 |  | 0 | 0 | 1.6147 | 13.3764 | 29.4622 | 51.5645 | 82.0633 | 124.3104 | 183.0351 | 264.9202 | 379.4209 | 539.932 | 765.4491 | 1082.9374 | 1530.7073 | 2163.2303 | 3058.0102 | 4318.4209 | 6101.7897 | 6372.1926 | 6346.0979 | 6309.9695 | 6259.7645 | 6189.7661 | 6091.8792 | 5954.6255 | 5761.7117 | 5489.9856 | 5106.5183 | 4564.438
| TRUE | 4654 | 22009472 | WBE | Blank | 22 | CB BT 1-2 | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 3.4047 | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 9.2417 | 0.041791 | 0 | 0.041791 | 114.924 | 0 | 114.924 | 118.6274 | 16.7204 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 30.9493 | 250.2718 | 30.9493 | 219.3225 |  | 0.099856 |  | 3.7623 | 4.1574 | 4.5939 | 5.0764 | 5.6094 | 6.1985 | 6.8494 | 7.5687 | 8.3635 | 9.2417 | 10.2122 | 11.2846 | 12.4696 | 13.7791 | 15.2261 | 16.825 | 18.5918 | 20.5441 | 22.7015 | 25.0854 | 27.7197 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0056413 | 0.0071108 | 0.0090201 | 0.011509 | 0.014763 | 0.01903 | 0.024639 | 0.03203 | 0.041791 | 0.054706 | 0.071825 | 0.094556 | 0.12478 | 0.16503 | 0.21869 | 0.29031 | 0.38601 | 0.51398 | 0.68527 | 0.9147 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9493 | 33.7844 | 42.5847 | 54.0185 | 68.9231 | 88.4112 | 113.9639 | 147.5553 | 191.8189 | 250.2718 | 327.6157 | 430.1411 | 566.2704 | 747.2891 | 988.3282 | 1309.6866 | 1738.611 | 2311.6912 | 3078.0859 | 4103.8667 | 5477.869 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 14.2118 | 15.5137 | 19.5548 | 24.8051 | 31.6493 | 40.5981 | 52.3319 | 67.757 | 88.0827 | 114.924 | 150.4401 | 197.5195 | 260.0296 | 343.1529 | 453.8373 | 601.4041 | 798.3648 | 1061.5215 | 1413.4476 | 1884.483 | 2515.4206 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 0 | 1.3019 | 5.3429 | 10.5933 | 17.4375 | 26.3863 | 38.1201 | 53.5451 | 73.8708 | 100.7122 | 136.2283 | 183.3076 | 245.8178 | 328.941 | 439.6254 | 587.1922 | 784.153 | 1044.5108 | 1390.899 | 1854.3324 | 2474.7879 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.3019 | 5.3429 | 10.5933 | 17.4375 | 26.3863 | 38.1201 | 53.5451 | 73.8708 | 100.7122 | 136.2283 | 183.3076 | 245.8178 | 328.941 | 439.6254 | 587.1922 | 784.153 | 1044.5108 | 1390.899 | 1854.3324 | 2474.7879 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 14.6698 | 16.0136 | 20.1849 | 25.6045 | 32.6691 | 41.9064 | 54.0182 | 69.9404 | 90.921 | 118.6274 | 155.2879 | 203.8843 | 268.4088 | 354.2106 | 468.4617 | 620.7837 | 824.0913 | 1095.728 | 1458.9945 | 1945.2086 | 2596.4776 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 0 | 1.3438 | 5.5151 | 10.9347 | 17.9994 | 27.2366 | 39.3485 | 55.2706 | 76.2512 | 103.9576 | 140.6181 | 189.2145 | 253.739 | 339.5408 | 453.7919 | 606.1139 | 809.4215 | 1078.1691 | 1435.7193 | 1914.0864 | 2554.5355 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 2.0677 | 2.2571 | 2.845 | 3.6089 | 4.6047 | 5.9067 | 7.6138 | 9.858 | 12.8152 | 16.7204 | 21.8877 | 28.7373 | 37.8319 | 49.9256 | 66.0292 | 87.4988 | 116.1548 | 154.4417 | 205.6438 | 274.1751 | 365.9708 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 0 | 0.18941 | 0.77735 | 1.5412 | 2.537 | 3.839 | 5.5461 | 7.7903 | 10.7475 | 14.6527 | 19.82 | 26.6696 | 35.7643 | 47.8579 | 63.9615 | 85.4311 | 114.0871 | 151.9668 | 202.3632 | 269.7885 | 360.0591 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2.8351 | 11.6354 | 23.0692 | 37.9738 | 57.4619 | 83.0146 | 116.606 | 160.8696 | 219.3225 | 296.6664 | 399.1918 | 535.3211 | 716.3398 | 957.3789 | 1278.7373 | 1707.6617 | 2274.6468 | 3028.9814 | 4038.2073 | 5389.3825 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 4655 | 22009471 | WBE | Blank | 22 | CB BT 2-3 | CB FAIL | BU | EMAIL | GROUP_3183 | GROUP 3183 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 235.3564 | 0 | 235.3564 | 121.4703 | 17.1211 | 0 |  | 20.1542 | 0.31092 | 0 | 0.31092 | 1710.0365 | 0 | 1710.0365 | 882.5704 | 124.3974 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 373.9478 | 2717.0043 | 45.1611 | 2671.8431 |  | 0.071088 |  | 10.6294 | 11.4125 | 12.2533 | 13.1561 | 14.1254 | 15.1661 | 16.2834 | 17.4831 | 18.7712 | 20.1542 | 21.639 | 23.2333 | 24.945 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.051896 | 0.063029 | 0.076653 | 0.093338 | 0.11379 | 0.13887 | 0.16964 | 0.20743 | 0.25385 | 0.31092 | 0.38109 | 0.46742 | 0.57368 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.5085 | 550.7932 | 669.8476 | 815.6541 | 994.3516 | 1213.5054 | 1482.442 | 1812.6618 | 2218.3493 | 2717.0043 | 3330.2204 | 4084.6492 | 5013.1908 | 6156.4658 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 285.4306 | 346.6599 | 421.5907 | 513.3589 | 625.8281 | 763.7598 | 933.0239 | 1140.8586 | 1396.1915 | 1710.0365 | 2095.9844 | 2570.8091 | 3155.2174 | 3874.7754 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 271.2187 | 332.4481 | 407.3789 | 499.1471 | 611.6162 | 749.548 | 918.8121 | 1126.6468 | 1381.9797 | 1695.8247 | 2081.7725 | 2556.5973 | 3141.0056 | 3860.5636 | 4392.8169 | 4392.8169 | 4392.8169 | 4390.018 | 4384.48 | 4376.8781 | 4366.3959 | 4351.8833 | 4331.7161 | 4303.598 | 4264.2771 | 4209.1427 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 271.2187 | 332.4481 | 407.3789 | 499.1471 | 611.6162 | 749.548 | 918.8121 | 1126.6468 | 1381.9797 | 1695.8247 | 2081.7725 | 2556.5973 | 3141.0056 | 3860.5636 | 4392.8169 | 4392.8169 | 4392.8169 | 4390.018 | 4384.48 | 4376.8781 | 4366.3959 | 4351.8833 | 4331.7161 | 4303.598 | 4264.2771 | 4209.1427 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 147.3141 | 178.9154 | 217.588 | 264.9507 | 322.9974 | 394.1856 | 481.5448 | 588.8108 | 720.5912 | 882.5704 | 1081.7627 | 1326.8254 | 1628.4456 | 1999.8181 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 132.6444 | 164.2456 | 202.9183 | 250.2809 | 308.3276 | 379.5158 | 466.8751 | 574.1411 | 705.9214 | 867.9006 | 1067.0929 | 1312.1557 | 1613.7758 | 1985.1483 | 2259.8506 | 2259.8506 | 2259.8506 | 2256.9616 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 20.7638 | 25.2179 | 30.6688 | 37.3445 | 45.5261 | 55.5601 | 67.8732 | 82.9923 | 101.5666 | 124.3974 | 152.4733 | 187.0147 | 229.5277 | 281.8723 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 18.6961 | 23.1502 | 28.6011 | 35.2768 | 43.4585 | 53.4924 | 65.8056 | 80.9246 | 99.4989 | 122.3297 | 150.4056 | 184.947 | 227.46 | 279.8046 | 318.5236 | 318.5236 | 318.5236 | 318.1164 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 422.5592 | 519.8439 | 638.8983 | 784.7048 | 963.4023 | 1182.5561 | 1451.4927 | 1781.7125 | 2187.4 | 2686.055 | 3299.2711 | 4053.6999 | 4982.2415 | 6125.5165 | 6971.1911 | 6971.1911 | 6971.1911 | 6965.096 | 6953.0359 | 6936.481 | 6913.6539 | 6882.0494 | 6838.131 | 6776.8978 | 6691.2682 | 6571.2012 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 4656 | 22008218 | WBE | Blank | 22 | CB TR NO.1 | CB FAIL | Y | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 5.5 | 0.010964 | 0 | 0.010964 | 30.1506 | 0 | 30.1506 | 31.1222 | 4.3866 | 0 |  | 12.2319 | 0.089657 | 0 | 0.089657 | 246.5573 | 0 | 246.5573 | 254.5023 | 35.8718 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 65.6594 | 536.9314 | 30.9493 | 505.9821 |  | 0.07993 |  | 5.9577 | 6.4534 | 6.9904 | 7.5721 | 8.2022 | 8.8847 | 9.624 | 10.4248 | 11.2923 | 12.2319 | 13.2497 | 14.3522 | 15.5465 | 16.8401 | 18.2414 | 19.7593 | 21.4035 | 23.1845 | 25.1137 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.013366 | 0.016347 | 0.020053 | 0.024668 | 0.030423 | 0.037611 | 0.0466 | 0.057853 | 0.071959 | 0.089657 | 0.11189 | 0.13983 | 0.17499 | 0.21925 | 0.27503 | 0.34535 | 0.43407 | 0.54606 | 0.6875 | 0.86622 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0438 | 97.8962 | 120.091 | 147.729 | 182.1968 | 225.2426 | 279.0712 | 346.4655 | 430.9392 | 536.9314 | 670.0528 | 837.3975 | 1047.9389 | 1313.0319 | 1647.0491 | 2068.1891 | 2599.5008 | 3270.1846 | 4117.2423 | 5187.5732 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 36.7559 | 44.9536 | 55.1454 | 67.8367 | 83.6642 | 103.4307 | 128.1487 | 159.0959 | 197.886 | 246.5573 | 307.6862 | 384.5303 | 481.2103 | 602.9402 | 756.3199 | 949.7061 | 1193.6828 | 1501.6587 | 1890.625 | 2382.1177 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 22.544 | 30.7418 | 40.9336 | 53.6249 | 69.4524 | 89.2189 | 113.9368 | 144.8841 | 183.6741 | 232.3454 | 293.4744 | 370.3185 | 466.9985 | 588.7284 | 742.1081 | 935.4943 | 1179.471 | 1484.648 | 1868.0764 | 2351.9671 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22.544 | 30.7418 | 40.9336 | 53.6249 | 69.4524 | 89.2189 | 113.9368 | 144.8841 | 183.6741 | 232.3454 | 293.4744 | 370.3185 | 466.9985 | 588.7284 | 742.1081 | 935.4943 | 1179.471 | 1484.648 | 1868.0764 | 2351.9671 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 37.9403 | 46.4022 | 56.9224 | 70.0227 | 86.3602 | 106.7637 | 132.2781 | 164.2226 | 204.2626 | 254.5023 | 317.6011 | 396.9214 | 496.7168 | 622.3693 | 780.6916 | 980.3094 | 1232.148 | 1550.0482 | 1951.5485 | 2458.879 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 23.2705 | 31.7324 | 42.2526 | 55.3529 | 71.6904 | 92.0939 | 117.6083 | 149.5528 | 189.5929 | 239.8325 | 302.9313 | 382.2517 | 482.0471 | 607.6996 | 766.0218 | 965.6396 | 1217.4783 | 1532.4893 | 1928.2733 | 2427.7569 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 5.3476 | 6.5403 | 8.0232 | 9.8696 | 12.1724 | 15.0482 | 18.6445 | 23.147 | 28.7906 | 35.8718 | 44.7655 | 55.9457 | 70.0117 | 87.7223 | 110.0377 | 138.1736 | 173.67 | 218.4777 | 275.0688 | 346.5765 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 3.28 | 4.4727 | 5.9555 | 7.8019 | 10.1047 | 12.9805 | 16.5768 | 21.0793 | 26.7229 | 33.8042 | 42.6979 | 53.878 | 67.944 | 85.6546 | 107.97 | 136.1059 | 171.6023 | 216.0028 | 271.7881 | 342.1898 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49.0945 | 66.9469 | 89.1417 | 116.7797 | 151.2475 | 194.2933 | 248.1219 | 315.5162 | 399.9899 | 505.9821 | 639.1035 | 806.4482 | 1016.9896 | 1282.0826 | 1616.0998 | 2037.2398 | 2568.5515 | 3233.1402 | 4068.1378 | 5121.9138 | 5551.4471 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 4657 | 22008217 | WBE | Blank | 22 | CB TR NO.1 | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 5.5 | 0.010964 | 0 | 0.010964 | 30.1506 | 0 | 30.1506 | 31.1222 | 4.3866 | 0 |  | 12.2319 | 0.089657 | 0 | 0.089657 | 246.5573 | 0 | 246.5573 | 254.5023 | 35.8718 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 65.6594 | 536.9314 | 30.9493 | 505.9821 |  | 0.07993 |  | 5.9577 | 6.4534 | 6.9904 | 7.5721 | 8.2022 | 8.8847 | 9.624 | 10.4248 | 11.2923 | 12.2319 | 13.2497 | 14.3522 | 15.5465 | 16.8401 | 18.2414 | 19.7593 | 21.4035 | 23.1845 | 25.1137 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.013366 | 0.016347 | 0.020053 | 0.024668 | 0.030423 | 0.037611 | 0.0466 | 0.057853 | 0.071959 | 0.089657 | 0.11189 | 0.13983 | 0.17499 | 0.21925 | 0.27503 | 0.34535 | 0.43407 | 0.54606 | 0.6875 | 0.86622 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0438 | 97.8962 | 120.091 | 147.729 | 182.1968 | 225.2426 | 279.0712 | 346.4655 | 430.9392 | 536.9314 | 670.0528 | 837.3975 | 1047.9389 | 1313.0319 | 1647.0491 | 2068.1891 | 2599.5008 | 3270.1846 | 4117.2423 | 5187.5732 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 36.7559 | 44.9536 | 55.1454 | 67.8367 | 83.6642 | 103.4307 | 128.1487 | 159.0959 | 197.886 | 246.5573 | 307.6862 | 384.5303 | 481.2103 | 602.9402 | 756.3199 | 949.7061 | 1193.6828 | 1501.6587 | 1890.625 | 2382.1177 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 22.544 | 30.7418 | 40.9336 | 53.6249 | 69.4524 | 89.2189 | 113.9368 | 144.8841 | 183.6741 | 232.3454 | 293.4744 | 370.3185 | 466.9985 | 588.7284 | 742.1081 | 935.4943 | 1179.471 | 1484.648 | 1868.0764 | 2351.9671 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22.544 | 30.7418 | 40.9336 | 53.6249 | 69.4524 | 89.2189 | 113.9368 | 144.8841 | 183.6741 | 232.3454 | 293.4744 | 370.3185 | 466.9985 | 588.7284 | 742.1081 | 935.4943 | 1179.471 | 1484.648 | 1868.0764 | 2351.9671 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 37.9403 | 46.4022 | 56.9224 | 70.0227 | 86.3602 | 106.7637 | 132.2781 | 164.2226 | 204.2626 | 254.5023 | 317.6011 | 396.9214 | 496.7168 | 622.3693 | 780.6916 | 980.3094 | 1232.148 | 1550.0482 | 1951.5485 | 2458.879 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 23.2705 | 31.7324 | 42.2526 | 55.3529 | 71.6904 | 92.0939 | 117.6083 | 149.5528 | 189.5929 | 239.8325 | 302.9313 | 382.2517 | 482.0471 | 607.6996 | 766.0218 | 965.6396 | 1217.4783 | 1532.4893 | 1928.2733 | 2427.7569 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 5.3476 | 6.5403 | 8.0232 | 9.8696 | 12.1724 | 15.0482 | 18.6445 | 23.147 | 28.7906 | 35.8718 | 44.7655 | 55.9457 | 70.0117 | 87.7223 | 110.0377 | 138.1736 | 173.67 | 218.4777 | 275.0688 | 346.5765 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 3.28 | 4.4727 | 5.9555 | 7.8019 | 10.1047 | 12.9805 | 16.5768 | 21.0793 | 26.7229 | 33.8042 | 42.6979 | 53.878 | 67.944 | 85.6546 | 107.97 | 136.1059 | 171.6023 | 216.0028 | 271.7881 | 342.1898 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49.0945 | 66.9469 | 89.1417 | 116.7797 | 151.2475 | 194.2933 | 248.1219 | 315.5162 | 399.9899 | 505.9821 | 639.1035 | 806.4482 | 1016.9896 | 1282.0826 | 1616.0998 | 2037.2398 | 2568.5515 | 3233.1402 | 4068.1378 | 5121.9138 | 5551.4471 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 4658 | 22008221 | WBE | Blank | 22 | CB TR NO.2 | CB FAIL | X | EMAIL | GROUP_3183 | GROUP 3183 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 235.3564 | 0 | 235.3564 | 121.4703 | 17.1211 | 0 |  | 20.1542 | 0.31092 | 0 | 0.31092 | 1710.0365 | 0 | 1710.0365 | 882.5704 | 124.3974 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 373.9478 | 2717.0043 | 45.1611 | 2671.8431 |  | 0.071088 |  | 10.6294 | 11.4125 | 12.2533 | 13.1561 | 14.1254 | 15.1661 | 16.2834 | 17.4831 | 18.7712 | 20.1542 | 21.639 | 23.2333 | 24.945 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.051896 | 0.063029 | 0.076653 | 0.093338 | 0.11379 | 0.13887 | 0.16964 | 0.20743 | 0.25385 | 0.31092 | 0.38109 | 0.46742 | 0.57368 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.5085 | 550.7932 | 669.8476 | 815.6541 | 994.3516 | 1213.5054 | 1482.442 | 1812.6618 | 2218.3493 | 2717.0043 | 3330.2204 | 4084.6492 | 5013.1908 | 6156.4658 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 285.4306 | 346.6599 | 421.5907 | 513.3589 | 625.8281 | 763.7598 | 933.0239 | 1140.8586 | 1396.1915 | 1710.0365 | 2095.9844 | 2570.8091 | 3155.2174 | 3874.7754 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 271.2187 | 332.4481 | 407.3789 | 499.1471 | 611.6162 | 749.548 | 918.8121 | 1126.6468 | 1381.9797 | 1695.8247 | 2081.7725 | 2556.5973 | 3141.0056 | 3860.5636 | 4392.8169 | 4392.8169 | 4392.8169 | 4390.018 | 4384.48 | 4376.8781 | 4366.3959 | 4351.8833 | 4331.7161 | 4303.598 | 4264.2771 | 4209.1427 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 271.2187 | 332.4481 | 407.3789 | 499.1471 | 611.6162 | 749.548 | 918.8121 | 1126.6468 | 1381.9797 | 1695.8247 | 2081.7725 | 2556.5973 | 3141.0056 | 3860.5636 | 4392.8169 | 4392.8169 | 4392.8169 | 4390.018 | 4384.48 | 4376.8781 | 4366.3959 | 4351.8833 | 4331.7161 | 4303.598 | 4264.2771 | 4209.1427 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 147.3141 | 178.9154 | 217.588 | 264.9507 | 322.9974 | 394.1856 | 481.5448 | 588.8108 | 720.5912 | 882.5704 | 1081.7627 | 1326.8254 | 1628.4456 | 1999.8181 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 132.6444 | 164.2456 | 202.9183 | 250.2809 | 308.3276 | 379.5158 | 466.8751 | 574.1411 | 705.9214 | 867.9006 | 1067.0929 | 1312.1557 | 1613.7758 | 1985.1483 | 2259.8506 | 2259.8506 | 2259.8506 | 2256.9616 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 20.7638 | 25.2179 | 30.6688 | 37.3445 | 45.5261 | 55.5601 | 67.8732 | 82.9923 | 101.5666 | 124.3974 | 152.4733 | 187.0147 | 229.5277 | 281.8723 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 18.6961 | 23.1502 | 28.6011 | 35.2768 | 43.4585 | 53.4924 | 65.8056 | 80.9246 | 99.4989 | 122.3297 | 150.4056 | 184.947 | 227.46 | 279.8046 | 318.5236 | 318.5236 | 318.5236 | 318.1164 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 422.5592 | 519.8439 | 638.8983 | 784.7048 | 963.4023 | 1182.5561 | 1451.4927 | 1781.7125 | 2187.4 | 2686.055 | 3299.2711 | 4053.6999 | 4982.2415 | 6125.5165 | 6971.1911 | 6971.1911 | 6971.1911 | 6965.096 | 6953.0359 | 6936.481 | 6913.6539 | 6882.0494 | 6838.131 | 6776.8978 | 6691.2682 | 6571.2012 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 4659 | 22008219 | WBE | Blank | 22 | CB TR NO.2 | CB FAIL | Y | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 5.5 | 0.010964 | 0 | 0.010964 | 30.1506 | 0 | 30.1506 | 31.1222 | 4.3866 | 0 |  | 12.2319 | 0.089657 | 0 | 0.089657 | 246.5573 | 0 | 246.5573 | 254.5023 | 35.8718 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 65.6594 | 536.9314 | 30.9493 | 505.9821 |  | 0.07993 |  | 5.9577 | 6.4534 | 6.9904 | 7.5721 | 8.2022 | 8.8847 | 9.624 | 10.4248 | 11.2923 | 12.2319 | 13.2497 | 14.3522 | 15.5465 | 16.8401 | 18.2414 | 19.7593 | 21.4035 | 23.1845 | 25.1137 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.013366 | 0.016347 | 0.020053 | 0.024668 | 0.030423 | 0.037611 | 0.0466 | 0.057853 | 0.071959 | 0.089657 | 0.11189 | 0.13983 | 0.17499 | 0.21925 | 0.27503 | 0.34535 | 0.43407 | 0.54606 | 0.6875 | 0.86622 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0438 | 97.8962 | 120.091 | 147.729 | 182.1968 | 225.2426 | 279.0712 | 346.4655 | 430.9392 | 536.9314 | 670.0528 | 837.3975 | 1047.9389 | 1313.0319 | 1647.0491 | 2068.1891 | 2599.5008 | 3270.1846 | 4117.2423 | 5187.5732 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 36.7559 | 44.9536 | 55.1454 | 67.8367 | 83.6642 | 103.4307 | 128.1487 | 159.0959 | 197.886 | 246.5573 | 307.6862 | 384.5303 | 481.2103 | 602.9402 | 756.3199 | 949.7061 | 1193.6828 | 1501.6587 | 1890.625 | 2382.1177 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 22.544 | 30.7418 | 40.9336 | 53.6249 | 69.4524 | 89.2189 | 113.9368 | 144.8841 | 183.6741 | 232.3454 | 293.4744 | 370.3185 | 466.9985 | 588.7284 | 742.1081 | 935.4943 | 1179.471 | 1484.648 | 1868.0764 | 2351.9671 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22.544 | 30.7418 | 40.9336 | 53.6249 | 69.4524 | 89.2189 | 113.9368 | 144.8841 | 183.6741 | 232.3454 | 293.4744 | 370.3185 | 466.9985 | 588.7284 | 742.1081 | 935.4943 | 1179.471 | 1484.648 | 1868.0764 | 2351.9671 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 37.9403 | 46.4022 | 56.9224 | 70.0227 | 86.3602 | 106.7637 | 132.2781 | 164.2226 | 204.2626 | 254.5023 | 317.6011 | 396.9214 | 496.7168 | 622.3693 | 780.6916 | 980.3094 | 1232.148 | 1550.0482 | 1951.5485 | 2458.879 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 23.2705 | 31.7324 | 42.2526 | 55.3529 | 71.6904 | 92.0939 | 117.6083 | 149.5528 | 189.5929 | 239.8325 | 302.9313 | 382.2517 | 482.0471 | 607.6996 | 766.0218 | 965.6396 | 1217.4783 | 1532.4893 | 1928.2733 | 2427.7569 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 5.3476 | 6.5403 | 8.0232 | 9.8696 | 12.1724 | 15.0482 | 18.6445 | 23.147 | 28.7906 | 35.8718 | 44.7655 | 55.9457 | 70.0117 | 87.7223 | 110.0377 | 138.1736 | 173.67 | 218.4777 | 275.0688 | 346.5765 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 3.28 | 4.4727 | 5.9555 | 7.8019 | 10.1047 | 12.9805 | 16.5768 | 21.0793 | 26.7229 | 33.8042 | 42.6979 | 53.878 | 67.944 | 85.6546 | 107.97 | 136.1059 | 171.6023 | 216.0028 | 271.7881 | 342.1898 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49.0945 | 66.9469 | 89.1417 | 116.7797 | 151.2475 | 194.2933 | 248.1219 | 315.5162 | 399.9899 | 505.9821 | 639.1035 | 806.4482 | 1016.9896 | 1282.0826 | 1616.0998 | 2037.2398 | 2568.5515 | 3233.1402 | 4068.1378 | 5121.9138 | 5551.4471 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 4660 | 22008222 | WBE | Blank | 22 | CB TR NO.3 | CB FAIL | X | EMAIL | GROUP_3183 | GROUP 3183 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 235.3564 | 0 | 235.3564 | 121.4703 | 17.1211 | 0 |  | 20.1542 | 0.31092 | 0 | 0.31092 | 1710.0365 | 0 | 1710.0365 | 882.5704 | 124.3974 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 373.9478 | 2717.0043 | 45.1611 | 2671.8431 |  | 0.071088 |  | 10.6294 | 11.4125 | 12.2533 | 13.1561 | 14.1254 | 15.1661 | 16.2834 | 17.4831 | 18.7712 | 20.1542 | 21.639 | 23.2333 | 24.945 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.051896 | 0.063029 | 0.076653 | 0.093338 | 0.11379 | 0.13887 | 0.16964 | 0.20743 | 0.25385 | 0.31092 | 0.38109 | 0.46742 | 0.57368 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.5085 | 550.7932 | 669.8476 | 815.6541 | 994.3516 | 1213.5054 | 1482.442 | 1812.6618 | 2218.3493 | 2717.0043 | 3330.2204 | 4084.6492 | 5013.1908 | 6156.4658 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 285.4306 | 346.6599 | 421.5907 | 513.3589 | 625.8281 | 763.7598 | 933.0239 | 1140.8586 | 1396.1915 | 1710.0365 | 2095.9844 | 2570.8091 | 3155.2174 | 3874.7754 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 271.2187 | 332.4481 | 407.3789 | 499.1471 | 611.6162 | 749.548 | 918.8121 | 1126.6468 | 1381.9797 | 1695.8247 | 2081.7725 | 2556.5973 | 3141.0056 | 3860.5636 | 4392.8169 | 4392.8169 | 4392.8169 | 4390.018 | 4384.48 | 4376.8781 | 4366.3959 | 4351.8833 | 4331.7161 | 4303.598 | 4264.2771 | 4209.1427 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 271.2187 | 332.4481 | 407.3789 | 499.1471 | 611.6162 | 749.548 | 918.8121 | 1126.6468 | 1381.9797 | 1695.8247 | 2081.7725 | 2556.5973 | 3141.0056 | 3860.5636 | 4392.8169 | 4392.8169 | 4392.8169 | 4390.018 | 4384.48 | 4376.8781 | 4366.3959 | 4351.8833 | 4331.7161 | 4303.598 | 4264.2771 | 4209.1427 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 147.3141 | 178.9154 | 217.588 | 264.9507 | 322.9974 | 394.1856 | 481.5448 | 588.8108 | 720.5912 | 882.5704 | 1081.7627 | 1326.8254 | 1628.4456 | 1999.8181 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 132.6444 | 164.2456 | 202.9183 | 250.2809 | 308.3276 | 379.5158 | 466.8751 | 574.1411 | 705.9214 | 867.9006 | 1067.0929 | 1312.1557 | 1613.7758 | 1985.1483 | 2259.8506 | 2259.8506 | 2259.8506 | 2256.9616 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 20.7638 | 25.2179 | 30.6688 | 37.3445 | 45.5261 | 55.5601 | 67.8732 | 82.9923 | 101.5666 | 124.3974 | 152.4733 | 187.0147 | 229.5277 | 281.8723 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 18.6961 | 23.1502 | 28.6011 | 35.2768 | 43.4585 | 53.4924 | 65.8056 | 80.9246 | 99.4989 | 122.3297 | 150.4056 | 184.947 | 227.46 | 279.8046 | 318.5236 | 318.5236 | 318.5236 | 318.1164 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 422.5592 | 519.8439 | 638.8983 | 784.7048 | 963.4023 | 1182.5561 | 1451.4927 | 1781.7125 | 2187.4 | 2686.055 | 3299.2711 | 4053.6999 | 4982.2415 | 6125.5165 | 6971.1911 | 6971.1911 | 6971.1911 | 6965.096 | 6953.0359 | 6936.481 | 6913.6539 | 6882.0494 | 6838.131 | 6776.8978 | 6691.2682 | 6571.2012 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 4661 | 22008220 | WBE | Blank | 22 | CB TR NO.3 | CB FAIL | Y | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 5.5 | 0.010964 | 0 | 0.010964 | 30.1506 | 0 | 30.1506 | 31.1222 | 4.3866 | 0 |  | 12.2319 | 0.089657 | 0 | 0.089657 | 246.5573 | 0 | 246.5573 | 254.5023 | 35.8718 | 0 |  | 0.0051679 | 0 | 0.0051679 | 14.2118 | 0 | 14.2118 | 14.6698 | 2.0677 | 0 |  | 65.6594 | 536.9314 | 30.9493 | 505.9821 |  | 0.07993 |  | 5.9577 | 6.4534 | 6.9904 | 7.5721 | 8.2022 | 8.8847 | 9.624 | 10.4248 | 11.2923 | 12.2319 | 13.2497 | 14.3522 | 15.5465 | 16.8401 | 18.2414 | 19.7593 | 21.4035 | 23.1845 | 25.1137 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.013366 | 0.016347 | 0.020053 | 0.024668 | 0.030423 | 0.037611 | 0.0466 | 0.057853 | 0.071959 | 0.089657 | 0.11189 | 0.13983 | 0.17499 | 0.21925 | 0.27503 | 0.34535 | 0.43407 | 0.54606 | 0.6875 | 0.86622 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0438 | 97.8962 | 120.091 | 147.729 | 182.1968 | 225.2426 | 279.0712 | 346.4655 | 430.9392 | 536.9314 | 670.0528 | 837.3975 | 1047.9389 | 1313.0319 | 1647.0491 | 2068.1891 | 2599.5008 | 3270.1846 | 4117.2423 | 5187.5732 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 | 5639.9336 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 36.7559 | 44.9536 | 55.1454 | 67.8367 | 83.6642 | 103.4307 | 128.1487 | 159.0959 | 197.886 | 246.5573 | 307.6862 | 384.5303 | 481.2103 | 602.9402 | 756.3199 | 949.7061 | 1193.6828 | 1501.6587 | 1890.625 | 2382.1177 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 | 2589.8402 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 22.544 | 30.7418 | 40.9336 | 53.6249 | 69.4524 | 89.2189 | 113.9368 | 144.8841 | 183.6741 | 232.3454 | 293.4744 | 370.3185 | 466.9985 | 588.7284 | 742.1081 | 935.4943 | 1179.471 | 1484.648 | 1868.0764 | 2351.9671 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22.544 | 30.7418 | 40.9336 | 53.6249 | 69.4524 | 89.2189 | 113.9368 | 144.8841 | 183.6741 | 232.3454 | 293.4744 | 370.3185 | 466.9985 | 588.7284 | 742.1081 | 935.4943 | 1179.471 | 1484.648 | 1868.0764 | 2351.9671 | 2549.2075 | 2534.6948 | 2514.5276 | 2486.4095 | 2447.0886 | 2391.9542 | 2314.4614 | 2205.3099 | 2051.2723 | 1833.5203 |  | 37.9403 | 46.4022 | 56.9224 | 70.0227 | 86.3602 | 106.7637 | 132.2781 | 164.2226 | 204.2626 | 254.5023 | 317.6011 | 396.9214 | 496.7168 | 622.3693 | 780.6916 | 980.3094 | 1232.148 | 1550.0482 | 1951.5485 | 2458.879 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 23.2705 | 31.7324 | 42.2526 | 55.3529 | 71.6904 | 92.0939 | 117.6083 | 149.5528 | 189.5929 | 239.8325 | 302.9313 | 382.2517 | 482.0471 | 607.6996 | 766.0218 | 965.6396 | 1217.4783 | 1532.4893 | 1928.2733 | 2427.7569 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 5.3476 | 6.5403 | 8.0232 | 9.8696 | 12.1724 | 15.0482 | 18.6445 | 23.147 | 28.7906 | 35.8718 | 44.7655 | 55.9457 | 70.0117 | 87.7223 | 110.0377 | 138.1736 | 173.67 | 218.4777 | 275.0688 | 346.5765 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 3.28 | 4.4727 | 5.9555 | 7.8019 | 10.1047 | 12.9805 | 16.5768 | 21.0793 | 26.7229 | 33.8042 | 42.6979 | 53.878 | 67.944 | 85.6546 | 107.97 | 136.1059 | 171.6023 | 216.0028 | 271.7881 | 342.1898 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49.0945 | 66.9469 | 89.1417 | 116.7797 | 151.2475 | 194.2933 | 248.1219 | 315.5162 | 399.9899 | 505.9821 | 639.1035 | 806.4482 | 1016.9896 | 1282.0826 | 1616.0998 | 2037.2398 | 2568.5515 | 3233.1402 | 4068.1378 | 5121.9138 | 5551.4471 | 5519.8426 | 5475.9243 | 5414.691 | 5329.0614 | 5208.9944 | 5040.2371 | 4802.5362 | 4467.0862 | 3992.8845
| TRUE | 4662 | 22013834 | WBE | Blank | 22 | ALL FEEDERS | MASTER EARTH FAULT | X | RMS | 2C138 | 2C138 | RMS 2C13X | Electronic |  | 0.81881 | 2190 |  | 1.3888 | 0.004397 | 0.0035096 | 0.00088747 | 13.057 | 245.6698 | 258.7268 | 32.4061 | 1.7943 | 7322.4144 |  | 5.9766 | 0.011462 | 0.0091489 | 0.0023135 | 34.0375 | 640.4228 | 674.4603 | 84.4777 | 4.6776 | 19088.386 |  | 0.0051679 | 5.7967e-06 | 0.0051621 | 14.2134 | 0.40577 | 14.6192 | 14.7027 | 2.0677 | 12.0942 |  | 7615.3417 | 19852.0016 | 43.4839 | 19808.5177 |  | 0.14594 |  | 1.607 | 1.8595 | 2.1517 | 2.4898 | 2.881 | 3.3337 | 3.8575 | 4.4636 | 5.165 | 5.9766 | 6.9156 | 8.0023 | 9.2597 | 10.7146 | 12.3982 | 14.3463 | 16.6004 | 19.2088 | 22.2271 | 25.7196 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.004397 | 0.0056559 | 0.0080024 | 0.011462 | 0.016596 | 0.024256 | 0.035742 | 0.053038 | 0.079183 | 0.11883 | 0.17914 | 0.27108 | 0.41157 | 0.62663 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0035096 | 0.0035096 | 0.0035096 | 0.0035096 | 0.0035096 | 0.0035096 | 0.0035096 | 0.0045143 | 0.0063873 | 0.0091489 | 0.013247 | 0.019361 | 0.028528 | 0.042333 | 0.063201 | 0.094848 | 0.14298 | 0.21637 | 0.3285 | 0.50016 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 0.63955 | 7615.3417 | 7615.3417 | 7615.3417 | 7615.3417 | 7615.3417 | 7615.3417 | 7615.3417 | 9795.5759 | 13859.6247 | 19852.0016 | 28743.422 | 42010.1058 | 61902.4218 | 91858.0993 | 137138.4079 | 205808.438 | 310248.6979 | 469487.4731 | 712801.5805 | 1085277.949 | 1387754.1931 | 1387754.1931 | 1387754.1931 | 1387754.1931 | 1387754.1931 | 1387754.1931 | 1387754.1931 | 1387754.1931 | 1387754.1931 | 1387754.1931 |  | 43.4839 | 43.4839 | 43.4839 | 43.4839 | 43.4839 | 43.4839 | 43.4839 | 43.4839 | 43.4839 | 43.4839 | 43.4839 | 43.4839 | 43.4839 | 43.4839 | 43.4839 | 43.4839 | 43.4839 | 52.0475 | 68.992 | 92.2516 | 124.3238 | 168.7282 | 230.4337 | 316.4665 | 436.7764 | 605.4709 | 842.5755 | 1176.5459 | 1647.8541 | 2314.1089 |  | 13.057 | 13.057 | 13.057 | 13.057 | 13.057 | 13.057 | 13.057 | 16.7951 | 23.7632 | 34.0375 | 49.2824 | 72.029 | 106.1356 | 157.4965 | 235.1324 | 352.8715 | 531.9408 | 804.9657 | 1222.143 | 1860.7771 | 2379.3916 | 2379.3916 | 2379.3916 | 2379.3916 | 2379.3916 | 2379.3916 | 2379.3916 | 2379.3916 | 2379.3916 | 2379.3916 |  | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 14.2134 | 17.0126 | 22.5512 | 30.154 | 40.6373 | 55.1516 | 75.321 | 103.4423 | 142.7676 | 197.9082 | 275.4097 | 384.5735 | 538.6283 | 756.4047 |  | -1.1564 | -1.1564 | -1.1564 | -1.1564 | -1.1564 | -1.1564 | -1.1564 | 2.5817 | 9.5498 | 19.8241 | 35.069 | 57.8155 | 91.9222 | 143.2831 | 220.919 | 338.6581 | 517.7274 | 787.9531 | 1199.5918 | 1830.6231 | 2338.7543 | 2324.24 | 2304.0705 | 2275.9493 | 2236.624 | 2181.4834 | 2103.9819 | 1994.8181 | 1840.7633 | 1622.9869 |  | 245.6698 | 245.6698 | 245.6698 | 245.6698 | 245.6698 | 245.6698 | 245.6698 | 316.0039 | 447.1095 | 640.4228 | 927.2587 | 1355.2401 | 1996.9634 | 2963.3293 | 4424.0657 | 6639.3512 | 10008.5792 | 15145.5996 | 22994.8783 | 35010.9134 | 44768.7543 | 44768.7543 | 44768.7543 | 44768.7543 | 44768.7543 | 44768.7543 | 44768.7543 | 44768.7543 | 44768.7543 | 44768.7543 |  | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.40577 | 0.48568 | 0.64379 | 0.86084 | 1.1601 | 1.5745 | 2.1503 | 2.9531 | 4.0757 | 5.6499 | 7.8624 | 10.9788 | 15.3768 | 21.5939 |  | 245.2641 | 245.2641 | 245.2641 | 245.2641 | 245.2641 | 245.2641 | 245.2641 | 315.5981 | 446.7038 | 640.017 | 926.853 | 1354.8343 | 1996.5576 | 2962.9235 | 4423.6599 | 6638.9454 | 10008.1734 | 15145.1139 | 22994.2346 | 35010.0526 | 44767.5942 | 44767.1799 | 44766.6041 | 44765.8013 | 44764.6786 | 44763.1044 | 44760.8919 | 44757.7755 | 44753.3775 | 44747.1604 |  | 244.1076 | 244.1076 | 244.1076 | 244.1076 | 244.1076 | 244.1076 | 244.1076 | 318.1798 | 456.2535 | 659.8411 | 961.922 | 1412.6499 | 2088.4798 | 3106.2066 | 4644.5789 | 6977.6034 | 10525.9009 | 15933.0671 | 24193.8264 | 36840.6757 | 47106.3485 | 47091.4199 | 47070.6746 | 47041.7505 | 47001.3026 | 46944.5879 | 46864.8738 | 46752.5936 | 46594.1408 | 46370.1473 |  | 32.4061 | 32.4061 | 32.4061 | 32.4061 | 32.4061 | 32.4061 | 32.4061 | 41.6839 | 58.9779 | 84.4777 | 122.314 | 178.7688 | 263.418 | 390.8907 | 583.5754 | 875.7921 | 1320.2246 | 1997.8454 | 3033.2382 | 4618.2649 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 | 5905.4148 |  | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 14.7027 | 17.5982 | 23.3275 | 31.192 | 42.0362 | 57.0501 | 77.9139 | 107.0032 | 147.6822 | 204.7209 | 284.8903 | 397.8119 | 557.1698 | 782.4429 |  | 17.7034 | 17.7034 | 17.7034 | 17.7034 | 17.7034 | 17.7034 | 17.7034 | 26.9812 | 44.2752 | 69.775 | 107.6114 | 164.0661 | 248.7153 | 376.188 | 568.8727 | 861.0894 | 1305.5219 | 1980.2471 | 3009.9107 | 4587.0729 | 5863.3786 | 5848.3647 | 5827.5009 | 5798.4116 | 5757.7326 | 5700.6939 | 5620.5245 | 5507.6029 | 5348.2449 | 5122.9719 |  | 1.7943 | 1.7943 | 1.7943 | 1.7943 | 1.7943 | 1.7943 | 1.7943 | 2.3081 | 3.2656 | 4.6776 | 6.7726 | 9.8985 | 14.5856 | 21.6439 | 32.313 | 48.4932 | 73.1017 | 110.6221 | 167.9525 | 255.7165 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 | 326.9868 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.475 | 3.2807 | 4.3868 | 5.9119 | 8.0234 | 10.9576 | 15.0486 | 20.7696 | 28.7914 | 40.0662 | 55.9472 | 78.3589 | 110.0408 |  | -0.2734 | -0.2734 | -0.2734 | -0.2734 | -0.2734 | -0.2734 | -0.2734 | 0.24031 | 1.1979 | 2.6098 | 4.7049 | 7.8308 | 12.5179 | 19.5761 | 30.2452 | 46.4255 | 71.034 | 108.1471 | 164.6718 | 251.3297 | 321.075 | 318.9635 | 316.0292 | 311.9382 | 306.2172 | 298.1954 | 286.9206 | 271.0396 | 248.6279 | 216.9461 |  | 7322.4144 | 7322.4144 | 7322.4144 | 7322.4144 | 7322.4144 | 7322.4144 | 7322.4144 | 9418.785 | 13326.5085 | 19088.386 | 27637.7942 | 40394.1694 | 59521.3192 | 88324.739 | 131863.3215 | 197891.9301 | 298314.8515 | 451428.4403 | 685383.3685 | 1043532.2772 | 1334373.6456 | 1334373.6456 | 1334373.6456 | 1334373.6456 | 1334373.6456 | 1334373.6456 | 1334373.6456 | 1334373.6456 | 1334373.6456 | 1334373.6456 |  | 12.0942 | 12.0942 | 12.0942 | 12.0942 | 12.0942 | 12.0942 | 12.0942 | 12.0942 | 12.0942 | 12.0942 | 12.0942 | 12.0942 | 12.0942 | 12.0942 | 12.0942 | 12.0942 | 12.0942 | 14.476 | 19.1888 | 25.6581 | 34.5784 | 46.9286 | 64.0909 | 88.0193 | 121.4813 | 168.4005 | 234.3468 | 327.2345 | 458.3202 | 643.6266 |  | 7310.3202 | 7310.3202 | 7310.3202 | 7310.3202 | 7310.3202 | 7310.3202 | 7310.3202 | 9406.6908 | 13314.4142 | 19076.2918 | 27625.7 | 40382.0752 | 59509.225 | 88312.6448 | 131851.2272 | 197879.8358 | 298302.7573 | 451413.9643 | 685364.1796 | 1043506.6191 | 1334339.0672 | 1334326.7169 | 1334309.5547 | 1334285.6263 | 1334252.1643 | 1334205.245 | 1334139.2988 | 1334046.4111 | 1333915.3254 | 1333730.0189 |  | 7571.8579 | 7571.8579 | 7571.8579 | 7571.8579 | 7571.8579 | 7571.8579 | 7571.8579 | 9752.0921 | 13816.1409 | 19808.5177 | 28699.9382 | 41966.6219 | 61858.938 | 91814.6155 | 137094.924 | 205764.9542 | 310205.214 | 469435.4256 | 712732.5885 | 1085185.6974 | 1387629.8693 | 1387585.4649 | 1387523.7595 | 1387437.7266 | 1387317.4167 | 1387148.7223 | 1386911.6177 | 1386577.6472 | 1386106.339 | 1385440.0842
| TRUE | 4663 | 22010042 | WBE | Blank | 22 | ALL FEEDERS | COMMON BUEF | BU | Schweitzer | SEL_351A | SEL 351 | SEL 300s | Digital |  | 0.15703 | 1 |  | 6.6 | 0.017308 | 3.723e-06 | 0.017304 | 59.497 | 0.39092 | 59.888 | 49.1515 | 6.9249 | 7.7678 |  | 14.9721 | 0.15742 | 3.3861e-05 | 0.15738 | 541.1327 | 3.5555 | 544.6882 | 447.0388 | 62.9829 | 70.649 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 17.7652 | 0.11672 | 17.8819 | 14.6761 | 2.0677 | 2.3194 |  | 123.7322 | 1125.3589 | 36.9451 | 1088.4138 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021358 | 0.026432 | 0.032797 | 0.040794 | 0.050854 | 0.063527 | 0.079507 | 0.099681 | 0.12517 | 0.15742 | 0.19823 | 0.24994 | 0.31549 | 0.39864 | 0.5042 | 0.63826 | 0.80862 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.5943e-06 | 5.6856e-06 | 7.0548e-06 | 8.775e-06 | 1.0939e-05 | 1.3665e-05 | 1.7103e-05 | 2.1442e-05 | 2.6926e-05 | 3.3861e-05 | 4.2641e-05 | 5.3763e-05 | 6.7863e-05 | 8.5751e-05 | 0.00010846 | 0.00013729 | 0.00017394 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 152.6868 | 188.9565 | 234.4596 | 291.6289 | 363.5511 | 454.1453 | 568.3899 | 712.6121 | 894.8572 | 1125.3589 | 1417.1402 | 1786.7797 | 2255.3887 | 2849.8598 | 3604.4592 | 4562.8602 | 5780.7393 | 6732.5495 | 6732.5495 | 6732.5495 | 6732.5495 | 6732.5495 | 6732.5495 | 6732.5495 | 6732.5495 | 6732.5495 | 6732.5495 | 6732.5495 | 6732.5495 | 6732.5495 |  | 33.3929 | 33.3929 | 33.3929 | 33.3929 | 33.3929 | 33.3929 | 33.3929 | 33.3929 | 33.3929 | 33.3929 | 33.3929 | 33.3929 | 33.3929 | 33.3929 | 33.3929 | 33.3929 | 33.3929 | 39.9692 | 52.9815 | 70.8435 | 95.4729 | 129.5726 | 176.9586 | 243.0264 | 335.4168 | 464.9636 | 647.045 | 903.5133 | 1265.4483 | 1777.0902 |  | 73.42 | 90.8604 | 112.7407 | 140.2308 | 174.8148 | 218.3773 | 273.3122 | 342.662 | 430.2952 | 541.1327 | 681.4368 | 859.1792 | 1084.5115 | 1370.365 | 1733.2168 | 2194.0672 | 2779.6886 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 | 3237.3699 |  | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 14.2121 | 17.011 | 22.5491 | 30.1512 | 40.6336 | 55.1466 | 75.3142 | 103.4329 | 142.7547 | 197.8902 | 275.3847 | 384.5386 | 538.5795 | 756.3362 |  | 59.2078 | 76.6482 | 98.5286 | 126.0187 | 160.6027 | 204.1652 | 259.1001 | 328.4499 | 416.0831 | 526.9206 | 667.2247 | 844.9671 | 1070.2994 | 1356.1529 | 1719.0046 | 2179.8551 | 2765.4765 | 3220.3589 | 3214.8208 | 3207.2186 | 3196.7363 | 3182.2233 | 3162.0557 | 3133.9369 | 3094.6152 | 3039.4797 | 2961.9851 | 2852.8313 | 2698.7904 | 2481.0337 |  | 0.4824 | 0.59699 | 0.74075 | 0.92137 | 1.1486 | 1.4348 | 1.7958 | 2.2514 | 2.8272 | 3.5555 | 4.4773 | 5.6451 | 7.1257 | 9.0038 | 11.3879 | 14.4159 | 18.2636 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 | 21.2708 |  | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.11672 | 0.13971 | 0.1852 | 0.24763 | 0.33372 | 0.45292 | 0.61855 | 0.84949 | 1.1724 | 1.6253 | 2.2617 | 3.1582 | 4.4233 | 6.2118 |  | 0.36567 | 0.48026 | 0.62403 | 0.80465 | 1.0319 | 1.3181 | 1.679 | 2.1347 | 2.7105 | 3.4387 | 4.3606 | 5.5284 | 7.0089 | 8.8871 | 11.2712 | 14.2991 | 18.1469 | 21.1311 | 21.0856 | 21.0231 | 20.9371 | 20.8179 | 20.6522 | 20.4213 | 20.0983 | 19.6455 | 19.009 | 18.1126 | 16.8474 | 15.059 |  | 59.5735 | 77.1285 | 99.1526 | 126.8233 | 161.6346 | 205.4833 | 260.7792 | 330.5846 | 418.7935 | 530.3593 | 671.5853 | 850.4955 | 1077.3083 | 1365.04 | 1730.2758 | 2194.1542 | 2783.6234 | 3241.4899 | 3235.9063 | 3228.2418 | 3217.6733 | 3203.0411 | 3182.7079 | 3154.3582 | 3114.7136 | 3059.1252 | 2980.9942 | 2870.9438 | 2715.6378 | 2496.0927 |  | 60.6535 | 75.0613 | 93.137 | 115.847 | 144.4174 | 180.4052 | 225.7878 | 283.0788 | 355.474 | 447.0388 | 562.9463 | 709.7823 | 895.9331 | 1132.0814 | 1431.8393 | 1812.5556 | 2296.3472 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 45.9774 | 60.3852 | 78.4609 | 101.1709 | 129.7413 | 165.7291 | 211.1117 | 268.4027 | 340.7979 | 432.3627 | 548.2702 | 695.1062 | 881.257 | 1117.4053 | 1417.1632 | 1797.8795 | 2281.6711 | 2656.8789 | 2651.16 | 2643.3098 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 8.5454 | 10.5753 | 13.122 | 16.3216 | 20.3468 | 25.4171 | 31.811 | 39.8827 | 50.0824 | 62.9829 | 79.313 | 100.0006 | 126.2272 | 159.4979 | 201.7306 | 255.3693 | 323.5303 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 6.4777 | 8.5076 | 11.0543 | 14.2539 | 18.2791 | 23.3494 | 29.7433 | 37.815 | 48.0147 | 60.9152 | 77.2453 | 97.9329 | 124.1595 | 157.4302 | 199.6629 | 253.3016 | 321.4626 | 374.3253 | 373.5196 | 372.4136 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 9.5855 | 11.8625 | 14.7192 | 18.3082 | 22.8234 | 28.5108 | 35.683 | 44.7371 | 56.1783 | 70.649 | 88.9668 | 112.1724 | 141.5912 | 178.9116 | 226.2847 | 286.4522 | 362.9095 | 422.6633 | 422.6633 | 422.6633 | 422.6633 | 422.6633 | 422.6633 | 422.6633 | 422.6633 | 422.6633 | 422.6633 | 422.6633 | 422.6633 | 422.6633 |  | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.3194 | 2.7761 | 3.68 | 4.9206 | 6.6313 | 8.9998 | 12.2911 | 16.8799 | 23.2971 | 32.2951 | 44.942 | 62.7556 | 87.8946 | 123.4318 |  | 7.2662 | 9.5431 | 12.3998 | 15.9888 | 20.504 | 26.1914 | 33.3636 | 42.4178 | 53.8589 | 68.3296 | 86.6474 | 109.853 | 139.2719 | 176.5922 | 223.9653 | 284.1328 | 360.5902 | 419.8872 | 418.9834 | 417.7427 | 416.032 | 413.6636 | 410.3723 | 405.7834 | 399.3662 | 390.3682 | 377.7213 | 359.9078 | 334.7687 | 299.2315 |  | 119.2947 | 155.5644 | 201.0676 | 258.2369 | 330.1591 | 420.7532 | 534.9978 | 679.2201 | 861.4651 | 1091.9668 | 1383.7482 | 1753.3876 | 2221.9967 | 2816.4678 | 3571.0672 | 4529.4682 | 5747.3472 | 6692.5813 | 6679.5693 | 6661.7078 | 6637.079 | 6602.9801 | 6555.5954 | 6489.5292 | 6397.1411 | 6267.5977 | 6085.5208 | 5829.059 | 5467.133 | 4955.5041
| TRUE | 4664 | 22009481 | WBE | WBE011 | 22 | WBE 11 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 4.0857 | 0.0054221 | 4.2659e-06 | 0.0054179 | 14.9121 | 0.29862 | 15.2107 | 15.4156 | 2.1694 | 10.3779 |  | 11.2347 | 0.070957 | 5.5827e-05 | 0.070902 | 195.148 | 3.9079 | 199.0559 | 201.7376 | 28.3906 | 135.8107 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 9.8913 |  | 43.1736 | 564.9948 | 41.1495 | 523.8453 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0068474 | 0.0087043 | 0.011132 | 0.014316 | 0.018505 | 0.024029 | 0.031333 | 0.041011 | 0.053862 | 0.070957 | 0.093738 | 0.12414 | 0.16478 | 0.21915 | 0.292 | 0.38971 | 0.52087 | 0.69709 | 0.93404 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 5.3872e-06 | 6.8482e-06 | 8.7584e-06 | 1.1264e-05 | 1.4559e-05 | 1.8905e-05 | 2.4651e-05 | 3.2266e-05 | 4.2376e-05 | 5.5827e-05 | 7.375e-05 | 9.767e-05 | 0.00012964 | 0.00017242 | 0.00022974 | 0.00030661 | 0.0004098 | 0.00054844 | 0.00073487 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 54.5218 | 69.3079 | 88.6394 | 113.9937 | 147.3441 | 191.3301 | 249.4856 | 326.5477 | 428.8723 | 564.9948 | 746.3862 | 988.4749 | 1312.0249 | 1744.9984 | 2325.0713 | 3103.0335 | 4147.3839 | 5550.5433 | 7437.2546 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 |  | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 49.2533 | 65.2882 | 87.2992 | 117.6496 | 159.6702 | 218.063 | 299.4773 | 413.3284 | 572.9667 | 797.3425 | 1113.384 | 1559.3904 | 2189.8779 |  | 18.8317 | 23.9388 | 30.6159 | 39.3732 | 50.8924 | 66.085 | 86.1718 | 112.7889 | 148.1316 | 195.148 | 257.8003 | 341.4172 | 453.1708 | 602.7189 | 803.0749 | 1071.7815 | 1432.498 | 1917.1465 | 2568.8127 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 4.6188 | 9.7259 | 16.4029 | 25.1602 | 36.6794 | 51.8721 | 71.9589 | 98.576 | 133.9187 | 180.9351 | 243.5873 | 327.2043 | 438.9578 | 588.506 | 788.862 | 1057.5686 | 1418.2851 | 1900.1345 | 2546.2623 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.37711 | 0.47938 | 0.61309 | 0.78845 | 1.0191 | 1.3234 | 1.7256 | 2.2586 | 2.9664 | 3.9079 | 5.1625 | 6.8369 | 9.0748 | 12.0695 | 16.0817 | 21.4625 | 28.6859 | 38.3911 | 51.4408 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.092491 | 0.19476 | 0.32847 | 0.50384 | 0.73451 | 1.0387 | 1.441 | 1.974 | 2.6817 | 3.6232 | 4.8779 | 6.5523 | 8.7902 | 11.7849 | 15.797 | 21.1779 | 28.4013 | 38.0504 | 50.9892 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 4.7113 | 9.9206 | 16.7314 | 25.6641 | 37.4139 | 52.9108 | 73.3999 | 100.55 | 136.6004 | 184.5584 | 248.4652 | 333.7566 | 447.748 | 600.2909 | 804.659 | 1078.7465 | 1446.6864 | 1938.1849 | 2597.2515 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 19.4676 | 24.7471 | 31.6497 | 40.7027 | 52.6108 | 68.3165 | 89.0816 | 116.5974 | 153.1336 | 201.7376 | 266.5054 | 352.9458 | 468.4729 | 623.0709 | 830.1923 | 1107.9722 | 1480.869 | 1981.8826 | 2655.5536 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 4.7747 | 10.0543 | 16.9568 | 26.0098 | 37.918 | 53.6236 | 74.3887 | 101.9046 | 138.4407 | 187.0447 | 251.8125 | 338.253 | 453.7801 | 608.378 | 815.4994 | 1093.2794 | 1466.1762 | 1964.2961 | 2632.2417 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.7397 | 3.4827 | 4.4541 | 5.7281 | 7.4039 | 9.6142 | 12.5365 | 16.4088 | 21.5505 | 28.3906 | 37.5054 | 49.6702 | 65.9283 | 87.6849 | 116.8332 | 155.9253 | 208.4031 | 278.9109 | 373.7168 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.67195 | 1.4149 | 2.3863 | 3.6604 | 5.3362 | 7.5465 | 10.4687 | 14.3411 | 19.4828 | 26.3229 | 35.4377 | 47.6024 | 63.8606 | 85.6172 | 114.7655 | 153.8575 | 206.3354 | 276.436 | 370.4362 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 13.1057 | 16.6599 | 21.3067 | 27.4012 | 35.4179 | 45.991 | 59.9701 | 78.4939 | 103.0902 | 135.8107 | 179.4126 | 237.6047 | 315.3781 | 419.4541 | 558.8892 | 745.8919 | 996.9277 | 1334.2123 | 1787.7307 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 |  | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 11.8393 | 15.6937 | 20.9845 | 28.28 | 38.3807 | 52.4169 | 71.9869 | 99.3539 | 137.7269 | 191.6613 | 267.6298 | 374.8386 | 526.3921 |  | 3.2144 | 6.7686 | 11.4154 | 17.5099 | 25.5266 | 36.0997 | 50.0788 | 68.6026 | 93.1989 | 125.9194 | 169.5213 | 227.7134 | 305.4868 | 409.5628 | 548.9979 | 736.0006 | 987.0364 | 1322.373 | 1772.037 | 1781.5217 | 1774.2262 | 1764.1255 | 1750.0894 | 1730.5194 | 1703.1524 | 1664.7794 | 1610.845 | 1534.8765 | 1427.6677 | 1276.1142 |  | 13.3723 | 28.1584 | 47.4899 | 72.8442 | 106.1947 | 150.1806 | 208.3361 | 285.3982 | 387.7228 | 523.8453 | 705.2367 | 947.3254 | 1270.8755 | 1703.8489 | 2283.9218 | 3061.884 | 4106.2344 | 5501.29 | 7371.9664 | 7411.4243 | 7381.0739 | 7339.0533 | 7280.6605 | 7199.2462 | 7085.395 | 6925.7568 | 6701.381 | 6385.3395 | 5939.3331 | 5308.8456
| TRUE | 4665 | 22009482 | WBE | WBE012 | 22 | WBE 12 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 4.0857 | 0.0054221 | 4.2659e-06 | 0.0054179 | 14.9121 | 0.29862 | 15.2107 | 15.4156 | 2.1694 | 10.3779 |  | 11.2347 | 0.070957 | 5.5827e-05 | 0.070902 | 195.148 | 3.9079 | 199.0559 | 201.7376 | 28.3906 | 135.8107 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 9.8913 |  | 43.1736 | 564.9948 | 41.1495 | 523.8453 |  | 0.10115 |  | 4.5206 | 5.0018 | 5.5342 | 6.1233 | 6.7751 | 7.4962 | 8.2941 | 9.177 | 10.1538 | 11.2347 | 12.4305 | 13.7537 | 15.2177 | 16.8375 | 18.6297 | 20.6128 | 22.8069 | 25.2345 | 27.9206 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0068474 | 0.0087043 | 0.011132 | 0.014316 | 0.018505 | 0.024029 | 0.031333 | 0.041011 | 0.053862 | 0.070957 | 0.093738 | 0.12414 | 0.16478 | 0.21915 | 0.292 | 0.38971 | 0.52087 | 0.69709 | 0.93404 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 5.3872e-06 | 6.8482e-06 | 8.7584e-06 | 1.1264e-05 | 1.4559e-05 | 1.8905e-05 | 2.4651e-05 | 3.2266e-05 | 4.2376e-05 | 5.5827e-05 | 7.375e-05 | 9.767e-05 | 0.00012964 | 0.00017242 | 0.00022974 | 0.00030661 | 0.0004098 | 0.00054844 | 0.00073487 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 54.5218 | 69.3079 | 88.6394 | 113.9937 | 147.3441 | 191.3301 | 249.4856 | 326.5477 | 428.8723 | 564.9948 | 746.3862 | 988.4749 | 1312.0249 | 1744.9984 | 2325.0713 | 3103.0335 | 4147.3839 | 5550.5433 | 7437.2546 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 |  | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 49.2533 | 65.2882 | 87.2992 | 117.6496 | 159.6702 | 218.063 | 299.4773 | 413.3284 | 572.9667 | 797.3425 | 1113.384 | 1559.3904 | 2189.8779 |  | 18.8317 | 23.9388 | 30.6159 | 39.3732 | 50.8924 | 66.085 | 86.1718 | 112.7889 | 148.1316 | 195.148 | 257.8003 | 341.4172 | 453.1708 | 602.7189 | 803.0749 | 1071.7815 | 1432.498 | 1917.1465 | 2568.8127 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 4.6188 | 9.7259 | 16.4029 | 25.1602 | 36.6794 | 51.8721 | 71.9589 | 98.576 | 133.9187 | 180.9351 | 243.5873 | 327.2043 | 438.9578 | 588.506 | 788.862 | 1057.5686 | 1418.2851 | 1900.1345 | 2546.2623 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.37711 | 0.47938 | 0.61309 | 0.78845 | 1.0191 | 1.3234 | 1.7256 | 2.2586 | 2.9664 | 3.9079 | 5.1625 | 6.8369 | 9.0748 | 12.0695 | 16.0817 | 21.4625 | 28.6859 | 38.3911 | 51.4408 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.092491 | 0.19476 | 0.32847 | 0.50384 | 0.73451 | 1.0387 | 1.441 | 1.974 | 2.6817 | 3.6232 | 4.8779 | 6.5523 | 8.7902 | 11.7849 | 15.797 | 21.1779 | 28.4013 | 38.0504 | 50.9892 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 4.7113 | 9.9206 | 16.7314 | 25.6641 | 37.4139 | 52.9108 | 73.3999 | 100.55 | 136.6004 | 184.5584 | 248.4652 | 333.7566 | 447.748 | 600.2909 | 804.659 | 1078.7465 | 1446.6864 | 1938.1849 | 2597.2515 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 19.4676 | 24.7471 | 31.6497 | 40.7027 | 52.6108 | 68.3165 | 89.0816 | 116.5974 | 153.1336 | 201.7376 | 266.5054 | 352.9458 | 468.4729 | 623.0709 | 830.1923 | 1107.9722 | 1480.869 | 1981.8826 | 2655.5536 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 4.7747 | 10.0543 | 16.9568 | 26.0098 | 37.918 | 53.6236 | 74.3887 | 101.9046 | 138.4407 | 187.0447 | 251.8125 | 338.253 | 453.7801 | 608.378 | 815.4994 | 1093.2794 | 1466.1762 | 1964.2961 | 2632.2417 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.7397 | 3.4827 | 4.4541 | 5.7281 | 7.4039 | 9.6142 | 12.5365 | 16.4088 | 21.5505 | 28.3906 | 37.5054 | 49.6702 | 65.9283 | 87.6849 | 116.8332 | 155.9253 | 208.4031 | 278.9109 | 373.7168 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0.67195 | 1.4149 | 2.3863 | 3.6604 | 5.3362 | 7.5465 | 10.4687 | 14.3411 | 19.4828 | 26.3229 | 35.4377 | 47.6024 | 63.8606 | 85.6172 | 114.7655 | 153.8575 | 206.3354 | 276.436 | 370.4362 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 13.1057 | 16.6599 | 21.3067 | 27.4012 | 35.4179 | 45.991 | 59.9701 | 78.4939 | 103.0902 | 135.8107 | 179.4126 | 237.6047 | 315.3781 | 419.4541 | 558.8892 | 745.8919 | 996.9277 | 1334.2123 | 1787.7307 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 |  | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 11.8393 | 15.6937 | 20.9845 | 28.28 | 38.3807 | 52.4169 | 71.9869 | 99.3539 | 137.7269 | 191.6613 | 267.6298 | 374.8386 | 526.3921 |  | 3.2144 | 6.7686 | 11.4154 | 17.5099 | 25.5266 | 36.0997 | 50.0788 | 68.6026 | 93.1989 | 125.9194 | 169.5213 | 227.7134 | 305.4868 | 409.5628 | 548.9979 | 736.0006 | 987.0364 | 1322.373 | 1772.037 | 1781.5217 | 1774.2262 | 1764.1255 | 1750.0894 | 1730.5194 | 1703.1524 | 1664.7794 | 1610.845 | 1534.8765 | 1427.6677 | 1276.1142 |  | 13.3723 | 28.1584 | 47.4899 | 72.8442 | 106.1947 | 150.1806 | 208.3361 | 285.3982 | 387.7228 | 523.8453 | 705.2367 | 947.3254 | 1270.8755 | 1703.8489 | 2283.9218 | 3061.884 | 4106.2344 | 5501.29 | 7371.9664 | 7411.4243 | 7381.0739 | 7339.0533 | 7280.6605 | 7199.2462 | 7085.395 | 6925.7568 | 6701.381 | 6385.3395 | 5939.3331 | 5308.8456
| FALSE | 4666 | 22011672 | WBE | WBE013 | 22 | WBE 13 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 2.8514 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 19.7826 |  | 9.4101 | 0.043865 | 3.4512e-05 | 0.043831 | 120.6389 | 2.4158 | 123.0547 | 124.7125 | 17.5508 | 167.9141 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 19.7826 |  | 51.0408 | 433.2322 | 51.0408 | 382.1914 |  | 0.1194 |  | 3.213 | 3.6205 | 4.0796 | 4.597 | 5.1799 | 5.8369 | 6.5771 | 7.4112 | 8.351 | 9.4101 | 10.6034 | 11.9482 | 13.4634 | 15.1708 | 17.0947 | 19.2626 | 21.7055 | 24.4581 | 27.5598 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0054038 | 0.0071219 | 0.0094715 | 0.0127 | 0.017155 | 0.023326 | 0.031904 | 0.043865 | 0.060591 | 0.084037 | 0.11698 | 0.16335 | 0.22876 | 0.32115 | 0.45186 | 0.63698 | 0.8995 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.2515e-06 | 5.6032e-06 | 7.4518e-06 | 9.9919e-06 | 1.3497e-05 | 1.8352e-05 | 2.5101e-05 | 3.4512e-05 | 4.767e-05 | 6.6117e-05 | 9.2034e-05 | 0.00012852 | 0.00017998 | 0.00025267 | 0.0003555 | 0.00050116 | 0.00070769 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 51.0408 | 51.0408 | 53.3702 | 70.3385 | 93.5449 | 125.4312 | 169.4307 | 230.3791 | 315.0994 | 433.2322 | 598.4184 | 829.9823 | 1155.3283 | 1613.3578 | 2259.3402 | 3171.8598 | 4462.7284 | 6291.1319 | 8883.8268 | 9301.2297 | 9301.2297 | 9301.2297 | 9301.2297 | 9301.2297 | 9301.2297 | 9301.2297 | 9301.2297 | 9301.2297 | 9301.2297 | 9301.2297 |  | 51.0408 | 51.0408 | 51.0408 | 51.0408 | 51.0408 | 51.0408 | 51.0408 | 51.0408 | 51.0408 | 51.0408 | 51.0408 | 51.0408 | 51.0408 | 51.0408 | 51.0408 | 51.0408 | 51.0408 | 61.0926 | 80.9819 | 108.2837 | 145.9296 | 198.0509 | 270.4799 | 371.4641 | 512.6823 | 710.6936 | 989.0037 | 1381.0138 | 1934.229 | 2716.2699 |  | 14.2129 | 14.2129 | 14.8616 | 19.5866 | 26.0487 | 34.9279 | 47.1801 | 64.152 | 87.7434 | 120.6389 | 166.6371 | 231.119 | 321.7156 | 449.2597 | 629.1416 | 883.2441 | 1242.7026 | 1751.8445 | 2473.8129 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0.64867 | 5.3737 | 11.8358 | 20.7149 | 32.9672 | 49.939 | 73.5304 | 106.426 | 152.4242 | 216.906 | 307.5027 | 435.0468 | 614.9286 | 869.0312 | 1228.4897 | 1734.8325 | 2451.2625 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.29761 | 0.39222 | 0.52163 | 0.69943 | 0.94479 | 1.2846 | 1.7571 | 2.4158 | 3.3369 | 4.6282 | 6.4424 | 8.9965 | 12.5986 | 17.6871 | 24.8853 | 35.0809 | 49.5384 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0.01299 | 0.10761 | 0.23701 | 0.41482 | 0.66017 | 1 | 1.4725 | 2.1312 | 3.0523 | 4.3436 | 6.1578 | 8.7119 | 12.314 | 17.4024 | 24.6006 | 34.7402 | 49.0868 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0.66166 | 5.4813 | 12.0728 | 21.1298 | 33.6273 | 50.939 | 75.0029 | 108.5572 | 155.4765 | 221.2496 | 313.6605 | 443.7586 | 627.2427 | 886.4336 | 1253.0903 | 1769.5727 | 2500.3493 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 15.3634 | 20.248 | 26.9283 | 36.1073 | 48.7732 | 66.3182 | 90.7062 | 124.7125 | 172.2639 | 238.9231 | 332.579 | 464.4298 | 650.3857 | 913.0685 | 1284.6648 | 1810.9989 | 2557.3459 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0.67057 | 5.5552 | 12.2355 | 21.4144 | 34.0804 | 51.6253 | 76.0133 | 110.0197 | 157.5711 | 224.2303 | 317.8861 | 449.7369 | 635.6929 | 898.3757 | 1269.972 | 1793.4124 | 2534.034 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.1621 | 2.8495 | 3.7896 | 5.0814 | 6.8639 | 9.333 | 12.7651 | 17.5508 | 24.2428 | 33.6237 | 46.8039 | 65.3593 | 91.529 | 128.4964 | 180.7913 | 254.8624 | 359.896 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0.09437 | 0.78178 | 1.7219 | 3.0137 | 4.7961 | 7.2652 | 10.6974 | 15.4831 | 22.175 | 31.556 | 44.7362 | 63.2916 | 89.4612 | 126.4287 | 178.7235 | 252.3875 | 356.6154 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 19.7826 | 19.7826 | 20.6855 | 27.2621 | 36.2565 | 48.6152 | 65.6687 | 89.2914 | 122.1276 | 167.9141 | 231.9377 | 321.6883 | 447.7873 | 625.3125 | 875.6853 | 1229.3637 | 1729.6844 | 2438.3452 | 3443.2336 | 3605.0125 | 3605.0125 | 3605.0125 | 3605.0125 | 3605.0125 | 3605.0125 | 3605.0125 | 3605.0125 | 3605.0125 | 3605.0125 | 3605.0125 |  | 19.7826 | 19.7826 | 19.7826 | 19.7826 | 19.7826 | 19.7826 | 19.7826 | 19.7826 | 19.7826 | 19.7826 | 19.7826 | 19.7826 | 19.7826 | 19.7826 | 19.7826 | 19.7826 | 19.7826 | 23.6785 | 31.3873 | 41.9691 | 56.5601 | 76.7615 | 104.8338 | 143.9737 | 198.7077 | 275.4538 | 383.3225 | 535.2595 | 749.6772 | 1052.7841 |  | 0 | 0 | 0.90287 | 7.4795 | 16.4739 | 28.8326 | 45.8861 | 69.5088 | 102.345 | 148.1315 | 212.1551 | 301.9057 | 428.0047 | 605.5299 | 855.9026 | 1209.5811 | 1709.9018 | 2414.6667 | 3411.8463 | 3563.0434 | 3548.4525 | 3528.2511 | 3500.1787 | 3461.0388 | 3406.3048 | 3329.5587 | 3221.69 | 3069.753 | 2855.3354 | 2552.2284 |  | 0 | 0 | 2.3295 | 19.2977 | 42.5041 | 74.3904 | 118.3899 | 179.3383 | 264.0586 | 382.1914 | 547.3777 | 778.9415 | 1104.2875 | 1562.317 | 2208.2994 | 3120.819 | 4411.6876 | 6230.0393 | 8802.845 | 9192.946 | 9155.3001 | 9103.1789 | 9030.7498 | 8929.7656 | 8788.5474 | 8590.5362 | 8312.226 | 7920.216 | 7367.0008 | 6584.9598
| FALSE | 4667 | 22011673 | WBE | WBE014 | 22 | WBE 14 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 2.5292 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 9.8913 |  | 8.8804 | 0.037562 | 2.9553e-05 | 0.037533 | 103.305 | 2.0687 | 105.3737 | 106.7933 | 15.029 | 71.8937 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 9.8913 |  | 41.1495 | 299.0897 | 41.1495 | 257.9402 |  | 0.12559 |  | 2.8677 | 3.2514 | 3.6865 | 4.1799 | 4.7392 | 5.3734 | 6.0925 | 6.9078 | 7.8322 | 8.8804 | 10.0687 | 11.4161 | 12.9438 | 14.676 | 16.64 | 18.8667 | 21.3915 | 24.2541 | 27.4998 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0057115 | 0.0076532 | 0.010356 | 0.014137 | 0.019449 | 0.026946 | 0.037562 | 0.052647 | 0.074144 | 0.10486 | 0.14884 | 0.21196 | 0.3027 | 0.43337 | 0.62179 | 0.89383 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.4936e-06 | 6.0213e-06 | 8.1476e-06 | 1.1122e-05 | 1.5302e-05 | 2.12e-05 | 2.9553e-05 | 4.1421e-05 | 5.8334e-05 | 8.2498e-05 | 0.0001171 | 0.00016676 | 0.00023816 | 0.00034096 | 0.0004892 | 0.00070323 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 41.1495 | 41.1495 | 41.1495 | 45.4773 | 60.9386 | 82.4583 | 112.5618 | 154.8647 | 214.5552 | 299.0897 | 419.2027 | 590.369 | 834.9253 | 1185.1489 | 1687.7282 | 2410.2558 | 3450.6655 | 4950.9501 | 7117.1096 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 | 7498.7235 |  | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 41.1495 | 49.2533 | 65.2882 | 87.2992 | 117.6496 | 159.6702 | 218.063 | 299.4773 | 413.3284 | 572.9667 | 797.3425 | 1113.384 | 1559.3904 | 2189.8779 |  | 14.2129 | 14.2129 | 14.2129 | 15.7078 | 21.0481 | 28.4809 | 38.8786 | 53.49 | 74.1069 | 103.305 | 144.7918 | 203.9122 | 288.3815 | 409.3481 | 582.9379 | 832.4975 | 1191.8529 | 1710.0482 | 2458.2353 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 1.4948 | 6.8351 | 14.268 | 24.6657 | 39.277 | 59.894 | 89.092 | 130.5788 | 189.6993 | 274.1686 | 395.1351 | 568.725 | 818.2845 | 1177.64 | 1693.0362 | 2435.6849 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.31455 | 0.42149 | 0.57033 | 0.77855 | 1.0711 | 1.484 | 2.0687 | 2.8995 | 4.0834 | 5.7749 | 8.1972 | 11.6734 | 16.6709 | 23.867 | 34.2439 | 49.2264 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0.029934 | 0.13687 | 0.28572 | 0.49393 | 0.78653 | 1.1994 | 1.7841 | 2.6149 | 3.7987 | 5.4903 | 7.9126 | 11.3888 | 16.3862 | 23.5824 | 33.9032 | 48.7749 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 1.5248 | 6.972 | 14.5537 | 25.1596 | 40.0635 | 61.0934 | 90.8761 | 133.1937 | 193.4981 | 279.6588 | 403.0477 | 580.1137 | 834.6708 | 1201.2223 | 1726.9394 | 2484.4597 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 16.2382 | 21.7588 | 29.4427 | 40.1914 | 55.2962 | 76.6093 | 106.7933 | 149.6809 | 210.7977 | 298.1193 | 423.1705 | 602.6219 | 860.6083 | 1232.0981 | 1767.7912 | 2541.2423 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 1.5453 | 7.0659 | 14.7498 | 25.4985 | 40.6033 | 61.9164 | 92.1004 | 134.9881 | 196.1049 | 283.4264 | 408.4776 | 587.9291 | 845.9155 | 1217.4052 | 1750.2048 | 2517.9304 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.2852 | 3.0621 | 4.1435 | 5.6561 | 7.7818 | 10.7812 | 15.029 | 21.0646 | 29.6656 | 41.9544 | 59.5529 | 84.8072 | 121.1137 | 173.3935 | 248.7818 | 357.6298 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0.21747 | 0.99439 | 2.0757 | 3.5884 | 5.7141 | 8.7135 | 12.9613 | 18.9969 | 27.5979 | 39.8867 | 57.4852 | 82.7394 | 119.0459 | 171.3258 | 246.3068 | 354.3491 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 9.8913 | 9.8913 | 9.8913 | 10.9316 | 14.6481 | 19.8209 | 27.057 | 37.2256 | 51.5737 | 71.8937 | 100.7659 | 141.91 | 200.6952 | 284.8803 | 405.6878 | 579.3654 | 829.454 | 1190.085 | 1710.7758 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 | 1802.5063 |  | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 9.8913 | 11.8393 | 15.6937 | 20.9845 | 28.28 | 38.3807 | 52.4169 | 71.9869 | 99.3539 | 137.7269 | 191.6613 | 267.6298 | 374.8386 | 526.3921 |  | 0 | 0 | 0 | 1.0403 | 4.7568 | 9.9296 | 17.1657 | 27.3343 | 41.6824 | 62.0024 | 90.8746 | 132.0187 | 190.8039 | 274.989 | 395.7965 | 569.4741 | 819.5627 | 1178.2458 | 1695.0822 | 1781.5217 | 1774.2262 | 1764.1255 | 1750.0894 | 1730.5194 | 1703.1524 | 1664.7794 | 1610.845 | 1534.8765 | 1427.6677 | 1276.1142 |  | 0 | 0 | 0 | 4.3278 | 19.7891 | 41.3089 | 71.4123 | 113.7153 | 173.4057 | 257.9402 | 378.0532 | 549.2195 | 793.7758 | 1143.9995 | 1646.5787 | 2369.1063 | 3409.516 | 4901.6968 | 7051.8214 | 7411.4243 | 7381.0739 | 7339.0533 | 7280.6605 | 7199.2462 | 7085.395 | 6925.7568 | 6701.381 | 6385.3395 | 5939.3331 | 5308.8456
| TRUE | 4668 | 22008105 | WBE | WBE021 | 22 | WBE 21 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 6.6 | 0.017308 | 1.3617e-05 | 0.017294 | 59.5004 | 1.4298 | 60.9302 | 49.2077 | 6.925 | 26.6349 |  | 14.9721 | 0.15742 | 0.00012385 | 0.15729 | 541.1637 | 13.0042 | 554.1679 | 447.5497 | 62.9838 | 242.2479 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 17.7662 | 0.42692 | 18.1931 | 14.6929 | 2.0677 | 7.9529 |  | 143.6978 | 1306.9492 | 42.9066 | 1264.0426 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021358 | 0.026432 | 0.032797 | 0.040794 | 0.050854 | 0.063527 | 0.079507 | 0.099681 | 0.12517 | 0.15742 | 0.19823 | 0.24994 | 0.31549 | 0.39864 | 0.5042 | 0.63826 | 0.80862 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.6804e-05 | 2.0795e-05 | 2.5803e-05 | 3.2095e-05 | 4.001e-05 | 4.998e-05 | 6.2553e-05 | 7.8426e-05 | 9.8482e-05 | 0.00012385 | 0.00015596 | 0.00019664 | 0.00024821 | 0.00031364 | 0.00039668 | 0.00050216 | 0.00063619 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 177.3246 | 219.4469 | 272.2926 | 338.6868 | 422.2145 | 527.4272 | 660.1065 | 827.6008 | 1039.2533 | 1306.9492 | 1645.8131 | 2075.0983 | 2619.3232 | 3309.7195 | 4186.0827 | 5299.1333 | 6713.532 | 7818.9285 | 7818.9285 | 7818.9285 | 7818.9285 | 7818.9285 | 7818.9285 | 7818.9285 | 7818.9285 | 7818.9285 | 7818.9285 | 7818.9285 | 7818.9285 | 7818.9285 |  | 39.3564 | 39.3564 | 39.3564 | 39.3564 | 39.3564 | 39.3564 | 39.3564 | 39.3564 | 39.3564 | 39.3564 | 39.3564 | 39.3564 | 39.3564 | 39.3564 | 39.3564 | 39.3564 | 39.3564 | 47.1072 | 62.4434 | 83.4952 | 112.5232 | 152.7128 | 208.5612 | 286.428 | 395.3183 | 548.0005 | 762.5995 | 1064.87 | 1491.4423 | 2094.4572 |  | 73.4242 | 90.8656 | 112.7472 | 140.2388 | 174.8248 | 218.3898 | 273.3279 | 342.6816 | 430.3198 | 541.1637 | 681.4758 | 859.2283 | 1084.5735 | 1370.4434 | 1733.3159 | 2194.1926 | 2779.8475 | 3237.5549 | 3237.5549 | 3237.5549 | 3237.5549 | 3237.5549 | 3237.5549 | 3237.5549 | 3237.5549 | 3237.5549 | 3237.5549 | 3237.5549 | 3237.5549 | 3237.5549 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 59.2112 | 76.6526 | 98.5342 | 126.0259 | 160.6119 | 204.1769 | 259.1149 | 328.4687 | 416.1068 | 526.9507 | 667.2628 | 845.0154 | 1070.3606 | 1356.2304 | 1719.1029 | 2179.9797 | 2765.6346 | 3220.5429 | 3215.0045 | 3207.402 | 3196.919 | 3182.4052 | 3162.2364 | 3134.1161 | 3094.7921 | 3039.6534 | 2962.1545 | 2852.9943 | 2698.9446 | 2481.1755 |  | 1.7644 | 2.1835 | 2.7093 | 3.37 | 4.2011 | 5.2479 | 6.5681 | 8.2347 | 10.3406 | 13.0042 | 16.376 | 20.6474 | 26.0624 | 32.9319 | 41.6518 | 52.7267 | 66.8001 | 77.7989 | 77.7989 | 77.7989 | 77.7989 | 77.7989 | 77.7989 | 77.7989 | 77.7989 | 77.7989 | 77.7989 | 77.7989 | 77.7989 | 77.7989 |  | 0.42692 | 0.42692 | 0.42692 | 0.42692 | 0.42692 | 0.42692 | 0.42692 | 0.42692 | 0.42692 | 0.42692 | 0.42692 | 0.42692 | 0.42692 | 0.42692 | 0.42692 | 0.42692 | 0.42692 | 0.511 | 0.67736 | 0.90572 | 1.2206 | 1.6566 | 2.2624 | 3.1071 | 4.2883 | 5.9445 | 8.2724 | 11.5513 | 16.1786 | 22.7199 |  | 1.3375 | 1.7566 | 2.2824 | 2.943 | 3.7741 | 4.821 | 6.1412 | 7.8078 | 9.9137 | 12.5773 | 15.949 | 20.2204 | 25.6355 | 32.505 | 41.2249 | 52.2998 | 66.3732 | 77.2879 | 77.1215 | 76.8932 | 76.5783 | 76.1423 | 75.5365 | 74.6918 | 73.5106 | 71.8544 | 69.5265 | 66.2476 | 61.6203 | 55.079 |  | 60.5487 | 78.4092 | 100.8166 | 128.9689 | 164.386 | 208.9979 | 265.2561 | 336.2764 | 426.0206 | 539.528 | 683.2118 | 865.2358 | 1095.9961 | 1388.7354 | 1760.3278 | 2232.2795 | 2832.0077 | 3297.8308 | 3292.126 | 3284.2951 | 3273.4973 | 3258.5475 | 3237.7729 | 3208.8079 | 3168.3027 | 3111.5078 | 3031.6809 | 2919.2419 | 2760.5649 | 2536.2545 |  | 60.7228 | 75.1471 | 93.2434 | 115.9794 | 144.5825 | 180.6113 | 226.0458 | 283.4023 | 355.8803 | 447.5497 | 563.5897 | 710.5935 | 896.957 | 1133.3752 | 1433.4757 | 1814.627 | 2298.9715 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 46.0299 | 60.4542 | 78.5506 | 101.2865 | 129.8896 | 165.9185 | 211.353 | 268.7095 | 341.1874 | 432.8568 | 548.8968 | 695.9006 | 882.2641 | 1118.6823 | 1418.7828 | 1799.9341 | 2284.2786 | 2659.9153 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 8.5455 | 10.5755 | 13.1222 | 16.3218 | 20.3471 | 25.4175 | 31.8115 | 39.8833 | 50.0831 | 62.9838 | 79.3141 | 100.002 | 126.229 | 159.5002 | 201.7335 | 255.373 | 323.5349 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 6.4778 | 8.5077 | 11.0544 | 14.2541 | 18.2794 | 23.3498 | 29.7438 | 37.8156 | 48.0154 | 60.9161 | 77.2464 | 97.9343 | 124.1613 | 157.4325 | 199.6657 | 253.3053 | 321.4672 | 374.3307 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 32.8678 | 40.6753 | 50.4704 | 62.7769 | 78.259 | 97.7606 | 122.3532 | 153.3989 | 192.6294 | 242.2479 | 305.0575 | 384.6272 | 485.5012 | 613.4687 | 775.9059 | 982.214 | 1244.378 | 1449.2673 | 1449.2673 | 1449.2673 | 1449.2673 | 1449.2673 | 1449.2673 | 1449.2673 | 1449.2673 | 1449.2673 | 1449.2673 | 1449.2673 | 1449.2673 | 1449.2673 |  | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 9.5191 | 12.6182 | 16.8722 | 22.738 | 30.8592 | 42.1447 | 57.8795 | 79.8834 | 110.7364 | 154.1012 | 215.1821 | 301.3811 | 423.2345 |  | 24.9149 | 32.7224 | 42.5175 | 54.824 | 70.3061 | 89.8077 | 114.4003 | 145.446 | 184.6765 | 234.295 | 297.1046 | 376.6743 | 477.5483 | 605.5158 | 767.953 | 974.2611 | 1236.4251 | 1439.7482 | 1436.6491 | 1432.3951 | 1426.5293 | 1418.4081 | 1407.1226 | 1391.3878 | 1369.3839 | 1338.5309 | 1295.1661 | 1234.0852 | 1147.8862 | 1026.0328 |  | 137.9713 | 180.0935 | 232.9392 | 299.3334 | 382.8611 | 488.0738 | 620.7531 | 788.2474 | 999.8999 | 1267.5959 | 1606.4597 | 2035.745 | 2579.9698 | 3270.3661 | 4146.7293 | 5259.7799 | 6674.1787 | 7771.8249 | 7756.49 | 7735.4397 | 7706.414 | 7666.2276 | 7610.3835 | 7532.5228 | 7423.6411 | 7270.9708 | 7056.3886 | 6754.1417 | 6327.6027 | 5724.6349
| TRUE | 4669 | 22008239 | WBE | WBE022 | 22 | WBE 22 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 6.6 | 0.017308 | 1.3617e-05 | 0.017294 | 47.6003 | 0.9532 | 48.5536 | 49.2077 | 6.925 | 53.2699 |  | 15.598 | 0.17662 | 0.00013896 | 0.17648 | 485.7464 | 9.7271 | 495.4735 | 502.1485 | 70.6675 | 543.6018 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 15.9058 |  | 157.9561 | 1611.8913 | 47.164 | 1564.7274 |  | 0.086007 |  | 7.1928 | 7.8388 | 8.5428 | 9.3101 | 10.1463 | 11.0575 | 12.0507 | 13.133 | 14.3125 | 15.598 | 16.9989 | 18.5257 | 20.1895 | 22.0028 | 23.979 | 26.1326 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021585 | 0.027005 | 0.033883 | 0.042625 | 0.053753 | 0.067937 | 0.086039 | 0.10917 | 0.13875 | 0.17662 | 0.22515 | 0.28739 | 0.36726 | 0.46984 | 0.60168 | 0.7712 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.6983e-05 | 2.1246e-05 | 2.6658e-05 | 3.3536e-05 | 4.2291e-05 | 5.345e-05 | 6.7692e-05 | 8.5889e-05 | 0.00010916 | 0.00013896 | 0.00017714 | 0.0002261 | 0.00028895 | 0.00036966 | 0.00047338 | 0.00060675 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 196.9947 | 246.4542 | 309.2225 | 389.0059 | 490.564 | 620.0131 | 785.2173 | 996.2934 | 1266.2624 | 1611.8913 | 2054.7791 | 2622.7605 | 3351.7187 | 4287.9279 | 5491.0801 | 7038.1967 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 |  | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 56.4523 | 74.8309 | 100.059 | 134.8455 | 183.0079 | 249.9355 | 343.2495 | 473.7414 | 656.7126 | 913.8836 | 1276.1184 | 1787.314 | 2509.9548 |  | 59.3647 | 74.2694 | 93.1847 | 117.2276 | 147.8323 | 186.8421 | 236.6266 | 300.2348 | 381.5905 | 485.7464 | 619.2114 | 790.3736 | 1010.0465 | 1292.1748 | 1654.7469 | 2120.9733 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 45.1518 | 60.0565 | 78.9718 | 103.0147 | 133.6194 | 172.6291 | 222.4137 | 286.0219 | 367.3775 | 471.5334 | 604.9984 | 776.1607 | 995.8335 | 1277.9619 | 1640.5339 | 2106.7603 | 2575.831 | 2573.032 | 2567.4935 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 1.1888 | 1.4873 | 1.866 | 2.3475 | 2.9604 | 3.7415 | 4.7385 | 6.0122 | 7.6414 | 9.7271 | 12.3998 | 15.8273 | 20.2263 | 25.8759 | 33.1365 | 42.4727 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0.90417 | 1.2026 | 1.5814 | 2.0629 | 2.6757 | 3.4569 | 4.4539 | 5.7276 | 7.3568 | 9.4425 | 12.1152 | 15.5427 | 19.9417 | 25.5913 | 32.8519 | 42.1881 | 51.5813 | 51.5252 | 51.4143 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 46.0559 | 61.2591 | 80.5532 | 105.0776 | 136.2951 | 176.086 | 226.8676 | 291.7495 | 374.7343 | 480.9759 | 617.1136 | 791.7034 | 1015.7752 | 1303.5532 | 1673.3858 | 2148.9484 | 2627.4123 | 2624.5572 | 2618.9079 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 61.3693 | 76.7773 | 96.3313 | 121.186 | 152.8242 | 193.1511 | 244.6168 | 310.3728 | 394.4756 | 502.1485 | 640.1202 | 817.0621 | 1044.1526 | 1335.8076 | 1710.6226 | 2192.592 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 46.6764 | 62.0844 | 81.6384 | 106.4932 | 138.1313 | 178.4583 | 229.9239 | 295.6799 | 379.7827 | 487.4556 | 625.4274 | 802.3692 | 1029.4598 | 1321.1147 | 1695.9297 | 2177.8991 | 2662.8089 | 2659.9153 | 2654.1898 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 8.6365 | 10.8049 | 13.5567 | 17.0545 | 21.507 | 27.1822 | 34.425 | 43.6789 | 55.5147 | 70.6675 | 90.0843 | 114.9854 | 146.9439 | 187.9886 | 240.7364 | 308.5641 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 6.5688 | 8.7372 | 11.489 | 14.9868 | 19.4393 | 25.1145 | 32.3573 | 41.6111 | 53.4469 | 68.5998 | 88.0166 | 112.9177 | 144.8762 | 185.9209 | 238.6687 | 306.4964 | 374.7379 | 374.3307 | 373.5249 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 66.4354 | 83.1154 | 104.2836 | 131.1902 | 165.4401 | 209.0961 | 264.8104 | 335.9947 | 427.0403 | 543.6018 | 692.9634 | 884.5121 | 1130.3494 | 1446.081 | 1851.8377 | 2373.5946 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 |  | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 19.0382 | 25.2363 | 33.7444 | 45.4759 | 61.7184 | 84.2894 | 115.7591 | 159.7668 | 221.4729 | 308.2024 | 430.3642 | 602.7622 | 846.469 |  | 50.5296 | 67.2096 | 88.3779 | 115.2844 | 149.5343 | 193.1903 | 248.9046 | 320.0889 | 411.1345 | 527.696 | 677.0576 | 868.6063 | 1114.4436 | 1430.1752 | 1835.9319 | 2357.6888 | 2882.6288 | 2879.4964 | 2873.2983 | 2864.7902 | 2853.0587 | 2836.8162 | 2814.2452 | 2782.7755 | 2738.7678 | 2677.0618 | 2590.3322 | 2468.1704 | 2295.7724 | 2052.0656 |  | 149.8307 | 199.2902 | 262.0585 | 341.8419 | 443.4 | 572.8491 | 738.0533 | 949.1294 | 1219.0985 | 1564.7274 | 2007.6151 | 2575.5965 | 3304.5548 | 4240.764 | 5443.9161 | 6991.0327 | 8547.5879 | 8538.2995 | 8519.921 | 8494.6928 | 8459.9063 | 8411.7439 | 8344.8163 | 8251.5024 | 8121.0105 | 7938.0392 | 7680.8682 | 7318.6334 | 6807.4378 | 6084.797
| FALSE | 4670 | 22015533 | WBE | WBE023 | 22 | WBE 23 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 0.96924 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 15.9058 |  | 5.0708 | 0.0089964 | 7.078e-06 | 0.0089893 | 24.7421 | 0.49546 | 25.2376 | 25.5776 | 3.5995 | 27.689 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 15.9058 |  | 47.164 | 82.1037 | 47.164 | 34.9398 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.7894e-06 | 7.078e-06 | 1.0629e-05 | 1.6185e-05 | 2.4939e-05 | 3.8815e-05 | 6.0929e-05 | 9.6332e-05 | 0.00015323 | 0.00024497 | 0.00039332 | 0.00063378 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 55.5561 | 82.1037 | 123.2986 | 187.7446 | 289.2822 | 450.2446 | 706.763 | 1117.4237 | 1777.4082 | 2841.6073 | 4562.4364 | 7351.7367 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 |  | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 56.4523 | 74.8309 | 100.059 | 134.8455 | 183.0079 | 249.9355 | 343.2495 | 473.7414 | 656.7126 | 913.8836 | 1276.1184 | 1787.314 | 2509.9548 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.7419 | 24.7421 | 37.1563 | 56.5772 | 87.1757 | 135.682 | 212.9843 | 336.7377 | 535.6252 | 856.3235 | 1374.8984 | 2215.4591 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.529 | 10.5292 | 22.9433 | 42.3642 | 72.9628 | 121.4691 | 198.7714 | 322.5247 | 521.4122 | 839.3115 | 1352.348 | 2185.3061 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.33526 | 0.49546 | 0.74406 | 1.133 | 1.7457 | 2.717 | 4.265 | 6.7432 | 10.726 | 17.148 | 27.5325 | 44.3648 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050643 | 0.21085 | 0.45944 | 0.84835 | 1.4611 | 2.4324 | 3.9804 | 6.4586 | 10.4413 | 16.8073 | 27.0809 | 43.761 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5796 | 10.74 | 23.4028 | 43.2126 | 74.4239 | 123.9015 | 202.7518 | 328.9833 | 531.8536 | 856.1188 | 1379.4289 | 2229.0671 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.3072 | 25.5776 | 38.4109 | 58.4876 | 90.1194 | 140.2636 | 220.1761 | 348.1082 | 553.7116 | 885.2389 | 1421.3245 | 2290.2683 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6144 | 10.8847 | 23.7181 | 43.7947 | 75.4265 | 125.5707 | 205.4833 | 333.4154 | 539.0187 | 867.6524 | 1398.0126 | 2259.0972 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5995 | 5.4056 | 8.231 | 12.6825 | 19.7393 | 30.9855 | 48.9894 | 77.924 | 124.5799 | 200.0234 | 322.3101 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6148 | 17.6716 | 28.9177 | 46.9216 | 75.8563 | 122.105 | 196.7427 | 317.9234 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 18.736 | 27.689 | 41.5818 | 63.3159 | 97.5589 | 151.8426 | 238.3521 | 376.8452 | 599.4215 | 958.317 | 1538.6575 | 2479.3343 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 |  | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 19.0382 | 25.2363 | 33.7444 | 45.4759 | 61.7184 | 84.2894 | 115.7591 | 159.7668 | 221.4729 | 308.2024 | 430.3642 | 602.7622 | 846.469 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8302 | 11.7833 | 25.676 | 47.4101 | 81.6531 | 135.9368 | 222.4463 | 360.9395 | 583.5157 | 939.2788 | 1513.4212 | 2445.59 | 2853.0587 | 2836.8162 | 2814.2452 | 2782.7755 | 2738.7678 | 2677.0618 | 2590.3322 | 2468.1704 | 2295.7724 | 2052.0656 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3921 | 34.9398 | 76.1347 | 140.5807 | 242.1183 | 403.0807 | 659.599 | 1070.2598 | 1730.2442 | 2785.155 | 4487.6055 | 7251.6777 | 8459.9063 | 8411.7439 | 8344.8163 | 8251.5024 | 8121.0105 | 7938.0392 | 7680.8682 | 7318.6334 | 6807.4378 | 6084.797
| FALSE | 4671 | 22015534 | WBE | WBE024 | 22 | WBE 24 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 0.96924 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 15.9058 |  | 5.0708 | 0.0089964 | 7.078e-06 | 0.0089893 | 24.7421 | 0.49546 | 25.2376 | 25.5776 | 3.5995 | 27.689 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 15.9058 |  | 47.164 | 82.1037 | 47.164 | 34.9398 |  | 0.16548 |  | 1.1437 | 1.3495 | 1.5923 | 1.8788 | 2.2169 | 2.6159 | 3.0866 | 3.6421 | 4.2975 | 5.0708 | 5.9833 | 7.0601 | 8.3306 | 9.8297 | 11.5986 | 13.6858 | 16.1486 | 19.0546 | 22.4835 | 26.5295 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0060875 | 0.0089964 | 0.01351 | 0.020572 | 0.031698 | 0.049335 | 0.077443 | 0.12244 | 0.19476 | 0.31137 | 0.49992 | 0.80556 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.0659e-06 | 4.7894e-06 | 7.078e-06 | 1.0629e-05 | 1.6185e-05 | 2.4939e-05 | 3.8815e-05 | 6.0929e-05 | 9.6332e-05 | 0.00015323 | 0.00024497 | 0.00039332 | 0.00063378 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 55.5561 | 82.1037 | 123.2986 | 187.7446 | 289.2822 | 450.2446 | 706.763 | 1117.4237 | 1777.4082 | 2841.6073 | 4562.4364 | 7351.7367 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 | 8594.7518 |  | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 47.164 | 56.4523 | 74.8309 | 100.059 | 134.8455 | 183.0079 | 249.9355 | 343.2495 | 473.7414 | 656.7126 | 913.8836 | 1276.1184 | 1787.314 | 2509.9548 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 16.7419 | 24.7421 | 37.1563 | 56.5772 | 87.1757 | 135.682 | 212.9843 | 336.7377 | 535.6252 | 856.3235 | 1374.8984 | 2215.4591 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.529 | 10.5292 | 22.9433 | 42.3642 | 72.9628 | 121.4691 | 198.7714 | 322.5247 | 521.4122 | 839.3115 | 1352.348 | 2185.3061 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.33526 | 0.49546 | 0.74406 | 1.133 | 1.7457 | 2.717 | 4.265 | 6.7432 | 10.726 | 17.148 | 27.5325 | 44.3648 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050643 | 0.21085 | 0.45944 | 0.84835 | 1.4611 | 2.4324 | 3.9804 | 6.4586 | 10.4413 | 16.8073 | 27.0809 | 43.761 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5796 | 10.74 | 23.4028 | 43.2126 | 74.4239 | 123.9015 | 202.7518 | 328.9833 | 531.8536 | 856.1188 | 1379.4289 | 2229.0671 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.3072 | 25.5776 | 38.4109 | 58.4876 | 90.1194 | 140.2636 | 220.1761 | 348.1082 | 553.7116 | 885.2389 | 1421.3245 | 2290.2683 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6144 | 10.8847 | 23.7181 | 43.7947 | 75.4265 | 125.5707 | 205.4833 | 333.4154 | 539.0187 | 867.6524 | 1398.0126 | 2259.0972 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4357 | 3.5995 | 5.4056 | 8.231 | 12.6825 | 19.7393 | 30.9855 | 48.9894 | 77.924 | 124.5799 | 200.0234 | 322.3101 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36792 | 1.5318 | 3.3378 | 6.1632 | 10.6148 | 17.6716 | 28.9177 | 46.9216 | 75.8563 | 122.105 | 196.7427 | 317.9234 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 18.736 | 27.689 | 41.5818 | 63.3159 | 97.5589 | 151.8426 | 238.3521 | 376.8452 | 599.4215 | 958.317 | 1538.6575 | 2479.3343 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 | 2898.5346 |  | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 15.9058 | 19.0382 | 25.2363 | 33.7444 | 45.4759 | 61.7184 | 84.2894 | 115.7591 | 159.7668 | 221.4729 | 308.2024 | 430.3642 | 602.7622 | 846.469 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8302 | 11.7833 | 25.676 | 47.4101 | 81.6531 | 135.9368 | 222.4463 | 360.9395 | 583.5157 | 939.2788 | 1513.4212 | 2445.59 | 2853.0587 | 2836.8162 | 2814.2452 | 2782.7755 | 2738.7678 | 2677.0618 | 2590.3322 | 2468.1704 | 2295.7724 | 2052.0656 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3921 | 34.9398 | 76.1347 | 140.5807 | 242.1183 | 403.0807 | 659.599 | 1070.2598 | 1730.2442 | 2785.155 | 4487.6055 | 7251.6777 | 8459.9063 | 8411.7439 | 8344.8163 | 8251.5024 | 8121.0105 | 7938.0392 | 7680.8682 | 7318.6334 | 6807.4378 | 6084.797
| FALSE | 4672 | 22010041 | WBE | WBE031 | 22 | WBE 31 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 2.8514 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 7.6055 |  | 9.4101 | 0.043865 | 3.4512e-05 | 0.043831 | 120.6389 | 2.4158 | 123.0547 | 124.7125 | 17.5508 | 64.5551 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 7.6055 |  | 38.8637 | 329.8732 | 38.8637 | 291.0096 |  | 0.1194 |  | 3.213 | 3.6205 | 4.0796 | 4.597 | 5.1799 | 5.8369 | 6.5771 | 7.4112 | 8.351 | 9.4101 | 10.6034 | 11.9482 | 13.4634 | 15.1708 | 17.0947 | 19.2626 | 21.7055 | 24.4581 | 27.5598 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0054038 | 0.0071219 | 0.0094715 | 0.0127 | 0.017155 | 0.023326 | 0.031904 | 0.043865 | 0.060591 | 0.084037 | 0.11698 | 0.16335 | 0.22876 | 0.32115 | 0.45186 | 0.63698 | 0.8995 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.2515e-06 | 5.6032e-06 | 7.4518e-06 | 9.9919e-06 | 1.3497e-05 | 1.8352e-05 | 2.5101e-05 | 3.4512e-05 | 4.767e-05 | 6.6117e-05 | 9.2034e-05 | 0.00012852 | 0.00017998 | 0.00025267 | 0.0003555 | 0.00050116 | 0.00070769 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 38.8637 | 38.8637 | 40.6374 | 53.5574 | 71.2273 | 95.5063 | 129.0085 | 175.4161 | 239.9241 | 329.8732 | 455.65 | 631.9682 | 879.6943 | 1228.4489 | 1720.3152 | 2415.1292 | 3398.0271 | 4790.2169 | 6764.3563 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 |  | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 46.5174 | 61.6615 | 82.4498 | 111.1143 | 150.8006 | 205.9498 | 282.8416 | 390.3685 | 541.1389 | 753.0509 | 1051.5366 | 1472.7678 | 2068.2323 |  | 14.2129 | 14.2129 | 14.8616 | 19.5866 | 26.0487 | 34.9279 | 47.1801 | 64.152 | 87.7434 | 120.6389 | 166.6371 | 231.119 | 321.7156 | 449.2597 | 629.1416 | 883.2441 | 1242.7026 | 1751.8445 | 2473.8129 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0.64867 | 5.3737 | 11.8358 | 20.7149 | 32.9672 | 49.939 | 73.5304 | 106.426 | 152.4242 | 216.906 | 307.5027 | 435.0468 | 614.9286 | 869.0312 | 1228.4897 | 1734.8325 | 2451.2625 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.29761 | 0.39222 | 0.52163 | 0.69943 | 0.94479 | 1.2846 | 1.7571 | 2.4158 | 3.3369 | 4.6282 | 6.4424 | 8.9965 | 12.5986 | 17.6871 | 24.8853 | 35.0809 | 49.5384 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0.01299 | 0.10761 | 0.23701 | 0.41482 | 0.66017 | 1 | 1.4725 | 2.1312 | 3.0523 | 4.3436 | 6.1578 | 8.7119 | 12.314 | 17.4024 | 24.6006 | 34.7402 | 49.0868 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0.66166 | 5.4813 | 12.0728 | 21.1298 | 33.6273 | 50.939 | 75.0029 | 108.5572 | 155.4765 | 221.2496 | 313.6605 | 443.7586 | 627.2427 | 886.4336 | 1253.0903 | 1769.5727 | 2500.3493 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 15.3634 | 20.248 | 26.9283 | 36.1073 | 48.7732 | 66.3182 | 90.7062 | 124.7125 | 172.2639 | 238.9231 | 332.579 | 464.4298 | 650.3857 | 913.0685 | 1284.6648 | 1810.9989 | 2557.3459 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0.67057 | 5.5552 | 12.2355 | 21.4144 | 34.0804 | 51.6253 | 76.0133 | 110.0197 | 157.5711 | 224.2303 | 317.8861 | 449.7369 | 635.6929 | 898.3757 | 1269.972 | 1793.4124 | 2534.034 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.1621 | 2.8495 | 3.7896 | 5.0814 | 6.8639 | 9.333 | 12.7651 | 17.5508 | 24.2428 | 33.6237 | 46.8039 | 65.3593 | 91.529 | 128.4964 | 180.7913 | 254.8624 | 359.896 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0.09437 | 0.78178 | 1.7219 | 3.0137 | 4.7961 | 7.2652 | 10.6974 | 15.4831 | 22.175 | 31.556 | 44.7362 | 63.2916 | 89.4612 | 126.4287 | 178.7235 | 252.3875 | 356.6154 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 7.6055 | 7.6055 | 7.9526 | 10.481 | 13.939 | 18.6903 | 25.2466 | 34.3284 | 46.9524 | 64.5551 | 89.1693 | 123.6742 | 172.1534 | 240.4036 | 336.6602 | 472.6331 | 664.9832 | 937.4303 | 1323.7631 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 |  | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 9.1033 | 12.067 | 16.1352 | 21.7447 | 29.5112 | 40.3037 | 55.3512 | 76.3939 | 105.8992 | 147.3697 | 205.7824 | 288.216 | 404.7465 |  | 0 | 0 | 0.34711 | 2.8755 | 6.3335 | 11.0848 | 17.6411 | 26.7229 | 39.3469 | 56.9497 | 81.5638 | 116.0687 | 164.5479 | 232.7981 | 329.0547 | 465.0276 | 657.3777 | 928.327 | 1311.6961 | 1369.8244 | 1364.2149 | 1356.4484 | 1345.6558 | 1330.6084 | 1309.5657 | 1280.0604 | 1238.5899 | 1180.1772 | 1097.7436 | 981.2131 |  | 0 | 0 | 1.7737 | 14.6938 | 32.3636 | 56.6426 | 90.1449 | 136.5525 | 201.0605 | 291.0096 | 416.7863 | 593.1045 | 840.8307 | 1189.5852 | 1681.4515 | 2376.2656 | 3359.1635 | 4743.6996 | 6702.6948 | 6999.727 | 6971.0625 | 6931.3761 | 6876.2269 | 6799.3352 | 6691.8083 | 6541.0378 | 6329.1259 | 6030.6401 | 5609.409 | 5013.9445
| FALSE | 4673 | 22009843 | WBE | WBE032 | 22 | WBE 32 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 2.8514 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 7.6055 |  | 9.4101 | 0.043865 | 3.4512e-05 | 0.043831 | 120.6389 | 2.4158 | 123.0547 | 124.7125 | 17.5508 | 64.5551 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 7.6055 |  | 38.8637 | 329.8732 | 38.8637 | 291.0096 |  | 0.1194 |  | 3.213 | 3.6205 | 4.0796 | 4.597 | 5.1799 | 5.8369 | 6.5771 | 7.4112 | 8.351 | 9.4101 | 10.6034 | 11.9482 | 13.4634 | 15.1708 | 17.0947 | 19.2626 | 21.7055 | 24.4581 | 27.5598 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0054038 | 0.0071219 | 0.0094715 | 0.0127 | 0.017155 | 0.023326 | 0.031904 | 0.043865 | 0.060591 | 0.084037 | 0.11698 | 0.16335 | 0.22876 | 0.32115 | 0.45186 | 0.63698 | 0.8995 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.2515e-06 | 5.6032e-06 | 7.4518e-06 | 9.9919e-06 | 1.3497e-05 | 1.8352e-05 | 2.5101e-05 | 3.4512e-05 | 4.767e-05 | 6.6117e-05 | 9.2034e-05 | 0.00012852 | 0.00017998 | 0.00025267 | 0.0003555 | 0.00050116 | 0.00070769 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 38.8637 | 38.8637 | 40.6374 | 53.5574 | 71.2273 | 95.5063 | 129.0085 | 175.4161 | 239.9241 | 329.8732 | 455.65 | 631.9682 | 879.6943 | 1228.4489 | 1720.3152 | 2415.1292 | 3398.0271 | 4790.2169 | 6764.3563 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 |  | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 46.5174 | 61.6615 | 82.4498 | 111.1143 | 150.8006 | 205.9498 | 282.8416 | 390.3685 | 541.1389 | 753.0509 | 1051.5366 | 1472.7678 | 2068.2323 |  | 14.2129 | 14.2129 | 14.8616 | 19.5866 | 26.0487 | 34.9279 | 47.1801 | 64.152 | 87.7434 | 120.6389 | 166.6371 | 231.119 | 321.7156 | 449.2597 | 629.1416 | 883.2441 | 1242.7026 | 1751.8445 | 2473.8129 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0.64867 | 5.3737 | 11.8358 | 20.7149 | 32.9672 | 49.939 | 73.5304 | 106.426 | 152.4242 | 216.906 | 307.5027 | 435.0468 | 614.9286 | 869.0312 | 1228.4897 | 1734.8325 | 2451.2625 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.29761 | 0.39222 | 0.52163 | 0.69943 | 0.94479 | 1.2846 | 1.7571 | 2.4158 | 3.3369 | 4.6282 | 6.4424 | 8.9965 | 12.5986 | 17.6871 | 24.8853 | 35.0809 | 49.5384 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0.01299 | 0.10761 | 0.23701 | 0.41482 | 0.66017 | 1 | 1.4725 | 2.1312 | 3.0523 | 4.3436 | 6.1578 | 8.7119 | 12.314 | 17.4024 | 24.6006 | 34.7402 | 49.0868 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0.66166 | 5.4813 | 12.0728 | 21.1298 | 33.6273 | 50.939 | 75.0029 | 108.5572 | 155.4765 | 221.2496 | 313.6605 | 443.7586 | 627.2427 | 886.4336 | 1253.0903 | 1769.5727 | 2500.3493 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 15.3634 | 20.248 | 26.9283 | 36.1073 | 48.7732 | 66.3182 | 90.7062 | 124.7125 | 172.2639 | 238.9231 | 332.579 | 464.4298 | 650.3857 | 913.0685 | 1284.6648 | 1810.9989 | 2557.3459 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0.67057 | 5.5552 | 12.2355 | 21.4144 | 34.0804 | 51.6253 | 76.0133 | 110.0197 | 157.5711 | 224.2303 | 317.8861 | 449.7369 | 635.6929 | 898.3757 | 1269.972 | 1793.4124 | 2534.034 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.1621 | 2.8495 | 3.7896 | 5.0814 | 6.8639 | 9.333 | 12.7651 | 17.5508 | 24.2428 | 33.6237 | 46.8039 | 65.3593 | 91.529 | 128.4964 | 180.7913 | 254.8624 | 359.896 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0.09437 | 0.78178 | 1.7219 | 3.0137 | 4.7961 | 7.2652 | 10.6974 | 15.4831 | 22.175 | 31.556 | 44.7362 | 63.2916 | 89.4612 | 126.4287 | 178.7235 | 252.3875 | 356.6154 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 7.6055 | 7.6055 | 7.9526 | 10.481 | 13.939 | 18.6903 | 25.2466 | 34.3284 | 46.9524 | 64.5551 | 89.1693 | 123.6742 | 172.1534 | 240.4036 | 336.6602 | 472.6331 | 664.9832 | 937.4303 | 1323.7631 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 |  | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 9.1033 | 12.067 | 16.1352 | 21.7447 | 29.5112 | 40.3037 | 55.3512 | 76.3939 | 105.8992 | 147.3697 | 205.7824 | 288.216 | 404.7465 |  | 0 | 0 | 0.34711 | 2.8755 | 6.3335 | 11.0848 | 17.6411 | 26.7229 | 39.3469 | 56.9497 | 81.5638 | 116.0687 | 164.5479 | 232.7981 | 329.0547 | 465.0276 | 657.3777 | 928.327 | 1311.6961 | 1369.8244 | 1364.2149 | 1356.4484 | 1345.6558 | 1330.6084 | 1309.5657 | 1280.0604 | 1238.5899 | 1180.1772 | 1097.7436 | 981.2131 |  | 0 | 0 | 1.7737 | 14.6938 | 32.3636 | 56.6426 | 90.1449 | 136.5525 | 201.0605 | 291.0096 | 416.7863 | 593.1045 | 840.8307 | 1189.5852 | 1681.4515 | 2376.2656 | 3359.1635 | 4743.6996 | 6702.6948 | 6999.727 | 6971.0625 | 6931.3761 | 6876.2269 | 6799.3352 | 6691.8083 | 6541.0378 | 6329.1259 | 6030.6401 | 5609.409 | 5013.9445
| FALSE | 4674 | 22009844 | WBE | WBE033 | 22 | WBE 33 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 2.8514 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 15.211 |  | 9.4101 | 0.043865 | 3.4512e-05 | 0.043831 | 120.6389 | 2.4158 | 123.0547 | 124.7125 | 17.5508 | 129.1103 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 15.211 |  | 46.4691 | 394.4284 | 46.4691 | 347.9592 |  | 0.1194 |  | 3.213 | 3.6205 | 4.0796 | 4.597 | 5.1799 | 5.8369 | 6.5771 | 7.4112 | 8.351 | 9.4101 | 10.6034 | 11.9482 | 13.4634 | 15.1708 | 17.0947 | 19.2626 | 21.7055 | 24.4581 | 27.5598 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0054038 | 0.0071219 | 0.0094715 | 0.0127 | 0.017155 | 0.023326 | 0.031904 | 0.043865 | 0.060591 | 0.084037 | 0.11698 | 0.16335 | 0.22876 | 0.32115 | 0.45186 | 0.63698 | 0.8995 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.2515e-06 | 5.6032e-06 | 7.4518e-06 | 9.9919e-06 | 1.3497e-05 | 1.8352e-05 | 2.5101e-05 | 3.4512e-05 | 4.767e-05 | 6.6117e-05 | 9.2034e-05 | 0.00012852 | 0.00017998 | 0.00025267 | 0.0003555 | 0.00050116 | 0.00070769 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 46.4691 | 46.4691 | 48.59 | 64.0384 | 85.1662 | 114.1966 | 154.2551 | 209.7445 | 286.8765 | 394.4284 | 544.8192 | 755.6424 | 1051.8477 | 1468.8524 | 2056.9754 | 2887.7624 | 4063.0103 | 5727.6472 | 8088.1194 | 8468.1363 | 8468.1363 | 8468.1363 | 8468.1363 | 8468.1363 | 8468.1363 | 8468.1363 | 8468.1363 | 8468.1363 | 8468.1363 | 8468.1363 |  | 46.4691 | 46.4691 | 46.4691 | 46.4691 | 46.4691 | 46.4691 | 46.4691 | 46.4691 | 46.4691 | 46.4691 | 46.4691 | 46.4691 | 46.4691 | 46.4691 | 46.4691 | 46.4691 | 46.4691 | 55.6207 | 73.7285 | 98.585 | 132.859 | 180.3118 | 246.2536 | 338.1928 | 466.7623 | 647.0381 | 900.4206 | 1257.319 | 1760.9838 | 2472.9788 |  | 14.2129 | 14.2129 | 14.8616 | 19.5866 | 26.0487 | 34.9279 | 47.1801 | 64.152 | 87.7434 | 120.6389 | 166.6371 | 231.119 | 321.7156 | 449.2597 | 629.1416 | 883.2441 | 1242.7026 | 1751.8445 | 2473.8129 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0.64867 | 5.3737 | 11.8358 | 20.7149 | 32.9672 | 49.939 | 73.5304 | 106.426 | 152.4242 | 216.906 | 307.5027 | 435.0468 | 614.9286 | 869.0312 | 1228.4897 | 1734.8325 | 2451.2625 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.29761 | 0.39222 | 0.52163 | 0.69943 | 0.94479 | 1.2846 | 1.7571 | 2.4158 | 3.3369 | 4.6282 | 6.4424 | 8.9965 | 12.5986 | 17.6871 | 24.8853 | 35.0809 | 49.5384 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0.01299 | 0.10761 | 0.23701 | 0.41482 | 0.66017 | 1 | 1.4725 | 2.1312 | 3.0523 | 4.3436 | 6.1578 | 8.7119 | 12.314 | 17.4024 | 24.6006 | 34.7402 | 49.0868 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0.66166 | 5.4813 | 12.0728 | 21.1298 | 33.6273 | 50.939 | 75.0029 | 108.5572 | 155.4765 | 221.2496 | 313.6605 | 443.7586 | 627.2427 | 886.4336 | 1253.0903 | 1769.5727 | 2500.3493 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 15.3634 | 20.248 | 26.9283 | 36.1073 | 48.7732 | 66.3182 | 90.7062 | 124.7125 | 172.2639 | 238.9231 | 332.579 | 464.4298 | 650.3857 | 913.0685 | 1284.6648 | 1810.9989 | 2557.3459 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0.67057 | 5.5552 | 12.2355 | 21.4144 | 34.0804 | 51.6253 | 76.0133 | 110.0197 | 157.5711 | 224.2303 | 317.8861 | 449.7369 | 635.6929 | 898.3757 | 1269.972 | 1793.4124 | 2534.034 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.1621 | 2.8495 | 3.7896 | 5.0814 | 6.8639 | 9.333 | 12.7651 | 17.5508 | 24.2428 | 33.6237 | 46.8039 | 65.3593 | 91.529 | 128.4964 | 180.7913 | 254.8624 | 359.896 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0.09437 | 0.78178 | 1.7219 | 3.0137 | 4.7961 | 7.2652 | 10.6974 | 15.4831 | 22.175 | 31.556 | 44.7362 | 63.2916 | 89.4612 | 126.4287 | 178.7235 | 252.3875 | 356.6154 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 15.211 | 15.211 | 15.9052 | 20.962 | 27.8779 | 37.3806 | 50.4931 | 68.6568 | 93.9048 | 129.1103 | 178.3385 | 247.3483 | 344.3068 | 480.8071 | 673.3205 | 945.2663 | 1329.9663 | 1874.8606 | 2647.5262 | 2771.9191 | 2771.9191 | 2771.9191 | 2771.9191 | 2771.9191 | 2771.9191 | 2771.9191 | 2771.9191 | 2771.9191 | 2771.9191 | 2771.9191 |  | 15.211 | 15.211 | 15.211 | 15.211 | 15.211 | 15.211 | 15.211 | 15.211 | 15.211 | 15.211 | 15.211 | 15.211 | 15.211 | 15.211 | 15.211 | 15.211 | 15.211 | 18.2066 | 24.1339 | 32.2703 | 43.4894 | 59.0224 | 80.6075 | 110.7024 | 152.7877 | 211.7983 | 294.7393 | 411.5648 | 576.432 | 809.493 |  | 0 | 0 | 0.69422 | 5.751 | 12.6669 | 22.1696 | 35.2821 | 53.4458 | 78.6938 | 113.8993 | 163.1275 | 232.1374 | 329.0958 | 465.5961 | 658.1095 | 930.0553 | 1314.7553 | 1856.654 | 2623.3923 | 2739.6488 | 2728.4297 | 2712.8967 | 2691.3117 | 2661.2167 | 2619.1314 | 2560.1208 | 2477.1798 | 2360.3544 | 2195.4871 | 1962.4261 |  | 0 | 0 | 2.1208 | 17.5693 | 38.6971 | 67.7274 | 107.7859 | 163.2754 | 240.4074 | 347.9592 | 498.3501 | 709.1732 | 1005.3786 | 1422.3833 | 2010.5063 | 2841.2932 | 4016.5412 | 5672.0266 | 8014.3909 | 8369.5514 | 8335.2773 | 8287.8245 | 8221.8828 | 8129.9435 | 8001.374 | 7821.0982 | 7567.7158 | 7210.8173 | 6707.1526 | 5995.1575
| FALSE | 4675 | 22009845 | WBE | WBE034 | 22 | WBE 34 | FEEDER MANAGEMENT | X | Schweitzer | SEL_351S | SEL 351 | SEL 300s | Digital |  | 0.57434 | 1 |  | 2.8514 | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 7.6055 |  | 9.4101 | 0.043865 | 3.4512e-05 | 0.043831 | 120.6389 | 2.4158 | 123.0547 | 124.7125 | 17.5508 | 64.5551 |  | 0.0051679 | 4.0659e-06 | 0.0051639 | 14.2129 | 0.28462 | 14.4976 | 14.6929 | 2.0677 | 7.6055 |  | 38.8637 | 329.8732 | 38.8637 | 291.0096 |  | 0.1194 |  | 3.213 | 3.6205 | 4.0796 | 4.597 | 5.1799 | 5.8369 | 6.5771 | 7.4112 | 8.351 | 9.4101 | 10.6034 | 11.9482 | 13.4634 | 15.1708 | 17.0947 | 19.2626 | 21.7055 | 24.4581 | 27.5598 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0054038 | 0.0071219 | 0.0094715 | 0.0127 | 0.017155 | 0.023326 | 0.031904 | 0.043865 | 0.060591 | 0.084037 | 0.11698 | 0.16335 | 0.22876 | 0.32115 | 0.45186 | 0.63698 | 0.8995 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.0659e-06 | 4.0659e-06 | 4.2515e-06 | 5.6032e-06 | 7.4518e-06 | 9.9919e-06 | 1.3497e-05 | 1.8352e-05 | 2.5101e-05 | 3.4512e-05 | 4.767e-05 | 6.6117e-05 | 9.2034e-05 | 0.00012852 | 0.00017998 | 0.00025267 | 0.0003555 | 0.00050116 | 0.00070769 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 0.00074094 | 38.8637 | 38.8637 | 40.6374 | 53.5574 | 71.2273 | 95.5063 | 129.0085 | 175.4161 | 239.9241 | 329.8732 | 455.65 | 631.9682 | 879.6943 | 1228.4489 | 1720.3152 | 2415.1292 | 3398.0271 | 4790.2169 | 6764.3563 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 | 7082.1768 |  | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 38.8637 | 46.5174 | 61.6615 | 82.4498 | 111.1143 | 150.8006 | 205.9498 | 282.8416 | 390.3685 | 541.1389 | 753.0509 | 1051.5366 | 1472.7678 | 2068.2323 |  | 14.2129 | 14.2129 | 14.8616 | 19.5866 | 26.0487 | 34.9279 | 47.1801 | 64.152 | 87.7434 | 120.6389 | 166.6371 | 231.119 | 321.7156 | 449.2597 | 629.1416 | 883.2441 | 1242.7026 | 1751.8445 | 2473.8129 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 | 2590.044 |  | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 14.2129 | 17.012 | 22.5504 | 30.153 | 40.6359 | 55.1498 | 75.3185 | 103.4388 | 142.7628 | 197.9015 | 275.4005 | 384.5606 | 538.6103 | 756.3794 |  | 0 | 0 | 0.64867 | 5.3737 | 11.8358 | 20.7149 | 32.9672 | 49.939 | 73.5304 | 106.426 | 152.4242 | 216.906 | 307.5027 | 435.0468 | 614.9286 | 869.0312 | 1228.4897 | 1734.8325 | 2451.2625 | 2559.891 | 2549.408 | 2534.8942 | 2514.7254 | 2486.6051 | 2447.2811 | 2392.1424 | 2314.6435 | 2205.4834 | 2051.4337 | 1833.6646 |  | 0.28462 | 0.28462 | 0.29761 | 0.39222 | 0.52163 | 0.69943 | 0.94479 | 1.2846 | 1.7571 | 2.4158 | 3.3369 | 4.6282 | 6.4424 | 8.9965 | 12.5986 | 17.6871 | 24.8853 | 35.0809 | 49.5384 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 | 51.8659 |  | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.28462 | 0.34067 | 0.45157 | 0.60382 | 0.81374 | 1.1044 | 1.5083 | 2.0714 | 2.8588 | 3.963 | 5.5149 | 7.7009 | 10.7857 | 15.1466 |  | 0 | 0 | 0.01299 | 0.10761 | 0.23701 | 0.41482 | 0.66017 | 1 | 1.4725 | 2.1312 | 3.0523 | 4.3436 | 6.1578 | 8.7119 | 12.314 | 17.4024 | 24.6006 | 34.7402 | 49.0868 | 51.2621 | 51.0522 | 50.7615 | 50.3577 | 49.7945 | 49.0071 | 47.9029 | 46.351 | 44.165 | 41.0802 | 36.7193 |  | 0 | 0 | 0.66166 | 5.4813 | 12.0728 | 21.1298 | 33.6273 | 50.939 | 75.0029 | 108.5572 | 155.4765 | 221.2496 | 313.6605 | 443.7586 | 627.2427 | 886.4336 | 1253.0903 | 1769.5727 | 2500.3493 | 2611.1531 | 2600.4602 | 2585.6557 | 2565.0831 | 2536.3997 | 2496.2882 | 2440.0453 | 2360.9945 | 2249.6484 | 2092.5138 | 1870.3839 |  | 14.6929 | 14.6929 | 15.3634 | 20.248 | 26.9283 | 36.1073 | 48.7732 | 66.3182 | 90.7062 | 124.7125 | 172.2639 | 238.9231 | 332.579 | 464.4298 | 650.3857 | 913.0685 | 1284.6648 | 1810.9989 | 2557.3459 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 | 2677.5017 |  | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 14.6929 | 17.5864 | 23.3119 | 31.1711 | 42.0081 | 57.012 | 77.8618 | 106.9317 | 147.5835 | 204.584 | 284.6999 | 397.546 | 556.7975 | 781.92 |  | 0 | 0 | 0.67057 | 5.5552 | 12.2355 | 21.4144 | 34.0804 | 51.6253 | 76.0133 | 110.0197 | 157.5711 | 224.2303 | 317.8861 | 449.7369 | 635.6929 | 898.3757 | 1269.972 | 1793.4124 | 2534.034 | 2646.3306 | 2635.4936 | 2620.4897 | 2599.6399 | 2570.5701 | 2529.9183 | 2472.9177 | 2392.8018 | 2279.9557 | 2120.7042 | 1895.5817 |  | 2.0677 | 2.0677 | 2.1621 | 2.8495 | 3.7896 | 5.0814 | 6.8639 | 9.333 | 12.7651 | 17.5508 | 24.2428 | 33.6237 | 46.8039 | 65.3593 | 91.529 | 128.4964 | 180.7913 | 254.8624 | 359.896 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 | 376.8056 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2807 | 4.3867 | 5.9118 | 8.0233 | 10.9575 | 15.0485 | 20.7695 | 28.7912 | 40.0659 | 55.9468 | 78.3583 | 110.0398 |  | 0 | 0 | 0.09437 | 0.78178 | 1.7219 | 3.0137 | 4.7961 | 7.2652 | 10.6974 | 15.4831 | 22.175 | 31.556 | 44.7362 | 63.2916 | 89.4612 | 126.4287 | 178.7235 | 252.3875 | 356.6154 | 372.4189 | 370.8938 | 368.7823 | 365.8481 | 361.7571 | 356.0361 | 348.0144 | 336.7397 | 320.8588 | 298.4473 | 266.7658 |  | 7.6055 | 7.6055 | 7.9526 | 10.481 | 13.939 | 18.6903 | 25.2466 | 34.3284 | 46.9524 | 64.5551 | 89.1693 | 123.6742 | 172.1534 | 240.4036 | 336.6602 | 472.6331 | 664.9832 | 937.4303 | 1323.7631 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 | 1385.9596 |  | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 7.6055 | 9.1033 | 12.067 | 16.1352 | 21.7447 | 29.5112 | 40.3037 | 55.3512 | 76.3939 | 105.8992 | 147.3697 | 205.7824 | 288.216 | 404.7465 |  | 0 | 0 | 0.34711 | 2.8755 | 6.3335 | 11.0848 | 17.6411 | 26.7229 | 39.3469 | 56.9497 | 81.5638 | 116.0687 | 164.5479 | 232.7981 | 329.0547 | 465.0276 | 657.3777 | 928.327 | 1311.6961 | 1369.8244 | 1364.2149 | 1356.4484 | 1345.6558 | 1330.6084 | 1309.5657 | 1280.0604 | 1238.5899 | 1180.1772 | 1097.7436 | 981.2131 |  | 0 | 0 | 1.7737 | 14.6938 | 32.3636 | 56.6426 | 90.1449 | 136.5525 | 201.0605 | 291.0096 | 416.7863 | 593.1045 | 840.8307 | 1189.5852 | 1681.4515 | 2376.2656 | 3359.1635 | 4743.6996 | 6702.6948 | 6999.727 | 6971.0625 | 6931.3761 | 6876.2269 | 6799.3352 | 6691.8083 | 6541.0378 | 6329.1259 | 6030.6401 | 5609.409 | 5013.9445
| TRUE | 4676 | 22004395 | WBE | Blank | 22 | STN STN | BATTERY UV & BUS NV | Blank | EMAIL | GROUP_3062 | GROUP 3062 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 235.3564 | 0 | 235.3564 | 121.4703 | 17.1211 | 0 |  | 20.1542 | 0.31092 | 0 | 0.31092 | 1710.0365 | 0 | 1710.0365 | 882.5704 | 124.3974 | 0 |  | 0.0051679 | 0 | 0.0051679 | 28.4236 | 0 | 28.4236 | 14.6698 | 2.0677 | 0 |  | 373.9478 | 2717.0043 | 45.1611 | 2671.8431 |  | 0.071088 |  | 10.6294 | 11.4125 | 12.2533 | 13.1561 | 14.1254 | 15.1661 | 16.2834 | 17.4831 | 18.7712 | 20.1542 | 21.639 | 23.2333 | 24.945 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.051896 | 0.063029 | 0.076653 | 0.093338 | 0.11379 | 0.13887 | 0.16964 | 0.20743 | 0.25385 | 0.31092 | 0.38109 | 0.46742 | 0.57368 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.5085 | 550.7932 | 669.8476 | 815.6541 | 994.3516 | 1213.5054 | 1482.442 | 1812.6618 | 2218.3493 | 2717.0043 | 3330.2204 | 4084.6492 | 5013.1908 | 6156.4658 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 | 7002.1404 |  | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 |  | 285.4306 | 346.6599 | 421.5907 | 513.3589 | 625.8281 | 763.7598 | 933.0239 | 1140.8586 | 1396.1915 | 1710.0365 | 2095.9844 | 2570.8091 | 3155.2174 | 3874.7754 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 | 4407.0287 |  | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 |  | 271.2187 | 332.4481 | 407.3789 | 499.1471 | 611.6162 | 749.548 | 918.8121 | 1126.6468 | 1381.9797 | 1695.8247 | 2081.7725 | 2556.5973 | 3141.0056 | 3860.5636 | 4392.8169 | 4392.8169 | 4392.8169 | 4390.018 | 4384.48 | 4376.8781 | 4366.3959 | 4351.8833 | 4331.7161 | 4303.598 | 4264.2771 | 4209.1427 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 271.2187 | 332.4481 | 407.3789 | 499.1471 | 611.6162 | 749.548 | 918.8121 | 1126.6468 | 1381.9797 | 1695.8247 | 2081.7725 | 2556.5973 | 3141.0056 | 3860.5636 | 4392.8169 | 4392.8169 | 4392.8169 | 4390.018 | 4384.48 | 4376.8781 | 4366.3959 | 4351.8833 | 4331.7161 | 4303.598 | 4264.2771 | 4209.1427 | 4131.6499 | 4022.4983 | 3868.4608 | 3650.7088 |  | 147.3141 | 178.9154 | 217.588 | 264.9507 | 322.9974 | 394.1856 | 481.5448 | 588.8108 | 720.5912 | 882.5704 | 1081.7627 | 1326.8254 | 1628.4456 | 1999.8181 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 132.6444 | 164.2456 | 202.9183 | 250.2809 | 308.3276 | 379.5158 | 466.8751 | 574.1411 | 705.9214 | 867.9006 | 1067.0929 | 1312.1557 | 1613.7758 | 1985.1483 | 2259.8506 | 2259.8506 | 2259.8506 | 2256.9616 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 20.7638 | 25.2179 | 30.6688 | 37.3445 | 45.5261 | 55.5601 | 67.8732 | 82.9923 | 101.5666 | 124.3974 | 152.4733 | 187.0147 | 229.5277 | 281.8723 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 18.6961 | 23.1502 | 28.6011 | 35.2768 | 43.4585 | 53.4924 | 65.8056 | 80.9246 | 99.4989 | 122.3297 | 150.4056 | 184.947 | 227.46 | 279.8046 | 318.5236 | 318.5236 | 318.5236 | 318.1164 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 422.5592 | 519.8439 | 638.8983 | 784.7048 | 963.4023 | 1182.5561 | 1451.4927 | 1781.7125 | 2187.4 | 2686.055 | 3299.2711 | 4053.6999 | 4982.2415 | 6125.5165 | 6971.1911 | 6971.1911 | 6971.1911 | 6965.096 | 6953.0359 | 6936.481 | 6913.6539 | 6882.0494 | 6838.131 | 6776.8978 | 6691.2682 | 6571.2012 | 6402.4438 | 6164.7429 | 5829.293 | 5355.0913
| TRUE | 4677 | 22008229 | WBE | Blank | 22 | TRANS TR NO.3 | RESTRICTED EF | X | ABB | GROUP_3173 | GROUP 3173 | GROUP 3000s | Electronic |  | 0.066046 | 2190 |  | 9.9 | 0.042792 | 0.0074621 | 0.03533 | 457.152 | 3283.3267 | 3740.4788 | 163.8344 | 17.1957 | 1022.3214 |  | 20.1542 | 0.31092 | 0.054218 | 0.2567 | 3321.5437 | 23855.7685 | 27177.3122 | 1190.3766 | 124.9396 | 7427.9123 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.064057 |  | 4943.8303 | 35920.5406 | 71.2737 | 35849.2669 |  | 0.071088 |  | 10.6294 | 11.4125 | 12.2533 | 13.1561 | 14.1254 | 15.1661 | 16.2834 | 17.4831 | 18.7712 | 20.1542 | 21.639 | 23.2333 | 24.945 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.051896 | 0.063029 | 0.076653 | 0.093338 | 0.11379 | 0.13887 | 0.16964 | 0.20743 | 0.25385 | 0.31092 | 0.38109 | 0.46742 | 0.57368 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0090497 | 0.010991 | 0.013367 | 0.016276 | 0.019842 | 0.024215 | 0.029582 | 0.036172 | 0.044267 | 0.054218 | 0.066454 | 0.081509 | 0.10004 | 0.12285 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 5995.6733 | 7281.8401 | 8855.8151 | 10783.4713 | 13145.9665 | 16043.3207 | 19598.835 | 23964.5522 | 29328.0023 | 35920.5406 | 44027.6516 | 54001.6851 | 66277.6004 | 81392.43 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 |  | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 52.8382 | 70.0402 | 93.6533 | 126.2127 | 171.2918 | 233.9348 | 321.2747 | 443.4126 | 614.6701 | 855.3771 | 1194.4218 | 1672.8908 | 2349.2683 |  | 554.4151 | 673.3459 | 818.8901 | 997.139 | 1215.597 | 1483.513 | 1812.2886 | 2215.983 | 2711.9369 | 3321.5437 | 4071.2018 | 4993.4927 | 6128.6368 | 7526.293 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 527.2832 | 646.214 | 791.7582 | 970.0071 | 1188.4651 | 1456.3811 | 1785.1567 | 2188.8511 | 2684.805 | 3294.4118 | 4044.0699 | 4966.3608 | 6101.5049 | 7499.1611 | 8533.0001 | 8533.0001 | 8533.0001 | 8527.6569 | 8517.0843 | 8502.5713 | 8482.5598 | 8454.8535 | 8416.3522 | 8362.6716 | 8287.6038 | 8182.3464 | 8034.4041 | 7826.022 | 7531.9476 | 7116.2356 |  | 3981.8831 | 4836.0601 | 5881.3779 | 7161.5847 | 8730.5794 | 10654.788 | 13016.0979 | 15915.4845 | 19477.4917 | 23855.7685 | 29239.9125 | 35863.9284 | 44016.6842 | 54054.837 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 3981.6774 | 4835.8543 | 5881.1722 | 7161.379 | 8730.3737 | 10654.5822 | 13015.8921 | 15915.2788 | 19477.286 | 23855.5628 | 29239.7068 | 35863.7227 | 44016.4784 | 54054.6313 | 61479.8009 | 61479.8009 | 61479.8009 | 61479.7604 | 61479.6802 | 61479.5702 | 61479.4184 | 61479.2083 | 61478.9164 | 61478.5094 | 61477.9402 | 61477.142 | 61476.0203 | 61474.4402 | 61472.2104 | 61469.0582 |  | 4508.9606 | 5482.0684 | 6672.9304 | 8131.3861 | 9918.8388 | 12110.9634 | 14801.0488 | 18104.1299 | 22162.091 | 27149.9746 | 33283.7766 | 40830.0835 | 50117.9833 | 61553.7924 | 70012.801 | 70012.801 | 70012.801 | 70007.4172 | 69996.7645 | 69982.1415 | 69961.9782 | 69934.0618 | 69895.2686 | 69841.181 | 69765.544 | 69659.4884 | 69510.4244 | 69300.4622 | 69004.158 | 68585.2938 |  | 198.6916 | 241.3141 | 293.4743 | 357.3552 | 435.6463 | 531.6622 | 649.489 | 794.1652 | 971.9054 | 1190.3766 | 1459.0394 | 1789.5705 | 2196.3841 | 2697.2769 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 184.0191 | 226.6416 | 278.8018 | 342.6828 | 420.9739 | 516.9897 | 634.8165 | 779.4927 | 957.233 | 1175.7041 | 1444.367 | 1774.8981 | 2181.7116 | 2682.6044 | 3053.1122 | 3053.1122 | 3053.1122 | 3050.2227 | 3044.5052 | 3036.6568 | 3025.835 | 3010.8519 | 2990.0311 | 2961.0017 | 2920.4064 | 2863.485 | 2783.4806 | 2670.7914 | 2511.7613 | 2286.9518 |  | 20.8543 | 25.3278 | 30.8025 | 37.5073 | 45.7246 | 55.8022 | 68.1691 | 83.354 | 102.0093 | 124.9396 | 153.1379 | 187.8298 | 230.5281 | 283.1008 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 18.7866 | 23.2601 | 28.7348 | 35.4396 | 43.6569 | 53.7345 | 66.1014 | 81.2863 | 99.9416 | 122.8719 | 151.0702 | 185.7621 | 228.4604 | 281.0331 | 319.9209 | 319.9209 | 319.9209 | 319.5137 | 318.7079 | 317.6019 | 316.0769 | 313.9654 | 311.0313 | 306.9403 | 301.2195 | 293.1979 | 281.9234 | 266.0428 | 243.6317 | 211.9507 |  | 1239.8292 | 1505.7922 | 1831.2703 | 2229.8851 | 2718.4192 | 3317.5553 | 4052.7905 | 4955.5655 | 6064.6589 | 7427.9123 | 9104.36 | 11166.8636 | 13705.3672 | 16830.9223 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 |  | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.076673 | 0.10163 | 0.1359 | 0.18315 | 0.24856 | 0.33946 | 0.4662 | 0.64343 | 0.89194 | 1.2412 | 1.7332 | 2.4275 | 3.409 |  | 1239.7651 | 1505.7281 | 1831.2062 | 2229.8211 | 2718.3551 | 3317.4912 | 4052.7265 | 4955.5014 | 6064.5949 | 7427.8482 | 9104.296 | 11166.7996 | 13705.3032 | 16830.8583 | 19142.8152 | 19142.8152 | 19142.8152 | 19142.8026 | 19142.7776 | 19142.7433 | 19142.6961 | 19142.6307 | 19142.5398 | 19142.413 | 19142.2358 | 19141.9873 | 19141.638 | 19141.146 | 19140.4517 | 19139.4702 |  | 5951.5315 | 7237.6983 | 8811.6733 | 10739.3295 | 13101.8247 | 15999.1788 | 19554.6932 | 23920.4103 | 29283.8604 | 35876.3988 | 43983.5098 | 53957.5432 | 66233.4585 | 81348.2882 | 92528.6493 | 92528.6493 | 92528.6493 | 92519.9561 | 92502.7552 | 92479.1436 | 92446.5861 | 92401.5098 | 92338.8707 | 92251.536 | 92129.4056 | 91958.1586 | 91717.4663 | 91378.4424 | 90900.0027 | 90223.6665
| TRUE | 4678 | 22008213 | WBE | Blank | 66 | BUS NO.1 | HIBP | Y | ABB | RADHA_3110 | RADHA 3110 | RADHA | Electronic |  | 0.0034106 | 2190 |  | 6.6 | 0.014726 | 0.00014965 | 0.014576 | 154.7806 | 65.8469 | 220.6275 | 42.6512 | 5.8934 | 20.5026 |  | 12.1996 | 0.075729 | 0.00076959 | 0.07496 | 795.9639 | 338.6195 | 1134.5834 | 219.3351 | 30.3069 | 105.4351 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 54.2634 | 0.010624 | 54.274 | 14.6699 | 2.0677 | 0.0033079 |  | 289.6747 | 1489.6605 | 71.0149 | 1418.6456 |  | 0.061434 |  | 7.0182 | 7.4628 | 7.9357 | 8.4385 | 8.9732 | 9.5417 | 10.1463 | 10.7891 | 11.4727 | 12.1996 | 12.9726 | 13.7946 | 14.6686 | 15.598 | 16.5863 | 17.6372 | 18.7547 | 19.943 | 21.2066 | 22.5502 | 23.979 | 25.4983 | 27.1139 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.017237 | 0.020209 | 0.023729 | 0.027904 | 0.032859 | 0.038742 | 0.045735 | 0.05405 | 0.063946 | 0.075729 | 0.089768 | 0.1065 | 0.12646 | 0.15027 | 0.1787 | 0.21265 | 0.25322 | 0.3017 | 0.35966 | 0.42899 | 0.51193 | 0.61118 | 0.73 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00017517 | 0.00020537 | 0.00024115 | 0.00028358 | 0.00033392 | 0.00039371 | 0.00046477 | 0.00054928 | 0.00064985 | 0.00076959 | 0.00091225 | 0.0010823 | 0.0012851 | 0.0015272 | 0.0018161 | 0.0021611 | 0.0025733 | 0.003066 | 0.003655 | 0.0043595 | 0.0052024 | 0.0062111 | 0.0074186 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 339.0622 | 397.5214 | 466.7803 | 548.9036 | 646.3588 | 762.0957 | 899.6423 | 1063.2192 | 1257.8768 | 1489.6605 | 1765.8085 | 2094.9889 | 2487.5851 | 2956.0377 | 3515.2553 | 4183.1072 | 4981.0159 | 5934.6675 | 7074.8653 | 8438.5556 | 10070.0584 | 12022.5467 | 14359.8229 | 15761.8632 | 15761.8632 | 15761.8632 | 15761.8632 | 15761.8632 | 15761.8632 | 15761.8632 |  | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 43.8834 | 52.5256 | 69.6258 | 93.0992 | 125.466 | 170.2784 | 232.5507 | 319.374 | 440.7893 | 611.0335 | 850.3165 | 1187.3553 | 1662.9935 | 2335.3695 |  | 181.1696 | 212.4059 | 249.4127 | 293.2933 | 345.3661 | 407.2073 | 480.702 | 568.1053 | 672.1159 | 795.9639 | 943.5168 | 1119.4064 | 1329.1806 | 1579.4869 | 1878.2912 | 2235.1417 | 2661.4848 | 3171.0453 | 3780.2823 | 4508.937 | 5380.6909 | 6423.9556 | 7672.8223 | 8421.9685 | 8421.9685 | 8421.9685 | 8421.9685 | 8421.9685 | 8421.9685 | 8421.9685 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2777 | 143.7787 | 197.4587 | 272.5259 | 377.7825 | 525.7234 | 734.1037 | 1028.1756 | 1443.8841 |  | 154.038 | 185.2742 | 222.281 | 266.1616 | 318.2344 | 380.0756 | 453.5703 | 540.9736 | 644.9842 | 768.8322 | 916.3852 | 1092.2747 | 1302.0489 | 1552.3552 | 1851.1595 | 2208.01 | 2634.3531 | 3138.5704 | 3737.2349 | 4451.3768 | 5303.1193 | 6318.6779 | 7529.0436 | 8224.5097 | 8149.4426 | 8044.186 | 7896.245 | 7687.8647 | 7393.7929 | 6978.0843 |  | 77.0733 | 90.3619 | 106.1053 | 124.7731 | 146.9259 | 173.2344 | 204.5006 | 241.6838 | 285.932 | 338.6195 | 401.3916 | 476.2187 | 565.461 | 671.9464 | 799.064 | 950.8756 | 1132.2508 | 1349.0284 | 1608.2104 | 1918.1952 | 2289.0574 | 2732.8838 | 3264.1776 | 3582.8799 | 3582.8799 | 3582.8799 | 3582.8799 | 3582.8799 | 3582.8799 | 3582.8799 |  | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.010624 | 0.012716 | 0.016856 | 0.022538 | 0.030374 | 0.041223 | 0.056298 | 0.077317 | 0.10671 | 0.14793 | 0.20585 | 0.28745 | 0.40259 | 0.56537 |  | 77.0627 | 90.3512 | 106.0947 | 124.7624 | 146.9153 | 173.2238 | 204.49 | 241.6732 | 285.9214 | 338.6089 | 401.381 | 476.208 | 565.4503 | 671.9358 | 799.0534 | 950.865 | 1132.2402 | 1349.0157 | 1608.1936 | 1918.1727 | 2289.027 | 2732.8426 | 3264.1213 | 3582.8026 | 3582.7732 | 3582.732 | 3582.674 | 3582.5924 | 3582.4773 | 3582.3145 |  | 231.1007 | 275.6254 | 328.3758 | 390.9241 | 465.1497 | 553.2994 | 658.0603 | 782.6468 | 930.9056 | 1107.4411 | 1317.7661 | 1568.4827 | 1867.4993 | 2224.291 | 2650.2129 | 3158.875 | 3766.5933 | 4487.586 | 5345.4284 | 6369.5495 | 7592.1463 | 9051.5205 | 10793.1649 | 11807.3123 | 11732.2158 | 11626.918 | 11478.9191 | 11270.4572 | 10976.2701 | 10560.3989 |  | 49.9229 | 58.5304 | 68.7279 | 80.8196 | 95.1688 | 112.2097 | 132.4618 | 156.5466 | 185.2076 | 219.3351 | 259.9946 | 308.4625 | 366.2677 | 435.2419 | 517.5801 | 615.9135 | 733.3962 | 873.8102 | 1041.691 | 1242.4784 | 1482.6981 | 1770.1791 | 2114.3156 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 35.253 | 43.8604 | 54.058 | 66.1497 | 80.4988 | 97.5397 | 117.7919 | 141.8766 | 170.5377 | 204.6651 | 245.3247 | 293.7926 | 351.5978 | 420.572 | 502.9102 | 601.2436 | 718.7263 | 856.2512 | 1018.4155 | 1211.3559 | 1440.7556 | 1713.2561 | 2036.5754 | 2213.9849 | 2173.3966 | 2116.485 | 2036.4943 | 1923.8244 | 1764.8217 | 1540.0507 |  | 6.8982 | 8.0875 | 9.4966 | 11.1674 | 13.1501 | 15.5047 | 18.3031 | 21.631 | 25.5913 | 30.3069 | 35.9251 | 42.6222 | 50.6095 | 60.1401 | 71.5173 | 85.1047 | 101.338 | 120.7399 | 143.9371 | 171.6811 | 204.8738 | 244.5969 | 292.1484 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 4.8305 | 6.0198 | 7.4289 | 9.0997 | 11.0824 | 13.437 | 16.2354 | 19.5633 | 23.5236 | 28.2392 | 33.8574 | 40.5545 | 48.5419 | 58.0725 | 69.4496 | 83.037 | 99.2703 | 118.265 | 140.6564 | 167.2945 | 198.9621 | 236.5737 | 281.1911 | 305.6245 | 299.9037 | 291.8821 | 280.6076 | 264.7271 | 242.316 | 210.6351 |  | 23.9981 | 28.1358 | 33.0378 | 38.8503 | 45.748 | 53.9396 | 63.6748 | 75.2525 | 89.03 | 105.4351 | 124.9803 | 148.279 | 176.0662 | 209.2223 | 248.8026 | 296.0718 | 352.5462 | 420.0437 | 500.7445 | 597.2638 | 712.7382 | 850.9313 | 1016.359 | 1115.5925 | 1115.5925 | 1115.5925 | 1115.5925 | 1115.5925 | 1115.5925 | 1115.5925 |  | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0039593 | 0.0052483 | 0.0070177 | 0.0094575 | 0.012835 | 0.017529 | 0.024074 | 0.033226 | 0.046059 | 0.064096 | 0.089502 | 0.12535 | 0.17604 |  | 23.9948 | 28.1324 | 33.0345 | 38.847 | 45.7446 | 53.9363 | 63.6715 | 75.2492 | 89.0266 | 105.4318 | 124.977 | 148.2757 | 176.0629 | 209.219 | 248.7993 | 296.0685 | 352.5428 | 420.0397 | 500.7393 | 597.2567 | 712.7287 | 850.9185 | 1016.3415 | 1115.5685 | 1115.5593 | 1115.5465 | 1115.5284 | 1115.503 | 1115.4672 | 1115.4165 |  | 295.179 | 353.6381 | 422.8971 | 505.0204 | 602.4755 | 718.2124 | 855.7591 | 1019.336 | 1213.9936 | 1445.7773 | 1721.9253 | 2051.1056 | 2443.7018 | 2912.1545 | 3471.3721 | 4139.224 | 4937.1327 | 5882.142 | 7005.2397 | 8345.4567 | 9944.5927 | 11852.2688 | 14127.2729 | 15442.4902 | 15321.0754 | 15150.8316 | 14911.5494 | 14574.5117 | 14098.875 | 13426.5012
| TRUE | 4679 | 22008214 | WBE | Blank | 66 | BUS NO.3 | HIBP | Y | ABB | RADHA_3110 | RADHA 3110 | RADHA | Electronic |  | 0.0034106 | 2190 |  | 6.6 | 0.014726 | 0.00014965 | 0.014576 | 116.0855 | 32.9234 | 149.0089 | 42.6512 | 5.8934 | 20.5026 |  | 14.9721 | 0.13394 | 0.0013611 | 0.13257 | 1055.8114 | 299.4427 | 1355.2541 | 387.9178 | 53.6011 | 186.4735 |  | 0.0051679 | 2.4145e-08 | 0.0051679 | 40.6975 | 0.0053119 | 40.7028 | 14.6699 | 2.0677 | 0.0033079 |  | 218.0561 | 1983.2465 | 57.4437 | 1925.8028 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.018172 | 0.022489 | 0.027904 | 0.034708 | 0.043268 | 0.05405 | 0.067647 | 0.084812 | 0.1065 | 0.13394 | 0.16866 | 0.21265 | 0.26843 | 0.33918 | 0.42899 | 0.54305 | 0.688 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00018467 | 0.00022854 | 0.00028358 | 0.00035272 | 0.00043971 | 0.00054928 | 0.00068746 | 0.00086189 | 0.0010823 | 0.0013611 | 0.001714 | 0.0021611 | 0.0027279 | 0.0034469 | 0.0043595 | 0.0055187 | 0.0069917 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 0.0081429 | 269.0835 | 333.0025 | 413.1938 | 513.9446 | 640.6947 | 800.351 | 1001.6869 | 1255.8532 | 1577.0279 | 1983.2465 | 2497.4597 | 3148.884 | 3974.7249 | 5022.3754 | 6352.2237 | 8041.2364 | 10187.5335 | 11864.9312 | 11864.9312 | 11864.9312 | 11864.9312 | 11864.9312 | 11864.9312 | 11864.9312 | 11864.9312 | 11864.9312 | 11864.9312 | 11864.9312 | 11864.9312 | 11864.9312 |  | 43.878 | 43.878 | 43.878 | 43.878 | 43.878 | 43.878 | 43.878 | 43.878 | 43.878 | 43.878 | 43.878 | 43.878 | 43.878 | 43.878 | 43.878 | 43.878 | 43.878 | 52.5192 | 69.6173 | 93.0878 | 125.4507 | 170.2575 | 232.5222 | 319.3348 | 440.7352 | 610.9586 | 850.2122 | 1187.2097 | 1662.7896 | 2335.0831 |  | 143.2507 | 177.2789 | 219.97 | 273.6062 | 341.0836 | 426.079 | 533.2632 | 668.5725 | 839.5548 | 1055.8114 | 1329.5606 | 1676.3563 | 2116.0052 | 2673.7378 | 3381.7028 | 4280.8743 | 5423.4882 | 6316.4763 | 6316.4763 | 6316.4763 | 6316.4763 | 6316.4763 | 6316.4763 | 6316.4763 | 6316.4763 | 6316.4763 | 6316.4763 | 6316.4763 | 6316.4763 | 6316.4763 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2777 | 143.7787 | 197.4587 | 272.5259 | 377.7825 | 525.7234 | 734.1037 | 1028.1756 | 1443.8841 |  | 116.119 | 150.1472 | 192.8383 | 246.4745 | 313.9519 | 398.9473 | 506.1316 | 641.4408 | 812.4231 | 1028.6797 | 1302.4289 | 1649.2246 | 2088.8735 | 2646.6061 | 3354.5711 | 4253.7427 | 5396.3565 | 6284.0014 | 6273.4289 | 6258.9161 | 6238.9047 | 6211.1987 | 6172.6977 | 6119.0176 | 6043.9505 | 5938.6939 | 5790.7529 | 5582.3726 | 5288.3007 | 4872.5922 |  | 40.6279 | 50.2788 | 62.3865 | 77.5985 | 96.736 | 120.8419 | 151.2408 | 189.6164 | 238.1093 | 299.4427 | 377.0818 | 475.4378 | 600.1283 | 758.309 | 959.0976 | 1214.1151 | 1538.1762 | 1791.4399 | 1791.4399 | 1791.4399 | 1791.4399 | 1791.4399 | 1791.4399 | 1791.4399 | 1791.4399 | 1791.4399 | 1791.4399 | 1791.4399 | 1791.4399 | 1791.4399 |  | 0.0053119 | 0.0053119 | 0.0053119 | 0.0053119 | 0.0053119 | 0.0053119 | 0.0053119 | 0.0053119 | 0.0053119 | 0.0053119 | 0.0053119 | 0.0053119 | 0.0053119 | 0.0053119 | 0.0053119 | 0.0053119 | 0.0053119 | 0.006358 | 0.0084279 | 0.011269 | 0.015187 | 0.020611 | 0.028149 | 0.038659 | 0.053355 | 0.073963 | 0.10293 | 0.14372 | 0.2013 | 0.28269 |  | 40.6226 | 50.2734 | 62.3812 | 77.5932 | 96.7307 | 120.8366 | 151.2355 | 189.6111 | 238.104 | 299.4374 | 377.0764 | 475.4325 | 600.123 | 758.3037 | 959.0923 | 1214.1098 | 1538.1709 | 1791.4336 | 1791.4315 | 1791.4287 | 1791.4248 | 1791.4193 | 1791.4118 | 1791.4013 | 1791.3866 | 1791.366 | 1791.337 | 1791.2962 | 1791.2386 | 1791.1573 |  | 156.7416 | 200.4207 | 255.2195 | 324.0677 | 410.6826 | 519.7839 | 657.3671 | 831.0519 | 1050.5271 | 1328.1171 | 1679.5054 | 2124.6571 | 2688.9965 | 3404.9098 | 4313.6634 | 5467.8524 | 6934.5274 | 8075.435 | 8064.8604 | 8050.3448 | 8030.3295 | 8002.618 | 7964.1095 | 7910.4189 | 7835.3371 | 7730.0599 | 7582.0899 | 7373.6688 | 7079.5394 | 6663.7495 |  | 52.632 | 65.1344 | 80.8196 | 100.5262 | 125.3182 | 156.5466 | 195.9273 | 245.6416 | 308.4625 | 387.9178 | 488.4966 | 615.9135 | 777.4458 | 982.3635 | 1242.4784 | 1572.8449 | 1992.655 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 | 2320.7496 |  | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 14.6699 | 17.559 | 23.2755 | 31.1225 | 41.9425 | 56.923 | 77.7402 | 106.7647 | 147.353 | 204.2645 | 284.2553 | 396.9252 | 555.9279 | 780.6988 |  | 37.9621 | 50.4645 | 66.1497 | 85.8563 | 110.6483 | 141.8766 | 181.2574 | 230.9717 | 293.7926 | 373.2479 | 473.8267 | 601.2436 | 762.7759 | 967.6936 | 1227.8085 | 1558.1749 | 1977.9851 | 2303.1906 | 2297.4741 | 2289.6271 | 2278.8071 | 2263.8266 | 2243.0094 | 2213.9849 | 2173.3966 | 2116.485 | 2036.4943 | 1923.8244 | 1764.8217 | 1540.0507 |  | 7.2725 | 9 | 11.1674 | 13.8903 | 17.316 | 21.631 | 27.0725 | 33.9419 | 42.6222 | 53.6011 | 67.4987 | 85.1047 | 107.4246 | 135.7394 | 171.6811 | 217.33 | 275.3378 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 | 320.6727 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 5.2048 | 6.9323 | 9.0997 | 11.8227 | 15.2483 | 19.5633 | 25.0048 | 31.8742 | 40.5545 | 51.5334 | 65.431 | 83.037 | 105.3569 | 133.6717 | 169.6135 | 215.2623 | 273.2701 | 318.1978 | 317.3921 | 316.2861 | 314.761 | 312.6496 | 309.7154 | 305.6245 | 299.9037 | 291.8821 | 280.6076 | 264.7271 | 242.316 | 210.6351 |  | 25.3004 | 31.3103 | 38.8503 | 48.3233 | 60.2409 | 75.2525 | 94.183 | 118.0808 | 148.279 | 186.4735 | 234.822 | 296.0718 | 373.721 | 472.2256 | 597.2638 | 756.0721 | 957.8763 | 1115.5925 | 1115.5925 | 1115.5925 | 1115.5925 | 1115.5925 | 1115.5925 | 1115.5925 | 1115.5925 | 1115.5925 | 1115.5925 | 1115.5925 | 1115.5925 | 1115.5925 |  | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0033079 | 0.0039593 | 0.0052483 | 0.0070177 | 0.0094575 | 0.012835 | 0.017529 | 0.024074 | 0.033226 | 0.046059 | 0.064096 | 0.089502 | 0.12535 | 0.17604 |  | 25.2971 | 31.307 | 38.847 | 48.32 | 60.2376 | 75.2492 | 94.1797 | 118.0775 | 148.2757 | 186.4702 | 234.8187 | 296.0685 | 373.7176 | 472.2223 | 597.2605 | 756.0688 | 957.873 | 1115.5886 | 1115.5873 | 1115.5855 | 1115.5831 | 1115.5797 | 1115.575 | 1115.5685 | 1115.5593 | 1115.5465 | 1115.5284 | 1115.503 | 1115.4672 | 1115.4165 |  | 225.2056 | 289.1245 | 369.3159 | 470.0666 | 596.8168 | 756.473 | 957.809 | 1211.9753 | 1533.15 | 1939.3686 | 2453.5818 | 3105.0061 | 3930.8469 | 4978.4975 | 6308.3458 | 7997.3585 | 10143.6556 | 11812.412 | 11795.314 | 11771.8435 | 11739.4807 | 11694.6739 | 11632.4093 | 11545.5968 | 11424.1967 | 11253.9735 | 11014.7203 | 10677.7234 | 10202.1442 | 9529.8518
| TRUE | 4680 | 22008215 | WBE | Blank | 66 | CB A | CB FAIL | X | Schweitzer | SEL_551 | SEL 551 | SEL 500s | Digital |  | 0 | 1 |  | 5.5 | 0.010964 | 0 | 0.010964 | 57.5602 | 0 | 57.5602 | 31.1222 | 4.3866 | 0 |  | 12.2319 | 0.089657 | 0 | 0.089657 | 470.7002 | 0 | 470.7002 | 254.5023 | 35.8718 | 0 |  | 0.0051679 | 0 | 0.0051679 | 27.1317 | 0 | 27.1317 | 14.6698 | 2.0677 | 0 |  | 93.069 | 761.0744 | 43.8691 | 717.2053 |  | 0.07993 |  | 5.9577 | 6.4534 | 6.9904 | 7.5721 | 8.2022 | 8.8847 | 9.624 | 10.4248 | 11.2923 | 12.2319 | 13.2497 | 14.3522 | 15.5465 | 16.8401 | 18.2414 | 19.7593 | 21.4035 | 23.1845 | 25.1137 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.013366 | 0.016347 | 0.020053 | 0.024668 | 0.030423 | 0.037611 | 0.0466 | 0.057853 | 0.071959 | 0.089657 | 0.11189 | 0.13983 | 0.17499 | 0.21925 | 0.27503 | 0.34535 | 0.43407 | 0.54606 | 0.6875 | 0.86622 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.4582 | 138.7631 | 170.2232 | 209.3987 | 258.2552 | 319.2705 | 395.57 | 491.0981 | 610.8355 | 761.0744 | 949.7675 | 1186.9705 | 1485.4028 | 1861.1593 | 2334.6127 | 2931.5583 | 3684.667 | 4635.3288 | 5835.9923 | 7353.1347 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 | 7994.3338 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 70.1703 | 85.8206 | 105.2776 | 129.5064 | 159.7226 | 197.4586 | 244.6474 | 303.7285 | 377.7823 | 470.7002 | 587.4009 | 734.1034 | 918.6742 | 1151.0676 | 1443.8834 | 1813.0752 | 2278.849 | 2866.803 | 3609.3751 | 4547.6792 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 | 4944.2404 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 43.0386 | 58.6889 | 78.1459 | 102.3747 | 132.5909 | 170.327 | 217.5158 | 276.5969 | 350.6506 | 443.5686 | 560.2692 | 706.9717 | 891.5426 | 1123.936 | 1416.7518 | 1785.9436 | 2251.7173 | 2834.3281 | 3566.3276 | 4490.119 | 4866.6688 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 43.0386 | 58.6889 | 78.1459 | 102.3747 | 132.5909 | 170.327 | 217.5158 | 276.5969 | 350.6506 | 443.5686 | 560.2692 | 706.9717 | 891.5426 | 1123.936 | 1416.7518 | 1785.9436 | 2251.7173 | 2834.3281 | 3566.3276 | 4490.119 | 4866.6688 | 4838.9628 | 4800.4618 | 4746.7817 | 4671.7146 | 4566.4581 | 4418.5172 | 4210.137 | 3916.0652 | 3500.3569 |  | 37.9403 | 46.4022 | 56.9224 | 70.0227 | 86.3602 | 106.7637 | 132.2781 | 164.2226 | 204.2626 | 254.5023 | 317.6011 | 396.9214 | 496.7168 | 622.3693 | 780.6916 | 980.3094 | 1232.148 | 1550.0482 | 1951.5485 | 2458.879 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 | 2673.2952 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 23.2705 | 31.7324 | 42.2526 | 55.3529 | 71.6904 | 92.0939 | 117.6083 | 149.5528 | 189.5929 | 239.8325 | 302.9313 | 382.2517 | 482.0471 | 607.6996 | 766.0218 | 965.6396 | 1217.4783 | 1532.4893 | 1928.2733 | 2427.7569 | 2631.3531 | 2616.3728 | 2595.5558 | 2566.5316 | 2525.9436 | 2469.0326 | 2389.0426 | 2276.3738 | 2117.3725 | 1892.6037 |  | 5.3476 | 6.5403 | 8.0232 | 9.8696 | 12.1724 | 15.0482 | 18.6445 | 23.147 | 28.7906 | 35.8718 | 44.7655 | 55.9457 | 70.0117 | 87.7223 | 110.0377 | 138.1736 | 173.67 | 218.4777 | 275.0688 | 346.5765 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 | 376.7982 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 3.28 | 4.4727 | 5.9555 | 7.8019 | 10.1047 | 12.9805 | 16.5768 | 21.0793 | 26.7229 | 33.8042 | 42.6979 | 53.878 | 67.944 | 85.6546 | 107.97 | 136.1059 | 171.6023 | 216.0028 | 271.7881 | 342.1898 | 370.8865 | 368.775 | 365.8409 | 361.75 | 356.0291 | 348.0076 | 336.7331 | 320.8525 | 298.4415 | 266.7605 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 69.5891 | 94.894 | 126.354 | 165.5295 | 214.386 | 275.4014 | 351.7009 | 447.229 | 566.9664 | 717.2053 | 905.8984 | 1143.1014 | 1441.5337 | 1817.2902 | 2290.7435 | 2887.6891 | 3640.7979 | 4582.8202 | 5766.3891 | 7260.0657 | 7868.9084 | 7824.1106 | 7761.8584 | 7675.0633 | 7553.6874 | 7383.4983 | 7144.2929 | 6807.3633 | 6331.8792 | 5659.7211
| TRUE | 4681 | 22004385 | WBE | Blank | 66 | CB B | CB FAIL | Blank | EMAIL | GROUP_3183 | GROUP 3183 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 449.3168 | 0 | 449.3168 | 121.4703 | 17.1211 | 0 |  | 20.1542 | 0.31092 | 0 | 0.31092 | 3264.6152 | 0 | 3264.6152 | 882.5704 | 124.3974 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 587.9082 | 4271.5829 | 71.0008 | 4200.5821 |  | 0.071088 |  | 10.6294 | 11.4125 | 12.2533 | 13.1561 | 14.1254 | 15.1661 | 16.2834 | 17.4831 | 18.7712 | 20.1542 | 21.639 | 23.2333 | 24.945 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.051896 | 0.063029 | 0.076653 | 0.093338 | 0.11379 | 0.13887 | 0.16964 | 0.20743 | 0.25385 | 0.31092 | 0.38109 | 0.46742 | 0.57368 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 712.9908 | 865.9386 | 1053.1119 | 1282.3441 | 1563.2862 | 1907.8325 | 2330.6456 | 2849.806 | 3487.6144 | 4271.5829 | 5235.6607 | 6421.7484 | 7881.5703 | 9678.9889 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 544.9129 | 661.8053 | 804.855 | 980.0488 | 1194.7627 | 1458.0868 | 1781.2275 | 2178.0029 | 2665.4566 | 3264.6152 | 4001.4247 | 4907.9083 | 6023.5969 | 7397.2985 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 517.7812 | 634.6737 | 777.7234 | 952.9172 | 1167.631 | 1430.9552 | 1754.0958 | 2150.8712 | 2638.3249 | 3237.4835 | 3974.293 | 4880.7766 | 5996.4653 | 7370.1668 | 8386.2867 | 8386.2867 | 8386.2867 | 8380.9435 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 517.7812 | 634.6737 | 777.7234 | 952.9172 | 1167.631 | 1430.9552 | 1754.0958 | 2150.8712 | 2638.3249 | 3237.4835 | 3974.293 | 4880.7766 | 5996.4653 | 7370.1668 | 8386.2867 | 8386.2867 | 8386.2867 | 8380.9435 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 147.3141 | 178.9154 | 217.588 | 264.9507 | 322.9974 | 394.1856 | 481.5448 | 588.8108 | 720.5912 | 882.5704 | 1081.7627 | 1326.8254 | 1628.4456 | 1999.8181 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 132.6444 | 164.2456 | 202.9183 | 250.2809 | 308.3276 | 379.5158 | 466.8751 | 574.1411 | 705.9214 | 867.9006 | 1067.0929 | 1312.1557 | 1613.7758 | 1985.1483 | 2259.8506 | 2259.8506 | 2259.8506 | 2256.9616 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 20.7638 | 25.2179 | 30.6688 | 37.3445 | 45.5261 | 55.5601 | 67.8732 | 82.9923 | 101.5666 | 124.3974 | 152.4733 | 187.0147 | 229.5277 | 281.8723 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 18.6961 | 23.1502 | 28.6011 | 35.2768 | 43.4585 | 53.4924 | 65.8056 | 80.9246 | 99.4989 | 122.3297 | 150.4056 | 184.947 | 227.46 | 279.8046 | 318.5236 | 318.5236 | 318.5236 | 318.1164 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 669.1217 | 822.0695 | 1009.2428 | 1238.4749 | 1519.4171 | 1863.9633 | 2286.7764 | 2805.9368 | 3443.7452 | 4227.7138 | 5191.7916 | 6377.8793 | 7837.7011 | 9635.1197 | 10964.661 | 10964.661 | 10964.661 | 10956.0215 | 10938.9268 | 10915.4611 | 10883.1047 | 10838.3069 | 10776.0547 | 10689.2596 | 10567.8837 | 10397.6946 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| TRUE | 4682 | 22008216 | WBE | Blank | 66 | CB C | CB FAIL | BU | EMAIL | GROUP_3183 | GROUP 3183 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 449.3168 | 0 | 449.3168 | 121.4703 | 17.1211 | 0 |  | 20.1542 | 0.31092 | 0 | 0.31092 | 3264.6152 | 0 | 3264.6152 | 882.5704 | 124.3974 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 587.9082 | 4271.5829 | 71.0008 | 4200.5821 |  | 0.071088 |  | 10.6294 | 11.4125 | 12.2533 | 13.1561 | 14.1254 | 15.1661 | 16.2834 | 17.4831 | 18.7712 | 20.1542 | 21.639 | 23.2333 | 24.945 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.051896 | 0.063029 | 0.076653 | 0.093338 | 0.11379 | 0.13887 | 0.16964 | 0.20743 | 0.25385 | 0.31092 | 0.38109 | 0.46742 | 0.57368 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 712.9908 | 865.9386 | 1053.1119 | 1282.3441 | 1563.2862 | 1907.8325 | 2330.6456 | 2849.806 | 3487.6144 | 4271.5829 | 5235.6607 | 6421.7484 | 7881.5703 | 9678.9889 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 544.9129 | 661.8053 | 804.855 | 980.0488 | 1194.7627 | 1458.0868 | 1781.2275 | 2178.0029 | 2665.4566 | 3264.6152 | 4001.4247 | 4907.9083 | 6023.5969 | 7397.2985 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 517.7812 | 634.6737 | 777.7234 | 952.9172 | 1167.631 | 1430.9552 | 1754.0958 | 2150.8712 | 2638.3249 | 3237.4835 | 3974.293 | 4880.7766 | 5996.4653 | 7370.1668 | 8386.2867 | 8386.2867 | 8386.2867 | 8380.9435 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 517.7812 | 634.6737 | 777.7234 | 952.9172 | 1167.631 | 1430.9552 | 1754.0958 | 2150.8712 | 2638.3249 | 3237.4835 | 3974.293 | 4880.7766 | 5996.4653 | 7370.1668 | 8386.2867 | 8386.2867 | 8386.2867 | 8380.9435 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 147.3141 | 178.9154 | 217.588 | 264.9507 | 322.9974 | 394.1856 | 481.5448 | 588.8108 | 720.5912 | 882.5704 | 1081.7627 | 1326.8254 | 1628.4456 | 1999.8181 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 132.6444 | 164.2456 | 202.9183 | 250.2809 | 308.3276 | 379.5158 | 466.8751 | 574.1411 | 705.9214 | 867.9006 | 1067.0929 | 1312.1557 | 1613.7758 | 1985.1483 | 2259.8506 | 2259.8506 | 2259.8506 | 2256.9616 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 20.7638 | 25.2179 | 30.6688 | 37.3445 | 45.5261 | 55.5601 | 67.8732 | 82.9923 | 101.5666 | 124.3974 | 152.4733 | 187.0147 | 229.5277 | 281.8723 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 18.6961 | 23.1502 | 28.6011 | 35.2768 | 43.4585 | 53.4924 | 65.8056 | 80.9246 | 99.4989 | 122.3297 | 150.4056 | 184.947 | 227.46 | 279.8046 | 318.5236 | 318.5236 | 318.5236 | 318.1164 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 669.1217 | 822.0695 | 1009.2428 | 1238.4749 | 1519.4171 | 1863.9633 | 2286.7764 | 2805.9368 | 3443.7452 | 4227.7138 | 5191.7916 | 6377.8793 | 7837.7011 | 9635.1197 | 10964.661 | 10964.661 | 10964.661 | 10956.0215 | 10938.9268 | 10915.4611 | 10883.1047 | 10838.3069 | 10776.0547 | 10689.2596 | 10567.8837 | 10397.6946 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| TRUE | 4683 | 22004384 | WBE | Blank | 66 | CB D | CB FAIL | Blank | EMAIL | GROUP_3183 | GROUP 3183 | GROUP 3000s | Electronic |  | 0 | 2190 |  | 9.9 | 0.042792 | 0 | 0.042792 | 449.3168 | 0 | 449.3168 | 121.4703 | 17.1211 | 0 |  | 20.1542 | 0.31092 | 0 | 0.31092 | 3264.6152 | 0 | 3264.6152 | 882.5704 | 124.3974 | 0 |  | 0.0051679 | 0 | 0.0051679 | 54.2633 | 0 | 54.2633 | 14.6698 | 2.0677 | 0 |  | 587.9082 | 4271.5829 | 71.0008 | 4200.5821 |  | 0.071088 |  | 10.6294 | 11.4125 | 12.2533 | 13.1561 | 14.1254 | 15.1661 | 16.2834 | 17.4831 | 18.7712 | 20.1542 | 21.639 | 23.2333 | 24.945 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.051896 | 0.063029 | 0.076653 | 0.093338 | 0.11379 | 0.13887 | 0.16964 | 0.20743 | 0.25385 | 0.31092 | 0.38109 | 0.46742 | 0.57368 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 712.9908 | 865.9386 | 1053.1119 | 1282.3441 | 1563.2862 | 1907.8325 | 2330.6456 | 2849.806 | 3487.6144 | 4271.5829 | 5235.6607 | 6421.7484 | 7881.5703 | 9678.9889 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 | 11008.5301 |  | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 43.8691 | 52.5086 | 69.6033 | 93.069 | 125.4254 | 170.2232 | 232.4754 | 319.2705 | 440.6464 | 610.8355 | 850.0409 | 1186.9705 | 1662.4546 | 2334.6127 |  | 544.9129 | 661.8053 | 804.855 | 980.0488 | 1194.7627 | 1458.0868 | 1781.2275 | 2178.0029 | 2665.4566 | 3264.6152 | 4001.4247 | 4907.9083 | 6023.5969 | 7397.2985 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 | 8413.4184 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5602 | 77.5716 | 105.2776 | 143.7786 | 197.4586 | 272.5257 | 377.7823 | 525.7232 | 734.1034 | 1028.1751 | 1443.8834 |  | 517.7812 | 634.6737 | 777.7234 | 952.9172 | 1167.631 | 1430.9552 | 1754.0958 | 2150.8712 | 2638.3249 | 3237.4835 | 3974.293 | 4880.7766 | 5996.4653 | 7370.1668 | 8386.2867 | 8386.2867 | 8386.2867 | 8380.9435 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 517.7812 | 634.6737 | 777.7234 | 952.9172 | 1167.631 | 1430.9552 | 1754.0958 | 2150.8712 | 2638.3249 | 3237.4835 | 3974.293 | 4880.7766 | 5996.4653 | 7370.1668 | 8386.2867 | 8386.2867 | 8386.2867 | 8380.9435 | 8370.371 | 8355.8582 | 8335.8468 | 8308.1408 | 8269.6398 | 8215.9598 | 8140.8927 | 8035.6361 | 7887.6952 | 7679.315 | 7385.2433 | 6969.535 |  | 147.3141 | 178.9154 | 217.588 | 264.9507 | 322.9974 | 394.1856 | 481.5448 | 588.8108 | 720.5912 | 882.5704 | 1081.7627 | 1326.8254 | 1628.4456 | 1999.8181 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 | 2274.5204 |  | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 |  | 132.6444 | 164.2456 | 202.9183 | 250.2809 | 308.3276 | 379.5158 | 466.8751 | 574.1411 | 705.9214 | 867.9006 | 1067.0929 | 1312.1557 | 1613.7758 | 1985.1483 | 2259.8506 | 2259.8506 | 2259.8506 | 2256.9616 | 2251.2452 | 2243.3982 | 2232.5783 | 2217.598 | 2196.7809 | 2167.7567 | 2127.1688 | 2070.2578 | 1990.2678 | 1877.599 | 1718.5977 | 1493.8289 |  | 20.7638 | 25.2179 | 30.6688 | 37.3445 | 45.5261 | 55.5601 | 67.8732 | 82.9923 | 101.5666 | 124.3974 | 152.4733 | 187.0147 | 229.5277 | 281.8723 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 | 320.5913 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 |  | 18.6961 | 23.1502 | 28.6011 | 35.2768 | 43.4585 | 53.4924 | 65.8056 | 80.9246 | 99.4989 | 122.3297 | 150.4056 | 184.947 | 227.46 | 279.8046 | 318.5236 | 318.5236 | 318.5236 | 318.1164 | 317.3107 | 316.2047 | 314.6796 | 312.5681 | 309.634 | 305.5431 | 299.8222 | 291.8007 | 280.5262 | 264.6456 | 242.2346 | 210.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 669.1217 | 822.0695 | 1009.2428 | 1238.4749 | 1519.4171 | 1863.9633 | 2286.7764 | 2805.9368 | 3443.7452 | 4227.7138 | 5191.7916 | 6377.8793 | 7837.7011 | 9635.1197 | 10964.661 | 10964.661 | 10964.661 | 10956.0215 | 10938.9268 | 10915.4611 | 10883.1047 | 10838.3069 | 10776.0547 | 10689.2596 | 10567.8837 | 10397.6946 | 10158.4892 | 9821.5596 | 9346.0755 | 8673.9175
| FALSE | 4684 | 22016104 | WBE | WBE-ATS Line [Prev LV] | 66 | ATS Line [Prev LV] LINE | DISTANCE & DIR EF | X | GE | GE_D30 | GE D30 | GE RELAYS | Digital |  | 0.15703 | 1 |  | 1.0927 | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.1523 |  | 5.2187 | 0.0096441 | 2.0745e-06 | 0.009642 | 50.6327 | 0.2282 | 50.8609 | 27.3877 | 3.8586 | 0.28421 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.1523 |  | 44.1506 | 82.3915 | 44.1506 | 38.2409 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.4296e-06 | 2.0745e-06 | 3.0526e-06 | 4.5467e-06 | 6.8434e-06 | 1.0393e-05 | 1.5905e-05 | 2.4501e-05 | 3.7951e-05 | 5.9062e-05 | 9.2284e-05 | 0.00014468 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 56.7797 | 82.3915 | 121.2377 | 180.5783 | 271.7942 | 412.7743 | 631.7026 | 973.0736 | 1507.2539 | 2345.6948 | 3665.1501 | 5746.2541 | 8045.6296 | 8045.6296 | 8045.6296 | 8045.6296 | 8045.6296 | 8045.6296 | 8045.6296 | 8045.6296 | 8045.6296 | 8045.6296 |  | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 52.8455 | 70.0499 | 93.6662 | 126.2302 | 171.3154 | 233.9671 | 321.3191 | 443.4738 | 614.755 | 855.4952 | 1194.5867 | 1673.1218 | 2349.5927 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 34.8933 | 50.6327 | 74.5052 | 110.9723 | 167.0279 | 253.6656 | 388.2054 | 597.9909 | 926.2651 | 1441.519 | 2252.3748 | 3531.2926 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.761 | 23.5005 | 47.373 | 83.84 | 139.8957 | 226.5333 | 361.0731 | 570.8586 | 899.1328 | 1409.0434 | 2209.3264 | 3473.7312 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.15726 | 0.2282 | 0.33579 | 0.50014 | 0.75278 | 1.1432 | 1.7496 | 2.6951 | 4.1746 | 6.4968 | 10.1512 | 15.9152 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034978 | 0.10591 | 0.21351 | 0.37786 | 0.6305 | 1.021 | 1.6273 | 2.5728 | 4.0523 | 6.3504 | 9.9572 | 15.6558 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.796 | 23.6064 | 47.5865 | 84.2179 | 140.5262 | 227.5543 | 362.7004 | 573.4314 | 903.1851 | 1415.3939 | 2219.2836 | 3489.387 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 18.8741 | 27.3877 | 40.3006 | 60.026 | 90.347 | 137.2102 | 209.9841 | 323.4591 | 501.0258 | 779.7317 | 1218.3314 | 1910.1106 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.198 | 12.7116 | 25.6245 | 45.3499 | 75.6709 | 122.5341 | 195.308 | 308.783 | 486.3497 | 762.1653 | 1195.0462 | 1878.975 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6592 | 3.8586 | 5.6779 | 8.457 | 12.7289 | 19.3314 | 29.5845 | 45.5719 | 70.5891 | 109.8557 | 171.6496 | 269.1138 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59146 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2637 | 27.5168 | 43.5042 | 68.5214 | 107.3808 | 168.369 | 264.7271 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.19586 | 0.28421 | 0.41821 | 0.62291 | 0.93756 | 1.4239 | 2.1791 | 3.3566 | 5.1993 | 8.0915 | 12.643 | 19.8219 | 27.7536 | 27.7536 | 27.7536 | 27.7536 | 27.7536 | 27.7536 | 27.7536 | 27.7536 | 27.7536 | 27.7536 |  | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.18229 | 0.24164 | 0.3231 | 0.43543 | 0.59096 | 0.80708 | 1.1084 | 1.5298 | 2.1206 | 2.9511 | 4.1208 | 5.7715 | 8.105 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043564 | 0.13191 | 0.26591 | 0.47061 | 0.78526 | 1.2716 | 2.0268 | 3.2043 | 5.047 | 7.9093 | 12.4014 | 19.4988 | 27.3182 | 27.1627 | 26.9466 | 26.6452 | 26.2239 | 25.633 | 24.8026 | 23.6329 | 21.9822 | 19.6487 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6291 | 38.2409 | 77.0871 | 136.4277 | 227.6436 | 368.6237 | 587.5519 | 928.9229 | 1463.1032 | 2292.8492 | 3595.1002 | 5652.5879 | 7919.3994 | 7874.3142 | 7811.6625 | 7724.3105 | 7602.1558 | 7430.8746 | 7190.1344 | 6851.0429 | 6372.5078 | 5696.0368
| TRUE | 4685 | 22008212 | WBE | WBE-ATS Line [Prev LV] | 66 | ATS Line [Prev LV] LINE | DISTANCE & DIR EF | Y | Schweitzer | SEL_311C | SEL 311C | SEL 300s | Digital |  | 0.016937 | 1 |  | 6.6 | 0.017308 | 4.0157e-07 | 0.017307 | 113.5831 | 0.066259 | 113.6493 | 49.1326 | 6.9249 | 0.055015 |  | 14.9721 | 0.15742 | 3.6523e-06 | 0.15741 | 1033.0517 | 0.60263 | 1033.6544 | 446.8673 | 62.9826 | 0.50037 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 33.9147 | 0.019784 | 33.9344 | 14.6705 | 2.0677 | 0.016427 |  | 169.7619 | 1544.0046 | 50.689 | 1493.3156 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021358 | 0.026432 | 0.032797 | 0.040794 | 0.050854 | 0.063527 | 0.079507 | 0.099681 | 0.12517 | 0.15742 | 0.19823 | 0.24994 | 0.31549 | 0.39864 | 0.5042 | 0.63826 | 0.80862 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 4.9554e-07 | 6.1325e-07 | 7.6093e-07 | 9.4647e-07 | 1.1799e-06 | 1.4739e-06 | 1.8447e-06 | 2.3128e-06 | 2.9042e-06 | 3.6523e-06 | 4.5993e-06 | 5.7989e-06 | 7.3198e-06 | 9.2491e-06 | 1.1698e-05 | 1.4809e-05 | 1.8761e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 209.4879 | 259.2503 | 321.6812 | 400.1181 | 498.7961 | 623.0923 | 779.8371 | 977.7116 | 1227.7538 | 1544.0046 | 1944.3318 | 2451.4812 | 3094.4179 | 3910.0388 | 4945.3573 | 6260.2939 | 7931.2373 | 9237.1313 | 9237.1313 | 9237.1313 | 9237.1313 | 9237.1313 | 9237.1313 | 9237.1313 | 9237.1313 | 9237.1313 | 9237.1313 | 9237.1313 | 9237.1313 | 9237.1313 |  | 43.9063 | 43.9063 | 43.9063 | 43.9063 | 43.9063 | 43.9063 | 43.9063 | 43.9063 | 43.9063 | 43.9063 | 43.9063 | 43.9063 | 43.9063 | 43.9063 | 43.9063 | 43.9063 | 43.9063 | 52.5531 | 69.6622 | 93.1478 | 125.5315 | 170.3672 | 232.6721 | 319.5407 | 441.0194 | 611.3525 | 850.7604 | 1187.9751 | 1663.8616 | 2336.5886 |  | 140.1627 | 173.4574 | 215.2282 | 267.7082 | 333.731 | 416.8942 | 521.7679 | 654.1604 | 821.4569 | 1033.0517 | 1300.8999 | 1640.2198 | 2070.3914 | 2616.1012 | 3308.8049 | 4188.5934 | 5306.5764 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 | 6180.3148 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 113.031 | 146.3257 | 188.0965 | 240.5765 | 306.5992 | 389.7625 | 494.6362 | 627.0287 | 794.3251 | 1005.92 | 1273.7681 | 1613.088 | 2043.2596 | 2588.9695 | 3281.6732 | 4161.4617 | 5279.4447 | 6147.8398 | 6137.2673 | 6122.7545 | 6102.743 | 6075.037 | 6036.5359 | 5982.8557 | 5907.7884 | 5802.5316 | 5654.5904 | 5446.2097 | 5152.1373 | 4736.428 |  | 0.081764 | 0.10119 | 0.12555 | 0.15617 | 0.19468 | 0.2432 | 0.30437 | 0.3816 | 0.4792 | 0.60263 | 0.75888 | 0.95682 | 1.2078 | 1.5261 | 1.9302 | 2.4434 | 3.0956 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 | 3.6053 |  | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.019784 | 0.02368 | 0.03139 | 0.041972 | 0.056564 | 0.076767 | 0.10484 | 0.14398 | 0.19872 | 0.27547 | 0.38335 | 0.5353 | 0.74973 | 1.0529 |  | 0.06198 | 0.081402 | 0.10577 | 0.13638 | 0.1749 | 0.22341 | 0.28459 | 0.36182 | 0.45941 | 0.58285 | 0.7391 | 0.93704 | 1.188 | 1.5063 | 1.9104 | 2.4236 | 3.0758 | 3.5816 | 3.5739 | 3.5633 | 3.5487 | 3.5285 | 3.5004 | 3.4613 | 3.4066 | 3.3298 | 3.2219 | 3.07 | 2.8556 | 2.5524 |  | 113.0929 | 146.4071 | 188.2022 | 240.7128 | 306.7741 | 389.9859 | 494.9208 | 627.3905 | 794.7845 | 1006.5029 | 1274.5072 | 1614.0251 | 2044.4476 | 2590.4758 | 3283.5836 | 4163.8853 | 5282.5205 | 6151.4214 | 6140.8412 | 6126.3178 | 6106.2917 | 6078.5655 | 6040.0363 | 5986.317 | 5911.195 | 5805.8615 | 5657.8123 | 5449.2797 | 5154.9928 | 4738.9804 |  | 60.6302 | 75.0325 | 93.1013 | 115.8025 | 144.362 | 180.336 | 225.7012 | 282.9702 | 355.3377 | 446.8673 | 562.7304 | 709.51 | 895.5894 | 1131.6471 | 1431.29 | 1811.8602 | 2295.4662 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 45.9597 | 60.362 | 78.4308 | 101.1321 | 129.6916 | 165.6655 | 211.0307 | 268.2997 | 340.6672 | 432.1968 | 548.0599 | 694.8395 | 880.9189 | 1116.9766 | 1416.6195 | 1797.1897 | 2280.7957 | 2655.8596 | 2650.1429 | 2642.2957 | 2631.4752 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 8.5454 | 10.5753 | 13.1219 | 16.3215 | 20.3467 | 25.417 | 31.8109 | 39.8825 | 50.0822 | 62.9826 | 79.3126 | 100.0001 | 126.2266 | 159.4972 | 201.7296 | 255.3681 | 323.5288 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 6.4777 | 8.5076 | 11.0542 | 14.2538 | 18.2791 | 23.3493 | 29.7432 | 37.8148 | 48.0145 | 60.9149 | 77.2449 | 97.9324 | 124.1589 | 157.4295 | 199.6619 | 253.3004 | 321.4611 | 374.3235 | 373.5178 | 372.4118 | 370.8867 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.06789 | 0.084016 | 0.10425 | 0.12967 | 0.16165 | 0.20193 | 0.25273 | 0.31685 | 0.39788 | 0.50037 | 0.63011 | 0.79446 | 1.0028 | 1.2671 | 1.6027 | 2.0288 | 2.5703 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 |  | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.019662 | 0.026063 | 0.03485 | 0.046966 | 0.063741 | 0.087051 | 0.11955 | 0.165 | 0.22873 | 0.3183 | 0.44447 | 0.62251 | 0.87421 |  | 0.051463 | 0.067589 | 0.087822 | 0.11324 | 0.14522 | 0.1855 | 0.2363 | 0.30042 | 0.38146 | 0.48394 | 0.61368 | 0.77803 | 0.98639 | 1.2507 | 1.5862 | 2.0124 | 2.5539 | 2.9739 | 2.9675 | 2.9587 | 2.9465 | 2.9298 | 2.9065 | 2.874 | 2.8285 | 2.7648 | 2.6752 | 2.549 | 2.371 | 2.1193 |  | 165.5818 | 215.3442 | 277.7751 | 356.212 | 454.89 | 579.1862 | 735.931 | 933.8055 | 1183.8477 | 1500.0985 | 1900.4257 | 2407.5751 | 3050.5118 | 3866.1327 | 4901.4512 | 6216.3878 | 7887.3312 | 9184.5785 | 9167.4694 | 9143.9839 | 9111.6003 | 9066.7647 | 9004.4601 | 8917.5918 | 8796.1137 | 8625.7812 | 8386.3743 | 8049.1609 | 7573.2762 | 6900.5519
| FALSE | 4686 | 22016103 | WBE | WBE-HCP | 66 | HCP LINE | DISTANCE & DIR EF | X | GE | GE_D30 | GE D30 | GE RELAYS | Digital |  | 0.15703 | 1 |  | 1.0927 | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.1523 |  | 5.2187 | 0.0096441 | 2.0745e-06 | 0.009642 | 50.6327 | 0.2282 | 50.8609 | 27.3877 | 3.8586 | 0.28421 |  | 0.0051679 | 1.1117e-06 | 0.0051668 | 27.1322 | 0.12228 | 27.2545 | 14.6761 | 2.0677 | 0.1523 |  | 44.1506 | 82.3915 | 44.1506 | 38.2409 |  | 0.15636 |  | 1.2776 | 1.4939 | 1.7467 | 2.0423 | 2.388 | 2.7921 | 3.2647 | 3.8172 | 4.4633 | 5.2187 | 6.1019 | 7.1346 | 8.3421 | 9.754 | 11.4048 | 13.335 | 15.5919 | 18.2308 | 21.3163 | 24.924 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0051679 | 0.0066462 | 0.0096441 | 0.014191 | 0.021137 | 0.031814 | 0.048316 | 0.073942 | 0.1139 | 0.17643 | 0.27457 | 0.42901 | 0.67261 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.1117e-06 | 1.4296e-06 | 2.0745e-06 | 3.0526e-06 | 4.5467e-06 | 6.8434e-06 | 1.0393e-05 | 1.5905e-05 | 2.4501e-05 | 3.7951e-05 | 5.9062e-05 | 9.2284e-05 | 0.00014468 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 0.00020258 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 56.7797 | 82.3915 | 121.2377 | 180.5783 | 271.7942 | 412.7743 | 631.7026 | 973.0736 | 1507.2539 | 2345.6948 | 3665.1501 | 5746.2541 | 8045.6296 | 8045.6296 | 8045.6296 | 8045.6296 | 8045.6296 | 8045.6296 | 8045.6296 | 8045.6296 | 8045.6296 | 8045.6296 |  | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 44.1506 | 52.8455 | 70.0499 | 93.6662 | 126.2302 | 171.3154 | 233.9671 | 321.3191 | 443.4738 | 614.755 | 855.4952 | 1194.5867 | 1673.1218 | 2349.5927 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 34.8933 | 50.6327 | 74.5052 | 110.9723 | 167.0279 | 253.6656 | 388.2054 | 597.9909 | 926.2651 | 1441.519 | 2252.3748 | 3531.2926 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 | 4944.3467 |  | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 27.1322 | 32.4756 | 43.0483 | 57.5615 | 77.5733 | 105.2799 | 143.7817 | 197.4629 | 272.5316 | 377.7904 | 525.7345 | 734.1192 | 1028.1972 | 1443.9145 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.761 | 23.5005 | 47.373 | 83.84 | 139.8957 | 226.5333 | 361.0731 | 570.8586 | 899.1328 | 1409.0434 | 2209.3264 | 3473.7312 | 4866.7735 | 4839.0669 | 4800.565 | 4746.8839 | 4671.8151 | 4566.5563 | 4418.6122 | 4210.2276 | 3916.1495 | 3500.4322 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.15726 | 0.2282 | 0.33579 | 0.50014 | 0.75278 | 1.1432 | 1.7496 | 2.6951 | 4.1746 | 6.4968 | 10.1512 | 15.9152 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 | 22.2837 |  | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.12228 | 0.14636 | 0.19401 | 0.25942 | 0.34961 | 0.47449 | 0.64801 | 0.88995 | 1.2283 | 1.7027 | 2.3694 | 3.3086 | 4.634 | 6.5076 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034978 | 0.10591 | 0.21351 | 0.37786 | 0.6305 | 1.021 | 1.6273 | 2.5728 | 4.0523 | 6.3504 | 9.9572 | 15.6558 | 21.9341 | 21.8092 | 21.6357 | 21.3937 | 21.0554 | 20.581 | 19.9142 | 18.9751 | 17.6497 | 15.7761 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.796 | 23.6064 | 47.5865 | 84.2179 | 140.5262 | 227.5543 | 362.7004 | 573.4314 | 903.1851 | 1415.3939 | 2219.2836 | 3489.387 | 4888.7075 | 4860.876 | 4822.2007 | 4768.2776 | 4692.8705 | 4587.1373 | 4438.5265 | 4229.2026 | 3933.7992 | 3516.2083 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 18.8741 | 27.3877 | 40.3006 | 60.026 | 90.347 | 137.2102 | 209.9841 | 323.4591 | 501.0258 | 779.7317 | 1218.3314 | 1910.1106 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 | 2674.4453 |  | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 14.6761 | 17.5664 | 23.2853 | 31.1356 | 41.9601 | 56.9469 | 77.7729 | 106.8096 | 147.415 | 204.3505 | 284.3749 | 397.0922 | 556.1619 | 781.0274 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.198 | 12.7116 | 25.6245 | 45.3499 | 75.6709 | 122.5341 | 195.308 | 308.783 | 486.3497 | 762.1653 | 1195.0462 | 1878.975 | 2632.4852 | 2617.4984 | 2596.6724 | 2567.6357 | 2527.0303 | 2470.0948 | 2390.0704 | 2277.3531 | 2118.2834 | 1893.4179 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.6592 | 3.8586 | 5.6779 | 8.457 | 12.7289 | 19.3314 | 29.5845 | 45.5719 | 70.5891 | 109.8557 | 171.6496 | 269.1138 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 | 376.8002 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3867 | 5.9117 | 8.0232 | 10.9574 | 15.0483 | 20.7692 | 28.7908 | 40.0653 | 55.946 | 78.3572 | 110.0383 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59146 | 1.7909 | 3.6102 | 6.3893 | 10.6612 | 17.2637 | 27.5168 | 43.5042 | 68.5214 | 107.3808 | 168.369 | 264.7271 | 370.8885 | 368.777 | 365.8429 | 361.7519 | 356.0311 | 348.0095 | 336.7349 | 320.8543 | 298.4431 | 266.762 |  | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.19586 | 0.28421 | 0.41821 | 0.62291 | 0.93756 | 1.4239 | 2.1791 | 3.3566 | 5.1993 | 8.0915 | 12.643 | 19.8219 | 27.7536 | 27.7536 | 27.7536 | 27.7536 | 27.7536 | 27.7536 | 27.7536 | 27.7536 | 27.7536 | 27.7536 |  | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.1523 | 0.18229 | 0.24164 | 0.3231 | 0.43543 | 0.59096 | 0.80708 | 1.1084 | 1.5298 | 2.1206 | 2.9511 | 4.1208 | 5.7715 | 8.105 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043564 | 0.13191 | 0.26591 | 0.47061 | 0.78526 | 1.2716 | 2.0268 | 3.2043 | 5.047 | 7.9093 | 12.4014 | 19.4988 | 27.3182 | 27.1627 | 26.9466 | 26.6452 | 26.2239 | 25.633 | 24.8026 | 23.6329 | 21.9822 | 19.6487 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6291 | 38.2409 | 77.0871 | 136.4277 | 227.6436 | 368.6237 | 587.5519 | 928.9229 | 1463.1032 | 2292.8492 | 3595.1002 | 5652.5879 | 7919.3994 | 7874.3142 | 7811.6625 | 7724.3105 | 7602.1558 | 7430.8746 | 7190.1344 | 6851.0429 | 6372.5078 | 5696.0368
| TRUE | 4687 | 22008211 | WBE | WBE-HCP | 66 | HCP LINE | DISTANCE & DIR EF | Y | Schweitzer | SEL_311C | SEL 311C | SEL 300s | Digital |  | 0.016937 | 1 |  | 6.6 | 0.017308 | 4.0157e-07 | 0.017307 | 90.8665 | 0.044172 | 90.9106 | 49.1326 | 6.9249 | 0.055015 |  | 15.598 | 0.17662 | 4.0979e-06 | 0.17662 | 927.2631 | 0.45077 | 927.7139 | 501.3829 | 70.6662 | 0.56141 |  | 0.0051679 | 1.199e-07 | 0.0051678 | 27.1317 | 0.013189 | 27.1449 | 14.6705 | 2.0677 | 0.016427 |  | 147.0232 | 1500.3243 | 43.8995 | 1456.4248 |  | 0.086007 |  | 7.1928 | 7.8388 | 8.5428 | 9.3101 | 10.1463 | 11.0575 | 12.0507 | 13.133 | 14.3125 | 15.598 | 16.9989 | 18.5257 | 20.1895 | 22.0028 | 23.979 | 26.1326 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021585 | 0.027005 | 0.033883 | 0.042625 | 0.053753 | 0.067937 | 0.086039 | 0.10917 | 0.13875 | 0.17662 | 0.22515 | 0.28739 | 0.36726 | 0.46984 | 0.60168 | 0.7712 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 5.0081e-07 | 6.2655e-07 | 7.8613e-07 | 9.8896e-07 | 1.2471e-06 | 1.5762e-06 | 1.9962e-06 | 2.5328e-06 | 3.2192e-06 | 4.0979e-06 | 5.2238e-06 | 6.6678e-06 | 8.521e-06 | 1.0901e-05 | 1.396e-05 | 1.7893e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 2.185e-05 | 183.3597 | 229.3959 | 287.8197 | 362.0808 | 456.6096 | 577.0989 | 730.8685 | 927.335 | 1178.6182 | 1500.3243 | 1912.5577 | 2441.2263 | 3119.7297 | 3991.1393 | 5111.0153 | 6551.0483 | 7999.8666 | 7999.8666 | 7999.8666 | 7999.8666 | 7999.8666 | 7999.8666 | 7999.8666 | 7999.8666 | 7999.8666 | 7999.8666 | 7999.8666 | 7999.8666 | 7999.8666 | 7999.8666 |  | 43.8995 | 43.8995 | 43.8995 | 43.8995 | 43.8995 | 43.8995 | 43.8995 | 43.8995 | 43.8995 | 43.8995 | 43.8995 | 43.8995 | 43.8995 | 43.8995 | 43.8995 | 43.8995 | 43.8995 | 52.545 | 69.6514 | 93.1334 | 125.5122 | 170.341 | 232.6363 | 319.4915 | 440.9514 | 611.2583 | 850.6292 | 1187.792 | 1663.6052 | 2336.2284 |  | 113.324 | 141.7762 | 177.8846 | 223.7811 | 282.2038 | 356.6712 | 451.7073 | 573.1318 | 728.4353 | 927.2631 | 1182.0406 | 1508.7799 | 1928.1233 | 2466.6908 | 3158.821 | 4048.8216 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 | 4944.2518 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.475 | 43.0475 | 57.5603 | 77.5718 | 105.2778 | 143.7789 | 197.4591 | 272.5264 | 377.7832 | 525.7244 | 734.1051 | 1028.1775 | 1443.8868 |  | 86.1922 | 114.6445 | 150.7528 | 196.6494 | 255.0721 | 329.5395 | 424.5756 | 546 | 701.3035 | 900.1314 | 1154.9088 | 1481.6481 | 1900.9916 | 2439.5591 | 3131.6893 | 4021.6899 | 4917.1201 | 4911.7769 | 4901.2043 | 4886.6915 | 4866.6801 | 4838.974 | 4800.4729 | 4746.7928 | 4671.7255 | 4566.4687 | 4418.5274 | 4210.1468 | 3916.0743 | 3500.3651 |  | 0.05509 | 0.068921 | 0.086474 | 0.10879 | 0.13719 | 0.17339 | 0.21959 | 0.27861 | 0.35411 | 0.45077 | 0.57462 | 0.73345 | 0.93731 | 1.1991 | 1.5356 | 1.9682 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 | 2.4035 |  | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.013189 | 0.015787 | 0.020926 | 0.027982 | 0.03771 | 0.051178 | 0.069894 | 0.09599 | 0.13248 | 0.18365 | 0.25557 | 0.35687 | 0.49982 | 0.70191 |  | 0.0419 | 0.055732 | 0.073285 | 0.095596 | 0.124 | 0.1602 | 0.2064 | 0.26542 | 0.34092 | 0.43758 | 0.56143 | 0.72027 | 0.92412 | 1.1859 | 1.5224 | 1.955 | 2.3903 | 2.3877 | 2.3826 | 2.3755 | 2.3658 | 2.3523 | 2.3336 | 2.3075 | 2.271 | 2.2199 | 2.148 | 2.0467 | 1.9037 | 1.7016 |  | 86.2341 | 114.7002 | 150.8261 | 196.745 | 255.1961 | 329.6997 | 424.782 | 546.2655 | 701.6445 | 900.569 | 1155.4703 | 1482.3684 | 1901.9157 | 2440.745 | 3133.2117 | 4023.6449 | 4919.5104 | 4914.1646 | 4903.5869 | 4889.067 | 4869.0459 | 4841.3263 | 4802.8065 | 4749.1003 | 4673.9965 | 4568.6886 | 4420.6754 | 4212.1934 | 3917.978 | 3502.0667 |  | 61.2757 | 76.6602 | 96.1844 | 121.0013 | 152.5912 | 192.8566 | 244.2438 | 309.8996 | 393.8741 | 501.3829 | 639.1442 | 815.8163 | 1042.5606 | 1333.7708 | 1708.0143 | 2189.2489 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 | 2673.4193 |  | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 14.6705 | 17.5596 | 23.2763 | 31.1236 | 41.944 | 56.9251 | 77.7431 | 106.7686 | 147.3584 | 204.2721 | 284.2658 | 396.9399 | 555.9485 | 780.7278 |  | 46.6052 | 61.9897 | 81.514 | 106.3308 | 137.9207 | 178.1862 | 229.5734 | 295.2291 | 379.2037 | 486.7124 | 624.4738 | 801.1458 | 1027.8901 | 1319.1004 | 1693.3439 | 2174.5784 | 2658.7488 | 2655.8596 | 2650.1429 | 2642.2957 | 2631.4752 | 2616.4942 | 2595.6762 | 2566.6507 | 2526.0608 | 2469.1472 | 2389.1535 | 2276.4794 | 2117.4707 | 1892.6915 |  | 8.6363 | 10.8047 | 13.5565 | 17.0542 | 21.5066 | 27.1817 | 34.4243 | 43.678 | 55.5136 | 70.6662 | 90.0826 | 114.9832 | 146.9411 | 187.985 | 240.7318 | 308.5582 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 | 376.7984 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 6.5687 | 8.737 | 11.4888 | 14.9865 | 19.4389 | 25.114 | 32.3566 | 41.6103 | 53.4459 | 68.5985 | 88.0149 | 112.9155 | 144.8734 | 185.9173 | 238.6641 | 306.4905 | 374.7307 | 374.3235 | 373.5178 | 372.4118 | 370.8867 | 368.7753 | 365.8411 | 361.7502 | 356.0294 | 348.0078 | 336.7333 | 320.8527 | 298.4416 | 266.7607 |  | 0.068612 | 0.085839 | 0.1077 | 0.13549 | 0.17086 | 0.21595 | 0.27349 | 0.347 | 0.44103 | 0.56141 | 0.71567 | 0.9135 | 1.1674 | 1.4935 | 1.9125 | 2.4514 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 | 2.9935 |  | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.016427 | 0.019662 | 0.026063 | 0.03485 | 0.046966 | 0.063741 | 0.087051 | 0.11955 | 0.165 | 0.22873 | 0.3183 | 0.44447 | 0.62251 | 0.87421 |  | 0.052185 | 0.069412 | 0.091274 | 0.11906 | 0.15443 | 0.19952 | 0.25706 | 0.33058 | 0.42461 | 0.54499 | 0.69924 | 0.89707 | 1.151 | 1.477 | 1.8961 | 2.4349 | 2.9771 | 2.9739 | 2.9675 | 2.9587 | 2.9465 | 2.9298 | 2.9065 | 2.874 | 2.8285 | 2.7648 | 2.6752 | 2.549 | 2.371 | 2.1193 |  | 139.4602 | 185.4963 | 243.9202 | 318.1813 | 412.7101 | 533.1994 | 686.969 | 883.4355 | 1134.7186 | 1456.4248 | 1868.6582 | 2397.3268 | 3075.8302 | 3947.2398 | 5067.1158 | 6507.1488 | 7955.9671 | 7947.3216 | 7930.2151 | 7906.7331 | 7874.3544 | 7829.5256 | 7767.2303 | 7680.3751 | 7558.9152 | 7388.6083 | 7149.2373 | 6812.0746 | 6336.2614 | 5663.6382
| TRUE | 4688 | 22008224 | WBE | Blank | 66 | TRANS NO.1 | DIFFERENTIAL | Y | Schweitzer | SEL_387E | SEL 387E | SEL 300s | Digital |  | 0.0068096 | 1 |  | 6.6 | 0.017308 | 1.6145e-07 | 0.017308 | 113.5829 | 0.026639 | 113.6096 | 49.1313 | 6.9249 | 0.022119 |  | 14.9721 | 0.15742 | 1.4684e-06 | 0.15742 | 1033.0503 | 0.24229 | 1033.2926 | 446.8549 | 62.9826 | 0.20118 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 33.9146 | 0.0079542 | 33.9226 | 14.6701 | 2.0677 | 0.0066045 |  | 169.6878 | 1543.3312 | 50.6669 | 1492.6643 |  | 0.081912 |  | 7.1634 | 7.7748 | 8.4385 | 9.1588 | 9.9406 | 10.7891 | 11.7101 | 12.7097 | 13.7946 | 14.9721 | 16.2501 | 17.6372 | 19.1427 | 20.7767 | 22.5502 | 24.4751 | 26.5643 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.021358 | 0.026432 | 0.032797 | 0.040794 | 0.050854 | 0.063527 | 0.079507 | 0.099681 | 0.12517 | 0.15742 | 0.19823 | 0.24994 | 0.31549 | 0.39864 | 0.5042 | 0.63826 | 0.80862 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 | 0.94176 |  | 1.9923e-07 | 2.4656e-07 | 3.0593e-07 | 3.8053e-07 | 4.7438e-07 | 5.9259e-07 | 7.4166e-07 | 9.2984e-07 | 1.1676e-06 | 1.4684e-06 | 1.8491e-06 | 2.3315e-06 | 2.9429e-06 | 3.7186e-06 | 4.7032e-06 | 5.9538e-06 | 7.5429e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 8.7849e-06 | 209.3965 | 259.1373 | 321.5409 | 399.9436 | 498.5785 | 622.8205 | 779.497 | 977.2852 | 1227.2183 | 1543.3312 | 1943.4838 | 2450.412 | 3093.0683 | 3908.3335 | 4943.2005 | 6257.5636 | 7927.7782 | 9233.1027 | 9233.1027 | 9233.1027 | 9233.1027 | 9233.1027 | 9233.1027 | 9233.1027 | 9233.1027 | 9233.1027 | 9233.1027 | 9233.1027 | 9233.1027 | 9233.1027 |  | 43.8841 | 43.8841 | 43.8841 | 43.8841 | 43.8841 | 43.8841 | 43.8841 | 43.8841 | 43.8841 | 43.8841 | 43.8841 | 43.8841 | 43.8841 | 43.8841 | 43.8841 | 43.8841 | 43.8841 | 52.5265 | 69.627 | 93.1007 | 125.4681 | 170.2811 | 232.5545 | 319.3791 | 440.7964 | 611.0434 | 850.3302 | 1187.3744 | 1663.0203 | 2335.4071 |  | 140.1625 | 173.4572 | 215.2279 | 267.7078 | 333.7305 | 416.8936 | 521.7672 | 654.1595 | 821.4557 | 1033.0503 | 1300.898 | 1640.2175 | 2070.3885 | 2616.0976 | 3308.8003 | 4188.5876 | 5306.5691 | 6180.3062 | 6180.3062 | 6180.3062 | 6180.3062 | 6180.3062 | 6180.3062 | 6180.3062 | 6180.3062 | 6180.3062 | 6180.3062 | 6180.3062 | 6180.3062 | 6180.3062 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 113.0308 | 146.3255 | 188.0962 | 240.5761 | 306.5988 | 389.7619 | 494.6355 | 627.0278 | 794.324 | 1005.9186 | 1273.7664 | 1613.0858 | 2043.2568 | 2588.9659 | 3281.6686 | 4161.4559 | 5279.4374 | 6147.8313 | 6137.2588 | 6122.746 | 6102.7346 | 6075.0285 | 6036.5275 | 5982.8474 | 5907.7802 | 5802.5236 | 5654.5825 | 5446.2022 | 5152.1301 | 4736.4214 |  | 0.032873 | 0.040682 | 0.050479 | 0.062787 | 0.078272 | 0.097777 | 0.12237 | 0.15342 | 0.19266 | 0.24229 | 0.30511 | 0.38469 | 0.48558 | 0.61357 | 0.77603 | 0.98238 | 1.2446 | 1.4495 | 1.4495 | 1.4495 | 1.4495 | 1.4495 | 1.4495 | 1.4495 | 1.4495 | 1.4495 | 1.4495 | 1.4495 | 1.4495 | 1.4495 |  | 0.0079542 | 0.0079542 | 0.0079542 | 0.0079542 | 0.0079542 | 0.0079542 | 0.0079542 | 0.0079542 | 0.0079542 | 0.0079542 | 0.0079542 | 0.0079542 | 0.0079542 | 0.0079542 | 0.0079542 | 0.0079542 | 0.0079542 | 0.0095207 | 0.01262 | 0.016875 | 0.022742 | 0.030864 | 0.042152 | 0.057889 | 0.079897 | 0.11075 | 0.15413 | 0.21522 | 0.30143 | 0.4233 |  | 0.024919 | 0.032728 | 0.042525 | 0.054833 | 0.070318 | 0.089823 | 0.11442 | 0.14547 | 0.18471 | 0.23433 | 0.29715 | 0.37674 | 0.47763 | 0.60562 | 0.76808 | 0.97442 | 1.2366 | 1.44 | 1.4369 | 1.4326 | 1.4268 | 1.4186 | 1.4074 | 1.3916 | 1.3696 | 1.3388 | 1.2954 | 1.2343 | 1.1481 | 1.0262 |  | 113.0557 | 146.3582 | 188.1387 | 240.631 | 306.6691 | 389.8517 | 494.7499 | 627.1733 | 794.5087 | 1006.153 | 1274.0635 | 1613.4625 | 2043.7344 | 2589.5715 | 3282.4367 | 4162.4303 | 5280.674 | 6149.2713 | 6138.6957 | 6124.1786 | 6104.1613 | 6076.4472 | 6037.9348 | 5984.239 | 5909.1498 | 5803.8623 | 5655.8779 | 5447.4365 | 5153.2782 | 4737.4477 |  | 60.6285 | 75.0304 | 93.0987 | 115.7993 | 144.358 | 180.331 | 225.6949 | 282.9624 | 355.3278 | 446.8549 | 562.7147 | 709.4903 | 895.5645 | 1131.6157 | 1431.2503 | 1811.8099 | 2295.4025 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 | 2673.3451 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 45.9584 | 60.3603 | 78.4286 | 101.1293 | 129.688 | 165.6609 | 211.0249 | 268.2923 | 340.6577 | 432.1848 | 548.0447 | 694.8203 | 880.8944 | 1116.9457 | 1416.5802 | 1797.1398 | 2280.7324 | 2655.786 | 2650.0694 | 2642.2224 | 2631.4022 | 2616.4216 | 2595.6042 | 2566.5794 | 2525.9907 | 2469.0787 | 2389.0872 | 2276.4162 | 2117.412 | 1892.639 |  | 8.5454 | 10.5753 | 13.1219 | 16.3215 | 20.3467 | 25.417 | 31.8109 | 39.8825 | 50.0822 | 62.9826 | 79.3126 | 100.0001 | 126.2266 | 159.4971 | 201.7295 | 255.368 | 323.5287 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 | 376.7983 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 6.4777 | 8.5076 | 11.0542 | 14.2538 | 18.279 | 23.3493 | 29.7432 | 37.8148 | 48.0145 | 60.9149 | 77.2449 | 97.9324 | 124.1589 | 157.4294 | 199.6618 | 253.3003 | 321.461 | 374.3234 | 373.5177 | 372.4117 | 370.8866 | 368.7751 | 365.841 | 361.7501 | 356.0292 | 348.0077 | 336.7332 | 320.8526 | 298.4415 | 266.7606 |  | 0.027295 | 0.033779 | 0.041913 | 0.052133 | 0.06499 | 0.081185 | 0.10161 | 0.12739 | 0.15997 | 0.20118 | 0.25334 | 0.31941 | 0.40319 | 0.50946 | 0.64435 | 0.81568 | 1.0334 | 1.2035 | 1.2035 | 1.2035 | 1.2035 | 1.2035 | 1.2035 | 1.2035 | 1.2035 | 1.2035 | 1.2035 | 1.2035 | 1.2035 | 1.2035 |  | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0079052 | 0.010479 | 0.014012 | 0.018883 | 0.025627 | 0.034999 | 0.048066 | 0.066339 | 0.091961 | 0.12797 | 0.1787 | 0.25028 | 0.35148 |  | 0.020691 | 0.027174 | 0.035309 | 0.045529 | 0.058386 | 0.074581 | 0.095004 | 0.12079 | 0.15336 | 0.19457 | 0.24673 | 0.31281 | 0.39658 | 0.50285 | 0.63775 | 0.80908 | 1.0268 | 1.1956 | 1.1931 | 1.1895 | 1.1847 | 1.1779 | 1.1685 | 1.1555 | 1.1372 | 1.1116 | 1.0756 | 1.0248 | 0.95326 | 0.85207 |  | 165.5125 | 215.2533 | 277.6569 | 356.0596 | 454.6945 | 578.9365 | 735.613 | 933.4012 | 1183.3343 | 1499.4472 | 1899.5998 | 2406.528 | 3049.1843 | 3864.4495 | 4899.3165 | 6213.6796 | 7883.8942 | 9180.5763 | 9163.4758 | 9140.0021 | 9107.6348 | 9062.8218 | 9000.5486 | 8913.724 | 8792.307 | 8622.0603 | 8382.7738 | 8045.7302 | 7570.085 | 6897.6993
| TRUE | 4689 | 22008223 | WBE | Blank | 66 | TRANS NO.1 | DIFFERENTIAL & REF | X | ABB | SPAD_346C | SPAD 346C | SPAD | Electronic |  | 0.066046 | 2190 |  | 5.5 | 0.0093284 | 0.0016267 | 0.0077017 | 74.742 | 357.8712 | 432.6132 | 35.7148 | 3.7485 | 222.859 |  | 11.7751 | 0.068685 | 0.011977 | 0.056708 | 550.3257 | 2635.0081 | 3185.3337 | 262.968 | 27.6006 | 1640.912 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 40.6979 | 0.10286 | 40.8007 | 14.6724 | 2.0677 | 0.064057 |  | 694.9354 | 5116.8143 | 57.6049 | 5059.2094 |  | 0.076124 |  | 5.935 | 6.4045 | 6.911 | 7.4577 | 8.0475 | 8.6841 | 9.3709 | 10.1121 | 10.912 | 11.7751 | 12.7064 | 13.7115 | 14.796 | 15.9663 | 17.2292 | 18.5919 | 20.0625 | 21.6493 | 23.3617 | 25.2095 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.011264 | 0.013642 | 0.016568 | 0.020172 | 0.024619 | 0.030112 | 0.036906 | 0.045319 | 0.055747 | 0.068685 | 0.084752 | 0.10472 | 0.12956 | 0.16048 | 0.199 | 0.24701 | 0.30689 | 0.38161 | 0.47489 | 0.59141 | 0.73701 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0019643 | 0.002379 | 0.0028891 | 0.0035176 | 0.0042931 | 0.005251 | 0.0064358 | 0.0079028 | 0.0097212 | 0.011977 | 0.014779 | 0.018262 | 0.022593 | 0.027985 | 0.034702 | 0.043074 | 0.053516 | 0.066545 | 0.082812 | 0.10313 | 0.12852 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 839.1619 | 1016.3144 | 1234.2523 | 1502.7609 | 1834.0319 | 2243.2633 | 2749.4119 | 3376.135 | 4152.9704 | 5116.8143 | 6313.7745 | 7801.4921 | 9652.0531 | 11955.6385 | 14825.1026 | 18401.7147 | 22862.3617 | 28428.5847 | 35377.9169 | 44058.1113 | 54904.9959 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 |  | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 52.7135 | 69.8749 | 93.4322 | 125.9148 | 170.8874 | 233.3825 | 320.5163 | 442.3658 | 613.219 | 853.3578 | 1191.602 | 1668.9415 | 2343.7223 |  | 90.2539 | 109.3071 | 132.7468 | 161.6255 | 197.2545 | 241.2684 | 295.7058 | 363.1114 | 446.6619 | 550.3257 | 679.0616 | 839.0692 | 1038.1015 | 1285.8576 | 1594.4754 | 1979.1486 | 2458.9019 | 3057.5625 | 3804.9799 | 4738.5556 | 5905.1641 | 6420.099 | 6420.099 | 6420.099 | 6420.099 | 6420.099 | 6420.099 | 6420.099 | 6420.099 | 6420.099 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 63.122 | 82.1751 | 105.6149 | 134.4936 | 170.1226 | 214.1364 | 268.5739 | 335.9795 | 419.53 | 523.1938 | 651.9297 | 811.9373 | 1010.9696 | 1258.7257 | 1567.3435 | 1952.0167 | 2431.77 | 3025.0873 | 3761.9321 | 4680.9949 | 5827.5918 | 6314.8205 | 6276.3191 | 6222.6386 | 6147.5708 | 6042.3133 | 5894.3711 | 5685.989 | 5391.9146 | 4976.2025 |  | 432.1436 | 523.3719 | 635.6034 | 773.8774 | 944.4722 | 1155.2142 | 1415.8658 | 1738.6097 | 2138.6569 | 2635.0081 | 3251.4072 | 4017.5377 | 4970.5219 | 6156.8002 | 7634.4894 | 9476.3388 | 11773.4401 | 14639.8804 | 18218.5809 | 22688.6243 | 28274.4491 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 |  | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.12312 | 0.16321 | 0.21823 | 0.2941 | 0.39914 | 0.54511 | 0.74863 | 1.0332 | 1.4323 | 1.9932 | 2.7832 | 3.8981 | 5.4742 |  | 432.0407 | 523.269 | 635.5006 | 773.7746 | 944.3693 | 1155.1114 | 1415.7629 | 1738.5068 | 2138.5541 | 2634.9052 | 3251.3043 | 4017.4349 | 4970.419 | 6156.6974 | 7634.3865 | 9476.236 | 11773.3373 | 14639.7572 | 18218.4177 | 22688.4061 | 28274.155 | 30739.6042 | 30739.4582 | 30739.2547 | 30738.9701 | 30738.571 | 30738.0101 | 30737.2201 | 30736.1052 | 30734.5291 |  | 495.1627 | 605.4442 | 741.1154 | 908.2682 | 1114.4919 | 1369.2478 | 1684.3369 | 2074.4863 | 2558.0841 | 3158.0989 | 3903.234 | 4829.3722 | 5981.3886 | 7415.4231 | 9201.73 | 11428.2527 | 14205.1072 | 17664.8446 | 21980.3498 | 27369.401 | 34101.7468 | 37054.4247 | 37015.7773 | 36961.8933 | 36886.5409 | 36780.8844 | 36632.3812 | 36423.2091 | 36128.0198 | 35710.7316 |  | 43.127 | 52.2314 | 63.4318 | 77.2313 | 94.2562 | 115.2878 | 141.3003 | 173.5094 | 213.4333 | 262.968 | 324.4833 | 400.9414 | 496.0471 | 614.4351 | 761.9052 | 945.7178 | 1174.9634 | 1461.0278 | 1818.1743 | 2264.2747 | 2821.7278 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 28.4545 | 37.5589 | 48.7594 | 62.5588 | 79.5838 | 100.6154 | 126.6278 | 158.837 | 198.7608 | 248.2956 | 309.8108 | 386.269 | 481.3747 | 599.7627 | 747.2328 | 931.0453 | 1160.291 | 1443.4658 | 1794.8948 | 2233.147 | 2779.7781 | 3010.8519 | 2990.0311 | 2961.0017 | 2920.4064 | 2863.485 | 2783.4806 | 2670.7914 | 2511.7613 | 2286.9518 |  | 4.5265 | 5.4821 | 6.6577 | 8.106 | 9.8929 | 12.1004 | 14.8306 | 18.2112 | 22.4015 | 27.6006 | 34.0571 | 42.082 | 52.0641 | 64.4899 | 79.9681 | 99.2607 | 123.3218 | 153.3466 | 190.832 | 237.6538 | 296.1629 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 2.4588 | 3.4144 | 4.59 | 6.0383 | 7.8253 | 10.0327 | 12.7629 | 16.1435 | 20.3338 | 25.5329 | 31.9894 | 40.0143 | 49.9964 | 62.4222 | 77.9004 | 97.193 | 121.2541 | 150.8717 | 187.5513 | 233.2671 | 290.2512 | 313.9654 | 311.0313 | 306.9403 | 301.2195 | 293.1979 | 281.9234 | 266.0428 | 243.6317 | 211.9507 |  | 269.111 | 325.922 | 395.8126 | 481.9206 | 588.156 | 719.3925 | 881.7093 | 1082.6933 | 1331.8167 | 1640.912 | 2024.7654 | 2501.8618 | 3095.3185 | 3834.0556 | 4754.2646 | 5901.2489 | 7331.7345 | 9116.7675 | 11345.3499 | 14129.0029 | 17607.4921 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 |  | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.076673 | 0.10163 | 0.1359 | 0.18315 | 0.24856 | 0.33946 | 0.4662 | 0.64343 | 0.89194 | 1.2412 | 1.7332 | 2.4275 | 3.409 |  | 269.0469 | 325.858 | 395.7485 | 481.8566 | 588.0919 | 719.3284 | 881.6453 | 1082.6292 | 1331.7527 | 1640.848 | 2024.7013 | 2501.7977 | 3095.2544 | 3833.9916 | 4754.2005 | 5901.1848 | 7331.6704 | 9116.6908 | 11345.2483 | 14128.867 | 17607.3089 | 19142.6307 | 19142.5398 | 19142.413 | 19142.2358 | 19141.9873 | 19141.638 | 19141.146 | 19140.4517 | 19139.4702 |  | 795.123 | 972.2755 | 1190.2133 | 1458.722 | 1789.9929 | 2199.2243 | 2705.3729 | 3332.0961 | 4108.9314 | 5072.7754 | 6269.7356 | 7757.4532 | 9608.0141 | 11911.5995 | 14781.0636 | 18357.6757 | 22818.3228 | 28375.8729 | 35308.0442 | 43964.682 | 54779.085 | 59521.8726 | 59459.3795 | 59372.2483 | 59250.4026 | 59079.5546 | 58839.4232 | 58501.1893 | 58023.8645 | 57349.1044
| TRUE | 4690 | 22008227 | WBE | Blank | 66 | TRANS NO.2 | DIFFERENTIAL | Y | Alstom | KBCH_120 | KBCH 120 | KBCH | Electronic |  | 0.0068096 | 2190 |  | 6.6 | 0.014726 | 0.00029678 | 0.014429 | 154.9351 | 130.5836 | 285.5188 | 43.4865 | 5.8949 | 40.6595 |  | 12.1996 | 0.075729 | 0.0015262 | 0.074203 | 796.7583 | 671.5301 | 1468.2885 | 223.6305 | 30.3145 | 209.0927 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.0066045 |  | 375.5596 | 1931.3262 | 71.0289 | 1860.2972 |  | 0.061434 |  | 7.0182 | 7.4628 | 7.9357 | 8.4385 | 8.9732 | 9.5417 | 10.1463 | 10.7891 | 11.4727 | 12.1996 | 12.9726 | 13.7946 | 14.6686 | 15.598 | 16.5863 | 17.6372 | 18.7547 | 19.943 | 21.2066 | 22.5502 | 23.979 | 25.4983 | 27.1139 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.017237 | 0.020209 | 0.023729 | 0.027904 | 0.032859 | 0.038742 | 0.045735 | 0.05405 | 0.063946 | 0.075729 | 0.089768 | 0.1065 | 0.12646 | 0.15027 | 0.1787 | 0.21265 | 0.25322 | 0.3017 | 0.35966 | 0.42899 | 0.51193 | 0.61118 | 0.73 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.00034738 | 0.00040727 | 0.00047823 | 0.00056237 | 0.00066222 | 0.00078079 | 0.00092171 | 0.0010893 | 0.0012887 | 0.0015262 | 0.0018091 | 0.0021464 | 0.0025486 | 0.0030286 | 0.0036015 | 0.0042857 | 0.0051032 | 0.0060803 | 0.0072484 | 0.0086456 | 0.010317 | 0.012317 | 0.014712 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 439.5899 | 515.3815 | 605.1748 | 711.6467 | 837.996 | 988.0475 | 1166.3749 | 1378.4503 | 1630.8215 | 1931.3262 | 2289.3485 | 2716.1267 | 3225.1228 | 3832.4657 | 4557.4843 | 5423.346 | 6457.8246 | 7694.2218 | 9172.474 | 10940.4813 | 13055.7042 | 15587.0807 | 18617.33 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 |  | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 52.5426 | 69.6483 | 93.1293 | 125.5066 | 170.3334 | 232.6258 | 319.4771 | 440.9316 | 611.2309 | 850.5911 | 1187.7387 | 1663.5306 | 2336.1237 |  | 181.3505 | 212.6179 | 249.6617 | 293.586 | 345.7108 | 407.6137 | 481.1818 | 568.6723 | 672.7867 | 796.7583 | 944.4586 | 1120.5236 | 1330.5072 | 1581.0634 | 1880.1659 | 2237.3726 | 2664.1412 | 3174.2103 | 3784.0554 | 4513.4374 | 5386.0613 | 6430.3673 | 7680.4805 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 154.2188 | 185.4862 | 222.53 | 266.4544 | 318.5791 | 380.482 | 454.0501 | 541.5407 | 645.655 | 769.6267 | 917.3269 | 1093.3919 | 1303.3756 | 1553.9317 | 1853.0342 | 2210.2409 | 2637.0095 | 3141.7354 | 3741.0079 | 4455.8771 | 5308.4897 | 6325.0896 | 7536.7017 | 8232.9156 | 8157.8484 | 8052.5917 | 7904.6507 | 7696.2703 | 7402.1983 | 6986.4896 |  | 152.8472 | 179.2003 | 210.4218 | 247.4425 | 291.3747 | 343.5482 | 405.5534 | 479.2929 | 567.0434 | 671.5301 | 796.016 | 944.4085 | 1121.3886 | 1332.5642 | 1584.6562 | 1885.7199 | 2245.4124 | 2675.3128 | 3189.3073 | 3804.0507 | 4539.5225 | 5419.6926 | 6473.3229 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 152.826 | 179.1791 | 210.4006 | 247.4213 | 291.3535 | 343.527 | 405.5322 | 479.2717 | 567.0222 | 671.5089 | 795.9948 | 944.3873 | 1121.3674 | 1332.543 | 1584.635 | 1885.6987 | 2245.3912 | 2675.2875 | 3189.2736 | 3804.0057 | 4539.4619 | 5419.6103 | 6473.2105 | 7105.2 | 7105.1413 | 7105.059 | 7104.9433 | 7104.7804 | 7104.5505 | 7104.2255 |  | 307.0448 | 364.6653 | 432.9305 | 513.8756 | 609.9326 | 724.009 | 859.5823 | 1020.8123 | 1212.6772 | 1441.1356 | 1713.3216 | 2037.7793 | 2424.7429 | 2886.4747 | 3437.6692 | 4095.9396 | 4882.4007 | 5817.0228 | 6930.2815 | 8259.8829 | 9847.9515 | 11744.6999 | 14009.9122 | 15338.1155 | 15262.9896 | 15157.6507 | 15009.594 | 14801.0507 | 14506.7488 | 14090.7151 |  | 50.9006 | 59.6766 | 70.0739 | 82.4024 | 97.0325 | 114.4072 | 135.0559 | 159.6124 | 188.8347 | 223.6305 | 265.0864 | 314.5035 | 373.4408 | 443.7657 | 527.7165 | 627.9756 | 747.7591 | 890.923 | 1062.0916 | 1266.8112 | 1511.7354 | 1804.8464 | 2155.7225 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 36.2306 | 45.0066 | 55.4038 | 67.7323 | 82.3625 | 99.7371 | 120.3859 | 144.9423 | 174.1647 | 208.9605 | 250.4163 | 299.8335 | 358.7707 | 429.0957 | 513.0464 | 613.3056 | 733.089 | 873.3639 | 1038.8159 | 1235.6885 | 1469.7925 | 1747.9229 | 2077.9816 | 2259.4337 | 2218.845 | 2161.9329 | 2081.9414 | 1969.2705 | 1810.2663 | 1585.4933 |  | 6.8999 | 8.0895 | 9.4989 | 11.1701 | 13.1534 | 15.5086 | 18.3077 | 21.6364 | 25.5977 | 30.3145 | 35.9341 | 42.6329 | 50.6222 | 60.1552 | 71.5352 | 85.1259 | 101.3633 | 120.7701 | 143.973 | 171.724 | 204.925 | 244.658 | 292.2214 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 4.8322 | 6.0218 | 7.4313 | 9.1025 | 11.0857 | 13.4409 | 16.24 | 19.5687 | 23.53 | 28.2468 | 33.8664 | 40.5652 | 48.5545 | 58.0875 | 69.4675 | 83.0582 | 99.2956 | 118.2952 | 140.6924 | 167.3374 | 199.0133 | 236.6348 | 281.2641 | 305.7046 | 299.9837 | 291.9622 | 280.6877 | 264.8071 | 242.396 | 210.7151 |  | 47.5917 | 55.7972 | 65.5185 | 77.0456 | 90.7246 | 106.9698 | 126.2762 | 149.2363 | 176.5589 | 209.0927 | 247.8535 | 294.0582 | 349.164 | 414.9173 | 493.4105 | 587.152 | 699.1486 | 833.0056 | 993.0468 | 1184.458 | 1413.46 | 1687.5164 | 2015.5827 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 |  | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0079052 | 0.010479 | 0.014012 | 0.018883 | 0.025627 | 0.034999 | 0.048066 | 0.066339 | 0.091961 | 0.12797 | 0.1787 | 0.25028 | 0.35148 |  | 47.5851 | 55.7905 | 65.5119 | 77.039 | 90.718 | 106.9632 | 126.2696 | 149.2297 | 176.5523 | 209.0861 | 247.8469 | 294.0516 | 349.1574 | 414.9107 | 493.4039 | 587.1454 | 699.142 | 832.9977 | 993.0363 | 1184.444 | 1413.4411 | 1687.4908 | 2015.5477 | 2212.3287 | 2212.3105 | 2212.2848 | 2212.2488 | 2212.1981 | 2212.1265 | 2212.0253 |  | 395.6926 | 471.4842 | 561.2776 | 667.7494 | 794.0988 | 944.1502 | 1122.4777 | 1334.553 | 1586.9242 | 1887.4289 | 2245.4513 | 2672.2295 | 3181.2255 | 3788.5685 | 4513.5871 | 5379.4487 | 6413.9273 | 7641.6795 | 9102.8261 | 10847.3527 | 12930.1984 | 15416.7485 | 18384.7056 | 20115.5825 | 19994.1288 | 19823.8306 | 19584.4719 | 19247.3264 | 18771.5376 | 18098.9488
| TRUE | 4691 | 22008225 | WBE | Blank | 66 | TRANS NO.2 | DIFFERENTIAL & REF | X | ABB | SPAD_346C | SPAD 346C | SPAD | Electronic |  | 0.066046 | 2190 |  | 5.5 | 0.0093284 | 0.0016267 | 0.0077017 | 74.742 | 357.8712 | 432.6132 | 35.7148 | 3.7485 | 222.859 |  | 11.7751 | 0.068685 | 0.011977 | 0.056708 | 550.3257 | 2635.0081 | 3185.3337 | 262.968 | 27.6006 | 1640.912 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 40.6979 | 0.10286 | 40.8007 | 14.6724 | 2.0677 | 0.064057 |  | 694.9354 | 5116.8143 | 57.6049 | 5059.2094 |  | 0.076124 |  | 5.935 | 6.4045 | 6.911 | 7.4577 | 8.0475 | 8.6841 | 9.3709 | 10.1121 | 10.912 | 11.7751 | 12.7064 | 13.7115 | 14.796 | 15.9663 | 17.2292 | 18.5919 | 20.0625 | 21.6493 | 23.3617 | 25.2095 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.011264 | 0.013642 | 0.016568 | 0.020172 | 0.024619 | 0.030112 | 0.036906 | 0.045319 | 0.055747 | 0.068685 | 0.084752 | 0.10472 | 0.12956 | 0.16048 | 0.199 | 0.24701 | 0.30689 | 0.38161 | 0.47489 | 0.59141 | 0.73701 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0019643 | 0.002379 | 0.0028891 | 0.0035176 | 0.0042931 | 0.005251 | 0.0064358 | 0.0079028 | 0.0097212 | 0.011977 | 0.014779 | 0.018262 | 0.022593 | 0.027985 | 0.034702 | 0.043074 | 0.053516 | 0.066545 | 0.082812 | 0.10313 | 0.12852 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 839.1619 | 1016.3144 | 1234.2523 | 1502.7609 | 1834.0319 | 2243.2633 | 2749.4119 | 3376.135 | 4152.9704 | 5116.8143 | 6313.7745 | 7801.4921 | 9652.0531 | 11955.6385 | 14825.1026 | 18401.7147 | 22862.3617 | 28428.5847 | 35377.9169 | 44058.1113 | 54904.9959 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 |  | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 52.7135 | 69.8749 | 93.4322 | 125.9148 | 170.8874 | 233.3825 | 320.5163 | 442.3658 | 613.219 | 853.3578 | 1191.602 | 1668.9415 | 2343.7223 |  | 90.2539 | 109.3071 | 132.7468 | 161.6255 | 197.2545 | 241.2684 | 295.7058 | 363.1114 | 446.6619 | 550.3257 | 679.0616 | 839.0692 | 1038.1015 | 1285.8576 | 1594.4754 | 1979.1486 | 2458.9019 | 3057.5625 | 3804.9799 | 4738.5556 | 5905.1641 | 6420.099 | 6420.099 | 6420.099 | 6420.099 | 6420.099 | 6420.099 | 6420.099 | 6420.099 | 6420.099 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 63.122 | 82.1751 | 105.6149 | 134.4936 | 170.1226 | 214.1364 | 268.5739 | 335.9795 | 419.53 | 523.1938 | 651.9297 | 811.9373 | 1010.9696 | 1258.7257 | 1567.3435 | 1952.0167 | 2431.77 | 3025.0873 | 3761.9321 | 4680.9949 | 5827.5918 | 6314.8205 | 6276.3191 | 6222.6386 | 6147.5708 | 6042.3133 | 5894.3711 | 5685.989 | 5391.9146 | 4976.2025 |  | 432.1436 | 523.3719 | 635.6034 | 773.8774 | 944.4722 | 1155.2142 | 1415.8658 | 1738.6097 | 2138.6569 | 2635.0081 | 3251.4072 | 4017.5377 | 4970.5219 | 6156.8002 | 7634.4894 | 9476.3388 | 11773.4401 | 14639.8804 | 18218.5809 | 22688.6243 | 28274.4491 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 |  | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.12312 | 0.16321 | 0.21823 | 0.2941 | 0.39914 | 0.54511 | 0.74863 | 1.0332 | 1.4323 | 1.9932 | 2.7832 | 3.8981 | 5.4742 |  | 432.0407 | 523.269 | 635.5006 | 773.7746 | 944.3693 | 1155.1114 | 1415.7629 | 1738.5068 | 2138.5541 | 2634.9052 | 3251.3043 | 4017.4349 | 4970.419 | 6156.6974 | 7634.3865 | 9476.236 | 11773.3373 | 14639.7572 | 18218.4177 | 22688.4061 | 28274.155 | 30739.6042 | 30739.4582 | 30739.2547 | 30738.9701 | 30738.571 | 30738.0101 | 30737.2201 | 30736.1052 | 30734.5291 |  | 495.1627 | 605.4442 | 741.1154 | 908.2682 | 1114.4919 | 1369.2478 | 1684.3369 | 2074.4863 | 2558.0841 | 3158.0989 | 3903.234 | 4829.3722 | 5981.3886 | 7415.4231 | 9201.73 | 11428.2527 | 14205.1072 | 17664.8446 | 21980.3498 | 27369.401 | 34101.7468 | 37054.4247 | 37015.7773 | 36961.8933 | 36886.5409 | 36780.8844 | 36632.3812 | 36423.2091 | 36128.0198 | 35710.7316 |  | 43.127 | 52.2314 | 63.4318 | 77.2313 | 94.2562 | 115.2878 | 141.3003 | 173.5094 | 213.4333 | 262.968 | 324.4833 | 400.9414 | 496.0471 | 614.4351 | 761.9052 | 945.7178 | 1174.9634 | 1461.0278 | 1818.1743 | 2264.2747 | 2821.7278 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 28.4545 | 37.5589 | 48.7594 | 62.5588 | 79.5838 | 100.6154 | 126.6278 | 158.837 | 198.7608 | 248.2956 | 309.8108 | 386.269 | 481.3747 | 599.7627 | 747.2328 | 931.0453 | 1160.291 | 1443.4658 | 1794.8948 | 2233.147 | 2779.7781 | 3010.8519 | 2990.0311 | 2961.0017 | 2920.4064 | 2863.485 | 2783.4806 | 2670.7914 | 2511.7613 | 2286.9518 |  | 4.5265 | 5.4821 | 6.6577 | 8.106 | 9.8929 | 12.1004 | 14.8306 | 18.2112 | 22.4015 | 27.6006 | 34.0571 | 42.082 | 52.0641 | 64.4899 | 79.9681 | 99.2607 | 123.3218 | 153.3466 | 190.832 | 237.6538 | 296.1629 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 2.4588 | 3.4144 | 4.59 | 6.0383 | 7.8253 | 10.0327 | 12.7629 | 16.1435 | 20.3338 | 25.5329 | 31.9894 | 40.0143 | 49.9964 | 62.4222 | 77.9004 | 97.193 | 121.2541 | 150.8717 | 187.5513 | 233.2671 | 290.2512 | 313.9654 | 311.0313 | 306.9403 | 301.2195 | 293.1979 | 281.9234 | 266.0428 | 243.6317 | 211.9507 |  | 269.111 | 325.922 | 395.8126 | 481.9206 | 588.156 | 719.3925 | 881.7093 | 1082.6933 | 1331.8167 | 1640.912 | 2024.7654 | 2501.8618 | 3095.3185 | 3834.0556 | 4754.2646 | 5901.2489 | 7331.7345 | 9116.7675 | 11345.3499 | 14129.0029 | 17607.4921 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 |  | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.076673 | 0.10163 | 0.1359 | 0.18315 | 0.24856 | 0.33946 | 0.4662 | 0.64343 | 0.89194 | 1.2412 | 1.7332 | 2.4275 | 3.409 |  | 269.0469 | 325.858 | 395.7485 | 481.8566 | 588.0919 | 719.3284 | 881.6453 | 1082.6292 | 1331.7527 | 1640.848 | 2024.7013 | 2501.7977 | 3095.2544 | 3833.9916 | 4754.2005 | 5901.1848 | 7331.6704 | 9116.6908 | 11345.2483 | 14128.867 | 17607.3089 | 19142.6307 | 19142.5398 | 19142.413 | 19142.2358 | 19141.9873 | 19141.638 | 19141.146 | 19140.4517 | 19139.4702 |  | 795.123 | 972.2755 | 1190.2133 | 1458.722 | 1789.9929 | 2199.2243 | 2705.3729 | 3332.0961 | 4108.9314 | 5072.7754 | 6269.7356 | 7757.4532 | 9608.0141 | 11911.5995 | 14781.0636 | 18357.6757 | 22818.3228 | 28375.8729 | 35308.0442 | 43964.682 | 54779.085 | 59521.8726 | 59459.3795 | 59372.2483 | 59250.4026 | 59079.5546 | 58839.4232 | 58501.1893 | 58023.8645 | 57349.1044
| TRUE | 4692 | 22004389 | WBE | Blank | 66 | TRANS NO.3 | GAS & T/C PROT | Blank | ASEA | GROUP_2920 | GROUP 2920 | GROUP 2000s | Electronic |  | 0.066046 | 2190 |  | 8.25 | 0.026286 | 0.0045837 | 0.021702 | 280.8119 | 2016.8282 | 2297.64 | 100.6375 | 10.5627 | 627.9749 |  | 16.0817 | 0.16378 | 0.028559 | 0.13522 | 1749.6419 | 12566.1611 | 14315.803 | 627.0376 | 65.8126 | 3912.6948 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 54.2638 | 0.20573 | 54.4695 | 14.6724 | 2.0677 | 0.064057 |  | 3036.8151 | 18921.348 | 71.2737 | 18850.0743 |  | 0.066747 |  | 8.8195 | 9.4282 | 10.079 | 10.7747 | 11.5184 | 12.3135 | 13.1634 | 14.072 | 15.0433 | 16.0817 | 17.1917 | 18.3783 | 19.6469 | 21.003 | 22.4528 | 24.0025 | 25.6593 | 27.4304 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.031378 | 0.037515 | 0.044918 | 0.053853 | 0.064647 | 0.077697 | 0.093482 | 0.11259 | 0.13573 | 0.16378 | 0.19778 | 0.23903 | 0.28909 | 0.34986 | 0.42368 | 0.51338 | 0.6224 | 0.75496 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0054718 | 0.006542 | 0.0078328 | 0.0093909 | 0.011273 | 0.013549 | 0.016301 | 0.019633 | 0.023669 | 0.028559 | 0.034489 | 0.041682 | 0.050411 | 0.061009 | 0.073882 | 0.089523 | 0.10853 | 0.13165 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 3625.1739 | 4334.2109 | 5189.4106 | 6221.7346 | 7468.812 | 8976.3895 | 10800.1002 | 13007.6197 | 15681.2944 | 18921.348 | 22849.7915 | 27615.1919 | 33398.4913 | 40420.1042 | 48948.5785 | 59311.1629 | 71906.7027 | 87221.3779 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 | 92572.7911 |  | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 44.1445 | 52.8382 | 70.0402 | 93.6533 | 126.2127 | 171.2918 | 233.9348 | 321.2747 | 443.4126 | 614.6701 | 855.3771 | 1194.4218 | 1672.8908 | 2349.2683 |  | 335.2169 | 400.781 | 479.8607 | 575.3188 | 690.6351 | 830.0396 | 998.6766 | 1202.8042 | 1450.0368 | 1749.6419 | 2112.902 | 2553.5547 | 3088.3318 | 3737.6148 | 4526.236 | 5484.4559 | 6649.1554 | 8065.2911 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 | 8560.1321 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 308.085 | 373.6491 | 452.7287 | 548.1869 | 663.5032 | 802.9077 | 971.5447 | 1175.6723 | 1422.9049 | 1722.51 | 2085.7701 | 2526.4228 | 3061.1999 | 3710.4828 | 4499.104 | 5457.3239 | 6622.0234 | 8032.8159 | 8517.0843 | 8502.5713 | 8482.5598 | 8454.8535 | 8416.3522 | 8362.6716 | 8287.6038 | 8182.3464 | 8034.4041 | 7826.022 | 7531.9476 | 7116.2356 |  | 2407.5726 | 2878.4625 | 3446.423 | 4132.0164 | 4960.233 | 5961.4545 | 7172.6284 | 8638.6997 | 10414.3569 | 12566.1611 | 15175.1429 | 18339.9697 | 22180.8097 | 26844.0461 | 32508.0285 | 39390.0912 | 47755.1179 | 57925.9934 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 | 61480.0066 |  | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.20573 | 0.24625 | 0.32641 | 0.43646 | 0.5882 | 0.79828 | 1.0902 | 1.4973 | 2.0665 | 2.8646 | 3.9864 | 5.5664 | 7.7963 | 10.9484 |  | 2407.3668 | 2878.2568 | 3446.2173 | 4131.8106 | 4960.0272 | 5961.2488 | 7172.4227 | 8638.494 | 10414.1511 | 12565.9553 | 15174.9371 | 18339.7639 | 22180.604 | 26843.8404 | 32507.8228 | 39389.8855 | 47754.9122 | 57925.7472 | 61479.6802 | 61479.5702 | 61479.4184 | 61479.2083 | 61478.9164 | 61478.5094 | 61477.9402 | 61477.142 | 61476.0203 | 61474.4402 | 61472.2104 | 61469.0582 |  | 2715.4519 | 3251.9059 | 3898.946 | 4679.9976 | 5623.5304 | 6764.1564 | 8143.9674 | 9814.1663 | 11837.056 | 14288.4654 | 17260.7072 | 20866.1868 | 25241.8039 | 30554.3232 | 37006.9268 | 44847.2094 | 54376.9356 | 65958.5631 | 69996.7645 | 69982.1415 | 69961.9782 | 69934.0618 | 69895.2686 | 69841.181 | 69765.544 | 69659.4884 | 69510.4244 | 69300.4622 | 69004.158 | 68585.2938 |  | 120.1352 | 143.6321 | 171.9727 | 206.1831 | 247.5102 | 297.47 | 357.9063 | 431.0616 | 519.6649 | 627.0376 | 757.2229 | 915.1443 | 1106.798 | 1339.4883 | 1622.1148 | 1965.5222 | 2382.9278 | 2890.4433 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 105.4628 | 128.9597 | 157.3003 | 191.5106 | 232.8377 | 282.7976 | 343.2338 | 416.3892 | 504.9925 | 612.3652 | 742.5505 | 900.4719 | 1092.1255 | 1324.8159 | 1607.4424 | 1950.8497 | 2368.2554 | 2872.8813 | 3044.5052 | 3036.6568 | 3025.835 | 3010.8519 | 2990.0311 | 2961.0017 | 2920.4064 | 2863.485 | 2783.4806 | 2670.7914 | 2511.7613 | 2286.9518 |  | 12.6092 | 15.0753 | 18.0499 | 21.6406 | 25.9782 | 31.2219 | 37.5651 | 45.2434 | 54.543 | 65.8126 | 79.4766 | 96.0517 | 116.1673 | 140.59 | 170.2539 | 206.2973 | 250.1074 | 303.3752 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 10.5415 | 13.0076 | 15.9822 | 19.5729 | 23.9105 | 29.1542 | 35.4974 | 43.1757 | 52.4753 | 63.7449 | 77.4089 | 93.984 | 114.0996 | 138.5223 | 168.1863 | 204.2296 | 248.0397 | 300.9003 | 318.7079 | 317.6019 | 316.0769 | 313.9654 | 311.0313 | 306.9403 | 301.2195 | 293.1979 | 281.9234 | 266.0428 | 243.6317 | 211.9507 |  | 749.64 | 896.2598 | 1073.1043 | 1286.5758 | 1544.4556 | 1856.2035 | 2233.3238 | 2689.8108 | 3242.6928 | 3912.6948 | 4725.0471 | 5710.4715 | 6906.3844 | 8358.365 | 10121.9453 | 12264.7963 | 14869.3942 | 18036.2748 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 |  | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.076673 | 0.10163 | 0.1359 | 0.18315 | 0.24856 | 0.33946 | 0.4662 | 0.64343 | 0.89194 | 1.2412 | 1.7332 | 2.4275 | 3.409 |  | 749.5759 | 896.1958 | 1073.0402 | 1286.5118 | 1544.3915 | 1856.1394 | 2233.2597 | 2689.7467 | 3242.6288 | 3912.6308 | 4724.983 | 5710.4074 | 6906.3204 | 8358.3009 | 10121.8812 | 12264.7323 | 14869.3302 | 18036.1982 | 19142.7776 | 19142.7433 | 19142.6961 | 19142.6307 | 19142.5398 | 19142.413 | 19142.2358 | 19141.9873 | 19141.638 | 19141.146 | 19140.4517 | 19139.4702 |  | 3581.032 | 4290.069 | 5145.2687 | 6177.5928 | 7424.6702 | 8932.2476 | 10755.9584 | 12963.4778 | 15637.1525 | 18877.2062 | 22805.6496 | 27571.0501 | 33354.3494 | 40375.9624 | 48904.4367 | 59267.021 | 71862.5608 | 87168.5429 | 92502.7552 | 92479.1436 | 92446.5861 | 92401.5098 | 92338.8707 | 92251.536 | 92129.4056 | 91958.1586 | 91717.4663 | 91378.4424 | 90900.0027 | 90223.6665
| TRUE | 4693 | 22008228 | WBE | Blank | 66 | TRANS NO.3 | DIFFERENTIAL | Y | ASEA | GROUP_3058 | GROUP 3058 | GROUP 3000s | Electronic |  | 0.0068096 | 2190 |  | 9.9 | 0.042792 | 0.00086241 | 0.04193 | 450.2224 | 379.4599 | 829.6823 | 126.3664 | 17.1297 | 118.1515 |  | 20.1542 | 0.31092 | 0.006266 | 0.30465 | 3271.1945 | 2757.0538 | 6028.2483 | 918.1441 | 124.46 | 858.4571 |  | 0.0051679 | 4.8207e-08 | 0.0051679 | 54.2634 | 0.021211 | 54.2846 | 14.6701 | 2.0677 | 0.0066045 |  | 1091.3299 | 7929.3096 | 71.0289 | 7858.2806 |  | 0.071088 |  | 10.6294 | 11.4125 | 12.2533 | 13.1561 | 14.1254 | 15.1661 | 16.2834 | 17.4831 | 18.7712 | 20.1542 | 21.639 | 23.2333 | 24.945 | 26.7829 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.051896 | 0.063029 | 0.076653 | 0.093338 | 0.11379 | 0.13887 | 0.16964 | 0.20743 | 0.25385 | 0.31092 | 0.38109 | 0.46742 | 0.57368 | 0.7045 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0010459 | 0.0012703 | 0.0015448 | 0.0018811 | 0.0022932 | 0.0027986 | 0.0034188 | 0.0041804 | 0.005116 | 0.006266 | 0.0076802 | 0.0094201 | 0.011562 | 0.014198 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 0.016149 | 1323.5199 | 1607.4358 | 1954.8843 | 2380.4063 | 2901.9173 | 3541.4961 | 4326.3611 | 5290.075 | 6474.0342 | 7929.3096 | 9718.9205 | 11920.6468 | 14630.5039 | 17967.0396 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 | 20435.0577 |  | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 43.8975 | 52.5426 | 69.6483 | 93.1293 | 125.5066 | 170.3334 | 232.6258 | 319.4771 | 440.9316 | 611.2309 | 850.5911 | 1187.7387 | 1663.5306 | 2336.1237 |  | 546.0111 | 663.1391 | 806.4771 | 982.024 | 1197.1705 | 1461.0254 | 1784.8173 | 2182.3923 | 2670.8284 | 3271.1945 | 4009.489 | 4917.7994 | 6035.7366 | 7412.2066 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 | 8430.3744 |  | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 27.1317 | 32.4749 | 43.0474 | 57.5603 | 77.5717 | 105.2777 | 143.7787 | 197.4588 | 272.526 | 377.7826 | 525.7237 | 734.1041 | 1028.1761 | 1443.8848 |  | 518.8794 | 636.0074 | 779.3454 | 954.8923 | 1170.0389 | 1433.8937 | 1757.6856 | 2155.2606 | 2643.6967 | 3244.0628 | 3982.3573 | 4890.6678 | 6008.6049 | 7385.0749 | 8403.2427 | 8403.2427 | 8403.2427 | 8397.8994 | 8387.3269 | 8372.8141 | 8352.8027 | 8325.0967 | 8286.5956 | 8232.9156 | 8157.8484 | 8052.5917 | 7904.6507 | 7696.2703 | 7402.1983 | 6986.4896 |  | 460.1934 | 558.9121 | 679.7214 | 827.6772 | 1009.0087 | 1231.3929 | 1504.2937 | 1839.381 | 2251.0486 | 2757.0538 | 3379.309 | 4144.8584 | 5087.0869 | 6247.2142 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 | 7105.3543 |  | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.021211 | 0.025389 | 0.033654 | 0.045 | 0.060645 | 0.082305 | 0.1124 | 0.15437 | 0.21306 | 0.29535 | 0.411 | 0.57391 | 0.80382 | 1.1288 |  | 460.1721 | 558.8909 | 679.7002 | 827.6559 | 1008.9875 | 1231.3717 | 1504.2725 | 1839.3598 | 2251.0273 | 2757.0326 | 3379.2878 | 4144.8371 | 5087.0657 | 6247.193 | 7105.3331 | 7105.3331 | 7105.3331 | 7105.3289 | 7105.3207 | 7105.3093 | 7105.2937 | 7105.272 | 7105.2419 | 7105.2 | 7105.1413 | 7105.059 | 7104.9433 | 7104.7804 | 7104.5505 | 7104.2255 |  | 979.0515 | 1194.8983 | 1459.0456 | 1782.5482 | 2179.0263 | 2665.2654 | 3261.9581 | 3994.6204 | 4894.724 | 6001.0954 | 7361.6451 | 9035.5049 | 11095.6706 | 13632.2679 | 15508.5758 | 15508.5758 | 15508.5758 | 15503.2284 | 15492.6476 | 15478.1234 | 15458.0964 | 15430.3687 | 15391.8376 | 15338.1155 | 15262.9896 | 15157.6507 | 15009.594 | 14801.0507 | 14506.7488 | 14090.7151 |  | 153.2519 | 186.1269 | 226.3583 | 275.63 | 336.0164 | 410.074 | 500.9544 | 612.544 | 749.636 | 918.1441 | 1125.3652 | 1380.3057 | 1694.0833 | 2080.4247 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 | 2366.1994 |  | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 14.6701 | 17.5591 | 23.2757 | 31.1227 | 41.9429 | 56.9235 | 77.7409 | 106.7656 | 147.3544 | 204.2664 | 284.2579 | 396.9289 | 555.9331 | 780.7061 |  | 138.5819 | 171.4568 | 211.6883 | 260.96 | 321.3464 | 395.4039 | 486.2844 | 597.8739 | 734.966 | 903.474 | 1110.6952 | 1365.6357 | 1679.4132 | 2065.7546 | 2351.5293 | 2351.5293 | 2351.5293 | 2348.6402 | 2342.9237 | 2335.0766 | 2324.2565 | 2309.2759 | 2288.4584 | 2259.4337 | 2218.845 | 2161.9329 | 2081.9414 | 1969.2705 | 1810.2663 | 1585.4933 |  | 20.7742 | 25.2306 | 30.6843 | 37.3633 | 45.5491 | 55.588 | 67.9074 | 83.0341 | 101.6177 | 124.46 | 152.5501 | 187.1089 | 229.6433 | 282.0143 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 | 320.7528 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3568 | 110.0377 |  | 18.7065 | 23.1629 | 28.6166 | 35.2956 | 43.4814 | 53.5203 | 65.8397 | 80.9664 | 99.5501 | 122.3924 | 150.4824 | 185.0412 | 227.5757 | 279.9466 | 318.6851 | 318.6851 | 318.6851 | 318.2779 | 317.4722 | 316.3662 | 314.8411 | 312.7296 | 309.7955 | 305.7046 | 299.9837 | 291.9622 | 280.6877 | 264.8071 | 242.396 | 210.7151 |  | 143.2893 | 174.0271 | 211.6432 | 257.7118 | 314.1726 | 383.4158 | 468.3883 | 572.7236 | 700.9035 | 858.4571 | 1052.2072 | 1290.5744 | 1583.9538 | 1945.1798 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 | 2212.3768 |  | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0066045 | 0.0079052 | 0.010479 | 0.014012 | 0.018883 | 0.025627 | 0.034999 | 0.048066 | 0.066339 | 0.091961 | 0.12797 | 0.1787 | 0.25028 | 0.35148 |  | 143.2827 | 174.0205 | 211.6366 | 257.7052 | 314.166 | 383.4092 | 468.3816 | 572.717 | 700.8969 | 858.4505 | 1052.2006 | 1290.5678 | 1583.9472 | 1945.1732 | 2212.3702 | 2212.3702 | 2212.3702 | 2212.3689 | 2212.3663 | 2212.3628 | 2212.3579 | 2212.3512 | 2212.3418 | 2212.3287 | 2212.3105 | 2212.2848 | 2212.2488 | 2212.1981 | 2212.1265 | 2212.0253 |  | 1279.6226 | 1563.5386 | 1910.987 | 2336.5091 | 2858.02 | 3497.5989 | 4282.4639 | 5246.1777 | 6430.137 | 7885.4123 | 9675.0233 | 11876.7496 | 14586.6067 | 17923.1423 | 20391.1604 | 20391.1604 | 20391.1604 | 20382.5154 | 20365.4098 | 20341.929 | 20309.5519 | 20264.7254 | 20202.4333 | 20115.5825 | 19994.1288 | 19823.8306 | 19584.4719 | 19247.3264 | 18771.5376 | 18098.9488
| TRUE | 4694 | 22008226 | WBE | Blank | 66 | TRANS NO.3 | DIFFERENTIAL | X | ABB | SPAD_346C | SPAD 346C | SPAD | Electronic |  | 0.066046 | 2190 |  | 5.5 | 0.0093284 | 0.0016267 | 0.0077017 | 74.742 | 357.8712 | 432.6132 | 35.7148 | 3.7485 | 222.859 |  | 11.7751 | 0.068685 | 0.011977 | 0.056708 | 550.3257 | 2635.0081 | 3185.3337 | 262.968 | 27.6006 | 1640.912 |  | 0.0051679 | 4.6757e-07 | 0.0051675 | 40.6979 | 0.10286 | 40.8007 | 14.6724 | 2.0677 | 0.064057 |  | 694.9354 | 5116.8143 | 57.6049 | 5059.2094 |  | 0.076124 |  | 5.935 | 6.4045 | 6.911 | 7.4577 | 8.0475 | 8.6841 | 9.3709 | 10.1121 | 10.912 | 11.7751 | 12.7064 | 13.7115 | 14.796 | 15.9663 | 17.2292 | 18.5919 | 20.0625 | 21.6493 | 23.3617 | 25.2095 | 27.2035 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 0.011264 | 0.013642 | 0.016568 | 0.020172 | 0.024619 | 0.030112 | 0.036906 | 0.045319 | 0.055747 | 0.068685 | 0.084752 | 0.10472 | 0.12956 | 0.16048 | 0.199 | 0.24701 | 0.30689 | 0.38161 | 0.47489 | 0.59141 | 0.73701 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 | 0.80128 |  | 0.0019643 | 0.002379 | 0.0028891 | 0.0035176 | 0.0042931 | 0.005251 | 0.0064358 | 0.0079028 | 0.0097212 | 0.011977 | 0.014779 | 0.018262 | 0.022593 | 0.027985 | 0.034702 | 0.043074 | 0.053516 | 0.066545 | 0.082812 | 0.10313 | 0.12852 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 0.13973 | 839.1619 | 1016.3144 | 1234.2523 | 1502.7609 | 1834.0319 | 2243.2633 | 2749.4119 | 3376.135 | 4152.9704 | 5116.8143 | 6313.7745 | 7801.4921 | 9652.0531 | 11955.6385 | 14825.1026 | 18401.7147 | 22862.3617 | 28428.5847 | 35377.9169 | 44058.1113 | 54904.9959 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 | 59692.7548 |  | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 44.0403 | 52.7135 | 69.8749 | 93.4322 | 125.9148 | 170.8874 | 233.3825 | 320.5163 | 442.3658 | 613.219 | 853.3578 | 1191.602 | 1668.9415 | 2343.7223 |  | 90.2539 | 109.3071 | 132.7468 | 161.6255 | 197.2545 | 241.2684 | 295.7058 | 363.1114 | 446.6619 | 550.3257 | 679.0616 | 839.0692 | 1038.1015 | 1285.8576 | 1594.4754 | 1979.1486 | 2458.9019 | 3057.5625 | 3804.9799 | 4738.5556 | 5905.1641 | 6420.099 | 6420.099 | 6420.099 | 6420.099 | 6420.099 | 6420.099 | 6420.099 | 6420.099 | 6420.099 |  | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 27.1319 | 32.4752 | 43.0478 | 57.5607 | 77.5723 | 105.2786 | 143.7799 | 197.4604 | 272.5282 | 377.7857 | 525.7279 | 734.11 | 1028.1844 | 1443.8965 |  | 63.122 | 82.1751 | 105.6149 | 134.4936 | 170.1226 | 214.1364 | 268.5739 | 335.9795 | 419.53 | 523.1938 | 651.9297 | 811.9373 | 1010.9696 | 1258.7257 | 1567.3435 | 1952.0167 | 2431.77 | 3025.0873 | 3761.9321 | 4680.9949 | 5827.5918 | 6314.8205 | 6276.3191 | 6222.6386 | 6147.5708 | 6042.3133 | 5894.3711 | 5685.989 | 5391.9146 | 4976.2025 |  | 432.1436 | 523.3719 | 635.6034 | 773.8774 | 944.4722 | 1155.2142 | 1415.8658 | 1738.6097 | 2138.6569 | 2635.0081 | 3251.4072 | 4017.5377 | 4970.5219 | 6156.8002 | 7634.4894 | 9476.3388 | 11773.4401 | 14639.8804 | 18218.5809 | 22688.6243 | 28274.4491 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 | 30740.0033 |  | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.10286 | 0.12312 | 0.16321 | 0.21823 | 0.2941 | 0.39914 | 0.54511 | 0.74863 | 1.0332 | 1.4323 | 1.9932 | 2.7832 | 3.8981 | 5.4742 |  | 432.0407 | 523.269 | 635.5006 | 773.7746 | 944.3693 | 1155.1114 | 1415.7629 | 1738.5068 | 2138.5541 | 2634.9052 | 3251.3043 | 4017.4349 | 4970.419 | 6156.6974 | 7634.3865 | 9476.236 | 11773.3373 | 14639.7572 | 18218.4177 | 22688.4061 | 28274.155 | 30739.6042 | 30739.4582 | 30739.2547 | 30738.9701 | 30738.571 | 30738.0101 | 30737.2201 | 30736.1052 | 30734.5291 |  | 495.1627 | 605.4442 | 741.1154 | 908.2682 | 1114.4919 | 1369.2478 | 1684.3369 | 2074.4863 | 2558.0841 | 3158.0989 | 3903.234 | 4829.3722 | 5981.3886 | 7415.4231 | 9201.73 | 11428.2527 | 14205.1072 | 17664.8446 | 21980.3498 | 27369.401 | 34101.7468 | 37054.4247 | 37015.7773 | 36961.8933 | 36886.5409 | 36780.8844 | 36632.3812 | 36423.2091 | 36128.0198 | 35710.7316 |  | 43.127 | 52.2314 | 63.4318 | 77.2313 | 94.2562 | 115.2878 | 141.3003 | 173.5094 | 213.4333 | 262.968 | 324.4833 | 400.9414 | 496.0471 | 614.4351 | 761.9052 | 945.7178 | 1174.9634 | 1461.0278 | 1818.1743 | 2264.2747 | 2821.7278 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 | 3067.7846 |  | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 14.6724 | 17.562 | 23.2795 | 31.1278 | 41.9497 | 56.9327 | 77.7535 | 106.783 | 147.3783 | 204.2996 | 284.3041 | 396.9933 | 556.0233 | 780.8328 |  | 28.4545 | 37.5589 | 48.7594 | 62.5588 | 79.5838 | 100.6154 | 126.6278 | 158.837 | 198.7608 | 248.2956 | 309.8108 | 386.269 | 481.3747 | 599.7627 | 747.2328 | 931.0453 | 1160.291 | 1443.4658 | 1794.8948 | 2233.147 | 2779.7781 | 3010.8519 | 2990.0311 | 2961.0017 | 2920.4064 | 2863.485 | 2783.4806 | 2670.7914 | 2511.7613 | 2286.9518 |  | 4.5265 | 5.4821 | 6.6577 | 8.106 | 9.8929 | 12.1004 | 14.8306 | 18.2112 | 22.4015 | 27.6006 | 34.0571 | 42.082 | 52.0641 | 64.4899 | 79.9681 | 99.2607 | 123.3218 | 153.3466 | 190.832 | 237.6538 | 296.1629 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 | 321.9886 |  | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0483 | 20.7691 | 28.7907 | 40.0652 | 55.9458 | 78.3569 | 110.0379 |  | 2.4588 | 3.4144 | 4.59 | 6.0383 | 7.8253 | 10.0327 | 12.7629 | 16.1435 | 20.3338 | 25.5329 | 31.9894 | 40.0143 | 49.9964 | 62.4222 | 77.9004 | 97.193 | 121.2541 | 150.8717 | 187.5513 | 233.2671 | 290.2512 | 313.9654 | 311.0313 | 306.9403 | 301.2195 | 293.1979 | 281.9234 | 266.0428 | 243.6317 | 211.9507 |  | 269.111 | 325.922 | 395.8126 | 481.9206 | 588.156 | 719.3925 | 881.7093 | 1082.6933 | 1331.8167 | 1640.912 | 2024.7654 | 2501.8618 | 3095.3185 | 3834.0556 | 4754.2646 | 5901.2489 | 7331.7345 | 9116.7675 | 11345.3499 | 14129.0029 | 17607.4921 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 | 19142.8792 |  | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.064057 | 0.076673 | 0.10163 | 0.1359 | 0.18315 | 0.24856 | 0.33946 | 0.4662 | 0.64343 | 0.89194 | 1.2412 | 1.7332 | 2.4275 | 3.409 |  | 269.0469 | 325.858 | 395.7485 | 481.8566 | 588.0919 | 719.3284 | 881.6453 | 1082.6292 | 1331.7527 | 1640.848 | 2024.7013 | 2501.7977 | 3095.2544 | 3833.9916 | 4754.2005 | 5901.1848 | 7331.6704 | 9116.6908 | 11345.2483 | 14128.867 | 17607.3089 | 19142.6307 | 19142.5398 | 19142.413 | 19142.2358 | 19141.9873 | 19141.638 | 19141.146 | 19140.4517 | 19139.4702 |  | 795.123 | 972.2755 | 1190.2133 | 1458.722 | 1789.9929 | 2199.2243 | 2705.3729 | 3332.0961 | 4108.9314 | 5072.7754 | 6269.7356 | 7757.4532 | 9608.0141 | 11911.5995 | 14781.0636 | 18357.6757 | 22818.3228 | 28375.8729 | 35308.0442 | 43964.682 | 54779.085 | 59521.8726 | 59459.3795 | 59372.2483 | 59250.4026 | 59079.5546 | 58839.4232 | 58501.1893 | 58023.8645 | 57349.1044
Aggregated by ZSS
| AllAC | Future | All | AC | [145 empty] | 124417.5829 | 143132.9024 | 164919.8724 | 190322.692 | 219978.3259 | 254650.3976 | 295249.0406 | 342860.8108 | 398785.0537 | 464578.1828 | 542107.6711 | 633617.9796 | 741811.1722 | 869945.624 | 1021957.0412 | 1202607.0283 | 1356851.6608 | 1501630.704 | 1668859.0556 | 1862088.6963 | 2013563.9507 | 2141258.6462 | 2287389.3094 | 2455283.4972 | 2648219.141 | 2764799.0351 | 2785684.316 | 2809349.1471 | 2836168.5534 | 2866568.6173 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10289.7726 | 11765.5409 | 13468.919 | 15438.4928 | 17714.812 | 20348.0464 | 23396.9883 | 26930.6209 | 31029.9915 | 35790.454 | 41324.3591 | 47764.2882 | 55266.9534 | 64017.9087 | 74237.2596 | 86186.6 | 98588.8195 | 112075.2983 | 127702.1065 | 145824.5428 | 159768.5343 | 170775.3083 | 183148.4935 | 197360.5513 | 213687.8911 | 223828.5695 | 226207.6097 | 228907.7262 | 231972.8023 | 235452.7688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107345.1846 | 123588.1553 | 142515.344 | 164603.2313 | 190418.7414 | 220637.5206 | 256066.1216 | 297668.967 | 346601.1695 | 404248.5366 | 472276.3965 | 552689.2723 | 647903.9036 | 760838.7132 | 895023.5506 | 1054734.4607 | 1188124.708 | 1310816.8951 | 1452428.7928 | 1615918.0149 | 1744426.0117 | 1854173.4765 | 1980246.4008 | 2125101.9818 | 2291570.0792 | 2391735.2264 | 2408817.0507 | 2428166.0087 | 2450087.2021 | 2474927.1694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5302.9155 | 6085.514 | 6994.1946 | 8052.1907 | 9282.647 | 10715.5197 | 12386.317 | 14337.2 | 16618.3199 | 19289.443 | 22421.9311 | 26101.1604 | 30429.4834 | 35529.8653 | 41550.3571 | 48669.6159 | 55359.6191 | 62167.3272 | 70082.2983 | 79297.1116 | 86355.6896 | 91630.2186 | 97438.2399 | 104110.8343 | 111778.1428 | 116477.7723 | 117456.1563 | 118566.6187 | 119827.2158 | 121258.4928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 499.0884 | 571.3747 | 655.0702 | 752.3052 | 864.9771 | 995.6783 | 1147.4634 | 1323.9379 | 1529.3654 | 1768.7969 | 2048.2287 | 2374.7945 | 2757.0005 | 3205.0144 | 3731.0206 | 4349.6608 | 4979.0761 | 5656.8532 | 6447.1453 | 7370.2744 | 8073.4253 | 8570.9945 | 9107.0979 | 9722.8719 | 10430.2911 | 10871.6639 | 10979.2008 | 11101.3128 | 11239.9996 | 11397.5375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980.6217 | 1122.3175 | 1286.3445 | 1476.472 | 1697.1485 | 1953.6325 | 2252.1503 | 2600.0851 | 3006.2075 | 3480.9523 | 4036.7557 | 4688.4642 | 5453.8312 | 6354.1223 | 7414.8533 | 8666.6909 | 9799.438 | 10914.3303 | 12198.7127 | 13678.7527 | 14940.2897 | 16108.6482 | 17449.0774 | 18987.2579 | 20752.7369 | 21885.8031 | 22224.2985 | 22607.4808 | 23041.3335 | 23532.6489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AllBAN | Future | All | BAN | [145 empty] | 41356.6592 | 49888.5293 | 60533.5034 | 73856.502 | 90579.8156 | 111627.9421 | 138185.3615 | 171771.012 | 214505.4103 | 269071.2934 | 338622.8916 | 427466.1042 | 541195.0811 | 687198.2707 | 875003.8606 | 1117099.6253 | 1367930.8084 | 1405369.4877 | 1454401.1655 | 1524052.3453 | 1568602.769 | 1583885.7797 | 1599964.6727 | 1618854.6218 | 1641242.218 | 1668041.1169 | 1700480.6358 | 1740231.2708 | 1780495.2633 | 1816333.5551 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5113.1572 | 5747.8909 | 6490.465 | 7362.1819 | 8389.1064 | 9603.2298 | 11043.9346 | 12759.843 | 14882.502 | 17560.4102 | 20860.2778 | 24967.5694 | 30138.8619 | 36792.0319 | 45444.1989 | 56838.4502 | 71682.8986 | 88913.5469 | 110316.7165 | 140260.6084 | 160222.5839 | 166684.5831 | 173169.11 | 180938.806 | 190346.7209 | 201870.5229 | 216162.3272 | 234119.4471 | 250039.6744 | 262339.5121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6950.5003 | 7991.8786 | 9232.3089 | 10717.5036 | 12504.9792 | 14667.3069 | 17296.2877 | 20508.3198 | 24451.9235 | 29316.1115 | 35340.7561 | 42833.2183 | 52186.8617 | 63906.0786 | 78637.8316 | 97213.3527 | 116211.6157 | 119475.9356 | 123174.2017 | 127381.6436 | 131962.8171 | 136985.1396 | 142620.4146 | 148945.801 | 156047.6518 | 164023.4747 | 172983.486 | 183052.427 | 194371.7025 | 207064.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2206.2769 | 2473.3343 | 2793.3045 | 3178.2423 | 3643.2211 | 4207.1341 | 4893.7173 | 5732.8537 | 6835.9409 | 8326.8378 | 10238.7335 | 12719.9038 | 15982.7739 | 20371.2763 | 26341.9278 | 34572.4772 | 45529.288 | 58066.332 | 75608.7174 | 101581.6717 | 116301.8266 | 118654.8176 | 121014.4199 | 123949.4965 | 127648.2928 | 132371.7277 | 138483.4685 | 146492.7827 | 155238.0161 | 161963.6174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286.7594 | 319.5965 | 358.7447 | 405.6012 | 461.9048 | 529.8255 | 612.0774 | 712.0635 | 844.4401 | 1025.3243 | 1257.6845 | 1560.211 | 1960.0004 | 2501.8614 | 3245.4119 | 4280.0779 | 5697.5031 | 7457.9162 | 9922.5759 | 13573.873 | 15639.4968 | 15962.0874 | 16284.4948 | 16686.7527 | 17195.2294 | 17846.5126 | 18691.6436 | 19802.1517 | 21014.0098 | 21938.8449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26799.9654 | 33355.829 | 41658.6803 | 52192.9731 | 65580.6041 | 82620.4457 | 104339.3444 | 132057.932 | 167490.6037 | 212842.6096 | 270925.4397 | 345385.2017 | 440926.5833 | 563627.0225 | 721334.4905 | 924195.2673 | 1128809.503 | 1131455.757 | 1135378.9539 | 1141254.5486 | 1144476.0447 | 1145599.152 | 1146876.2332 | 1148333.7656 | 1150004.3231 | 1151928.879 | 1154159.7105 | 1156764.4623 | 1159831.8605 | 1163026.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AllDDL | Future | All | DDL | [145 empty] | 164605.6753 | 184871.1725 | 207792.7549 | 233738.2497 | 263130.1204 | 296440.6089 | 334218.7991 | 377095.8897 | 425814.39 | 481231.2267 | 544315.9537 | 616208.9958 | 698241.9751 | 791982.7595 | 899285.0008 | 1022356.6244 | 1163851.3131 | 1326993.1977 | 1499749.27 | 1691919.4909 | 1906083.6032 | 2146619.8895 | 2418959.1286 | 2726293.6491 | 3075330.0324 | 3471840.2471 | 3921522.9142 | 4431005.01 | 4506856.7032 | 4522775.1808 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4107.2262 | 4669.9502 | 5324.3056 | 6089.1827 | 6988.1493 | 8045.4344 | 9293.8509 | 10774.064 | 12546.3401 | 14685.1674 | 17268.6909 | 20406.7721 | 24241.1833 | 28959.0952 | 34807.9992 | 42118.8762 | 51339.8401 | 63085.6564 | 71284.2735 | 79251.1044 | 86003.9429 | 92138.5243 | 98753.8661 | 105276.0037 | 112763.7695 | 121385.6102 | 130935.2699 | 141244.7129 | 143087.4064 | 143798.3547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27783.093 | 31182.8599 | 35021.4741 | 39357.2322 | 44256.3265 | 49793.8251 | 56055.0366 | 63136.866 | 71149.4191 | 80217.823 | 90484.2994 | 102110.5557 | 115280.4961 | 130203.3279 | 147117.1167 | 166292.8603 | 188039.1649 | 212707.6189 | 240590.2339 | 272184.1556 | 308019.762 | 348677.4355 | 394814.2362 | 447176.4054 | 506614.0901 | 574093.3069 | 650712.8282 | 737722.5041 | 750314.8685 | 752576.6262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2530.3009 | 2892.0535 | 3316.5406 | 3818.0652 | 4414.7884 | 5124.3667 | 5971.8814 | 6988.7556 | 8219.7328 | 9720.7864 | 11555.8586 | 13810.6658 | 16595.7714 | 20057.3815 | 24388.1139 | 29843.9424 | 36768.2823 | 45626.6571 | 51103.4589 | 55754.1626 | 59739.4024 | 63459.9704 | 67458.8689 | 71340.2155 | 75834.3299 | 81062.8142 | 86753.3283 | 92664.8321 | 93723.6873 | 94134.1823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283.3533 | 325.3684 | 375.0658 | 434.3063 | 505.4736 | 590.8571 | 693.7646 | 818.3668 | 970.6758 | 1158.2458 | 1389.7076 | 1676.7075 | 2034.3325 | 2482.6231 | 3048.0804 | 3766.042 | 4684.0626 | 5866.7829 | 6565.037 | 7137.3001 | 7604.6223 | 8021.9431 | 8464.0657 | 8873.2278 | 9350.1264 | 9909.3576 | 10509.6421 | 11113.7149 | 11229.4587 | 11280.9346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129901.7019 | 145800.9403 | 163755.3688 | 184039.4633 | 206965.3826 | 232886.1257 | 262204.2655 | 295377.8373 | 332928.2222 | 375449.2041 | 423617.3971 | 478204.2948 | 540090.1918 | 610280.3317 | 689923.6906 | 780334.9035 | 883019.9632 | 999706.4825 | 1130206.2668 | 1277592.7682 | 1444715.8735 | 1634322.0162 | 1849468.0917 | 2093627.7966 | 2370767.7165 | 2685389.1582 | 3042611.8456 | 3448259.2459 | 3508501.2823 | 3520985.0831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AllECA | Future | All | ECA | [145 empty] | 19042.3031 | 22970.6433 | 27864.5613 | 33975.484 | 41622.1649 | 51223.8244 | 63297.141 | 78493.0397 | 97759.8871 | 122185.4019 | 153121.0263 | 192378.4677 | 242272.5382 | 305800.7228 | 386848.5044 | 490474.2182 | 623302.8421 | 733063.9903 | 751956.5783 | 780969.8008 | 806530.623 | 813525.5048 | 816180.5732 | 819537.2452 | 823850.0719 | 829477.1555 | 836023.1717 | 841357.244 | 844727.6686 | 847299.3844 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 904.4908 | 1006.2759 | 1131.0184 | 1284.3902 | 1473.5322 | 1716.5182 | 2026.7461 | 2417.9192 | 2975.0432 | 3734.347 | 4733.6117 | 6065.77 | 7855.1333 | 10285.3278 | 13625.2308 | 18273.2657 | 24828.9617 | 33049.9277 | 42827.3278 | 57914.3155 | 72002.2855 | 75634.2054 | 76537.4041 | 77734.9976 | 79339.0492 | 81507.4465 | 84049.6293 | 86027.7307 | 87055.0632 | 87584.6958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2780.7549 | 3316.605 | 3979.3723 | 4801.7427 | 5825.1301 | 7102.0663 | 8699.1933 | 10701.1188 | 13215.772 | 16380.2202 | 20368.141 | 25401.1529 | 31761.4156 | 39808.4586 | 50000.6023 | 62922.4077 | 79319.8842 | 92209.5867 | 92481.4571 | 92817.7863 | 93110.5967 | 93358.1987 | 93621.0191 | 93906.0677 | 94215.6931 | 94552.6684 | 94920.3251 | 95314.3933 | 95731.3552 | 96179.7493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 641.9072 | 719.7677 | 816.085 | 935.5332 | 1084.0133 | 1273.8878 | 1515.6905 | 1821.0098 | 2248.6088 | 2833.5401 | 3603.0721 | 4628.7895 | 6003.7811 | 7866.0897 | 10417.2334 | 13955.2445 | 18928.9474 | 25021.6182 | 31977.4295 | 42803.4408 | 51773.1075 | 53981.6889 | 54753.8425 | 55806.4438 | 57251.5894 | 59248.1238 | 61594.5799 | 63316.7299 | 64158.5898 | 64664.0267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6401 | 85.795 | 95.8507 | 108.2828 | 123.6904 | 143.5211 | 168.885 | 200.9394 | 247.3577 | 312.3064 | 398.6516 | 515.2321 | 673.575 | 891.1053 | 1193.634 | 1619.8577 | 2228.8074 | 3015.227 | 3994.4249 | 5518.5617 | 6781.7051 | 7092.5046 | 7200.8299 | 7348.6289 | 7551.6908 | 7832.3905 | 8162.3124 | 8404.2084 | 8522.0595 | 8592.4502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14637.51 | 17842.1996 | 21842.2348 | 26845.5351 | 33115.7989 | 40987.8311 | 50886.6263 | 63352.0526 | 79073.1054 | 98924.9882 | 124017.5499 | 155767.5232 | 195978.6331 | 246949.7413 | 311611.804 | 393703.4425 | 497996.2414 | 579767.6306 | 580675.9391 | 581915.6965 | 582862.9283 | 583458.9072 | 584067.4775 | 584741.1073 | 585492.0495 | 586336.5263 | 587296.3251 | 588294.1818 | 589260.6009 | 590278.4625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AllFDN | Future | All | FDN | [145 empty] | 22893.0467 | 26720.1545 | 31233.9364 | 36545.8101 | 42801.3654 | 50173.5732 | 58868.1359 | 69129.9433 | 81250.8787 | 95579.2819 | 112531.4528 | 132605.6764 | 156399.3778 | 184630.1743 | 218161.8054 | 258036.1914 | 305513.226 | 362120.3721 | 386681.829 | 393056.8152 | 400851.2408 | 405868.3768 | 410541.1715 | 410541.1715 | 410541.1715 | 410541.1715 | 410541.1715 | 410541.1715 | 410541.1715 | 410541.1715 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4994.1476 | 5826.2539 | 6814.8468 | 7980.894 | 9357.8048 | 10985.6427 | 12912.5531 | 15196.5271 | 17907.5909 | 21130.5335 | 24968.3195 | 29546.379 | 35018.0233 | 41571.312 | 49437.7989 | 58903.721 | 70324.3711 | 84142.6397 | 92368.6227 | 95786.9422 | 99994.7224 | 102381.9642 | 104538.2383 | 104538.2383 | 104538.2383 | 104538.2383 | 104538.2383 | 104538.2383 | 104538.2383 | 104538.2383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16019.3716 | 18699.9327 | 21848.5663 | 25548.8887 | 29899.6685 | 35017.5928 | 41040.5453 | 48131.4878 | 56483.0564 | 66323.0049 | 77920.6502 | 91594.5076 | 107721.3345 | 126746.8438 | 149198.3964 | 175700.0386 | 206990.3216 | 243943.4159 | 256326.9933 | 257625.1398 | 259142.3392 | 260915.0232 | 262732.3911 | 262732.3911 | 262732.3911 | 262732.3911 | 262732.3911 | 262732.3911 | 262732.3911 | 262732.3911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1580.6199 | 1845.0511 | 2161.9741 | 2537.0302 | 2981.5628 | 3509.3023 | 4136.9172 | 4884.7084 | 5777.484 | 6845.6698 | 8126.7239 | 9666.9452 | 11523.7984 | 13768.912 | 16491.9623 | 19805.7212 | 23852.6442 | 28813.493 | 32225.4659 | 33673.6765 | 35481.1371 | 36225.0664 | 36830.2797 | 36830.2797 | 36830.2797 | 36830.2797 | 36830.2797 | 36830.2797 | 36830.2797 | 36830.2797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194.0155 | 226.4723 | 265.4869 | 311.7044 | 366.5461 | 431.7376 | 509.3806 | 602.0437 | 712.8774 | 845.7608 | 1005.4895 | 1198.0169 | 1430.7652 | 1713.0288 | 2056.4993 | 2475.9493 | 2990.129 | 3622.9436 | 4081.5539 | 4283.3397 | 4535.3683 | 4637.0401 | 4719.0804 | 4719.0804 | 4719.0804 | 4719.0804 | 4719.0804 | 4719.0804 | 4719.0804 | 4719.0804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.892 | 122.4445 | 143.0622 | 167.2928 | 195.7832 | 229.2977 | 268.7396 | 315.1763 | 369.87 | 434.3129 | 510.2697 | 599.8278 | 705.4565 | 830.0776 | 977.1485 | 1150.7613 | 1355.7602 | 1597.88 | 1679.1932 | 1687.717 | 1697.6737 | 1709.2829 | 1721.1819 | 1721.1819 | 1721.1819 | 1721.1819 | 1721.1819 | 1721.1819 | 1721.1819 | 1721.1819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AllGCY | Future | All | GCY | [145 empty] | 132683.1134 | 149955.5567 | 169630.7221 | 192042.9216 | 217590.2898 | 246732.2369 | 279999.7841 | 318007.9148 | 361477.3754 | 411245.1002 | 468279.3674 | 533728.8653 | 608939.8307 | 695505.6608 | 795329.1593 | 910695.5423 | 1044373.4366 | 1199752.1751 | 1381032.309 | 1566438.3999 | 1777361.3162 | 2001400.5843 | 2246527.6633 | 2525657.2295 | 2844658.1163 | 3209318.205 | 3543811.6645 | 3554294.9976 | 3564990.3988 | 3577078.5469 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6430.0484 | 7297.4826 | 8305.4621 | 9470.3443 | 10820.2732 | 12389.4457 | 14219.6782 | 16362.4405 | 18884.7037 | 21868.9691 | 25414.7866 | 29655.0566 | 34756.7877 | 40935.7497 | 48475.7731 | 57751.6766 | 69263.5567 | 83686.0532 | 101940.1365 | 113088.9261 | 125506.5593 | 136534.1471 | 148070.1755 | 160762.4445 | 175321.0226 | 192039.4333 | 207579.3814 | 208509.0459 | 209030.9326 | 209620.7791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49204.4945 | 55641.3982 | 62965.4996 | 71302.5109 | 80796.2778 | 91611.4242 | 103936.3897 | 117986.9179 | 134010.0604 | 152288.7748 | 173147.2067 | 196956.7606 | 224143.0768 | 255194.0559 | 290669.0912 | 331209.6958 | 377551.7447 | 430539.5854 | 491142.3166 | 560313.3562 | 639429.2646 | 719284.1286 | 802431.2488 | 897408.0077 | 1005915.718 | 1129901.0194 | 1243290.7212 | 1245487.6802 | 1247970.3607 | 1250776.3338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3214.9107 | 3659.4855 | 4180.4667 | 4788.003 | 5499.2248 | 6335.3763 | 7322.9804 | 8495.3693 | 9898.0029 | 11587.5863 | 13632.4699 | 16127.9755 | 19195.2375 | 22993.8057 | 27738.273 | 33717.6244 | 41324.9481 | 51100.784 | 63797.2829 | 69652.4914 | 75877.6169 | 81366.263 | 87101.3875 | 93332.8594 | 100512.3729 | 108802.1896 | 116635.555 | 117399.1415 | 117716.315 | 118074.7906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341.2854 | 389.3622 | 446.203 | 512.9548 | 591.7072 | 685.083 | 796.3951 | 929.8542 | 1091.3094 | 1288.1133 | 1529.166 | 1827.0612 | 2197.9068 | 2663.0818 | 3251.5586 | 4002.6043 | 4969.9386 | 6227.8088 | 7879.9925 | 8549.7071 | 9249.3055 | 9838.7115 | 10451.1568 | 11105.6985 | 11861.9933 | 12738.3276 | 13575.1135 | 13676.5401 | 13714.2389 | 13756.8468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73492.3744 | 82967.8283 | 93733.0906 | 105969.1086 | 119882.8068 | 135710.9077 | 153724.3408 | 174233.333 | 197593.299 | 224211.6567 | 254555.7382 | 289162.0114 | 328646.8219 | 373718.9677 | 425194.4634 | 484013.9412 | 551263.2485 | 628197.9437 | 716272.5806 | 814833.919 | 927298.5699 | 1054377.3342 | 1198473.6946 | 1363048.2194 | 1551047.0095 | 1765837.235 | 1962730.8935 | 1969222.5899 | 1976558.5516 | 1984849.7966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AllMLN | Future | All | MLN | [145 empty] | 66176.2404 | 74135.797 | 83162.0902 | 93408.3389 | 105051.9467 | 118300.8777 | 133406.1777 | 150641.8935 | 170462.0706 | 193262.603 | 219512.0331 | 249845.9203 | 285322.7933 | 326917.3594 | 375824.636 | 433773.406 | 501760.5174 | 577808.581 | 670363.9576 | 770298.0303 | 881498.8126 | 984201.2052 | 1103122.5514 | 1241429.7915 | 1403123.6645 | 1593323.2491 | 1818662.5308 | 1984570.941 | 2054277.527 | 2080033.7557 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3059.3675 | 3376.7793 | 3749.0208 | 4187.5038 | 4706.4626 | 5324.5036 | 6068.3758 | 6964.1635 | 8116.2926 | 9574.9163 | 11403.7935 | 13727.849 | 16828.3183 | 20935.2282 | 26354.9061 | 33601.4549 | 42897.6857 | 53293.9122 | 68054.1634 | 83932.2109 | 101042.6094 | 107298.7101 | 115335.224 | 125786.6948 | 139540.9369 | 157844.9896 | 182456.2344 | 211912.7058 | 231730.0047 | 232375.9622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13893.5983 | 15586.7735 | 17499.7891 | 19662.1334 | 22107.3378 | 24873.5571 | 28004.2691 | 31548.8102 | 35563.6436 | 40112.8372 | 45269.3883 | 51116.6727 | 57755.594 | 65294.6174 | 73856.4981 | 83585.0327 | 94640.2233 | 107191.9237 | 121477.0319 | 137653.6243 | 156031.2832 | 176900.0458 | 200662.3915 | 227737.261 | 258609.9478 | 293844.7824 | 334101.051 | 357767.6239 | 363648.5072 | 369152.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1963.8668 | 2185.7384 | 2450.3066 | 2767.4743 | 3149.8002 | 3614.0645 | 4185.1254 | 4886.7659 | 5800.3368 | 6972.9123 | 8465.2422 | 10385.2664 | 12947.3204 | 16351.3754 | 20866.0811 | 26917.3219 | 34575.5334 | 42614.981 | 54029.8041 | 64877.3894 | 76158.7961 | 79815.3505 | 84525.1115 | 90666.1805 | 98768.0472 | 109574.9951 | 124136.5449 | 141754.6321 | 153741.8249 | 154181.2244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237.8431 | 264.3962 | 296.3533 | 335.0276 | 382.0947 | 439.8123 | 511.5608 | 600.553 | 718.0935 | 870.6346 | 1066.5297 | 1320.7517 | 1663.169 | 2121.6496 | 2733.706 | 3558.9189 | 4606.7494 | 5704.0402 | 7271.8777 | 8754.7536 | 10292.5091 | 10748.5091 | 11344.3562 | 12131.9458 | 13184.2283 | 14604.0685 | 16536.889 | 18943.3402 | 20608.1656 | 20654.5662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47021.5647 | 52722.1096 | 59166.6202 | 66456.1998 | 74706.2514 | 84048.9402 | 94636.8465 | 106641.6008 | 120263.704 | 135731.3026 | 153307.0795 | 173295.3805 | 196128.3915 | 222214.4889 | 252013.4447 | 286110.6776 | 325040.3256 | 369003.7239 | 419531.0805 | 475080.0522 | 537973.6148 | 609438.5896 | 691255.4682 | 785107.7093 | 893020.5042 | 1017454.4135 | 1161431.8115 | 1254192.639 | 1284549.0246 | 1303669.7668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AllSA | Future | All | SA | [145 empty] | 147365.8952 | 170045.5001 | 197277.2623 | 230128.2755 | 269982.8575 | 318469.714 | 377713.3391 | 450396.6862 | 539912.9252 | 650559.1884 | 787790.151 | 958522.0055 | 1171541.787 | 1438029.366 | 1772217.1697 | 2192238.5181 | 2719995.5082 | 3152964.4651 | 3219109.5314 | 3284733.3345 | 3359948.312 | 3435497.5109 | 3508223.3976 | 3588559.9 | 3678054.6266 | 3777839.9986 | 3870215.4578 | 3936580.213 | 4009589.8539 | 4090213.535 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4081.2218 | 4614.4706 | 5264.584 | 6058.7879 | 7056.4176 | 8270.0885 | 9755.9455 | 11586.3648 | 13854.9482 | 16683.1226 | 20231.6726 | 24706.6673 | 30377.0973 | 37597.4762 | 46834.022 | 58701.3319 | 73488.4589 | 89002.8434 | 100348.1748 | 109457.1914 | 120860.0575 | 129112.4794 | 132082.2884 | 135109.0812 | 138575.1659 | 142571.4457 | 146137.9882 | 148200.3876 | 150448.4515 | 152933.9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28286.2703 | 31709.1017 | 35658.8884 | 40237.1919 | 45568.8599 | 51807.8111 | 59144.4641 | 67815.1306 | 78113.9329 | 90407.9309 | 105156.3372 | 122934.9428 | 144467.1864 | 170663.6939 | 202672.6257 | 241943.813 | 290307.4137 | 331631.0618 | 344734.5356 | 359240.0827 | 375350.7643 | 393250.574 | 413143.1592 | 435256.7487 | 459845.4085 | 487192.8535 | 512425.4451 | 530118.4501 | 549503.6296 | 570895.5851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2627.7138 | 3036.3475 | 3545.0937 | 4180.3082 | 4991.9959 | 5999.3441 | 7255.4408 | 8828.7648 | 10807.8374 | 13307.3275 | 16478.962 | 20516.2465 | 25670.7028 | 32272.4312 | 40753.2383 | 51679.0098 | 65252.561 | 78788.121 | 86660.534 | 92665.1189 | 100284.7552 | 105624.2287 | 107180.6704 | 108743.6278 | 110581.945 | 112768.6726 | 114698.8718 | 115710.1797 | 116810.7761 | 118028.6216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290.4705 | 336.5212 | 394.5178 | 467.6894 | 562.4758 | 680.82 | 829.2485 | 1016.2111 | 1252.6703 | 1552.8782 | 1935.8071 | 2425.6787 | 3054.0794 | 3862.637 | 4905.9986 | 6256.0332 | 7931.3343 | 9644.8188 | 10724.2544 | 11537.5301 | 12574.7658 | 13286.498 | 13460.4245 | 13630.1411 | 13832.9457 | 14078.4681 | 14292.0964 | 14393.935 | 14504.7722 | 14627.5119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112080.2189 | 130349.0592 | 152414.1784 | 179184.2981 | 211803.1084 | 251711.6504 | 300728.2401 | 361150.215 | 435883.5363 | 528607.9292 | 643987.3722 | 787938.4702 | 967972.7211 | 1193633.1277 | 1477051.2852 | 1833658.3302 | 2283015.7402 | 2643897.6201 | 2676642.0326 | 2711833.4114 | 2750877.9691 | 2794223.7308 | 2842356.855 | 2895820.3013 | 2955219.1615 | 3021228.5587 | 3082661.0563 | 3128157.2606 | 3178322.2245 | 3233727.9011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AllSHL | Future | All | SHL | [145 empty] | 13479.252 | 14385.9465 | 15405.1022 | 17016.6089 | 19968.6904 | 23902.7113 | 29154.1827 | 36076.402 | 45317.919 | 57801.7967 | 74846.2249 | 98339.0985 | 130990.9496 | 176701.7162 | 241092.9921 | 332280.9462 | 461594.6719 | 644438.1531 | 906718.7905 | 980304.2851 | 1017411.024 | 1063100.0337 | 1072336.3085 | 1082704.374 | 1094344.9136 | 1107416.2549 | 1122096.5949 | 1138586.5075 | 1157111.7685 | 1177926.538 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1152.8692 | 1238.0577 | 1337.4983 | 1468.7201 | 1658.3159 | 1960.6373 | 2406.7672 | 2991.2798 | 3765.4596 | 4801.505 | 6201.5317 | 8110.5873 | 10735.5064 | 14372.2838 | 19445.892 | 26568.3054 | 36373.5728 | 49166.2185 | 67602.4117 | 79732.7855 | 90599.3229 | 104205.5392 | 104814.4805 | 105498.0398 | 106265.4926 | 107127.2771 | 108095.1417 | 109182.3102 | 110403.6679 | 111775.9712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4018.8006 | 4426.3147 | 4881.2099 | 5415.221 | 6075.6886 | 6842.013 | 7738.084 | 8793.6076 | 10050.865 | 11567.404 | 13422.4166 | 15725.9271 | 18632.0569 | 22358.201 | 27212.7885 | 33635.5099 | 42255.4206 | 53975.1635 | 70096.3589 | 75932.5695 | 80014.2603 | 84677.3006 | 89050.7973 | 93960.2117 | 99472.1593 | 105661.61 | 112612.9427 | 120421.1317 | 129193.0847 | 139049.1499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 682.3159 | 718.0342 | 760.2564 | 827.4996 | 948.422 | 1152.6552 | 1464.6797 | 1884.3938 | 2453.8104 | 3232.452 | 4304.9384 | 5791.9476 | 7866.0746 | 10774.8156 | 14873.9253 | 20675.895 | 28785.5162 | 39745.5758 | 55538.5253 | 64657.2448 | 73024.5784 | 83528.5666 | 83746.7993 | 83991.7737 | 84266.8138 | 84575.6606 | 84922.5244 | 85312.1444 | 85749.8552 | 86241.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4517 | 90.7542 | 95.8882 | 104.1597 | 119.1342 | 145.2897 | 185.8836 | 240.6522 | 315.1368 | 417.1864 | 557.9568 | 753.3533 | 1026.1185 | 1408.8578 | 1948.4302 | 2712.3301 | 3778.9524 | 5214.8943 | 7285.2144 | 8534.0568 | 9700.3284 | 11165.2269 | 11188.1322 | 11213.8442 | 11242.7119 | 11275.1278 | 11311.5339 | 11352.4277 | 11398.3689 | 11449.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7538.8145 | 7912.7857 | 8330.2494 | 9201.0086 | 11167.1297 | 13802.1161 | 17358.7681 | 22166.4686 | 28732.6473 | 37783.2493 | 50359.3814 | 67957.2833 | 92731.1932 | 127787.558 | 177611.9562 | 248688.9058 | 350401.2099 | 496336.301 | 706196.2802 | 751447.6285 | 764072.5341 | 779523.4003 | 783536.0993 | 788040.5046 | 793097.7362 | 798776.5794 | 805154.4521 | 812318.4934 | 820366.7917 | 829409.7669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AllSHN | Future | All | SHN | [145 empty] | 76914.2841 | 88077.7777 | 101021.4359 | 116057.3752 | 133537.3765 | 153886.3375 | 177607.6189 | 205298.412 | 237668.3041 | 275561.7566 | 319985.3792 | 372141.0982 | 433466.5943 | 505684.7303 | 590864.1336 | 691493.6733 | 810574.3023 | 951732.6929 | 1105965.6747 | 1239637.3559 | 1318714.7523 | 1395638.6808 | 1473164.1304 | 1561518.7001 | 1662235.3256 | 1777065.8555 | 1885062.3294 | 1904868.9252 | 1927132.5987 | 1952162.6578 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5217.0401 | 5941.4343 | 6780.2524 | 7757.0609 | 8893.7091 | 10220.0356 | 11772.2747 | 13594.612 | 15741.1599 | 18278.4723 | 21288.7587 | 24874.0047 | 29161.2718 | 34309.536 | 40518.5391 | 48040.2803 | 57193.9798 | 68385.6244 | 75932.7052 | 82617.3918 | 89546.5951 | 96697.5766 | 104276.128 | 112919.8289 | 122780.2218 | 134030.5816 | 144537.1444 | 146027.6252 | 147705.7516 | 149595.4794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28864.4852 | 32914.444 | 37582.1484 | 42967.5044 | 49187.2172 | 56377.95 | 64699.7958 | 74340.4526 | 85520.1675 | 98497.5957 | 113576.7479 | 131115.2337 | 151534.0506 | 175329.2137 | 203085.5847 | 235493.3229 | 273367.4725 | 317671.2955 | 369457.6817 | 417227.1209 | 450274.1923 | 484388.6847 | 520551.5436 | 561798.1078 | 608851.9536 | 662540.4813 | 712481.9665 | 718472.7053 | 725201.4018 | 732760.3191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2726.84 | 3127.9295 | 3598.0201 | 4153.9331 | 4809.4455 | 5585.0819 | 6506.1742 | 7604.1105 | 8917.9373 | 10496.4172 | 12400.6817 | 14707.6599 | 17514.5231 | 20944.4627 | 25154.2218 | 30343.9406 | 36770.0628 | 44762.3016 | 49523.9479 | 53078.5009 | 56292.0314 | 59499.4253 | 62805.603 | 66574.9986 | 70873.3363 | 75775.7433 | 80381.311 | 81191.7573 | 82104.4191 | 83132.3677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315.7705 | 362.5148 | 417.4613 | 482.7285 | 559.9636 | 651.7126 | 761.1383 | 892.1853 | 1049.7923 | 1240.1665 | 1471.1391 | 1752.6262 | 2097.2283 | 2521.0135 | 3044.5409 | 3694.2029 | 4503.9906 | 5517.8193 | 6057.531 | 6440.7422 | 6819.86 | 7197.8491 | 7587.1231 | 8030.9326 | 8537.0144 | 9114.2121 | 9657.002 | 9755.5039 | 9866.4707 | 9991.5014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39790.1483 | 45731.4551 | 52643.5537 | 60696.1483 | 70087.0412 | 81051.5573 | 93868.236 | 108867.0517 | 126439.2472 | 147049.1049 | 171248.0517 | 199691.5737 | 233159.5206 | 272580.5044 | 319061.2471 | 373921.9266 | 438738.7966 | 515395.652 | 604993.8089 | 680273.6 | 715782.0735 | 747855.1451 | 777943.7328 | 812194.8322 | 851192.7995 | 895604.8372 | 938004.9055 | 949421.3334 | 962254.5554 | 976682.9902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AllTYA | Future | All | TYA | [145 empty] | 65385.4938 | 76118.5728 | 88716.7913 | 103514.3572 | 120906.5356 | 141360.9477 | 165430.9795 | 193771.697 | 227158.7383 | 266510.7429 | 312915.9845 | 367663.9988 | 432283.1486 | 508585.2443 | 598718.5536 | 705230.7825 | 831143.9124 | 948120.4618 | 976633.3399 | 1009718.4243 | 1048122.3315 | 1092715.1422 | 1130018.3535 | 1168450.1491 | 1212830.368 | 1264092.1005 | 1323316.0943 | 1391754.2613 | 1445967.8378 | 1473826.3433 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5328.6964 | 6193.9347 | 7207.7459 | 8396.4193 | 9790.9847 | 11428.0791 | 13350.9711 | 15610.7759 | 18267.8935 | 21393.7137 | 25072.6351 | 29404.4588 | 34507.2252 | 40520.5763 | 47609.7423 | 55970.2679 | 65833.6165 | 75668.976 | 81064.0102 | 87377.6071 | 94768.3372 | 103422.3961 | 106963.7814 | 108941.9027 | 111224.3524 | 113858.5996 | 116899.5854 | 120410.9061 | 123316.1781 | 125062.5071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40975.1514 | 47709.9471 | 55616.7183 | 64905.773 | 75825.8976 | 88671.4882 | 103791.0156 | 121597.074 | 142578.3137 | 167313.6096 | 196488.8898 | 230917.125 | 271562.0757 | 319566.5055 | 376285.7076 | 443327.3458 | 522598.8065 | 595627.2032 | 610676.3904 | 628089.7555 | 648245.4862 | 671583.0214 | 694499.7258 | 719642.9247 | 748679.4465 | 782220.2581 | 820973.0457 | 865757.6183 | 901120.306 | 919059.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1942.8426 | 2259.3078 | 2630.3045 | 3065.5177 | 3576.3858 | 4176.422 | 4881.595 | 5710.7812 | 6686.2989 | 7834.5437 | 9186.7401 | 10779.8339 | 12657.5501 | 14871.6478 | 17483.4087 | 20565.4035 | 24203.587 | 27757.6784 | 29400.6634 | 31320.956 | 33566.0605 | 36191.7003 | 37429.9991 | 38272.9698 | 39245.9371 | 40369.2229 | 41666.3548 | 43164.5747 | 44383.4625 | 45075.464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.254 | 232.7644 | 270.8561 | 315.5167 | 367.9115 | 429.4164 | 501.6566 | 586.5514 | 686.3692 | 803.7908 | 941.9854 | 1104.7003 | 1296.3678 | 1522.231 | 1788.4935 | 2102.4968 | 2472.9307 | 2842.7238 | 3047.2739 | 3286.6643 | 3566.9116 | 3895.0808 | 4028.4614 | 4102.1223 | 4187.1141 | 4285.2039 | 4398.4368 | 4529.1803 | 4637.4731 | 4702.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16938.5494 | 19722.6188 | 22991.1665 | 26831.1306 | 31345.356 | 36655.5419 | 42905.7411 | 50266.5144 | 58939.8628 | 69165.0851 | 81225.7342 | 95457.8808 | 112259.9298 | 132104.2837 | 155551.2014 | 183265.2685 | 216034.9717 | 246223.8803 | 252445.002 | 259643.4414 | 267975.536 | 277622.9437 | 287096.3859 | 297490.2295 | 309493.5179 | 323358.8161 | 339378.6716 | 357891.9819 | 372510.418 | 379926.1842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AllWBE | Future | All | WBE | [145 empty] | 66850.7342 | 79664.8805 | 95513.9798 | 115208.0003 | 139637.1321 | 169975.6935 | 207708.6981 | 256885.3063 | 319605.6002 | 398903.4403 | 499497.1233 | 627630.4833 | 791593.5064 | 1002491.7238 | 1258674.8436 | 1562553.8687 | 1964287.7422 | 2386282.2858 | 2725548.2469 | 3189478.9418 | 3591089.8031 | 3662391.0104 | 3723492.7794 | 3760532.24 | 3761484.0145 | 3762834.9425 | 3763853.7635 | 3763853.7635 | 3763853.7635 | 3763853.7635 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7509.8188 | 9075.5603 | 11006.124 | 13410.0912 | 16378.977 | 20047.0657 | 24585.3361 | 30211.7721 | 37215.3147 | 45940.3236 | 56814.9993 | 70392.7135 | 87377.4224 | 108670.5426 | 129912.3608 | 146612.8938 | 167873.1927 | 189525.5092 | 208167.6079 | 223957.7811 | 237988.0142 | 243747.1029 | 247783.1715 | 250381.9168 | 250818.9687 | 251439.3107 | 251907.1502 | 251907.1502 | 251907.1502 | 251907.1502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11430.4468 | 13770.2003 | 16631.9094 | 20136.6918 | 24433.6663 | 29707.7488 | 36188.0961 | 44229.1395 | 54173.9242 | 66461.4947 | 81666.523 | 100512.1252 | 123910.959 | 153019.2639 | 183615.5513 | 211407.6698 | 246597.6733 | 284719.3794 | 311241.4347 | 341813.173 | 374465.0674 | 388703.0195 | 396564.1925 | 401279.8019 | 401279.8019 | 401279.8019 | 401279.8019 | 401279.8019 | 401279.8019 | 401279.8019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3576.1208 | 4306.7367 | 5215.026 | 6367.0011 | 7800.0965 | 9582.3753 | 11802.9829 | 14584.145 | 18081.6482 | 22484.5477 | 28030.764 | 35034.6725 | 43903.5807 | 55170.5406 | 67450.335 | 79405.8672 | 94846.0949 | 111115.0567 | 126660.5527 | 138714.9011 | 148123.5308 | 150906.3461 | 152627.9464 | 153844.0581 | 154295.1936 | 154935.5255 | 155418.4406 | 155418.4406 | 155418.4406 | 155418.4406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471.0932 | 567.6085 | 687.6776 | 840.2437 | 1030.1409 | 1266.4076 | 1560.915 | 1929.2299 | 2392.3324 | 2975.4953 | 3710.2009 | 4638.0917 | 5813.0848 | 7305.706 | 8924.9916 | 10485.5352 | 12498.8255 | 14614.1871 | 16657.8217 | 18157.6085 | 19295.2839 | 19642.2289 | 19864.3278 | 20023.4051 | 20086.9922 | 20177.2463 | 20245.3127 | 20245.3127 | 20245.3127 | 20245.3127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43863.2546 | 51944.7748 | 61973.2427 | 74453.9725 | 89994.2514 | 109372.0962 | 133571.3679 | 165931.0198 | 207742.3807 | 261041.579 | 329274.6361 | 417052.8804 | 530588.4595 | 678325.6707 | 868771.605 | 1114641.9028 | 1442471.9559 | 1786308.1534 | 2062820.8298 | 2466835.4781 | 2811217.9068 | 2859392.3129 | 2906653.1411 | 2935003.0582 | 2935003.0582 | 2935003.0582 | 2935003.0582 | 2935003.0582 | 2935003.0582 | 2935003.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not replacedAC | Future | Not replaced | AC | [145 empty] | 30701.9076 | 34894.591 | 39695.1202 | 45194.4711 | 51497.5135 | 58725.1614 | 67016.8602 | 76533.4625 | 87460.5538 | 100012.2996 | 114435.8962 | 131016.7191 | 150084.2809 | 172019.1252 | 197260.805 | 226317.1172 | 259774.7913 | 298311.8638 | 342712.003 | 393881.096 | 437876.187 | 478955.8664 | 526103.5057 | 580227.494 | 642373.4118 | 680293.5009 | 687839.4184 | 696334.3341 | 705899.3115 | 716670.9963 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3280.1058 | 3727.7098 | 4239.9579 | 4826.4699 | 5498.324 | 6268.281 | 7151.0428 | 8163.551 | 9325.3315 | 10658.8939 | 12190.1907 | 13949.1499 | 15970.2897 | 18293.4282 | 20964.5046 | 24036.5278 | 27570.6731 | 31637.5499 | 36318.667 | 41708.1273 | 46979.4005 | 52448.0902 | 58732.1816 | 65954.6819 | 74257.2939 | 79081.6404 | 79552.4017 | 80082.3673 | 80679.0901 | 81351.0948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25630.5895 | 29131.1379 | 33139.4956 | 37731.735 | 42995.5591 | 49032.1043 | 55958.0254 | 63907.9068 | 73037.0524 | 83524.7122 | 95577.8165 | 109435.2971 | 125373.0878 | 143709.9118 | 164813.9821 | 189110.7566 | 217091.9186 | 249325.773 | 286469.2867 | 329282.031 | 365303.0216 | 398260.0035 | 436075.7012 | 479476.3137 | 529297.5688 | 559996.7485 | 566711.5937 | 574270.9188 | 582782.4541 | 592367.7957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1091.7538 | 1240.7682 | 1411.3286 | 1606.6471 | 1830.4236 | 2086.9213 | 2381.0534 | 2718.4832 | 3105.7403 | 3550.3542 | 4061.0091 | 4647.7227 | 5322.0535 | 6097.3389 | 6988.9726 | 8014.7233 | 9195.1051 | 10553.8041 | 12118.1734 | 13919.8047 | 15616.7067 | 17327.9839 | 19293.8028 | 21552.4868 | 24148.1745 | 25675.9337 | 25866.4573 | 26080.9417 | 26322.4437 | 26594.4133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.0359 | 127.3242 | 144.8203 | 164.8527 | 187.7998 | 214.0974 | 244.2474 | 278.8285 | 318.5073 | 364.0526 | 416.3504 | 476.4228 | 545.4482 | 624.7864 | 716.0058 | 820.9163 | 941.6066 | 1080.4874 | 1240.3415 | 1424.3816 | 1604.7487 | 1792.1444 | 2007.485 | 2254.9863 | 2539.5055 | 2704.7207 | 2720.6118 | 2738.5015 | 2758.6446 | 2781.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.4225 | 667.6509 | 759.5177 | 864.7664 | 985.4069 | 1123.7574 | 1282.4912 | 1464.693 | 1673.9221 | 1914.2868 | 2190.5296 | 2508.1265 | 2873.4017 | 3293.6598 | 3777.3399 | 4334.193 | 4975.4879 | 5714.2494 | 6565.5344 | 7546.7515 | 8372.3096 | 9127.6444 | 9994.3351 | 10989.0253 | 12130.8691 | 12834.4577 | 12988.3539 | 13161.6046 | 13356.6789 | 13576.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not replacedBAN | Future | Not replaced | BAN | [145 empty] | 5843.8849 | 6463.3148 | 7188.0281 | 8038.8943 | 9041.4215 | 10226.8685 | 11633.6349 | 13309.0032 | 15482.407 | 18404.9381 | 22102.229 | 26852.675 | 33063.1708 | 41438.1812 | 52889.7747 | 68794.7909 | 91355.1903 | 122381.4309 | 164038.2767 | 226930.6989 | 263861.6163 | 270552.8 | 276941.3398 | 284899.6332 | 294952.7315 | 307831.502 | 324558.4073 | 346569.8318 | 375890.6534 | 400698.2718 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1711.7911 | 1918.5465 | 2171.581 | 2481.9474 | 2863.4441 | 3333.314 | 3913.1248 | 4629.8771 | 5588.7541 | 6905.9573 | 8608.4522 | 10832.5753 | 13773.9176 | 17774.3394 | 23255.84 | 30842.0433 | 41522.4032 | 55728.9383 | 73649.8582 | 100337.5613 | 116616.7371 | 118912.5391 | 120683.0468 | 123117.8039 | 126486.914 | 131173.9145 | 137724.0874 | 146913.4852 | 159847.5919 | 169755.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2535.7917 | 2810.6337 | 3117.4652 | 3460.1423 | 3842.997 | 4270.8961 | 4749.309 | 5284.3829 | 5883.6484 | 6555.5974 | 7308.7106 | 8153.4549 | 9101.9142 | 10168.4377 | 11369.7017 | 12725.7497 | 14261.4526 | 16007.7288 | 18004.6372 | 20308.9746 | 22756.7917 | 25387.1675 | 28340.0413 | 31656.7404 | 35383.3224 | 39571.9743 | 44281.9375 | 49580.6137 | 55544.9037 | 62225.7607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1025.1794 | 1114.8667 | 1224.6029 | 1359.173 | 1524.5498 | 1728.1972 | 1979.4501 | 2289.9943 | 2748.1707 | 3448.5507 | 4387.0368 | 5664.3335 | 7432.0569 | 9956.2734 | 13593.6326 | 18893.6143 | 26744.9241 | 38082.3027 | 54203.0945 | 79272.4288 | 92970.8095 | 94168.1728 | 95220.4866 | 96676.413 | 98701.2794 | 101530.0016 | 105496.7402 | 111077.2777 | 118949.5905 | 124954.7313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139.8952 | 152.0419 | 166.9567 | 185.3072 | 207.9274 | 235.8604 | 270.4121 | 313.2184 | 376.7113 | 474.1984 | 605.089 | 783.5522 | 1030.9264 | 1384.6695 | 1894.9951 | 2639.2746 | 3742.6573 | 5336.7299 | 7604.1042 | 11131.4547 | 13056.8918 | 13220.8936 | 13363.8575 | 13563.034 | 13841.6337 | 14232.6605 | 14783.0883 | 15559.8298 | 16658.2677 | 17492.3522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 431.2276 | 467.226 | 507.4223 | 552.3244 | 602.5032 | 658.6007 | 721.339 | 791.5304 | 885.1225 | 1020.6343 | 1192.9404 | 1418.7592 | 1724.3557 | 2154.4612 | 2775.6054 | 3694.1091 | 5083.7531 | 7225.7312 | 10576.5827 | 15880.2796 | 18460.3861 | 18864.027 | 19333.9077 | 19885.6419 | 20539.5821 | 21322.9511 | 22272.554 | 23438.6256 | 24890.2996 | 26270.3691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not replacedDDL | Future | Not replaced | DDL | [145 empty] | 457.2238 | 540.8994 | 647.0493 | 781.9558 | 953.6997 | 1172.6822 | 1452.3014 | 1809.8258 | 2283.1454 | 2919.1688 | 3754.5593 | 4853.116 | 6301.042 | 8221.7131 | 10788.3717 | 14247.4643 | 18954.3626 | 25428.632 | 30338.464 | 35698.821 | 38250.0902 | 38585.5401 | 39059.7419 | 39731.1028 | 40682.8773 | 42033.8053 | 43052.6264 | 43052.6264 | 43052.6264 | 43052.6264 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270.0381 | 319.8473 | 383.0251 | 463.3054 | 565.4897 | 695.7572 | 862.0655 | 1074.6687 | 1356.4434 | 1735.6784 | 2233.1499 | 2887.1226 | 3749.5658 | 4894.4452 | 6425.8293 | 8492.0842 | 11307.6453 | 15186.7722 | 18090.1837 | 21376.845 | 22916.1204 | 23070.158 | 23287.9099 | 23596.1968 | 24033.2488 | 24653.5908 | 25121.4303 | 25121.4303 | 25121.4303 | 25121.4303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77848 | 0.96392 | 1.1989 | 1.4972 | 1.8764 | 2.3594 | 2.9752 | 3.7615 | 4.7713 | 6.0725 | 7.7432 | 9.8919 | 12.6599 | 16.2318 | 20.8502 | 26.8349 | 34.6099 | 44.7406 | 47.1191 | 48.6792 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.9184 | 192.3289 | 229.6473 | 277.0873 | 337.4968 | 414.5432 | 512.9519 | 638.8156 | 805.2151 | 1028.3703 | 1322.0909 | 1708.5977 | 2217.6881 | 2892.3968 | 3792.9961 | 5004.9805 | 6651.253 | 8910.9264 | 10665.9884 | 12481.2162 | 13367.171 | 13526.1723 | 13750.9411 | 14069.1623 | 14520.2977 | 15160.6296 | 15643.5448 | 15643.5448 | 15643.5448 | 15643.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9576 | 27.1016 | 32.3599 | 39.0444 | 47.5563 | 58.4125 | 72.2787 | 90.0134 | 113.46 | 144.9041 | 186.2917 | 240.754 | 312.4899 | 407.5637 | 534.4691 | 705.2541 | 937.2386 | 1255.6645 | 1503.0216 | 1758.8649 | 1883.7343 | 1906.1453 | 1937.8263 | 1982.6792 | 2046.2663 | 2136.5204 | 2204.5868 | 2204.5868 | 2204.5868 | 2204.5868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53119 | 0.65772 | 0.81806 | 1.0216 | 1.2804 | 1.6099 | 2.0301 | 2.5666 | 3.2557 | 4.1435 | 5.2835 | 6.7497 | 8.6383 | 11.0756 | 14.2269 | 18.3106 | 23.6157 | 30.5283 | 32.1512 | 33.2157 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not replacedECA | Future | Not replaced | ECA | [145 empty] | 683.0002 | 683.0002 | 683.0002 | 683.0002 | 683.0002 | 697.8367 | 730.8489 | 780.9356 | 967.8452 | 1325.749 | 1865.958 | 2694.8136 | 3956.1722 | 5882.9073 | 8838.7822 | 13394.6584 | 20455.9194 | 31455.6188 | 48668.3075 | 75713.176 | 98956.5879 | 104229.3918 | 105597.2961 | 107531.1062 | 110269.0697 | 114150.7946 | 118759.9531 | 121941.7864 | 123379.6682 | 124464.0667 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359.1826 | 359.1826 | 359.1826 | 359.1826 | 359.1826 | 368.2555 | 388.4434 | 419.1075 | 527.125 | 725.7914 | 1023.8537 | 1477.4624 | 2164.3007 | 3208.8509 | 4804.9305 | 7255.6569 | 11039.4903 | 16910.8817 | 26062.81 | 40386.4567 | 53540.9853 | 56600.2157 | 57203.551 | 58056.5149 | 59264.2087 | 60976.4498 | 62993.3216 | 64366.107 | 64986.4735 | 65454.3316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7227 | 2.7227 | 2.7227 | 2.7227 | 2.7227 | 2.7399 | 2.7781 | 2.8304 | 3.321 | 4.6568 | 6.7074 | 9.9388 | 15.0038 | 22.9652 | 35.5238 | 55.4117 | 87.058 | 137.6247 | 218.7154 | 349.1615 | 419.7642 | 427.5123 | 431.4031 | 436.8993 | 444.6756 | 455.6936 | 471.3244 | 485.1768 | 491.4367 | 496.1577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264.2659 | 264.2659 | 264.2659 | 264.2659 | 264.2659 | 269.1724 | 280.0896 | 296.672 | 362.568 | 493.6749 | 692.9694 | 1001.2146 | 1472.3711 | 2194.785 | 3306.8267 | 5026.256 | 7699.8175 | 11878.0461 | 18437.4286 | 28776.808 | 37148.152 | 39012.8251 | 39635.902 | 40516.7754 | 41763.9851 | 43532.2504 | 45615.3182 | 47033.4074 | 47674.247 | 48157.5451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.2188 | 37.2188 | 37.2188 | 37.2188 | 37.2188 | 37.9102 | 39.4487 | 41.7856 | 51.0687 | 69.534 | 97.6028 | 141.0154 | 207.3706 | 309.1093 | 465.7163 | 707.8551 | 1084.3512 | 1672.7243 | 2596.3885 | 4052.3048 | 5231.5143 | 5494.2711 | 5582.0492 | 5706.1453 | 5881.8505 | 6130.9613 | 6424.3911 | 6624.1129 | 6714.3679 | 6782.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6102 | 19.6102 | 19.6102 | 19.6102 | 19.6102 | 19.7587 | 20.089 | 20.54 | 23.7625 | 32.0919 | 44.8248 | 65.1824 | 97.126 | 147.1968 | 225.7849 | 349.4787 | 545.2024 | 856.342 | 1352.9649 | 2148.4449 | 2616.1721 | 2694.5676 | 2744.3908 | 2814.7712 | 2914.3498 | 3055.4395 | 3255.5978 | 3432.9823 | 3513.143 | 3573.5973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not replacedFDN | Future | Not replaced | FDN | [145 empty] | 116.6014 | 148.2232 | 189.5659 | 243.7891 | 315.1131 | 409.1823 | 533.5548 | 698.3614 | 917.1949 | 1208.309 | 1596.2364 | 2113.9721 | 2805.9226 | 3731.8882 | 4972.4437 | 6636.209 | 8869.6776 | 11870.5022 | 15905.4606 | 16036.9191 | 16036.9191 | 16036.9191 | 16036.9191 | 16036.9191 | 16036.9191 | 16036.9191 | 16036.9191 | 16036.9191 | 16036.9191 | 16036.9191 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8988 | 91.3974 | 116.8902 | 150.3254 | 194.3052 | 252.3102 | 329.0008 | 430.6239 | 565.5612 | 745.0681 | 984.2721 | 1303.5186 | 1730.1895 | 2301.1589 | 3066.1108 | 4092.0227 | 5469.2253 | 7319.5953 | 9807.6335 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32404 | 0.41192 | 0.52681 | 0.6775 | 0.87571 | 1.1371 | 1.4828 | 1.9408 | 2.5489 | 3.3579 | 4.436 | 5.8748 | 7.7978 | 10.3711 | 13.8187 | 18.4423 | 24.6492 | 32.9887 | 44.202 | 44.5673 | 44.5673 | 44.5673 | 44.5673 | 44.5673 | 44.5673 | 44.5673 | 44.5673 | 44.5673 | 44.5673 | 44.5673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.8908 | 49.4378 | 63.2271 | 81.3125 | 105.1016 | 136.4771 | 177.9598 | 232.9287 | 305.9175 | 403.0146 | 532.4024 | 705.0859 | 935.8763 | 1244.7193 | 1658.4892 | 2213.4149 | 2958.3572 | 3959.2404 | 5305.0445 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4793 | 6.9652 | 8.908 | 11.456 | 14.8077 | 19.2281 | 25.0726 | 32.8171 | 43.1005 | 56.7804 | 75.0097 | 99.3389 | 131.8548 | 175.3674 | 233.6631 | 311.8461 | 416.8003 | 557.8139 | 747.423 | 753.6005 | 753.6005 | 753.6005 | 753.6005 | 753.6005 | 753.6005 | 753.6005 | 753.6005 | 753.6005 | 753.6005 | 753.6005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0084865 | 0.010788 | 0.013797 | 0.017743 | 0.022935 | 0.029781 | 0.038833 | 0.050828 | 0.066755 | 0.087943 | 0.11618 | 0.15386 | 0.20422 | 0.27161 | 0.3619 | 0.483 | 0.64555 | 0.86396 | 1.1576 | 1.1672 | 1.1672 | 1.1672 | 1.1672 | 1.1672 | 1.1672 | 1.1672 | 1.1672 | 1.1672 | 1.1672 | 1.1672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not replacedGCY | Future | Not replaced | GCY | [145 empty] | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 30.9493 | 37.0444 | 49.1045 | 65.6594 | 88.4865 | 120.091 | 164.0094 | 225.2426 | 310.8722 | 430.9392 | 599.6966 | 837.3975 | 1172.8474 | 1647.0491 | 2318.4101 | 3270.1846 | 4621.1126 | 5639.9336 | 5639.9336 | 5639.9336 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not replacedMLN | Future | Not replaced | MLN | [145 empty] | 2148.6798 | 2213.6442 | 2296.0896 | 2400.8841 | 2534.2793 | 2704.3091 | 2921.3027 | 3198.5484 | 3674.9641 | 4375.9846 | 5332.4072 | 6659.5597 | 8793.7532 | 11960.2448 | 16444.3949 | 22861.6757 | 31571.4024 | 41761.0772 | 57419.6666 | 81593.2979 | 109521.8001 | 117603.807 | 128988.5268 | 145056.1062 | 167771.1571 | 199932.3006 | 245528.8046 | 308958.818 | 355693.615 | 355693.615 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964.2623 | 994.0694 | 1031.8971 | 1079.9791 | 1141.1837 | 1219.1971 | 1318.7584 | 1445.9648 | 1675.5556 | 2019.5091 | 2492.1748 | 3154.1249 | 4202.273 | 5755.5136 | 7972.8906 | 11172.2641 | 15575.1552 | 20899.3131 | 29119.68 | 41865.246 | 56460.0522 | 59855.857 | 64639.5329 | 71391.092 | 80936.1814 | 94450.9637 | 113612.0074 | 140020.939 | 159263.9932 | 159263.9932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5123 | 30.5159 | 30.5204 | 30.5261 | 30.5333 | 30.5426 | 30.5545 | 30.5696 | 30.8068 | 31.2733 | 31.9751 | 33.0837 | 40.6089 | 54.728 | 74.5423 | 102.5378 | 142.3189 | 199.1042 | 280.874 | 399.2947 | 554.6719 | 717.3191 | 946.4184 | 1269.7353 | 1726.7929 | 2373.891 | 3291.2803 | 4586.859 | 5558.3427 | 5558.3427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 650.9154 | 681.6833 | 720.7303 | 770.3621 | 833.5396 | 914.0676 | 1016.8381 | 1148.1448 | 1362.2613 | 1670.9115 | 2088.4516 | 2661.632 | 3523.698 | 4766.6628 | 6514.8131 | 9000.161 | 12302.0651 | 15896.4573 | 21458.1607 | 30098.5818 | 39952.0997 | 41985.6593 | 44850.3058 | 48893.3546 | 54609.2069 | 62702.1516 | 74176.1182 | 90035.7214 | 101631.9746 | 101631.9746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.4054 | 95.7421 | 101.2457 | 108.2412 | 117.1459 | 128.4961 | 142.9814 | 161.4888 | 191.6659 | 235.1652 | 294.0101 | 374.7885 | 496.214 | 671.2541 | 917.4378 | 1267.4401 | 1732.408 | 2238.419 | 3021.4527 | 4238.0368 | 5625.1977 | 5910.0076 | 6311.2155 | 6877.4647 | 7677.9989 | 8811.4574 | 10418.4459 | 12639.3317 | 14262.9096 | 14262.9096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411.5844 | 411.6336 | 411.6962 | 411.7756 | 411.8768 | 412.0057 | 412.1702 | 412.3805 | 414.6744 | 419.1255 | 425.7956 | 435.9305 | 530.9593 | 712.0863 | 964.7112 | 1319.2727 | 1819.4552 | 2527.7837 | 3539.4992 | 4992.1387 | 6929.7786 | 9134.964 | 12241.0541 | 16624.4595 | 22820.977 | 31593.837 | 44030.9526 | 61675.9669 | 74976.3948 | 74976.3948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not replacedSA | Future | Not replaced | SA | [145 empty] | 444.8025 | 476.5101 | 536.8883 | 617.964 | 736.0349 | 885.4732 | 1076.5715 | 1323.3707 | 1645.0898 | 2068.113 | 2628.7529 | 3377.0975 | 4382.3686 | 5740.3884 | 7583.993 | 10097.559 | 13537.2765 | 18259.4555 | 24760.0565 | 28265.8025 | 32247.8359 | 34753.7496 | 35073.1282 | 35431.1218 | 35832.4445 | 36282.3889 | 36597.9281 | 36597.9281 | 36597.9281 | 36597.9281 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313.9785 | 337.9735 | 380.1332 | 435.6357 | 514.6142 | 613.6539 | 739.185 | 899.9582 | 1107.9268 | 1379.4725 | 1737.1096 | 2211.8576 | 2846.544 | 3700.4077 | 4855.5174 | 6425.7245 | 8569.1569 | 11505.6622 | 15541.1667 | 17739.6982 | 20238.248 | 21828.8566 | 22072.946 | 22346.5475 | 22653.2638 | 22997.1399 | 23238.295 | 23238.295 | 23238.295 | 23238.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27094 | 0.27537 | 0.34955 | 0.45158 | 0.59458 | 0.78829 | 1.0516 | 1.4108 | 1.9021 | 2.5759 | 3.5024 | 4.7791 | 6.5417 | 8.9794 | 12.3564 | 17.041 | 23.5478 | 32.596 | 45.191 | 47.5869 | 48.707 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.2355 | 120.9883 | 136.8392 | 159.0924 | 193.1301 | 236.9974 | 294.0496 | 368.8822 | 467.8061 | 599.5087 | 775.973 | 1013.7585 | 1335.7847 | 1773.8172 | 2371.9359 | 3191.3727 | 4317.2647 | 5868.0827 | 8008.8004 | 9150.7503 | 10449.2041 | 11250.3838 | 11316.372 | 11390.3386 | 11473.2576 | 11566.2226 | 11631.4175 | 11631.4175 | 11631.4175 | 11631.4175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.0994 | 17.0512 | 19.2848 | 22.4207 | 27.2172 | 33.3989 | 41.4384 | 51.9834 | 65.9231 | 84.4816 | 109.3474 | 142.8539 | 188.2305 | 249.9532 | 334.2331 | 449.6983 | 608.3449 | 826.8661 | 1128.5075 | 1289.447 | 1472.4546 | 1585.3753 | 1594.6763 | 1605.1018 | 1616.7891 | 1629.8925 | 1639.0816 | 1639.0816 | 1639.0816 | 1639.0816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21818 | 0.22175 | 0.28148 | 0.36364 | 0.4788 | 0.63479 | 0.84684 | 1.136 | 1.5317 | 2.0743 | 2.8204 | 3.8484 | 5.2678 | 7.2309 | 9.9502 | 13.7225 | 18.9623 | 26.2485 | 36.3908 | 38.3201 | 39.2222 | 39.7596 | 39.7596 | 39.7596 | 39.7596 | 39.7596 | 39.7596 | 39.7596 | 39.7596 | 39.7596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not replacedSHL | Future | Not replaced | SHL | [145 empty] | 5365.7002 | 5365.7002 | 5365.7002 | 5830.0985 | 7489.1668 | 9963.3907 | 13563.9034 | 18615.4218 | 25732.8425 | 35799.4226 | 50086.0482 | 70424.1292 | 99456.4189 | 141001.125 | 200580.8008 | 286191.0154 | 409418.0669 | 587064.9756 | 843517.8897 | 910566.4936 | 940339.4085 | 977798.9189 | 977798.9189 | 977798.9189 | 977798.9189 | 977798.9189 | 977798.9189 | 977798.9189 | 977798.9189 | 977798.9189 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 516.7386 | 516.7386 | 516.7386 | 531.342 | 583.513 | 723.084 | 975.4906 | 1328.2248 | 1823.6626 | 2522.7639 | 3513.4286 | 4922.6797 | 6934.4475 | 9815.5641 | 13953.8045 | 19913.6209 | 28517.8884 | 40967.9277 | 59019.9031 | 70719.3042 | 81102.3277 | 94165.9788 | 94165.9788 | 94165.9788 | 94165.9788 | 94165.9788 | 94165.9788 | 94165.9788 | 94165.9788 | 94165.9788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.8263 | 263.8263 | 263.8263 | 289.8608 | 382.8691 | 515.0633 | 702.2587 | 965.0911 | 1335.65 | 1860.0311 | 2604.5551 | 3664.7783 | 5178.5571 | 7344.9984 | 10451.9656 | 14916.0197 | 21340.4392 | 30599.5372 | 43961.2295 | 46702.137 | 47311.1663 | 48077.4312 | 48077.4312 | 48077.4312 | 48077.4312 | 48077.4312 | 48077.4312 | 48077.4312 | 48077.4312 | 48077.4312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433.6738 | 433.6738 | 433.6738 | 450.7537 | 511.772 | 644.0991 | 869.3666 | 1183.8733 | 1625.0737 | 2246.7036 | 3126.0225 | 4374.3286 | 6152.2443 | 8691.9603 | 12329.6384 | 17552.659 | 25068.5783 | 35905.8544 | 51561.1078 | 60525.375 | 68719.4266 | 79028.97 | 79028.97 | 79028.97 | 79028.97 | 79028.97 | 79028.97 | 79028.97 | 79028.97 | 79028.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.1501 | 58.1501 | 58.1501 | 60.2636 | 67.8141 | 84.9737 | 114.6128 | 155.9768 | 213.9827 | 295.6846 | 411.2238 | 575.2099 | 808.7272 | 1142.2567 | 1619.9329 | 2305.7528 | 3292.6409 | 4715.6957 | 6771.5635 | 8004.1948 | 9152.2792 | 10596.7691 | 10596.7691 | 10596.7691 | 10596.7691 | 10596.7691 | 10596.7691 | 10596.7691 | 10596.7691 | 10596.7691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4093.3114 | 4093.3114 | 4093.3114 | 4497.8784 | 5943.1986 | 7996.1706 | 10902.1747 | 14982.2559 | 20734.4734 | 28874.2394 | 40430.8183 | 56887.1327 | 80382.4428 | 114006.3455 | 162225.4594 | 231502.963 | 331198.5201 | 474875.9607 | 682204.0859 | 724615.4825 | 734054.2088 | 745929.7697 | 745929.7697 | 745929.7697 | 745929.7697 | 745929.7697 | 745929.7697 | 745929.7697 | 745929.7697 | 745929.7697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not replacedSHN | Future | Not replaced | SHN | [145 empty] | 3852.391 | 4361.158 | 4945.9793 | 5619.7382 | 6397.8277 | 7298.712 | 8344.6264 | 9562.4568 | 10984.8428 | 12651.5706 | 14611.3308 | 16923.947 | 19663.2032 | 22920.4409 | 26809.1422 | 31470.78 | 37082.2963 | 43865.6746 | 48199.894 | 52556.1056 | 57517.1951 | 63168.4813 | 69607.4415 | 76945.4574 | 85309.8115 | 94845.9716 | 103757.1128 | 105078.5904 | 106557.5944 | 108213.1753 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 529.66 | 616.4194 | 720.2639 | 845.0864 | 995.7653 | 1178.4317 | 1400.8112 | 1672.6631 | 2006.3436 | 2417.5309 | 2926.1562 | 3557.6041 | 4344.2571 | 5327.4876 | 6560.2254 | 8110.2714 | 10064.5733 | 12534.7473 | 13252.8884 | 13713.3481 | 14238.3368 | 14837.0253 | 15519.8996 | 16298.9509 | 17187.8926 | 18202.4088 | 19140.468 | 19220.8811 | 19310.8798 | 19411.6234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2930.8813 | 3291.6478 | 3699.8568 | 4161.9661 | 4685.3318 | 5278.335 | 5950.5267 | 6712.7934 | 7577.5461 | 8558.9371 | 9673.1062 | 10938.4643 | 12376.016 | 14009.7293 | 15866.9582 | 17978.9261 | 20381.279 | 23114.7181 | 26224.5518 | 29764.5056 | 33795.2658 | 38385.9761 | 43615.6236 | 49574.4507 | 56365.5698 | 64106.8113 | 71352.9709 | 72499.9675 | 73783.6916 | 75220.6783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224.2332 | 263.2341 | 310.4075 | 367.7102 | 437.6115 | 523.2339 | 628.5346 | 758.5396 | 919.6433 | 1119.9953 | 1369.9986 | 1682.9511 | 2075.8741 | 2570.5794 | 3195.0488 | 3985.2132 | 4987.2523 | 6260.5643 | 6577.7738 | 6745.648 | 6936.9835 | 7155.1069 | 7403.8214 | 7687.4748 | 8011.0384 | 8380.1967 | 8722.6167 | 8758.4154 | 8798.4815 | 8843.3311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.3414 | 31.1905 | 37.1063 | 44.353 | 53.2654 | 64.2685 | 77.903 | 94.8576 | 116.0114 | 142.4876 | 175.7234 | 217.5601 | 270.3588 | 337.151 | 421.8313 | 529.4079 | 666.3256 | 840.8831 | 880.0076 | 897.3119 | 917.0415 | 939.5413 | 965.2054 | 994.4845 | 1027.8943 | 1066.0242 | 1101.2745 | 1104.2604 | 1107.6022 | 1111.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.2751 | 158.6663 | 178.3449 | 200.6224 | 225.8536 | 254.4429 | 286.8509 | 323.6031 | 365.2983 | 412.6197 | 466.3464 | 527.3674 | 596.6971 | 675.4935 | 765.0785 | 866.9614 | 982.8661 | 1114.7618 | 1264.6724 | 1435.2919 | 1629.5675 | 1850.8316 | 2102.8914 | 2390.0964 | 2717.4164 | 3090.5307 | 3439.7828 | 3495.066 | 3556.9393 | 3626.1995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not replacedTYA | Future | Not replaced | TYA | [145 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not replacedWBE | Future | Not replaced | WBE | [145 empty] | 535.6717 | 535.6717 | 548.4939 | 646.2202 | 789.4162 | 986.4479 | 1258.7378 | 1636.5194 | 2204.5779 | 3043.67 | 4239.1956 | 5944.5926 | 8382.0133 | 11880.0819 | 16920.841 | 24214.1338 | 34809.4367 | 50264.7161 | 72902.4872 | 85491.1787 | 92813.6609 | 93149.1108 | 93623.3125 | 94294.6735 | 95246.448 | 96597.376 | 97616.197 | 97616.197 | 97616.197 | 97616.197 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.6041 | 210.6041 | 215.1448 | 249.7142 | 300.2885 | 369.8744 | 466.0361 | 599.4486 | 805.7828 | 1112.7253 | 1551.5663 | 2179.3665 | 3078.9125 | 4373.443 | 6244.3826 | 8959.8759 | 12917.8419 | 18711.1981 | 27227.078 | 32488.941 | 36173.3704 | 36327.408 | 36545.1599 | 36853.4468 | 37290.4987 | 37910.8407 | 38378.6802 | 38378.6802 | 38378.6802 | 38378.6802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6815 | 2.6815 | 2.7538 | 3.31 | 4.1368 | 5.2746 | 6.8476 | 9.0306 | 12.2425 | 16.9536 | 23.6204 | 33.0932 | 46.6067 | 65.9595 | 93.7808 | 133.9293 | 192.0889 | 276.666 | 400.1443 | 460.9229 | 488.6621 | 488.6621 | 488.6621 | 488.6621 | 488.6621 | 488.6621 | 488.6621 | 488.6621 | 488.6621 | 488.6621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.9175 | 190.9175 | 195.61 | 231.3363 | 283.604 | 355.5199 | 454.9015 | 592.7812 | 798.3802 | 1100.0996 | 1530.1212 | 2143.0226 | 3017.4759 | 4270.0198 | 6071.096 | 8670.8999 | 12438.0888 | 17917.9857 | 25920.462 | 30098.9768 | 32514.7819 | 32673.7832 | 32898.552 | 33216.7731 | 33667.9086 | 34308.2405 | 34791.1556 | 34791.1556 | 34791.1556 | 34791.1556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.8804 | 26.8804 | 27.5409 | 32.5703 | 39.928 | 50.0516 | 64.0416 | 83.451 | 112.394 | 154.8684 | 215.4051 | 301.6873 | 424.7902 | 601.1197 | 854.6704 | 1220.6646 | 1751.0017 | 2522.4518 | 3649.0287 | 4237.3472 | 4577.5916 | 4600.0027 | 4631.6836 | 4676.5366 | 4740.1236 | 4830.3778 | 4898.4441 | 4898.4441 | 4898.4441 | 4898.4441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5882 | 104.5882 | 107.4444 | 129.2894 | 161.459 | 205.7274 | 266.911 | 351.808 | 475.7785 | 659.0231 | 918.4826 | 1287.423 | 1814.228 | 2569.5399 | 3656.9112 | 5228.7641 | 7510.4154 | 10836.4146 | 15705.7743 | 18204.9908 | 19059.2549 | 19059.2549 | 19059.2549 | 19059.2549 | 19059.2549 | 19059.2549 | 19059.2549 | 19059.2549 | 19059.2549 | 19059.2549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ReplacedAC | New | Replaced | AC | [145 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1203.0793 | 1594.7528 | 2132.4007 | 2873.751 | 3900.1598 | 5326.4843 | 7315.1376 | 10096.1069 | 13995.4862 | 19476.1692 | 27195.9119 | 38090.2212 | 53490.7316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 626.0093 | 829.8125 | 1109.5717 | 1495.3254 | 2029.4061 | 2771.5787 | 3806.3531 | 5253.4005 | 7282.4005 | 10134.2149 | 14151.0998 | 19819.8363 | 27833.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 15.5796 | 20.6516 | 27.614 | 37.2143 | 50.506 | 68.9766 | 94.7291 | 130.7419 | 181.2378 | 252.2112 | 352.1798 | 493.2583 | 692.6908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 491.9587 | 652.1204 | 871.9733 | 1175.1235 | 1594.8388 | 2178.0861 | 2991.2788 | 4128.4623 | 5722.982 | 7964.1224 | 11120.8507 | 15575.711 | 21873.2302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 69.2977 | 91.8582 | 122.8268 | 165.5288 | 224.6502 | 306.8068 | 421.3537 | 581.5382 | 806.1434 | 1121.8321 | 1566.4911 | 2194.006 | 3081.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.081413 | 0.10792 | 0.1443 | 0.19447 | 0.26392 | 0.36044 | 0.49502 | 0.68321 | 0.94708 | 1.318 | 1.8404 | 2.5776 | 3.6197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ReplacedBAN | New | Replaced | BAN | [145 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 744.8096 | 744.8096 | 744.8096 | 744.8096 | 744.8096 | 744.8096 | 744.8096 | 744.8096 | 744.8096 | 744.8096 | 744.8096 | 744.8096 | 744.8096 | 744.8096 | 744.8096 | 744.8096 | 744.8096 | 891.4904 | 1181.7234 | 1580.1243 | 2129.4703 | 2890.0466 | 3946.9634 | 5420.5698 | 7481.2881 | 10370.7564 | 14431.9821 | 20152.3671 | 28225.1291 | 39637.0185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 522.6933 | 692.8609 | 926.4489 | 1248.5382 | 1694.4747 | 2314.1597 | 3178.1558 | 4386.3837 | 6080.5193 | 8461.6726 | 11815.6142 | 16548.7873 | 23239.7373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.97683 | 1.2949 | 1.7314 | 2.3333 | 3.1667 | 4.3248 | 5.9395 | 8.1975 | 11.3636 | 15.8136 | 22.0816 | 30.9271 | 43.4315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 316.0949 | 419.0025 | 560.2631 | 755.0441 | 1024.7209 | 1399.4708 | 1921.966 | 2652.6328 | 3677.1487 | 5117.1334 | 7145.4046 | 10007.7557 | 14054.0579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 44.5482 | 59.0513 | 78.9596 | 106.4107 | 144.417 | 197.2317 | 270.8685 | 373.8436 | 518.2317 | 721.1731 | 1007.0235 | 1410.4233 | 1980.6809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 7.1681 | 9.5018 | 12.7052 | 17.1222 | 23.2377 | 31.736 | 43.5847 | 60.1541 | 83.3871 | 116.0418 | 162.0372 | 226.9471 | 318.7056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ReplacedDDL | New | Replaced | DDL | [145 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1006.5229 | 1006.5229 | 1006.5229 | 1006.5229 | 1006.5229 | 1006.5229 | 1006.5229 | 1006.5229 | 1006.5229 | 1006.5229 | 1006.5229 | 1006.5229 | 1006.5229 | 1006.5229 | 1006.5229 | 1006.5229 | 1006.5229 | 1204.7448 | 1596.9606 | 2135.3527 | 2877.7294 | 3905.5591 | 5333.8582 | 7325.2646 | 10110.0837 | 14014.8613 | 19503.1316 | 27233.5614 | 38142.9526 | 53564.7831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 538.1733 | 713.3805 | 953.8865 | 1285.5146 | 1744.6579 | 2382.6954 | 3272.2794 | 4516.2899 | 6260.5986 | 8712.2717 | 12165.5429 | 17038.8926 | 23928.0004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 8.9824 | 11.9067 | 15.9208 | 21.4559 | 29.1192 | 39.7684 | 54.616 | 75.3791 | 104.4925 | 145.4121 | 203.0489 | 284.3875 | 399.3702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 492.0069 | 652.1843 | 872.0588 | 1175.2387 | 1594.9951 | 2178.2996 | 2991.572 | 4128.867 | 5723.5429 | 7964.903 | 11121.9408 | 15577.2377 | 21875.3742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 69.2977 | 91.8583 | 122.8269 | 165.529 | 224.6504 | 306.8072 | 421.3542 | 581.5389 | 806.1444 | 1121.8335 | 1566.4931 | 2194.0087 | 3081.0829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 96.2184 | 127.5431 | 170.5425 | 229.8333 | 311.9221 | 425.9949 | 585.0409 | 807.4538 | 1119.3135 | 1557.6407 | 2175.0406 | 3046.332 | 4278.0147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ReplacedECA | New | Replaced | ECA | [145 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 308.6779 | 308.6779 | 308.6779 | 308.6779 | 308.6779 | 308.6779 | 308.6779 | 308.6779 | 308.6779 | 308.6779 | 308.6779 | 308.6779 | 308.6779 | 308.6779 | 308.6779 | 308.6779 | 308.6779 | 369.4681 | 489.7519 | 654.8647 | 882.5349 | 1197.7472 | 1635.7744 | 2246.4939 | 3100.5353 | 4298.0428 | 5981.1719 | 8351.9209 | 11697.5859 | 16427.1145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 197.9456 | 262.3886 | 350.8491 | 472.8253 | 641.7028 | 876.3794 | 1203.5774 | 1661.137 | 2302.7114 | 3204.4615 | 4474.6096 | 6267.0768 | 8800.9602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.8968 | 2.5143 | 3.3619 | 4.5307 | 6.1489 | 8.3977 | 11.533 | 15.9174 | 22.0651 | 30.7059 | 42.8767 | 60.0526 | 84.3328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 140.5286 | 186.279 | 249.0803 | 335.6755 | 455.5677 | 622.173 | 854.4625 | 1179.3004 | 1634.7769 | 2274.9614 | 3176.6848 | 4449.2211 | 6248.1152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 19.7993 | 26.2451 | 35.0933 | 47.2938 | 64.1856 | 87.6588 | 120.3864 | 166.1533 | 230.3261 | 320.5226 | 447.5677 | 626.8571 | 880.3059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 9.2763 | 12.2963 | 16.4418 | 22.158 | 30.0721 | 41.0698 | 56.4033 | 77.8459 | 107.912 | 150.1708 | 209.6938 | 293.6942 | 412.4396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ReplacedFDN | New | Replaced | FDN | [145 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 527.5134 | 527.5134 | 527.5134 | 527.5134 | 527.5134 | 527.5134 | 527.5134 | 527.5134 | 527.5134 | 527.5134 | 527.5134 | 527.5134 | 527.5134 | 527.5134 | 527.5134 | 527.5134 | 527.5134 | 631.4005 | 836.9588 | 1119.1273 | 1508.2031 | 2046.8833 | 2795.4475 | 3839.1332 | 5298.6425 | 7345.1162 | 10221.4903 | 14272.9685 | 19990.5239 | 28073.0254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 389.7004 | 516.571 | 690.7254 | 930.863 | 1263.3365 | 1725.3503 | 2369.5132 | 3270.3224 | 4533.4061 | 6308.7043 | 8809.2769 | 12338.1524 | 17326.6727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.2533 | 1.6613 | 2.2214 | 2.9936 | 4.0629 | 5.5487 | 7.6203 | 10.5173 | 14.5793 | 20.2886 | 28.3304 | 39.6791 | 55.7221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 210.7232 | 279.326 | 373.4968 | 503.3466 | 683.1254 | 932.9507 | 1281.2696 | 1768.3653 | 2451.354 | 3411.313 | 4763.4505 | 6671.6235 | 9369.0719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 29.6988 | 39.3675 | 52.6397 | 70.9404 | 96.278 | 131.4877 | 180.5789 | 249.2289 | 345.4877 | 480.7819 | 671.3487 | 940.2818 | 1320.4534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0088258 | 0.011699 | 0.015643 | 0.021082 | 0.028612 | 0.039075 | 0.053664 | 0.074065 | 0.10267 | 0.14288 | 0.19951 | 0.27943 | 0.39241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ReplacedGCY | New | Replaced | GCY | [145 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1507.5999 | 1507.5999 | 1507.5999 | 1507.5999 | 1507.5999 | 1507.5999 | 1507.5999 | 1507.5999 | 1507.5999 | 1507.5999 | 1507.5999 | 1507.5999 | 1507.5999 | 1507.5999 | 1507.5999 | 1507.5999 | 1507.5999 | 1804.5026 | 2391.9751 | 3198.3949 | 4310.3488 | 5849.8627 | 7989.2117 | 10971.9994 | 15143.1845 | 20991.8766 | 29212.3714 | 40791.2393 | 57131.6503 | 80230.9273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 927.8758 | 1229.9543 | 1644.6156 | 2216.3826 | 3008.0011 | 4108.055 | 5641.8053 | 7786.6299 | 10794.0291 | 15021.0099 | 20974.8671 | 29377.1112 | 41254.7662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 11.3537 | 15.05 | 20.1239 | 27.1202 | 36.8066 | 50.2672 | 69.0345 | 95.2791 | 132.0784 | 183.8008 | 256.6537 | 359.4656 | 504.8036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 702.7486 | 931.5349 | 1245.5883 | 1678.6296 | 2278.1805 | 3111.3322 | 4272.9541 | 5897.3875 | 8175.1121 | 11376.5155 | 15885.8095 | 22249.4469 | 31245.2686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 98.9966 | 131.2258 | 175.4667 | 236.4694 | 320.9285 | 438.295 | 601.9333 | 830.7681 | 1151.6324 | 1602.6159 | 2237.8425 | 3134.2915 | 4401.5378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 63.4336 | 84.085 | 112.433 | 151.5215 | 205.64 | 280.8444 | 385.6982 | 532.3277 | 737.9266 | 1026.9013 | 1433.9328 | 2008.3466 | 2820.3545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ReplacedMLN | New | Replaced | MLN | [145 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 726.5133 | 726.5133 | 726.5133 | 726.5133 | 726.5133 | 726.5133 | 726.5133 | 726.5133 | 726.5133 | 726.5133 | 726.5133 | 726.5133 | 726.5133 | 726.5133 | 726.5133 | 726.5133 | 726.5133 | 869.5909 | 1152.6943 | 1541.3085 | 2077.1598 | 2819.0525 | 3850.0061 | 5287.4133 | 7297.51 | 10115.9984 | 14077.4599 | 19657.3235 | 27531.7777 | 38663.3336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 371.1561 | 491.9894 | 657.8565 | 886.5669 | 1203.2192 | 1643.2476 | 2256.7573 | 3114.7005 | 4317.679 | 6008.4977 | 8390.0777 | 11751.0278 | 16502.1639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 6.3 | 8.351 | 11.1665 | 15.0486 | 20.4235 | 27.8925 | 38.3062 | 52.8689 | 73.2883 | 101.9883 | 142.4132 | 199.462 | 280.1078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 351.4724 | 465.8975 | 622.968 | 839.5491 | 1139.4082 | 1556.1004 | 2137.0735 | 2949.5169 | 4088.6972 | 5689.8458 | 7945.1222 | 11127.8292 | 15626.9958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 49.4985 | 65.6131 | 87.7337 | 118.2351 | 160.4648 | 219.1483 | 300.9677 | 415.3855 | 575.8182 | 801.3107 | 1118.9252 | 1567.1512 | 2200.7766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 91.1258 | 120.7926 | 161.5161 | 217.6688 | 295.4129 | 403.4481 | 554.0762 | 764.7174 | 1060.0711 | 1475.1988 | 2059.9213 | 2885.0976 | 4051.5905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ReplacedSA | New | Replaced | SA | [145 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2289.3644 | 2289.3644 | 2289.3644 | 2289.3644 | 2289.3644 | 2289.3644 | 2289.3644 | 2289.3644 | 2289.3644 | 2289.3644 | 2289.3644 | 2289.3644 | 2289.3644 | 2289.3644 | 2289.3644 | 2289.3644 | 2289.3644 | 2740.2257 | 3632.3315 | 4856.9195 | 6545.476 | 8883.3034 | 12132.0097 | 16661.5192 | 22995.6683 | 31877.1942 | 44360.4186 | 61943.4973 | 86757.2128 | 121834.5978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1331.5006 | 1764.983 | 2360.0214 | 3180.5064 | 4316.478 | 5895.054 | 8095.9839 | 11173.8046 | 15489.419 | 21555.1314 | 30098.9095 | 42156.1199 | 59200.5407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 14.3354 | 19.0024 | 25.4088 | 34.2424 | 46.4726 | 63.4681 | 87.1641 | 120.3009 | 166.7642 | 232.0697 | 324.0549 | 453.8668 | 637.3727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 1071.6543 | 1420.5413 | 1899.4563 | 2559.8212 | 3474.1046 | 4744.6168 | 6516.0287 | 8993.2036 | 12466.613 | 17348.5837 | 24225.0181 | 33929.2282 | 47647.3798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 150.9697 | 200.1193 | 267.5866 | 360.6157 | 489.4158 | 668.3996 | 917.9479 | 1266.9209 | 1756.2387 | 2443.9881 | 3412.7084 | 4779.7925 | 6712.3422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 171.6507 | 227.5331 | 304.2426 | 410.0156 | 556.4596 | 759.962 | 1043.6953 | 1440.4732 | 1996.8214 | 2778.7839 | 3880.2067 | 5434.5643 | 7631.8491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ReplacedSHL | New | Replaced | SHL | [145 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 176.8005 | 176.8005 | 176.8005 | 176.8005 | 176.8005 | 176.8005 | 176.8005 | 176.8005 | 176.8005 | 176.8005 | 176.8005 | 176.8005 | 176.8005 | 176.8005 | 176.8005 | 176.8005 | 176.8005 | 211.6191 | 280.5136 | 375.0847 | 505.4867 | 686.0298 | 936.9172 | 1286.7171 | 1775.8836 | 2461.7761 | 3425.8165 | 4783.7028 | 6699.9885 | 9408.9053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 129.9006 | 172.191 | 230.2427 | 310.2889 | 421.1138 | 575.119 | 789.8407 | 1090.1116 | 1511.1411 | 2102.9094 | 2936.4368 | 4112.7331 | 5775.5796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.77004 | 1.0207 | 1.3649 | 1.8394 | 2.4963 | 3.4093 | 4.6821 | 6.4621 | 8.9579 | 12.4659 | 17.407 | 24.38 | 34.2372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 70.2464 | 93.1158 | 124.5084 | 167.795 | 227.7258 | 311.0072 | 427.1224 | 589.5 | 817.1802 | 1137.191 | 1587.9378 | 2224.0439 | 3123.2618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 9.8996 | 13.1225 | 17.5466 | 23.6468 | 32.0927 | 43.8293 | 60.193 | 83.0764 | 115.1627 | 160.2608 | 223.7831 | 313.4276 | 440.1515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.79269 | 1.0508 | 1.405 | 1.8935 | 2.5697 | 3.5095 | 4.8198 | 6.6521 | 9.2214 | 12.8325 | 17.9189 | 25.097 | 35.2441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ReplacedSHN | New | Replaced | SHN | [145 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1095.5091 | 1095.5091 | 1095.5091 | 1095.5091 | 1095.5091 | 1095.5091 | 1095.5091 | 1095.5091 | 1095.5091 | 1095.5091 | 1095.5091 | 1095.5091 | 1095.5091 | 1095.5091 | 1095.5091 | 1095.5091 | 1095.5091 | 1311.2557 | 1738.1471 | 2324.1383 | 3132.1481 | 4250.8478 | 5805.4222 | 7972.8879 | 11003.9116 | 15253.9088 | 21227.3946 | 29641.2681 | 41515.1536 | 58300.4211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 635.5955 | 842.5195 | 1126.5627 | 1518.2235 | 2060.4826 | 2814.0202 | 3864.6401 | 5333.8463 | 7393.9167 | 10289.4011 | 14367.797 | 20123.3395 | 28259.5406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 7.3999 | 9.8091 | 13.1161 | 17.676 | 23.9893 | 32.7624 | 44.9942 | 62.0995 | 86.084 | 119.7948 | 167.2777 | 234.2869 | 329.0129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 544.6253 | 721.9331 | 965.3225 | 1300.9264 | 1765.5743 | 2411.2611 | 3311.5102 | 4570.435 | 6335.656 | 8816.7217 | 12311.3937 | 17243.1692 | 24214.8695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 76.7223 | 101.7 | 135.9867 | 183.2638 | 248.7196 | 339.6786 | 466.4983 | 643.8452 | 892.515 | 1242.0271 | 1734.3278 | 2429.0757 | 3411.1914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 46.8585 | 62.1138 | 83.0545 | 111.9293 | 151.9067 | 207.4604 | 284.9161 | 393.2317 | 545.108 | 758.5743 | 1059.2493 | 1483.57 | 2083.4021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ReplacedTYA | New | Replaced | TYA | [145 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 707.7566 | 707.7566 | 707.7566 | 707.7566 | 707.7566 | 707.7566 | 707.7566 | 707.7566 | 707.7566 | 707.7566 | 707.7566 | 707.7566 | 707.7566 | 707.7566 | 707.7566 | 707.7566 | 707.7566 | 847.1403 | 1122.9347 | 1501.5158 | 2023.5328 | 2746.2717 | 3750.6087 | 5150.9057 | 7109.1068 | 9854.829 | 13714.0157 | 19149.8214 | 26820.9772 | 37665.1446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 519.6042 | 688.7662 | 920.9737 | 1241.1594 | 1684.4605 | 2300.4833 | 3159.3732 | 4360.4606 | 6044.584 | 8411.6649 | 11745.7851 | 16450.9855 | 23102.3928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.8607 | 6.4432 | 8.6154 | 11.6106 | 15.7576 | 21.5203 | 29.5549 | 40.7907 | 56.5451 | 78.6884 | 109.878 | 153.8936 | 216.1154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 281.0037 | 372.4871 | 498.0657 | 671.2233 | 910.962 | 1244.1092 | 1708.5999 | 2358.152 | 3268.9318 | 4549.0573 | 6352.1609 | 8896.7495 | 12493.8533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 39.5985 | 52.4901 | 70.1864 | 94.5874 | 128.3709 | 175.3173 | 240.7723 | 332.3058 | 460.651 | 641.0436 | 895.1332 | 1253.7113 | 1760.6076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 2.0094 | 2.6635 | 3.5615 | 4.7997 | 6.514 | 8.8962 | 12.2176 | 16.8623 | 23.375 | 32.5287 | 45.422 | 63.6174 | 89.339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ReplacedWBE | New | Replaced | WBE | [145 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1667.3874 | 1667.3874 | 1667.3874 | 1667.3874 | 1667.3874 | 1667.3874 | 1667.3874 | 1667.3874 | 1667.3874 | 1667.3874 | 1667.3874 | 1667.3874 | 1667.3874 | 1667.3874 | 1667.3874 | 1667.3874 | 1667.3874 | 1995.7582 | 2645.4958 | 3537.3864 | 4767.194 | 6469.8779 | 8835.9722 | 12134.8996 | 16748.1802 | 23216.7635 | 32308.532 | 45114.6208 | 63186.9192 | 88734.4423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 1012.918 | 1342.6828 | 1795.3489 | 2419.5198 | 3283.6922 | 4484.5688 | 6158.8913 | 8500.2946 | 11783.3297 | 16397.7242 | 22897.2678 | 32069.5993 | 45035.8719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.7201 | 4.9312 | 6.5936 | 8.886 | 12.0597 | 16.4701 | 22.6192 | 31.2183 | 43.2756 | 60.2225 | 84.0929 | 117.7793 | 165.3995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 790.3432 | 1047.6467 | 1400.8456 | 1887.8636 | 2562.1459 | 3499.1464 | 4805.5596 | 6632.4717 | 9194.1049 | 12794.5496 | 17865.9078 | 25022.7455 | 35139.858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 111.3707 | 147.6285 | 197.3993 | 266.0271 | 361.0431 | 493.08 | 677.1723 | 934.6105 | 1295.5814 | 1802.9357 | 2517.5629 | 3526.0641 | 4951.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 77.3829 | 102.5756 | 137.1574 | 184.8416 | 250.8609 | 342.603 | 470.5145 | 649.3883 | 900.1989 | 1252.7201 | 1749.2591 | 2449.9883 | 3440.5593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Risk_consol
Powercor
Relay replacements
RISK CONSOLIDATION CALCS
All
|  | Risk | Assets | ZSS | Type | Option 1 Yr | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
[7 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
Risk without replacement
| Safety | Future | All | AC | Safety |  | 5302.9155 | 6085.514 | 6994.1946 | 8052.1907 | 9282.647 | 10715.5197 | 12386.317 | 14337.2 | 16618.3199 | 19289.443 | 22421.9311 | 26101.1604 | 30429.4834 | 35529.8653 | 41550.3571 | 48669.6159 | 55359.6191 | 62167.3272 | 70082.2983 | 79297.1116 | 86355.6896 | 91630.2186 | 97438.2399 | 104110.8343 | 111778.1428 | 116477.7723 | 117456.1563 | 118566.6187 | 119827.2158 | 121258.4928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10289.7726 | 11765.5409 | 13468.919 | 15438.4928 | 17714.812 | 20348.0464 | 23396.9883 | 26930.6209 | 31029.9915 | 35790.454 | 41324.3591 | 47764.2882 | 55266.9534 | 64017.9087 | 74237.2596 | 86186.6 | 98588.8195 | 112075.2983 | 127702.1065 | 145824.5428 | 159768.5343 | 170775.3083 | 183148.4935 | 197360.5513 | 213687.8911 | 223828.5695 | 226207.6097 | 228907.7262 | 231972.8023 | 235452.7688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107345.1846 | 123588.1553 | 142515.344 | 164603.2313 | 190418.7414 | 220637.5206 | 256066.1216 | 297668.967 | 346601.1695 | 404248.5366 | 472276.3965 | 552689.2723 | 647903.9036 | 760838.7132 | 895023.5506 | 1054734.4607 | 1188124.708 | 1310816.8951 | 1452428.7928 | 1615918.0149 | 1744426.0117 | 1854173.4765 | 1980246.4008 | 2125101.9818 | 2291570.0792 | 2391735.2264 | 2408817.0507 | 2428166.0087 | 2450087.2021 | 2474927.1694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5302.9155 | 6085.514 | 6994.1946 | 8052.1907 | 9282.647 | 10715.5197 | 12386.317 | 14337.2 | 16618.3199 | 19289.443 | 22421.9311 | 26101.1604 | 30429.4834 | 35529.8653 | 41550.3571 | 48669.6159 | 55359.6191 | 62167.3272 | 70082.2983 | 79297.1116 | 86355.6896 | 91630.2186 | 97438.2399 | 104110.8343 | 111778.1428 | 116477.7723 | 117456.1563 | 118566.6187 | 119827.2158 | 121258.4928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 499.0884 | 571.3747 | 655.0702 | 752.3052 | 864.9771 | 995.6783 | 1147.4634 | 1323.9379 | 1529.3654 | 1768.7969 | 2048.2287 | 2374.7945 | 2757.0005 | 3205.0144 | 3731.0206 | 4349.6608 | 4979.0761 | 5656.8532 | 6447.1453 | 7370.2744 | 8073.4253 | 8570.9945 | 9107.0979 | 9722.8719 | 10430.2911 | 10871.6639 | 10979.2008 | 11101.3128 | 11239.9996 | 11397.5375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980.6217 | 1122.3175 | 1286.3445 | 1476.472 | 1697.1485 | 1953.6325 | 2252.1503 | 2600.0851 | 3006.2075 | 3480.9523 | 4036.7557 | 4688.4642 | 5453.8312 | 6354.1223 | 7414.8533 | 8666.6909 | 9799.438 | 10914.3303 | 12198.7127 | 13678.7527 | 14940.2897 | 16108.6482 | 17449.0774 | 18987.2579 | 20752.7369 | 21885.8031 | 22224.2985 | 22607.4808 | 23041.3335 | 23532.6489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety | Future | All | BAN | Safety |  | 2206.2769 | 2473.3343 | 2793.3045 | 3178.2423 | 3643.2211 | 4207.1341 | 4893.7173 | 5732.8537 | 6835.9409 | 8326.8378 | 10238.7335 | 12719.9038 | 15982.7739 | 20371.2763 | 26341.9278 | 34572.4772 | 45529.288 | 58066.332 | 75608.7174 | 101581.6717 | 116301.8266 | 118654.8176 | 121014.4199 | 123949.4965 | 127648.2928 | 132371.7277 | 138483.4685 | 146492.7827 | 155238.0161 | 161963.6174
| Safety | Future | All | DDL | Safety |  | 2530.3009 | 2892.0535 | 3316.5406 | 3818.0652 | 4414.7884 | 5124.3667 | 5971.8814 | 6988.7556 | 8219.7328 | 9720.7864 | 11555.8586 | 13810.6658 | 16595.7714 | 20057.3815 | 24388.1139 | 29843.9424 | 36768.2823 | 45626.6571 | 51103.4589 | 55754.1626 | 59739.4024 | 63459.9704 | 67458.8689 | 71340.2155 | 75834.3299 | 81062.8142 | 86753.3283 | 92664.8321 | 93723.6873 | 94134.1823
| Safety | Future | All | ECA | Safety |  | 641.9072 | 719.7677 | 816.085 | 935.5332 | 1084.0133 | 1273.8878 | 1515.6905 | 1821.0098 | 2248.6088 | 2833.5401 | 3603.0721 | 4628.7895 | 6003.7811 | 7866.0897 | 10417.2334 | 13955.2445 | 18928.9474 | 25021.6182 | 31977.4295 | 42803.4408 | 51773.1075 | 53981.6889 | 54753.8425 | 55806.4438 | 57251.5894 | 59248.1238 | 61594.5799 | 63316.7299 | 64158.5898 | 64664.0267
| Safety | Future | All | FDN | Safety |  | 1580.6199 | 1845.0511 | 2161.9741 | 2537.0302 | 2981.5628 | 3509.3023 | 4136.9172 | 4884.7084 | 5777.484 | 6845.6698 | 8126.7239 | 9666.9452 | 11523.7984 | 13768.912 | 16491.9623 | 19805.7212 | 23852.6442 | 28813.493 | 32225.4659 | 33673.6765 | 35481.1371 | 36225.0664 | 36830.2797 | 36830.2797 | 36830.2797 | 36830.2797 | 36830.2797 | 36830.2797 | 36830.2797 | 36830.2797
| Safety | Future | All | GCY | Safety |  | 3214.9107 | 3659.4855 | 4180.4667 | 4788.003 | 5499.2248 | 6335.3763 | 7322.9804 | 8495.3693 | 9898.0029 | 11587.5863 | 13632.4699 | 16127.9755 | 19195.2375 | 22993.8057 | 27738.273 | 33717.6244 | 41324.9481 | 51100.784 | 63797.2829 | 69652.4914 | 75877.6169 | 81366.263 | 87101.3875 | 93332.8594 | 100512.3729 | 108802.1896 | 116635.555 | 117399.1415 | 117716.315 | 118074.7906
| Safety | Future | All | MLN | Safety |  | 1963.8668 | 2185.7384 | 2450.3066 | 2767.4743 | 3149.8002 | 3614.0645 | 4185.1254 | 4886.7659 | 5800.3368 | 6972.9123 | 8465.2422 | 10385.2664 | 12947.3204 | 16351.3754 | 20866.0811 | 26917.3219 | 34575.5334 | 42614.981 | 54029.8041 | 64877.3894 | 76158.7961 | 79815.3505 | 84525.1115 | 90666.1805 | 98768.0472 | 109574.9951 | 124136.5449 | 141754.6321 | 153741.8249 | 154181.2244
| Safety | Future | All | SA | Safety |  | 2627.7138 | 3036.3475 | 3545.0937 | 4180.3082 | 4991.9959 | 5999.3441 | 7255.4408 | 8828.7648 | 10807.8374 | 13307.3275 | 16478.962 | 20516.2465 | 25670.7028 | 32272.4312 | 40753.2383 | 51679.0098 | 65252.561 | 78788.121 | 86660.534 | 92665.1189 | 100284.7552 | 105624.2287 | 107180.6704 | 108743.6278 | 110581.945 | 112768.6726 | 114698.8718 | 115710.1797 | 116810.7761 | 118028.6216
| Safety | Future | All | SHL | Safety |  | 682.3159 | 718.0342 | 760.2564 | 827.4996 | 948.422 | 1152.6552 | 1464.6797 | 1884.3938 | 2453.8104 | 3232.452 | 4304.9384 | 5791.9476 | 7866.0746 | 10774.8156 | 14873.9253 | 20675.895 | 28785.5162 | 39745.5758 | 55538.5253 | 64657.2448 | 73024.5784 | 83528.5666 | 83746.7993 | 83991.7737 | 84266.8138 | 84575.6606 | 84922.5244 | 85312.1444 | 85749.8552 | 86241.662
| Safety | Future | All | SHN | Safety |  | 2726.84 | 3127.9295 | 3598.0201 | 4153.9331 | 4809.4455 | 5585.0819 | 6506.1742 | 7604.1105 | 8917.9373 | 10496.4172 | 12400.6817 | 14707.6599 | 17514.5231 | 20944.4627 | 25154.2218 | 30343.9406 | 36770.0628 | 44762.3016 | 49523.9479 | 53078.5009 | 56292.0314 | 59499.4253 | 62805.603 | 66574.9986 | 70873.3363 | 75775.7433 | 80381.311 | 81191.7573 | 82104.4191 | 83132.3677
| Safety | Future | All | TYA | Safety |  | 1942.8426 | 2259.3078 | 2630.3045 | 3065.5177 | 3576.3858 | 4176.422 | 4881.595 | 5710.7812 | 6686.2989 | 7834.5437 | 9186.7401 | 10779.8339 | 12657.5501 | 14871.6478 | 17483.4087 | 20565.4035 | 24203.587 | 27757.6784 | 29400.6634 | 31320.956 | 33566.0605 | 36191.7003 | 37429.9991 | 38272.9698 | 39245.9371 | 40369.2229 | 41666.3548 | 43164.5747 | 44383.4625 | 45075.464
| Safety | Future | All | WBE | Safety |  | 3576.1208 | 4306.7367 | 5215.026 | 6367.0011 | 7800.0965 | 9582.3753 | 11802.9829 | 14584.145 | 18081.6482 | 22484.5477 | 28030.764 | 35034.6725 | 43903.5807 | 55170.5406 | 67450.335 | 79405.8672 | 94846.0949 | 111115.0567 | 126660.5527 | 138714.9011 | 148123.5308 | 150906.3461 | 152627.9464 | 153844.0581 | 154295.1936 | 154935.5255 | 155418.4406 | 155418.4406 | 155418.4406 | 155418.4406
| Environment | Future | All | AC | Environment |  | 499.0884 | 571.3747 | 655.0702 | 752.3052 | 864.9771 | 995.6783 | 1147.4634 | 1323.9379 | 1529.3654 | 1768.7969 | 2048.2287 | 2374.7945 | 2757.0005 | 3205.0144 | 3731.0206 | 4349.6608 | 4979.0761 | 5656.8532 | 6447.1453 | 7370.2744 | 8073.4253 | 8570.9945 | 9107.0979 | 9722.8719 | 10430.2911 | 10871.6639 | 10979.2008 | 11101.3128 | 11239.9996 | 11397.5375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10289.7726 | 11765.5409 | 13468.919 | 15438.4928 | 17714.812 | 20348.0464 | 23396.9883 | 26930.6209 | 31029.9915 | 35790.454 | 41324.3591 | 47764.2882 | 55266.9534 | 64017.9087 | 74237.2596 | 86186.6 | 98588.8195 | 112075.2983 | 127702.1065 | 145824.5428 | 159768.5343 | 170775.3083 | 183148.4935 | 197360.5513 | 213687.8911 | 223828.5695 | 226207.6097 | 228907.7262 | 231972.8023 | 235452.7688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107345.1846 | 123588.1553 | 142515.344 | 164603.2313 | 190418.7414 | 220637.5206 | 256066.1216 | 297668.967 | 346601.1695 | 404248.5366 | 472276.3965 | 552689.2723 | 647903.9036 | 760838.7132 | 895023.5506 | 1054734.4607 | 1188124.708 | 1310816.8951 | 1452428.7928 | 1615918.0149 | 1744426.0117 | 1854173.4765 | 1980246.4008 | 2125101.9818 | 2291570.0792 | 2391735.2264 | 2408817.0507 | 2428166.0087 | 2450087.2021 | 2474927.1694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5302.9155 | 6085.514 | 6994.1946 | 8052.1907 | 9282.647 | 10715.5197 | 12386.317 | 14337.2 | 16618.3199 | 19289.443 | 22421.9311 | 26101.1604 | 30429.4834 | 35529.8653 | 41550.3571 | 48669.6159 | 55359.6191 | 62167.3272 | 70082.2983 | 79297.1116 | 86355.6896 | 91630.2186 | 97438.2399 | 104110.8343 | 111778.1428 | 116477.7723 | 117456.1563 | 118566.6187 | 119827.2158 | 121258.4928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 499.0884 | 571.3747 | 655.0702 | 752.3052 | 864.9771 | 995.6783 | 1147.4634 | 1323.9379 | 1529.3654 | 1768.7969 | 2048.2287 | 2374.7945 | 2757.0005 | 3205.0144 | 3731.0206 | 4349.6608 | 4979.0761 | 5656.8532 | 6447.1453 | 7370.2744 | 8073.4253 | 8570.9945 | 9107.0979 | 9722.8719 | 10430.2911 | 10871.6639 | 10979.2008 | 11101.3128 | 11239.9996 | 11397.5375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980.6217 | 1122.3175 | 1286.3445 | 1476.472 | 1697.1485 | 1953.6325 | 2252.1503 | 2600.0851 | 3006.2075 | 3480.9523 | 4036.7557 | 4688.4642 | 5453.8312 | 6354.1223 | 7414.8533 | 8666.6909 | 9799.438 | 10914.3303 | 12198.7127 | 13678.7527 | 14940.2897 | 16108.6482 | 17449.0774 | 18987.2579 | 20752.7369 | 21885.8031 | 22224.2985 | 22607.4808 | 23041.3335 | 23532.6489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environment | Future | All | BAN | Environment |  | 286.7594 | 319.5965 | 358.7447 | 405.6012 | 461.9048 | 529.8255 | 612.0774 | 712.0635 | 844.4401 | 1025.3243 | 1257.6845 | 1560.211 | 1960.0004 | 2501.8614 | 3245.4119 | 4280.0779 | 5697.5031 | 7457.9162 | 9922.5759 | 13573.873 | 15639.4968 | 15962.0874 | 16284.4948 | 16686.7527 | 17195.2294 | 17846.5126 | 18691.6436 | 19802.1517 | 21014.0098 | 21938.8449
| Environment | Future | All | DDL | Environment |  | 283.3533 | 325.3684 | 375.0658 | 434.3063 | 505.4736 | 590.8571 | 693.7646 | 818.3668 | 970.6758 | 1158.2458 | 1389.7076 | 1676.7075 | 2034.3325 | 2482.6231 | 3048.0804 | 3766.042 | 4684.0626 | 5866.7829 | 6565.037 | 7137.3001 | 7604.6223 | 8021.9431 | 8464.0657 | 8873.2278 | 9350.1264 | 9909.3576 | 10509.6421 | 11113.7149 | 11229.4587 | 11280.9346
| Environment | Future | All | ECA | Environment |  | 77.6401 | 85.795 | 95.8507 | 108.2828 | 123.6904 | 143.5211 | 168.885 | 200.9394 | 247.3577 | 312.3064 | 398.6516 | 515.2321 | 673.575 | 891.1053 | 1193.634 | 1619.8577 | 2228.8074 | 3015.227 | 3994.4249 | 5518.5617 | 6781.7051 | 7092.5046 | 7200.8299 | 7348.6289 | 7551.6908 | 7832.3905 | 8162.3124 | 8404.2084 | 8522.0595 | 8592.4502
| Environment | Future | All | FDN | Environment |  | 194.0155 | 226.4723 | 265.4869 | 311.7044 | 366.5461 | 431.7376 | 509.3806 | 602.0437 | 712.8774 | 845.7608 | 1005.4895 | 1198.0169 | 1430.7652 | 1713.0288 | 2056.4993 | 2475.9493 | 2990.129 | 3622.9436 | 4081.5539 | 4283.3397 | 4535.3683 | 4637.0401 | 4719.0804 | 4719.0804 | 4719.0804 | 4719.0804 | 4719.0804 | 4719.0804 | 4719.0804 | 4719.0804
| Environment | Future | All | GCY | Environment |  | 341.2854 | 389.3622 | 446.203 | 512.9548 | 591.7072 | 685.083 | 796.3951 | 929.8542 | 1091.3094 | 1288.1133 | 1529.166 | 1827.0612 | 2197.9068 | 2663.0818 | 3251.5586 | 4002.6043 | 4969.9386 | 6227.8088 | 7879.9925 | 8549.7071 | 9249.3055 | 9838.7115 | 10451.1568 | 11105.6985 | 11861.9933 | 12738.3276 | 13575.1135 | 13676.5401 | 13714.2389 | 13756.8468
| Environment | Future | All | MLN | Environment |  | 237.8431 | 264.3962 | 296.3533 | 335.0276 | 382.0947 | 439.8123 | 511.5608 | 600.553 | 718.0935 | 870.6346 | 1066.5297 | 1320.7517 | 1663.169 | 2121.6496 | 2733.706 | 3558.9189 | 4606.7494 | 5704.0402 | 7271.8777 | 8754.7536 | 10292.5091 | 10748.5091 | 11344.3562 | 12131.9458 | 13184.2283 | 14604.0685 | 16536.889 | 18943.3402 | 20608.1656 | 20654.5662
| Environment | Future | All | SA | Environment |  | 290.4705 | 336.5212 | 394.5178 | 467.6894 | 562.4758 | 680.82 | 829.2485 | 1016.2111 | 1252.6703 | 1552.8782 | 1935.8071 | 2425.6787 | 3054.0794 | 3862.637 | 4905.9986 | 6256.0332 | 7931.3343 | 9644.8188 | 10724.2544 | 11537.5301 | 12574.7658 | 13286.498 | 13460.4245 | 13630.1411 | 13832.9457 | 14078.4681 | 14292.0964 | 14393.935 | 14504.7722 | 14627.5119
| Environment | Future | All | SHL | Environment |  | 86.4517 | 90.7542 | 95.8882 | 104.1597 | 119.1342 | 145.2897 | 185.8836 | 240.6522 | 315.1368 | 417.1864 | 557.9568 | 753.3533 | 1026.1185 | 1408.8578 | 1948.4302 | 2712.3301 | 3778.9524 | 5214.8943 | 7285.2144 | 8534.0568 | 9700.3284 | 11165.2269 | 11188.1322 | 11213.8442 | 11242.7119 | 11275.1278 | 11311.5339 | 11352.4277 | 11398.3689 | 11449.988
| Environment | Future | All | SHN | Environment |  | 315.7705 | 362.5148 | 417.4613 | 482.7285 | 559.9636 | 651.7126 | 761.1383 | 892.1853 | 1049.7923 | 1240.1665 | 1471.1391 | 1752.6262 | 2097.2283 | 2521.0135 | 3044.5409 | 3694.2029 | 4503.9906 | 5517.8193 | 6057.531 | 6440.7422 | 6819.86 | 7197.8491 | 7587.1231 | 8030.9326 | 8537.0144 | 9114.2121 | 9657.002 | 9755.5039 | 9866.4707 | 9991.5014
| Environment | Future | All | TYA | Environment |  | 200.254 | 232.7644 | 270.8561 | 315.5167 | 367.9115 | 429.4164 | 501.6566 | 586.5514 | 686.3692 | 803.7908 | 941.9854 | 1104.7003 | 1296.3678 | 1522.231 | 1788.4935 | 2102.4968 | 2472.9307 | 2842.7238 | 3047.2739 | 3286.6643 | 3566.9116 | 3895.0808 | 4028.4614 | 4102.1223 | 4187.1141 | 4285.2039 | 4398.4368 | 4529.1803 | 4637.4731 | 4702.793
| Environment | Future | All | WBE | Environment |  | 471.0932 | 567.6085 | 687.6776 | 840.2437 | 1030.1409 | 1266.4076 | 1560.915 | 1929.2299 | 2392.3324 | 2975.4953 | 3710.2009 | 4638.0917 | 5813.0848 | 7305.706 | 8924.9916 | 10485.5352 | 12498.8255 | 14614.1871 | 16657.8217 | 18157.6085 | 19295.2839 | 19642.2289 | 19864.3278 | 20023.4051 | 20086.9922 | 20177.2463 | 20245.3127 | 20245.3127 | 20245.3127 | 20245.3127
| NP | Future | All | AC | NP |  | 980.6217 | 1122.3175 | 1286.3445 | 1476.472 | 1697.1485 | 1953.6325 | 2252.1503 | 2600.0851 | 3006.2075 | 3480.9523 | 4036.7557 | 4688.4642 | 5453.8312 | 6354.1223 | 7414.8533 | 8666.6909 | 9799.438 | 10914.3303 | 12198.7127 | 13678.7527 | 14940.2897 | 16108.6482 | 17449.0774 | 18987.2579 | 20752.7369 | 21885.8031 | 22224.2985 | 22607.4808 | 23041.3335 | 23532.6489
| NP | Future | All | BAN | NP |  | 26799.9654 | 33355.829 | 41658.6803 | 52192.9731 | 65580.6041 | 82620.4457 | 104339.3444 | 132057.932 | 167490.6037 | 212842.6096 | 270925.4397 | 345385.2017 | 440926.5833 | 563627.0225 | 721334.4905 | 924195.2673 | 1128809.503 | 1131455.757 | 1135378.9539 | 1141254.5486 | 1144476.0447 | 1145599.152 | 1146876.2332 | 1148333.7656 | 1150004.3231 | 1151928.879 | 1154159.7105 | 1156764.4623 | 1159831.8605 | 1163026.7474
| NP | Future | All | DDL | NP |  | 129901.7019 | 145800.9403 | 163755.3688 | 184039.4633 | 206965.3826 | 232886.1257 | 262204.2655 | 295377.8373 | 332928.2222 | 375449.2041 | 423617.3971 | 478204.2948 | 540090.1918 | 610280.3317 | 689923.6906 | 780334.9035 | 883019.9632 | 999706.4825 | 1130206.2668 | 1277592.7682 | 1444715.8735 | 1634322.0162 | 1849468.0917 | 2093627.7966 | 2370767.7165 | 2685389.1582 | 3042611.8456 | 3448259.2459 | 3508501.2823 | 3520985.0831
| NP | Future | All | ECA | NP |  | 14637.51 | 17842.1996 | 21842.2348 | 26845.5351 | 33115.7989 | 40987.8311 | 50886.6263 | 63352.0526 | 79073.1054 | 98924.9882 | 124017.5499 | 155767.5232 | 195978.6331 | 246949.7413 | 311611.804 | 393703.4425 | 497996.2414 | 579767.6306 | 580675.9391 | 581915.6965 | 582862.9283 | 583458.9072 | 584067.4775 | 584741.1073 | 585492.0495 | 586336.5263 | 587296.3251 | 588294.1818 | 589260.6009 | 590278.4625
| NP | Future | All | FDN | NP |  | 104.892 | 122.4445 | 143.0622 | 167.2928 | 195.7832 | 229.2977 | 268.7396 | 315.1763 | 369.87 | 434.3129 | 510.2697 | 599.8278 | 705.4565 | 830.0776 | 977.1485 | 1150.7613 | 1355.7602 | 1597.88 | 1679.1932 | 1687.717 | 1697.6737 | 1709.2829 | 1721.1819 | 1721.1819 | 1721.1819 | 1721.1819 | 1721.1819 | 1721.1819 | 1721.1819 | 1721.1819
| NP | Future | All | GCY | NP |  | 73492.3744 | 82967.8283 | 93733.0906 | 105969.1086 | 119882.8068 | 135710.9077 | 153724.3408 | 174233.333 | 197593.299 | 224211.6567 | 254555.7382 | 289162.0114 | 328646.8219 | 373718.9677 | 425194.4634 | 484013.9412 | 551263.2485 | 628197.9437 | 716272.5806 | 814833.919 | 927298.5699 | 1054377.3342 | 1198473.6946 | 1363048.2194 | 1551047.0095 | 1765837.235 | 1962730.8935 | 1969222.5899 | 1976558.5516 | 1984849.7966
| NP | Future | All | MLN | NP |  | 47021.5647 | 52722.1096 | 59166.6202 | 66456.1998 | 74706.2514 | 84048.9402 | 94636.8465 | 106641.6008 | 120263.704 | 135731.3026 | 153307.0795 | 173295.3805 | 196128.3915 | 222214.4889 | 252013.4447 | 286110.6776 | 325040.3256 | 369003.7239 | 419531.0805 | 475080.0522 | 537973.6148 | 609438.5896 | 691255.4682 | 785107.7093 | 893020.5042 | 1017454.4135 | 1161431.8115 | 1254192.639 | 1284549.0246 | 1303669.7668
| NP | Future | All | SA | NP |  | 112080.2189 | 130349.0592 | 152414.1784 | 179184.2981 | 211803.1084 | 251711.6504 | 300728.2401 | 361150.215 | 435883.5363 | 528607.9292 | 643987.3722 | 787938.4702 | 967972.7211 | 1193633.1277 | 1477051.2852 | 1833658.3302 | 2283015.7402 | 2643897.6201 | 2676642.0326 | 2711833.4114 | 2750877.9691 | 2794223.7308 | 2842356.855 | 2895820.3013 | 2955219.1615 | 3021228.5587 | 3082661.0563 | 3128157.2606 | 3178322.2245 | 3233727.9011
| NP | Future | All | SHL | NP |  | 7538.8145 | 7912.7857 | 8330.2494 | 9201.0086 | 11167.1297 | 13802.1161 | 17358.7681 | 22166.4686 | 28732.6473 | 37783.2493 | 50359.3814 | 67957.2833 | 92731.1932 | 127787.558 | 177611.9562 | 248688.9058 | 350401.2099 | 496336.301 | 706196.2802 | 751447.6285 | 764072.5341 | 779523.4003 | 783536.0993 | 788040.5046 | 793097.7362 | 798776.5794 | 805154.4521 | 812318.4934 | 820366.7917 | 829409.7669
| NP | Future | All | SHN | NP |  | 39790.1483 | 45731.4551 | 52643.5537 | 60696.1483 | 70087.0412 | 81051.5573 | 93868.236 | 108867.0517 | 126439.2472 | 147049.1049 | 171248.0517 | 199691.5737 | 233159.5206 | 272580.5044 | 319061.2471 | 373921.9266 | 438738.7966 | 515395.652 | 604993.8089 | 680273.6 | 715782.0735 | 747855.1451 | 777943.7328 | 812194.8322 | 851192.7995 | 895604.8372 | 938004.9055 | 949421.3334 | 962254.5554 | 976682.9902
| NP | Future | All | TYA | NP |  | 16938.5494 | 19722.6188 | 22991.1665 | 26831.1306 | 31345.356 | 36655.5419 | 42905.7411 | 50266.5144 | 58939.8628 | 69165.0851 | 81225.7342 | 95457.8808 | 112259.9298 | 132104.2837 | 155551.2014 | 183265.2685 | 216034.9717 | 246223.8803 | 252445.002 | 259643.4414 | 267975.536 | 277622.9437 | 287096.3859 | 297490.2295 | 309493.5179 | 323358.8161 | 339378.6716 | 357891.9819 | 372510.418 | 379926.1842
| NP | Future | All | WBE | NP |  | 43863.2546 | 51944.7748 | 61973.2427 | 74453.9725 | 89994.2514 | 109372.0962 | 133571.3679 | 165931.0198 | 207742.3807 | 261041.579 | 329274.6361 | 417052.8804 | 530588.4595 | 678325.6707 | 868771.605 | 1114641.9028 | 1442471.9559 | 1786308.1534 | 2062820.8298 | 2466835.4781 | 2811217.9068 | 2859392.3129 | 2906653.1411 | 2935003.0582 | 2935003.0582 | 2935003.0582 | 2935003.0582 | 2935003.0582 | 2935003.0582 | 2935003.0582
| Opex | Future | All | AC | Financial |  | 10289.7726 | 11765.5409 | 13468.919 | 15438.4928 | 17714.812 | 20348.0464 | 23396.9883 | 26930.6209 | 31029.9915 | 35790.454 | 41324.3591 | 47764.2882 | 55266.9534 | 64017.9087 | 74237.2596 | 86186.6 | 98588.8195 | 112075.2983 | 127702.1065 | 145824.5428 | 159768.5343 | 170775.3083 | 183148.4935 | 197360.5513 | 213687.8911 | 223828.5695 | 226207.6097 | 228907.7262 | 231972.8023 | 235452.7688
| Opex | Future | All | BAN | Financial |  | 5113.1572 | 5747.8909 | 6490.465 | 7362.1819 | 8389.1064 | 9603.2298 | 11043.9346 | 12759.843 | 14882.502 | 17560.4102 | 20860.2778 | 24967.5694 | 30138.8619 | 36792.0319 | 45444.1989 | 56838.4502 | 71682.8986 | 88913.5469 | 110316.7165 | 140260.6084 | 160222.5839 | 166684.5831 | 173169.11 | 180938.806 | 190346.7209 | 201870.5229 | 216162.3272 | 234119.4471 | 250039.6744 | 262339.5121
| Opex | Future | All | DDL | Financial |  | 4107.2262 | 4669.9502 | 5324.3056 | 6089.1827 | 6988.1493 | 8045.4344 | 9293.8509 | 10774.064 | 12546.3401 | 14685.1674 | 17268.6909 | 20406.7721 | 24241.1833 | 28959.0952 | 34807.9992 | 42118.8762 | 51339.8401 | 63085.6564 | 71284.2735 | 79251.1044 | 86003.9429 | 92138.5243 | 98753.8661 | 105276.0037 | 112763.7695 | 121385.6102 | 130935.2699 | 141244.7129 | 143087.4064 | 143798.3547
| Opex | Future | All | ECA | Financial |  | 904.4908 | 1006.2759 | 1131.0184 | 1284.3902 | 1473.5322 | 1716.5182 | 2026.7461 | 2417.9192 | 2975.0432 | 3734.347 | 4733.6117 | 6065.77 | 7855.1333 | 10285.3278 | 13625.2308 | 18273.2657 | 24828.9617 | 33049.9277 | 42827.3278 | 57914.3155 | 72002.2855 | 75634.2054 | 76537.4041 | 77734.9976 | 79339.0492 | 81507.4465 | 84049.6293 | 86027.7307 | 87055.0632 | 87584.6958
| Opex | Future | All | FDN | Financial |  | 4994.1476 | 5826.2539 | 6814.8468 | 7980.894 | 9357.8048 | 10985.6427 | 12912.5531 | 15196.5271 | 17907.5909 | 21130.5335 | 24968.3195 | 29546.379 | 35018.0233 | 41571.312 | 49437.7989 | 58903.721 | 70324.3711 | 84142.6397 | 92368.6227 | 95786.9422 | 99994.7224 | 102381.9642 | 104538.2383 | 104538.2383 | 104538.2383 | 104538.2383 | 104538.2383 | 104538.2383 | 104538.2383 | 104538.2383
| Opex | Future | All | GCY | Financial |  | 6430.0484 | 7297.4826 | 8305.4621 | 9470.3443 | 10820.2732 | 12389.4457 | 14219.6782 | 16362.4405 | 18884.7037 | 21868.9691 | 25414.7866 | 29655.0566 | 34756.7877 | 40935.7497 | 48475.7731 | 57751.6766 | 69263.5567 | 83686.0532 | 101940.1365 | 113088.9261 | 125506.5593 | 136534.1471 | 148070.1755 | 160762.4445 | 175321.0226 | 192039.4333 | 207579.3814 | 208509.0459 | 209030.9326 | 209620.7791
| Opex | Future | All | MLN | Financial |  | 3059.3675 | 3376.7793 | 3749.0208 | 4187.5038 | 4706.4626 | 5324.5036 | 6068.3758 | 6964.1635 | 8116.2926 | 9574.9163 | 11403.7935 | 13727.849 | 16828.3183 | 20935.2282 | 26354.9061 | 33601.4549 | 42897.6857 | 53293.9122 | 68054.1634 | 83932.2109 | 101042.6094 | 107298.7101 | 115335.224 | 125786.6948 | 139540.9369 | 157844.9896 | 182456.2344 | 211912.7058 | 231730.0047 | 232375.9622
| Opex | Future | All | SA | Financial |  | 4081.2218 | 4614.4706 | 5264.584 | 6058.7879 | 7056.4176 | 8270.0885 | 9755.9455 | 11586.3648 | 13854.9482 | 16683.1226 | 20231.6726 | 24706.6673 | 30377.0973 | 37597.4762 | 46834.022 | 58701.3319 | 73488.4589 | 89002.8434 | 100348.1748 | 109457.1914 | 120860.0575 | 129112.4794 | 132082.2884 | 135109.0812 | 138575.1659 | 142571.4457 | 146137.9882 | 148200.3876 | 150448.4515 | 152933.9155
| Opex | Future | All | SHL | Financial |  | 1152.8692 | 1238.0577 | 1337.4983 | 1468.7201 | 1658.3159 | 1960.6373 | 2406.7672 | 2991.2798 | 3765.4596 | 4801.505 | 6201.5317 | 8110.5873 | 10735.5064 | 14372.2838 | 19445.892 | 26568.3054 | 36373.5728 | 49166.2185 | 67602.4117 | 79732.7855 | 90599.3229 | 104205.5392 | 104814.4805 | 105498.0398 | 106265.4926 | 107127.2771 | 108095.1417 | 109182.3102 | 110403.6679 | 111775.9712
| Opex | Future | All | SHN | Financial |  | 5217.0401 | 5941.4343 | 6780.2524 | 7757.0609 | 8893.7091 | 10220.0356 | 11772.2747 | 13594.612 | 15741.1599 | 18278.4723 | 21288.7587 | 24874.0047 | 29161.2718 | 34309.536 | 40518.5391 | 48040.2803 | 57193.9798 | 68385.6244 | 75932.7052 | 82617.3918 | 89546.5951 | 96697.5766 | 104276.128 | 112919.8289 | 122780.2218 | 134030.5816 | 144537.1444 | 146027.6252 | 147705.7516 | 149595.4794
| Opex | Future | All | TYA | Financial |  | 5328.6964 | 6193.9347 | 7207.7459 | 8396.4193 | 9790.9847 | 11428.0791 | 13350.9711 | 15610.7759 | 18267.8935 | 21393.7137 | 25072.6351 | 29404.4588 | 34507.2252 | 40520.5763 | 47609.7423 | 55970.2679 | 65833.6165 | 75668.976 | 81064.0102 | 87377.6071 | 94768.3372 | 103422.3961 | 106963.7814 | 108941.9027 | 111224.3524 | 113858.5996 | 116899.5854 | 120410.9061 | 123316.1781 | 125062.5071
| Opex | Future | All | WBE | Financial |  | 7509.8188 | 9075.5603 | 11006.124 | 13410.0912 | 16378.977 | 20047.0657 | 24585.3361 | 30211.7721 | 37215.3147 | 45940.3236 | 56814.9993 | 70392.7135 | 87377.4224 | 108670.5426 | 129912.3608 | 146612.8938 | 167873.1927 | 189525.5092 | 208167.6079 | 223957.7811 | 237988.0142 | 243747.1029 | 247783.1715 | 250381.9168 | 250818.9687 | 251439.3107 | 251907.1502 | 251907.1502 | 251907.1502 | 251907.1502
| Capex | Future | All | AC | Financial |  | 107345.1846 | 123588.1553 | 142515.344 | 164603.2313 | 190418.7414 | 220637.5206 | 256066.1216 | 297668.967 | 346601.1695 | 404248.5366 | 472276.3965 | 552689.2723 | 647903.9036 | 760838.7132 | 895023.5506 | 1054734.4607 | 1188124.708 | 1310816.8951 | 1452428.7928 | 1615918.0149 | 1744426.0117 | 1854173.4765 | 1980246.4008 | 2125101.9818 | 2291570.0792 | 2391735.2264 | 2408817.0507 | 2428166.0087 | 2450087.2021 | 2474927.1694
| Capex | Future | All | BAN | Financial |  | 6950.5003 | 7991.8786 | 9232.3089 | 10717.5036 | 12504.9792 | 14667.3069 | 17296.2877 | 20508.3198 | 24451.9235 | 29316.1115 | 35340.7561 | 42833.2183 | 52186.8617 | 63906.0786 | 78637.8316 | 97213.3527 | 116211.6157 | 119475.9356 | 123174.2017 | 127381.6436 | 131962.8171 | 136985.1396 | 142620.4146 | 148945.801 | 156047.6518 | 164023.4747 | 172983.486 | 183052.427 | 194371.7025 | 207064.8332
| Capex | Future | All | DDL | Financial |  | 27783.093 | 31182.8599 | 35021.4741 | 39357.2322 | 44256.3265 | 49793.8251 | 56055.0366 | 63136.866 | 71149.4191 | 80217.823 | 90484.2994 | 102110.5557 | 115280.4961 | 130203.3279 | 147117.1167 | 166292.8603 | 188039.1649 | 212707.6189 | 240590.2339 | 272184.1556 | 308019.762 | 348677.4355 | 394814.2362 | 447176.4054 | 506614.0901 | 574093.3069 | 650712.8282 | 737722.5041 | 750314.8685 | 752576.6262
| Capex | Future | All | ECA | Financial |  | 2780.7549 | 3316.605 | 3979.3723 | 4801.7427 | 5825.1301 | 7102.0663 | 8699.1933 | 10701.1188 | 13215.772 | 16380.2202 | 20368.141 | 25401.1529 | 31761.4156 | 39808.4586 | 50000.6023 | 62922.4077 | 79319.8842 | 92209.5867 | 92481.4571 | 92817.7863 | 93110.5967 | 93358.1987 | 93621.0191 | 93906.0677 | 94215.6931 | 94552.6684 | 94920.3251 | 95314.3933 | 95731.3552 | 96179.7493
| Capex | Future | All | FDN | Financial |  | 16019.3716 | 18699.9327 | 21848.5663 | 25548.8887 | 29899.6685 | 35017.5928 | 41040.5453 | 48131.4878 | 56483.0564 | 66323.0049 | 77920.6502 | 91594.5076 | 107721.3345 | 126746.8438 | 149198.3964 | 175700.0386 | 206990.3216 | 243943.4159 | 256326.9933 | 257625.1398 | 259142.3392 | 260915.0232 | 262732.3911 | 262732.3911 | 262732.3911 | 262732.3911 | 262732.3911 | 262732.3911 | 262732.3911 | 262732.3911
| Capex | Future | All | GCY | Financial |  | 49204.4945 | 55641.3982 | 62965.4996 | 71302.5109 | 80796.2778 | 91611.4242 | 103936.3897 | 117986.9179 | 134010.0604 | 152288.7748 | 173147.2067 | 196956.7606 | 224143.0768 | 255194.0559 | 290669.0912 | 331209.6958 | 377551.7447 | 430539.5854 | 491142.3166 | 560313.3562 | 639429.2646 | 719284.1286 | 802431.2488 | 897408.0077 | 1005915.718 | 1129901.0194 | 1243290.7212 | 1245487.6802 | 1247970.3607 | 1250776.3338
| Capex | Future | All | MLN | Financial |  | 13893.5983 | 15586.7735 | 17499.7891 | 19662.1334 | 22107.3378 | 24873.5571 | 28004.2691 | 31548.8102 | 35563.6436 | 40112.8372 | 45269.3883 | 51116.6727 | 57755.594 | 65294.6174 | 73856.4981 | 83585.0327 | 94640.2233 | 107191.9237 | 121477.0319 | 137653.6243 | 156031.2832 | 176900.0458 | 200662.3915 | 227737.261 | 258609.9478 | 293844.7824 | 334101.051 | 357767.6239 | 363648.5072 | 369152.236
| Capex | Future | All | SA | Financial |  | 28286.2703 | 31709.1017 | 35658.8884 | 40237.1919 | 45568.8599 | 51807.8111 | 59144.4641 | 67815.1306 | 78113.9329 | 90407.9309 | 105156.3372 | 122934.9428 | 144467.1864 | 170663.6939 | 202672.6257 | 241943.813 | 290307.4137 | 331631.0618 | 344734.5356 | 359240.0827 | 375350.7643 | 393250.574 | 413143.1592 | 435256.7487 | 459845.4085 | 487192.8535 | 512425.4451 | 530118.4501 | 549503.6296 | 570895.5851
| Capex | Future | All | SHL | Financial |  | 4018.8006 | 4426.3147 | 4881.2099 | 5415.221 | 6075.6886 | 6842.013 | 7738.084 | 8793.6076 | 10050.865 | 11567.404 | 13422.4166 | 15725.9271 | 18632.0569 | 22358.201 | 27212.7885 | 33635.5099 | 42255.4206 | 53975.1635 | 70096.3589 | 75932.5695 | 80014.2603 | 84677.3006 | 89050.7973 | 93960.2117 | 99472.1593 | 105661.61 | 112612.9427 | 120421.1317 | 129193.0847 | 139049.1499
| Capex | Future | All | SHN | Financial |  | 28864.4852 | 32914.444 | 37582.1484 | 42967.5044 | 49187.2172 | 56377.95 | 64699.7958 | 74340.4526 | 85520.1675 | 98497.5957 | 113576.7479 | 131115.2337 | 151534.0506 | 175329.2137 | 203085.5847 | 235493.3229 | 273367.4725 | 317671.2955 | 369457.6817 | 417227.1209 | 450274.1923 | 484388.6847 | 520551.5436 | 561798.1078 | 608851.9536 | 662540.4813 | 712481.9665 | 718472.7053 | 725201.4018 | 732760.3191
| Capex | Future | All | TYA | Financial |  | 40975.1514 | 47709.9471 | 55616.7183 | 64905.773 | 75825.8976 | 88671.4882 | 103791.0156 | 121597.074 | 142578.3137 | 167313.6096 | 196488.8898 | 230917.125 | 271562.0757 | 319566.5055 | 376285.7076 | 443327.3458 | 522598.8065 | 595627.2032 | 610676.3904 | 628089.7555 | 648245.4862 | 671583.0214 | 694499.7258 | 719642.9247 | 748679.4465 | 782220.2581 | 820973.0457 | 865757.6183 | 901120.306 | 919059.395
| Capex | Future | All | WBE | Financial |  | 11430.4468 | 13770.2003 | 16631.9094 | 20136.6918 | 24433.6663 | 29707.7488 | 36188.0961 | 44229.1395 | 54173.9242 | 66461.4947 | 81666.523 | 100512.1252 | 123910.959 | 153019.2639 | 183615.5513 | 211407.6698 | 246597.6733 | 284719.3794 | 311241.4347 | 341813.173 | 374465.0674 | 388703.0195 | 396564.1925 | 401279.8019 | 401279.8019 | 401279.8019 | 401279.8019 | 401279.8019 | 401279.8019 | 401279.8019
Residual risk of assets not replaced
| Safety | Future | Not replaced | AC | Safety | 27 | 5302.9155 | 6085.514 | 1411.3286 | 1606.6471 | 1830.4236 | 2086.9213 | 2381.0534 | 2718.4832 | 3105.7403 | 3550.3542 | 4061.0091 | 4647.7227 | 5322.0535 | 6097.3389 | 6988.9726 | 8014.7233 | 9195.1051 | 10553.8041 | 12118.1734 | 13919.8047 | 15616.7067 | 17327.9839 | 19293.8028 | 21552.4868 | 24148.1745 | 25675.9337 | 25866.4573 | 26080.9417 | 26322.4437 | 26594.4133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3280.1058 | 3727.7098 | 4239.9579 | 4826.4699 | 5498.324 | 6268.281 | 7151.0428 | 8163.551 | 9325.3315 | 10658.8939 | 12190.1907 | 13949.1499 | 15970.2897 | 18293.4282 | 20964.5046 | 24036.5278 | 27570.6731 | 31637.5499 | 36318.667 | 41708.1273 | 46979.4005 | 52448.0902 | 58732.1816 | 65954.6819 | 74257.2939 | 79081.6404 | 79552.4017 | 80082.3673 | 80679.0901 | 81351.0948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25630.5895 | 29131.1379 | 33139.4956 | 37731.735 | 42995.5591 | 49032.1043 | 55958.0254 | 63907.9068 | 73037.0524 | 83524.7122 | 95577.8165 | 109435.2971 | 125373.0878 | 143709.9118 | 164813.9821 | 189110.7566 | 217091.9186 | 249325.773 | 286469.2867 | 329282.031 | 365303.0216 | 398260.0035 | 436075.7012 | 479476.3137 | 529297.5688 | 559996.7485 | 566711.5937 | 574270.9188 | 582782.4541 | 592367.7957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1091.7538 | 1240.7682 | 1411.3286 | 1606.6471 | 1830.4236 | 2086.9213 | 2381.0534 | 2718.4832 | 3105.7403 | 3550.3542 | 4061.0091 | 4647.7227 | 5322.0535 | 6097.3389 | 6988.9726 | 8014.7233 | 9195.1051 | 10553.8041 | 12118.1734 | 13919.8047 | 15616.7067 | 17327.9839 | 19293.8028 | 21552.4868 | 24148.1745 | 25675.9337 | 25866.4573 | 26080.9417 | 26322.4437 | 26594.4133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.0359 | 127.3242 | 144.8203 | 164.8527 | 187.7998 | 214.0974 | 244.2474 | 278.8285 | 318.5073 | 364.0526 | 416.3504 | 476.4228 | 545.4482 | 624.7864 | 716.0058 | 820.9163 | 941.6066 | 1080.4874 | 1240.3415 | 1424.3816 | 1604.7487 | 1792.1444 | 2007.485 | 2254.9863 | 2539.5055 | 2704.7207 | 2720.6118 | 2738.5015 | 2758.6446 | 2781.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 587.4225 | 667.6509 | 759.5177 | 864.7664 | 985.4069 | 1123.7574 | 1282.4912 | 1464.693 | 1673.9221 | 1914.2868 | 2190.5296 | 2508.1265 | 2873.4017 | 3293.6598 | 3777.3399 | 4334.193 | 4975.4879 | 5714.2494 | 6565.5344 | 7546.7515 | 8372.3096 | 9127.6444 | 9994.3351 | 10989.0253 | 12130.8691 | 12834.4577 | 12988.3539 | 13161.6046 | 13356.6789 | 13576.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety | Future | Not replaced | BAN | Safety | 28 | 2206.2769 | 2473.3343 | 2793.3045 | 1359.173 | 1524.5498 | 1728.1972 | 1979.4501 | 2289.9943 | 2748.1707 | 3448.5507 | 4387.0368 | 5664.3335 | 7432.0569 | 9956.2734 | 13593.6326 | 18893.6143 | 26744.9241 | 38082.3027 | 54203.0945 | 79272.4288 | 92970.8095 | 94168.1728 | 95220.4866 | 96676.413 | 98701.2794 | 101530.0016 | 105496.7402 | 111077.2777 | 118949.5905 | 124954.7313
| Safety | Future | Not replaced | DDL | Safety | 27 | 2530.3009 | 2892.0535 | 229.6473 | 277.0873 | 337.4968 | 414.5432 | 512.9519 | 638.8156 | 805.2151 | 1028.3703 | 1322.0909 | 1708.5977 | 2217.6881 | 2892.3968 | 3792.9961 | 5004.9805 | 6651.253 | 8910.9264 | 10665.9884 | 12481.2162 | 13367.171 | 13526.1723 | 13750.9411 | 14069.1623 | 14520.2977 | 15160.6296 | 15643.5448 | 15643.5448 | 15643.5448 | 15643.5448
| Safety | Future | Not replaced | ECA | Safety | 30 | 641.9072 | 719.7677 | 816.085 | 935.5332 | 1084.0133 | 269.1724 | 280.0896 | 296.672 | 362.568 | 493.6749 | 692.9694 | 1001.2146 | 1472.3711 | 2194.785 | 3306.8267 | 5026.256 | 7699.8175 | 11878.0461 | 18437.4286 | 28776.808 | 37148.152 | 39012.8251 | 39635.902 | 40516.7754 | 41763.9851 | 43532.2504 | 45615.3182 | 47033.4074 | 47674.247 | 48157.5451
| Safety | Future | Not replaced | FDN | Safety | 29 | 1580.6199 | 1845.0511 | 2161.9741 | 2537.0302 | 105.1016 | 136.4771 | 177.9598 | 232.9287 | 305.9175 | 403.0146 | 532.4024 | 705.0859 | 935.8763 | 1244.7193 | 1658.4892 | 2213.4149 | 2958.3572 | 3959.2404 | 5305.0445 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906 | 5348.8906
| Safety | Future | Not replaced | GCY | Safety | 29 | 3214.9107 | 3659.4855 | 4180.4667 | 4788.003 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 14.6698 | 17.5588 | 23.2752 | 31.1222 | 41.9421 | 56.9224 | 77.7395 | 106.7637 | 147.3516 | 204.2626 | 284.2526 | 396.9214 | 555.9227 | 780.6916 | 1098.9127 | 1550.0482 | 2190.3801 | 2673.2952 | 2673.2952 | 2673.2952
| Safety | Future | Not replaced | MLN | Safety | 30 | 1963.8668 | 2185.7384 | 2450.3066 | 2767.4743 | 3149.8002 | 914.0676 | 1016.8381 | 1148.1448 | 1362.2613 | 1670.9115 | 2088.4516 | 2661.632 | 3523.698 | 4766.6628 | 6514.8131 | 9000.161 | 12302.0651 | 15896.4573 | 21458.1607 | 30098.5818 | 39952.0997 | 41985.6593 | 44850.3058 | 48893.3546 | 54609.2069 | 62702.1516 | 74176.1182 | 90035.7214 | 101631.9746 | 101631.9746
| Safety | Future | Not replaced | SA | Safety | 29 | 2627.7138 | 3036.3475 | 3545.0937 | 4180.3082 | 193.1301 | 236.9974 | 294.0496 | 368.8822 | 467.8061 | 599.5087 | 775.973 | 1013.7585 | 1335.7847 | 1773.8172 | 2371.9359 | 3191.3727 | 4317.2647 | 5868.0827 | 8008.8004 | 9150.7503 | 10449.2041 | 11250.3838 | 11316.372 | 11390.3386 | 11473.2576 | 11566.2226 | 11631.4175 | 11631.4175 | 11631.4175 | 11631.4175
| Safety | Future | Not replaced | SHL | Safety | 31 | 682.3159 | 718.0342 | 760.2564 | 827.4996 | 948.422 | 1152.6552 | 869.3666 | 1183.8733 | 1625.0737 | 2246.7036 | 3126.0225 | 4374.3286 | 6152.2443 | 8691.9603 | 12329.6384 | 17552.659 | 25068.5783 | 35905.8544 | 51561.1078 | 60525.375 | 68719.4266 | 79028.97 | 79028.97 | 79028.97 | 79028.97 | 79028.97 | 79028.97 | 79028.97 | 79028.97 | 79028.97
| Safety | Future | Not replaced | SHN | Safety | 31 | 2726.84 | 3127.9295 | 3598.0201 | 4153.9331 | 4809.4455 | 5585.0819 | 628.5346 | 758.5396 | 919.6433 | 1119.9953 | 1369.9986 | 1682.9511 | 2075.8741 | 2570.5794 | 3195.0488 | 3985.2132 | 4987.2523 | 6260.5643 | 6577.7738 | 6745.648 | 6936.9835 | 7155.1069 | 7403.8214 | 7687.4748 | 8011.0384 | 8380.1967 | 8722.6167 | 8758.4154 | 8798.4815 | 8843.3311
| Safety | Future | Not replaced | TYA | Safety | 29 | 1942.8426 | 2259.3078 | 2630.3045 | 3065.5177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety | Future | Not replaced | WBE | Safety | 28 | 3576.1208 | 4306.7367 | 5215.026 | 231.3363 | 283.604 | 355.5199 | 454.9015 | 592.7812 | 798.3802 | 1100.0996 | 1530.1212 | 2143.0226 | 3017.4759 | 4270.0198 | 6071.096 | 8670.8999 | 12438.0888 | 17917.9857 | 25920.462 | 30098.9768 | 32514.7819 | 32673.7832 | 32898.552 | 33216.7731 | 33667.9086 | 34308.2405 | 34791.1556 | 34791.1556 | 34791.1556 | 34791.1556
| Environment | Future | Not replaced | AC | Environment | 27 | 499.0884 | 571.3747 | 144.8203 | 164.8527 | 187.7998 | 214.0974 | 244.2474 | 278.8285 | 318.5073 | 364.0526 | 416.3504 | 476.4228 | 545.4482 | 624.7864 | 716.0058 | 820.9163 | 941.6066 | 1080.4874 | 1240.3415 | 1424.3816 | 1604.7487 | 1792.1444 | 2007.485 | 2254.9863 | 2539.5055 | 2704.7207 | 2720.6118 | 2738.5015 | 2758.6446 | 2781.329
| Environment | Future | Not replaced | BAN | Environment | 28 | 286.7594 | 319.5965 | 358.7447 | 185.3072 | 207.9274 | 235.8604 | 270.4121 | 313.2184 | 376.7113 | 474.1984 | 605.089 | 783.5522 | 1030.9264 | 1384.6695 | 1894.9951 | 2639.2746 | 3742.6573 | 5336.7299 | 7604.1042 | 11131.4547 | 13056.8918 | 13220.8936 | 13363.8575 | 13563.034 | 13841.6337 | 14232.6605 | 14783.0883 | 15559.8298 | 16658.2677 | 17492.3522
| Environment | Future | Not replaced | DDL | Environment | 27 | 283.3533 | 325.3684 | 32.3599 | 39.0444 | 47.5563 | 58.4125 | 72.2787 | 90.0134 | 113.46 | 144.9041 | 186.2917 | 240.754 | 312.4899 | 407.5637 | 534.4691 | 705.2541 | 937.2386 | 1255.6645 | 1503.0216 | 1758.8649 | 1883.7343 | 1906.1453 | 1937.8263 | 1982.6792 | 2046.2663 | 2136.5204 | 2204.5868 | 2204.5868 | 2204.5868 | 2204.5868
| Environment | Future | Not replaced | ECA | Environment | 30 | 77.6401 | 85.795 | 95.8507 | 108.2828 | 123.6904 | 37.9102 | 39.4487 | 41.7856 | 51.0687 | 69.534 | 97.6028 | 141.0154 | 207.3706 | 309.1093 | 465.7163 | 707.8551 | 1084.3512 | 1672.7243 | 2596.3885 | 4052.3048 | 5231.5143 | 5494.2711 | 5582.0492 | 5706.1453 | 5881.8505 | 6130.9613 | 6424.3911 | 6624.1129 | 6714.3679 | 6782.435
| Environment | Future | Not replaced | FDN | Environment | 29 | 194.0155 | 226.4723 | 265.4869 | 311.7044 | 14.8077 | 19.2281 | 25.0726 | 32.8171 | 43.1005 | 56.7804 | 75.0097 | 99.3389 | 131.8548 | 175.3674 | 233.6631 | 311.8461 | 416.8003 | 557.8139 | 747.423 | 753.6005 | 753.6005 | 753.6005 | 753.6005 | 753.6005 | 753.6005 | 753.6005 | 753.6005 | 753.6005 | 753.6005 | 753.6005
| Environment | Future | Not replaced | GCY | Environment | 29 | 341.2854 | 389.3622 | 446.203 | 512.9548 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.0677 | 2.4749 | 3.2806 | 4.3866 | 5.9117 | 8.0232 | 10.9573 | 15.0482 | 20.7691 | 28.7906 | 40.0651 | 55.9457 | 78.3567 | 110.0377 | 154.8906 | 218.4777 | 308.7318 | 376.7982 | 376.7982 | 376.7982
| Environment | Future | Not replaced | MLN | Environment | 30 | 237.8431 | 264.3962 | 296.3533 | 335.0276 | 382.0947 | 128.4961 | 142.9814 | 161.4888 | 191.6659 | 235.1652 | 294.0101 | 374.7885 | 496.214 | 671.2541 | 917.4378 | 1267.4401 | 1732.408 | 2238.419 | 3021.4527 | 4238.0368 | 5625.1977 | 5910.0076 | 6311.2155 | 6877.4647 | 7677.9989 | 8811.4574 | 10418.4459 | 12639.3317 | 14262.9096 | 14262.9096
| Environment | Future | Not replaced | SA | Environment | 29 | 290.4705 | 336.5212 | 394.5178 | 467.6894 | 27.2172 | 33.3989 | 41.4384 | 51.9834 | 65.9231 | 84.4816 | 109.3474 | 142.8539 | 188.2305 | 249.9532 | 334.2331 | 449.6983 | 608.3449 | 826.8661 | 1128.5075 | 1289.447 | 1472.4546 | 1585.3753 | 1594.6763 | 1605.1018 | 1616.7891 | 1629.8925 | 1639.0816 | 1639.0816 | 1639.0816 | 1639.0816
| Environment | Future | Not replaced | SHL | Environment | 31 | 86.4517 | 90.7542 | 95.8882 | 104.1597 | 119.1342 | 145.2897 | 114.6128 | 155.9768 | 213.9827 | 295.6846 | 411.2238 | 575.2099 | 808.7272 | 1142.2567 | 1619.9329 | 2305.7528 | 3292.6409 | 4715.6957 | 6771.5635 | 8004.1948 | 9152.2792 | 10596.7691 | 10596.7691 | 10596.7691 | 10596.7691 | 10596.7691 | 10596.7691 | 10596.7691 | 10596.7691 | 10596.7691
| Environment | Future | Not replaced | SHN | Environment | 31 | 315.7705 | 362.5148 | 417.4613 | 482.7285 | 559.9636 | 651.7126 | 77.903 | 94.8576 | 116.0114 | 142.4876 | 175.7234 | 217.5601 | 270.3588 | 337.151 | 421.8313 | 529.4079 | 666.3256 | 840.8831 | 880.0076 | 897.3119 | 917.0415 | 939.5413 | 965.2054 | 994.4845 | 1027.8943 | 1066.0242 | 1101.2745 | 1104.2604 | 1107.6022 | 1111.343
| Environment | Future | Not replaced | TYA | Environment | 29 | 200.254 | 232.7644 | 270.8561 | 315.5167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environment | Future | Not replaced | WBE | Environment | 28 | 471.0932 | 567.6085 | 687.6776 | 32.5703 | 39.928 | 50.0516 | 64.0416 | 83.451 | 112.394 | 154.8684 | 215.4051 | 301.6873 | 424.7902 | 601.1197 | 854.6704 | 1220.6646 | 1751.0017 | 2522.4518 | 3649.0287 | 4237.3472 | 4577.5916 | 4600.0027 | 4631.6836 | 4676.5366 | 4740.1236 | 4830.3778 | 4898.4441 | 4898.4441 | 4898.4441 | 4898.4441
| NP | Future | Not replaced | AC | NP | 27 | 980.6217 | 1122.3175 | 759.5177 | 864.7664 | 985.4069 | 1123.7574 | 1282.4912 | 1464.693 | 1673.9221 | 1914.2868 | 2190.5296 | 2508.1265 | 2873.4017 | 3293.6598 | 3777.3399 | 4334.193 | 4975.4879 | 5714.2494 | 6565.5344 | 7546.7515 | 8372.3096 | 9127.6444 | 9994.3351 | 10989.0253 | 12130.8691 | 12834.4577 | 12988.3539 | 13161.6046 | 13356.6789 | 13576.3635
| NP | Future | Not replaced | BAN | NP | 28 | 26799.9654 | 33355.829 | 41658.6803 | 552.3244 | 602.5032 | 658.6007 | 721.339 | 791.5304 | 885.1225 | 1020.6343 | 1192.9404 | 1418.7592 | 1724.3557 | 2154.4612 | 2775.6054 | 3694.1091 | 5083.7531 | 7225.7312 | 10576.5827 | 15880.2796 | 18460.3861 | 18864.027 | 19333.9077 | 19885.6419 | 20539.5821 | 21322.9511 | 22272.554 | 23438.6256 | 24890.2996 | 26270.3691
| NP | Future | Not replaced | DDL | NP | 27 | 129901.7019 | 145800.9403 | 0.81806 | 1.0216 | 1.2804 | 1.6099 | 2.0301 | 2.5666 | 3.2557 | 4.1435 | 5.2835 | 6.7497 | 8.6383 | 11.0756 | 14.2269 | 18.3106 | 23.6157 | 30.5283 | 32.1512 | 33.2157 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6901
| NP | Future | Not replaced | ECA | NP | 30 | 14637.51 | 17842.1996 | 21842.2348 | 26845.5351 | 33115.7989 | 19.7587 | 20.089 | 20.54 | 23.7625 | 32.0919 | 44.8248 | 65.1824 | 97.126 | 147.1968 | 225.7849 | 349.4787 | 545.2024 | 856.342 | 1352.9649 | 2148.4449 | 2616.1721 | 2694.5676 | 2744.3908 | 2814.7712 | 2914.3498 | 3055.4395 | 3255.5978 | 3432.9823 | 3513.143 | 3573.5973
| NP | Future | Not replaced | FDN | NP | 29 | 104.892 | 122.4445 | 143.0622 | 167.2928 | 0.022935 | 0.029781 | 0.038833 | 0.050828 | 0.066755 | 0.087943 | 0.11618 | 0.15386 | 0.20422 | 0.27161 | 0.3619 | 0.483 | 0.64555 | 0.86396 | 1.1576 | 1.1672 | 1.1672 | 1.1672 | 1.1672 | 1.1672 | 1.1672 | 1.1672 | 1.1672 | 1.1672 | 1.1672 | 1.1672
| NP | Future | Not replaced | GCY | NP | 29 | 73492.3744 | 82967.8283 | 93733.0906 | 105969.1086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NP | Future | Not replaced | MLN | NP | 30 | 47021.5647 | 52722.1096 | 59166.6202 | 66456.1998 | 74706.2514 | 412.0057 | 412.1702 | 412.3805 | 414.6744 | 419.1255 | 425.7956 | 435.9305 | 530.9593 | 712.0863 | 964.7112 | 1319.2727 | 1819.4552 | 2527.7837 | 3539.4992 | 4992.1387 | 6929.7786 | 9134.964 | 12241.0541 | 16624.4595 | 22820.977 | 31593.837 | 44030.9526 | 61675.9669 | 74976.3948 | 74976.3948
| NP | Future | Not replaced | SA | NP | 29 | 112080.2189 | 130349.0592 | 152414.1784 | 179184.2981 | 0.4788 | 0.63479 | 0.84684 | 1.136 | 1.5317 | 2.0743 | 2.8204 | 3.8484 | 5.2678 | 7.2309 | 9.9502 | 13.7225 | 18.9623 | 26.2485 | 36.3908 | 38.3201 | 39.2222 | 39.7596 | 39.7596 | 39.7596 | 39.7596 | 39.7596 | 39.7596 | 39.7596 | 39.7596 | 39.7596
| NP | Future | Not replaced | SHL | NP | 31 | 7538.8145 | 7912.7857 | 8330.2494 | 9201.0086 | 11167.1297 | 13802.1161 | 10902.1747 | 14982.2559 | 20734.4734 | 28874.2394 | 40430.8183 | 56887.1327 | 80382.4428 | 114006.3455 | 162225.4594 | 231502.963 | 331198.5201 | 474875.9607 | 682204.0859 | 724615.4825 | 734054.2088 | 745929.7697 | 745929.7697 | 745929.7697 | 745929.7697 | 745929.7697 | 745929.7697 | 745929.7697 | 745929.7697 | 745929.7697
| NP | Future | Not replaced | SHN | NP | 31 | 39790.1483 | 45731.4551 | 52643.5537 | 60696.1483 | 70087.0412 | 81051.5573 | 286.8509 | 323.6031 | 365.2983 | 412.6197 | 466.3464 | 527.3674 | 596.6971 | 675.4935 | 765.0785 | 866.9614 | 982.8661 | 1114.7618 | 1264.6724 | 1435.2919 | 1629.5675 | 1850.8316 | 2102.8914 | 2390.0964 | 2717.4164 | 3090.5307 | 3439.7828 | 3495.066 | 3556.9393 | 3626.1995
| NP | Future | Not replaced | TYA | NP | 29 | 16938.5494 | 19722.6188 | 22991.1665 | 26831.1306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NP | Future | Not replaced | WBE | NP | 28 | 43863.2546 | 51944.7748 | 61973.2427 | 129.2894 | 161.459 | 205.7274 | 266.911 | 351.808 | 475.7785 | 659.0231 | 918.4826 | 1287.423 | 1814.228 | 2569.5399 | 3656.9112 | 5228.7641 | 7510.4154 | 10836.4146 | 15705.7743 | 18204.9908 | 19059.2549 | 19059.2549 | 19059.2549 | 19059.2549 | 19059.2549 | 19059.2549 | 19059.2549 | 19059.2549 | 19059.2549 | 19059.2549
| Opex | Future | Not replaced | AC | Financial | 27 | 10289.7726 | 11765.5409 | 4239.9579 | 4826.4699 | 5498.324 | 6268.281 | 7151.0428 | 8163.551 | 9325.3315 | 10658.8939 | 12190.1907 | 13949.1499 | 15970.2897 | 18293.4282 | 20964.5046 | 24036.5278 | 27570.6731 | 31637.5499 | 36318.667 | 41708.1273 | 46979.4005 | 52448.0902 | 58732.1816 | 65954.6819 | 74257.2939 | 79081.6404 | 79552.4017 | 80082.3673 | 80679.0901 | 81351.0948
| Opex | Future | Not replaced | BAN | Financial | 28 | 5113.1572 | 5747.8909 | 6490.465 | 2481.9474 | 2863.4441 | 3333.314 | 3913.1248 | 4629.8771 | 5588.7541 | 6905.9573 | 8608.4522 | 10832.5753 | 13773.9176 | 17774.3394 | 23255.84 | 30842.0433 | 41522.4032 | 55728.9383 | 73649.8582 | 100337.5613 | 116616.7371 | 118912.5391 | 120683.0468 | 123117.8039 | 126486.914 | 131173.9145 | 137724.0874 | 146913.4852 | 159847.5919 | 169755.0585
| Opex | Future | Not replaced | DDL | Financial | 27 | 4107.2262 | 4669.9502 | 383.0251 | 463.3054 | 565.4897 | 695.7572 | 862.0655 | 1074.6687 | 1356.4434 | 1735.6784 | 2233.1499 | 2887.1226 | 3749.5658 | 4894.4452 | 6425.8293 | 8492.0842 | 11307.6453 | 15186.7722 | 18090.1837 | 21376.845 | 22916.1204 | 23070.158 | 23287.9099 | 23596.1968 | 24033.2488 | 24653.5908 | 25121.4303 | 25121.4303 | 25121.4303 | 25121.4303
| Opex | Future | Not replaced | ECA | Financial | 30 | 904.4908 | 1006.2759 | 1131.0184 | 1284.3902 | 1473.5322 | 368.2555 | 388.4434 | 419.1075 | 527.125 | 725.7914 | 1023.8537 | 1477.4624 | 2164.3007 | 3208.8509 | 4804.9305 | 7255.6569 | 11039.4903 | 16910.8817 | 26062.81 | 40386.4567 | 53540.9853 | 56600.2157 | 57203.551 | 58056.5149 | 59264.2087 | 60976.4498 | 62993.3216 | 64366.107 | 64986.4735 | 65454.3316
| Opex | Future | Not replaced | FDN | Financial | 29 | 4994.1476 | 5826.2539 | 6814.8468 | 7980.894 | 194.3052 | 252.3102 | 329.0008 | 430.6239 | 565.5612 | 745.0681 | 984.2721 | 1303.5186 | 1730.1895 | 2301.1589 | 3066.1108 | 4092.0227 | 5469.2253 | 7319.5953 | 9807.6335 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934 | 9888.6934
| Opex | Future | Not replaced | GCY | Financial | 29 | 6430.0484 | 7297.4826 | 8305.4621 | 9470.3443 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 14.2118 | 17.0107 | 22.5486 | 30.1506 | 40.6327 | 55.1454 | 75.3126 | 103.4307 | 142.7516 | 197.886 | 275.3788 | 384.5303 | 538.5679 | 756.3199 | 1064.6068 | 1501.6587 | 2122.0007 | 2589.8402 | 2589.8402 | 2589.8402
| Opex | Future | Not replaced | MLN | Financial | 30 | 3059.3675 | 3376.7793 | 3749.0208 | 4187.5038 | 4706.4626 | 1219.1971 | 1318.7584 | 1445.9648 | 1675.5556 | 2019.5091 | 2492.1748 | 3154.1249 | 4202.273 | 5755.5136 | 7972.8906 | 11172.2641 | 15575.1552 | 20899.3131 | 29119.68 | 41865.246 | 56460.0522 | 59855.857 | 64639.5329 | 71391.092 | 80936.1814 | 94450.9637 | 113612.0074 | 140020.939 | 159263.9932 | 159263.9932
| Opex | Future | Not replaced | SA | Financial | 29 | 4081.2218 | 4614.4706 | 5264.584 | 6058.7879 | 514.6142 | 613.6539 | 739.185 | 899.9582 | 1107.9268 | 1379.4725 | 1737.1096 | 2211.8576 | 2846.544 | 3700.4077 | 4855.5174 | 6425.7245 | 8569.1569 | 11505.6622 | 15541.1667 | 17739.6982 | 20238.248 | 21828.8566 | 22072.946 | 22346.5475 | 22653.2638 | 22997.1399 | 23238.295 | 23238.295 | 23238.295 | 23238.295
| Opex | Future | Not replaced | SHL | Financial | 31 | 1152.8692 | 1238.0577 | 1337.4983 | 1468.7201 | 1658.3159 | 1960.6373 | 975.4906 | 1328.2248 | 1823.6626 | 2522.7639 | 3513.4286 | 4922.6797 | 6934.4475 | 9815.5641 | 13953.8045 | 19913.6209 | 28517.8884 | 40967.9277 | 59019.9031 | 70719.3042 | 81102.3277 | 94165.9788 | 94165.9788 | 94165.9788 | 94165.9788 | 94165.9788 | 94165.9788 | 94165.9788 | 94165.9788 | 94165.9788
| Opex | Future | Not replaced | SHN | Financial | 31 | 5217.0401 | 5941.4343 | 6780.2524 | 7757.0609 | 8893.7091 | 10220.0356 | 1400.8112 | 1672.6631 | 2006.3436 | 2417.5309 | 2926.1562 | 3557.6041 | 4344.2571 | 5327.4876 | 6560.2254 | 8110.2714 | 10064.5733 | 12534.7473 | 13252.8884 | 13713.3481 | 14238.3368 | 14837.0253 | 15519.8996 | 16298.9509 | 17187.8926 | 18202.4088 | 19140.468 | 19220.8811 | 19310.8798 | 19411.6234
| Opex | Future | Not replaced | TYA | Financial | 29 | 5328.6964 | 6193.9347 | 7207.7459 | 8396.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex | Future | Not replaced | WBE | Financial | 28 | 7509.8188 | 9075.5603 | 11006.124 | 249.7142 | 300.2885 | 369.8744 | 466.0361 | 599.4486 | 805.7828 | 1112.7253 | 1551.5663 | 2179.3665 | 3078.9125 | 4373.443 | 6244.3826 | 8959.8759 | 12917.8419 | 18711.1981 | 27227.078 | 32488.941 | 36173.3704 | 36327.408 | 36545.1599 | 36853.4468 | 37290.4987 | 37910.8407 | 38378.6802 | 38378.6802 | 38378.6802 | 38378.6802
| Capex | Future | Not replaced | AC | Financial | 27 | 107345.1846 | 123588.1553 | 33139.4956 | 37731.735 | 42995.5591 | 49032.1043 | 55958.0254 | 63907.9068 | 73037.0524 | 83524.7122 | 95577.8165 | 109435.2971 | 125373.0878 | 143709.9118 | 164813.9821 | 189110.7566 | 217091.9186 | 249325.773 | 286469.2867 | 329282.031 | 365303.0216 | 398260.0035 | 436075.7012 | 479476.3137 | 529297.5688 | 559996.7485 | 566711.5937 | 574270.9188 | 582782.4541 | 592367.7957
| Capex | Future | Not replaced | BAN | Financial | 28 | 6950.5003 | 7991.8786 | 9232.3089 | 3460.1423 | 3842.997 | 4270.8961 | 4749.309 | 5284.3829 | 5883.6484 | 6555.5974 | 7308.7106 | 8153.4549 | 9101.9142 | 10168.4377 | 11369.7017 | 12725.7497 | 14261.4526 | 16007.7288 | 18004.6372 | 20308.9746 | 22756.7917 | 25387.1675 | 28340.0413 | 31656.7404 | 35383.3224 | 39571.9743 | 44281.9375 | 49580.6137 | 55544.9037 | 62225.7607
| Capex | Future | Not replaced | DDL | Financial | 27 | 27783.093 | 31182.8599 | 1.1989 | 1.4972 | 1.8764 | 2.3594 | 2.9752 | 3.7615 | 4.7713 | 6.0725 | 7.7432 | 9.8919 | 12.6599 | 16.2318 | 20.8502 | 26.8349 | 34.6099 | 44.7406 | 47.1191 | 48.6792 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744
| Capex | Future | Not replaced | ECA | Financial | 30 | 2780.7549 | 3316.605 | 3979.3723 | 4801.7427 | 5825.1301 | 2.7399 | 2.7781 | 2.8304 | 3.321 | 4.6568 | 6.7074 | 9.9388 | 15.0038 | 22.9652 | 35.5238 | 55.4117 | 87.058 | 137.6247 | 218.7154 | 349.1615 | 419.7642 | 427.5123 | 431.4031 | 436.8993 | 444.6756 | 455.6936 | 471.3244 | 485.1768 | 491.4367 | 496.1577
| Capex | Future | Not replaced | FDN | Financial | 29 | 16019.3716 | 18699.9327 | 21848.5663 | 25548.8887 | 0.87571 | 1.1371 | 1.4828 | 1.9408 | 2.5489 | 3.3579 | 4.436 | 5.8748 | 7.7978 | 10.3711 | 13.8187 | 18.4423 | 24.6492 | 32.9887 | 44.202 | 44.5673 | 44.5673 | 44.5673 | 44.5673 | 44.5673 | 44.5673 | 44.5673 | 44.5673 | 44.5673 | 44.5673 | 44.5673
| Capex | Future | Not replaced | GCY | Financial | 29 | 49204.4945 | 55641.3982 | 62965.4996 | 71302.5109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capex | Future | Not replaced | MLN | Financial | 30 | 13893.5983 | 15586.7735 | 17499.7891 | 19662.1334 | 22107.3378 | 30.5426 | 30.5545 | 30.5696 | 30.8068 | 31.2733 | 31.9751 | 33.0837 | 40.6089 | 54.728 | 74.5423 | 102.5378 | 142.3189 | 199.1042 | 280.874 | 399.2947 | 554.6719 | 717.3191 | 946.4184 | 1269.7353 | 1726.7929 | 2373.891 | 3291.2803 | 4586.859 | 5558.3427 | 5558.3427
| Capex | Future | Not replaced | SA | Financial | 29 | 28286.2703 | 31709.1017 | 35658.8884 | 40237.1919 | 0.59458 | 0.78829 | 1.0516 | 1.4108 | 1.9021 | 2.5759 | 3.5024 | 4.7791 | 6.5417 | 8.9794 | 12.3564 | 17.041 | 23.5478 | 32.596 | 45.191 | 47.5869 | 48.707 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744 | 49.3744
| Capex | Future | Not replaced | SHL | Financial | 31 | 4018.8006 | 4426.3147 | 4881.2099 | 5415.221 | 6075.6886 | 6842.013 | 702.2587 | 965.0911 | 1335.65 | 1860.0311 | 2604.5551 | 3664.7783 | 5178.5571 | 7344.9984 | 10451.9656 | 14916.0197 | 21340.4392 | 30599.5372 | 43961.2295 | 46702.137 | 47311.1663 | 48077.4312 | 48077.4312 | 48077.4312 | 48077.4312 | 48077.4312 | 48077.4312 | 48077.4312 | 48077.4312 | 48077.4312
| Capex | Future | Not replaced | SHN | Financial | 31 | 28864.4852 | 32914.444 | 37582.1484 | 42967.5044 | 49187.2172 | 56377.95 | 5950.5267 | 6712.7934 | 7577.5461 | 8558.9371 | 9673.1062 | 10938.4643 | 12376.016 | 14009.7293 | 15866.9582 | 17978.9261 | 20381.279 | 23114.7181 | 26224.5518 | 29764.5056 | 33795.2658 | 38385.9761 | 43615.6236 | 49574.4507 | 56365.5698 | 64106.8113 | 71352.9709 | 72499.9675 | 73783.6916 | 75220.6783
| Capex | Future | Not replaced | TYA | Financial | 29 | 40975.1514 | 47709.9471 | 55616.7183 | 64905.773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capex | Future | Not replaced | WBE | Financial | 28 | 11430.4468 | 13770.2003 | 16631.9094 | 3.31 | 4.1368 | 5.2746 | 6.8476 | 9.0306 | 12.2425 | 16.9536 | 23.6204 | 33.0932 | 46.6067 | 65.9595 | 93.7808 | 133.9293 | 192.0889 | 276.666 | 400.1443 | 460.9229 | 488.6621 | 488.6621 | 488.6621 | 488.6621 | 488.6621 | 488.6621 | 488.6621 | 488.6621 | 488.6621 | 488.6621
Risk after replacement
| Safety | New | Replaced | AC | Safety | 27 | 0 | 0 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 491.9587 | 652.1204 | 871.9733 | 1175.1235 | 1594.8388 | 2178.0861 | 2991.2788 | 4128.4623 | 5722.982 | 7964.1224 | 11120.8507 | 15575.711 | 21873.2302 | 0 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1203.0793 | 1594.7528 | 2132.4007 | 2873.751 | 3900.1598 | 5326.4843 | 7315.1376 | 10096.1069 | 13995.4862 | 19476.1692 | 27195.9119 | 38090.2212 | 53490.7316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 626.0093 | 829.8125 | 1109.5717 | 1495.3254 | 2029.4061 | 2771.5787 | 3806.3531 | 5253.4005 | 7282.4005 | 10134.2149 | 14151.0998 | 19819.8363 | 27833.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 15.5796 | 20.6516 | 27.614 | 37.2143 | 50.506 | 68.9766 | 94.7291 | 130.7419 | 181.2378 | 252.2112 | 352.1798 | 493.2583 | 692.6908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 491.9587 | 652.1204 | 871.9733 | 1175.1235 | 1594.8388 | 2178.0861 | 2991.2788 | 4128.4623 | 5722.982 | 7964.1224 | 11120.8507 | 15575.711 | 21873.2302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 69.2977 | 91.8582 | 122.8268 | 165.5288 | 224.6502 | 306.8068 | 421.3537 | 581.5382 | 806.1434 | 1121.8321 | 1566.4911 | 2194.006 | 3081.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.081413 | 0.10792 | 0.1443 | 0.19447 | 0.26392 | 0.36044 | 0.49502 | 0.68321 | 0.94708 | 1.318 | 1.8404 | 2.5776 | 3.6197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety | New | Replaced | BAN | Safety | 28 | 0 | 0 | 0 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 264.0864 | 316.0949 | 419.0025 | 560.2631 | 755.0441 | 1024.7209 | 1399.4708 | 1921.966 | 2652.6328 | 3677.1487 | 5117.1334 | 7145.4046 | 10007.7557 | 14054.0579
| Safety | New | Replaced | DDL | Safety | 27 | 0 | 0 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 411.0549 | 492.0069 | 652.1843 | 872.0588 | 1175.2387 | 1594.9951 | 2178.2996 | 2991.572 | 4128.867 | 5723.5429 | 7964.903 | 11121.9408 | 15577.2377 | 21875.3742
| Safety | New | Replaced | ECA | Safety | 30 | 0 | 0 | 0 | 0 | 0 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 117.4068 | 140.5286 | 186.279 | 249.0803 | 335.6755 | 455.5677 | 622.173 | 854.4625 | 1179.3004 | 1634.7769 | 2274.9614 | 3176.6848 | 4449.2211 | 6248.1152
| Safety | New | Replaced | FDN | Safety | 29 | 0 | 0 | 0 | 0 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 176.052 | 210.7232 | 279.326 | 373.4968 | 503.3466 | 683.1254 | 932.9507 | 1281.2696 | 1768.3653 | 2451.354 | 3411.313 | 4763.4505 | 6671.6235 | 9369.0719
| Safety | New | Replaced | GCY | Safety | 29 | 0 | 0 | 0 | 0 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 587.1223 | 702.7486 | 931.5349 | 1245.5883 | 1678.6296 | 2278.1805 | 3111.3322 | 4272.9541 | 5897.3875 | 8175.1121 | 11376.5155 | 15885.8095 | 22249.4469 | 31245.2686
| Safety | New | Replaced | MLN | Safety | 30 | 0 | 0 | 0 | 0 | 0 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 293.6431 | 351.4724 | 465.8975 | 622.968 | 839.5491 | 1139.4082 | 1556.1004 | 2137.0735 | 2949.5169 | 4088.6972 | 5689.8458 | 7945.1222 | 11127.8292 | 15626.9958
| Safety | New | Replaced | SA | Safety | 29 | 0 | 0 | 0 | 0 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 895.3304 | 1071.6543 | 1420.5413 | 1899.4563 | 2559.8212 | 3474.1046 | 4744.6168 | 6516.0287 | 8993.2036 | 12466.613 | 17348.5837 | 24225.0181 | 33929.2282 | 47647.3798
| Safety | New | Replaced | SHL | Safety | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 58.6885 | 70.2464 | 93.1158 | 124.5084 | 167.795 | 227.7258 | 311.0072 | 427.1224 | 589.5 | 817.1802 | 1137.191 | 1587.9378 | 2224.0439 | 3123.2618
| Safety | New | Replaced | SHN | Safety | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 455.0157 | 544.6253 | 721.9331 | 965.3225 | 1300.9264 | 1765.5743 | 2411.2611 | 3311.5102 | 4570.435 | 6335.656 | 8816.7217 | 12311.3937 | 17243.1692 | 24214.8695
| Safety | New | Replaced | TYA | Safety | 29 | 0 | 0 | 0 | 0 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 234.769 | 281.0037 | 372.4871 | 498.0657 | 671.2233 | 910.962 | 1244.1092 | 1708.5999 | 2358.152 | 3268.9318 | 4549.0573 | 6352.1609 | 8896.7495 | 12493.8533
| Safety | New | Replaced | WBE | Safety | 28 | 0 | 0 | 0 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 660.3046 | 790.3432 | 1047.6467 | 1400.8456 | 1887.8636 | 2562.1459 | 3499.1464 | 4805.5596 | 6632.4717 | 9194.1049 | 12794.5496 | 17865.9078 | 25022.7455 | 35139.858
| Environment | New | Replaced | AC | Environment | 27 | 0 | 0 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 69.2977 | 91.8582 | 122.8268 | 165.5288 | 224.6502 | 306.8068 | 421.3537 | 581.5382 | 806.1434 | 1121.8321 | 1566.4911 | 2194.006 | 3081.0792 | 0 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1005.1314 | 1203.0793 | 1594.7528 | 2132.4007 | 2873.751 | 3900.1598 | 5326.4843 | 7315.1376 | 10096.1069 | 13995.4862 | 19476.1692 | 27195.9119 | 38090.2212 | 53490.7316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 626.0093 | 829.8125 | 1109.5717 | 1495.3254 | 2029.4061 | 2771.5787 | 3806.3531 | 5253.4005 | 7282.4005 | 10134.2149 | 14151.0998 | 19819.8363 | 27833.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 15.5796 | 20.6516 | 27.614 | 37.2143 | 50.506 | 68.9766 | 94.7291 | 130.7419 | 181.2378 | 252.2112 | 352.1798 | 493.2583 | 692.6908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 411.0146 | 491.9587 | 652.1204 | 871.9733 | 1175.1235 | 1594.8388 | 2178.0861 | 2991.2788 | 4128.4623 | 5722.982 | 7964.1224 | 11120.8507 | 15575.711 | 21873.2302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 57.8958 | 69.2977 | 91.8582 | 122.8268 | 165.5288 | 224.6502 | 306.8068 | 421.3537 | 581.5382 | 806.1434 | 1121.8321 | 1566.4911 | 2194.006 | 3081.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.081413 | 0.10792 | 0.1443 | 0.19447 | 0.26392 | 0.36044 | 0.49502 | 0.68321 | 0.94708 | 1.318 | 1.8404 | 2.5776 | 3.6197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environment | New | Replaced | BAN | Environment | 28 | 0 | 0 | 0 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 37.2185 | 44.5482 | 59.0513 | 78.9596 | 106.4107 | 144.417 | 197.2317 | 270.8685 | 373.8436 | 518.2317 | 721.1731 | 1007.0235 | 1410.4233 | 1980.6809
| Environment | New | Replaced | DDL | Environment | 27 | 0 | 0 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 57.8959 | 69.2977 | 91.8583 | 122.8269 | 165.529 | 224.6504 | 306.8072 | 421.3542 | 581.5389 | 806.1444 | 1121.8335 | 1566.4931 | 2194.0087 | 3081.0829
| Environment | New | Replaced | ECA | Environment | 30 | 0 | 0 | 0 | 0 | 0 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 16.5416 | 19.7993 | 26.2451 | 35.0933 | 47.2938 | 64.1856 | 87.6588 | 120.3864 | 166.1533 | 230.3261 | 320.5226 | 447.5677 | 626.8571 | 880.3059
| Environment | New | Replaced | FDN | Environment | 29 | 0 | 0 | 0 | 0 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 24.8123 | 29.6988 | 39.3675 | 52.6397 | 70.9404 | 96.278 | 131.4877 | 180.5789 | 249.2289 | 345.4877 | 480.7819 | 671.3487 | 940.2818 | 1320.4534
| Environment | New | Replaced | GCY | Environment | 29 | 0 | 0 | 0 | 0 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 82.7082 | 98.9966 | 131.2258 | 175.4667 | 236.4694 | 320.9285 | 438.295 | 601.9333 | 830.7681 | 1151.6324 | 1602.6159 | 2237.8425 | 3134.2915 | 4401.5378
| Environment | New | Replaced | MLN | Environment | 30 | 0 | 0 | 0 | 0 | 0 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 41.3543 | 49.4985 | 65.6131 | 87.7337 | 118.2351 | 160.4648 | 219.1483 | 300.9677 | 415.3855 | 575.8182 | 801.3107 | 1118.9252 | 1567.1512 | 2200.7766
| Environment | New | Replaced | SA | Environment | 29 | 0 | 0 | 0 | 0 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 126.13 | 150.9697 | 200.1193 | 267.5866 | 360.6157 | 489.4158 | 668.3996 | 917.9479 | 1266.9209 | 1756.2387 | 2443.9881 | 3412.7084 | 4779.7925 | 6712.3422
| Environment | New | Replaced | SHL | Environment | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 8.2708 | 9.8996 | 13.1225 | 17.5466 | 23.6468 | 32.0927 | 43.8293 | 60.193 | 83.0764 | 115.1627 | 160.2608 | 223.7831 | 313.4276 | 440.1515
| Environment | New | Replaced | SHN | Environment | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 64.0989 | 76.7223 | 101.7 | 135.9867 | 183.2638 | 248.7196 | 339.6786 | 466.4983 | 643.8452 | 892.515 | 1242.0271 | 1734.3278 | 2429.0757 | 3411.1914
| Environment | New | Replaced | TYA | Environment | 29 | 0 | 0 | 0 | 0 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 33.0832 | 39.5985 | 52.4901 | 70.1864 | 94.5874 | 128.3709 | 175.3173 | 240.7723 | 332.3058 | 460.651 | 641.0436 | 895.1332 | 1253.7113 | 1760.6076
| Environment | New | Replaced | WBE | Environment | 28 | 0 | 0 | 0 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 93.0464 | 111.3707 | 147.6285 | 197.3993 | 266.0271 | 361.0431 | 493.08 | 677.1723 | 934.6105 | 1295.5814 | 1802.9357 | 2517.5629 | 3526.0641 | 4951.7105
| NP | New | Replaced | AC | NP | 27 | 0 | 0 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.068017 | 0.081413 | 0.10792 | 0.1443 | 0.19447 | 0.26392 | 0.36044 | 0.49502 | 0.68321 | 0.94708 | 1.318 | 1.8404 | 2.5776 | 3.6197
| NP | New | Replaced | BAN | NP | 28 | 0 | 0 | 0 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 5.9887 | 7.1681 | 9.5018 | 12.7052 | 17.1222 | 23.2377 | 31.736 | 43.5847 | 60.1541 | 83.3871 | 116.0418 | 162.0372 | 226.9471 | 318.7056
| NP | New | Replaced | DDL | NP | 27 | 0 | 0 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 80.3871 | 96.2184 | 127.5431 | 170.5425 | 229.8333 | 311.9221 | 425.9949 | 585.0409 | 807.4538 | 1119.3135 | 1557.6407 | 2175.0406 | 3046.332 | 4278.0147
| NP | New | Replaced | ECA | NP | 30 | 0 | 0 | 0 | 0 | 0 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 7.7501 | 9.2763 | 12.2963 | 16.4418 | 22.158 | 30.0721 | 41.0698 | 56.4033 | 77.8459 | 107.912 | 150.1708 | 209.6938 | 293.6942 | 412.4396
| NP | New | Replaced | FDN | NP | 29 | 0 | 0 | 0 | 0 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0073736 | 0.0088258 | 0.011699 | 0.015643 | 0.021082 | 0.028612 | 0.039075 | 0.053664 | 0.074065 | 0.10267 | 0.14288 | 0.19951 | 0.27943 | 0.39241
| NP | New | Replaced | GCY | NP | 29 | 0 | 0 | 0 | 0 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 52.9966 | 63.4336 | 84.085 | 112.433 | 151.5215 | 205.64 | 280.8444 | 385.6982 | 532.3277 | 737.9266 | 1026.9013 | 1433.9328 | 2008.3466 | 2820.3545
| NP | New | Replaced | MLN | NP | 30 | 0 | 0 | 0 | 0 | 0 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 76.1325 | 91.1258 | 120.7926 | 161.5161 | 217.6688 | 295.4129 | 403.4481 | 554.0762 | 764.7174 | 1060.0711 | 1475.1988 | 2059.9213 | 2885.0976 | 4051.5905
| NP | New | Replaced | SA | NP | 29 | 0 | 0 | 0 | 0 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 143.4082 | 171.6507 | 227.5331 | 304.2426 | 410.0156 | 556.4596 | 759.962 | 1043.6953 | 1440.4732 | 1996.8214 | 2778.7839 | 3880.2067 | 5434.5643 | 7631.8491
| NP | New | Replaced | SHL | NP | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.66226 | 0.79269 | 1.0508 | 1.405 | 1.8935 | 2.5697 | 3.5095 | 4.8198 | 6.6521 | 9.2214 | 12.8325 | 17.9189 | 25.097 | 35.2441
| NP | New | Replaced | SHN | NP | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 39.1487 | 46.8585 | 62.1138 | 83.0545 | 111.9293 | 151.9067 | 207.4604 | 284.9161 | 393.2317 | 545.108 | 758.5743 | 1059.2493 | 1483.57 | 2083.4021
| NP | New | Replaced | TYA | NP | 29 | 0 | 0 | 0 | 0 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 1.6787 | 2.0094 | 2.6635 | 3.5615 | 4.7997 | 6.514 | 8.8962 | 12.2176 | 16.8623 | 23.375 | 32.5287 | 45.422 | 63.6174 | 89.339
| NP | New | Replaced | WBE | NP | 28 | 0 | 0 | 0 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 64.6507 | 77.3829 | 102.5756 | 137.1574 | 184.8416 | 250.8609 | 342.603 | 470.5145 | 649.3883 | 900.1989 | 1252.7201 | 1749.2591 | 2449.9883 | 3440.5593
| Opex | New | Replaced | AC | Financial | 27 | 0 | 0 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 523.0093 | 626.0093 | 829.8125 | 1109.5717 | 1495.3254 | 2029.4061 | 2771.5787 | 3806.3531 | 5253.4005 | 7282.4005 | 10134.2149 | 14151.0998 | 19819.8363 | 27833.326
| Opex | New | Replaced | BAN | Financial | 28 | 0 | 0 | 0 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 436.6923 | 522.6933 | 692.8609 | 926.4489 | 1248.5382 | 1694.4747 | 2314.1597 | 3178.1558 | 4386.3837 | 6080.5193 | 8461.6726 | 11815.6142 | 16548.7873 | 23239.7373
| Opex | New | Replaced | DDL | Financial | 27 | 0 | 0 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 449.6253 | 538.1733 | 713.3805 | 953.8865 | 1285.5146 | 1744.6579 | 2382.6954 | 3272.2794 | 4516.2899 | 6260.5986 | 8712.2717 | 12165.5429 | 17038.8926 | 23928.0004
| Opex | New | Replaced | ECA | Financial | 30 | 0 | 0 | 0 | 0 | 0 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 165.3767 | 197.9456 | 262.3886 | 350.8491 | 472.8253 | 641.7028 | 876.3794 | 1203.5774 | 1661.137 | 2302.7114 | 3204.4615 | 4474.6096 | 6267.0768 | 8800.9602
| Opex | New | Replaced | FDN | Financial | 29 | 0 | 0 | 0 | 0 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 325.5813 | 389.7004 | 516.571 | 690.7254 | 930.863 | 1263.3365 | 1725.3503 | 2369.5132 | 3270.3224 | 4533.4061 | 6308.7043 | 8809.2769 | 12338.1524 | 17326.6727
| Opex | New | Replaced | GCY | Financial | 29 | 0 | 0 | 0 | 0 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 775.2083 | 927.8758 | 1229.9543 | 1644.6156 | 2216.3826 | 3008.0011 | 4108.055 | 5641.8053 | 7786.6299 | 10794.0291 | 15021.0099 | 20974.8671 | 29377.1112 | 41254.7662
| Opex | New | Replaced | MLN | Financial | 30 | 0 | 0 | 0 | 0 | 0 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 310.0882 | 371.1561 | 491.9894 | 657.8565 | 886.5669 | 1203.2192 | 1643.2476 | 2256.7573 | 3114.7005 | 4317.679 | 6008.4977 | 8390.0777 | 11751.0278 | 16502.1639
| Opex | New | Replaced | SA | Financial | 29 | 0 | 0 | 0 | 0 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1112.423 | 1331.5006 | 1764.983 | 2360.0214 | 3180.5064 | 4316.478 | 5895.054 | 8095.9839 | 11173.8046 | 15489.419 | 21555.1314 | 30098.9095 | 42156.1199 | 59200.5407
| Opex | New | Replaced | SHL | Financial | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 108.5275 | 129.9006 | 172.191 | 230.2427 | 310.2889 | 421.1138 | 575.119 | 789.8407 | 1090.1116 | 1511.1411 | 2102.9094 | 2936.4368 | 4112.7331 | 5775.5796
| Opex | New | Replaced | SHN | Financial | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 531.0182 | 635.5955 | 842.5195 | 1126.5627 | 1518.2235 | 2060.4826 | 2814.0202 | 3864.6401 | 5333.8463 | 7393.9167 | 10289.4011 | 14367.797 | 20123.3395 | 28259.5406
| Opex | New | Replaced | TYA | Financial | 29 | 0 | 0 | 0 | 0 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 434.1115 | 519.6042 | 688.7662 | 920.9737 | 1241.1594 | 1684.4605 | 2300.4833 | 3159.3732 | 4360.4606 | 6044.584 | 8411.6649 | 11745.7851 | 16450.9855 | 23102.3928
| Opex | New | Replaced | WBE | Financial | 28 | 0 | 0 | 0 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 846.2582 | 1012.918 | 1342.6828 | 1795.3489 | 2419.5198 | 3283.6922 | 4484.5688 | 6158.8913 | 8500.2946 | 11783.3297 | 16397.7242 | 22897.2678 | 32069.5993 | 45035.8719
| Capex | New | Replaced | AC | Financial | 27 | 0 | 0 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 13.0162 | 15.5796 | 20.6516 | 27.614 | 37.2143 | 50.506 | 68.9766 | 94.7291 | 130.7419 | 181.2378 | 252.2112 | 352.1798 | 493.2583 | 692.6908
| Capex | New | Replaced | BAN | Financial | 28 | 0 | 0 | 0 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.81611 | 0.97683 | 1.2949 | 1.7314 | 2.3333 | 3.1667 | 4.3248 | 5.9395 | 8.1975 | 11.3636 | 15.8136 | 22.0816 | 30.9271 | 43.4315
| Capex | New | Replaced | DDL | Financial | 27 | 0 | 0 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 7.5045 | 8.9824 | 11.9067 | 15.9208 | 21.4559 | 29.1192 | 39.7684 | 54.616 | 75.3791 | 104.4925 | 145.4121 | 203.0489 | 284.3875 | 399.3702
| Capex | New | Replaced | ECA | Financial | 30 | 0 | 0 | 0 | 0 | 0 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.5847 | 1.8968 | 2.5143 | 3.3619 | 4.5307 | 6.1489 | 8.3977 | 11.533 | 15.9174 | 22.0651 | 30.7059 | 42.8767 | 60.0526 | 84.3328
| Capex | New | Replaced | FDN | Financial | 29 | 0 | 0 | 0 | 0 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.0471 | 1.2533 | 1.6613 | 2.2214 | 2.9936 | 4.0629 | 5.5487 | 7.6203 | 10.5173 | 14.5793 | 20.2886 | 28.3304 | 39.6791 | 55.7221
| Capex | New | Replaced | GCY | Financial | 29 | 0 | 0 | 0 | 0 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 9.4856 | 11.3537 | 15.05 | 20.1239 | 27.1202 | 36.8066 | 50.2672 | 69.0345 | 95.2791 | 132.0784 | 183.8008 | 256.6537 | 359.4656 | 504.8036
| Capex | New | Replaced | MLN | Financial | 30 | 0 | 0 | 0 | 0 | 0 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 5.2634 | 6.3 | 8.351 | 11.1665 | 15.0486 | 20.4235 | 27.8925 | 38.3062 | 52.8689 | 73.2883 | 101.9883 | 142.4132 | 199.462 | 280.1078
| Capex | New | Replaced | SA | Financial | 29 | 0 | 0 | 0 | 0 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 11.9767 | 14.3354 | 19.0024 | 25.4088 | 34.2424 | 46.4726 | 63.4681 | 87.1641 | 120.3009 | 166.7642 | 232.0697 | 324.0549 | 453.8668 | 637.3727
| Capex | New | Replaced | SHL | Financial | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.64334 | 0.77004 | 1.0207 | 1.3649 | 1.8394 | 2.4963 | 3.4093 | 4.6821 | 6.4621 | 8.9579 | 12.4659 | 17.407 | 24.38 | 34.2372
| Capex | New | Replaced | SHN | Financial | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 6.1824 | 7.3999 | 9.8091 | 13.1161 | 17.676 | 23.9893 | 32.7624 | 44.9942 | 62.0995 | 86.084 | 119.7948 | 167.2777 | 234.2869 | 329.0129
| Capex | New | Replaced | TYA | Financial | 29 | 0 | 0 | 0 | 0 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.8607 | 6.4432 | 8.6154 | 11.6106 | 15.7576 | 21.5203 | 29.5549 | 40.7907 | 56.5451 | 78.6884 | 109.878 | 153.8936 | 216.1154
| Capex | New | Replaced | WBE | Financial | 28 | 0 | 0 | 0 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.108 | 3.7201 | 4.9312 | 6.5936 | 8.886 | 12.0597 | 16.4701 | 22.6192 | 31.2183 | 43.2756 | 60.2225 | 84.0929 | 117.7793 | 165.3995
Summary
Base case risk
Risk before replacement
| Base case |  | All |  | Safety |  | 28996.6312 | 33309.3002 | 38461.5729 | 44670.7987 | 52181.603 | 61275.53 | 72323.5019 | 85758.8579 | 102345.9582 | 122932.0639 | 148446.1175 | 180271.0669 | 220290.5974 | 270972.6038 | 333509.0777 | 410152.0636 | 506197.0843 | 615579.9261 | 726608.6804 | 828076.6658 | 912978.5325 | 960883.6424 | 992913.1681 | 1027463.7377 | 1067886.2805 | 1112792.7272 | 1158977.4151 | 1197822.1134 | 1225702.8821 | 1239003.1697
| Base case |  | All |  | Environment |  | 3284.0252 | 3772.5283 | 4359.1759 | 5070.5201 | 5936.0199 | 6990.1612 | 8278.3689 | 9852.5884 | 11810.4203 | 14258.6992 | 17312.5468 | 21147.225 | 26003.6281 | 32198.8098 | 39872.3655 | 49303.7092 | 61342.2996 | 75386.0153 | 89934.7026 | 103144.4114 | 114133.5822 | 120058.6739 | 123699.5508 | 127588.6514 | 132179.418 | 137451.6592 | 143078.2637 | 148036.7082 | 151699.4102 | 153357.3676
| Base case |  | All |  | NP |  | 513149.6159 | 589594.3624 | 679937.7921 | 787513.6029 | 916540.6623 | 1071030.1425 | 1256744.6667 | 1482959.2867 | 1758462.6863 | 2094721.9739 | 2507065.4055 | 3015200.7921 | 3644641.7336 | 4428405.8964 | 5406517.1899 | 6632352.0182 | 8127947.1542 | 9408805.3547 | 10299040.6803 | 11176077.0136 | 11963891.0141 | 12503631.4632 | 13086897.4386 | 13724115.9638 | 14416811.7948 | 15204525.0467 | 16032378.2103 | 16623853.9093 | 16811920.8832 | 16942813.5877
| Base case |  | All |  | Financial |  | 395740.0082 | 453291.2424 | 520313.4711 | 598559.6937 | 690128.3359 | 797449.0311 | 923492.7206 | 1071858.2744 | 1247099.4879 | 1454577.2778 | 1700701.1889 | 1993529.6097 | 2343122.7953 | 2761896.042 | 3254079.0674 | 3827032.6338 | 4455693.4032 | 5090505.2705 | 5631435.6853 | 6185397.8295 | 6698775.4098 | 7141528.5849 | 7586409.882 | 8080194.2161 | 8639036.1706 | 9181819.8991 | 9646836.7553 | 9937280.7217 | 10112389.9327 | 10243438.9243
Option 2 risk
Residual risk of assets not replaced
| Option 2 |  | Not replaced |  | Safety |  | 28996.6312 | 33309.3002 | 29791.8136 | 26729.5429 | 14280.6566 | 12894.303 | 8609.865 | 10243.7847 | 12515.4462 | 15675.8533 | 19900.7452 | 25620.206 | 33508.398 | 44489.6751 | 59865.3913 | 81610.2173 | 112440.4456 | 155340.0277 | 214403.3856 | 276622.7428 | 323308.4782 | 341874.8694 | 349303.9671 | 359161.3306 | 372371.9216 | 388783.5354 | 408511.6093 | 432103.0375 | 452494.0112 | 459299.2693
| Option 2 |  | Not replaced |  | Environment |  | 3284.0252 | 3772.5283 | 3506.2202 | 3059.8384 | 1712.187 | 1576.5252 | 1094.5045 | 1306.4883 | 1604.8926 | 2024.2246 | 2588.1212 | 3355.6579 | 4419.6912 | 5907.6176 | 7998.8666 | 10966.1331 | 15184.3324 | 21062.7838 | 29162.6078 | 37815.7348 | 44315.1194 | 46854.6966 | 47822.725 | 49120.8398 | 50877.322 | 53111.4619 | 55849.0256 | 59135.3166 | 61971.0725 | 62899.6492
| Option 2 |  | Not replaced |  | NP |  | 513149.6159 | 589594.3624 | 515656.4146 | 476898.1237 | 190827.3725 | 97275.7978 | 13894.9418 | 18350.5644 | 24577.8859 | 33338.3264 | 45677.9577 | 63140.6737 | 88033.321 | 123577.3611 | 174415.4295 | 247328.2582 | 352158.9237 | 503208.8841 | 721278.8135 | 774896.0829 | 791195.757 | 806735.6761 | 811480.2205 | 817767.6359 | 826186.8359 | 836960.8575 | 851050.8826 | 870267.8869 | 885357.0971 | 887086.5656
| Option 2 |  | Not replaced |  | Financial |  | 395740.0082 | 453291.2424 | 361747.1059 | 370663.2078 | 156724.1107 | 141881.3334 | 84963.9801 | 97598.0173 | 112686.188 | 130801.7703 | 152516.7387 | 178781.1284 | 210976.0399 | 250887.1015 | 300898.1482 | 364440.8862 | 446208.7277 | 551277.4937 | 683928.5711 | 817829.968 | 929201.643 | 1000206.7404 | 1061396.0651 | 1133549.7758 | 1219156.1198 | 1290217.8076 | 1340755.8806 | 1394119.6426 | 1444341.1847 | 1473197.164
Risk of replaced assets
| Option 2 |  | Replaced |  | Safety |  | 0 | 0 | 822.0694 | 1746.4604 | 3639.7339 | 4050.7839 | 4564.4881 | 4564.4881 | 4564.4881 | 4564.4881 | 4564.4881 | 4564.4881 | 4564.4881 | 4564.4881 | 4564.4881 | 4564.4881 | 4564.4881 | 5463.4061 | 7242.0685 | 9683.6271 | 13050.2366 | 17711.3492 | 24188.5535 | 33219.3972 | 45848.2944 | 63556.0996 | 88444.8978 | 123501.6815 | 172974.7615 | 242911.3363
| Option 2 |  | Replaced |  | Environment |  | 0 | 0 | 115.7917 | 246.0566 | 512.7903 | 570.6862 | 643.0558 | 643.0558 | 643.0558 | 643.0558 | 643.0558 | 643.0558 | 643.0558 | 643.0558 | 643.0558 | 643.0558 | 643.0558 | 769.6975 | 1020.2796 | 1364.2521 | 1838.548 | 2495.2165 | 3407.7403 | 4680.0267 | 6459.2154 | 8953.9326 | 12460.325 | 17399.2071 | 24369.0908 | 34221.9198
| Option 2 |  | Replaced |  | NP |  | 0 | 0 | 80.4552 | 151.0946 | 349.1855 | 433.068 | 472.879 | 472.879 | 472.879 | 472.879 | 472.879 | 472.879 | 472.879 | 472.879 | 472.879 | 472.879 | 472.879 | 566.0065 | 750.2752 | 1003.2196 | 1351.9989 | 1834.8882 | 2505.9238 | 3441.5154 | 4749.8637 | 6584.3848 | 9162.8537 | 12794.7215 | 17920.1115 | 25165.5108
| Option 2 |  | Replaced |  | Financial |  | 0 | 0 | 993.1552 | 2280.0297 | 4953.9242 | 5436.2372 | 6082.6086 | 6082.6086 | 6082.6086 | 6082.6086 | 6082.6086 | 6082.6086 | 6082.6086 | 6082.6086 | 6082.6086 | 6082.6086 | 6082.6086 | 7280.5013 | 9650.7359 | 12904.3418 | 17390.6648 | 23602.0347 | 32233.5173 | 44267.9638 | 61097.1544 | 84694.4663 | 117861.1254 | 164577.5792 | 230505.1005 | 323702.1488
Option 3 risk
Residual risk of assets not replaced
| Option 3 |  | Not replaced |  | Safety | 33 | 28996.6312 | 33309.3002 | 38461.5729 | 44670.7987 | 52181.603 | 61275.53 | 72323.5019 | 85758.8579 | 12515.4462 | 15675.8533 | 19900.7452 | 25620.206 | 33508.398 | 44489.6751 | 59865.3913 | 81610.2173 | 112440.4456 | 155340.0277 | 214403.3856 | 276622.7428 | 323308.4782 | 341874.8694 | 349303.9671 | 359161.3306 | 372371.9216 | 388783.5354 | 408511.6093 | 432103.0375 | 452494.0112 | 459299.2693
| Option 3 |  | Not replaced |  | Environment | 33 | 3284.0252 | 3772.5283 | 4359.1759 | 5070.5201 | 5936.0199 | 6990.1612 | 8278.3689 | 9852.5884 | 1604.8926 | 2024.2246 | 2588.1212 | 3355.6579 | 4419.6912 | 5907.6176 | 7998.8666 | 10966.1331 | 15184.3324 | 21062.7838 | 29162.6078 | 37815.7348 | 44315.1194 | 46854.6966 | 47822.725 | 49120.8398 | 50877.322 | 53111.4619 | 55849.0256 | 59135.3166 | 61971.0725 | 62899.6492
| Option 3 |  | Not replaced |  | NP | 33 | 513149.6159 | 589594.3624 | 679937.7921 | 787513.6029 | 916540.6623 | 1071030.1425 | 1256744.6667 | 1482959.2867 | 24577.8859 | 33338.3264 | 45677.9577 | 63140.6737 | 88033.321 | 123577.3611 | 174415.4295 | 247328.2582 | 352158.9237 | 503208.8841 | 721278.8135 | 774896.0829 | 791195.757 | 806735.6761 | 811480.2205 | 817767.6359 | 826186.8359 | 836960.8575 | 851050.8826 | 870267.8869 | 885357.0971 | 887086.5656
| Option 3 |  | Not replaced |  | Financial | 33 | 395740.0082 | 453291.2424 | 520313.4711 | 598559.6937 | 690128.3359 | 797449.0311 | 923492.7206 | 1071858.2744 | 112686.188 | 130801.7703 | 152516.7387 | 178781.1284 | 210976.0399 | 250887.1015 | 300898.1482 | 364440.8862 | 446208.7277 | 551277.4937 | 683928.5711 | 817829.968 | 929201.643 | 1000206.7404 | 1061396.0651 | 1133549.7758 | 1219156.1198 | 1290217.8076 | 1340755.8806 | 1394119.6426 | 1444341.1847 | 1473197.164
Risk of replaced assets
| Option 3 |  | Replaced |  | Safety | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4564.4881 | 4564.4881 | 4564.4881 | 4564.4881 | 4564.4881 | 4564.4881 | 4564.4881 | 4564.4881 | 4564.4881 | 5463.4061 | 7242.0685 | 9683.6271 | 13050.2366 | 17711.3492 | 24188.5535 | 33219.3972 | 45848.2944 | 63556.0996 | 88444.8978 | 123501.6815 | 172974.7615 | 242911.3363
| Option 3 |  | Replaced |  | Environment | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 643.0558 | 643.0558 | 643.0558 | 643.0558 | 643.0558 | 643.0558 | 643.0558 | 643.0558 | 643.0558 | 769.6975 | 1020.2796 | 1364.2521 | 1838.548 | 2495.2165 | 3407.7403 | 4680.0267 | 6459.2154 | 8953.9326 | 12460.325 | 17399.2071 | 24369.0908 | 34221.9198
| Option 3 |  | Replaced |  | NP | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472.879 | 472.879 | 472.879 | 472.879 | 472.879 | 472.879 | 472.879 | 472.879 | 472.879 | 566.0065 | 750.2752 | 1003.2196 | 1351.9989 | 1834.8882 | 2505.9238 | 3441.5154 | 4749.8637 | 6584.3848 | 9162.8537 | 12794.7215 | 17920.1115 | 25165.5108
| Option 3 |  | Replaced |  | Financial | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6082.6086 | 6082.6086 | 6082.6086 | 6082.6086 | 6082.6086 | 6082.6086 | 6082.6086 | 6082.6086 | 6082.6086 | 7280.5013 | 9650.7359 | 12904.3418 | 17390.6648 | 23602.0347 | 32233.5173 | 44267.9638 | 61097.1544 | 84694.4663 | 117861.1254 | 164577.5792 | 230505.1005 | 323702.1488

## Misc_calcs
Powercor
Relay replacements
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR | bar: 2021-06-30 to 2025-06-30
| Option | First year | Option included
| Option 2 | 1 | TRUE
| Option 3 | 7 | TRUE
| Option 4 | Not used | FALSE
| Option 5 | Not used | FALSE
| First year | 1
FLAGS | bar: 2021-06-30 to 2025-06-30
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
Powercor
Relay replacements
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | TRUE | Not used |  | TRUE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
CitiPower
| Reliability in worst-served areas | per MWh | 0
| Network resilience | per MWh | 0
| Enabling solar exports | per MWh | 4220.9954
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.54769
| Customer value of time - business | per minute customer time | 0.54769
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27 | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26 | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25 | 2024-25
2023
2022
2021
2020