## Cover
Powercor
Regulatory proposal 2026-31
66kV radial lines
| Model number: | 4.1
2025-01-31
9

## Summary
Powercor
Risk-based replacement of deteriorated and aged 66kV radial lines
SUMMARY
RESULTS
[5 empty] | PV of costs | PV of benefits | NPV |  | Total capital cost
| Option |  |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30 |  | 2026-06-30
| Option 1 (base case) | No change to existing practices |  |  | 0 | 0 | 0 |  | 0
| Option 2 | Risk based like-for-like conductor replacement of deteriorated aged 66kV radial lines |  |  | 8.6261 | 63.9213 | 55.2952 |  | 15.9581
NPV
| Preferred option: |  | 2026-06-30
| Option 2 | Risk based like-for-like conductor replacement of deteriorated aged 66kV radial lines | 55.2952
EXPENDITURE
Capital expenditure 2026-31
| 2026-06-30 |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Risk based like-for-like conductor replacement of deteriorated aged 66kV radial lines |  | 3.1916 | 3.1916 | 3.1916 | 3.1916 | 3.1916 |  | 15.9581
SENSITIVITIES
NPV
2026-06-30
| Option 2 |  | 55.2952
| Capex 10% higher |  | 54.4326
| Capex 10% lower |  | 56.1578
| Total benefits 10% higher |  | 61.6873
| Total benefits 10% lower |  | 48.903
| Capex 10% higher & Total benefits 10% lower |  | 48.0404
End |  |  | . | . | . | . | . | . | .

## Total
Powercor
Risk-based replacement of deteriorated and aged 66kV radial lines
| Total conductor length assessed (km) |  | 421.5236
| Total conductor length where replacement is preferred option (km) |  | 147.6269
| Total capital cost for feeders where option 2 is preferred | 2023-12-31 | 14339005.6535
97130
| Expenditure per year over 5 years | 2023-12-31 | 2867801.1307
| Expenditure per year over 5 years | 2026-06-30 | 3191612.1458

## Assumptions
Powercor
Risk-based replacement of deteriorated and aged 66kV radial lines
Project
|  | Business: | Powercor
|  | Descripton: | Risk-based replacement of deteriorated and aged 66kV radial lines
|  | Date of cost inputs: | December | 2023
|  | Option | Description
|  | Option 1 (base case) | No change to existing practices
|  | Option 2 | Risk based like-for-like conductor replacement of deteriorated aged 66kV radial lines
Timing & WACC
|  | Input dollars |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  | 3.5% | [real_disc]
|  | VCR date |  | 2023-12-31 | [vcr_date]
|  | Model start year |  | 2025 | [start]
|  | Analysis period (years) |  | 20 | [years]\
|  | Output dollars |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  | 2024-12-31 | [custval_date]
|  | Value of CO2 reductions value date |  | 2023-12-31
Costs
| Planned unit cost of replacing 3 phase bare conductor |  | $/m | 97.13
| Asset life (years) |  |  | 80
VNR
|  | Average to max. demand ratio based on ZSS network average |  | 50%
|  | Demand forecast flat after |  | 2034-35
|  | Average outage duration |  | 2 | hours | Based on network CAIDI
Other risks
SAFETY
|  | Value of statistical life |  | 5400000 | 2023-06-30
|  | Value of injury |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  | 1
|  | Harm to property from bushfire |  | 1
|  | Harm to environment |  | 1
|  | Safety - Public trespass |  | 1
|  | Safety - Single fatality or serious injury ^ |  | 3
|  | Safety from bushfire in HBRA |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  | 6
|  | Safety from bushfire (REFCL declared areas) |  | 6
|  | Safety from bushfire (electric line construction areas) |  | 10
^ Public or employee
|  | Incident type |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Premium for failure |  | 10%
|  | Probability of new conductor failure | per m per annum | 2.8157e-07
Other benefits
| ENVIRONMENTAL | [6 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  | 2023-12-31 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  | Value
|  | Reliability in worst-served areas |  | 151432.8174 | 2024-12-31 | per MWh
|  | Enabling solar exports |  | 88.3577 | 2024-12-31 | per MWh
|  | Aesthetics |  | 0 | 2024-12-31 | per customer
|  | Customer value of time - residential |  | 0.35181 | 2024-12-31 | per customer minute
|  | Customer value of time - business |  | 0.35181 | 2024-12-31 | per customer minute
|  | Communication |  | 0 | 2024-12-31 | per customer
|  | Information accessibility |  | 0 | 2024-12-31 | per customer
Sensitivities
|  |  |  | Capex | Total benefits
| 1 | Capex 10% higher |  | 10% | 0%
| 2 | Capex 10% lower |  | -10% | 0%
| 3 | Total benefits 10% higher |  | 0% | 10%
| 4 | Total benefits 10% lower |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  | 10% | -10%

## Demand
Powercor
Risk-based replacement of deteriorated and aged 66kV radial lines
| Feeder | Weighted average demand (MW)
|  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46
| AC024 | 0.162 | 0.162 | 0.162 | 0.162 | 0.162 | 0.162 | 0.162 | 0.162 | 0.169 | 0.169 | 0.169 | 0.169 | 0.169 | 0.169 | 0.169 | 0.169 | 0.169 | 0.169 | 0.169 | 0.169
| AC025 | 6.075 | 6.164 | 6.299 | 6.424 | 6.463 | 6.516 | 6.651 | 6.829 | 6.877 | 6.877 | 6.877 | 6.877 | 6.877 | 6.877 | 6.877 | 6.877 | 6.877 | 6.877 | 6.877 | 6.877
| AC031 | 1.922 | 1.932 | 1.945 | 1.962 | 1.965 | 1.975 | 1.995 | 2.008 | 2.025 | 2.025 | 2.025 | 2.025 | 2.025 | 2.025 | 2.025 | 2.025 | 2.025 | 2.025 | 2.025 | 2.025
| AL002 | 2.852 | 2.865 | 2.895 | 2.918 | 2.928 | 2.938 | 2.978 | 3.021 | 3.031 | 3.031 | 3.031 | 3.031 | 3.031 | 3.031 | 3.031 | 3.031 | 3.031 | 3.031 | 3.031 | 3.031
| AL006 | 4.382 | 4.475 | 4.575 | 4.668 | 4.728 | 4.794 | 4.893 | 5.006 | 5.072 | 5.072 | 5.072 | 5.072 | 5.072 | 5.072 | 5.072 | 5.072 | 5.072 | 5.072 | 5.072 | 5.072
| AL007 | 2.687 | 2.707 | 2.747 | 2.777 | 2.807 | 2.837 | 2.88 | 2.94 | 2.963 | 2.963 | 2.963 | 2.963 | 2.963 | 2.963 | 2.963 | 2.963 | 2.963 | 2.963 | 2.963 | 2.963
| AL011 | 3.332 | 3.352 | 3.375 | 3.385 | 3.395 | 3.408 | 3.438 | 3.461 | 3.481 | 3.481 | 3.481 | 3.481 | 3.481 | 3.481 | 3.481 | 3.481 | 3.481 | 3.481 | 3.481 | 3.481
| AL012 | 4.015 | 4.068 | 4.132 | 4.199 | 4.239 | 4.279 | 4.349 | 4.423 | 4.474 | 4.474 | 4.474 | 4.474 | 4.474 | 4.474 | 4.474 | 4.474 | 4.474 | 4.474 | 4.474 | 4.474
| AL013 | 1.213 | 1.213 | 1.223 | 1.223 | 1.226 | 1.233 | 1.233 | 1.243 | 1.253 | 1.253 | 1.253 | 1.253 | 1.253 | 1.253 | 1.253 | 1.253 | 1.253 | 1.253 | 1.253 | 1.253
| AL014 | 7.579 | 7.678 | 7.804 | 7.9 | 7.963 | 8.032 | 8.16 | 8.313 | 8.386 | 8.386 | 8.386 | 8.386 | 8.386 | 8.386 | 8.386 | 8.386 | 8.386 | 8.386 | 8.386 | 8.386
| AP001 | 3.4 | 3.483 | 3.579 | 3.669 | 3.752 | 3.832 | 3.928 | 4.031 | 4.121 | 4.121 | 4.121 | 4.121 | 4.121 | 4.121 | 4.121 | 4.121 | 4.121 | 4.121 | 4.121 | 4.121
| AP003 | 4.438 | 4.568 | 4.711 | 4.824 | 4.92 | 5.04 | 5.193 | 5.336 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45
| AP005 | 5.454 | 5.643 | 5.83 | 6.003 | 6.156 | 6.339 | 6.575 | 6.771 | 6.912 | 6.912 | 6.912 | 6.912 | 6.912 | 6.912 | 6.912 | 6.912 | 6.912 | 6.912 | 6.912 | 6.912
| AP006 | 4.039 | 4.112 | 4.195 | 4.268 | 4.328 | 4.398 | 4.478 | 4.564 | 4.627 | 4.627 | 4.627 | 4.627 | 4.627 | 4.627 | 4.627 | 4.627 | 4.627 | 4.627 | 4.627 | 4.627
| AP007 | 2.688 | 2.761 | 2.841 | 2.901 | 2.954 | 3.024 | 3.107 | 3.197 | 3.247 | 3.247 | 3.247 | 3.247 | 3.247 | 3.247 | 3.247 | 3.247 | 3.247 | 3.247 | 3.247 | 3.247
| AP008 | 5.874 | 6.073 | 6.315 | 6.53 | 6.712 | 6.888 | 7.12 | 7.365 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56
| AP009 | 5.223 | 5.309 | 5.408 | 5.497 | 5.573 | 5.639 | 5.731 | 5.837 | 5.896 | 5.896 | 5.896 | 5.896 | 5.896 | 5.896 | 5.896 | 5.896 | 5.896 | 5.896 | 5.896 | 5.896
| AP011 | 2.037 | 2.08 | 2.133 | 2.172 | 2.212 | 2.255 | 2.304 | 2.357 | 2.393 | 2.393 | 2.393 | 2.393 | 2.393 | 2.393 | 2.393 | 2.393 | 2.393 | 2.393 | 2.393 | 2.393
| AP012 | 1.237 | 1.267 | 1.287 | 1.31 | 1.33 | 1.35 | 1.377 | 1.4 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42
| AP013 | 2.293 | 2.369 | 2.469 | 2.545 | 2.608 | 2.681 | 2.771 | 2.874 | 2.937 | 2.937 | 2.937 | 2.937 | 2.937 | 2.937 | 2.937 | 2.937 | 2.937 | 2.937 | 2.937 | 2.937
| AP014 | 3.995 | 4.061 | 4.137 | 4.216 | 4.276 | 4.339 | 4.425 | 4.519 | 4.579 | 4.579 | 4.579 | 4.579 | 4.579 | 4.579 | 4.579 | 4.579 | 4.579 | 4.579 | 4.579 | 4.579
| AP015 | 3.401 | 3.51 | 3.646 | 3.772 | 3.878 | 3.977 | 4.103 | 4.258 | 4.348 | 4.348 | 4.348 | 4.348 | 4.348 | 4.348 | 4.348 | 4.348 | 4.348 | 4.348 | 4.348 | 4.348
| AP017 | 5.154 | 5.254 | 5.374 | 5.474 | 5.544 | 5.628 | 5.738 | 5.851 | 5.914 | 5.914 | 5.914 | 5.914 | 5.914 | 5.914 | 5.914 | 5.914 | 5.914 | 5.914 | 5.914 | 5.914
| AP018 | 2.8 | 2.84 | 2.887 | 2.923 | 2.963 | 2.999 | 3.039 | 3.089 | 3.142 | 3.142 | 3.142 | 3.142 | 3.142 | 3.142 | 3.142 | 3.142 | 3.142 | 3.142 | 3.142 | 3.142
| AP019 | 5.175 | 5.253 | 5.266 | 5.289 | 5.299 | 5.309 | 5.322 | 5.342 | 5.355 | 5.355 | 5.355 | 5.355 | 5.355 | 5.355 | 5.355 | 5.355 | 5.355 | 5.355 | 5.355 | 5.355
| AR002 | 2.777 | 2.794 | 2.817 | 2.847 | 2.86 | 2.876 | 2.906 | 2.939 | 2.952 | 2.952 | 2.952 | 2.952 | 2.952 | 2.952 | 2.952 | 2.952 | 2.952 | 2.952 | 2.952 | 2.952
| AR003 | 4.426 | 4.479 | 4.542 | 4.595 | 4.618 | 4.651 | 4.704 | 4.78 | 4.807 | 4.807 | 4.807 | 4.807 | 4.807 | 4.807 | 4.807 | 4.807 | 4.807 | 4.807 | 4.807 | 4.807
| AR004 | 4.427 | 4.486 | 4.576 | 4.638 | 4.688 | 4.755 | 4.814 | 4.913 | 4.952 | 4.952 | 4.952 | 4.952 | 4.952 | 4.952 | 4.952 | 4.952 | 4.952 | 4.952 | 4.952 | 4.952
| AR005 | 2.857 | 2.884 | 2.927 | 2.957 | 2.977 | 2.997 | 3.04 | 3.083 | 3.103 | 3.103 | 3.103 | 3.103 | 3.103 | 3.103 | 3.103 | 3.103 | 3.103 | 3.103 | 3.103 | 3.103
| AR006 | 4.743 | 4.799 | 4.869 | 4.922 | 4.965 | 5.008 | 5.068 | 5.124 | 5.167 | 5.167 | 5.167 | 5.167 | 5.167 | 5.167 | 5.167 | 5.167 | 5.167 | 5.167 | 5.167 | 5.167
| AR007 | 4.108 | 4.142 | 4.162 | 4.168 | 4.172 | 4.175 | 4.205 | 4.255 | 4.265 | 4.265 | 4.265 | 4.265 | 4.265 | 4.265 | 4.265 | 4.265 | 4.265 | 4.265 | 4.265 | 4.265
| AR009 | 3.046 | 3.079 | 3.129 | 3.162 | 3.192 | 3.218 | 3.261 | 3.321 | 3.354 | 3.354 | 3.354 | 3.354 | 3.354 | 3.354 | 3.354 | 3.354 | 3.354 | 3.354 | 3.354 | 3.354
| AR010 | 4.426 | 4.553 | 4.703 | 4.826 | 4.912 | 5.029 | 5.196 | 5.332 | 5.427 | 5.427 | 5.427 | 5.427 | 5.427 | 5.427 | 5.427 | 5.427 | 5.427 | 5.427 | 5.427 | 5.427
| AR011 | 3.815 | 3.885 | 3.972 | 4.022 | 4.048 | 4.108 | 4.211 | 4.281 | 4.315 | 4.315 | 4.315 | 4.315 | 4.315 | 4.315 | 4.315 | 4.315 | 4.315 | 4.315 | 4.315 | 4.315
| AR012 | 4.24 | 4.303 | 4.386 | 4.459 | 4.509 | 4.558 | 4.641 | 4.724 | 4.774 | 4.774 | 4.774 | 4.774 | 4.774 | 4.774 | 4.774 | 4.774 | 4.774 | 4.774 | 4.774 | 4.774
| AR013 | 2.143 | 2.156 | 2.179 | 2.199 | 2.206 | 2.209 | 2.232 | 2.259 | 2.259 | 2.259 | 2.259 | 2.259 | 2.259 | 2.259 | 2.259 | 2.259 | 2.259 | 2.259 | 2.259 | 2.259
| ART023 | 4.828 | 4.799 | 4.796 | 4.783 | 4.743 | 4.734 | 4.738 | 4.732 | 4.702 | 4.702 | 4.702 | 4.702 | 4.702 | 4.702 | 4.702 | 4.702 | 4.702 | 4.702 | 4.702 | 4.702
| ART031 | 3.693 | 3.67 | 3.673 | 3.67 | 3.653 | 3.637 | 3.64 | 3.667 | 3.664 | 3.664 | 3.664 | 3.664 | 3.664 | 3.664 | 3.664 | 3.664 | 3.664 | 3.664 | 3.664 | 3.664
| ART033 | 5.511 | 5.554 | 5.619 | 5.666 | 5.662 | 5.675 | 5.744 | 5.833 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81 | 5.81
| ART034 | 5.114 | 5.124 | 5.147 | 5.16 | 5.15 | 5.14 | 5.163 | 5.206 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196 | 5.196
| AWT011 | 1.33 | 3.09 | 4.66 | 5.28 | 5.91 | 6.4 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
| AWT021 | 1.33 | 3.09 | 4.66 | 5.28 | 5.91 | 6.4 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
| B002 | 2.2 | 2.246 | 2.299 | 2.342 | 2.388 | 2.431 | 2.48 | 2.523 | 2.566 | 2.566 | 2.566 | 2.566 | 2.566 | 2.566 | 2.566 | 2.566 | 2.566 | 2.566 | 2.566 | 2.566
| B003 | 1.732 | 1.768 | 1.824 | 1.87 | 1.896 | 1.929 | 1.985 | 2.054 | 2.077 | 2.077 | 2.077 | 2.077 | 2.077 | 2.077 | 2.077 | 2.077 | 2.077 | 2.077 | 2.077 | 2.077
| B004 | 3.33 | 3.453 | 3.589 | 3.702 | 3.798 | 3.918 | 4.071 | 4.21 | 4.306 | 4.306 | 4.306 | 4.306 | 4.306 | 4.306 | 4.306 | 4.306 | 4.306 | 4.306 | 4.306 | 4.306
| B005 | 3.307 | 3.382 | 3.415 | 3.438 | 3.438 | 3.441 | 3.477 | 3.523 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52
| B006 | 2.09 | 2.123 | 2.163 | 2.196 | 2.229 | 2.259 | 2.292 | 2.335 | 2.368 | 2.368 | 2.368 | 2.368 | 2.368 | 2.368 | 2.368 | 2.368 | 2.368 | 2.368 | 2.368 | 2.368
| B011 | 4.459 | 4.499 | 4.549 | 4.592 | 4.612 | 4.635 | 4.685 | 4.732 | 4.752 | 4.752 | 4.752 | 4.752 | 4.752 | 4.752 | 4.752 | 4.752 | 4.752 | 4.752 | 4.752 | 4.752
| B012 | 14.055 | 14.301 | 14.55 | 14.776 | 14.972 | 15.191 | 15.45 | 15.709 | 15.938 | 15.938 | 15.938 | 15.938 | 15.938 | 15.938 | 15.938 | 15.938 | 15.938 | 15.938 | 15.938 | 15.938
| B013 | 3.292 | 3.365 | 3.468 | 3.545 | 3.618 | 3.691 | 3.784 | 3.887 | 3.957 | 3.957 | 3.957 | 3.957 | 3.957 | 3.957 | 3.957 | 3.957 | 3.957 | 3.957 | 3.957 | 3.957
| B014 | 2.434 | 2.497 | 2.57 | 2.633 | 2.693 | 2.746 | 2.816 | 2.896 | 2.945 | 2.945 | 2.945 | 2.945 | 2.945 | 2.945 | 2.945 | 2.945 | 2.945 | 2.945 | 2.945 | 2.945
| B015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| B016 | 1.931 | 1.961 | 1.994 | 2.014 | 2.034 | 2.067 | 2.097 | 2.13 | 2.143 | 2.143 | 2.143 | 2.143 | 2.143 | 2.143 | 2.143 | 2.143 | 2.143 | 2.143 | 2.143 | 2.143
| B021 | 4.682 | 4.742 | 4.819 | 4.875 | 4.925 | 4.975 | 5.052 | 5.12 | 5.164 | 5.164 | 5.164 | 5.164 | 5.164 | 5.164 | 5.164 | 5.164 | 5.164 | 5.164 | 5.164 | 5.164
| B025 | 2.579 | 2.642 | 2.715 | 2.781 | 2.834 | 2.897 | 2.97 | 3.053 | 3.106 | 3.106 | 3.106 | 3.106 | 3.106 | 3.106 | 3.106 | 3.106 | 3.106 | 3.106 | 3.106 | 3.106
| B026_B027 | 3.687 | 3.77 | 3.903 | 4.006 | 4.036 | 4.089 | 4.225 | 4.388 | 4.398 | 4.398 | 4.398 | 4.398 | 4.398 | 4.398 | 4.398 | 4.398 | 4.398 | 4.398 | 4.398 | 4.398
| BAE011 | 11.883 | 12.029 | 12.255 | 12.443 | 12.521 | 12.647 | 12.855 | 13.103 | 13.279 | 13.279 | 13.279 | 13.279 | 13.279 | 13.279 | 13.279 | 13.279 | 13.279 | 13.279 | 13.279 | 13.279
| BAE012 | 11.54 | 11.723 | 11.933 | 12.082 | 12.192 | 12.355 | 12.631 | 12.818 | 12.846 | 12.846 | 12.846 | 12.846 | 12.846 | 12.846 | 12.846 | 12.846 | 12.846 | 12.846 | 12.846 | 12.846
| BAE021 | 0 | 0 | 3.512 | 3.578 | 3.615 | 3.655 | 3.738 | 3.828 | 3.887 | 3.887 | 3.887 | 3.887 | 3.887 | 3.887 | 3.887 | 3.887 | 3.887 | 3.887 | 3.887 | 3.887
| BAE022 | 11.254 | 11.576 | 11.924 | 12.249 | 12.494 | 12.769 | 13.121 | 13.52 | 13.799 | 13.799 | 13.799 | 13.799 | 13.799 | 13.799 | 13.799 | 13.799 | 13.799 | 13.799 | 13.799 | 13.799
| BAN001 | 5.902 | 5.888 | 5.887 | 5.86 | 5.826 | 5.812 | 5.838 | 5.85 | 5.799 | 5.799 | 5.799 | 5.799 | 5.799 | 5.799 | 5.799 | 5.799 | 5.799 | 5.799 | 5.799 | 5.799
| BAN002 | 9.422 | 9.472 | 9.545 | 9.606 | 9.62 | 9.676 | 9.774 | 9.845 | 9.883 | 9.883 | 9.883 | 9.883 | 9.883 | 9.883 | 9.883 | 9.883 | 9.883 | 9.883 | 9.883 | 9.883
| BAN003 | 9.22 | 9.443 | 9.738 | 9.94 | 10.113 | 10.336 | 10.637 | 10.903 | 11.04 | 11.04 | 11.04 | 11.04 | 11.04 | 11.04 | 11.04 | 11.04 | 11.04 | 11.04 | 11.04 | 11.04
| BAN004 | 9.899 | 9.913 | 9.959 | 9.963 | 9.953 | 9.973 | 10.049 | 10.099 | 10.079 | 10.079 | 10.079 | 10.079 | 10.079 | 10.079 | 10.079 | 10.079 | 10.079 | 10.079 | 10.079 | 10.079
| BAN005 | 8.233 | 8.146 | 8.053 | 7.976 | 7.889 | 7.834 | 7.816 | 7.826 | 7.806 | 7.806 | 7.806 | 7.806 | 7.806 | 7.806 | 7.806 | 7.806 | 7.806 | 7.806 | 7.806 | 7.806
| BAN006 | 10.393 | 10.505 | 10.661 | 10.803 | 10.847 | 10.926 | 11.095 | 11.32 | 11.408 | 11.408 | 11.408 | 11.408 | 11.408 | 11.408 | 11.408 | 11.408 | 11.408 | 11.408 | 11.408 | 11.408
| BAN007 | 9.693 | 1.016 | 1.036 | 1.046 | 1.056 | 1.066 | 1.096 | 1.106 | 1.113 | 1.113 | 1.113 | 1.113 | 1.113 | 1.113 | 1.113 | 1.113 | 1.113 | 1.113 | 1.113 | 1.113
| BAN008 | 8.414 | 0.083 | 0.083 | 0.086 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093
| BAN009 | 9.291 | 9.329 | 9.396 | 9.476 | 9.467 | 9.484 | 9.578 | 9.708 | 9.743 | 9.743 | 9.743 | 9.743 | 9.743 | 9.743 | 9.743 | 9.743 | 9.743 | 9.743 | 9.743 | 9.743
| BAN011 | 13.266 | 13.551 | 13.996 | 14.404 | 14.512 | 14.665 | 15.106 | 15.676 | 15.824 | 15.824 | 15.824 | 15.824 | 15.824 | 15.824 | 15.824 | 15.824 | 15.824 | 15.824 | 15.824 | 15.824
| BAN013 | 10.593 | 10.743 | 10.946 | 11.125 | 11.284 | 11.503 | 11.812 | 12.082 | 12.249 | 12.249 | 12.249 | 12.249 | 12.249 | 12.249 | 12.249 | 12.249 | 12.249 | 12.249 | 12.249 | 12.249
| BAN015 | 11.914 | 8.481 | 8.664 | 8.796 | 8.873 | 8.973 | 9.143 | 9.374 | 9.519 | 9.519 | 9.519 | 9.519 | 9.519 | 9.519 | 9.519 | 9.519 | 9.519 | 9.519 | 9.519 | 9.519
| BAS011 | 18.915 | 11.467 | 11.749 | 12.001 | 12.16 | 12.339 | 12.627 | 12.935 | 13.125 | 13.125 | 13.125 | 13.125 | 13.125 | 13.125 | 13.125 | 13.125 | 13.125 | 13.125 | 13.125 | 13.125
| BAS012 | 6.833 | 6.236 | 6.252 | 6.248 | 6.231 | 6.257 | 6.304 | 6.337 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34 | 6.34
| BAS014 | 8.546 | 16.365 | 17.354 | 17.3 | 17.202 | 17.165 | 17.175 | 17.184 | 17.118 | 17.118 | 17.118 | 17.118 | 17.118 | 17.118 | 17.118 | 17.118 | 17.118 | 17.118 | 17.118 | 17.118
| BAS021 | 5.356 | 5.429 | 5.542 | 5.604 | 5.65 | 5.753 | 5.883 | 5.982 | 6.045 | 6.045 | 6.045 | 6.045 | 6.045 | 6.045 | 6.045 | 6.045 | 6.045 | 6.045 | 6.045 | 6.045
| BAS022 | 11.78 | 11.938 | 12.188 | 8.844 | 8.928 | 9.038 | 9.234 | 9.464 | 9.612 | 9.612 | 9.612 | 9.612 | 9.612 | 9.612 | 9.612 | 9.612 | 9.612 | 9.612 | 9.612 | 9.612
| BAS023 | 7.874 | 1.989 | 2.029 | 2.055 | 2.068 | 2.108 | 2.158 | 2.191 | 2.211 | 2.211 | 2.211 | 2.211 | 2.211 | 2.211 | 2.211 | 2.211 | 2.211 | 2.211 | 2.211 | 2.211
| BAS024 | 14.676 | 9.53 | 9.825 | 10.11 | 10.349 | 10.604 | 10.933 | 11.309 | 11.578 | 11.578 | 11.578 | 11.578 | 11.578 | 11.578 | 11.578 | 11.578 | 11.578 | 11.578 | 11.578 | 11.578
| BAS031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BAS032 | 11.251 | 11.298 | 11.443 | 11.532 | 11.597 | 11.719 | 11.894 | 12.077 | 12.209 | 12.209 | 12.209 | 12.209 | 12.209 | 12.209 | 12.209 | 12.209 | 12.209 | 12.209 | 12.209 | 12.209
| BAS033 | 9.72 | 7.974 | 8.184 | 8.383 | 8.552 | 8.754 | 9.053 | 9.379 | 9.614 | 9.614 | 9.614 | 9.614 | 9.614 | 9.614 | 9.614 | 9.614 | 9.614 | 9.614 | 9.614 | 9.614
| BAS034 | 10.507 | 10.647 | 10.831 | 10.992 | 11.096 | 11.213 | 11.404 | 11.656 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802
| BBD013 | 11.642 | 11.785 | 12.025 | 12.207 | 12.244 | 12.307 | 12.55 | 12.866 | 12.899 | 12.899 | 12.899 | 12.899 | 12.899 | 12.899 | 12.899 | 12.899 | 12.899 | 12.899 | 12.899 | 12.899
| BBD014 | 11.255 | 11.169 | 11.126 | 11.063 | 10.937 | 10.827 | 10.807 | 10.81 | 10.711 | 10.711 | 10.711 | 10.711 | 10.711 | 10.711 | 10.711 | 10.711 | 10.711 | 10.711 | 10.711 | 10.711
| BBD021 | 7.949 | 7.989 | 8.095 | 8.168 | 8.148 | 8.148 | 8.264 | 8.42 | 8.407 | 8.407 | 8.407 | 8.407 | 8.407 | 8.407 | 8.407 | 8.407 | 8.407 | 8.407 | 8.407 | 8.407
| BBD022 | 6.529 | 6.466 | 6.426 | 6.376 | 6.3 | 6.23 | 6.2 | 6.19 | 6.137 | 6.137 | 6.137 | 6.137 | 6.137 | 6.137 | 6.137 | 6.137 | 6.137 | 6.137 | 6.137 | 6.137
| BC002 | 4.801 | 6.757 | 7.298 | 7.321 | 7.331 | 7.335 | 7.332 | 7.325 | 7.282 | 7.282 | 7.282 | 7.282 | 7.282 | 7.282 | 7.282 | 7.282 | 7.282 | 7.282 | 7.282 | 7.282
| BC003 | 6.922 | 4.483 | 4.529 | 4.565 | 4.575 | 4.596 | 4.636 | 4.682 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672
| BC006 | 2.537 | 2.607 | 2.67 | 2.727 | 2.77 | 2.83 | 2.903 | 2.973 | 3.023 | 3.023 | 3.023 | 3.023 | 3.023 | 3.023 | 3.023 | 3.023 | 3.023 | 3.023 | 3.023 | 3.023
| BC007 | 5.284 | 5.282 | 5.295 | 5.292 | 5.289 | 5.282 | 5.292 | 5.325 | 5.316 | 5.316 | 5.316 | 5.316 | 5.316 | 5.316 | 5.316 | 5.316 | 5.316 | 5.316 | 5.316 | 5.316
| BC011 | 2.871 | 2.928 | 2.998 | 3.051 | 3.094 | 3.141 | 3.204 | 3.267 | 3.304 | 3.304 | 3.304 | 3.304 | 3.304 | 3.304 | 3.304 | 3.304 | 3.304 | 3.304 | 3.304 | 3.304
| BC012 | 3.733 | 3.774 | 3.834 | 3.891 | 3.931 | 3.975 | 4.032 | 4.109 | 4.159 | 4.159 | 4.159 | 4.159 | 4.159 | 4.159 | 4.159 | 4.159 | 4.159 | 4.159 | 4.159 | 4.159
| BC013 | 4.178 | 4.268 | 4.371 | 4.448 | 4.498 | 4.575 | 4.685 | 4.787 | 4.838 | 4.838 | 4.838 | 4.838 | 4.838 | 4.838 | 4.838 | 4.838 | 4.838 | 4.838 | 4.838 | 4.838
| BC014 | 2.257 | 2.307 | 2.36 | 2.403 | 2.446 | 2.496 | 2.546 | 2.599 | 2.642 | 2.642 | 2.642 | 2.642 | 2.642 | 2.642 | 2.642 | 2.642 | 2.642 | 2.642 | 2.642 | 2.642
| BC015 | 3.08 | 3.196 | 3.32 | 3.422 | 3.518 | 3.625 | 3.784 | 3.921 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005 | 4.005
| BC019 | 6.051 | 6.004 | 5.967 | 5.937 | 5.883 | 5.833 | 5.799 | 5.772 | 5.739 | 5.739 | 5.739 | 5.739 | 5.739 | 5.739 | 5.739 | 5.739 | 5.739 | 5.739 | 5.739 | 5.739
| BC020 | 2.242 | 2.292 | 2.345 | 2.379 | 2.405 | 2.445 | 2.505 | 2.565 | 2.612 | 2.612 | 2.612 | 2.612 | 2.612 | 2.612 | 2.612 | 2.612 | 2.612 | 2.612 | 2.612 | 2.612
| BC022 | 2.101 | 2.154 | 2.224 | 2.277 | 2.317 | 2.36 | 2.423 | 2.496 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536
| BC024 | 5.775 | 5.802 | 5.832 | 5.838 | 5.835 | 5.851 | 5.892 | 5.945 | 5.945 | 5.945 | 5.945 | 5.945 | 5.945 | 5.945 | 5.945 | 5.945 | 5.945 | 5.945 | 5.945 | 5.945
| BET001 | 13.706 | 13.841 | 14.034 | 14.19 | 14.296 | 14.399 | 14.602 | 14.834 | 14.975 | 14.975 | 14.975 | 14.975 | 14.975 | 14.975 | 14.975 | 14.975 | 14.975 | 14.975 | 14.975 | 14.975
| BET002 | 6.405 | 6.458 | 6.551 | 6.617 | 6.66 | 6.714 | 6.817 | 6.947 | 7.028 | 7.028 | 7.028 | 7.028 | 7.028 | 7.028 | 7.028 | 7.028 | 7.028 | 7.028 | 7.028 | 7.028
| BET003 | 2.667 | 2.671 | 2.679 | 2.683 | 2.68 | 2.681 | 2.702 | 2.716 | 2.717 | 2.717 | 2.717 | 2.717 | 2.717 | 2.717 | 2.717 | 2.717 | 2.717 | 2.717 | 2.717 | 2.717
| BET004 | 9.447 | 9.57 | 9.73 | 9.864 | 9.953 | 10.047 | 10.22 | 10.41 | 10.53 | 10.53 | 10.53 | 10.53 | 10.53 | 10.53 | 10.53 | 10.53 | 10.53 | 10.53 | 10.53 | 10.53
| BET005 | 11.191 | 11.38 | 11.636 | 11.851 | 11.981 | 12.14 | 12.419 | 12.758 | 12.924 | 12.924 | 12.924 | 12.924 | 12.924 | 12.924 | 12.924 | 12.924 | 12.924 | 12.924 | 12.924 | 12.924
| BET006 | 15.345 | 15.551 | 15.825 | 16.081 | 16.224 | 16.404 | 16.724 | 17.039 | 17.258 | 17.258 | 17.258 | 17.258 | 17.258 | 17.258 | 17.258 | 17.258 | 17.258 | 17.258 | 17.258 | 17.258
| BET007 | 12.741 | 13.025 | 13.333 | 13.626 | 13.821 | 14.05 | 14.423 | 14.841 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09 | 15.09
| BET008 | 9.07 | 9.08 | 9.126 | 9.182 | 9.216 | 9.245 | 9.349 | 9.439 | 9.476 | 9.476 | 9.476 | 9.476 | 9.476 | 9.476 | 9.476 | 9.476 | 9.476 | 9.476 | 9.476 | 9.476
| BGO011 | 3.733 | 3.706 | 3.682 | 3.662 | 3.632 | 3.602 | 3.585 | 3.568 | 3.559 | 3.559 | 3.559 | 3.559 | 3.559 | 3.559 | 3.559 | 3.559 | 3.559 | 3.559 | 3.559 | 3.559
| BGO012 | 6.369 | 6.372 | 6.398 | 6.408 | 6.401 | 6.401 | 6.447 | 6.496 | 6.507 | 6.507 | 6.507 | 6.507 | 6.507 | 6.507 | 6.507 | 6.507 | 6.507 | 6.507 | 6.507 | 6.507
| BGO013 | 7.065 | 7.245 | 7.458 | 7.645 | 7.794 | 7.974 | 8.2 | 8.467 | 8.643 | 8.643 | 8.643 | 8.643 | 8.643 | 8.643 | 8.643 | 8.643 | 8.643 | 8.643 | 8.643 | 8.643
| BGO014 | 2.971 | 2.941 | 2.928 | 2.908 | 2.871 | 2.834 | 2.804 | 2.787 | 2.756 | 2.756 | 2.756 | 2.756 | 2.756 | 2.756 | 2.756 | 2.756 | 2.756 | 2.756 | 2.756 | 2.756
| BGO022 | 8.963 | 9.006 | 9.092 | 9.149 | 9.162 | 9.202 | 9.333 | 9.469 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
| BGO023 | 10.783 | 10.955 | 11.159 | 11.352 | 11.501 | 11.647 | 11.879 | 12.139 | 12.328 | 12.328 | 12.328 | 12.328 | 12.328 | 12.328 | 12.328 | 12.328 | 12.328 | 12.328 | 12.328 | 12.328
| BGO024 | 5.905 | 5.845 | 5.821 | 5.798 | 5.738 | 5.675 | 5.649 | 5.626 | 5.526 | 5.526 | 5.526 | 5.526 | 5.526 | 5.526 | 5.526 | 5.526 | 5.526 | 5.526 | 5.526 | 5.526
| BK002 | 2.749 | 2.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK003 | 1.551 | 1.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK004 | 2.449 | 2.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK005 | 1.195 | 1.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK006 | 0.838 | 0.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK007 | 2.03 | 2.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK009 | 2.174 | 2.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK010 | 2.586 | 2.803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BK011 | 3.208 | 3.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLT016 | 12.303 | 12.48 | 12.7 | 12.869 | 12.972 | 13.136 | 13.373 | 13.606 | 13.691 | 13.691 | 13.691 | 13.691 | 13.691 | 13.691 | 13.691 | 13.691 | 13.691 | 13.691 | 13.691 | 13.691
| BLT017 | 8.939 | 8.952 | 8.968 | 9.053 | 9.095 | 9.148 | 9.25 | 9.364 | 9.396 | 9.396 | 9.396 | 9.396 | 9.396 | 9.396 | 9.396 | 9.396 | 9.396 | 9.396 | 9.396 | 9.396
| BLT020 | 7.751 | 7.953 | 8.162 | 8.361 | 8.547 | 8.733 | 8.939 | 9.145 | 9.334 | 9.334 | 9.334 | 9.334 | 9.334 | 9.334 | 9.334 | 9.334 | 9.334 | 9.334 | 9.334 | 9.334
| BLT021 | 7.604 | 7.634 | 7.687 | 7.733 | 7.757 | 7.767 | 7.82 | 7.889 | 7.906 | 7.906 | 7.906 | 7.906 | 7.906 | 7.906 | 7.906 | 7.906 | 7.906 | 7.906 | 7.906 | 7.906
| BLT022 | 6.821 | 6.903 | 7.051 | 7.11 | 7.117 | 7.2 | 7.372 | 7.524 | 7.487 | 7.487 | 7.487 | 7.487 | 7.487 | 7.487 | 7.487 | 7.487 | 7.487 | 7.487 | 7.487 | 7.487
| BLT030 | 6.372 | 6.438 | 6.538 | 6.606 | 6.646 | 6.692 | 6.795 | 6.931 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99 | 6.99
| BLT031 | 2.145 | 2.165 | 2.205 | 2.235 | 2.245 | 2.255 | 2.295 | 2.338 | 2.341 | 2.341 | 2.341 | 2.341 | 2.341 | 2.341 | 2.341 | 2.341 | 2.341 | 2.341 | 2.341 | 2.341
| BMH003 | 7.457 | 7.71 | 7.98 | 8.193 | 8.386 | 8.636 | 8.978 | 9.292 | 9.472 | 9.472 | 9.472 | 9.472 | 9.472 | 9.472 | 9.472 | 9.472 | 9.472 | 9.472 | 9.472 | 9.472
| BMH004 | 8.577 | 8.893 | 9.272 | 9.622 | 9.942 | 10.282 | 10.714 | 11.215 | 11.625 | 11.625 | 11.625 | 11.625 | 11.625 | 11.625 | 11.625 | 11.625 | 11.625 | 11.625 | 11.625 | 11.625
| BMH005 | 10.585 | 10.947 | 11.365 | 11.771 | 12.113 | 12.5 | 12.968 | 13.496 | 13.922 | 13.922 | 13.922 | 13.922 | 13.922 | 13.922 | 13.922 | 13.922 | 13.922 | 13.922 | 13.922 | 13.922
| BMH006 | 4.767 | 4.791 | 4.862 | 4.939 | 4.99 | 5.041 | 5.158 | 5.272 | 5.356 | 5.356 | 5.356 | 5.356 | 5.356 | 5.356 | 5.356 | 5.356 | 5.356 | 5.356 | 5.356 | 5.356
| BQ011 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
| BQ012 | 3.487 | 3.49 | 3.5 | 3.49 | 3.48 | 3.49 | 3.503 | 3.523 | 3.523 | 3.523 | 3.523 | 3.523 | 3.523 | 3.523 | 3.523 | 3.523 | 3.523 | 3.523 | 3.523 | 3.523
| BQ013 | 4.137 | 4.167 | 4.197 | 4.237 | 4.243 | 4.273 | 4.316 | 4.359 | 4.402 | 4.402 | 4.402 | 4.402 | 4.402 | 4.402 | 4.402 | 4.402 | 4.402 | 4.402 | 4.402 | 4.402
| BQ014 | 3.24 | 3.243 | 3.263 | 3.273 | 3.27 | 3.273 | 3.3 | 3.333 | 3.343 | 3.343 | 3.343 | 3.343 | 3.343 | 3.343 | 3.343 | 3.343 | 3.343 | 3.343 | 3.343 | 3.343
| BQ017 | 9.584 | 9.736 | 9.875 | 9.953 | 9.992 | 10.062 | 10.27 | 10.496 | 10.486 | 10.486 | 10.486 | 10.486 | 10.486 | 10.486 | 10.486 | 10.486 | 10.486 | 10.486 | 10.486 | 10.486
| BQ021 | 3.286 | 3.31 | 3.313 | 3.316 | 3.316 | 3.316 | 3.326 | 3.336 | 3.339 | 3.339 | 3.339 | 3.339 | 3.339 | 3.339 | 3.339 | 3.339 | 3.339 | 3.339 | 3.339 | 3.339
| BQ024 | 3.083 | 3.073 | 3.073 | 3.07 | 3.053 | 3.05 | 3.053 | 3.07 | 3.073 | 3.073 | 3.073 | 3.073 | 3.073 | 3.073 | 3.073 | 3.073 | 3.073 | 3.073 | 3.073 | 3.073
| BQ025 | 3.047 | 3.037 | 3.044 | 3.044 | 3.034 | 3.034 | 3.044 | 3.057 | 3.067 | 3.067 | 3.067 | 3.067 | 3.067 | 3.067 | 3.067 | 3.067 | 3.067 | 3.067 | 3.067 | 3.067
| BQ026 | 5.925 | 6.064 | 6.276 | 6.442 | 6.495 | 6.571 | 6.793 | 7.055 | 7.085 | 7.085 | 7.085 | 7.085 | 7.085 | 7.085 | 7.085 | 7.085 | 7.085 | 7.085 | 7.085 | 7.085
| BQ027 | 3.136 | 3.193 | 3.233 | 3.263 | 3.296 | 3.325 | 3.368 | 3.411 | 3.431 | 3.431 | 3.431 | 3.431 | 3.431 | 3.431 | 3.431 | 3.431 | 3.431 | 3.431 | 3.431 | 3.431
| BQ032 | 4.055 | 4.068 | 4.098 | 4.111 | 4.108 | 4.118 | 4.161 | 4.214 | 4.217 | 4.217 | 4.217 | 4.217 | 4.217 | 4.217 | 4.217 | 4.217 | 4.217 | 4.217 | 4.217 | 4.217
| BQ034 | 4.213 | 4.203 | 4.193 | 4.18 | 4.16 | 4.14 | 4.14 | 4.133 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123 | 4.123
| BQ035 | 4.878 | 4.855 | 4.825 | 4.802 | 4.772 | 4.742 | 4.729 | 4.729 | 4.729 | 4.729 | 4.729 | 4.729 | 4.729 | 4.729 | 4.729 | 4.729 | 4.729 | 4.729 | 4.729 | 4.729
| BQ036 | 4.426 | 4.476 | 4.495 | 4.505 | 4.505 | 4.518 | 4.551 | 4.588 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585
| BQ037 | 0.869 | 0.862 | 0.859 | 0.859 | 0.859 | 0.849 | 0.849 | 0.859 | 0.859 | 0.859 | 0.859 | 0.859 | 0.859 | 0.859 | 0.859 | 0.859 | 0.859 | 0.859 | 0.859 | 0.859
| BQ041 | 4.283 | 4.311 | 4.365 | 4.395 | 4.415 | 4.448 | 4.522 | 4.584 | 4.581 | 4.581 | 4.581 | 4.581 | 4.581 | 4.581 | 4.581 | 4.581 | 4.581 | 4.581 | 4.581 | 4.581
| BQ043 | 4.229 | 4.209 | 4.199 | 4.179 | 4.166 | 4.149 | 4.156 | 4.159 | 4.169 | 4.169 | 4.169 | 4.169 | 4.169 | 4.169 | 4.169 | 4.169 | 4.169 | 4.169 | 4.169 | 4.169
| BQ046 | 1.59 | 1.63 | 1.683 | 1.726 | 1.743 | 1.763 | 1.826 | 1.889 | 1.889 | 1.889 | 1.889 | 1.889 | 1.889 | 1.889 | 1.889 | 1.889 | 1.889 | 1.889 | 1.889 | 1.889
| BQ047 | 7.679 | 8.106 | 8.238 | 8.327 | 8.34 | 8.366 | 8.491 | 8.643 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652
| BQ051 | 4.62 | 4.686 | 4.763 | 4.793 | 4.816 | 4.859 | 4.942 | 5.005 | 5.019 | 5.019 | 5.019 | 5.019 | 5.019 | 5.019 | 5.019 | 5.019 | 5.019 | 5.019 | 5.019 | 5.019
| BQ052 | 3.174 | 3.154 | 3.144 | 3.131 | 3.111 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101
| BQ053 | 4.053 | 4.04 | 4.04 | 4.03 | 4.017 | 4.007 | 4.007 | 4.021 | 4.018 | 4.018 | 4.018 | 4.018 | 4.018 | 4.018 | 4.018 | 4.018 | 4.018 | 4.018 | 4.018 | 4.018
| BQ056 | 4.147 | 4.289 | 4.425 | 4.558 | 4.674 | 4.803 | 4.951 | 5.094 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218
| BQ057 | 2.43 | 2.46 | 2.483 | 2.503 | 2.503 | 2.506 | 2.529 | 2.562 | 2.562 | 2.562 | 2.562 | 2.562 | 2.562 | 2.562 | 2.562 | 2.562 | 2.562 | 2.562 | 2.562 | 2.562
| BQ061 | 4.05 | 4.02 | 4 | 3.98 | 3.957 | 3.937 | 3.93 | 3.93 | 3.937 | 3.937 | 3.937 | 3.937 | 3.937 | 3.937 | 3.937 | 3.937 | 3.937 | 3.937 | 3.937 | 3.937
| BQ062 | 7.113 | 7.067 | 7.027 | 6.984 | 6.938 | 6.908 | 6.898 | 6.898 | 6.898 | 6.898 | 6.898 | 6.898 | 6.898 | 6.898 | 6.898 | 6.898 | 6.898 | 6.898 | 6.898 | 6.898
| BQ065 | 4.946 | 4.916 | 4.89 | 4.874 | 4.854 | 4.839 | 4.856 | 4.879 | 4.889 | 4.889 | 4.889 | 4.889 | 4.889 | 4.889 | 4.889 | 4.889 | 4.889 | 4.889 | 4.889 | 4.889
| BQ066 | 1.617 | 1.653 | 1.709 | 1.759 | 1.769 | 1.795 | 1.851 | 1.927 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93
| BQ067 | 6.582 | 6.691 | 6.856 | 6.978 | 7.021 | 7.087 | 7.269 | 7.477 | 7.51 | 7.51 | 7.51 | 7.51 | 7.51 | 7.51 | 7.51 | 7.51 | 7.51 | 7.51 | 7.51 | 7.51
| BW021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CDN001 | 8.865 | 8.926 | 9.025 | 9.063 | 9.056 | 9.091 | 9.236 | 9.348 | 9.261 | 9.261 | 9.261 | 9.261 | 9.261 | 9.261 | 9.261 | 9.261 | 9.261 | 9.261 | 9.261 | 9.261
| CDN002 | 1.948 | 1.981 | 2.031 | 2.074 | 2.084 | 2.094 | 2.147 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217 | 2.217
| CDN003 | 3.341 | 3.342 | 3.349 | 3.336 | 3.313 | 3.304 | 3.308 | 3.309 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286
| CDN004 | 1.399 | 1.403 | 1.427 | 1.433 | 1.43 | 1.437 | 1.461 | 1.481 | 1.467 | 1.467 | 1.467 | 1.467 | 1.467 | 1.467 | 1.467 | 1.467 | 1.467 | 1.467 | 1.467 | 1.467
| CDN006 | 2.34 | 2.364 | 2.401 | 2.414 | 2.414 | 2.428 | 2.472 | 2.505 | 2.477 | 2.477 | 2.477 | 2.477 | 2.477 | 2.477 | 2.477 | 2.477 | 2.477 | 2.477 | 2.477 | 2.477
| CFD021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CFD023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA003 | 3.48 | 3.47 | 3.48 | 3.47 | 3.447 | 3.427 | 3.434 | 3.447 | 3.424 | 3.424 | 3.424 | 3.424 | 3.424 | 3.424 | 3.424 | 3.424 | 3.424 | 3.424 | 3.424 | 3.424
| CHA005 | 4.863 | 4.866 | 4.922 | 4.962 | 4.946 | 4.95 | 5.04 | 5.153 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13 | 5.13
| CHA006 | 6.993 | 7.072 | 7.205 | 7.288 | 7.288 | 7.318 | 7.458 | 7.621 | 7.601 | 7.601 | 7.601 | 7.601 | 7.601 | 7.601 | 7.601 | 7.601 | 7.601 | 7.601 | 7.601 | 7.601
| CHA007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHA008 | 2.225 | 2.192 | 2.169 | 2.15 | 2.127 | 2.101 | 2.078 | 2.055 | 2.042 | 2.042 | 2.042 | 2.042 | 2.042 | 2.042 | 2.042 | 2.042 | 2.042 | 2.042 | 2.042 | 2.042
| CHM011 | 2.19 | 2.187 | 2.187 | 2.187 | 2.174 | 2.157 | 2.154 | 2.164 | 2.144 | 2.144 | 2.144 | 2.144 | 2.144 | 2.144 | 2.144 | 2.144 | 2.144 | 2.144 | 2.144 | 2.144
| CL011 | 4.642 | 4.678 | 4.713 | 4.733 | 4.752 | 4.791 | 4.843 | 4.916 | 4.949 | 4.949 | 4.949 | 4.949 | 4.949 | 4.949 | 4.949 | 4.949 | 4.949 | 4.949 | 4.949 | 4.949
| CL013 | 4.565 | 4.801 | 4.794 | 4.784 | 4.757 | 4.737 | 4.737 | 4.736 | 4.719 | 4.719 | 4.719 | 4.719 | 4.719 | 4.719 | 4.719 | 4.719 | 4.719 | 4.719 | 4.719 | 4.719
| CL014 | 2.873 | 2.9 | 2.933 | 2.953 | 2.973 | 2.986 | 3.016 | 3.039 | 3.059 | 3.059 | 3.059 | 3.059 | 3.059 | 3.059 | 3.059 | 3.059 | 3.059 | 3.059 | 3.059 | 3.059
| CL015 | 2.394 | 2.424 | 2.464 | 2.494 | 2.507 | 2.534 | 2.567 | 2.607 | 2.627 | 2.627 | 2.627 | 2.627 | 2.627 | 2.627 | 2.627 | 2.627 | 2.627 | 2.627 | 2.627 | 2.627
| CL016 | 3.571 | 3.581 | 3.594 | 3.611 | 3.611 | 3.611 | 3.62 | 3.643 | 3.646 | 3.646 | 3.646 | 3.646 | 3.646 | 3.646 | 3.646 | 3.646 | 3.646 | 3.646 | 3.646 | 3.646
| CL021 | 3.3 | 3.336 | 3.379 | 3.412 | 3.442 | 3.478 | 3.521 | 3.598 | 3.631 | 3.631 | 3.631 | 3.631 | 3.631 | 3.631 | 3.631 | 3.631 | 3.631 | 3.631 | 3.631 | 3.631
| CL022 | 3.377 | 3.427 | 3.483 | 3.526 | 3.556 | 3.599 | 3.649 | 3.712 | 3.742 | 3.742 | 3.742 | 3.742 | 3.742 | 3.742 | 3.742 | 3.742 | 3.742 | 3.742 | 3.742 | 3.742
| CL023 | 4.09 | 4.082 | 4.11 | 4.14 | 4.15 | 4.169 | 4.202 | 4.268 | 4.283 | 4.283 | 4.283 | 4.283 | 4.283 | 4.283 | 4.283 | 4.283 | 4.283 | 4.283 | 4.283 | 4.283
| CL026 | 2.041 | 2.041 | 2.057 | 2.087 | 2.107 | 2.137 | 2.18 | 2.23 | 2.257 | 2.257 | 2.257 | 2.257 | 2.257 | 2.257 | 2.257 | 2.257 | 2.257 | 2.257 | 2.257 | 2.257
| CL027 | 1.827 | 1.834 | 1.844 | 1.844 | 1.854 | 1.854 | 1.861 | 1.871 | 1.881 | 1.881 | 1.881 | 1.881 | 1.881 | 1.881 | 1.881 | 1.881 | 1.881 | 1.881 | 1.881 | 1.881
| CL028 | 4.374 | 4.394 | 4.414 | 4.427 | 4.437 | 4.447 | 4.467 | 4.49 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51 | 4.51
| CL033 | 3.273 | 3.343 | 3.423 | 3.493 | 3.543 | 3.6 | 3.687 | 3.787 | 3.844 | 3.844 | 3.844 | 3.844 | 3.844 | 3.844 | 3.844 | 3.844 | 3.844 | 3.844 | 3.844 | 3.844
| CL035 | 1.304 | 1.304 | 1.307 | 1.314 | 1.307 | 1.297 | 1.307 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32
| CL036 | 3.903 | 3.96 | 4.03 | 4.08 | 4.12 | 4.16 | 4.218 | 4.302 | 4.329 | 4.329 | 4.329 | 4.329 | 4.329 | 4.329 | 4.329 | 4.329 | 4.329 | 4.329 | 4.329 | 4.329
| CL037 | 3.206 | 3.203 | 3.219 | 3.236 | 3.253 | 3.273 | 3.33 | 3.385 | 3.404 | 3.404 | 3.404 | 3.404 | 3.404 | 3.404 | 3.404 | 3.404 | 3.404 | 3.404 | 3.404 | 3.404
| CL038 | 4.724 | 4.696 | 4.705 | 4.711 | 4.7 | 4.702 | 4.735 | 4.801 | 4.817 | 4.817 | 4.817 | 4.817 | 4.817 | 4.817 | 4.817 | 4.817 | 4.817 | 4.817 | 4.817 | 4.817
| CLC001 | 7.617 | 7.583 | 7.579 | 7.579 | 7.549 | 7.525 | 7.548 | 7.568 | 7.558 | 7.558 | 7.558 | 7.558 | 7.558 | 7.558 | 7.558 | 7.558 | 7.558 | 7.558 | 7.558 | 7.558
| CLC002 | 5.704 | 5.694 | 5.721 | 5.729 | 5.733 | 5.746 | 5.789 | 5.865 | 5.853 | 5.853 | 5.853 | 5.853 | 5.853 | 5.853 | 5.853 | 5.853 | 5.853 | 5.853 | 5.853 | 5.853
| CLC003 | 6.433 | 6.53 | 6.669 | 6.757 | 6.801 | 6.892 | 7.035 | 7.175 | 7.202 | 7.202 | 7.202 | 7.202 | 7.202 | 7.202 | 7.202 | 7.202 | 7.202 | 7.202 | 7.202 | 7.202
| CLC004 | 8.819 | 9.346 | 9.407 | 9.423 | 9.41 | 9.435 | 9.516 | 9.589 | 9.555 | 9.555 | 9.555 | 9.555 | 9.555 | 9.555 | 9.555 | 9.555 | 9.555 | 9.555 | 9.555 | 9.555
| CLC006 | 10.698 | 10.712 | 10.746 | 10.752 | 10.732 | 10.73 | 10.777 | 10.824 | 10.83 | 10.83 | 10.83 | 10.83 | 10.83 | 10.83 | 10.83 | 10.83 | 10.83 | 10.83 | 10.83 | 10.83
| CLC012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLC013 | 6.98 | 7.071 | 7.221 | 7.316 | 7.379 | 7.505 | 7.585 | 7.724 | 7.748 | 7.748 | 7.748 | 7.748 | 7.748 | 7.748 | 7.748 | 7.748 | 7.748 | 7.748 | 7.748 | 7.748
| CLC014 | 6.26 | 6.297 | 6.364 | 6.418 | 6.436 | 6.44 | 6.481 | 6.547 | 6.565 | 6.565 | 6.565 | 6.565 | 6.565 | 6.565 | 6.565 | 6.565 | 6.565 | 6.565 | 6.565 | 6.565
| CME014 | 11.628 | 11.781 | 12.001 | 12.136 | 12.23 | 12.36 | 12.578 | 12.799 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892
| CME015 | 7.496 | 7.503 | 7.552 | 7.601 | 7.591 | 7.571 | 7.64 | 7.75 | 7.762 | 7.762 | 7.762 | 7.762 | 7.762 | 7.762 | 7.762 | 7.762 | 7.762 | 7.762 | 7.762 | 7.762
| CME016 | 8.415 | 8.528 | 8.692 | 8.828 | 8.898 | 8.978 | 9.158 | 9.37 | 9.449 | 9.449 | 9.449 | 9.449 | 9.449 | 9.449 | 9.449 | 9.449 | 9.449 | 9.449 | 9.449 | 9.449
| CME021 | 6.896 | 6.903 | 6.936 | 6.953 | 6.926 | 6.906 | 6.936 | 6.986 | 6.976 | 6.976 | 6.976 | 6.976 | 6.976 | 6.976 | 6.976 | 6.976 | 6.976 | 6.976 | 6.976 | 6.976
| CME022 | 10.612 | 10.539 | 10.489 | 10.429 | 10.345 | 10.272 | 10.229 | 10.196 | 10.146 | 10.146 | 10.146 | 10.146 | 10.146 | 10.146 | 10.146 | 10.146 | 10.146 | 10.146 | 10.146 | 10.146
| CMN001 | 4.251 | 4.315 | 4.399 | 4.468 | 4.508 | 4.559 | 4.656 | 4.744 | 4.796 | 4.796 | 4.796 | 4.796 | 4.796 | 4.796 | 4.796 | 4.796 | 4.796 | 4.796 | 4.796 | 4.796
| CMN002 | 3.623 | 3.647 | 3.674 | 3.697 | 3.707 | 3.734 | 3.774 | 3.814 | 3.827 | 3.827 | 3.827 | 3.827 | 3.827 | 3.827 | 3.827 | 3.827 | 3.827 | 3.827 | 3.827 | 3.827
| CMN003 | 6.601 | 6.677 | 6.797 | 6.9 | 6.959 | 7.029 | 7.156 | 7.288 | 7.356 | 7.356 | 7.356 | 7.356 | 7.356 | 7.356 | 7.356 | 7.356 | 7.356 | 7.356 | 7.356 | 7.356
| CMN004 | 3.342 | 3.375 | 3.428 | 3.478 | 3.491 | 3.521 | 3.578 | 3.647 | 3.678 | 3.678 | 3.678 | 3.678 | 3.678 | 3.678 | 3.678 | 3.678 | 3.678 | 3.678 | 3.678 | 3.678
| CMN005 | 9.401 | 9.434 | 9.488 | 9.527 | 9.544 | 9.577 | 9.624 | 9.684 | 9.72 | 9.72 | 9.72 | 9.72 | 9.72 | 9.72 | 9.72 | 9.72 | 9.72 | 9.72 | 9.72 | 9.72
| CMN008 | 5.285 | 5.366 | 5.47 | 5.552 | 5.595 | 5.663 | 5.787 | 5.888 | 5.957 | 5.957 | 5.957 | 5.957 | 5.957 | 5.957 | 5.957 | 5.957 | 5.957 | 5.957 | 5.957 | 5.957
| COB011 | 5.849 | 5.945 | 6.097 | 6.206 | 6.219 | 6.275 | 6.444 | 6.643 | 6.636 | 6.636 | 6.636 | 6.636 | 6.636 | 6.636 | 6.636 | 6.636 | 6.636 | 6.636 | 6.636 | 6.636
| COB012 | 1.176 | 1.186 | 1.196 | 1.206 | 1.206 | 1.206 | 1.226 | 1.246 | 1.236 | 1.236 | 1.236 | 1.236 | 1.236 | 1.236 | 1.236 | 1.236 | 1.236 | 1.236 | 1.236 | 1.236
| COB021 | 4.254 | 4.207 | 4.167 | 4.127 | 4.084 | 4.041 | 4.011 | 3.981 | 3.951 | 3.951 | 3.951 | 3.951 | 3.951 | 3.951 | 3.951 | 3.951 | 3.951 | 3.951 | 3.951 | 3.951
| COB022 | 6.781 | 6.711 | 6.654 | 6.587 | 6.51 | 6.443 | 6.393 | 6.353 | 6.309 | 6.309 | 6.309 | 6.309 | 6.309 | 6.309 | 6.309 | 6.309 | 6.309 | 6.309 | 6.309 | 6.309
| CRO013 | 4.011 | 4.027 | 4.066 | 4.096 | 4.11 | 4.113 | 4.156 | 4.208 | 4.225 | 4.225 | 4.225 | 4.225 | 4.225 | 4.225 | 4.225 | 4.225 | 4.225 | 4.225 | 4.225 | 4.225
| CRO014 | 1.378 | 1.375 | 1.375 | 1.368 | 1.365 | 1.358 | 1.355 | 1.355 | 1.355 | 1.355 | 1.355 | 1.355 | 1.355 | 1.355 | 1.355 | 1.355 | 1.355 | 1.355 | 1.355 | 1.355
| CRO021 | 5.126 | 5.103 | 5.118 | 5.105 | 5.079 | 5.074 | 5.095 | 5.112 | 5.076 | 5.076 | 5.076 | 5.076 | 5.076 | 5.076 | 5.076 | 5.076 | 5.076 | 5.076 | 5.076 | 5.076
| CRO022 | 2.715 | 2.713 | 2.743 | 2.77 | 2.787 | 2.804 | 2.837 | 2.887 | 2.907 | 2.907 | 2.907 | 2.907 | 2.907 | 2.907 | 2.907 | 2.907 | 2.907 | 2.907 | 2.907 | 2.907
| CRO023 | 0.974 | 0.974 | 0.977 | 0.977 | 0.974 | 0.974 | 0.977 | 0.987 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
| CRO024 | 0.192 | 0.192 | 0.202 | 0.202 | 0.205 | 0.205 | 0.212 | 0.215 | 0.222 | 0.222 | 0.222 | 0.222 | 0.222 | 0.222 | 0.222 | 0.222 | 0.222 | 0.222 | 0.222 | 0.222
| CRO031 | 9.158 | 9.141 | 9.121 | 9.091 | 9.045 | 9.009 | 8.993 | 8.989 | 8.989 | 8.989 | 8.989 | 8.989 | 8.989 | 8.989 | 8.989 | 8.989 | 8.989 | 8.989 | 8.989 | 8.989
| CRO032 | 17.441 | 17.889 | 18.552 | 18.93 | 19.007 | 19.364 | 20.101 | 20.797 | 20.528 | 20.528 | 20.528 | 20.528 | 20.528 | 20.528 | 20.528 | 20.528 | 20.528 | 20.528 | 20.528 | 20.528
| CRO033 | 5.783 | 5.77 | 5.76 | 5.74 | 5.72 | 5.697 | 5.677 | 5.677 | 5.677 | 5.677 | 5.677 | 5.677 | 5.677 | 5.677 | 5.677 | 5.677 | 5.677 | 5.677 | 5.677 | 5.677
| CRO034 | 4.463 | 4.406 | 4.366 | 4.326 | 4.279 | 4.232 | 4.212 | 4.192 | 4.148 | 4.148 | 4.148 | 4.148 | 4.148 | 4.148 | 4.148 | 4.148 | 4.148 | 4.148 | 4.148 | 4.148
| CTN001 | 7.014 | 7.058 | 7.147 | 7.22 | 7.207 | 7.207 | 7.31 | 7.436 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41 | 7.41
| CTN002 | 2.597 | 2.594 | 2.614 | 2.624 | 2.614 | 2.607 | 2.627 | 2.657 | 2.654 | 2.654 | 2.654 | 2.654 | 2.654 | 2.654 | 2.654 | 2.654 | 2.654 | 2.654 | 2.654 | 2.654
| CTN003 | 2.094 | 2.097 | 2.124 | 2.134 | 2.124 | 2.124 | 2.137 | 2.167 | 2.157 | 2.157 | 2.157 | 2.157 | 2.157 | 2.157 | 2.157 | 2.157 | 2.157 | 2.157 | 2.157 | 2.157
| CTN004 | 8.694 | 8.645 | 8.629 | 8.655 | 8.556 | 8.483 | 8.466 | 8.474 | 8.421 | 8.421 | 8.421 | 8.421 | 8.421 | 8.421 | 8.421 | 8.421 | 8.421 | 8.421 | 8.421 | 8.421
| CTN005 | 1.371 | 1.371 | 1.368 | 1.361 | 1.348 | 1.338 | 1.335 | 1.325 | 1.305 | 1.305 | 1.305 | 1.305 | 1.305 | 1.305 | 1.305 | 1.305 | 1.305 | 1.305 | 1.305 | 1.305
| CTN006 | 6.044 | 6.02 | 6.033 | 6.033 | 5.986 | 5.956 | 5.959 | 5.982 | 5.932 | 5.932 | 5.932 | 5.932 | 5.932 | 5.932 | 5.932 | 5.932 | 5.932 | 5.932 | 5.932 | 5.932
| CW002 | 3.766 | 5.584 | 5.732 | 5.849 | 5.955 | 6.073 | 6.248 | 6.399 | 6.499 | 6.499 | 6.499 | 6.499 | 6.499 | 6.499 | 6.499 | 6.499 | 6.499 | 6.499 | 6.499 | 6.499
| CW003 | 4.095 | 6.007 | 6.185 | 6.312 | 6.416 | 6.557 | 6.765 | 6.959 | 7.065 | 7.065 | 7.065 | 7.065 | 7.065 | 7.065 | 7.065 | 7.065 | 7.065 | 7.065 | 7.065 | 7.065
| CW004 | 2.615 | 2.865 | 2.885 | 2.908 | 2.905 | 2.912 | 2.932 | 2.959 | 2.962 | 2.962 | 2.962 | 2.962 | 2.962 | 2.962 | 2.962 | 2.962 | 2.962 | 2.962 | 2.962 | 2.962
| CW005 | 3.233 | 3.25 | 3.291 | 3.325 | 3.349 | 3.38 | 3.445 | 3.488 | 3.508 | 3.508 | 3.508 | 3.508 | 3.508 | 3.508 | 3.508 | 3.508 | 3.508 | 3.508 | 3.508 | 3.508
| CW006 | 1.312 | 1.355 | 1.409 | 1.452 | 1.492 | 1.539 | 1.596 | 1.646 | 1.693 | 1.693 | 1.693 | 1.693 | 1.693 | 1.693 | 1.693 | 1.693 | 1.693 | 1.693 | 1.693 | 1.693
| CW007 | 2.993 | 3.02 | 3.053 | 3.083 | 3.106 | 3.126 | 3.169 | 3.212 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242 | 3.242
| CW008 | 1.443 | 1.476 | 1.513 | 1.546 | 1.576 | 1.613 | 1.66 | 1.697 | 1.727 | 1.727 | 1.727 | 1.727 | 1.727 | 1.727 | 1.727 | 1.727 | 1.727 | 1.727 | 1.727 | 1.727
| CW009 | 3.631 | 3.77 | 3.853 | 3.925 | 3.975 | 4.024 | 4.113 | 4.213 | 4.281 | 4.281 | 4.281 | 4.281 | 4.281 | 4.281 | 4.281 | 4.281 | 4.281 | 4.281 | 4.281 | 4.281
| CW011 | 3.19 | 3.253 | 3.336 | 3.416 | 3.476 | 3.529 | 3.605 | 3.705 | 3.758 | 3.758 | 3.758 | 3.758 | 3.758 | 3.758 | 3.758 | 3.758 | 3.758 | 3.758 | 3.758 | 3.758
| CW012 | 2.207 | 2.251 | 2.304 | 2.364 | 2.407 | 2.46 | 2.526 | 2.596 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639 | 2.639
| CW013 | 1.68 | 1.693 | 1.713 | 1.73 | 1.74 | 1.76 | 1.77 | 1.79 | 1.793 | 1.793 | 1.793 | 1.793 | 1.793 | 1.793 | 1.793 | 1.793 | 1.793 | 1.793 | 1.793 | 1.793
| CW014 | 5.969 | 7.559 | 7.821 | 8.042 | 8.216 | 8.434 | 8.728 | 8.983 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14 | 9.14
| CW015 | 6.108 | 6.183 | 6.238 | 6.283 | 6.295 | 6.307 | 6.365 | 6.427 | 6.422 | 6.422 | 6.422 | 6.422 | 6.422 | 6.422 | 6.422 | 6.422 | 6.422 | 6.422 | 6.422 | 6.422
| CW017 | 1.47 | 2.196 | 2.227 | 2.237 | 2.265 | 2.284 | 2.329 | 2.379 | 2.375 | 2.375 | 2.375 | 2.375 | 2.375 | 2.375 | 2.375 | 2.375 | 2.375 | 2.375 | 2.375 | 2.375
| CW018 | 0.21 | 0.313 | 0.316 | 0.316 | 0.323 | 0.326 | 0.326 | 0.333 | 0.336 | 0.336 | 0.336 | 0.336 | 0.336 | 0.336 | 0.336 | 0.336 | 0.336 | 0.336 | 0.336 | 0.336
| DA004 | 0.829 | 0.819 | 0.816 | 0.809 | 0.806 | 0.796 | 0.789 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786 | 0.786
| DA005 | 6.094 | 6.379 | 6.648 | 6.911 | 7.157 | 7.389 | 7.652 | 7.924 | 8.17 | 8.17 | 8.17 | 8.17 | 8.17 | 8.17 | 8.17 | 8.17 | 8.17 | 8.17 | 8.17 | 8.17
| DA006 | 5.491 | 5.717 | 5.98 | 6.208 | 6.391 | 6.587 | 6.853 | 7.136 | 7.321 | 7.321 | 7.321 | 7.321 | 7.321 | 7.321 | 7.321 | 7.321 | 7.321 | 7.321 | 7.321 | 7.321
| DA007 | 1.921 | 2.017 | 2.117 | 2.213 | 2.296 | 2.379 | 2.478 | 2.588 | 2.681 | 2.681 | 2.681 | 2.681 | 2.681 | 2.681 | 2.681 | 2.681 | 2.681 | 2.681 | 2.681 | 2.681
| DA008 | 2.97 | 2.954 | 2.962 | 2.952 | 2.939 | 2.929 | 2.939 | 2.982 | 2.966 | 2.966 | 2.966 | 2.966 | 2.966 | 2.966 | 2.966 | 2.966 | 2.966 | 2.966 | 2.966 | 2.966
| DA009 | 4.245 | 4.43 | 4.612 | 4.788 | 4.947 | 5.106 | 5.285 | 5.461 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63 | 5.63
| DA013 | 0.794 | 0.834 | 0.864 | 0.897 | 0.927 | 0.96 | 0.99 | 1.023 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06
| DA016 | 2.326 | 2.306 | 2.293 | 2.273 | 2.253 | 2.24 | 2.227 | 2.217 | 2.207 | 2.207 | 2.207 | 2.207 | 2.207 | 2.207 | 2.207 | 2.207 | 2.207 | 2.207 | 2.207 | 2.207
| DA020 | 1.884 | 1.894 | 1.914 | 1.92 | 1.92 | 1.927 | 1.947 | 1.973 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959
| DA021 | 5.565 | 5.649 | 5.672 | 5.688 | 5.704 | 5.71 | 5.732 | 5.758 | 5.771 | 5.771 | 5.771 | 5.771 | 5.771 | 5.771 | 5.771 | 5.771 | 5.771 | 5.771 | 5.771 | 5.771
| DA022 | 2.557 | 2.687 | 2.82 | 2.943 | 3.063 | 3.179 | 3.312 | 3.452 | 3.575 | 3.575 | 3.575 | 3.575 | 3.575 | 3.575 | 3.575 | 3.575 | 3.575 | 3.575 | 3.575 | 3.575
| DA026 | 2.198 | 2.181 | 2.171 | 2.161 | 2.148 | 2.128 | 2.128 | 2.118 | 2.118 | 2.118 | 2.118 | 2.118 | 2.118 | 2.118 | 2.118 | 2.118 | 2.118 | 2.118 | 2.118 | 2.118
| DA027 | 2.505 | 2.614 | 2.727 | 2.823 | 2.926 | 3.019 | 3.122 | 3.225 | 3.331 | 3.331 | 3.331 | 3.331 | 3.331 | 3.331 | 3.331 | 3.331 | 3.331 | 3.331 | 3.331 | 3.331
| DA028 | 1.491 | 1.488 | 1.488 | 1.481 | 1.478 | 1.471 | 1.468 | 1.471 | 1.471 | 1.471 | 1.471 | 1.471 | 1.471 | 1.471 | 1.471 | 1.471 | 1.471 | 1.471 | 1.471 | 1.471
| DA029 | 0.296 | 0.323 | 0.353 | 0.376 | 0.403 | 0.433 | 0.47 | 0.5 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53
| DA030 | 3.834 | 3.811 | 3.781 | 3.758 | 3.721 | 3.698 | 3.671 | 3.658 | 3.638 | 3.638 | 3.638 | 3.638 | 3.638 | 3.638 | 3.638 | 3.638 | 3.638 | 3.638 | 3.638 | 3.638
| DA031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DDL011 | 10.438 | 10.7 | 11.032 | 11.371 | 11.612 | 11.874 | 12.196 | 12.656 | 12.943 | 12.943 | 12.943 | 12.943 | 12.943 | 12.943 | 12.943 | 12.943 | 12.943 | 12.943 | 12.943 | 12.943
| DDL012 | 8.698 | 8.776 | 8.9 | 9.02 | 9.132 | 9.225 | 9.287 | 9.419 | 9.513 | 9.513 | 9.513 | 9.513 | 9.513 | 9.513 | 9.513 | 9.513 | 9.513 | 9.513 | 9.513 | 9.513
| DDL013 | 11.101 | 11.412 | 11.807 | 12.194 | 12.417 | 12.686 | 13.05 | 13.574 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97 | 13.97
| DDL014 | 2.825 | 2.868 | 2.918 | 2.971 | 2.991 | 3.017 | 3.07 | 3.14 | 3.176 | 3.176 | 3.176 | 3.176 | 3.176 | 3.176 | 3.176 | 3.176 | 3.176 | 3.176 | 3.176 | 3.176
| DDL021 | 8.912 | 9.154 | 9.445 | 9.748 | 10 | 10.245 | 10.457 | 10.779 | 11.039 | 11.039 | 11.039 | 11.039 | 11.039 | 11.039 | 11.039 | 11.039 | 11.039 | 11.039 | 11.039 | 11.039
| DDL022 | 9.741 | 10.133 | 10.581 | 11.019 | 11.41 | 11.804 | 12.282 | 12.838 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29 | 13.29
| DDL023 | 11.743 | 12.163 | 12.707 | 13.231 | 13.667 | 14.074 | 14.539 | 15.137 | 15.595 | 15.595 | 15.595 | 15.595 | 15.595 | 15.595 | 15.595 | 15.595 | 15.595 | 15.595 | 15.595 | 15.595
| DDL024 | 8.606 | 8.865 | 9.181 | 9.464 | 9.706 | 9.945 | 10.234 | 10.624 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9
| DLF001 | 5.912 | 6.238 | 6.567 | 6.873 | 7.156 | 7.435 | 7.754 | 8.103 | 8.396 | 8.396 | 8.396 | 8.396 | 8.396 | 8.396 | 8.396 | 8.396 | 8.396 | 8.396 | 8.396 | 8.396
| DLF002 | 3.091 | 3.094 | 3.101 | 3.104 | 3.104 | 3.104 | 3.121 | 3.134 | 3.154 | 3.154 | 3.154 | 3.154 | 3.154 | 3.154 | 3.154 | 3.154 | 3.154 | 3.154 | 3.154 | 3.154
| DLF003 | 3.333 | 3.409 | 3.525 | 3.624 | 3.657 | 3.697 | 3.813 | 3.962 | 3.998 | 3.998 | 3.998 | 3.998 | 3.998 | 3.998 | 3.998 | 3.998 | 3.998 | 3.998 | 3.998 | 3.998
| DLF063 | 7.565 | 7.572 | 7.582 | 7.595 | 7.595 | 7.595 | 7.628 | 7.671 | 7.714 | 7.714 | 7.714 | 7.714 | 7.714 | 7.714 | 7.714 | 7.714 | 7.714 | 7.714 | 7.714 | 7.714
| E021 | 0.06 | 0.063 | 0.07 | 0.073 | 0.073 | 0.08 | 0.083 | 0.09 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093
| E032 | 1.789 | 1.918 | 2.047 | 2.176 | 2.285 | 2.394 | 2.52 | 2.639 | 2.748 | 2.748 | 2.748 | 2.748 | 2.748 | 2.748 | 2.748 | 2.748 | 2.748 | 2.748 | 2.748 | 2.748
| E033 | 0.468 | 0.508 | 0.541 | 0.581 | 0.614 | 0.647 | 0.687 | 0.72 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76
| ECA001 | 6.648 | 6.671 | 6.72 | 6.76 | 6.763 | 6.773 | 6.823 | 6.893 | 6.913 | 6.913 | 6.913 | 6.913 | 6.913 | 6.913 | 6.913 | 6.913 | 6.913 | 6.913 | 6.913 | 6.913
| ECA003 | 7.163 | 7.164 | 7.214 | 7.257 | 7.26 | 7.277 | 7.357 | 7.43 | 7.46 | 7.46 | 7.46 | 7.46 | 7.46 | 7.46 | 7.46 | 7.46 | 7.46 | 7.46 | 7.46 | 7.46
| ECA005 | 9.143 | 9.183 | 9.253 | 9.293 | 9.286 | 9.32 | 9.393 | 9.493 | 9.496 | 9.496 | 9.496 | 9.496 | 9.496 | 9.496 | 9.496 | 9.496 | 9.496 | 9.496 | 9.496 | 9.496
| ECA007 | 4.786 | 4.718 | 4.677 | 4.583 | 4.452 | 4.38 | 4.327 | 4.408 | 4.379 | 4.379 | 4.379 | 4.379 | 4.379 | 4.379 | 4.379 | 4.379 | 4.379 | 4.379 | 4.379 | 4.379
| ECA010 | 7.421 | 7.468 | 7.578 | 7.652 | 7.675 | 7.718 | 7.831 | 7.984 | 8.021 | 8.021 | 8.021 | 8.021 | 8.021 | 8.021 | 8.021 | 8.021 | 8.021 | 8.021 | 8.021 | 8.021
| ECA012 | 6.682 | 6.772 | 6.915 | 7.025 | 7.048 | 7.094 | 7.253 | 7.439 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44 | 7.44
| EHK021 | 10.843 | 10.945 | 11.099 | 11.264 | 11.316 | 11.368 | 11.537 | 11.768 | 11.826 | 11.826 | 11.826 | 11.826 | 11.826 | 11.826 | 11.826 | 11.826 | 11.826 | 11.826 | 11.826 | 11.826
| EHK022 | 5.468 | 5.464 | 5.477 | 5.49 | 5.497 | 5.503 | 5.556 | 5.602 | 5.615 | 5.615 | 5.615 | 5.615 | 5.615 | 5.615 | 5.615 | 5.615 | 5.615 | 5.615 | 5.615 | 5.615
| EHK023 | 8.261 | 8.351 | 8.464 | 8.571 | 8.617 | 8.681 | 8.81 | 8.957 | 9.045 | 9.045 | 9.045 | 9.045 | 9.045 | 9.045 | 9.045 | 9.045 | 9.045 | 9.045 | 9.045 | 9.045
| EHK024 | 8.651 | 8.767 | 8.936 | 9.072 | 9.122 | 9.198 | 9.364 | 9.563 | 9.619 | 9.619 | 9.619 | 9.619 | 9.619 | 9.619 | 9.619 | 9.619 | 9.619 | 9.619 | 9.619 | 9.619
| EHK031 | 9.328 | 9.546 | 9.824 | 10.063 | 10.275 | 10.508 | 10.827 | 11.177 | 11.406 | 11.406 | 11.406 | 11.406 | 11.406 | 11.406 | 11.406 | 11.406 | 11.406 | 11.406 | 11.406 | 11.406
| EHK032 | 0.647 | 0.65 | 0.65 | 0.653 | 0.653 | 0.653 | 0.656 | 0.656 | 0.656 | 0.656 | 0.656 | 0.656 | 0.656 | 0.656 | 0.656 | 0.656 | 0.656 | 0.656 | 0.656 | 0.656
| EHK033 | 13.275 | 13.65 | 14.054 | 14.449 | 14.788 | 15.134 | 15.607 | 16.132 | 16.537 | 16.537 | 16.537 | 16.537 | 16.537 | 16.537 | 16.537 | 16.537 | 16.537 | 16.537 | 16.537 | 16.537
| EHK034 | 5.605 | 5.566 | 5.546 | 5.529 | 5.516 | 5.496 | 5.506 | 5.509 | 5.519 | 5.519 | 5.519 | 5.519 | 5.519 | 5.519 | 5.519 | 5.519 | 5.519 | 5.519 | 5.519 | 5.519
| ETSA001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ETSA003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F026 | 1.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F027 | 2.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F028 | 2.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F029 | 1.994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F030 | 0.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F032 | 0.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F033 | 1.895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F034 | 2.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F035 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F037 | 2.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FB002 | 3.088 | 3.343 | 3.592 | 3.831 | 4.05 | 4.266 | 4.488 | 4.714 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93 | 4.93
| FB004 | 0.19 | 0.21 | 0.223 | 0.24 | 0.253 | 0.263 | 0.28 | 0.293 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31
| FB005 | 2.474 | 2.64 | 2.8 | 2.949 | 3.092 | 3.225 | 3.368 | 3.521 | 3.681 | 3.681 | 3.681 | 3.681 | 3.681 | 3.681 | 3.681 | 3.681 | 3.681 | 3.681 | 3.681 | 3.681
| FB006 | 3.372 | 3.647 | 3.905 | 4.157 | 4.392 | 4.631 | 4.87 | 5.119 | 5.358 | 5.358 | 5.358 | 5.358 | 5.358 | 5.358 | 5.358 | 5.358 | 5.358 | 5.358 | 5.358 | 5.358
| FB010 | 4.604 | 4.965 | 5.33 | 5.665 | 5.983 | 6.305 | 6.627 | 6.959 | 7.274 | 7.274 | 7.274 | 7.274 | 7.274 | 7.274 | 7.274 | 7.274 | 7.274 | 7.274 | 7.274 | 7.274
| FB011 | 6.076 | 6.59 | 7.084 | 7.555 | 8.006 | 8.434 | 8.871 | 9.319 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76 | 9.76
| FB013 | 3.531 | 3.551 | 3.574 | 3.594 | 3.604 | 3.607 | 3.627 | 3.64 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66
| FB014 | 2.713 | 2.919 | 3.125 | 3.324 | 3.513 | 3.692 | 3.891 | 4.087 | 4.279 | 4.279 | 4.279 | 4.279 | 4.279 | 4.279 | 4.279 | 4.279 | 4.279 | 4.279 | 4.279 | 4.279
| FB015 | 3.97 | 4.294 | 4.606 | 4.904 | 5.179 | 5.454 | 5.743 | 6.018 | 6.293 | 6.293 | 6.293 | 6.293 | 6.293 | 6.293 | 6.293 | 6.293 | 6.293 | 6.293 | 6.293 | 6.293
| FB018 | 5.591 | 6.034 | 6.46 | 6.869 | 7.255 | 7.638 | 8.031 | 8.424 | 8.803 | 8.803 | 8.803 | 8.803 | 8.803 | 8.803 | 8.803 | 8.803 | 8.803 | 8.803 | 8.803 | 8.803
| FB019 | 8.934 | 9.65 | 10.337 | 11.001 | 11.617 | 12.23 | 12.856 | 13.485 | 14.104 | 14.104 | 14.104 | 14.104 | 14.104 | 14.104 | 14.104 | 14.104 | 14.104 | 14.104 | 14.104 | 14.104
| FB020 | 5.9 | 6.199 | 6.535 | 6.796 | 6.995 | 7.245 | 7.575 | 7.903 | 8.046 | 8.046 | 8.046 | 8.046 | 8.046 | 8.046 | 8.046 | 8.046 | 8.046 | 8.046 | 8.046 | 8.046
| FB022 | 1.329 | 1.435 | 1.545 | 1.648 | 1.741 | 1.834 | 1.927 | 2.02 | 2.113 | 2.113 | 2.113 | 2.113 | 2.113 | 2.113 | 2.113 | 2.113 | 2.113 | 2.113 | 2.113 | 2.113
| FB023 | 1.942 | 2.058 | 2.217 | 2.383 | 2.542 | 2.698 | 2.857 | 3.026 | 3.185 | 3.185 | 3.185 | 3.185 | 3.185 | 3.185 | 3.185 | 3.185 | 3.185 | 3.185 | 3.185 | 3.185
| FF084 | 2.987 | 3.056 | 3.139 | 3.206 | 3.259 | 3.319 | 3.399 | 3.502 | 3.553 | 3.553 | 3.553 | 3.553 | 3.553 | 3.553 | 3.553 | 3.553 | 3.553 | 3.553 | 3.553 | 3.553
| FF085 | 1.688 | 1.702 | 1.736 | 1.746 | 1.743 | 1.757 | 1.791 | 1.821 | 1.811 | 1.811 | 1.811 | 1.811 | 1.811 | 1.811 | 1.811 | 1.811 | 1.811 | 1.811 | 1.811 | 1.811
| FF086 | 2.045 | 2.075 | 2.108 | 2.138 | 2.165 | 2.188 | 2.218 | 2.261 | 2.281 | 2.281 | 2.281 | 2.281 | 2.281 | 2.281 | 2.281 | 2.281 | 2.281 | 2.281 | 2.281 | 2.281
| FF091 | 0.847 | 0.854 | 0.874 | 0.877 | 0.884 | 0.894 | 0.904 | 0.917 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924 | 0.924
| FF092 | 1.345 | 1.359 | 1.376 | 1.386 | 1.396 | 1.403 | 1.43 | 1.46 | 1.456 | 1.456 | 1.456 | 1.456 | 1.456 | 1.456 | 1.456 | 1.456 | 1.456 | 1.456 | 1.456 | 1.456
| FF097 | 2.299 | 2.326 | 2.353 | 2.373 | 2.377 | 2.388 | 2.423 | 2.448 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439
| FNS011 | 7.497 | 7.567 | 7.683 | 7.773 | 7.803 | 7.849 | 7.976 | 8.129 | 8.159 | 8.159 | 8.159 | 8.159 | 8.159 | 8.159 | 8.159 | 8.159 | 8.159 | 8.159 | 8.159 | 8.159
| FNS012 | 6.109 | 6.219 | 6.359 | 6.486 | 6.569 | 6.655 | 6.812 | 7.004 | 7.124 | 7.124 | 7.124 | 7.124 | 7.124 | 7.124 | 7.124 | 7.124 | 7.124 | 7.124 | 7.124 | 7.124
| FNS013 | 10.793 | 11.023 | 11.297 | 11.577 | 11.803 | 12.053 | 12.345 | 12.704 | 12.995 | 12.995 | 12.995 | 12.995 | 12.995 | 12.995 | 12.995 | 12.995 | 12.995 | 12.995 | 12.995 | 12.995
| FNS021 | 10.633 | 12.567 | 14.013 | 14.153 | 14.216 | 14.316 | 14.506 | 14.725 | 14.819 | 14.819 | 14.819 | 14.819 | 14.819 | 14.819 | 14.819 | 14.819 | 14.819 | 14.819 | 14.819 | 14.819
| FNS022 | 5.796 | 5.908 | 6.064 | 6.213 | 6.319 | 6.442 | 6.605 | 6.795 | 6.925 | 6.925 | 6.925 | 6.925 | 6.925 | 6.925 | 6.925 | 6.925 | 6.925 | 6.925 | 6.925 | 6.925
| FNS032 | 4.847 | 4.894 | 4.974 | 5.017 | 5.04 | 5.081 | 5.165 | 5.241 | 5.243 | 5.243 | 5.243 | 5.243 | 5.243 | 5.243 | 5.243 | 5.243 | 5.243 | 5.243 | 5.243 | 5.243
| FNS033 | 0 | 0 | 0 | 0 | 3.108 | 10.764 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1
| FR001 | 2.415 | 2.428 | 2.448 | 2.468 | 2.488 | 2.501 | 2.528 | 2.558 | 2.581 | 2.581 | 2.581 | 2.581 | 2.581 | 2.581 | 2.581 | 2.581 | 2.581 | 2.581 | 2.581 | 2.581
| FR003 | 2.45 | 2.477 | 2.477 | 2.477 | 2.48 | 2.48 | 2.48 | 2.483 | 2.493 | 2.493 | 2.493 | 2.493 | 2.493 | 2.493 | 2.493 | 2.493 | 2.493 | 2.493 | 2.493 | 2.493
| FR004 | 1.896 | 1.916 | 1.936 | 1.949 | 1.969 | 1.989 | 2.009 | 2.039 | 2.062 | 2.062 | 2.062 | 2.062 | 2.062 | 2.062 | 2.062 | 2.062 | 2.062 | 2.062 | 2.062 | 2.062
| FR005 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
| FR007 | 2.477 | 2.497 | 2.527 | 2.547 | 2.567 | 2.58 | 2.62 | 2.65 | 2.673 | 2.673 | 2.673 | 2.673 | 2.673 | 2.673 | 2.673 | 2.673 | 2.673 | 2.673 | 2.673 | 2.673
| FR008 | 3.159 | 3.076 | 3.007 | 2.931 | 2.858 | 2.792 | 2.736 | 2.683 | 2.637 | 2.637 | 2.637 | 2.637 | 2.637 | 2.637 | 2.637 | 2.637 | 2.637 | 2.637 | 2.637 | 2.637
| FR009 | 0.426 | 0.426 | 0.416 | 0.416 | 0.416 | 0.406 | 0.406 | 0.406 | 0.406 | 0.406 | 0.406 | 0.406 | 0.406 | 0.406 | 0.406 | 0.406 | 0.406 | 0.406 | 0.406 | 0.406
| FR013 | 0.933 | 0.943 | 0.953 | 0.956 | 0.963 | 0.966 | 0.976 | 0.986 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
| FR014 | 3.046 | 3.05 | 3.017 | 2.977 | 2.924 | 2.888 | 2.855 | 2.829 | 2.786 | 2.786 | 2.786 | 2.786 | 2.786 | 2.786 | 2.786 | 2.786 | 2.786 | 2.786 | 2.786 | 2.786
| FR015 | 1.832 | 1.865 | 1.905 | 1.931 | 1.951 | 1.964 | 2.007 | 2.06 | 2.073 | 2.073 | 2.073 | 2.073 | 2.073 | 2.073 | 2.073 | 2.073 | 2.073 | 2.073 | 2.073 | 2.073
| FR016 | 1.87 | 1.88 | 1.89 | 1.903 | 1.903 | 1.913 | 1.923 | 1.943 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963
| FR018 | 2.632 | 2.679 | 2.679 | 2.679 | 2.672 | 2.672 | 2.672 | 2.675 | 2.675 | 2.675 | 2.675 | 2.675 | 2.675 | 2.675 | 2.675 | 2.675 | 2.675 | 2.675 | 2.675 | 2.675
| FR019 | 2.367 | 2.387 | 2.407 | 2.427 | 2.44 | 2.45 | 2.48 | 2.506 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536 | 2.536
| FR020 | 2.32 | 2.34 | 2.37 | 2.393 | 2.413 | 2.433 | 2.466 | 2.499 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529 | 2.529
| FR024 | 2.244 | 2.267 | 2.287 | 2.3 | 2.32 | 2.333 | 2.36 | 2.386 | 2.416 | 2.416 | 2.416 | 2.416 | 2.416 | 2.416 | 2.416 | 2.416 | 2.416 | 2.416 | 2.416 | 2.416
| FR026 | 3.487 | 3.726 | 3.749 | 3.769 | 3.769 | 3.779 | 3.809 | 3.842 | 3.842 | 3.842 | 3.842 | 3.842 | 3.842 | 3.842 | 3.842 | 3.842 | 3.842 | 3.842 | 3.842 | 3.842
| FR027 | 2.624 | 2.654 | 2.677 | 2.707 | 2.723 | 2.743 | 2.786 | 2.819 | 2.852 | 2.852 | 2.852 | 2.852 | 2.852 | 2.852 | 2.852 | 2.852 | 2.852 | 2.852 | 2.852 | 2.852
| FR028 | 2.413 | 2.443 | 2.483 | 2.513 | 2.533 | 2.556 | 2.596 | 2.639 | 2.669 | 2.669 | 2.669 | 2.669 | 2.669 | 2.669 | 2.669 | 2.669 | 2.669 | 2.669 | 2.669 | 2.669
| FR029 | 2.098 | 2.111 | 2.131 | 2.144 | 2.154 | 2.167 | 2.187 | 2.21 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233 | 2.233
| FR030 | 0.808 | 0.811 | 0.821 | 0.831 | 0.831 | 0.841 | 0.851 | 0.861 | 0.871 | 0.871 | 0.871 | 0.871 | 0.871 | 0.871 | 0.871 | 0.871 | 0.871 | 0.871 | 0.871 | 0.871
| FR031 | 4.127 | 4.62 | 4.633 | 4.624 | 4.607 | 4.59 | 4.59 | 4.593 | 4.583 | 4.583 | 4.583 | 4.583 | 4.583 | 4.583 | 4.583 | 4.583 | 4.583 | 4.583 | 4.583 | 4.583
| FR032 | 3.011 | 2.931 | 2.865 | 2.792 | 2.719 | 2.656 | 2.603 | 2.56 | 2.507 | 2.507 | 2.507 | 2.507 | 2.507 | 2.507 | 2.507 | 2.507 | 2.507 | 2.507 | 2.507 | 2.507
| GB011 | 3.168 | 3.198 | 3.218 | 3.248 | 3.268 | 3.288 | 3.311 | 3.341 | 3.371 | 3.371 | 3.371 | 3.371 | 3.371 | 3.371 | 3.371 | 3.371 | 3.371 | 3.371 | 3.371 | 3.371
| GB012 | 6.737 | 6.8 | 6.88 | 6.943 | 6.986 | 7.036 | 7.109 | 7.192 | 7.252 | 7.252 | 7.252 | 7.252 | 7.252 | 7.252 | 7.252 | 7.252 | 7.252 | 7.252 | 7.252 | 7.252
| GB014 | 1.408 | 1.441 | 1.461 | 1.471 | 1.481 | 1.491 | 1.507 | 1.527 | 1.547 | 1.547 | 1.547 | 1.547 | 1.547 | 1.547 | 1.547 | 1.547 | 1.547 | 1.547 | 1.547 | 1.547
| GB031 | 4.78 | 4.82 | 4.877 | 4.904 | 4.92 | 4.964 | 5.028 | 5.091 | 5.107 | 5.107 | 5.107 | 5.107 | 5.107 | 5.107 | 5.107 | 5.107 | 5.107 | 5.107 | 5.107 | 5.107
| GB032 | 3.051 | 3.078 | 3.101 | 3.124 | 3.144 | 3.164 | 3.184 | 3.214 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24
| GCY011 | 12.162 | 12.294 | 12.497 | 12.684 | 12.772 | 12.944 | 13.117 | 13.373 | 13.517 | 13.517 | 13.517 | 13.517 | 13.517 | 13.517 | 13.517 | 13.517 | 13.517 | 13.517 | 13.517 | 13.517
| GCY012 | 6.036 | 6.006 | 5.98 | 5.96 | 5.92 | 5.866 | 5.843 | 5.819 | 5.779 | 5.779 | 5.779 | 5.779 | 5.779 | 5.779 | 5.779 | 5.779 | 5.779 | 5.779 | 5.779 | 5.779
| GCY013 | 4.715 | 4.722 | 4.732 | 4.752 | 4.752 | 4.752 | 4.765 | 4.792 | 4.805 | 4.805 | 4.805 | 4.805 | 4.805 | 4.805 | 4.805 | 4.805 | 4.805 | 4.805 | 4.805 | 4.805
| GCY014 | 12 | 12.099 | 12.245 | 12.402 | 12.469 | 12.571 | 12.706 | 12.913 | 13.041 | 13.041 | 13.041 | 13.041 | 13.041 | 13.041 | 13.041 | 13.041 | 13.041 | 13.041 | 13.041 | 13.041
| GCY021 | 2.501 | 2.494 | 2.501 | 2.501 | 2.501 | 2.491 | 2.491 | 2.495 | 2.492 | 2.492 | 2.492 | 2.492 | 2.492 | 2.492 | 2.492 | 2.492 | 2.492 | 2.492 | 2.492 | 2.492
| GCY022 | 5.807 | 5.786 | 5.785 | 5.774 | 5.747 | 5.72 | 5.733 | 5.746 | 5.716 | 5.716 | 5.716 | 5.716 | 5.716 | 5.716 | 5.716 | 5.716 | 5.716 | 5.716 | 5.716 | 5.716
| GCY023 | 1.654 | 1.654 | 1.654 | 1.654 | 1.654 | 1.654 | 1.654 | 1.664 | 1.667 | 1.667 | 1.667 | 1.667 | 1.667 | 1.667 | 1.667 | 1.667 | 1.667 | 1.667 | 1.667 | 1.667
| GCY024 | 7.248 | 7.281 | 7.34 | 7.386 | 7.426 | 7.472 | 7.535 | 7.628 | 7.671 | 7.671 | 7.671 | 7.671 | 7.671 | 7.671 | 7.671 | 7.671 | 7.671 | 7.671 | 7.671 | 7.671
| GHP011 | 10.426 | 10.651 | 10.941 | 11.202 | 11.397 | 11.613 | 11.991 | 12.401 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67 | 12.67
| GHP012 | 9.772 | 9.938 | 10.151 | 10.351 | 10.485 | 10.627 | 10.826 | 11.102 | 11.252 | 11.252 | 11.252 | 11.252 | 11.252 | 11.252 | 11.252 | 11.252 | 11.252 | 11.252 | 11.252 | 11.252
| GHP021 | 8.814 | 9.042 | 9.32 | 9.586 | 9.761 | 9.966 | 10.328 | 10.709 | 10.997 | 10.997 | 10.997 | 10.997 | 10.997 | 10.997 | 10.997 | 10.997 | 10.997 | 10.997 | 10.997 | 10.997
| GHP022 | 5.804 | 5.897 | 6.023 | 6.123 | 6.183 | 6.253 | 6.379 | 6.542 | 6.609 | 6.609 | 6.609 | 6.609 | 6.609 | 6.609 | 6.609 | 6.609 | 6.609 | 6.609 | 6.609 | 6.609
| GL011 | 5.933 | 6.04 | 6.052 | 6.067 | 6.071 | 6.098 | 6.141 | 6.182 | 6.198 | 6.198 | 6.198 | 6.198 | 6.198 | 6.198 | 6.198 | 6.198 | 6.198 | 6.198 | 6.198 | 6.198
| GL012 | 2.28 | 2.3 | 2.33 | 2.353 | 2.366 | 2.386 | 2.413 | 2.456 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
| GL013 | 4.326 | 4.396 | 4.482 | 4.555 | 4.605 | 4.661 | 4.73 | 4.843 | 4.906 | 4.906 | 4.906 | 4.906 | 4.906 | 4.906 | 4.906 | 4.906 | 4.906 | 4.906 | 4.906 | 4.906
| GL014 | 4.49 | 4.573 | 4.679 | 4.775 | 4.855 | 4.935 | 5.031 | 5.17 | 5.253 | 5.253 | 5.253 | 5.253 | 5.253 | 5.253 | 5.253 | 5.253 | 5.253 | 5.253 | 5.253 | 5.253
| GL015 | 4.753 | 4.852 | 4.984 | 5.097 | 5.177 | 5.272 | 5.394 | 5.554 | 5.631 | 5.631 | 5.631 | 5.631 | 5.631 | 5.631 | 5.631 | 5.631 | 5.631 | 5.631 | 5.631 | 5.631
| GL021 | 5.422 | 5.505 | 5.605 | 5.699 | 5.736 | 5.783 | 5.883 | 6.003 | 6.057 | 6.057 | 6.057 | 6.057 | 6.057 | 6.057 | 6.057 | 6.057 | 6.057 | 6.057 | 6.057 | 6.057
| GL022 | 7.679 | 7.768 | 7.907 | 8.017 | 8.07 | 8.162 | 8.268 | 8.426 | 8.522 | 8.522 | 8.522 | 8.522 | 8.522 | 8.522 | 8.522 | 8.522 | 8.522 | 8.522 | 8.522 | 8.522
| GL023 | 5.381 | 5.35 | 5.38 | 5.427 | 5.448 | 5.479 | 5.532 | 5.624 | 5.661 | 5.661 | 5.661 | 5.661 | 5.661 | 5.661 | 5.661 | 5.661 | 5.661 | 5.661 | 5.661 | 5.661
| GL024 | 6.302 | 6.381 | 6.483 | 6.562 | 6.621 | 6.693 | 6.785 | 6.891 | 6.967 | 6.967 | 6.967 | 6.967 | 6.967 | 6.967 | 6.967 | 6.967 | 6.967 | 6.967 | 6.967 | 6.967
| GLE011 | 3.123 | 3.14 | 3.177 | 3.193 | 3.193 | 3.21 | 3.247 | 3.287 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286 | 3.286
| GLE012 | 9.694 | 9.874 | 10.09 | 10.29 | 10.427 | 10.59 | 10.782 | 11.067 | 11.227 | 11.227 | 11.227 | 11.227 | 11.227 | 11.227 | 11.227 | 11.227 | 11.227 | 11.227 | 11.227 | 11.227
| GLE013 | 12.272 | 12.66 | 13.105 | 13.521 | 13.836 | 14.184 | 14.648 | 15.159 | 15.513 | 15.513 | 15.513 | 15.513 | 15.513 | 15.513 | 15.513 | 15.513 | 15.513 | 15.513 | 15.513 | 15.513
| GLE021 | 5.506 | 5.553 | 5.636 | 5.703 | 5.713 | 5.733 | 5.821 | 5.944 | 5.954 | 5.954 | 5.954 | 5.954 | 5.954 | 5.954 | 5.954 | 5.954 | 5.954 | 5.954 | 5.954 | 5.954
| GLE022 | 7.622 | 7.834 | 8.083 | 8.316 | 8.482 | 8.667 | 8.919 | 9.211 | 9.401 | 9.401 | 9.401 | 9.401 | 9.401 | 9.401 | 9.401 | 9.401 | 9.401 | 9.401 | 9.401 | 9.401
| GLE023 | 2.217 | 2.217 | 2.227 | 2.234 | 2.237 | 2.237 | 2.247 | 2.257 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267
| GLE024 | 10.659 | 10.745 | 10.868 | 10.956 | 10.99 | 11.043 | 11.169 | 11.311 | 11.362 | 11.362 | 11.362 | 11.362 | 11.362 | 11.362 | 11.362 | 11.362 | 11.362 | 11.362 | 11.362 | 11.362
| GLE031 | 8.866 | 8.882 | 8.944 | 9.017 | 9.044 | 9.091 | 9.177 | 9.299 | 9.348 | 9.348 | 9.348 | 9.348 | 9.348 | 9.348 | 9.348 | 9.348 | 9.348 | 9.348 | 9.348 | 9.348
| GLE032 | 6.81 | 6.878 | 6.978 | 7.041 | 7.071 | 7.132 | 7.247 | 7.342 | 7.369 | 7.369 | 7.369 | 7.369 | 7.369 | 7.369 | 7.369 | 7.369 | 7.369 | 7.369 | 7.369 | 7.369
| GLE033 | 3.271 | 3.288 | 3.312 | 3.329 | 3.325 | 3.339 | 3.369 | 3.393 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
| GSB011 | 6.565 | 6.725 | 6.902 | 7.031 | 7.134 | 7.288 | 7.489 | 7.694 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82
| GSB012 | 12.644 | 12.918 | 13.265 | 13.513 | 13.724 | 13.997 | 14.418 | 14.839 | 15.094 | 15.094 | 15.094 | 15.094 | 15.094 | 15.094 | 15.094 | 15.094 | 15.094 | 15.094 | 15.094 | 15.094
| GSB013 | 7.363 | 7.513 | 7.717 | 7.876 | 7.994 | 8.124 | 8.334 | 8.588 | 8.755 | 8.755 | 8.755 | 8.755 | 8.755 | 8.755 | 8.755 | 8.755 | 8.755 | 8.755 | 8.755 | 8.755
| GSB014 | 4.918 | 4.99 | 5.079 | 5.139 | 5.183 | 5.241 | 5.343 | 5.443 | 5.483 | 5.483 | 5.483 | 5.483 | 5.483 | 5.483 | 5.483 | 5.483 | 5.483 | 5.483 | 5.483 | 5.483
| HSM001 | 2.886 | 2.88 | 2.883 | 2.883 | 2.863 | 2.853 | 2.863 | 2.883 | 2.863 | 2.863 | 2.863 | 2.863 | 2.863 | 2.863 | 2.863 | 2.863 | 2.863 | 2.863 | 2.863 | 2.863
| HSM002 | 3.13 | 3.137 | 3.157 | 3.174 | 3.157 | 3.147 | 3.177 | 3.207 | 3.187 | 3.187 | 3.187 | 3.187 | 3.187 | 3.187 | 3.187 | 3.187 | 3.187 | 3.187 | 3.187 | 3.187
| HSM003 | 4.426 | 4.446 | 4.479 | 4.499 | 4.479 | 4.462 | 4.495 | 4.542 | 4.515 | 4.515 | 4.515 | 4.515 | 4.515 | 4.515 | 4.515 | 4.515 | 4.515 | 4.515 | 4.515 | 4.515
| HSM004 | 4.948 | 4.951 | 4.971 | 4.975 | 4.929 | 4.899 | 4.919 | 4.942 | 4.899 | 4.899 | 4.899 | 4.899 | 4.899 | 4.899 | 4.899 | 4.899 | 4.899 | 4.899 | 4.899 | 4.899
| HSM005 | 4.346 | 4.336 | 4.336 | 4.323 | 4.293 | 4.263 | 4.259 | 4.266 | 4.236 | 4.236 | 4.236 | 4.236 | 4.236 | 4.236 | 4.236 | 4.236 | 4.236 | 4.236 | 4.236 | 4.236
| HSM006 | 7.42 | 7.391 | 7.388 | 7.379 | 7.326 | 7.29 | 7.287 | 7.307 | 7.257 | 7.257 | 7.257 | 7.257 | 7.257 | 7.257 | 7.257 | 7.257 | 7.257 | 7.257 | 7.257 | 7.257
| HSM009 | 7.05 | 7.051 | 7.09 | 7.103 | 7.083 | 7.067 | 7.104 | 7.132 | 7.115 | 7.115 | 7.115 | 7.115 | 7.115 | 7.115 | 7.115 | 7.115 | 7.115 | 7.115 | 7.115 | 7.115
| HSM010 | 8.621 | 8.555 | 8.537 | 8.52 | 8.453 | 8.438 | 8.465 | 8.509 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47
| HTN011 | 1.28 | 1.3 | 1.32 | 1.33 | 1.337 | 1.354 | 1.381 | 1.404 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
| HTN012 | 3.03 | 3.057 | 3.097 | 3.11 | 3.107 | 3.121 | 3.165 | 3.198 | 3.164 | 3.164 | 3.164 | 3.164 | 3.164 | 3.164 | 3.164 | 3.164 | 3.164 | 3.164 | 3.164 | 3.164
| HTN013 | 4.711 | 4.697 | 4.704 | 4.691 | 4.655 | 4.612 | 4.613 | 4.627 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585 | 4.585
| HTN032 | 6.337 | 6.307 | 6.306 | 6.316 | 6.279 | 6.252 | 6.303 | 6.329 | 6.285 | 6.285 | 6.285 | 6.285 | 6.285 | 6.285 | 6.285 | 6.285 | 6.285 | 6.285 | 6.285 | 6.285
| HTN033 | 7.071 | 7.061 | 7.082 | 7.072 | 7.046 | 7.016 | 7.016 | 7.06 | 7.02 | 7.02 | 7.02 | 7.02 | 7.02 | 7.02 | 7.02 | 7.02 | 7.02 | 7.02 | 7.02 | 7.02
| HTN034 | 3.144 | 3.167 | 3.197 | 3.217 | 3.197 | 3.187 | 3.217 | 3.26 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24
| HYT011 | 2.342 | 2.392 | 2.472 | 2.523 | 2.536 | 2.573 | 2.667 | 2.749 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72 | 2.72
| JA001 | 2.308 | 2.381 | 2.464 | 2.544 | 2.607 | 2.677 | 2.753 | 2.836 | 2.906 | 2.906 | 2.906 | 2.906 | 2.906 | 2.906 | 2.906 | 2.906 | 2.906 | 2.906 | 2.906 | 2.906
| JA002 | 4.388 | 4.537 | 4.563 | 4.606 | 4.709 | 4.812 | 4.925 | 5.041 | 5.144 | 5.144 | 5.144 | 5.144 | 5.144 | 5.144 | 5.144 | 5.144 | 5.144 | 5.144 | 5.144 | 5.144
| JA003 | 2.286 | 2.359 | 2.439 | 2.509 | 2.552 | 2.612 | 2.685 | 2.778 | 2.825 | 2.825 | 2.825 | 2.825 | 2.825 | 2.825 | 2.825 | 2.825 | 2.825 | 2.825 | 2.825 | 2.825
| JA005 | 13.132 | 13.627 | 13.954 | 14.369 | 14.747 | 15.135 | 15.583 | 16.044 | 16.452 | 16.452 | 16.452 | 16.452 | 16.452 | 16.452 | 16.452 | 16.452 | 16.452 | 16.452 | 16.452 | 16.452
| JA006 | 5.26 | 5.456 | 5.665 | 5.864 | 6.033 | 6.205 | 6.414 | 6.627 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83 | 6.83
| JA009 | 2.515 | 2.702 | 2.768 | 2.828 | 2.878 | 2.931 | 2.994 | 3.067 | 3.117 | 3.117 | 3.117 | 3.117 | 3.117 | 3.117 | 3.117 | 3.117 | 3.117 | 3.117 | 3.117 | 3.117
| JA010 | 5.18 | 5.372 | 5.567 | 5.749 | 5.898 | 6.047 | 6.236 | 6.444 | 6.596 | 6.596 | 6.596 | 6.596 | 6.596 | 6.596 | 6.596 | 6.596 | 6.596 | 6.596 | 6.596 | 6.596
| JA011 | 7.479 | 7.751 | 8.029 | 8.281 | 8.516 | 8.758 | 9.027 | 9.305 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557
| JA013 | 6.257 | 6.492 | 6.71 | 6.928 | 7.123 | 7.321 | 7.536 | 7.761 | 7.979 | 7.979 | 7.979 | 7.979 | 7.979 | 7.979 | 7.979 | 7.979 | 7.979 | 7.979 | 7.979 | 7.979
| JA014 | 1.931 | 1.941 | 1.941 | 1.931 | 1.911 | 1.901 | 1.894 | 1.894 | 1.874 | 1.874 | 1.874 | 1.874 | 1.874 | 1.874 | 1.874 | 1.874 | 1.874 | 1.874 | 1.874 | 1.874
| JA017 | 3.028 | 3.134 | 3.24 | 3.346 | 3.432 | 3.528 | 3.624 | 3.73 | 3.829 | 3.829 | 3.829 | 3.829 | 3.829 | 3.829 | 3.829 | 3.829 | 3.829 | 3.829 | 3.829 | 3.829
| JA018 | 4.213 | 4.465 | 4.517 | 4.663 | 4.792 | 4.921 | 5.057 | 5.202 | 5.348 | 5.348 | 5.348 | 5.348 | 5.348 | 5.348 | 5.348 | 5.348 | 5.348 | 5.348 | 5.348 | 5.348
| JA019 | 7.823 | 7.978 | 8.08 | 8.163 | 8.24 | 8.307 | 8.401 | 8.495 | 8.581 | 8.581 | 8.581 | 8.581 | 8.581 | 8.581 | 8.581 | 8.581 | 8.581 | 8.581 | 8.581 | 8.581
| JA021 | 2.375 | 2.458 | 2.551 | 2.634 | 2.707 | 2.777 | 2.86 | 2.953 | 3.026 | 3.026 | 3.026 | 3.026 | 3.026 | 3.026 | 3.026 | 3.026 | 3.026 | 3.026 | 3.026 | 3.026
| JA022 | 2.256 | 2.272 | 2.275 | 2.278 | 2.278 | 2.268 | 2.281 | 2.351 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407
| JA025 | 5.826 | 5.988 | 6.18 | 6.356 | 6.475 | 6.601 | 6.783 | 6.998 | 7.134 | 7.134 | 7.134 | 7.134 | 7.134 | 7.134 | 7.134 | 7.134 | 7.134 | 7.134 | 7.134 | 7.134
| JA026 | 2.027 | 2.113 | 2.196 | 2.275 | 2.348 | 2.417 | 2.493 | 2.576 | 2.652 | 2.652 | 2.652 | 2.652 | 2.652 | 2.652 | 2.652 | 2.652 | 2.652 | 2.652 | 2.652 | 2.652
| JA027 | 5.465 | 5.662 | 5.808 | 5.944 | 6.11 | 6.266 | 6.445 | 6.628 | 6.797 | 6.797 | 6.797 | 6.797 | 6.797 | 6.797 | 6.797 | 6.797 | 6.797 | 6.797 | 6.797 | 6.797
| JA029 | 6.329 | 6.54 | 6.764 | 6.965 | 7.113 | 7.288 | 7.512 | 7.746 | 7.901 | 7.901 | 7.901 | 7.901 | 7.901 | 7.901 | 7.901 | 7.901 | 7.901 | 7.901 | 7.901 | 7.901
| JA033 | 5.216 | 5.411 | 5.61 | 5.798 | 5.967 | 6.136 | 6.321 | 6.52 | 6.695 | 6.695 | 6.695 | 6.695 | 6.695 | 6.695 | 6.695 | 6.695 | 6.695 | 6.695 | 6.695 | 6.695
| JA034 | 2.889 | 2.999 | 3.112 | 3.218 | 3.301 | 3.394 | 3.51 | 3.633 | 3.733 | 3.733 | 3.733 | 3.733 | 3.733 | 3.733 | 3.733 | 3.733 | 3.733 | 3.733 | 3.733 | 3.733
| JA035 | 7.163 | 7.546 | 7.758 | 7.97 | 8.146 | 8.325 | 8.557 | 8.783 | 8.981 | 8.981 | 8.981 | 8.981 | 8.981 | 8.981 | 8.981 | 8.981 | 8.981 | 8.981 | 8.981 | 8.981
| JA037 | 7.451 | 7.634 | 7.766 | 7.878 | 7.972 | 8.057 | 8.186 | 8.328 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439
| JA038 | 5.028 | 5.137 | 5.246 | 5.345 | 5.434 | 5.523 | 5.639 | 5.758 | 5.847 | 5.847 | 5.847 | 5.847 | 5.847 | 5.847 | 5.847 | 5.847 | 5.847 | 5.847 | 5.847 | 5.847
| JA041 | 3.533 | 3.586 | 3.629 | 3.662 | 3.675 | 3.698 | 3.741 | 3.777 | 3.797 | 3.797 | 3.797 | 3.797 | 3.797 | 3.797 | 3.797 | 3.797 | 3.797 | 3.797 | 3.797 | 3.797
| JA042 | 7.761 | 8.055 | 8.356 | 8.636 | 8.897 | 9.141 | 9.44 | 9.746 | 10.003 | 10.003 | 10.003 | 10.003 | 10.003 | 10.003 | 10.003 | 10.003 | 10.003 | 10.003 | 10.003 | 10.003
| JA043 | 5.511 | 5.719 | 5.917 | 6.105 | 6.28 | 6.445 | 6.63 | 6.818 | 7.006 | 7.006 | 7.006 | 7.006 | 7.006 | 7.006 | 7.006 | 7.006 | 7.006 | 7.006 | 7.006 | 7.006
| JA045 | 3.079 | 3.192 | 3.305 | 3.408 | 3.508 | 3.601 | 3.711 | 3.827 | 3.927 | 3.927 | 3.927 | 3.927 | 3.927 | 3.927 | 3.927 | 3.927 | 3.927 | 3.927 | 3.927 | 3.927
| JA046 | 6.951 | 7.197 | 7.446 | 7.675 | 7.881 | 8.097 | 8.333 | 8.585 | 8.814 | 8.814 | 8.814 | 8.814 | 8.814 | 8.814 | 8.814 | 8.814 | 8.814 | 8.814 | 8.814 | 8.814
| K023 | 3.664 | 3.697 | 3.754 | 3.797 | 3.817 | 3.834 | 3.877 | 3.927 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95
| K024 | 4.876 | 4.952 | 5.038 | 5.117 | 5.163 | 5.216 | 5.302 | 5.401 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45
| K026 | 3.071 | 3.067 | 3.083 | 3.109 | 3.119 | 3.139 | 3.168 | 3.215 | 3.235 | 3.235 | 3.235 | 3.235 | 3.235 | 3.235 | 3.235 | 3.235 | 3.235 | 3.235 | 3.235 | 3.235
| K031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| K032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KGT002 | 6.246 | 6.256 | 6.279 | 6.289 | 6.256 | 6.23 | 6.25 | 6.283 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25
| KGT003 | 3.551 | 3.584 | 3.644 | 3.687 | 3.68 | 3.69 | 3.75 | 3.83 | 3.813 | 3.813 | 3.813 | 3.813 | 3.813 | 3.813 | 3.813 | 3.813 | 3.813 | 3.813 | 3.813 | 3.813
| KGT004 | 5.509 | 5.549 | 5.625 | 5.675 | 5.658 | 5.668 | 5.748 | 5.854 | 5.831 | 5.831 | 5.831 | 5.831 | 5.831 | 5.831 | 5.831 | 5.831 | 5.831 | 5.831 | 5.831 | 5.831
| KGT005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KRT012 | 3.039 | 3.072 | 3.135 | 3.185 | 3.188 | 3.211 | 3.271 | 3.354 | 3.361 | 3.361 | 3.361 | 3.361 | 3.361 | 3.361 | 3.361 | 3.361 | 3.361 | 3.361 | 3.361 | 3.361
| KRT013 | 6.225 | 6.262 | 6.341 | 6.404 | 6.421 | 6.444 | 6.544 | 6.664 | 6.691 | 6.691 | 6.691 | 6.691 | 6.691 | 6.691 | 6.691 | 6.691 | 6.691 | 6.691 | 6.691 | 6.691
| KRT022 | 7.504 | 7.597 | 7.724 | 7.794 | 7.85 | 7.924 | 8.051 | 8.192 | 8.242 | 8.242 | 8.242 | 8.242 | 8.242 | 8.242 | 8.242 | 8.242 | 8.242 | 8.242 | 8.242 | 8.242
| KRT023 | 8.401 | 8.389 | 8.432 | 8.472 | 8.465 | 8.474 | 8.534 | 8.617 | 8.647 | 8.647 | 8.647 | 8.647 | 8.647 | 8.647 | 8.647 | 8.647 | 8.647 | 8.647 | 8.647 | 8.647
| KRT031 | 14.287 | 14.291 | 14.324 | 14.353 | 14.356 | 14.346 | 14.369 | 14.415 | 14.454 | 14.454 | 14.454 | 14.454 | 14.454 | 14.454 | 14.454 | 14.454 | 14.454 | 14.454 | 14.454 | 14.454
| KYM001 | 6.861 | 6.911 | 7.01 | 7.116 | 7.133 | 7.146 | 7.235 | 7.384 | 7.423 | 7.423 | 7.423 | 7.423 | 7.423 | 7.423 | 7.423 | 7.423 | 7.423 | 7.423 | 7.423 | 7.423
| KYM002 | 4.893 | 4.854 | 4.847 | 4.803 | 4.757 | 4.724 | 4.714 | 4.695 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672 | 4.672
| KYM003 | 4.898 | 4.925 | 4.998 | 5.058 | 5.052 | 5.065 | 5.155 | 5.264 | 5.234 | 5.234 | 5.234 | 5.234 | 5.234 | 5.234 | 5.234 | 5.234 | 5.234 | 5.234 | 5.234 | 5.234
| KYM004 | 5.207 | 5.25 | 5.343 | 5.406 | 5.4 | 5.42 | 5.523 | 5.643 | 5.626 | 5.626 | 5.626 | 5.626 | 5.626 | 5.626 | 5.626 | 5.626 | 5.626 | 5.626 | 5.626 | 5.626
| KYM005 | 5.163 | 5.166 | 5.186 | 5.196 | 5.166 | 5.16 | 5.184 | 5.197 | 5.204 | 5.204 | 5.204 | 5.204 | 5.204 | 5.204 | 5.204 | 5.204 | 5.204 | 5.204 | 5.204 | 5.204
| KYM006 | 5.391 | 5.381 | 5.385 | 5.385 | 5.362 | 5.342 | 5.362 | 5.398 | 5.375 | 5.375 | 5.375 | 5.375 | 5.375 | 5.375 | 5.375 | 5.375 | 5.375 | 5.375 | 5.375 | 5.375
| L001 | 3.984 | 4.034 | 4.104 | 4.167 | 4.197 | 4.247 | 4.317 | 4.41 | 4.456 | 4.456 | 4.456 | 4.456 | 4.456 | 4.456 | 4.456 | 4.456 | 4.456 | 4.456 | 4.456 | 4.456
| L002 | 4.641 | 4.661 | 4.71 | 4.727 | 4.734 | 4.743 | 4.773 | 4.826 | 4.82 | 4.82 | 4.82 | 4.82 | 4.82 | 4.82 | 4.82 | 4.82 | 4.82 | 4.82 | 4.82 | 4.82
| L004 | 2.014 | 2.037 | 2.067 | 2.097 | 2.11 | 2.13 | 2.16 | 2.193 | 2.216 | 2.216 | 2.216 | 2.216 | 2.216 | 2.216 | 2.216 | 2.216 | 2.216 | 2.216 | 2.216 | 2.216
| L005 | 4.193 | 4.209 | 4.248 | 4.271 | 4.281 | 4.304 | 4.334 | 4.397 | 4.397 | 4.397 | 4.397 | 4.397 | 4.397 | 4.397 | 4.397 | 4.397 | 4.397 | 4.397 | 4.397 | 4.397
| L006 | 2.299 | 2.246 | 2.216 | 2.189 | 2.163 | 2.15 | 2.137 | 2.134 | 2.121 | 2.121 | 2.121 | 2.121 | 2.121 | 2.121 | 2.121 | 2.121 | 2.121 | 2.121 | 2.121 | 2.121
| L009 | 2.801 | 2.844 | 2.901 | 2.944 | 2.974 | 3.014 | 3.064 | 3.137 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17 | 3.17
| L010 | 4.149 | 4.189 | 4.266 | 4.326 | 4.356 | 4.399 | 4.465 | 4.549 | 4.593 | 4.593 | 4.593 | 4.593 | 4.593 | 4.593 | 4.593 | 4.593 | 4.593 | 4.593 | 4.593 | 4.593
| L013 | 2.031 | 2.022 | 2.005 | 2.002 | 1.992 | 1.989 | 1.992 | 2.015 | 2.022 | 2.022 | 2.022 | 2.022 | 2.022 | 2.022 | 2.022 | 2.022 | 2.022 | 2.022 | 2.022 | 2.022
| L014 | 3.73 | 3.737 | 3.757 | 3.773 | 3.78 | 3.78 | 3.81 | 3.857 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86 | 3.86
| L015 | 2.397 | 2.397 | 2.417 | 2.427 | 2.434 | 2.437 | 2.454 | 2.501 | 2.511 | 2.511 | 2.511 | 2.511 | 2.511 | 2.511 | 2.511 | 2.511 | 2.511 | 2.511 | 2.511 | 2.511
| L018 | 2.719 | 2.759 | 2.822 | 2.862 | 2.895 | 2.935 | 2.988 | 3.055 | 3.091 | 3.091 | 3.091 | 3.091 | 3.091 | 3.091 | 3.091 | 3.091 | 3.091 | 3.091 | 3.091 | 3.091
| L019 | 4.239 | 4.272 | 4.356 | 4.412 | 4.445 | 4.488 | 4.554 | 4.637 | 4.686 | 4.686 | 4.686 | 4.686 | 4.686 | 4.686 | 4.686 | 4.686 | 4.686 | 4.686 | 4.686 | 4.686
| L020 | 2.523 | 2.543 | 2.559 | 2.572 | 2.582 | 2.585 | 2.605 | 2.628 | 2.628 | 2.628 | 2.628 | 2.628 | 2.628 | 2.628 | 2.628 | 2.628 | 2.628 | 2.628 | 2.628 | 2.628
| L022 | 4.272 | 4.311 | 4.374 | 4.414 | 4.424 | 4.454 | 4.507 | 4.594 | 4.615 | 4.615 | 4.615 | 4.615 | 4.615 | 4.615 | 4.615 | 4.615 | 4.615 | 4.615 | 4.615 | 4.615
| L023 | 0.145 | 0.145 | 0.145 | 0.152 | 0.152 | 0.152 | 0.152 | 0.152 | 0.152 | 0.152 | 0.152 | 0.152 | 0.152 | 0.152 | 0.152 | 0.152 | 0.152 | 0.152 | 0.152 | 0.152
| LFSF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LQ001 | 3.459 | 3.578 | 3.704 | 3.82 | 3.926 | 4.032 | 4.151 | 4.267 | 4.386 | 4.386 | 4.386 | 4.386 | 4.386 | 4.386 | 4.386 | 4.386 | 4.386 | 4.386 | 4.386 | 4.386
| LQ002 | 1.656 | 1.712 | 1.761 | 1.807 | 1.853 | 1.899 | 1.955 | 2.011 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06
| LQ003 | 2.735 | 2.835 | 2.928 | 3.021 | 3.094 | 3.174 | 3.267 | 3.37 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45
| LQ004 | 3.46 | 3.509 | 3.558 | 3.604 | 3.643 | 3.682 | 3.728 | 3.79 | 3.876 | 3.876 | 3.876 | 3.876 | 3.876 | 3.876 | 3.876 | 3.876 | 3.876 | 3.876 | 3.876 | 3.876
| LQ007 | 0.439 | 0.449 | 0.462 | 0.472 | 0.475 | 0.482 | 0.502 | 0.518 | 0.518 | 0.518 | 0.518 | 0.518 | 0.518 | 0.518 | 0.518 | 0.518 | 0.518 | 0.518 | 0.518 | 0.518
| LQ008 | 0.279 | 0.282 | 0.292 | 0.299 | 0.309 | 0.312 | 0.322 | 0.332 | 0.339 | 0.339 | 0.339 | 0.339 | 0.339 | 0.339 | 0.339 | 0.339 | 0.339 | 0.339 | 0.339 | 0.339
| LQ009 | 1.84 | 1.893 | 1.966 | 2.019 | 2.052 | 2.095 | 2.161 | 2.234 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267 | 2.267
| LQ010 | 1.064 | 1.104 | 1.137 | 1.17 | 1.2 | 1.23 | 1.263 | 1.306 | 1.336 | 1.336 | 1.336 | 1.336 | 1.336 | 1.336 | 1.336 | 1.336 | 1.336 | 1.336 | 1.336 | 1.336
| LQ011 | 3.174 | 3.294 | 3.41 | 3.516 | 3.619 | 3.722 | 3.832 | 3.948 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061 | 4.061
| LQ012 | 3.761 | 3.897 | 4.03 | 4.156 | 4.269 | 4.378 | 4.511 | 4.644 | 4.76 | 4.76 | 4.76 | 4.76 | 4.76 | 4.76 | 4.76 | 4.76 | 4.76 | 4.76 | 4.76 | 4.76
| LQ014 | 3.076 | 3.152 | 3.238 | 3.314 | 3.387 | 3.453 | 3.539 | 3.622 | 3.701 | 3.701 | 3.701 | 3.701 | 3.701 | 3.701 | 3.701 | 3.701 | 3.701 | 3.701 | 3.701 | 3.701
| LQ015 | 2.015 | 2.098 | 2.174 | 2.257 | 2.32 | 2.393 | 2.469 | 2.552 | 2.625 | 2.625 | 2.625 | 2.625 | 2.625 | 2.625 | 2.625 | 2.625 | 2.625 | 2.625 | 2.625 | 2.625
| LQ016 | 2.304 | 2.384 | 2.467 | 2.54 | 2.603 | 2.666 | 2.746 | 2.832 | 2.895 | 2.895 | 2.895 | 2.895 | 2.895 | 2.895 | 2.895 | 2.895 | 2.895 | 2.895 | 2.895 | 2.895
| LQ017 | 2.993 | 3.092 | 3.215 | 3.311 | 3.394 | 3.48 | 3.596 | 3.719 | 3.802 | 3.802 | 3.802 | 3.802 | 3.802 | 3.802 | 3.802 | 3.802 | 3.802 | 3.802 | 3.802 | 3.802
| LQ021 | 2.512 | 2.598 | 2.691 | 2.781 | 2.864 | 2.947 | 3.033 | 3.126 | 3.219 | 3.219 | 3.219 | 3.219 | 3.219 | 3.219 | 3.219 | 3.219 | 3.219 | 3.219 | 3.219 | 3.219
| LQ022 | 2.745 | 2.841 | 2.934 | 3.027 | 3.11 | 3.193 | 3.279 | 3.379 | 3.465 | 3.465 | 3.465 | 3.465 | 3.465 | 3.465 | 3.465 | 3.465 | 3.465 | 3.465 | 3.465 | 3.465
| LQ023 | 2.518 | 2.614 | 2.71 | 2.806 | 2.899 | 2.995 | 3.088 | 3.187 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29

## Calcs
Powercor
Risk-based replacement of deteriorated and aged 66kV radial lines
| Total where option 2 is preferred |  |  |  |  | 147626.95 |  | 14339005.6535 | [42 empty] | 58299848.787 |  | 14339005.6535 | 7750912.3412 |  |  |  | 57436009.7484 | 49685097.4071 | 46
[9 empty] | Option 1 | [19 empty] | Option 1 | [19 empty] | Option 1 | Option 1 | Option 1 | Option 2 | Option 2 | Option 2 | Option 2 | Option 2 | Option 2 | Option 2 | Option 2 | Option 2
| SAP ID | Radial ZSS | Construction | Section start pole | Section end pole | Section length | VCR | Replacement | Probability of aged conductor failure | [19 empty] | Weighted energy at risk (MWh) | [19 empty] | PV of energy at | PV of unplanned | Total risk | Probability of new | Total replacement | Annualised capex | Energy at risk | Unplanned replacement | Total risk | Total benefits | NPV | preferred
|  |  | year | equipment ID | equipment ID | (m) | ($ 2023) | cost $/m ($ 2023) | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | risk ($ 2023) | replacement ($ 2023) | PV ($2023) | conductor failure | cost ($2023) | PV ($2023) | PV ($2023) | PV ($2023) | PV ($2023) | PV ($2023) | NPV ($2023)
| 60555946 | CTN | 2014 | 30296199 | 30296202 | 116.5 | 45198.6405 | 11315.645 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1550.1273 | 21.5969 | 1571.7241 | 3.2802e-05 | 11315.645 | 6116.6426 | 423.7315 | 5.9036 | 429.635 | 1142.0891 | -4974.5535 | 0
| 60555953 | RVL | 1999 | 33064146 | 33064126 | 1466.27 | 49456.6662 | 142418.8051 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 0.00157 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 30884.3765 | 3556.2917 | 34440.6682 | 0.00041285 | 142418.8051 | 76984.116 | 8121.4169 | 935.1695 | 9056.5864 | 25384.0818 | -51600.0342 | 0
| 60555962 | CTN | 1955 | 30021365 | 30021422 | 3284.68 | 45198.6405 | 319040.9684 | 0.03074 | 0.03314 | 0.03574 | 0.03855 | 0.04159 | 0.04489 | 0.04845 | 0.05231 | 0.05648 | 0.06101 | 0.0659 | 0.0712 | 0.07695 | 0.08317 | 0.08991 | 0.09721 | 0.10512 | 0.10765 | 0.10765 | 0.10765 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 809891.7006 | 317650.2442 | 1127541.9448 | 0.00092485 | 319040.9684 | 172456.7686 | 11946.972 | 4692.9786 | 16639.9505 | 1110901.9942 | 938445.2257 | 1
| 60555980 | RVL | 1998 | 33064595 | 33064586 | 216.42 | 49456.6662 | 21020.8746 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 4524.4628 | 76.8969 | 4601.3597 | 6.0936e-05 | 21020.8746 | 11362.7793 | 1198.7131 | 20.3731 | 1219.0862 | 3382.2735 | -7980.5057 | 0
| 60555985 | CTN | 2011 | 30296926 | 31037382 | 49.27 | 45198.6405 | 4785.5951 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 645.8864 | 3.8057 | 649.6921 | 1.3873e-05 | 4785.5951 | 2586.841 | 179.2039 | 1.0559 | 180.2598 | 469.4323 | -2117.4087 | 0
| 60556023 | RVL | 1998 | 33063738 | 33063736 | 130.66 | 49456.6662 | 12691.0058 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 2754.0208 | 28.2588 | 2782.2797 | 3.6789e-05 | 12691.0058 | 6860.0903 | 723.7032 | 7.4259 | 731.1291 | 2051.1506 | -4808.9397 | 0
| 60556219 | CME | 1999 | 33086441 | 33086369 | 1569.19 | 46875.2879 | 152415.4247 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 0.00168 | 38.435 | 38.637 | 39.003 | 39.298 | 39.32 | 39.352 | 39.702 | 40.078 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 45242.6784 | 4072.5703 | 49315.2487 | 0.00044183 | 152415.4247 | 82387.7628 | 11898.5277 | 1071.0593 | 12969.587 | 36345.6617 | -46042.1011 | 0
| 60556221 | CTN | 2014 | 30323205 | 30323207 | 15.1 | 45198.6405 | 1466.663 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 258.3545 | 0.46654 | 258.8211 | 4.2516e-06 | 1466.663 | 792.8009 | 54.9214 | 0.099178 | 55.0206 | 203.8005 | -589.0004 | 0
| 60652205 | RVL | 2017 | 30352478 | 30352855 | 811.8 | 49456.6662 | 78850.134 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 0.00087 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 17114.2723 | 1091.0686 | 18205.341 | 0.00022857 | 78850.134 | 42622.2356 | 4496.4203 | 286.6557 | 4783.076 | 13422.265 | -29199.9706 | 0
| 60652302 | RVL | 1973 | 33066420 | 30550524 | 238.75 | 49456.6662 | 23189.7875 | 0.00027 | 0.00029 | 0.00031 | 0.00033 | 0.00036 | 0.00038 | 0.00042 | 0.00045 | 0.00048 | 0.00052 | 0.00056 | 0.00061 | 0.00066 | 0.00072 | 0.00077 | 0.00084 | 0.00091 | 0.00099 | 0.00107 | 0.00116 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 11069.9748 | 204.532 | 11274.5068 | 6.7224e-05 | 23189.7875 | 12535.1795 | 1322.3951 | 24.7941 | 1347.1893 | 9927.3176 | -2607.862 | 0
| 60652318 | RVL | 2017 | 30352855 | 30352856 | 84.2 | 49456.6662 | 8178.346 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 1770.442 | 11.7068 | 1782.1488 | 2.3708e-05 | 8178.346 | 4420.7837 | 466.3693 | 3.0838 | 469.4531 | 1312.6957 | -3108.0881 | 0
| 60652444 | RVL | 2017 | 30352856 | 30352855 | 84.2 | 49456.6662 | 8178.346 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 1770.442 | 11.7068 | 1782.1488 | 2.3708e-05 | 8178.346 | 4420.7837 | 466.3693 | 3.0838 | 469.4531 | 1312.6957 | -3108.0881 | 0
| 60652627 | CHA | 2008 | 30256272 | 32038033 | 8.67 | 48008.7507 | 842.1171 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 146.7484 | 0.13394 | 146.8823 | 2.4412e-06 | 842.1171 | 455.2042 | 35.8238 | 0.032696 | 35.8564 | 111.0259 | -344.1783 | 0
| 60652630 | NKA | 1999 | 34022751 | 30246717 | 69.41 | 52400.9885 | 6741.7933 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 30.403 | 31.68 | 32.179 | 32.53 | 32.52 | 32.59 | 33.072 | 33.695 | 33.63 | 33.63 | 33.63 | 33.63 | 33.63 | 33.63 | 33.63 | 33.63 | 33.63 | 33.63 | 33.63 | 33.63 | 1748.6328 | 7.5059 | 1756.1387 | 1.9543e-05 | 6741.7933 | 3644.2589 | 488.204 | 2.0956 | 490.2995 | 1265.8392 | -2378.4197 | 0
| 60652643 | RVL | 1973 | 30550524 | 30550526 | 796.16 | 49456.6662 | 77331.0208 | 0.00089 | 0.00096 | 0.00103 | 0.00111 | 0.00119 | 0.00128 | 0.00138 | 0.00149 | 0.00161 | 0.00174 | 0.00188 | 0.00204 | 0.0022 | 0.00239 | 0.00258 | 0.0028 | 0.00303 | 0.00329 | 0.00357 | 0.00388 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 36899.6253 | 2273.2957 | 39172.921 | 0.00022417 | 77331.0208 | 41801.0829 | 4409.793 | 275.7167 | 4685.5098 | 34487.4112 | -7313.6717 | 0
| 60652659 | RVL | 1973 | 30550526 | 33066534 | 3167.76 | 49456.6662 | 307684.5288 | 0.00354 | 0.0038 | 0.00409 | 0.0044 | 0.00474 | 0.00511 | 0.00551 | 0.00594 | 0.00642 | 0.00693 | 0.00749 | 0.0081 | 0.00877 | 0.00949 | 0.01028 | 0.01114 | 0.01208 | 0.0131 | 0.01421 | 0.01543 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 146871.8812 | 36000.9131 | 182872.7943 | 0.00089193 | 307684.5288 | 166318.0746 | 17545.6768 | 4364.8265 | 21910.5032 | 160962.291 | -5355.7835 | 0
| 60652797 | CTN | 1955 | 30021422 | 30229285 | 17174.04 | 45198.6405 | 1668114.5052 | 0.16072 | 0.17328 | 0.18687 | 0.20157 | 0.21747 | 0.23469 | 0.25332 | 0.27349 | 0.29533 | 0.31897 | 0.34457 | 0.37229 | 0.40232 | 0.43485 | 0.47009 | 0.50827 | 0.54964 | 0.56288 | 0.56288 | 0.56288 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 4234593.695 | 8683871.5408 | 12918465.2358 | 0.0048356 | 1668114.5052 | 901694.9723 | 62465.0725 | 128294.3056 | 190759.3781 | 12727705.8577 | 11826010.8854 | 1
| 60652986 | CME | 1999 | 33085553 | 30246716 | 49.92 | 46875.2879 | 4848.7296 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 5e-05 | 38.435 | 38.637 | 39.003 | 39.298 | 39.32 | 39.352 | 39.702 | 40.078 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 1346.5083 | 3.8559 | 1350.3642 | 1.4056e-05 | 4848.7296 | 2620.9682 | 378.523 | 1.084 | 379.607 | 970.7573 | -1650.211 | 0
| 60669975 | CHA | 2008 | 32038033 | 32038042 | 30.27 | 48008.7507 | 2940.1251 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 440.2451 | 1.4029 | 441.648 | 8.523e-06 | 2940.1251 | 1589.277 | 125.0732 | 0.39855 | 125.4718 | 316.1762 | -1273.1008 | 0
| 60669993 | CTN | 2013 | 30320082 | 30296173 | 936.53 | 45198.6405 | 90965.1589 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 12917.7272 | 1446.7899 | 14364.5171 | 0.00026369 | 90965.1589 | 49170.9809 | 3406.3281 | 381.5099 | 3787.838 | 10576.6791 | -38594.3017 | 0
| 60670043 | WMN | 2018 | 30547413 | 30547415 | 84.15 | 61329.3035 | 8173.4895 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 2123.3554 | 11.6999 | 2135.0552 | 2.3694e-05 | 8173.4895 | 4418.1586 | 559.0015 | 3.0801 | 562.0816 | 1572.9736 | -2845.185 | 0
| 60670055 | WMN | 1998 | 30355658 | 30547413 | 22.19 | 61329.3035 | 2155.3147 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 3e-05 | 3e-05 | 4e-05 | 4e-05 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 525.2078 | 0.76136 | 525.9692 | 6.2479e-06 | 2155.3147 | 1165.0498 | 147.4063 | 0.21418 | 147.6205 | 378.3487 | -786.7011 | 0
| 60670067 | WMN | 2018 | 30547415 | 30547416 | 81.38 | 61329.3035 | 7904.4394 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 2123.3554 | 11.3147 | 2134.6701 | 2.2914e-05 | 7904.4394 | 4272.7242 | 540.6006 | 2.8807 | 543.4813 | 1591.1888 | -2681.5354 | 0
| 60670073 | CHA | 2008 | 32038033 | 30237361 | 67.14 | 48008.7507 | 6521.3082 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 1027.2387 | 7.2604 | 1034.4991 | 1.8904e-05 | 6521.3082 | 3525.0762 | 277.4172 | 1.9608 | 279.3779 | 755.1212 | -2769.9551 | 0
| 60555940 | CHM | 2005 | 33052089 | 33052660 | 112.25 | 43924.3002 | 10902.8425 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 159.6945 | 20.809 | 180.5035 | 3.1606e-05 | 10902.8425 | 5893.5033 | 42.0604 | 5.4807 | 47.5411 | 132.9624 | -5760.5408 | 0
| 60554187 | RVL | 1973 | 33063663 | 33063669 | 149.57 | 49456.6662 | 14527.7341 | 0.00017 | 0.00018 | 0.00019 | 0.00021 | 0.00022 | 0.00024 | 0.00026 | 0.00028 | 0.0003 | 0.00033 | 0.00035 | 0.00038 | 0.00041 | 0.00045 | 0.00049 | 0.00053 | 0.00057 | 0.00062 | 0.00067 | 0.00073 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 6931.2303 | 80.2231 | 7011.4534 | 4.2114e-05 | 14527.7341 | 7852.929 | 828.4425 | 9.7309 | 838.1733 | 6173.2801 | -1679.649 | 0
| 60554191 | RVL | 2017 | 30352471 | 30352473 | 75.43 | 49456.6662 | 7326.5159 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 1573.7262 | 9.3222 | 1583.0484 | 2.1238e-05 | 7326.5159 | 3960.3292 | 417.7938 | 2.4749 | 420.2686 | 1162.7797 | -2797.5494 | 0
| 60554210 | CTN | 2010 | 30147037 | 30147036 | 20.43 | 45198.6405 | 1984.3659 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 258.3545 | 0.63122 | 258.9858 | 5.7524e-06 | 1984.3659 | 1072.6438 | 74.3076 | 0.18155 | 74.4891 | 184.4966 | -888.1472 | 0
| 60554215 | RVL | 1998 | 33064076 | 33064074 | 38.93 | 49456.6662 | 3781.2709 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 786.8631 | 2.4056 | 789.2687 | 1.0961e-05 | 3781.2709 | 2043.9562 | 215.6266 | 0.65922 | 216.2858 | 572.9829 | -1470.9732 | 0
| 60554221 | CTN | 2014 | 30296202 | 30296216 | 1429.57 | 45198.6405 | 138854.1341 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 0.00153 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19764.1226 | 3378.9412 | 23143.0638 | 0.00040252 | 138854.1341 | 75057.2423 | 5199.6032 | 888.9417 | 6088.5449 | 17054.5189 | -58002.7234 | 0
| 60554226 | RVL | 1999 | 33064099 | 33064096 | 136.9 | 49456.6662 | 13297.097 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 2950.7366 | 31.7233 | 2982.4599 | 3.8546e-05 | 13297.097 | 7187.7113 | 758.2655 | 8.1521 | 766.4176 | 2216.0423 | -4971.669 | 0
| 60554247 | CTN | 2014 | 31037408 | 31037417 | 1062.33 | 45198.6405 | 103184.1129 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 0.00114 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 14726.209 | 1870.8892 | 16597.0982 | 0.00029911 | 103184.1129 | 55775.9048 | 3863.8853 | 490.8868 | 4354.7721 | 12242.3262 | -43533.5786 | 0
| 60554256 | CTN | 2014 | 30347933 | 30296910 | 910.32 | 45198.6405 | 88419.3816 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 0.00097 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 12530.1954 | 1364.1106 | 13894.306 | 0.00025631 | 88419.3816 | 47794.8676 | 3310.9976 | 360.4546 | 3671.4522 | 10222.8538 | -37572.0137 | 0
| 60554278 | RVL | 1998 | 33064091 | 33064093 | 104.01 | 49456.6662 | 10102.4913 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 0.00011 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 2163.8735 | 17.6747 | 2181.5482 | 2.9286e-05 | 10102.4913 | 5460.8755 | 576.0935 | 4.7056 | 580.799 | 1600.7491 | -3860.1263 | 0
| 60554279 | CTN | 1955 | 30020713 | 30334479 | 2315.34 | 45198.6405 | 224888.9742 | 0.02167 | 0.02336 | 0.02519 | 0.02717 | 0.02932 | 0.03164 | 0.03415 | 0.03687 | 0.03981 | 0.043 | 0.04645 | 0.05019 | 0.05424 | 0.05863 | 0.06338 | 0.06852 | 0.0741 | 0.07588 | 0.07588 | 0.07588 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 570874.5541 | 157828.2206 | 728702.7748 | 0.00065192 | 224888.9742 | 121563.1521 | 8421.308 | 2331.8037 | 10753.1117 | 717949.663 | 596386.5109 | 1
| 60554285 | CTN | 2011 | 31037381 | 30296926 | 52.98 | 45198.6405 | 5145.9474 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 775.0636 | 4.9107 | 779.9744 | 1.4917e-05 | 5145.9474 | 2781.6285 | 192.6978 | 1.2209 | 193.9187 | 586.0557 | -2195.5729 | 0
| 60554344 | RVL | 2017 | 30352466 | 30352465 | 52.59 | 49456.6662 | 5108.0667 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 1180.2946 | 4.8746 | 1185.1692 | 1.4808e-05 | 5108.0667 | 2761.1522 | 291.2869 | 1.203 | 292.49 | 892.6793 | -1868.4729 | 0
| 60554356 | CME | 1999 | 33086444 | 33086441 | 35.29 | 46875.2879 | 3427.7177 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 38.435 | 38.637 | 39.003 | 39.298 | 39.32 | 39.352 | 39.702 | 40.078 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 1077.2066 | 2.1807 | 1079.3873 | 9.9364e-06 | 3427.7177 | 1852.8439 | 267.5897 | 0.54171 | 268.1314 | 811.2559 | -1041.588 | 0
| 60554362 | CHM | 1998 | 30083003 | 30083009 | 602.69 | 43924.3002 | 58539.2797 | 0.00065 | 0.00065 | 0.00065 | 0.00065 | 0.00065 | 0.00065 | 0.00065 | 0.00065 | 0.00065 | 0.00065 | 0.00065 | 0.00065 | 0.00065 | 0.00065 | 0.00065 | 0.00068 | 0.00076 | 0.00085 | 0.00095 | 0.00107 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 916.4484 | 641.4419 | 1557.8903 | 0.0001697 | 58539.2797 | 31643.2559 | 225.8299 | 157.9976 | 383.8275 | 1174.0628 | -30469.1931 | 0
| 60554459 | RVL | 1998 | 33064074 | 33064048 | 818.74 | 49456.6662 | 79524.2162 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 0.00088 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 17310.9881 | 1113.0443 | 18424.0324 | 0.00023053 | 79524.2162 | 42986.609 | 4534.8598 | 291.5778 | 4826.4376 | 13597.5948 | -29389.0141 | 0
| 60554471 | CTN | 2014 | 31037382 | 31037393 | 1312.18 | 45198.6405 | 127452.0434 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 18084.8181 | 2837.9531 | 20922.7713 | 0.00036946 | 127452.0434 | 68893.8717 | 4772.6347 | 748.9439 | 5521.5785 | 15401.1927 | -53492.679 | 0
| 60554472 | RVL | 1999 | 33064399 | 33064397 | 371.22 | 49456.6662 | 36056.5986 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 7868.631 | 229.3903 | 8098.0213 | 0.00010452 | 36056.5986 | 19490.3009 | 2056.1236 | 59.9412 | 2116.0648 | 5981.9565 | -13508.3444 | 0
| 60554484 | CHA | 1959 | 32038282 | 30350615 | 88.85 | 48008.7507 | 8630.0005 | 0.00084 | 0.00091 | 0.00099 | 0.00107 | 0.00116 | 0.00126 | 0.00136 | 0.00148 | 0.0016 | 0.00174 | 0.00189 | 0.00205 | 0.00223 | 0.00242 | 0.00263 | 0.00286 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 25950.4618 | 241.8678 | 26192.3296 | 2.5017e-05 | 8630.0005 | 4664.9244 | 367.1212 | 3.4338 | 370.555 | 25821.7746 | 21156.8502 | 1
| 60554498 | CHM | 1998 | 32108497 | 30082976 | 1744.48 | 43924.3002 | 169441.3424 | 0.00187 | 0.00187 | 0.00187 | 0.00187 | 0.00187 | 0.00187 | 0.00187 | 0.00187 | 0.00187 | 0.00187 | 0.00187 | 0.00187 | 0.00187 | 0.00187 | 0.00187 | 0.00196 | 0.0022 | 0.00246 | 0.00276 | 0.0031 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2640.4969 | 5349.4797 | 7989.9765 | 0.00049118 | 169441.3424 | 91591.0785 | 653.6624 | 1323.7148 | 1977.3772 | 6012.5994 | -85578.4791 | 0
| 60554500 | CTN | 2014 | 31037417 | 31037418 | 54.64 | 45198.6405 | 5307.1832 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 775.0636 | 5.0646 | 780.1282 | 1.5385e-05 | 5307.1832 | 2868.7841 | 198.7355 | 1.2986 | 200.0341 | 580.0941 | -2288.69 | 0
| 60554517 | CME | 1999 | 33086152 | 33086121 | 136.08 | 46875.2879 | 13217.4504 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 38.435 | 38.637 | 39.003 | 39.298 | 39.32 | 39.352 | 39.702 | 40.078 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 4039.5249 | 31.5333 | 4071.0582 | 3.8315e-05 | 13217.4504 | 7144.6586 | 1031.8391 | 8.0547 | 1039.8939 | 3031.1643 | -4113.4943 | 0
| 60554539 | CTN | 2010 | 30282341 | 33107261 | 94.03 | 45198.6405 | 9133.1339 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1291.7727 | 14.5261 | 1306.2989 | 2.6476e-05 | 9133.1339 | 4936.8919 | 342.004 | 3.8459 | 345.8499 | 960.449 | -3976.4429 | 0
| 60554558 | CTN | 1955 | 30229285 | 30020713 | 6788.1 | 45198.6405 | 659328.153 | 0.06352 | 0.06849 | 0.07386 | 0.07967 | 0.08596 | 0.09276 | 0.10013 | 0.1081 | 0.11673 | 0.12607 | 0.13619 | 0.14715 | 0.15902 | 0.17188 | 0.18581 | 0.2009 | 0.21725 | 0.22248 | 0.22248 | 0.22248 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1673744.2553 | 1356645.8362 | 3030390.0916 | 0.0019113 | 659328.153 | 356398.1242 | 24689.5406 | 20042.8236 | 44732.3642 | 2985657.7274 | 2629259.6031 | 1
| 60554568 | RVL | 1998 | 33064584 | 33064572 | 507.22 | 49456.6662 | 49266.2786 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 0.00054 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 10622.6518 | 423.1301 | 11045.7819 | 0.00014282 | 49266.2786 | 26630.7592 | 2809.4042 | 111.9065 | 2921.3106 | 8124.4712 | -18506.288 | 0
| 60554582 | CHM | 2005 | 30229782 | 30229942 | 416.94 | 43924.3002 | 40497.3822 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 0.00045 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 598.8545 | 289.8477 | 888.7022 | 0.0001174 | 40497.3822 | 21890.755 | 156.2288 | 75.6153 | 231.8441 | 656.8581 | -21233.8968 | 0
| 60554597 | CTN | 1998 | 30147036 | 30147037 | 20.43 | 45198.6405 | 1984.3659 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 258.3545 | 0.63122 | 258.9858 | 5.7524e-06 | 1984.3659 | 1072.6438 | 74.3076 | 0.18155 | 74.4891 | 184.4966 | -888.1472 | 0
| 60554599 | RVL | 1999 | 33064477 | 33064452 | 1619.71 | 49456.6662 | 157322.4323 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 0.00173 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 34031.8289 | 4328.7962 | 38360.625 | 0.00045605 | 157322.4323 | 85040.233 | 8971.2946 | 1141.1348 | 10112.4294 | 28248.1956 | -56792.0374 | 0
| 60554623 | CHM | 1998 | 30086339 | 32118494 | 181.67 | 43924.3002 | 17645.6071 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.0002 | 0.00023 | 0.00026 | 0.00029 | 0.00032 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 269.8674 | 56.9392 | 326.8066 | 5.1152e-05 | 17645.6071 | 9538.2872 | 68.0723 | 14.3558 | 82.4282 | 244.3784 | -9293.9087 | 0
| 60554633 | OYN | 1998 | 33065210 | 33065532 | 16589.51 | 42821.2873 | 1611339.1063 | 0.01776 | 0.01776 | 0.01776 | 0.01776 | 0.01776 | 0.01776 | 0.01776 | 0.01776 | 0.01776 | 0.01776 | 0.01776 | 0.01776 | 0.01776 | 0.01776 | 0.01776 | 0.01868 | 0.0209 | 0.02341 | 0.02626 | 0.02951 | 6.588 | 6.564 | 6.571 | 6.554 | 6.491 | 6.444 | 6.444 | 6.454 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 75327.7134 | 483373.6034 | 558701.3167 | 0.004671 | 1611339.1063 | 871005.1775 | 18665.3904 | 119709.7593 | 138375.1497 | 420326.167 | -450679.0105 | 0
| 60554635 | CHM | 1998 | 32108610 | 30083003 | 525.66 | 43924.3002 | 51057.3558 | 0.00056 | 0.00056 | 0.00056 | 0.00056 | 0.00056 | 0.00056 | 0.00056 | 0.00056 | 0.00056 | 0.00056 | 0.00056 | 0.00056 | 0.00056 | 0.00056 | 0.00056 | 0.00059 | 0.00066 | 0.00074 | 0.00083 | 0.00094 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 791.8399 | 483.3997 | 1275.2396 | 0.00014801 | 51057.3558 | 27598.9213 | 196.9665 | 120.1911 | 317.1576 | 958.082 | -26640.8394 | 0
| 60554184 | RVL | 1998 | 33064753 | 33064771 | 80.93 | 49456.6662 | 7860.7309 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 1770.442 | 11.2522 | 1781.6941 | 2.2787e-05 | 7860.7309 | 4249.0977 | 448.2573 | 2.8489 | 451.1063 | 1330.5879 | -2918.5098 | 0
| 60548967 | OYN | 1998 | 30254690 | 30254687 | 14.32 | 42821.2873 | 1390.9016 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 3e-05 | 6.588 | 6.564 | 6.571 | 6.554 | 6.491 | 6.444 | 6.444 | 6.454 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 81.3198 | 0.45027 | 81.77 | 4.032e-06 | 1390.9016 | 751.8483 | 16.1119 | 0.089197 | 16.2011 | 65.569 | -686.2793 | 0
| 60548982 | RVL | 1999 | 33064420 | 33064404 | 692.37 | 49456.6662 | 67249.8981 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 0.00074 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 14556.9673 | 791.5051 | 15348.4724 | 0.00019495 | 67249.8981 | 36351.7581 | 3834.9181 | 208.5158 | 4043.4339 | 11305.0385 | -25046.7196 | 0
| 60553885 | RVL | 1998 | 33063773 | 33063770 | 35.56 | 49456.6662 | 3453.9428 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 786.8631 | 2.1974 | 789.0605 | 1.0012e-05 | 3453.9428 | 1867.0198 | 196.9607 | 0.55003 | 197.5107 | 591.5497 | -1275.4701 | 0
| 60553888 | RVL | 1973 | 30352465 | 30352466 | 52.59 | 49456.6662 | 5108.0667 | 6e-05 | 6e-05 | 7e-05 | 7e-05 | 8e-05 | 8e-05 | 9e-05 | 0.0001 | 0.00011 | 0.00012 | 0.00012 | 0.00013 | 0.00015 | 0.00016 | 0.00017 | 0.00018 | 0.0002 | 0.00022 | 0.00024 | 0.00026 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 2439.8797 | 9.9274 | 2449.807 | 1.4808e-05 | 5108.0667 | 2761.1522 | 291.2869 | 1.203 | 292.49 | 2157.3171 | -603.8351 | 0
| 60553897 | OYN | 1998 | 33065097 | 33065209 | 6703.72 | 42821.2873 | 651132.3236 | 0.00718 | 0.00718 | 0.00718 | 0.00718 | 0.00718 | 0.00718 | 0.00718 | 0.00718 | 0.00718 | 0.00718 | 0.00718 | 0.00718 | 0.00718 | 0.00718 | 0.00718 | 0.00755 | 0.00844 | 0.00946 | 0.01061 | 0.01193 | 6.588 | 6.564 | 6.571 | 6.554 | 6.491 | 6.444 | 6.444 | 6.454 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 30450.0684 | 78958.3933 | 109408.4616 | 0.0018875 | 651132.3236 | 351967.8899 | 7542.5706 | 19547.6328 | 27090.2035 | 82318.2582 | -269649.6317 | 0
| 60553934 | RVL | 1999 | 33064397 | 33064396 | 194.38 | 49456.6662 | 18880.1294 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 4131.0312 | 63.0601 | 4194.0913 | 5.4731e-05 | 18880.1294 | 10205.605 | 1076.6373 | 16.4348 | 1093.0722 | 3101.0192 | -7104.5858 | 0
| 60553939 | CHA | 1957 | 33021368 | 30223838 | 3878.26 | 48008.7507 | 376695.3938 | 0.0376 | 0.04065 | 0.04395 | 0.04754 | 0.05143 | 0.05565 | 0.06023 | 0.06521 | 0.07061 | 0.07647 | 0.08284 | 0.08975 | 0.09726 | 0.10542 | 0.11428 | 0.12391 | 0.12711 | 0.12711 | 0.12711 | 0.12711 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 1138886.9487 | 463362.9703 | 1602249.9189 | 0.001092 | 376695.3938 | 203621.7188 | 16024.6629 | 6542.3878 | 22567.0507 | 1579682.8682 | 1376061.1494 | 1
| 60553973 | CHM | 2005 | 30229785 | 30229783 | 196.1 | 43924.3002 | 19047.193 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 0.00021 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 279.4654 | 63.6181 | 343.0835 | 5.5215e-05 | 19047.193 | 10295.9108 | 73.4793 | 16.727 | 90.2063 | 252.8772 | -10043.0336 | 0
| 60554004 | RVL | 1998 | 33064647 | 33064645 | 95.45 | 49456.6662 | 9271.0585 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 1967.1577 | 14.7455 | 1981.9032 | 2.6875e-05 | 9271.0585 | 5011.4466 | 528.6811 | 3.9629 | 532.644 | 1449.2592 | -3562.1874 | 0
| 60554030 | CHM | 1975 | 30083715 | 33052943 | 17.75 | 43924.3002 | 1724.0575 | 5e-05 | 6e-05 | 6e-05 | 7e-05 | 8e-05 | 8e-05 | 9e-05 | 0.0001 | 0.00011 | 0.00012 | 0.00013 | 0.00014 | 0.00015 | 0.00017 | 0.00018 | 0.0002 | 0.00022 | 0.00024 | 0.00026 | 0.00029 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 168.1856 | 3.4777 | 171.6633 | 4.9978e-06 | 1724.0575 | 931.9348 | 6.651 | 0.13704 | 6.788 | 164.8753 | -767.0595 | 0
| 60554032 | RVL | 1999 | 33064126 | 33064099 | 2227.15 | 49456.6662 | 216323.0795 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 0.00238 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 46818.3542 | 8188.6102 | 55006.9643 | 0.00062709 | 216323.0795 | 116932.8799 | 12335.8001 | 2157.5525 | 14493.3526 | 40513.6117 | -76419.2682 | 0
| 60554065 | RVL | 1999 | 33064373 | 33064349 | 2550.88 | 49456.6662 | 247766.9744 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 0.00273 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 53703.4062 | 10758.1216 | 64461.5278 | 0.00071824 | 247766.9744 | 133929.7958 | 14128.8848 | 2830.3653 | 16959.2501 | 47502.2777 | -86427.5181 | 0
| 60554066 | CHM | 1998 | 31016836 | 31016837 | 178.79 | 43924.3002 | 17365.8727 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.0002 | 0.00023 | 0.00025 | 0.00028 | 0.00032 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 268.8836 | 55.8308 | 324.7144 | 5.0341e-05 | 17365.8727 | 9387.0775 | 66.9932 | 13.9043 | 80.8975 | 243.8169 | -9143.2606 | 0
| 60554101 | RVL | 1999 | 33064404 | 33064399 | 314.14 | 49456.6662 | 30512.4182 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 6688.3363 | 165.0008 | 6853.3371 | 8.8451e-05 | 30512.4182 | 16493.4086 | 1739.9673 | 42.9249 | 1782.8922 | 5070.4449 | -11422.9637 | 0
| 60554107 | RVL | 1998 | 33064076 | 33064091 | 939.65 | 49456.6662 | 91268.2045 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 0.00101 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 19868.2932 | 1466.1259 | 21334.419 | 0.00026457 | 91268.2045 | 49334.7914 | 5204.5594 | 384.0561 | 5588.6155 | 15745.8035 | -33588.9879 | 0
| 60555573 | CTN | 1955 | 30228881 | 30021528 | 65.76 | 45198.6405 | 6387.2688 | 0.00062 | 0.00066 | 0.00072 | 0.00077 | 0.00083 | 0.0009 | 0.00097 | 0.00105 | 0.00113 | 0.00122 | 0.00132 | 0.00143 | 0.00154 | 0.00167 | 0.0018 | 0.00195 | 0.0021 | 0.00216 | 0.00216 | 0.00216 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 16229.1467 | 127.4344 | 16356.5811 | 1.8516e-05 | 6387.2688 | 3452.6216 | 239.1809 | 1.881 | 241.0619 | 16115.5192 | 12662.8976 | 1
| 60555574 | RVL | 1998 | 33064572 | 33064567 | 37.33 | 49456.6662 | 3625.8629 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 786.8631 | 2.3068 | 789.1699 | 1.0511e-05 | 3625.8629 | 1959.9508 | 206.7644 | 0.60615 | 207.3706 | 581.7993 | -1378.1515 | 0
| 60555640 | OYN | 1998 | 30254709 | 30254690 | 7.68 | 42821.2873 | 745.9584 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 6.588 | 6.564 | 6.571 | 6.554 | 6.491 | 6.444 | 6.444 | 6.454 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 39.9599 | 0.11864 | 40.0786 | 2.1624e-06 | 745.9584 | 403.2259 | 8.641 | 0.025656 | 8.6667 | 31.4119 | -371.814 | 0
| 60555737 | RVL | 1998 | 33064567 | 33064551 | 411.54 | 49456.6662 | 39972.8802 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 8655.494 | 279.7361 | 8935.2301 | 0.00011588 | 39972.8802 | 21607.2368 | 2279.4491 | 73.6693 | 2353.1184 | 6582.1117 | -15025.1251 | 0
| 60555750 | RVL | 2017 | 30352471 | 30352470 | 40.09 | 49456.6662 | 3893.9417 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 786.8631 | 2.4773 | 789.3404 | 1.1288e-05 | 3893.9417 | 2104.8601 | 222.0516 | 0.69909 | 222.7507 | 566.5897 | -1538.2704 | 0
| 60555752 | RVL | 1973 | 33066540 | 33066545 | 359.26 | 49456.6662 | 34894.9238 | 0.0004 | 0.00043 | 0.00046 | 0.0005 | 0.00054 | 0.00058 | 0.00062 | 0.00067 | 0.00073 | 0.00079 | 0.00085 | 0.00092 | 0.00099 | 0.00108 | 0.00117 | 0.00126 | 0.00137 | 0.00149 | 0.00161 | 0.00175 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 16654.5018 | 462.9625 | 17117.4643 | 0.00010116 | 34894.9238 | 18862.3606 | 1989.8792 | 56.141 | 2046.0202 | 15071.444 | -3790.9166 | 0
| 60555770 | RVL | 1998 | 33064021 | 33064010 | 671.82 | 49456.6662 | 65253.8766 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 0.00072 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 14163.5357 | 747.2556 | 14910.7913 | 0.00018916 | 65253.8766 | 35272.8139 | 3721.0952 | 196.3217 | 3917.4169 | 10993.3744 | -24279.4394 | 0
| 60555795 | CHM | 2005 | 30229783 | 30229782 | 64.6 | 43924.3002 | 6274.598 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 93.1551 | 6.9858 | 100.1409 | 1.8189e-05 | 6274.598 | 3391.7177 | 24.2058 | 1.8152 | 26.021 | 74.1199 | -3317.5978 | 0
| 60555811 | RVL | 1998 | 33064624 | 33064595 | 869.07 | 49456.6662 | 84412.7691 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 0.00093 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 18294.567 | 1248.5947 | 19543.1616 | 0.0002447 | 84412.7691 | 45629.1036 | 4813.629 | 328.5277 | 5142.1566 | 14401.005 | -31228.0986 | 0
| 60555814 | CHA | 1959 | 32038590 | 32038688 | 2651.8 | 48008.7507 | 257569.334 | 0.02506 | 0.02714 | 0.02941 | 0.03188 | 0.03455 | 0.03747 | 0.04064 | 0.04409 | 0.04784 | 0.05192 | 0.05636 | 0.0612 | 0.06646 | 0.07219 | 0.07843 | 0.08523 | 0.08691 | 0.08691 | 0.08691 | 0.08691 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 774067.8369 | 215324.1109 | 989391.9478 | 0.00074665 | 257569.334 | 139228.4359 | 10957.0274 | 3058.7499 | 14015.7773 | 975376.1704 | 836147.7345 | 1
| 60555815 | CME | 1999 | 33086363 | 33086152 | 4096.89 | 46875.2879 | 397930.9257 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 0.00439 | 38.435 | 38.637 | 39.003 | 39.298 | 39.32 | 39.352 | 39.702 | 40.078 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 118223.4275 | 27784.5006 | 146007.9281 | 0.0011535 | 397930.9257 | 215100.5305 | 31065.0458 | 7300.81 | 38365.8558 | 107642.0723 | -107458.4582 | 0
| 60555821 | CHM | 1998 | 30082976 | 32108610 | 951.34 | 43924.3002 | 92403.6542 | 0.00102 | 0.00102 | 0.00102 | 0.00102 | 0.00102 | 0.00102 | 0.00102 | 0.00102 | 0.00102 | 0.00102 | 0.00102 | 0.00102 | 0.00102 | 0.00102 | 0.00102 | 0.00107 | 0.0012 | 0.00134 | 0.00151 | 0.00169 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 1440.4061 | 1591.4056 | 3031.8116 | 0.00026786 | 92403.6542 | 49948.5558 | 356.4702 | 393.6715 | 750.1417 | 2281.6699 | -47666.8858 | 0
| 60555840 | CTN | 1955 | 30241541 | 30146843 | 4244.11 | 45198.6405 | 412230.4043 | 0.03972 | 0.04282 | 0.04618 | 0.04981 | 0.05374 | 0.058 | 0.0626 | 0.06759 | 0.07298 | 0.07882 | 0.08515 | 0.092 | 0.09942 | 0.10746 | 0.11617 | 0.12561 | 0.13583 | 0.1391 | 0.1391 | 0.1391 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1046460.5611 | 530320.8161 | 1576781.3772 | 0.001195 | 412230.4043 | 222830.0766 | 15436.5914 | 7834.9405 | 23271.5319 | 1553509.8453 | 1330679.7687 | 1
| 60555841 | CHM | 1998 | 31016837 | 30086349 | 554.07 | 43924.3002 | 53816.8191 | 0.00059 | 0.00059 | 0.00059 | 0.00059 | 0.00059 | 0.00059 | 0.00059 | 0.00059 | 0.00059 | 0.00059 | 0.00059 | 0.00059 | 0.00059 | 0.00059 | 0.00059 | 0.00062 | 0.0007 | 0.00078 | 0.00088 | 0.00099 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 834.683 | 537.0959 | 1371.7789 | 0.00015601 | 53816.8191 | 29090.5421 | 207.6118 | 133.534 | 341.1458 | 1030.6331 | -28059.909 | 0
| 60555843 | RVL | 1998 | 33063891 | 33063883 | 175.16 | 49456.6662 | 17013.2908 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 3737.5997 | 51.4129 | 3789.0126 | 4.9319e-05 | 17013.2908 | 9196.4902 | 970.1811 | 13.3454 | 983.5265 | 2805.4861 | -6391.0041 | 0
| 60555867 | CHM | 1998 | 32118494 | 31016836 | 159.07 | 43924.3002 | 15450.4691 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00018 | 0.0002 | 0.00022 | 0.00025 | 0.00028 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 239.8318 | 44.3049 | 284.1367 | 4.4789e-05 | 15450.4691 | 8351.711 | 59.604 | 11.0062 | 70.6103 | 213.5264 | -8138.1846 | 0
| 60555871 | CTN | 2010 | 30147109 | 30147108 | 129.36 | 45198.6405 | 12564.7368 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 0.00014 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1808.4818 | 27.9777 | 1836.4595 | 3.6423e-05 | 12564.7368 | 6791.8359 | 470.5056 | 7.2788 | 477.7844 | 1358.6751 | -5433.1608 | 0
| 60555888 | CHM | 2005 | 30233881 | 30233882 | 55 | 43924.3002 | 5342.15 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 79.8473 | 5.098 | 84.9452 | 1.5486e-05 | 5342.15 | 2887.6853 | 20.6087 | 1.3158 | 21.9245 | 63.0208 | -2824.6646 | 0
| 60555891 | RVL | 1973 | 33066534 | 33066540 | 266.36 | 49456.6662 | 25871.5468 | 0.0003 | 0.00032 | 0.00034 | 0.00037 | 0.0004 | 0.00043 | 0.00046 | 0.0005 | 0.00054 | 0.00058 | 0.00063 | 0.00068 | 0.00074 | 0.0008 | 0.00086 | 0.00094 | 0.00102 | 0.0011 | 0.00119 | 0.0013 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 12347.4863 | 254.4956 | 12601.9819 | 7.4998e-05 | 25871.5468 | 13984.7976 | 1475.3221 | 30.8603 | 1506.1825 | 11095.7995 | -2888.9981 | 0
| 60555899 | CHM | 1998 | 30083009 | 31015919 | 174.21 | 43924.3002 | 16921.0173 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.00019 | 0.0002 | 0.00022 | 0.00025 | 0.00028 | 0.00031 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 267.8985 | 54.2 | 322.0985 | 4.9051e-05 | 16921.0173 | 9146.612 | 65.2771 | 13.2011 | 78.4781 | 243.6204 | -8902.9917 | 0
| 60555903 | CTN | 2014 | 30296912 | 30296910 | 216.23 | 45198.6405 | 21002.4199 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 0.00023 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 2971.0773 | 76.8294 | 3047.9067 | 6.0883e-05 | 21002.4199 | 11352.8036 | 786.4674 | 20.3373 | 806.8048 | 2241.1019 | -9111.7017 | 0
| 60555904 | CHA | 1965 | 33021502 | 30237361 | 4210.75 | 48008.7507 | 408990.1475 | 0.03624 | 0.03951 | 0.04309 | 0.04702 | 0.05132 | 0.05602 | 0.06118 | 0.06683 | 0.07302 | 0.0798 | 0.08724 | 0.0954 | 0.10434 | 0.11415 | 0.12491 | 0.13671 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 1197486.7101 | 528808.6861 | 1726295.3961 | 0.0011856 | 408990.1475 | 221078.5642 | 17398.4853 | 7712.2545 | 25110.7398 | 1701184.6563 | 1480106.0922 | 1
| 60555905 | RVL | 1973 | 33063669 | 33063699 | 1511.75 | 49456.6662 | 146836.2775 | 0.00169 | 0.00181 | 0.00195 | 0.0021 | 0.00226 | 0.00244 | 0.00263 | 0.00284 | 0.00306 | 0.00331 | 0.00358 | 0.00387 | 0.00418 | 0.00453 | 0.00491 | 0.00532 | 0.00576 | 0.00625 | 0.00678 | 0.00736 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 70093.5756 | 8199.3182 | 78292.8937 | 0.00042566 | 146836.2775 | 79371.9692 | 8373.3228 | 994.0824 | 9367.4052 | 68925.4886 | -10446.4806 | 0
| 60555915 | CTN | 1955 | 30228887 | 30240483 | 570.43 | 45198.6405 | 55405.8659 | 0.00534 | 0.00576 | 0.00621 | 0.0067 | 0.00722 | 0.0078 | 0.00841 | 0.00908 | 0.00981 | 0.01059 | 0.01144 | 0.01237 | 0.01336 | 0.01444 | 0.01561 | 0.01688 | 0.01826 | 0.0187 | 0.0187 | 0.0187 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 140656.4412 | 9580.5737 | 150237.0149 | 0.00016061 | 55405.8659 | 29949.4972 | 2074.7565 | 141.5361 | 2216.2926 | 148020.7223 | 118071.2251 | 1
| 60555938 | CTN | 1955 | 30146843 | 30546420 | 3795.77 | 45198.6405 | 368683.1401 | 0.03552 | 0.0383 | 0.0413 | 0.04455 | 0.04807 | 0.05187 | 0.05599 | 0.06045 | 0.06527 | 0.0705 | 0.07616 | 0.08228 | 0.08892 | 0.09611 | 0.1039 | 0.11234 | 0.12148 | 0.12441 | 0.12441 | 0.12441 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 935934.054 | 424203.553 | 1360137.607 | 0.0010688 | 368683.1401 | 199290.7158 | 13805.8982 | 6267.0364 | 20072.9346 | 1340064.6723 | 1140773.9565 | 1
| 60554643 | CHM | 1998 | 30086349 | 30233881 | 2376.25 | 43924.3002 | 230805.1625 | 0.00254 | 0.00254 | 0.00254 | 0.00254 | 0.00254 | 0.00254 | 0.00254 | 0.00254 | 0.00254 | 0.00254 | 0.00254 | 0.00254 | 0.00254 | 0.00254 | 0.00254 | 0.00268 | 0.00299 | 0.00335 | 0.00376 | 0.00423 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 3589.4707 | 9905.6935 | 13495.1642 | 0.00066907 | 230805.1625 | 124761.1324 | 890.3886 | 2456.1037 | 3346.4923 | 10148.6719 | -114612.4605 | 0
| 60554735 | CTN | 2011 | 30296727 | 30296728 | 23.96 | 45198.6405 | 2327.2348 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 387.5318 | 1.1104 | 388.6422 | 6.7463e-06 | 2327.2348 | 1257.9807 | 87.1468 | 0.24971 | 87.3965 | 301.2457 | -956.735 | 0
| 60554744 | RVL | 1999 | 33064301 | 33064196 | 7828.44 | 49456.6662 | 760376.3772 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 0.00838 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 164847.8184 | 101345.1612 | 266192.9796 | 0.0022042 | 760376.3772 | 411019.4799 | 43360.3802 | 26657.0996 | 70017.4798 | 196175.4998 | -214843.9801 | 0
| 60554745 | RVL | 1998 | 33063926 | 33063891 | 1103.79 | 49456.6662 | 107211.1227 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 0.00118 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 23212.4613 | 2012.1124 | 25224.5737 | 0.00031079 | 107211.1227 | 57952.6945 | 6113.7026 | 529.9506 | 6643.6532 | 18580.9205 | -39371.774 | 0
| 60554800 | RVL | 2017 | 30352812 | 30352811 | 79.17 | 49456.6662 | 7689.7821 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 1573.7262 | 9.7844 | 1583.5106 | 2.2292e-05 | 7689.7821 | 4156.6918 | 438.509 | 2.7264 | 441.2354 | 1142.2752 | -3014.4165 | 0
| 60554818 | CTN | 2014 | 30323206 | 30323204 | 31.95 | 45198.6405 | 3103.3035 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 387.5318 | 1.4807 | 389.0125 | 8.996e-06 | 3103.3035 | 1677.4827 | 116.2079 | 0.44402 | 116.6519 | 272.3606 | -1405.122 | 0
| 60554830 | RVL | 1998 | 33064645 | 33064624 | 614.62 | 49456.6662 | 59698.0406 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 0.00066 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 12983.2411 | 626.6635 | 13609.9046 | 0.00017306 | 59698.0406 | 32269.6211 | 3404.2743 | 164.3145 | 3568.5887 | 10041.3158 | -22228.3053 | 0
| 60554835 | RVL | 1999 | 33064498 | 33064490 | 269.05 | 49456.6662 | 26132.8265 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 0.00029 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 5704.7574 | 120.5354 | 5825.2929 | 7.5755e-05 | 26132.8265 | 14126.0316 | 1490.2216 | 31.4868 | 1521.7084 | 4303.5845 | -9822.4471 | 0
| 60554842 | CTN | 1998 | 33107261 | 30147032 | 1333.63 | 45198.6405 | 129535.4819 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 0.00143 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 18472.3499 | 2946.1521 | 21418.502 | 0.0003755 | 129535.4819 | 70020.069 | 4850.6522 | 773.6297 | 5624.2819 | 15794.2201 | -54225.8489 | 0
| 60554844 | RVL | 1998 | 33064048 | 33064038 | 399.16 | 49456.6662 | 38770.4108 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 0.00043 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 8458.7783 | 265.1546 | 8723.9329 | 0.00011239 | 38770.4108 | 20957.2451 | 2210.8785 | 69.3037 | 2280.1822 | 6443.7508 | -14513.4943 | 0
| 60554851 | CTN | 1955 | 30021420 | 30150101 | 4811.9 | 45198.6405 | 467379.847 | 0.04503 | 0.04855 | 0.05236 | 0.05648 | 0.06093 | 0.06576 | 0.07098 | 0.07663 | 0.08275 | 0.08937 | 0.09654 | 0.10431 | 0.11273 | 0.12184 | 0.13171 | 0.14241 | 0.154 | 0.15771 | 0.15771 | 0.15771 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1186478.8232 | 681719.5591 | 1868198.3824 | 0.0013549 | 467379.847 | 252640.9649 | 17501.7458 | 10071.5341 | 27573.2799 | 1840625.1025 | 1587984.1376 | 1
| 60554866 | CTN | 1955 | 30228886 | 30228887 | 365.21 | 45198.6405 | 35472.8473 | 0.00342 | 0.00368 | 0.00397 | 0.00429 | 0.00462 | 0.00499 | 0.00539 | 0.00582 | 0.00628 | 0.00678 | 0.00733 | 0.00792 | 0.00856 | 0.00925 | 0.01 | 0.01081 | 0.01169 | 0.01197 | 0.01197 | 0.01197 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 90057.9186 | 3927.2926 | 93985.2112 | 0.00010283 | 35472.8473 | 19174.7557 | 1328.3345 | 58.016 | 1386.3505 | 92598.8608 | 73424.1051 | 1
| 60554921 | RVL | 1998 | 33063753 | 33063752 | 33.81 | 49456.6662 | 3283.9653 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 786.8631 | 2.0892 | 788.9523 | 9.5197e-06 | 3283.9653 | 1775.1389 | 187.2678 | 0.49722 | 187.765 | 601.1873 | -1173.9516 | 0
| 60554944 | CTN | 2011 | 30296990 | 30296991 | 40.1 | 45198.6405 | 3894.913 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 516.7091 | 2.4779 | 519.187 | 1.1291e-05 | 3894.913 | 2105.3851 | 145.8509 | 0.69944 | 146.5504 | 372.6367 | -1732.7485 | 0
| 60554958 | CTN | 2014 | 30296164 | 30296163 | 40.32 | 45198.6405 | 3916.2816 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 516.7091 | 2.4915 | 519.2006 | 1.1353e-05 | 3916.2816 | 2116.9359 | 146.6511 | 0.70714 | 147.3582 | 371.8424 | -1745.0935 | 0
| 60554965 | CTN | 2014 | 30296728 | 30296743 | 1049.89 | 45198.6405 | 101975.8157 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 0.00112 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 14467.8545 | 1816.5426 | 16284.3971 | 0.00029561 | 101975.8157 | 55122.7629 | 3818.6388 | 479.4574 | 4298.0962 | 11986.3009 | -43136.4619 | 0
| 60554968 | RVL | 1999 | 33064490 | 33064477 | 925.18 | 49456.6662 | 89862.7334 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 0.00099 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 19474.8616 | 1414.9634 | 20889.825 | 0.0002605 | 89862.7334 | 48575.0676 | 5124.4126 | 372.3188 | 5496.7314 | 15393.0936 | -33181.974 | 0
| 60554977 | CHM | 2005 | 30229942 | 30152639 | 40.7 | 43924.3002 | 3953.191 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 53.2315 | 2.515 | 55.7465 | 1.146e-05 | 3953.191 | 2136.8871 | 15.2504 | 0.72053 | 15.971 | 39.7756 | -2097.1116 | 0
| 60554994 | RVL | 1998 | 33064771 | 33064866 | 3043.28 | 49456.6662 | 295593.7864 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 0.00326 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 64129.3422 | 15326.5104 | 79455.8526 | 0.00085688 | 295593.7864 | 159782.4551 | 16856.2035 | 4028.5269 | 20884.7304 | 58571.1222 | -101211.3329 | 0
| 60554999 | CTN | 1955 | 30323204 | 30228881 | 904.75 | 45198.6405 | 87878.3675 | 0.00847 | 0.00913 | 0.00984 | 0.01062 | 0.01146 | 0.01236 | 0.01335 | 0.01441 | 0.01556 | 0.0168 | 0.01815 | 0.01961 | 0.02119 | 0.02291 | 0.02477 | 0.02678 | 0.02896 | 0.02965 | 0.02965 | 0.02965 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 223085.4086 | 24100.6626 | 247186.0712 | 0.00025475 | 87878.3675 | 47502.4238 | 3290.7385 | 356.0571 | 3646.7956 | 243539.2757 | 196036.8519 | 1
| 60555007 | RVL | 2017 | 30352807 | 30352806 | 84.43 | 49456.6662 | 8200.6859 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 1770.442 | 11.7388 | 1782.1807 | 2.3773e-05 | 8200.6859 | 4432.8595 | 467.6432 | 3.1007 | 470.7439 | 1311.4369 | -3121.4227 | 0
| 60555024 | CTN | 2011 | 30296142 | 30296141 | 87.54 | 45198.6405 | 8502.7602 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1162.5954 | 12.1712 | 1174.7666 | 2.4648e-05 | 8502.7602 | 4596.145 | 318.3987 | 3.3333 | 321.732 | 853.0346 | -3743.1104 | 0
| 60555035 | RVL | 2017 | 30352812 | 30352477 | 319.46 | 49456.6662 | 31029.1498 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 6688.3363 | 167.7951 | 6856.1314 | 8.9949e-05 | 31029.1498 | 16772.7265 | 1769.4339 | 44.391 | 1813.8249 | 5042.3064 | -11730.4201 | 0
| 60555036 | CTN | 2010 | 30228693 | 30228694 | 116.7 | 45198.6405 | 11335.071 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1550.1273 | 21.634 | 1571.7612 | 3.2859e-05 | 11335.071 | 6127.1433 | 424.4589 | 5.9239 | 430.3827 | 1141.3785 | -4985.7648 | 0
| 60555040 | CHA | 1957 | 32038688 | 30028593 | 2428.21 | 48008.7507 | 235852.0373 | 0.02354 | 0.02545 | 0.02752 | 0.02976 | 0.0322 | 0.03484 | 0.03771 | 0.04083 | 0.04421 | 0.04788 | 0.05187 | 0.05619 | 0.0609 | 0.066 | 0.07155 | 0.07758 | 0.07958 | 0.07958 | 0.07958 | 0.07958 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 713049.0967 | 181639.1289 | 894688.2257 | 0.0006837 | 235852.0373 | 127489.2075 | 10033.1713 | 2564.6903 | 12597.8615 | 882090.3641 | 754601.1567 | 1
| 60555045 | OYN | 1998 | 30254691 | 30254709 | 7.93 | 42821.2873 | 770.2409 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 6.588 | 6.564 | 6.571 | 6.554 | 6.491 | 6.444 | 6.444 | 6.454 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 39.9599 | 0.12251 | 40.0824 | 2.2328e-06 | 770.2409 | 416.3517 | 8.9223 | 0.027353 | 8.9497 | 31.1328 | -385.2189 | 0
| 60555056 | MBN | 2011 | 30284425 | 33063623 | 10 | 42126.3122 | 971.3 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 49.002 | 49.526 | 50.315 | 50.958 | 51.207 | 51.625 | 52.399 | 53.346 | 53.67 | 53.67 | 53.67 | 53.67 | 53.67 | 53.67 | 53.67 | 53.67 | 53.67 | 53.67 | 53.67 | 53.67 | 318.87 | 0.15448 | 319.0245 | 2.8156e-06 | 971.3 | 525.0337 | 89.7826 | 0.043497 | 89.8261 | 229.1983 | -295.8354 | 0
| 60555102 | CTN | 2014 | 31037393 | 31037408 | 1765.19 | 45198.6405 | 171452.9047 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 0.00189 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 24414.5044 | 5153.9124 | 29568.4169 | 0.00049702 | 171452.9047 | 92678.4233 | 6420.3135 | 1355.331 | 7775.6445 | 21792.7724 | -70885.6509 | 0
| 60555569 | OYN | 1998 | 33065209 | 33065210 | 124.32 | 42821.2873 | 12075.2016 | 0.00013 | 0.00013 | 0.00013 | 0.00013 | 0.00013 | 0.00013 | 0.00013 | 0.00013 | 0.00013 | 0.00013 | 0.00013 | 0.00013 | 0.00013 | 0.00013 | 0.00013 | 0.00014 | 0.00016 | 0.00018 | 0.0002 | 0.00022 | 6.588 | 6.564 | 6.571 | 6.554 | 6.491 | 6.444 | 6.444 | 6.454 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 555.9812 | 26.7379 | 582.7191 | 3.5004e-05 | 12075.2016 | 6527.2189 | 139.8764 | 6.7227 | 146.5991 | 436.12 | -6091.0989 | 0
| 60845175 | CHA | 1957 | 30598579 | 33021368 | 487.13 | 48008.7507 | 47314.9369 | 0.00472 | 0.00511 | 0.00552 | 0.00597 | 0.00646 | 0.00699 | 0.00757 | 0.00819 | 0.00887 | 0.00961 | 0.0104 | 0.01127 | 0.01222 | 0.01324 | 0.01435 | 0.01556 | 0.01597 | 0.01597 | 0.01597 | 0.01597 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 143058.3095 | 7310.7491 | 150369.0586 | 0.00013716 | 47314.9369 | 25575.9665 | 2012.7825 | 103.2172 | 2115.9998 | 148253.0588 | 122677.0923 | 1
| 60846589 | CHM | 1937 | 33049269 | 33049217 | 5042.82 | 43924.3002 | 489809.1066 | 0.04718 | 0.05009 | 0.05319 | 0.05649 | 0.06 | 0.06374 | 0.06773 | 0.07197 | 0.07649 | 0.0813 | 0.08643 | 0.09189 | 0.09772 | 0.10392 | 0.11053 | 0.11757 | 0.12507 | 0.13307 | 0.1416 | 0.15069 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 110654.7757 | 649406.9846 | 760061.7603 | 0.0014199 | 489809.1066 | 264765.0431 | 1889.5611 | 11061.3816 | 12950.9427 | 747110.8176 | 482345.7745 | 1
| 60846644 | CHA | 1957 | 30028593 | 30598579 | 771.84 | 48008.7507 | 74968.8192 | 0.00748 | 0.00809 | 0.00875 | 0.00946 | 0.01024 | 0.01108 | 0.01199 | 0.01298 | 0.01405 | 0.01522 | 0.01649 | 0.01786 | 0.01936 | 0.02098 | 0.02274 | 0.02466 | 0.0253 | 0.0253 | 0.0253 | 0.0253 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 226675.0962 | 18354.1824 | 245029.2786 | 0.00021732 | 74968.8192 | 40524.2009 | 3189.1817 | 259.1296 | 3448.3113 | 241580.9673 | 201056.7664 | 1
| 60859339 | BBD | 2004 | 31030552 | 30224948 | 55.03 | 52622.2251 | 5345.0639 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1561.17 | 5.1008 | 1566.2708 | 1.5495e-05 | 5345.0639 | 2889.2604 | 403.1597 | 1.3172 | 404.4769 | 1161.7938 | -1727.4666 | 0
| 60859340 | BBD | 2008 | 30265958 | 30265959 | 37.02 | 52622.2251 | 3595.7526 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 4e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1040.78 | 2.2876 | 1043.0676 | 1.0424e-05 | 3595.7526 | 1943.6747 | 271.2152 | 0.59612 | 271.8113 | 771.2563 | -1172.4185 | 0
| 60859342 | BBD | 2018 | 30544878 | 30544876 | 58.99 | 52622.2251 | 5729.6987 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1561.17 | 5.4678 | 1566.6378 | 1.661e-05 | 5729.6987 | 3097.1738 | 432.1714 | 1.5136 | 433.685 | 1132.9528 | -1964.221 | 0
| 60823678 | CTN | 2005 | 30241541 | 30241539 | 20.52 | 45198.6405 | 1993.1076 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 258.3545 | 0.634 | 258.9885 | 5.7777e-06 | 1993.1076 | 1077.3691 | 74.6349 | 0.18315 | 74.8181 | 184.1705 | -893.1987 | 0
| 60823677 | CTN | 2005 | 30241532 | 30241530 | 22.76 | 45198.6405 | 2210.6788 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 2e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 258.3545 | 0.70321 | 259.0578 | 6.4084e-06 | 2210.6788 | 1194.9767 | 82.7822 | 0.22532 | 83.0075 | 176.0502 | -1018.9265 | 0
| 60823590 | CTN | 2005 | 30241530 | 30241536 | 25.44 | 45198.6405 | 2470.9872 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 387.5318 | 1.179 | 388.7108 | 7.163e-06 | 2470.9872 | 1335.6857 | 92.5299 | 0.28151 | 92.8114 | 295.8995 | -1039.7863 | 0
| 60823555 | CTN | 2005 | 30241536 | 30241541 | 24.26 | 45198.6405 | 2356.3738 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 387.5318 | 1.1243 | 388.6562 | 6.8308e-06 | 2356.3738 | 1273.7318 | 88.238 | 0.256 | 88.494 | 300.1622 | -973.5696 | 0
| 60823548 | CTN | 1955 | 30241541 | 30241536 | 24.26 | 45198.6405 | 2356.3738 | 0.00023 | 0.00024 | 0.00026 | 0.00028 | 0.00031 | 0.00033 | 0.00036 | 0.00039 | 0.00042 | 0.00045 | 0.00049 | 0.00053 | 0.00057 | 0.00061 | 0.00066 | 0.00072 | 0.00078 | 0.0008 | 0.0008 | 0.0008 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 5990.6851 | 17.3537 | 6008.0388 | 6.8308e-06 | 2356.3738 | 1273.7318 | 88.238 | 0.256 | 88.494 | 5919.5448 | 4645.8131 | 1
| 60823535 | CTN | 2005 | 30241536 | 30241530 | 25.44 | 45198.6405 | 2470.9872 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 387.5318 | 1.179 | 388.7108 | 7.163e-06 | 2470.9872 | 1335.6857 | 92.5299 | 0.28151 | 92.8114 | 295.8995 | -1039.7863 | 0
| 60859343 | BBD | 2008 | 30270040 | 30225889 | 30.74 | 52622.2251 | 2985.7762 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 780.585 | 1.4247 | 782.0097 | 8.6553e-06 | 2985.7762 | 1613.9536 | 225.2068 | 0.41103 | 225.6178 | 556.3918 | -1057.5617 | 0
| 60859403 | BBD | 2005 | 30238561 | 30238563 | 92.64 | 52622.2251 | 8998.1232 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 2601.95 | 14.3114 | 2616.2614 | 2.6084e-05 | 8998.1232 | 4863.9122 | 678.6974 | 3.733 | 682.4304 | 1933.8311 | -2930.0811 | 0
| 60859404 | BBD | 2004 | 30224948 | 31030552 | 55.03 | 52622.2251 | 5345.0639 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1561.17 | 5.1008 | 1566.2708 | 1.5495e-05 | 5345.0639 | 2889.2604 | 403.1597 | 1.3172 | 404.4769 | 1161.7938 | -1727.4666 | 0
| 60859408 | BBD | 2008 | 30265981 | 30265983 | 66 | 52622.2251 | 6410.58 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1821.365 | 7.1372 | 1828.5022 | 1.8583e-05 | 6410.58 | 3465.2224 | 483.5279 | 1.8947 | 485.4227 | 1343.0795 | -2122.1429 | 0
| 60859588 | BBD | 2008 | 30265960 | 30265959 | 60.06 | 52622.2251 | 5833.6278 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 6e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1561.17 | 5.567 | 1566.737 | 1.6911e-05 | 5833.6278 | 3153.3524 | 440.0104 | 1.569 | 441.5794 | 1125.1576 | -2028.1948 | 0
| 60859590 | CHA | 1999 | 33018658 | 33021817 | 110.27 | 48008.7507 | 10710.5251 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00012 | 0.00013 | 0.00014 | 0.00016 | 0.00018 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 1831.0696 | 21.2486 | 1852.3182 | 3.1048e-05 | 10710.5251 | 5789.5466 | 455.6269 | 5.289 | 460.9159 | 1391.4023 | -4398.1443 | 0
| 60859591 | BBD | 2008 | 30225892 | 30225889 | 373.91 | 52622.2251 | 36317.8783 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 10407.8001 | 231.0526 | 10638.8527 | 0.00010528 | 36317.8783 | 19631.535 | 2739.3322 | 60.813 | 2800.1452 | 7838.7075 | -11792.8275 | 0
| 60859634 | BBD | 2005 | 30238570 | 30238575 | 768.31 | 52622.2251 | 74625.9503 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 0.00082 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 21335.9903 | 973.2717 | 22309.262 | 0.00021633 | 74625.9503 | 40338.864 | 5628.7778 | 256.7648 | 5885.5426 | 16423.7194 | -23915.1446 | 0
| 60859637 | BBD | 2004 | 30224961 | 30224960 | 139.89 | 52622.2251 | 13587.5157 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 3902.9251 | 32.4162 | 3935.3412 | 3.9388e-05 | 13587.5157 | 7344.6964 | 1024.8594 | 8.5121 | 1033.3715 | 2901.9697 | -4442.7267 | 0
| 60859642 | BBD | 2008 | 30270041 | 30270040 | 30.54 | 52622.2251 | 2966.3502 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 3e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 780.585 | 1.4154 | 782.0004 | 8.599e-06 | 2966.3502 | 1603.4529 | 223.7416 | 0.4057 | 224.1473 | 557.8531 | -1045.5998 | 0
| 60859660 | BBD | 2004 | 30224978 | 30224961 | 2421.46 | 52622.2251 | 235196.4098 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 0.00259 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 67390.5059 | 9688.5957 | 77079.1017 | 0.0006818 | 235196.4098 | 127134.8097 | 17740.0533 | 2550.4513 | 20290.5046 | 56788.597 | -70346.2127 | 0
| 60859664 | BBD | 2004 | 30224980 | 30224978 | 321.18 | 52622.2251 | 31196.2134 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 8846.6301 | 168.6985 | 9015.3286 | 9.0433e-05 | 31196.2134 | 16863.0323 | 2353.0227 | 44.8703 | 2397.893 | 6617.4356 | -10245.5967 | 0
| 60859667 | BBD | 2008 | 30266163 | 30266167 | 415.04 | 52622.2251 | 40312.8352 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 0.00044 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 11448.5802 | 282.1151 | 11730.6953 | 0.00011686 | 40312.8352 | 21790.9986 | 3040.658 | 74.9277 | 3115.5857 | 8615.1096 | -13175.889 | 0
| 60859669 | BBD | 2006 | 30246893 | 30238557 | 239.88 | 52622.2251 | 23299.5444 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 6765.0701 | 96.3499 | 6861.42 | 6.7542e-05 | 23299.5444 | 12594.5083 | 1757.4042 | 25.0294 | 1782.4336 | 5078.9864 | -7515.522 | 0
| 60859672 | BBD | 2005 | 30238575 | 30238576 | 160.77 | 52622.2251 | 15615.5901 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 0.00017 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 4423.3151 | 42.2219 | 4465.537 | 4.5267e-05 | 15615.5901 | 8440.9668 | 1177.8301 | 11.2427 | 1189.0728 | 3276.4641 | -5164.5026 | 0
| 60859674 | BBD | 2004 | 30224960 | 30590487 | 140.28 | 52622.2251 | 13625.3964 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 0.00015 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 3902.9251 | 32.5065 | 3935.4316 | 3.9498e-05 | 13625.3964 | 7365.1727 | 1027.7166 | 8.5596 | 1036.2762 | 2899.1554 | -4466.0173 | 0
| 60740562 | CTN | 2010 | 30282337 | 30282335 | 227.69 | 45198.6405 | 22115.5297 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 0.00024 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 3100.2545 | 84.4188 | 3184.6733 | 6.411e-05 | 22115.5297 | 11954.4923 | 828.1495 | 22.5502 | 850.6997 | 2333.9736 | -9620.5186 | 0
| 60767383 | WMN | 2018 | 30547415 | 30547413 | 84.15 | 61329.3035 | 8173.4895 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 9e-05 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 2123.3554 | 11.6999 | 2135.0552 | 2.3694e-05 | 8173.4895 | 4418.1586 | 559.0015 | 3.0801 | 562.0816 | 1572.9736 | -2845.185 | 0
| 60767389 | WMN | 1998 | 30552207 | 33107012 | 1146.19 | 61329.3035 | 111329.4347 | 0.00123 | 0.00123 | 0.00123 | 0.00123 | 0.00123 | 0.00123 | 0.00123 | 0.00123 | 0.00123 | 0.00123 | 0.00123 | 0.00123 | 0.00123 | 0.00123 | 0.00123 | 0.00129 | 0.00144 | 0.00162 | 0.00181 | 0.00204 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 30837.2068 | 2311.289 | 33148.4958 | 0.00032273 | 111329.4347 | 60178.8374 | 7614.0454 | 571.4466 | 8185.492 | 24963.0038 | -35215.8336 | 0
| 60770694 | WMN | 1998 | 30355658 | 30312136 | 428.83 | 61329.3035 | 41652.2579 | 0.00046 | 0.00046 | 0.00046 | 0.00046 | 0.00046 | 0.00046 | 0.00046 | 0.00046 | 0.00046 | 0.00046 | 0.00046 | 0.00046 | 0.00046 | 0.00046 | 0.00046 | 0.00048 | 0.00054 | 0.00061 | 0.00068 | 0.00076 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 11535.6324 | 323.4795 | 11859.1119 | 0.00012074 | 41652.2579 | 22515.0201 | 2848.6822 | 79.9895 | 2928.6717 | 8930.4402 | -13584.5799 | 0
| 60785776 | CHA | 1959 | 32038422 | 32038476 | 1962.16 | 48008.7507 | 190584.6008 | 0.01854 | 0.02009 | 0.02176 | 0.02359 | 0.02557 | 0.02772 | 0.03007 | 0.03262 | 0.0354 | 0.03842 | 0.04171 | 0.04528 | 0.04918 | 0.05342 | 0.05804 | 0.06306 | 0.06431 | 0.06431 | 0.06431 | 0.06431 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 572777.7792 | 117894.4817 | 690672.2609 | 0.00055248 | 190584.6008 | 103020.012 | 8107.4896 | 1674.6779 | 9782.1674 | 680890.0935 | 577870.0815 | 1
| 60785863 | CHA | 1959 | 32038476 | 32038588 | 4032.56 | 48008.7507 | 391682.5528 | 0.03811 | 0.04128 | 0.04472 | 0.04847 | 0.05255 | 0.05698 | 0.0618 | 0.06704 | 0.07275 | 0.07896 | 0.08571 | 0.09307 | 0.10107 | 0.10978 | 0.11927 | 0.1296 | 0.13217 | 0.13217 | 0.13217 | 0.13217 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 1177142.4109 | 497946.6088 | 1675089.0197 | 0.0011354 | 391682.5528 | 211722.9887 | 16662.2183 | 7073.3332 | 23735.5515 | 1651353.4682 | 1439630.4795 | 1
| 60796872 | OYN | 1998 | 30590268 | 33065058 | 67.97 | 42821.2873 | 6601.9261 | 7.2753e-05 | 7.2753e-05 | 7.2753e-05 | 7.2753e-05 | 7.2753e-05 | 7.2753e-05 | 7.2753e-05 | 7.2753e-05 | 7.2753e-05 | 7.2753e-05 | 7.2753e-05 | 7.2753e-05 | 7.2753e-05 | 7.2753e-05 | 7.2753e-05 | 7.6546e-05 | 8.5615e-05 | 9.5911e-05 | 0.00010761 | 0.00012092 | 6.588 | 6.564 | 6.571 | 6.554 | 6.491 | 6.444 | 6.444 | 6.454 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 308.5916 | 8.1133 | 316.7048 | 1.9138e-05 | 6601.9261 | 3568.654 | 76.4752 | 2.0095 | 78.4848 | 238.2201 | -3330.434 | 0
| 60797805 | OYN | 1998 | 32154848 | 30590268 | 486.48 | 42821.2873 | 47251.8024 | 0.00052071 | 0.00052071 | 0.00052071 | 0.00052071 | 0.00052071 | 0.00052071 | 0.00052071 | 0.00052071 | 0.00052071 | 0.00052071 | 0.00052071 | 0.00052071 | 0.00052071 | 0.00052071 | 0.00052071 | 0.00054786 | 0.00061277 | 0.00068646 | 0.0007702 | 0.00086544 | 6.588 | 6.564 | 6.571 | 6.554 | 6.491 | 6.444 | 6.444 | 6.454 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 2208.6725 | 415.6149 | 2624.2874 | 0.00013698 | 47251.8024 | 25541.8393 | 547.3543 | 102.942 | 650.2962 | 1973.9912 | -23567.8482 | 0
| 60823120 | CTN | 2005 | 30241537 | 30241540 | 33.41 | 45198.6405 | 3245.1133 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 3.5761e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 461.9508 | 1.8457 | 463.7966 | 9.4071e-06 | 3245.1133 | 1754.1376 | 121.5182 | 0.48553 | 122.0037 | 341.7929 | -1412.3447 | 0
| 60823125 | CTN | 2005 | 30241532 | 30241534 | 33.63 | 45198.6405 | 3266.4819 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 3.5996e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 464.9917 | 1.8701 | 466.8618 | 9.469e-06 | 3266.4819 | 1765.6883 | 122.3184 | 0.49194 | 122.8103 | 344.0515 | -1421.6368 | 0
| 60860110 | BBD | 2007 | 30257966 | 30257967 | 249.52 | 52622.2251 | 24235.8776 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 0.00026708 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 6949.2361 | 102.9502 | 7052.1863 | 7.0256e-05 | 24235.8776 | 13100.6408 | 1828.0286 | 27.0815 | 1855.1101 | 5197.0762 | -7903.5646 | 0
| 60860115 | CHA | 1999 | 33018658 | 32039829 | 23.69 | 48008.7507 | 2301.0097 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.7628e-05 | 3.0942e-05 | 3.471e-05 | 3.8996e-05 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 388.7649 | 0.96918 | 389.7341 | 6.6703e-06 | 2301.0097 | 1243.8048 | 97.8852 | 0.24411 | 98.1293 | 291.6048 | -952.2001 | 0
| 60860119 | BBD | 2007 | 30246901 | 33061889 | 262.77 | 52622.2251 | 25522.8501 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 0.00028126 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 7318.2447 | 114.1741 | 7432.4188 | 7.3987e-05 | 25522.8501 | 13796.3105 | 1925.1005 | 30.0341 | 1955.1345 | 5477.2842 | -8319.0263 | 0
| 60860120 | BBD | 2004 | 30266185 | 30266175 | 651.09 | 52622.2251 | 63240.3717 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 0.00069691 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 18133.1199 | 700.9683 | 18834.0882 | 0.00018332 | 63240.3717 | 34184.419 | 4770.0029 | 184.393 | 4954.396 | 13879.6922 | -20304.7268 | 0
| 60860121 | BBD | 2004 | 30266189 | 30266185 | 106.89 | 52622.2251 | 10382.2257 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 0.00011441 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 2976.9431 | 18.8926 | 2995.8357 | 3.0096e-05 | 10382.2257 | 5612.0852 | 783.0954 | 4.9698 | 788.0652 | 2207.7705 | -3404.3147 | 0
| 60860123 | BBD | 2008 | 30266157 | 30266161 | 478 | 52622.2251 | 46428.14 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 0.00051163 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 13312.4871 | 377.8087 | 13690.2957 | 0.00013459 | 46428.14 | 25096.6107 | 3501.9143 | 99.3844 | 3601.2987 | 10088.997 | -15007.6137 | 0
| 60860134 | BBD | 2014 | 30322371 | 30322372 | 50.64 | 52622.2251 | 4918.6632 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 5.4203e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1410.3454 | 4.2404 | 1414.5858 | 1.4258e-05 | 4918.6632 | 2658.7706 | 370.9978 | 1.1154 | 372.1132 | 1042.4725 | -1616.2981 | 0
| 60860135 | BBD | 2008 | 30266052 | 30266058 | 678 | 52622.2251 | 65854.14 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 0.00072571 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 18882.5856 | 760.1092 | 19642.6948 | 0.0001909 | 65854.14 | 35597.2847 | 4967.1505 | 199.9502 | 5167.1007 | 14475.5941 | -21121.6906 | 0
| 60860138 | BBD | 2006 | 30246893 | 30246897 | 1261.98 | 52622.2251 | 122576.1174 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 0.0013508 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 35146.6727 | 2633.4284 | 37780.1011 | 0.00035533 | 122576.1174 | 66258.2026 | 9245.4934 | 692.7354 | 9938.2288 | 27841.8723 | -38416.3303 | 0
| 60860244 | BBD | 2004 | 30266174 | 30266175 | 29.5 | 52622.2251 | 2865.335 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 3.1576e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 821.5865 | 1.439 | 823.0255 | 8.3062e-06 | 2865.335 | 1548.8494 | 216.1223 | 0.37854 | 216.5009 | 606.5247 | -942.3247 | 0
| 60860280 | BBD | 2014 | 30270040 | 30322371 | 54.22 | 52622.2251 | 5266.3886 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 5.8035e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1510.0495 | 4.8611 | 1514.9106 | 1.5266e-05 | 5266.3886 | 2846.7327 | 397.2255 | 1.2787 | 398.5043 | 1116.4064 | -1730.3263 | 0
| 60863023 | CTN | 1955 | 31037333 | 30609791 | 20.62 | 45198.6405 | 2002.8206 | 0.00019297 | 0.00020805 | 0.00022436 | 0.00024201 | 0.00026111 | 0.00028178 | 0.00030415 | 0.00032837 | 0.00035458 | 0.00038297 | 0.00041371 | 0.00044699 | 0.00048305 | 0.00052211 | 0.00056442 | 0.00061026 | 0.00065993 | 0.00067582 | 0.00067582 | 0.00067582 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 5084.263 | 12.5183 | 5096.7813 | 5.8059e-06 | 2002.8206 | 1082.6195 | 74.9986 | 0.18494 | 75.1836 | 5021.5977 | 3938.9782 | 1
| 60863185 | BBD | 2006 | 30246906 | 30246909 | 456.99 | 52622.2251 | 44387.4387 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 0.00048915 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 12727.3605 | 345.3265 | 13072.687 | 0.00012867 | 44387.4387 | 23993.5149 | 3347.9913 | 90.8397 | 3438.831 | 9633.856 | -14359.6589 | 0
| 60863224 | BBD | 2006 | 30246902 | 30243871 | 547.21 | 52622.2251 | 53150.5073 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 0.00058572 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 15240.0377 | 495.1364 | 15735.1741 | 0.00015408 | 53150.5073 | 28730.369 | 4008.9593 | 130.2478 | 4139.2071 | 11595.967 | -17134.402 | 0
| 60863436 | CTN | 1955 | 30609791 | 33012636 | 7332.91 | 45198.6405 | 712245.5483 | 0.068623 | 0.073986 | 0.079788 | 0.086065 | 0.092857 | 0.10021 | 0.10816 | 0.11677 | 0.1261 | 0.13619 | 0.14712 | 0.15896 | 0.17178 | 0.18567 | 0.20072 | 0.21702 | 0.23469 | 0.24033 | 0.24033 | 0.24033 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1808072.3757 | 1583147.3527 | 3391219.7284 | 0.0020647 | 712245.5483 | 385002.4851 | 26671.1126 | 23389.1883 | 50060.3009 | 3341159.4275 | 2956156.9424 | 1
| 60863646 | BBD | 2006 | 30246909 | 30590486 | 311.51 | 52622.2251 | 30256.9663 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 0.00033343 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 8675.682 | 160.4577 | 8836.1397 | 8.771e-05 | 30256.9663 | 16355.3247 | 2282.1785 | 42.2091 | 2324.3877 | 6511.752 | -9843.5727 | 0
| 60863651 | BBD | 2006 | 30243871 | 30246906 | 146.13 | 52622.2251 | 14193.6069 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 0.00015641 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 4069.7881 | 35.3099 | 4105.098 | 4.1145e-05 | 14193.6069 | 7672.3174 | 1070.5748 | 9.2884 | 1079.8632 | 3025.2348 | -4647.0826 | 0
| 60872966 | CHM | 1998 | 30613971 | 30086339 | 7424.06 | 43924.3002 | 721098.9478 | 0.0079465 | 0.0079465 | 0.0079465 | 0.0079465 | 0.0079465 | 0.0079465 | 0.0079465 | 0.0079465 | 0.0079465 | 0.0079465 | 0.0079465 | 0.0079465 | 0.0079465 | 0.0079465 | 0.0079465 | 0.0083608 | 0.0093513 | 0.010476 | 0.011754 | 0.013207 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 11226.4193 | 96793.0497 | 108019.469 | 0.0020904 | 721098.9478 | 389788.1672 | 2781.8195 | 23974.2697 | 26756.0892 | 81263.3798 | -308524.7874 | 0
| 60872973 | CHM | 1998 | 30315709 | 30613971 | 1052.79 | 43924.3002 | 102257.4927 | 0.0011269 | 0.0011269 | 0.0011269 | 0.0011269 | 0.0011269 | 0.0011269 | 0.0011269 | 0.0011269 | 0.0011269 | 0.0011269 | 0.0011269 | 0.0011269 | 0.0011269 | 0.0011269 | 0.0011269 | 0.0011856 | 0.0013261 | 0.0014856 | 0.0016668 | 0.0018729 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 1591.9946 | 1946.4569 | 3538.4515 | 0.00029643 | 102257.4927 | 55275.0226 | 394.4839 | 482.1098 | 876.5936 | 2661.8579 | -52613.1648 | 0
| 60876392 | CTN | 2010 | 30609792 | 30282332 | 205.33 | 45198.6405 | 19943.7029 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 0.00021978 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 2839.0323 | 69.7141 | 2908.7463 | 5.7814e-05 | 19943.7029 | 10780.5169 | 746.8221 | 18.3386 | 765.1608 | 2143.5855 | -8636.9314 | 0
| 60876546 | CTN | 2010 | 30228695 | 30609792 | 126.75 | 45198.6405 | 12311.2275 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 0.00013567 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1752.5351 | 26.5652 | 1779.1003 | 3.5688e-05 | 12311.2275 | 6654.8021 | 461.0125 | 6.9881 | 468.0006 | 1311.0997 | -5343.7025 | 0
| 60860099 | BBD | 2008 | 30265959 | 30265958 | 37.02 | 52622.2251 | 3595.7526 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 3.9625e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1031.0227 | 2.2662 | 1033.2889 | 1.0424e-05 | 3595.7526 | 1943.6747 | 271.2152 | 0.59612 | 271.8113 | 761.4775 | -1182.1972 | 0
| 60859677 | BBD | 2008 | 30265983 | 30266023 | 515 | 52622.2251 | 50021.95 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 0.00055124 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 14342.9634 | 438.5619 | 14781.5253 | 0.00014501 | 50021.95 | 27039.2354 | 3772.983 | 115.3658 | 3888.3488 | 10893.1765 | -16146.0589 | 0
| 60859679 | BBD | 2008 | 30266161 | 30266163 | 60.1 | 52622.2251 | 5837.513 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 6.4329e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1673.811 | 5.9726 | 1679.7837 | 1.6922e-05 | 5837.513 | 3155.4525 | 440.3035 | 1.5711 | 441.8746 | 1237.9091 | -1917.5434 | 0
| 60859680 | BBD | 2004 | 30224952 | 30224948 | 626.63 | 52622.2251 | 60864.5719 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 0.00067072 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 17451.9034 | 649.2901 | 18101.1935 | 0.00017644 | 60864.5719 | 32900.1866 | 4590.8046 | 170.7988 | 4761.6034 | 13339.5901 | -19560.5965 | 0
| 60859734 | BBD | 2008 | 30265958 | 30544876 | 16.43 | 52622.2251 | 1595.8459 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 1.7586e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 457.5815 | 0.44637 | 458.0279 | 4.6261e-06 | 1595.8459 | 862.6304 | 120.3691 | 0.11742 | 120.4866 | 337.5413 | -525.089 | 0
| 60859738 | BBD | 2008 | 30266044 | 30266052 | 949.33 | 52622.2251 | 92208.4229 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 0.0010161 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 26439.2469 | 1490.2225 | 27929.4694 | 0.0002673 | 92208.4229 | 49843.024 | 6954.963 | 392.0097 | 7346.9728 | 20582.4966 | -29260.5274 | 0
| 60859739 | BBD | 2006 | 30246897 | 30257966 | 427.81 | 52622.2251 | 41553.1853 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 0.00045791 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 11914.6935 | 302.6346 | 12217.3281 | 0.00012046 | 41553.1853 | 22461.4666 | 3134.2133 | 79.6094 | 3213.8227 | 9003.5054 | -13457.9612 | 0
| 60859741 | BBD | 2005 | 30238563 | 30238568 | 794.61 | 52622.2251 | 77180.4693 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 0.00085052 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 22130.2095 | 1044.0574 | 23174.2669 | 0.00022373 | 77180.4693 | 41719.7026 | 5821.4564 | 274.6442 | 6096.1006 | 17078.1663 | -24641.5363 | 0
| 60859771 | BBD | 2004 | 30224957 | 30224954 | 479.57 | 52622.2251 | 46580.6341 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 0.00051332 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 13356.2258 | 380.295 | 13736.5208 | 0.00013503 | 46580.6341 | 25179.041 | 3513.4164 | 100.0383 | 3613.4548 | 10123.066 | -15055.975 | 0
| 60859772 | BBD | 2008 | 30265962 | 30265960 | 59.79 | 52622.2251 | 5807.4027 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 6.3997e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1665.1778 | 5.9112 | 1671.0889 | 1.6835e-05 | 5807.4027 | 3139.1765 | 438.0323 | 1.555 | 439.5873 | 1231.5016 | -1907.6748 | 0
| 60859773 | BBD | 2005 | 30238576 | 30246902 | 146.88 | 52622.2251 | 14266.4544 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 0.00015722 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 4090.6818 | 35.6733 | 4126.3551 | 4.1356e-05 | 14266.4544 | 7711.6949 | 1076.0694 | 9.384 | 1085.4534 | 3040.9017 | -4670.7933 | 0
| 60859774 | BBD | 2008 | 30266029 | 30266027 | 65.16 | 52622.2251 | 6328.9908 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 6.9745e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1814.7327 | 7.0207 | 1821.7533 | 1.8347e-05 | 6328.9908 | 3421.1196 | 477.3739 | 1.8468 | 479.2207 | 1342.5326 | -2078.587 | 0
| 60859776 | BBD | 2005 | 30238568 | 30238570 | 303.4 | 52622.2251 | 29469.242 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 0.00032475 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 8449.8067 | 152.2114 | 8602.0181 | 8.5427e-05 | 29469.242 | 15929.5224 | 2222.7632 | 40.04 | 2262.8032 | 6339.215 | -9590.3074 | 0
| 60859777 | BBD | 2004 | 31030552 | 30266189 | 167.26 | 52622.2251 | 16245.9638 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 0.00017903 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 4658.2711 | 46.2596 | 4704.5307 | 4.7095e-05 | 16245.9638 | 8781.7136 | 1225.377 | 12.1688 | 1237.5457 | 3466.985 | -5314.7286 | 0
| 60859779 | BBD | 2007 | 30257967 | 30246901 | 267.26 | 52622.2251 | 25958.9638 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 0.00028607 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 7443.2944 | 118.1093 | 7561.4037 | 7.5251e-05 | 25958.9638 | 14032.0506 | 1957.995 | 31.0692 | 1989.0643 | 5572.3394 | -8459.7112 | 0
| 60859795 | CHA | 1999 | 32039829 | 33018658 | 23.69 | 48008.7507 | 2301.0097 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.5357e-05 | 2.7628e-05 | 3.0942e-05 | 3.471e-05 | 3.8996e-05 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 388.7649 | 0.96918 | 389.7341 | 6.6703e-06 | 2301.0097 | 1243.8048 | 97.8852 | 0.24411 | 98.1293 | 291.6048 | -952.2001 | 0
| 60859797 | BBD | 2008 | 30265981 | 30265962 | 2175.21 | 52622.2251 | 211278.1473 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 0.0023283 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 60580.5002 | 7823.8203 | 68404.3204 | 0.00061246 | 211278.1473 | 114205.8549 | 15935.9813 | 2058.0922 | 17994.0735 | 50410.2469 | -63795.608 | 0
| 60859798 | BBD | 2008 | 30265959 | 30265960 | 60.06 | 52622.2251 | 5833.6278 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 6.4286e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1672.6974 | 5.9647 | 1678.6621 | 1.6911e-05 | 5833.6278 | 3153.3524 | 440.0104 | 1.569 | 441.5794 | 1237.0826 | -1916.2697 | 0
| 60859799 | BBD | 2008 | 30266042 | 30266044 | 60 | 52622.2251 | 5827.8 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 6.4222e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1671.0244 | 5.9528 | 1676.9771 | 1.6894e-05 | 5827.8 | 3150.2022 | 439.5708 | 1.5659 | 441.1367 | 1235.8404 | -1914.3618 | 0
| 60859803 | BBD | 2004 | 30238557 | 30224980 | 1097.64 | 52622.2251 | 106613.7732 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 0.0011749 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 30569.7385 | 1992.2162 | 32561.9547 | 0.00030906 | 106613.7732 | 57629.7988 | 8041.5089 | 524.0615 | 8565.5704 | 23996.3843 | -33633.4145 | 0
| 60859804 | BBD | 2008 | 30266027 | 30266024 | 321 | 52622.2251 | 31178.73 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 0.00034359 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 8939.9881 | 170.3832 | 9110.3713 | 9.0382e-05 | 31178.73 | 16853.5817 | 2351.704 | 44.8201 | 2396.524 | 6713.8473 | -10139.7344 | 0
| 60859807 | BBD | 2008 | 30266060 | 30266070 | 969 | 52622.2251 | 94118.97 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 0.0010372 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 26987.0615 | 1552.6165 | 28539.678 | 0.00027284 | 94118.97 | 50875.7653 | 7099.069 | 408.4228 | 7507.4918 | 21032.1862 | -29843.5791 | 0
| 60859911 | BBD | 2004 | 30266169 | 30266174 | 132.1 | 52622.2251 | 12830.873 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 0.00014139 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 3679.0273 | 28.855 | 3707.8822 | 3.7195e-05 | 12830.873 | 6935.6951 | 967.7885 | 7.5905 | 975.3789 | 2732.5033 | -4203.1918 | 0
| 60860042 | BBD | 2004 | 30590487 | 30224957 | 210.97 | 52622.2251 | 20491.5161 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 0.00022582 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 5875.5935 | 73.5965 | 5949.19 | 5.9402e-05 | 20491.5161 | 11076.6359 | 1545.6043 | 19.3599 | 1564.9643 | 4384.2257 | -6692.4102 | 0
| 60860044 | BBD | 2005 | 30238558 | 30238561 | 410.1 | 52622.2251 | 39833.013 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 0.00043896 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 11421.4678 | 278.0971 | 11699.565 | 0.00011547 | 39833.013 | 21531.6319 | 3004.4667 | 73.1547 | 3077.6213 | 8621.9436 | -12909.6883 | 0
| 60860045 | BBD | 2007 | 33061889 | 30238558 | 43.37 | 52622.2251 | 4212.5281 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 4.6422e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1207.872 | 3.1102 | 1210.9823 | 1.2211e-05 | 4212.5281 | 2277.0711 | 317.7365 | 0.81817 | 318.5546 | 892.4277 | -1384.6435 | 0
| 60860047 | BBD | 2008 | 30266058 | 30266060 | 82 | 52622.2251 | 7964.66 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 8.777e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 2283.7341 | 11.1184 | 2294.8526 | 2.3088e-05 | 7964.66 | 4305.2763 | 600.7468 | 2.9248 | 603.6716 | 1691.181 | -2614.0953 | 0
| 60860052 | BBD | 2008 | 30266167 | 30266169 | 241.3 | 52622.2251 | 23437.469 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 0.00025828 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 6720.3166 | 96.2791 | 6816.5956 | 6.7942e-05 | 23437.469 | 12669.0631 | 1767.8074 | 25.3266 | 1793.134 | 5023.4616 | -7645.6015 | 0
| 60860055 | BBD | 2008 | 30266023 | 30266024 | 37 | 52622.2251 | 3593.81 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 3.9604e-05 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 1030.4659 | 2.2637 | 1032.7296 | 1.0418e-05 | 3593.81 | 1942.6247 | 271.0687 | 0.59548 | 271.6642 | 761.0654 | -1181.5593 | 0
| 60860058 | BBD | 2008 | 30590561 | 30225892 | 351.27 | 52622.2251 | 34118.8551 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 0.00037599 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 9783.0199 | 204.0322 | 9987.0521 | 9.8905e-05 | 34118.8551 | 18442.8587 | 2573.4675 | 53.6716 | 2627.1391 | 7359.9131 | -11082.9456 | 0
| 60860060 | BBD | 2008 | 30590486 | 30590561 | 244.18 | 52622.2251 | 23717.2034 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 0.00026136 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 6800.5087 | 98.5908 | 6899.0994 | 6.8753e-05 | 23717.2034 | 12820.2728 | 1788.9068 | 25.9348 | 1814.8416 | 5084.2579 | -7736.015 | 0
| 60860065 | BBD | 2004 | 30224954 | 30224952 | 282.35 | 52622.2251 | 27424.6555 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 0.00030222 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 7863.5614 | 131.8232 | 7995.3846 | 7.95e-05 | 27424.6555 | 14824.3264 | 2068.5471 | 34.6767 | 2103.2238 | 5892.1608 | -8932.1657 | 0
| 60860078 | BBD | 2008 | 30266033 | 30266042 | 823.3 | 52622.2251 | 79967.129 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 0.00088123 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 22929.2424 | 1120.8117 | 24050.054 | 0.00023181 | 79967.129 | 43226.0243 | 6031.6445 | 294.8348 | 6326.4793 | 17723.5748 | -25502.4496 | 0
| 60860083 | BBD | 2008 | 30266029 | 30266033 | 392 | 52622.2251 | 38074.96 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 0.00041958 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 10917.366 | 254.0907 | 11171.4567 | 0.00011037 | 38074.96 | 20581.3209 | 2871.8628 | 66.8397 | 2938.7025 | 8232.7542 | -12348.5667 | 0
| 60860086 | BBD | 2008 | 30266070 | 30266157 | 280 | 52622.2251 | 27196.4 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 0.0002997 | 33.747 | 33.766 | 34.015 | 34.125 | 33.936 | 33.83 | 34.108 | 34.533 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 34.388 | 7798.1223 | 129.6382 | 7927.7605 | 7.8838e-05 | 27196.4 | 14700.9435 | 2051.3306 | 34.1019 | 2085.4325 | 5842.328 | -8858.6155 | 0
| 60740548 | CTN | 2010 | 30282335 | 30228694 | 70.02 | 45198.6405 | 6801.0426 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 968.1462 | 8.107 | 976.2532 | 1.9715e-05 | 6801.0426 | 3676.286 | 254.6753 | 2.1326 | 256.8079 | 719.4453 | -2956.8407 | 0
| 60674418 | WMN | 1998 | 32141222 | 32141124 | 1318.53 | 61329.3035 | 128068.8189 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014113 | 0.0014849 | 0.0016608 | 0.0018605 | 0.0020875 | 0.0023456 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 35410.8154 | 3053.1013 | 38463.9167 | 0.00037125 | 128068.8189 | 69227.2681 | 8758.8858 | 756.2101 | 9515.0959 | 28948.8209 | -40278.4473 | 0
| 60674424 | WMN | 1998 | 33061528 | 32141222 | 2282.13 | 61329.3035 | 221663.2869 | 0.0024427 | 0.0024427 | 0.0024427 | 0.0024427 | 0.0024427 | 0.0024427 | 0.0024427 | 0.0024427 | 0.0024427 | 0.0024427 | 0.0024427 | 0.0024427 | 0.0024427 | 0.0024427 | 0.0024427 | 0.0025701 | 0.0028746 | 0.0032203 | 0.0036131 | 0.0040598 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 61289.5367 | 9146.2273 | 70435.764 | 0.00064257 | 221663.2869 | 119819.5152 | 15160.0009 | 2265.3912 | 17425.392 | 53010.372 | -66809.1432 | 0
| 60674442 | WMN | 1998 | 30243870 | 30243869 | 165.81 | 61329.3035 | 16105.1253 | 0.00017748 | 0.00017748 | 0.00017748 | 0.00017748 | 0.00017748 | 0.00017748 | 0.00017748 | 0.00017748 | 0.00017748 | 0.00017748 | 0.00017748 | 0.00017748 | 0.00017748 | 0.00017748 | 0.00017748 | 0.00018673 | 0.00020885 | 0.00023397 | 0.00026251 | 0.00029497 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 4453.048 | 48.2818 | 4501.3298 | 4.6686e-05 | 16105.1253 | 8705.5837 | 1101.4621 | 11.9587 | 1113.4208 | 3387.909 | -5317.6747 | 0
| 60674477 | WMN | 2000 | 33107013 | 33107011 | 73.5 | 61329.3035 | 7139.055 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 7.8672e-05 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 1856.0957 | 8.9329 | 1865.0286 | 2.0695e-05 | 7139.055 | 3858.9977 | 488.2544 | 2.3498 | 490.6043 | 1374.4243 | -2484.5733 | 0
| 60674500 | WMN | 1998 | 30243869 | 32140844 | 1884.8 | 61329.3035 | 183070.624 | 0.0020174 | 0.0020174 | 0.0020174 | 0.0020174 | 0.0020174 | 0.0020174 | 0.0020174 | 0.0020174 | 0.0020174 | 0.0020174 | 0.0020174 | 0.0020174 | 0.0020174 | 0.0020174 | 0.0020174 | 0.0021226 | 0.0023741 | 0.0026596 | 0.002984 | 0.003353 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 50618.7284 | 6238.6666 | 56857.395 | 0.00053069 | 183070.624 | 98958.3513 | 12520.5706 | 1545.2295 | 14065.8 | 42791.595 | -56166.7564 | 0
| 60674370 | WMN | 2018 | 30547413 | 30355658 | 22.19 | 61329.3035 | 2155.3147 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 2.3751e-05 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 560.3629 | 0.8142 | 561.1771 | 6.2479e-06 | 2155.3147 | 1165.0498 | 147.4063 | 0.21418 | 147.6205 | 413.5566 | -751.4932 | 0
| 60674374 | WMN | 1998 | 32140731 | 32140595 | 1821.55 | 61329.3035 | 176927.1515 | 0.0019497 | 0.0019497 | 0.0019497 | 0.0019497 | 0.0019497 | 0.0019497 | 0.0019497 | 0.0019497 | 0.0019497 | 0.0019497 | 0.0019497 | 0.0019497 | 0.0019497 | 0.0019497 | 0.0019497 | 0.0020514 | 0.0022944 | 0.0025703 | 0.0028839 | 0.0032405 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 48920.0633 | 5826.978 | 54747.0413 | 0.00051288 | 176927.1515 | 95637.5132 | 12100.406 | 1443.2602 | 13543.6662 | 41203.3751 | -54434.1381 | 0
| 60674397 | WMN | 1998 | 32140844 | 32140731 | 1735.52 | 61329.3035 | 168571.0576 | 0.0018576 | 0.0018576 | 0.0018576 | 0.0018576 | 0.0018576 | 0.0018576 | 0.0018576 | 0.0018576 | 0.0018576 | 0.0018576 | 0.0018576 | 0.0018576 | 0.0018576 | 0.0018576 | 0.0018576 | 0.0019545 | 0.0021861 | 0.0024489 | 0.0027477 | 0.0030874 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 46609.6299 | 5289.5722 | 51899.2021 | 0.00048866 | 168571.0576 | 91120.6483 | 11528.9159 | 1310.152 | 12839.0679 | 39060.1343 | -52060.514 | 0
| 60674404 | WMN | 1998 | 32141065 | 30243870 | 1240.09 | 61329.3035 | 120449.9417 | 0.0013274 | 0.0013274 | 0.0013274 | 0.0013274 | 0.0013274 | 0.0013274 | 0.0013274 | 0.0013274 | 0.0013274 | 0.0013274 | 0.0013274 | 0.0013274 | 0.0013274 | 0.0013274 | 0.0013274 | 0.0013966 | 0.001562 | 0.0017499 | 0.0019633 | 0.0022061 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 33304.2187 | 2700.6464 | 36004.8652 | 0.00034917 | 120449.9417 | 65108.9038 | 8237.8153 | 668.9118 | 8906.7271 | 27098.138 | -38010.7658 | 0
| 60698175 | CTN | 1955 | 30241530 | 30240483 | 5677.03 | 45198.6405 | 551409.9239 | 0.053127 | 0.057279 | 0.061771 | 0.06663 | 0.071888 | 0.077579 | 0.083738 | 0.090405 | 0.097623 | 0.10544 | 0.1139 | 0.12307 | 0.13299 | 0.14374 | 0.15539 | 0.16801 | 0.18169 | 0.18606 | 0.18606 | 0.18606 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1399782.7757 | 948879.3772 | 2348662.1529 | 0.0015985 | 551409.9239 | 298063.2052 | 20648.3792 | 14018.6056 | 34666.9848 | 2313995.168 | 2015931.9628 | 1
| 60708224 | CHA | 1999 | 33021817 | 30566848 | 128.45 | 48008.7507 | 12476.3485 | 0.00013749 | 0.00013749 | 0.00013749 | 0.00013749 | 0.00013749 | 0.00013749 | 0.00013749 | 0.00013749 | 0.00013749 | 0.00013749 | 0.00013749 | 0.00013749 | 0.00013749 | 0.00013749 | 0.00013749 | 0.00013749 | 0.0001498 | 0.00016777 | 0.0001882 | 0.00021144 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 2107.933 | 28.4933 | 2136.4263 | 3.6167e-05 | 12476.3485 | 6744.0578 | 530.7452 | 7.1768 | 537.922 | 1598.5042 | -5145.5536 | 0
| 60708284 | CHA | 1959 | 30566848 | 32038282 | 945.65 | 48008.7507 | 91850.9845 | 0.0089363 | 0.0096799 | 0.010488 | 0.011367 | 0.012323 | 0.013362 | 0.014492 | 0.015722 | 0.01706 | 0.018515 | 0.0201 | 0.021824 | 0.023701 | 0.025745 | 0.02797 | 0.030393 | 0.030993 | 0.030993 | 0.030993 | 0.030993 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 276042.3478 | 27382.8755 | 303425.2232 | 0.00026626 | 91850.9845 | 49649.8116 | 3907.3508 | 388.9764 | 4296.3273 | 299128.896 | 249479.0843 | 1
| 60722942 | CHM | 1998 | 32104907 | 32104799 | 253.38 | 43924.3002 | 24610.7994 | 0.00027121 | 0.00027121 | 0.00027121 | 0.00027121 | 0.00027121 | 0.00027121 | 0.00027121 | 0.00027121 | 0.00027121 | 0.00027121 | 0.00027121 | 0.00027121 | 0.00027121 | 0.00027121 | 0.00027121 | 0.00028535 | 0.00031916 | 0.00035754 | 0.00040115 | 0.00045076 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 383.1533 | 112.7474 | 495.9007 | 7.1343e-05 | 24610.7994 | 13303.3038 | 94.9423 | 27.9259 | 122.8682 | 373.0325 | -12930.2714 | 0
| 60722951 | CHM | 1998 | 32104799 | 32104376 | 3557.57 | 43924.3002 | 345546.7741 | 0.0038079 | 0.0038079 | 0.0038079 | 0.0038079 | 0.0038079 | 0.0038079 | 0.0038079 | 0.0038079 | 0.0038079 | 0.0038079 | 0.0038079 | 0.0038079 | 0.0038079 | 0.0038079 | 0.0038079 | 0.0040065 | 0.0044811 | 0.00502 | 0.0056324 | 0.0063288 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 5379.6402 | 22226.349 | 27605.9893 | 0.0010017 | 345546.7741 | 186784.4131 | 1333.0331 | 5505.1524 | 6838.1855 | 20767.8037 | -166016.6094 | 0
| 60740522 | CTN | 2010 | 30228694 | 30282335 | 70.02 | 45198.6405 | 6801.0426 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 7.4947e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 968.1462 | 8.107 | 976.2532 | 1.9715e-05 | 6801.0426 | 3676.286 | 254.6753 | 2.1326 | 256.8079 | 719.4453 | -2956.8407 | 0
| 60674631 | WMN | 1998 | 32140595 | 30312136 | 327.22 | 61329.3035 | 31782.8786 | 0.00035025 | 0.00035025 | 0.00035025 | 0.00035025 | 0.00035025 | 0.00035025 | 0.00035025 | 0.00035025 | 0.00035025 | 0.00035025 | 0.00035025 | 0.00035025 | 0.00035025 | 0.00035025 | 0.00035025 | 0.00036851 | 0.00041216 | 0.00046173 | 0.00051806 | 0.00058212 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 8787.9218 | 188.0361 | 8975.9579 | 9.2134e-05 | 31782.8786 | 17180.1527 | 2173.6954 | 46.5738 | 2220.2693 | 6755.6887 | -10424.464 | 0
| 60674699 | WMN | 1998 | 30552207 | 33061528 | 3314.25 | 61329.3035 | 321913.1025 | 0.0035475 | 0.0035475 | 0.0035475 | 0.0035475 | 0.0035475 | 0.0035475 | 0.0035475 | 0.0035475 | 0.0035475 | 0.0035475 | 0.0035475 | 0.0035475 | 0.0035475 | 0.0035475 | 0.0035475 | 0.0037324 | 0.0041746 | 0.0046767 | 0.0052471 | 0.005896 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 89008.4389 | 19289.9775 | 108298.4164 | 0.00093318 | 321913.1025 | 174009.2932 | 22016.2887 | 4777.8551 | 26794.1438 | 81504.2726 | -92505.0206 | 0
| 60674701 | WMN | 1998 | 32141124 | 32141065 | 829.95 | 61329.3035 | 80613.0435 | 0.00088835 | 0.00088835 | 0.00088835 | 0.00088835 | 0.00088835 | 0.00088835 | 0.00088835 | 0.00088835 | 0.00088835 | 0.00088835 | 0.00088835 | 0.00088835 | 0.00088835 | 0.00088835 | 0.00088835 | 0.00093467 | 0.0010454 | 0.0011711 | 0.001314 | 0.0014765 | 25.014 | 25.256 | 25.701 | 26.019 | 26.042 | 26.139 | 26.601 | 27.202 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 27.223 | 22289.3702 | 1209.6647 | 23499.0349 | 0.00023368 | 80613.0435 | 43575.1717 | 5513.2892 | 299.6169 | 5812.9061 | 17686.1287 | -25889.043 | 0
| 60468509 | CTN | 2014 | 30296924 | 30319674 | 585.2 | 45198.6405 | 56840.476 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 0.00062638 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 8091.3931 | 566.2722 | 8657.6653 | 0.00016477 | 56840.476 | 30724.972 | 2128.4777 | 148.9605 | 2277.4381 | 6380.2272 | -24344.7448 | 0
| 60468506 | CTN | 2011 | 30296926 | 31037381 | 52.98 | 45198.6405 | 5145.9474 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 5.6708e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 732.5398 | 4.6413 | 737.1811 | 1.4917e-05 | 5145.9474 | 2781.6285 | 192.6978 | 1.2209 | 193.9187 | 543.2624 | -2238.3662 | 0
| 60468510 | CTN | 2014 | 30319674 | 30296918 | 30 | 45198.6405 | 2913.9 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 3.2111e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 414.8011 | 1.4882 | 416.2893 | 8.447e-06 | 2913.9 | 1575.1011 | 109.1154 | 0.39148 | 109.5069 | 306.7825 | -1268.3186 | 0
| 60468511 | CTN | 2014 | 30296918 | 30296912 | 198.17 | 45198.6405 | 19248.2521 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 0.00021211 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 2740.0437 | 64.9371 | 2804.9808 | 5.5798e-05 | 19248.2521 | 10404.5928 | 720.7799 | 17.082 | 737.8619 | 2067.1189 | -8337.4739 | 0
| 60468462 | CTN | 2014 | 30296807 | 30296817 | 1120.46 | 45198.6405 | 108830.2798 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 0.0011993 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 15492.2819 | 2075.9143 | 17568.1962 | 0.00031548 | 108830.2798 | 58827.9257 | 4075.3146 | 546.0786 | 4621.3931 | 12946.803 | -45881.1226 | 0
| 60468461 | CTN | 2014 | 30296806 | 30296807 | 35.31 | 45198.6405 | 3429.6603 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 3.7795e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 488.2216 | 2.0616 | 490.2833 | 9.9421e-06 | 3429.6603 | 1853.894 | 128.4288 | 0.54232 | 128.9711 | 361.3121 | -1492.5819 | 0
| 60468460 | CTN | 2014 | 30296788 | 30296806 | 2059.13 | 45198.6405 | 200003.2969 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 0.002204 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 28470.9937 | 7011.066 | 35482.0597 | 0.00057978 | 200003.2969 | 108111.2638 | 7489.4262 | 1844.2932 | 9333.7194 | 26148.3403 | -81962.9235 | 0
| 60467905 | CTN | 2014 | 30296732 | 30296994 | 108.17 | 45198.6405 | 10506.5521 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 0.00011578 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1495.6403 | 19.3478 | 1514.9881 | 3.0457e-05 | 10506.5521 | 5679.2895 | 393.4337 | 5.0895 | 398.5233 | 1116.4648 | -4562.8247 | 0
| 60468607 | CTN | 2014 | 30296199 | 30296196 | 113.82 | 45198.6405 | 11055.3366 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 0.00012183 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1573.7538 | 21.4217 | 1595.1754 | 3.2048e-05 | 11055.3366 | 5975.9335 | 413.9838 | 5.6351 | 419.6189 | 1175.5566 | -4800.377 | 0
| 60468608 | CTN | 2014 | 30296196 | 30296190 | 661.44 | 45198.6405 | 64245.6672 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 0.00070798 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 9145.5442 | 723.4319 | 9868.9761 | 0.00018624 | 64245.6672 | 34727.8289 | 2405.7762 | 190.302 | 2596.0782 | 7272.8979 | -27454.931 | 0
| 60468609 | CTN | 2014 | 30296190 | 30296187 | 96.43 | 45198.6405 | 9366.2459 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 0.00010322 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1333.3161 | 15.376 | 1348.6921 | 2.7151e-05 | 9366.2459 | 5062.8999 | 350.7333 | 4.0447 | 354.778 | 993.9142 | -4068.9858 | 0
| 60467904 | CTN | 2011 | 30296727 | 30296732 | 378.9 | 45198.6405 | 36802.557 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 0.00040556 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 5238.9393 | 237.3918 | 5476.331 | 0.00010668 | 36802.557 | 19893.5268 | 1378.1275 | 62.447 | 1440.5745 | 4035.7566 | -15857.7702 | 0
| 60467584 | CTN | 2010 | 30228695 | 30282332 | 332.08 | 45198.6405 | 32254.9304 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 0.00035545 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 4591.5803 | 182.3487 | 4773.929 | 9.3502e-05 | 32254.9304 | 17435.319 | 1207.8347 | 47.9676 | 1255.8023 | 3518.1267 | -13917.1923 | 0
| 60467585 | CTN | 2010 | 30282332 | 33012889 | 69 | 45198.6405 | 6701.97 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 7.3855e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 954.0426 | 7.8725 | 961.9152 | 1.9428e-05 | 6701.97 | 3622.7325 | 250.9654 | 2.0709 | 253.0363 | 708.8788 | -2913.8537 | 0
| 60467668 | CHM | 2005 | 30229785 | 30229786 | 32.7 | 43924.3002 | 3176.151 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 3.5001e-05 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 46.5789 | 1.7681 | 48.347 | 9.2072e-06 | 3176.151 | 1716.8602 | 12.2528 | 0.46511 | 12.7179 | 35.6291 | -1681.2311 | 0
| 60467669 | CHM | 2005 | 30229786 | 30229790 | 477.71 | 43924.3002 | 46399.9723 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 0.00051132 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 680.4651 | 377.3507 | 1057.8157 | 0.00013451 | 46399.9723 | 25081.3848 | 178.9995 | 99.2638 | 278.2633 | 779.5524 | -24301.8324 | 0
| 60467670 | CHM | 2005 | 30229790 | 30229792 | 129.4 | 43924.3002 | 12568.622 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 0.00013851 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 184.3221 | 27.6877 | 212.0098 | 3.6435e-05 | 12568.622 | 6793.936 | 48.4866 | 7.2833 | 55.7699 | 156.2398 | -6637.6962 | 0
| 60467671 | CHM | 2005 | 30229792 | 30229946 | 1114.76 | 43924.3002 | 108276.6388 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 0.0011932 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 1587.8987 | 2054.8453 | 3642.7439 | 0.00031388 | 108276.6388 | 58528.6565 | 417.7042 | 540.5367 | 958.2409 | 2684.503 | -55844.1535 | 0
| 60467672 | CHM | 2005 | 30229946 | 33049129 | 550.92 | 43924.3002 | 53510.8596 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 0.00058969 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 784.7483 | 501.873 | 1286.6213 | 0.00015512 | 53510.8596 | 28925.1565 | 206.4315 | 132.0199 | 338.4515 | 948.1698 | -27976.9866 | 0
| 60467781 | CTN | 1981 | 33011837 | 33011796 | 285.04 | 45198.6405 | 27685.9352 | 0.0003051 | 0.0003051 | 0.0003051 | 0.0003051 | 0.0003051 | 0.0003051 | 0.0003051 | 0.0003051 | 0.0003051 | 0.0003051 | 0.0003051 | 0.0003051 | 0.00031988 | 0.00034647 | 0.00037558 | 0.00040746 | 0.0004424 | 0.0004807 | 0.0005227 | 0.00056878 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 4445.4248 | 151.4758 | 4596.9006 | 8.0257e-05 | 27685.9352 | 14965.5605 | 1036.7417 | 35.3406 | 1072.0824 | 3524.8183 | -11440.7422 | 0
| 60467782 | CTN | 1981 | 33011796 | 33011789 | 20.41 | 45198.6405 | 1982.4233 | 2.1846e-05 | 2.1846e-05 | 2.1846e-05 | 2.1846e-05 | 2.1846e-05 | 2.1846e-05 | 2.1846e-05 | 2.1846e-05 | 2.1846e-05 | 2.1846e-05 | 2.1846e-05 | 2.1846e-05 | 2.2904e-05 | 2.4808e-05 | 2.6893e-05 | 2.9176e-05 | 3.1677e-05 | 3.442e-05 | 3.7427e-05 | 4.0727e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 318.3105 | 0.77664 | 319.0871 | 5.7467e-06 | 1982.4233 | 1071.5938 | 74.2348 | 0.1812 | 74.416 | 244.6711 | -826.9227 | 0
| 60467783 | CTN | 1981 | 33011789 | 33011741 | 1079.6 | 45198.6405 | 104861.548 | 0.0011556 | 0.0011556 | 0.0011556 | 0.0011556 | 0.0011556 | 0.0011556 | 0.0011556 | 0.0011556 | 0.0011556 | 0.0011556 | 0.0011556 | 0.0011556 | 0.0012115 | 0.0013122 | 0.0014225 | 0.0015433 | 0.0016756 | 0.0018207 | 0.0019797 | 0.0021543 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 16837.2276 | 2172.9899 | 19010.2175 | 0.00030398 | 104861.548 | 56682.638 | 3926.6994 | 506.9769 | 4433.6763 | 14576.5412 | -42106.0968 | 0
| 60467785 | CTN | 1981 | 32025856 | 33011670 | 503.6 | 45198.6405 | 48914.668 | 0.00053904 | 0.00053904 | 0.00053904 | 0.00053904 | 0.00053904 | 0.00053904 | 0.00053904 | 0.00053904 | 0.00053904 | 0.00053904 | 0.00053904 | 0.00053904 | 0.00056515 | 0.00061212 | 0.00066355 | 0.00071989 | 0.00078161 | 0.00084928 | 0.00092349 | 0.0010049 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 7854.0479 | 472.8284 | 8326.8763 | 0.0001418 | 48914.668 | 26440.697 | 1831.6838 | 110.3148 | 1941.9986 | 6384.8777 | -20055.8193 | 0
| 60467786 | CTN | 1981 | 33011670 | 33011639 | 132.29 | 45198.6405 | 12849.3277 | 0.0001416 | 0.0001416 | 0.0001416 | 0.0001416 | 0.0001416 | 0.0001416 | 0.0001416 | 0.0001416 | 0.0001416 | 0.0001416 | 0.0001416 | 0.0001416 | 0.00014846 | 0.0001608 | 0.00017431 | 0.00018911 | 0.00020532 | 0.0002231 | 0.00024259 | 0.00026398 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 2063.1702 | 32.6277 | 2095.7979 | 3.7248e-05 | 12849.3277 | 6945.6708 | 481.1625 | 7.6123 | 488.7748 | 1607.0231 | -5338.6477 | 0
| 60467787 | CTN | 1981 | 33011639 | 33011624 | 154.31 | 45198.6405 | 14988.1303 | 0.00016517 | 0.00016517 | 0.00016517 | 0.00016517 | 0.00016517 | 0.00016517 | 0.00016517 | 0.00016517 | 0.00016517 | 0.00016517 | 0.00016517 | 0.00016517 | 0.00017317 | 0.00018756 | 0.00020332 | 0.00022058 | 0.0002395 | 0.00026023 | 0.00028297 | 0.00030792 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 2406.5856 | 44.3935 | 2450.9791 | 4.3448e-05 | 14988.1303 | 8101.795 | 561.2532 | 10.3574 | 571.6106 | 1879.3685 | -6222.4265 | 0
| 60467788 | CTN | 1981 | 33011624 | 33011608 | 136.19 | 45198.6405 | 13228.1347 | 0.00014577 | 0.00014577 | 0.00014577 | 0.00014577 | 0.00014577 | 0.00014577 | 0.00014577 | 0.00014577 | 0.00014577 | 0.00014577 | 0.00014577 | 0.00014577 | 0.00015283 | 0.00016554 | 0.00017945 | 0.00019468 | 0.00021137 | 0.00022967 | 0.00024974 | 0.00027176 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 2123.9897 | 34.5798 | 2158.5694 | 3.8346e-05 | 13228.1347 | 7150.4339 | 495.3475 | 8.0678 | 503.4153 | 1655.1541 | -5495.2798 | 0
| 60467837 | CTN | 2010 | 30282341 | 30282338 | 238.54 | 45198.6405 | 23169.3902 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 0.00025532 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 3298.2187 | 94.0889 | 3392.3076 | 6.7165e-05 | 23169.3902 | 12524.1538 | 867.6129 | 24.7506 | 892.3634 | 2499.9442 | -10024.2097 | 0
| 60467838 | CTN | 2010 | 30282338 | 30282337 | 65 | 45198.6405 | 6313.45 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 898.7367 | 6.9862 | 905.7229 | 1.8302e-05 | 6313.45 | 3412.719 | 236.4167 | 1.8378 | 238.2545 | 667.4684 | -2745.2506 | 0
| 60467841 | CTN | 2010 | 30228694 | 30228693 | 116.7 | 45198.6405 | 11335.071 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 0.00012491 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1613.5791 | 22.5195 | 1636.0986 | 3.2859e-05 | 11335.071 | 6127.1433 | 424.4589 | 5.9239 | 430.3827 | 1205.7159 | -4921.4273 | 0
| 60467903 | CTN | 2011 | 30296728 | 30296727 | 23.96 | 45198.6405 | 2327.2348 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 2.5646e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 331.288 | 0.94927 | 332.2373 | 6.7463e-06 | 2327.2348 | 1257.9807 | 87.1468 | 0.24971 | 87.3965 | 244.8408 | -1013.14 | 0
| 60469531 | CHM | 1998 | 30082796 | 30082794 | 377.95 | 43924.3002 | 36710.2835 | 0.00040455 | 0.00040455 | 0.00040455 | 0.00040455 | 0.00040455 | 0.00040455 | 0.00040455 | 0.00040455 | 0.00040455 | 0.00040455 | 0.00040455 | 0.00040455 | 0.00040455 | 0.00040455 | 0.00040455 | 0.00042564 | 0.00047606 | 0.00053332 | 0.00059837 | 0.00067236 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 571.5233 | 250.859 | 822.3823 | 0.00010642 | 36710.2835 | 19843.6486 | 141.6191 | 62.1343 | 203.7534 | 618.6289 | -19225.0197 | 0
| 60469532 | CHM | 1998 | 30082794 | 30082791 | 313.52 | 43924.3002 | 30452.1976 | 0.00033558 | 0.00033558 | 0.00033558 | 0.00033558 | 0.00033558 | 0.00033558 | 0.00033558 | 0.00033558 | 0.00033558 | 0.00033558 | 0.00033558 | 0.00033558 | 0.00033558 | 0.00033558 | 0.00033558 | 0.00035308 | 0.00039491 | 0.0004424 | 0.00049637 | 0.00055774 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 474.0952 | 172.6204 | 646.7156 | 8.8276e-05 | 30452.1976 | 16460.8565 | 117.477 | 42.7556 | 160.2326 | 486.4831 | -15974.3734 | 0
| 60469533 | CHM | 1998 | 30082791 | 30082784 | 266.64 | 43924.3002 | 25898.7432 | 0.0002854 | 0.0002854 | 0.0002854 | 0.0002854 | 0.0002854 | 0.0002854 | 0.0002854 | 0.0002854 | 0.0002854 | 0.0002854 | 0.0002854 | 0.0002854 | 0.0002854 | 0.0002854 | 0.0002854 | 0.00030028 | 0.00033586 | 0.00037625 | 0.00042215 | 0.00047434 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 403.2045 | 124.8568 | 528.0613 | 7.5076e-05 | 25898.7432 | 13999.4985 | 99.9109 | 30.9252 | 130.8361 | 397.2252 | -13602.2733 | 0
| 60469535 | CHM | 1998 | 30317624 | 32104907 | 3168.38 | 43924.3002 | 307744.7494 | 0.0033913 | 0.0033913 | 0.0033913 | 0.0033913 | 0.0033913 | 0.0033913 | 0.0033913 | 0.0033913 | 0.0033913 | 0.0033913 | 0.0033913 | 0.0033913 | 0.0033913 | 0.0033913 | 0.0033913 | 0.0035682 | 0.0039909 | 0.0044708 | 0.0050162 | 0.0056365 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 4791.1201 | 17629.3281 | 22420.4482 | 0.0008921 | 307744.7494 | 166350.6267 | 1187.2023 | 4366.5352 | 5553.7375 | 16866.7106 | -149483.916 | 0
| 60469539 | CHM | 1998 | 32104383 | 30081687 | 770.81 | 43924.3002 | 74868.7753 | 0.00082505 | 0.00082505 | 0.00082505 | 0.00082505 | 0.00082505 | 0.00082505 | 0.00082505 | 0.00082505 | 0.00082505 | 0.00082505 | 0.00082505 | 0.00082505 | 0.00082505 | 0.00082505 | 0.00082505 | 0.00086807 | 0.00097091 | 0.0010877 | 0.0012204 | 0.0013713 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 1165.5938 | 1043.4124 | 2209.0063 | 0.00021703 | 74868.7753 | 40470.1224 | 288.825 | 258.4384 | 547.2635 | 1661.7428 | -38808.3797 | 0
| 60469540 | CHM | 1998 | 30081687 | 30081653 | 2787.83 | 43924.3002 | 270781.9279 | 0.002984 | 0.002984 | 0.002984 | 0.002984 | 0.002984 | 0.002984 | 0.002984 | 0.002984 | 0.002984 | 0.002984 | 0.002984 | 0.002984 | 0.002984 | 0.002984 | 0.002984 | 0.0031396 | 0.0035115 | 0.0039338 | 0.0044137 | 0.0049595 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 4215.6652 | 13648.7801 | 17864.4453 | 0.00078496 | 270781.9279 | 146370.4693 | 1044.609 | 3380.6096 | 4425.2186 | 13439.2267 | -132931.2426 | 0
| 60469541 | CHM | 1998 | 30081653 | 30081648 | 138.72 | 43924.3002 | 13473.8736 | 0.00014848 | 0.00014848 | 0.00014848 | 0.00014848 | 0.00014848 | 0.00014848 | 0.00014848 | 0.00014848 | 0.00014848 | 0.00014848 | 0.00014848 | 0.00014848 | 0.00014848 | 0.00014848 | 0.00014848 | 0.00015622 | 0.00017473 | 0.00019574 | 0.00021962 | 0.00024678 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 209.7675 | 33.7939 | 243.5614 | 3.9059e-05 | 13473.8736 | 7283.2675 | 51.9788 | 8.3703 | 60.3491 | 183.2123 | -7100.0552 | 0
| 60469542 | CHM | 1937 | 30081648 | 30081556 | 3620.45 | 43924.3002 | 351654.3085 | 0.033869 | 0.03596 | 0.038185 | 0.040554 | 0.043077 | 0.045763 | 0.048623 | 0.05167 | 0.054915 | 0.058371 | 0.062053 | 0.065975 | 0.070154 | 0.074607 | 0.079351 | 0.084407 | 0.089795 | 0.095538 | 0.10166 | 0.10818 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 79442.3875 | 334725.0734 | 414167.4609 | 0.0010194 | 351654.3085 | 190085.825 | 1356.5944 | 5701.4793 | 7058.0737 | 407109.3872 | 217023.5622 | 1
| 60469543 | CHM | 1937 | 30081556 | 30081481 | 3066.46 | 43924.3002 | 297845.2598 | 0.028687 | 0.030457 | 0.032342 | 0.034349 | 0.036485 | 0.03876 | 0.041183 | 0.043763 | 0.046512 | 0.049439 | 0.052558 | 0.05588 | 0.059419 | 0.06319 | 0.067209 | 0.071491 | 0.076055 | 0.080919 | 0.086103 | 0.091629 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 67286.3605 | 240125.2035 | 307411.564 | 0.00086341 | 297845.2598 | 160999.4832 | 1149.0126 | 4090.1294 | 5239.142 | 302172.4221 | 141172.9389 | 1
| 60469544 | CHM | 1937 | 30081481 | 30081443 | 1605.07 | 43924.3002 | 155900.4491 | 0.015015 | 0.015942 | 0.016929 | 0.017979 | 0.019097 | 0.020288 | 0.021556 | 0.022907 | 0.024346 | 0.025878 | 0.02751 | 0.029249 | 0.031102 | 0.033076 | 0.035179 | 0.037421 | 0.039809 | 0.042355 | 0.045069 | 0.047961 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 35219.5425 | 65788.6676 | 101008.2101 | 0.00045193 | 155900.4491 | 84271.5837 | 601.425 | 1120.5994 | 1722.0244 | 99286.1857 | 15014.602 | 1
| 60469545 | CHM | 1937 | 30081443 | 30081421 | 991.95 | 43924.3002 | 96348.1035 | 0.0092796 | 0.0098524 | 0.010462 | 0.011111 | 0.011802 | 0.012538 | 0.013322 | 0.014157 | 0.015046 | 0.015993 | 0.017002 | 0.018076 | 0.019221 | 0.020441 | 0.021741 | 0.023126 | 0.024603 | 0.026176 | 0.027853 | 0.029641 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 21766.0446 | 25127.1193 | 46893.1639 | 0.0002793 | 96348.1035 | 52080.7176 | 371.6869 | 427.9983 | 799.6852 | 46093.4787 | -5987.2389 | 0
| 60469546 | CHM | 1937 | 30081421 | 30081390 | 1207.26 | 43924.3002 | 117261.1638 | 0.011294 | 0.011991 | 0.012733 | 0.013523 | 0.014364 | 0.01526 | 0.016214 | 0.01723 | 0.018312 | 0.019464 | 0.020692 | 0.022 | 0.023393 | 0.024878 | 0.02646 | 0.028146 | 0.029943 | 0.031858 | 0.033899 | 0.036074 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 26490.5238 | 37219.0052 | 63709.5289 | 0.00033992 | 117261.1638 | 63385.2182 | 452.3643 | 633.9632 | 1086.3275 | 62623.2014 | -762.0167 | 0
| 60469547 | CHM | 1937 | 30081390 | 30079525 | 2081.87 | 43924.3002 | 202212.0331 | 0.019476 | 0.020678 | 0.021957 | 0.02332 | 0.02477 | 0.026315 | 0.02796 | 0.029712 | 0.031578 | 0.033565 | 0.035682 | 0.037938 | 0.040341 | 0.042901 | 0.045629 | 0.048537 | 0.051635 | 0.054937 | 0.058457 | 0.062209 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 45681.8139 | 110680.3061 | 156362.12 | 0.00058618 | 202212.0331 | 109305.1904 | 780.0835 | 1885.2531 | 2665.3365 | 153696.7835 | 44391.5931 | 1
| 60469548 | CHM | 1937 | 30079525 | 30079474 | 1686.52 | 43924.3002 | 163811.6876 | 0.015777 | 0.016751 | 0.017788 | 0.018891 | 0.020066 | 0.021318 | 0.02265 | 0.024069 | 0.025581 | 0.027191 | 0.028906 | 0.030733 | 0.03268 | 0.034754 | 0.036964 | 0.039319 | 0.041829 | 0.044505 | 0.047356 | 0.050395 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 37006.7742 | 72635.0315 | 109641.8057 | 0.00047487 | 163811.6876 | 88547.9832 | 631.9446 | 1237.2157 | 1869.1603 | 107772.6454 | 19224.6623 | 1
| 60469549 | CHM | 1937 | 30079474 | 30079449 | 1745.49 | 43924.3002 | 169539.4437 | 0.016329 | 0.017337 | 0.01841 | 0.019552 | 0.020768 | 0.022063 | 0.023442 | 0.024911 | 0.026475 | 0.028142 | 0.029917 | 0.031808 | 0.033823 | 0.035969 | 0.038257 | 0.040694 | 0.043292 | 0.046061 | 0.049012 | 0.052157 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 38300.7342 | 77803.2731 | 116104.0073 | 0.00049147 | 169539.4437 | 91644.1069 | 654.0408 | 1325.248 | 1979.2888 | 114124.7184 | 22480.6116 | 1
| 60469550 | CHM | 1937 | 30079449 | 33049427 | 1151.82 | 43924.3002 | 111876.2766 | 0.010775 | 0.01144 | 0.012148 | 0.012902 | 0.013705 | 0.014559 | 0.015469 | 0.016438 | 0.017471 | 0.01857 | 0.019742 | 0.020989 | 0.022319 | 0.023736 | 0.025245 | 0.026854 | 0.028568 | 0.030395 | 0.032342 | 0.034418 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 25274.0215 | 33879.1393 | 59153.1608 | 0.00032431 | 111876.2766 | 60474.4313 | 431.5907 | 577.0742 | 1008.6649 | 58144.4958 | -2329.9355 | 0
| 60469551 | CHM | 1937 | 33049427 | 33049269 | 8799.98 | 43924.3002 | 854742.0574 | 0.082323 | 0.087404 | 0.092813 | 0.098572 | 0.1047 | 0.11123 | 0.11819 | 0.12559 | 0.13348 | 0.14188 | 0.15083 | 0.16036 | 0.17052 | 0.18134 | 0.19287 | 0.20516 | 0.21826 | 0.23222 | 0.2471 | 0.26295 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 193095.1737 | 1977545.6057 | 2170640.7794 | 0.0024778 | 854742.0574 | 462028.6038 | 3297.3812 | 33684.1669 | 36981.5482 | 2133659.2313 | 1671630.6275 | 1
| 60469554 | CHM | 1937 | 33049217 | 33049212 | 189.63 | 43924.3002 | 18418.7619 | 0.001774 | 0.0018835 | 0.002 | 0.0021241 | 0.0022562 | 0.0023969 | 0.0025468 | 0.0027063 | 0.0028763 | 0.0030573 | 0.0032502 | 0.0034556 | 0.0036745 | 0.0039077 | 0.0041562 | 0.004421 | 0.0047033 | 0.005004 | 0.0053246 | 0.0056664 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 4160.9911 | 918.2845 | 5079.2755 | 5.3393e-05 | 18418.7619 | 9956.214 | 71.055 | 15.6414 | 86.6964 | 4992.5791 | -4963.6349 | 0
| 60469555 | CHM | 1937 | 33049212 | 33049131 | 1629.98 | 43924.3002 | 158319.9574 | 0.015248 | 0.016189 | 0.017191 | 0.018258 | 0.019394 | 0.020603 | 0.021891 | 0.023263 | 0.024723 | 0.026279 | 0.027937 | 0.029703 | 0.031584 | 0.033589 | 0.035725 | 0.038001 | 0.040427 | 0.043013 | 0.045768 | 0.048706 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 35766.1349 | 67846.5376 | 103612.6725 | 0.00045895 | 158319.9574 | 85579.4426 | 610.7588 | 1155.6518 | 1766.4106 | 101846.2619 | 16266.8193 | 1
| 60469559 | CTN | 2014 | 31037418 | 31037417 | 54.64 | 45198.6405 | 5307.1832 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 5.8485e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 755.492 | 4.9367 | 760.4287 | 1.5385e-05 | 5307.1832 | 2868.7841 | 198.7355 | 1.2986 | 200.0341 | 560.3946 | -2308.3896 | 0
| 60469899 | CTN | 2014 | 30296163 | 30296164 | 40.32 | 45198.6405 | 3916.2816 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 4.3157e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 557.4929 | 2.6882 | 560.1811 | 1.1353e-05 | 3916.2816 | 2116.9359 | 146.6511 | 0.70714 | 147.3582 | 412.8229 | -1704.113 | 0
| 60470115 | CTN | 2014 | 31037418 | 30323209 | 13.82 | 45198.6405 | 1342.3366 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 1.4792e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 191.0855 | 0.31582 | 191.4013 | 3.8912e-06 | 1342.3366 | 725.5966 | 50.2658 | 0.083077 | 50.3489 | 141.0524 | -584.5442 | 0
| 60470150 | CTN | 1981 | 33012013 | 33012889 | 513.09 | 45198.6405 | 49836.4317 | 0.0005492 | 0.0005492 | 0.0005492 | 0.0005492 | 0.0005492 | 0.0005492 | 0.0005492 | 0.0005492 | 0.0005492 | 0.0005492 | 0.0005492 | 0.0005492 | 0.0005758 | 0.00062366 | 0.00067606 | 0.00073345 | 0.00079634 | 0.00086528 | 0.00094089 | 0.0010238 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 8002.0544 | 490.8167 | 8492.871 | 0.00014447 | 49836.4317 | 26938.954 | 1866.2006 | 114.5116 | 1980.7122 | 6512.1588 | -20426.7952 | 0
| 60470187 | CTN | 2014 | 30296817 | 30296861 | 20.24 | 45198.6405 | 1965.9112 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 279.8522 | 0.67739 | 280.5296 | 5.6989e-06 | 1965.9112 | 1062.6682 | 73.6165 | 0.17819 | 73.7947 | 206.7349 | -855.9333 | 0
| 60470188 | CTN | 2014 | 30296861 | 30296870 | 950.8 | 45198.6405 | 92351.204 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 0.0010177 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 13146.4356 | 1494.8405 | 14641.2761 | 0.00026771 | 92351.204 | 49920.204 | 3458.2306 | 393.2247 | 3851.4553 | 10789.8208 | -39130.3832 | 0
| 60470198 | CTN | 2014 | 30296788 | 30296766 | 1663.74 | 45198.6405 | 161599.0662 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 0.0017808 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 23004.0566 | 4577.0699 | 27581.1265 | 0.00046845 | 161599.0662 | 87351.9564 | 6051.3216 | 1204.019 | 7255.3407 | 20325.7858 | -67026.1706 | 0
| 60469530 | CHM | 1998 | 33051758 | 30082796 | 2015.95 | 43924.3002 | 195809.2235 | 0.0021578 | 0.0021578 | 0.0021578 | 0.0021578 | 0.0021578 | 0.0021578 | 0.0021578 | 0.0021578 | 0.0021578 | 0.0021578 | 0.0021578 | 0.0021578 | 0.0021578 | 0.0021578 | 0.0021578 | 0.0022703 | 0.0025393 | 0.0028447 | 0.0031917 | 0.0035863 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 3048.4536 | 7137.0837 | 10185.5373 | 0.00056762 | 195809.2235 | 105844.1683 | 755.383 | 1767.7545 | 2523.1376 | 7662.3997 | -98181.7685 | 0
| 60468611 | CTN | 2011 | 30296173 | 30296172 | 33.43 | 45198.6405 | 3247.0559 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 462.2273 | 1.8479 | 464.0752 | 9.4127e-06 | 3247.0559 | 1755.1877 | 121.5909 | 0.48611 | 122.077 | 341.9982 | -1413.1895 | 0
| 60468612 | CTN | 2011 | 30296172 | 30296164 | 884.04 | 45198.6405 | 85866.8052 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 0.00094625 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 12223.3606 | 1292.2907 | 13515.6513 | 0.00024891 | 85866.8052 | 46415.079 | 3215.4125 | 339.9431 | 3555.3556 | 9960.2957 | -36454.7833 | 0
| 60469186 | CTN | 2011 | 30296143 | 30296142 | 20.92 | 45198.6405 | 2031.9596 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 289.255 | 0.72367 | 289.9787 | 5.8903e-06 | 2031.9596 | 1098.3705 | 76.0898 | 0.19036 | 76.2802 | 213.6985 | -884.672 | 0
| 60469205 | CTN | 2014 | 31037382 | 30296926 | 49.27 | 45198.6405 | 4785.5951 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 5.2737e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 681.2422 | 4.014 | 685.2562 | 1.3873e-05 | 4785.5951 | 2586.841 | 179.2039 | 1.0559 | 180.2598 | 504.9965 | -2081.8446 | 0
| 60469256 | CTN | 2014 | 30296895 | 30296896 | 47.14 | 45198.6405 | 4578.7082 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 651.7911 | 3.6745 | 655.4655 | 1.3273e-05 | 4578.7082 | 2475.0089 | 171.4567 | 0.96659 | 172.4232 | 483.0423 | -1991.9666 | 0
| 60469257 | CTN | 2014 | 30296896 | 30347934 | 267.48 | 45198.6405 | 25980.3324 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 0.0002863 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 3698.3711 | 118.304 | 3816.6751 | 7.5313e-05 | 25980.3324 | 14043.6013 | 972.8729 | 31.1204 | 1003.9933 | 2812.6819 | -11230.9195 | 0
| 60469527 | CHM | 1998 | 32108453 | 30082916 | 1519.33 | 43924.3002 | 147572.5229 | 0.0016262 | 0.0016262 | 0.0016262 | 0.0016262 | 0.0016262 | 0.0016262 | 0.0016262 | 0.0016262 | 0.0016262 | 0.0016262 | 0.0016262 | 0.0016262 | 0.0016262 | 0.0016262 | 0.0016262 | 0.001711 | 0.0019137 | 0.0021439 | 0.0024054 | 0.0027028 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2297.4809 | 4053.8294 | 6351.3104 | 0.00042779 | 147572.5229 | 79769.9448 | 569.2979 | 1004.0762 | 1573.3741 | 4777.9363 | -74992.0085 | 0
| 60469528 | CHM | 1998 | 30082916 | 30082812 | 9092.79 | 43924.3002 | 883182.6927 | 0.0097326 | 0.0097326 | 0.0097326 | 0.0097326 | 0.0097326 | 0.0097326 | 0.0097326 | 0.0097326 | 0.0097326 | 0.0097326 | 0.0097326 | 0.0097326 | 0.0097326 | 0.0097326 | 0.0097326 | 0.01024 | 0.011453 | 0.012831 | 0.014396 | 0.016176 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 13749.8182 | 145196.3031 | 158946.1213 | 0.0025602 | 883182.6927 | 477402.1154 | 3407.0981 | 35963.0703 | 39370.1685 | 119575.9529 | -357826.1626 | 0
| 60469529 | CHM | 1998 | 30082812 | 33051758 | 148.05 | 43924.3002 | 14380.0965 | 0.00015847 | 0.00015847 | 0.00015847 | 0.00015847 | 0.00015847 | 0.00015847 | 0.00015847 | 0.00015847 | 0.00015847 | 0.00015847 | 0.00015847 | 0.00015847 | 0.00015847 | 0.00015847 | 0.00015847 | 0.00016673 | 0.00018648 | 0.00020891 | 0.00023439 | 0.00026338 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 223.8765 | 38.4927 | 262.3692 | 4.1686e-05 | 14380.0965 | 7773.1239 | 55.4748 | 9.5341 | 65.0089 | 197.3603 | -7575.7636 | 0
| 60466995 | CHM | 2005 | 30082784 | 30230336 | 206.1 | 43924.3002 | 20018.493 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 0.0002206 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 293.5758 | 70.2382 | 363.8139 | 5.8031e-05 | 20018.493 | 10820.9445 | 77.2263 | 18.4764 | 95.7028 | 268.1112 | -10552.8333 | 0
| 60467004 | CTN | 2014 | 30296880 | 30296870 | 915.2 | 45198.6405 | 88893.376 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 0.0009796 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 12654.2056 | 1384.9961 | 14039.2017 | 0.00025769 | 88893.376 | 48051.084 | 3328.747 | 364.3296 | 3693.0766 | 10346.1251 | -37704.9589 | 0
| 60467035 | CTN | 2010 | 30147037 | 30147041 | 269.82 | 45198.6405 | 26207.6166 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 0.00028881 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 3730.7171 | 120.3827 | 3851.0998 | 7.5972e-05 | 26207.6166 | 14166.4592 | 981.3839 | 31.6673 | 1013.0511 | 2838.0487 | -11328.4105 | 0
| 60467036 | CTN | 2010 | 30147041 | 30147048 | 502.84 | 45198.6405 | 48840.8492 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 0.00053822 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 6952.6179 | 418.0958 | 7370.7137 | 0.00014158 | 48840.8492 | 26400.7944 | 1828.9195 | 109.9821 | 1938.9016 | 5431.8121 | -20968.9824 | 0
| 60467037 | CTN | 2010 | 30147048 | 30147075 | 1530.11 | 45198.6405 | 148619.5843 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 0.0016378 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 21156.3824 | 3871.3436 | 25027.726 | 0.00043083 | 148619.5843 | 80335.9311 | 5565.2853 | 1018.375 | 6583.6603 | 18444.0657 | -61891.8654 | 0
| 60467038 | CTN | 2010 | 30147075 | 30147105 | 3451.19 | 45198.6405 | 335214.0847 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 0.003694 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 47718.601 | 19694.9206 | 67413.5217 | 0.00097173 | 335214.0847 | 181199.1047 | 12552.5988 | 5180.84 | 17733.4388 | 49680.0829 | -131519.0217 | 0
| 60467039 | CTN | 2010 | 30147105 | 30147107 | 138.89 | 45198.6405 | 13490.3857 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 0.00014866 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1920.3881 | 31.8976 | 1952.2857 | 3.9107e-05 | 13490.3857 | 7292.193 | 505.1679 | 8.3908 | 513.5587 | 1438.7269 | -5853.4661 | 0
| 60467040 | CTN | 2010 | 30147107 | 30147108 | 108.4 | 45198.6405 | 10528.892 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1498.8181 | 19.4301 | 1518.2482 | 3.0522e-05 | 10528.892 | 5691.3653 | 394.2703 | 5.1112 | 399.3815 | 1118.8667 | -4572.4986 | 0
| 60467041 | CTN | 2010 | 30147108 | 30147109 | 129.36 | 45198.6405 | 12564.7368 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 0.00013846 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1788.6273 | 27.6705 | 1816.2978 | 3.6423e-05 | 12564.7368 | 6791.8359 | 470.5056 | 7.2788 | 477.7844 | 1338.5134 | -5453.3225 | 0
| 60467042 | CTN | 2010 | 30147109 | 30147125 | 999.1 | 45198.6405 | 97042.583 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 0.0010694 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 13814.2692 | 1650.5722 | 15464.8414 | 0.00028131 | 97042.583 | 52456.1167 | 3633.9064 | 434.1905 | 4068.0969 | 11396.7444 | -41059.3723 | 0
| 60467043 | CTN | 2010 | 30147125 | 30147126 | 361.58 | 45198.6405 | 35120.2654 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 0.00038702 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 4999.4575 | 216.1847 | 5215.6422 | 0.00010181 | 35120.2654 | 18984.1684 | 1315.1315 | 56.8684 | 1371.9999 | 3843.6423 | -15140.5261 | 0
| 60467044 | CTN | 1955 | 30147126 | 30020648 | 909.68 | 45198.6405 | 88357.2184 | 0.008513 | 0.0091783 | 0.0098981 | 0.010677 | 0.011519 | 0.012431 | 0.013418 | 0.014486 | 0.015643 | 0.016895 | 0.018251 | 0.01972 | 0.02131 | 0.023033 | 0.0249 | 0.026922 | 0.029114 | 0.029815 | 0.029815 | 0.029815 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 224299.3955 | 24363.8503 | 248663.2458 | 0.00025613 | 88357.2184 | 47761.2654 | 3308.6698 | 359.948 | 3668.6178 | 244994.628 | 197233.3626 | 1
| 60467045 | CTN | 1955 | 30020648 | 30020689 | 808.91 | 45198.6405 | 78569.4283 | 0.00757 | 0.0081616 | 0.0088016 | 0.009494 | 0.010243 | 0.011054 | 0.011932 | 0.012882 | 0.01391 | 0.015024 | 0.016229 | 0.017535 | 0.01895 | 0.020482 | 0.022142 | 0.02394 | 0.025889 | 0.026512 | 0.026512 | 0.026512 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 199452.5811 | 19265.0011 | 218717.5823 | 0.00022776 | 78569.4283 | 42470.5008 | 2942.1512 | 284.6183 | 3226.7695 | 215490.8128 | 173020.3119 | 1
| 60467046 | CTN | 1955 | 30020689 | 30019938 | 6159.46 | 45198.6405 | 598268.3498 | 0.057642 | 0.062147 | 0.06702 | 0.072292 | 0.077997 | 0.084171 | 0.090854 | 0.098087 | 0.10592 | 0.1144 | 0.12358 | 0.13352 | 0.14429 | 0.15596 | 0.1686 | 0.18229 | 0.19713 | 0.20187 | 0.20187 | 0.20187 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1518735.3285 | 1117001.8904 | 2635737.219 | 0.0017343 | 598268.3498 | 323392.4059 | 22403.0639 | 16502.4231 | 38905.487 | 2596831.7319 | 2273439.3261 | 1
| 60467047 | CTN | 1955 | 30019938 | 30333487 | 6039.4 | 45198.6405 | 586606.922 | 0.056518 | 0.060935 | 0.065714 | 0.070883 | 0.076477 | 0.082531 | 0.089083 | 0.096175 | 0.10385 | 0.11217 | 0.12117 | 0.13092 | 0.14148 | 0.15292 | 0.16531 | 0.17874 | 0.19329 | 0.19794 | 0.19794 | 0.19794 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1489132.1876 | 1073881.1495 | 2563013.337 | 0.0017005 | 586606.922 | 317088.8513 | 21966.3841 | 15865.3636 | 37831.7477 | 2525181.5894 | 2208092.7381 | 1
| 60467048 | CTN | 1955 | 30333487 | 31037333 | 70.3 | 45198.6405 | 6828.239 | 0.00065789 | 0.0007093 | 0.00076492 | 0.0008251 | 0.00089021 | 0.00096068 | 0.0010369 | 0.0011195 | 0.0012089 | 0.0013057 | 0.0014105 | 0.0015239 | 0.0016469 | 0.00178 | 0.0019243 | 0.0020806 | 0.0022499 | 0.0023041 | 0.0023041 | 0.0023041 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 17333.8411 | 145.5055 | 17479.3466 | 1.9794e-05 | 6828.239 | 3690.9869 | 255.6937 | 2.1497 | 257.8434 | 17221.5031 | 13530.5162 | 1
| 60467050 | CTN | 1955 | 32020883 | 33012636 | 7332.91 | 45198.6405 | 712245.5483 | 0.068623 | 0.073986 | 0.079788 | 0.086065 | 0.092857 | 0.10021 | 0.10816 | 0.11677 | 0.1261 | 0.13619 | 0.14712 | 0.15896 | 0.17178 | 0.18567 | 0.20072 | 0.21702 | 0.23469 | 0.24033 | 0.24033 | 0.24033 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1808072.3757 | 1583147.3527 | 3391219.7284 | 0.0020647 | 712245.5483 | 385002.4851 | 26671.1126 | 23389.1883 | 50060.3009 | 3341159.4275 | 2956156.9424 | 1
| 60467145 | CTN | 2014 | 30296994 | 30296991 | 361 | 45198.6405 | 35063.93 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 0.0003864 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 4991.4485 | 215.4922 | 5206.9407 | 0.00010164 | 35063.93 | 18953.7165 | 1313.0219 | 56.6861 | 1369.7081 | 3837.2326 | -15116.4838 | 0
| 60467146 | CTN | 2011 | 30296991 | 30296990 | 40.1 | 45198.6405 | 3894.913 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 4.2922e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 554.4508 | 2.6589 | 557.1097 | 1.1291e-05 | 3894.913 | 2105.3851 | 145.8509 | 0.69944 | 146.5504 | 410.5594 | -1694.8257 | 0
| 60467147 | CTN | 2011 | 30296990 | 30296987 | 315.1 | 45198.6405 | 30605.663 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 0.00033727 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 4356.8006 | 164.1775 | 4520.9782 | 8.8721e-05 | 30605.663 | 16543.8118 | 1146.0754 | 43.1876 | 1189.263 | 3331.7152 | -13212.0966 | 0
| 60467148 | CTN | 2011 | 30296987 | 30296216 | 35.2 | 45198.6405 | 3418.976 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 3.7677e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 486.6999 | 2.0488 | 488.7487 | 9.9111e-06 | 3418.976 | 1848.1186 | 128.0287 | 0.53895 | 128.5677 | 360.181 | -1487.9376 | 0
| 60467229 | CTN | 2014 | 30347933 | 30347934 | 43.89 | 45198.6405 | 4263.0357 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 4.6978e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 606.8542 | 3.1853 | 610.0394 | 1.2358e-05 | 4263.0357 | 2304.3729 | 159.6358 | 0.8379 | 160.4737 | 449.5657 | -1854.8072 | 0
| 60470199 | CTN | 2014 | 30296766 | 30296762 | 178.09 | 45198.6405 | 17297.8817 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 0.00019062 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 2462.403 | 52.4441 | 2514.8471 | 5.0144e-05 | 17297.8817 | 9350.3251 | 647.7454 | 13.7956 | 661.541 | 1853.3061 | -7497.019 | 0
| 60547067 | RVL | 1973 | 30352465 | 33066420 | 26.51 | 49456.6662 | 2574.9163 | 2.959e-05 | 3.1806e-05 | 3.4211e-05 | 3.6822e-05 | 3.9658e-05 | 4.2741e-05 | 4.6091e-05 | 4.9733e-05 | 5.3694e-05 | 5.8005e-05 | 6.2696e-05 | 6.7802e-05 | 7.3363e-05 | 7.9421e-05 | 8.602e-05 | 9.3213e-05 | 0.00010106 | 0.00010961 | 0.00011893 | 0.00012911 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 1228.9366 | 2.5209 | 1231.4576 | 7.4643e-06 | 2574.9163 | 1391.8643 | 146.8343 | 0.30569 | 147.14 | 1084.3175 | -307.5468 | 0
| 60547070 | CTN | 1998 | 30147032 | 30147036 | 334.81 | 45198.6405 | 32520.0953 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 0.00035837 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 4629.3259 | 185.3591 | 4814.685 | 9.4271e-05 | 32520.0953 | 17578.6532 | 1217.7642 | 48.7595 | 1266.5237 | 3548.1613 | -14030.4919 | 0
| 60547090 | RVL | 1998 | 33064753 | 33064664 | 1311.62 | 49456.6662 | 127397.6506 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 0.0014039 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 27617.2226 | 2844.6747 | 30461.8973 | 0.00036931 | 127397.6506 | 68864.4698 | 7264.8372 | 748.3047 | 8013.1419 | 22448.7554 | -46415.7145 | 0
| 60547094 | CME | 1999 | 33086121 | 33085553 | 7192.64 | 46875.2879 | 698621.1232 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 0.0076988 | 38.435 | 38.637 | 39.003 | 39.298 | 39.32 | 39.352 | 39.702 | 40.078 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 207329.0442 | 85544.7212 | 292873.7654 | 0.0020252 | 698621.1232 | 377637.8374 | 54538.8553 | 22502.931 | 77041.7863 | 215831.9791 | -161805.8584 | 0
| 60546911 | CTN | 1981 | 33011837 | 33011845 | 38.39 | 45198.6405 | 3728.8207 | 4.1091e-05 | 4.1091e-05 | 4.1091e-05 | 4.1091e-05 | 4.1091e-05 | 4.1091e-05 | 4.1091e-05 | 4.1091e-05 | 4.1091e-05 | 4.1091e-05 | 4.1091e-05 | 4.1091e-05 | 4.3082e-05 | 4.6663e-05 | 5.0584e-05 | 5.4878e-05 | 5.9583e-05 | 6.4742e-05 | 7.0399e-05 | 7.6605e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 598.7231 | 2.7477 | 601.4708 | 1.0809e-05 | 3728.8207 | 2015.6044 | 139.6313 | 0.64106 | 140.2724 | 461.1984 | -1554.406 | 0
| 60546908 | RVL | 1999 | 33064349 | 33064344 | 593.33 | 49456.6662 | 57630.1429 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 0.00063508 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 12493.045 | 582.1155 | 13075.1606 | 0.00016706 | 57630.1429 | 31151.8244 | 3286.3526 | 153.1282 | 3439.4808 | 9635.6798 | -21516.1446 | 0
| 60546906 | CTN | 1955 | 30546420 | 30021420 | 8392.04 | 45198.6405 | 815118.8452 | 0.078535 | 0.084673 | 0.091312 | 0.098496 | 0.10627 | 0.11468 | 0.12378 | 0.13364 | 0.14431 | 0.15586 | 0.16837 | 0.18192 | 0.19659 | 0.21249 | 0.22971 | 0.24837 | 0.26858 | 0.27505 | 0.27505 | 0.27505 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 2069221.5933 | 2073498.4756 | 4142720.0689 | 0.0023629 | 815118.8452 | 440610.3791 | 30523.3589 | 30633.5643 | 61156.9232 | 4081563.1457 | 3640952.7666 | 1
| 60546832 | CTN | 1981 | 33011845 | 33011903 | 511.34 | 45198.6405 | 49666.4542 | 0.00054732 | 0.00054732 | 0.00054732 | 0.00054732 | 0.00054732 | 0.00054732 | 0.00054732 | 0.00054732 | 0.00054732 | 0.00054732 | 0.00054732 | 0.00054732 | 0.00057383 | 0.00062153 | 0.00067375 | 0.00073095 | 0.00079363 | 0.00086233 | 0.00093768 | 0.0010203 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 7974.7629 | 487.4744 | 8462.2373 | 0.00014398 | 49666.4542 | 26847.0731 | 1859.8356 | 113.7318 | 1973.5674 | 6488.67 | -20358.4031 | 0
| 60546808 | CTN | 2011 | 30296172 | 30296173 | 33.43 | 45198.6405 | 3247.0559 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 3.5782e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 462.2273 | 1.8479 | 464.0752 | 9.4127e-06 | 3247.0559 | 1755.1877 | 121.5909 | 0.48611 | 122.077 | 341.9982 | -1413.1895 | 0
| 60546785 | CTN | 2010 | 30228695 | 30228693 | 55.32 | 45198.6405 | 5373.2316 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 764.8935 | 5.0604 | 769.9539 | 1.5576e-05 | 5373.2316 | 2904.4864 | 201.2088 | 1.3311 | 202.5399 | 567.4139 | -2337.0725 | 0
| 60546778 | CME | 1999 | 33086369 | 33086363 | 40.51 | 46875.2879 | 3934.7363 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 4.3361e-05 | 38.435 | 38.637 | 39.003 | 39.298 | 39.32 | 39.352 | 39.702 | 40.078 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 1167.7081 | 2.7136 | 1170.4217 | 1.1406e-05 | 3934.7363 | 2126.9115 | 307.1708 | 0.71382 | 307.8846 | 862.5371 | -1264.3744 | 0
| 60547145 | OYN | 1998 | 33065532 | 33065571 | 1288.66 | 42821.2873 | 125167.5458 | 0.0013793 | 0.0013793 | 0.0013793 | 0.0013793 | 0.0013793 | 0.0013793 | 0.0013793 | 0.0013793 | 0.0013793 | 0.0013793 | 0.0013793 | 0.0013793 | 0.0013793 | 0.0013793 | 0.0013793 | 0.0014513 | 0.0016232 | 0.0018184 | 0.0020402 | 0.0022925 | 6.588 | 6.564 | 6.571 | 6.554 | 6.491 | 6.444 | 6.444 | 6.454 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 5850.6579 | 2916.3379 | 8766.9958 | 0.00036284 | 125167.5458 | 67658.9925 | 1449.9127 | 722.3358 | 2172.2485 | 6594.7473 | -61064.2452 | 0
| 60547771 | CTN | 2014 | 30296861 | 30296817 | 20.24 | 45198.6405 | 1965.9112 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 2.1664e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 279.8522 | 0.67739 | 280.5296 | 5.6989e-06 | 1965.9112 | 1062.6682 | 73.6165 | 0.17819 | 73.7947 | 206.7349 | -855.9333 | 0
| 60547811 | RVL | 1999 | 33064518 | 33064498 | 1623.73 | 49456.6662 | 157712.8949 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 0.001738 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 34188.9458 | 4359.5746 | 38548.5203 | 0.00045719 | 157712.8949 | 85251.2966 | 8993.5607 | 1146.8063 | 10140.367 | 28408.1533 | -56843.1432 | 0
| 60547819 | RVL | 1999 | 33064396 | 33064383 | 1130.38 | 49456.6662 | 109793.8094 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 0.0012099 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 23801.0742 | 2112.8351 | 25913.9094 | 0.00031828 | 109793.8094 | 59348.7591 | 6260.98 | 555.7908 | 6816.7709 | 19097.1385 | -40251.6206 | 0
| 60547831 | CTN | 2010 | 30147108 | 30147107 | 108.4 | 45198.6405 | 10528.892 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 0.00011603 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1498.8181 | 19.4301 | 1518.2482 | 3.0522e-05 | 10528.892 | 5691.3653 | 394.2703 | 5.1112 | 399.3815 | 1118.8667 | -4572.4986 | 0
| 60547845 | RVL | 1998 | 33063883 | 33063773 | 1624.37 | 49456.6662 | 157775.0581 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 0.0017387 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 34202.4208 | 4363.0118 | 38565.4326 | 0.00045737 | 157775.0581 | 85284.8987 | 8997.1055 | 1147.7105 | 10144.816 | 28420.6166 | -56864.2821 | 0
| 60547856 | RVL | 1999 | 33064448 | 33064429 | 1107.66 | 49456.6662 | 107587.0158 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 0.0011856 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 23322.6812 | 2028.7547 | 25351.4358 | 0.00031188 | 107587.0158 | 58155.8825 | 6135.1379 | 533.6732 | 6668.8111 | 18682.6248 | -39473.2578 | 0
| 60547865 | RVL | 1998 | 33064038 | 33064021 | 701.38 | 49456.6662 | 68125.0394 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 0.00075073 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 14768.122 | 813.4357 | 15581.5577 | 0.00019748 | 68125.0394 | 36824.8135 | 3884.823 | 213.978 | 4098.801 | 11482.7567 | -25342.0568 | 0
| 60547903 | RVL | 2017 | 30352473 | 30352471 | 75.43 | 49456.6662 | 7326.5159 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 8.0738e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 1588.2399 | 9.4082 | 1597.648 | 2.1238e-05 | 7326.5159 | 3960.3292 | 417.7938 | 2.4749 | 420.2686 | 1177.3794 | -2782.9498 | 0
| 60546771 | OYN | 1998 | 33065757 | 33065791 | 217.43 | 42821.2873 | 21118.9759 | 0.00023273 | 0.00023273 | 0.00023273 | 0.00023273 | 0.00023273 | 0.00023273 | 0.00023273 | 0.00023273 | 0.00023273 | 0.00023273 | 0.00023273 | 0.00023273 | 0.00023273 | 0.00023273 | 0.00023273 | 0.00024486 | 0.00027387 | 0.00030681 | 0.00034424 | 0.0003868 | 6.588 | 6.564 | 6.571 | 6.554 | 6.491 | 6.444 | 6.444 | 6.454 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 987.1566 | 83.0234 | 1070.1799 | 6.1221e-05 | 21118.9759 | 11415.8077 | 244.6375 | 20.5637 | 265.2012 | 804.9787 | -10610.829 | 0
| 60546568 | RVL | 2017 | 30352811 | 30352807 | 274.24 | 49456.6662 | 26636.9312 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 0.00029354 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 5774.3358 | 124.3591 | 5898.6949 | 7.7216e-05 | 26636.9312 | 14398.5241 | 1518.9681 | 32.7133 | 1551.6814 | 4347.0135 | -10051.5106 | 0
| 60546625 | RVL | 1999 | 33064344 | 33064301 | 3743.66 | 49456.6662 | 363621.6958 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 0.0040071 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 78825.8007 | 23174.4468 | 102000.2475 | 0.0010541 | 363621.6958 | 196554.7652 | 20735.4876 | 6096.1443 | 26831.632 | 75168.6155 | -121386.1497 | 0
| 60546634 | CHM | 1998 | 32108453 | 32108497 | 1024.03 | 43924.3002 | 99464.0339 | 0.0010961 | 0.0010961 | 0.0010961 | 0.0010961 | 0.0010961 | 0.0010961 | 0.0010961 | 0.0010961 | 0.0010961 | 0.0010961 | 0.0010961 | 0.0010961 | 0.0010961 | 0.0010961 | 0.0010961 | 0.0011532 | 0.0012899 | 0.001445 | 0.0016213 | 0.0018217 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 1548.5044 | 1841.5629 | 3390.0672 | 0.00028833 | 99464.0339 | 53765.0257 | 383.7074 | 456.1291 | 839.8365 | 2550.2307 | -51214.795 | 0
| 60546637 | RVL | 1999 | 33064452 | 33064448 | 281.83 | 49456.6662 | 27374.1479 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 0.00030166 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 5934.1674 | 131.3384 | 6065.5057 | 7.9353e-05 | 27374.1479 | 14797.0247 | 1561.0078 | 34.5491 | 1595.5569 | 4469.9488 | -10327.0759 | 0
| 60546638 | CHM | 1998 | 31015919 | 30315709 | 5602.57 | 43924.3002 | 544177.6241 | 0.0059968 | 0.0059968 | 0.0059968 | 0.0059968 | 0.0059968 | 0.0059968 | 0.0059968 | 0.0059968 | 0.0059968 | 0.0059968 | 0.0059968 | 0.0059968 | 0.0059968 | 0.0059968 | 0.0059968 | 0.0063095 | 0.007057 | 0.0079056 | 0.00887 | 0.0099668 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 8472.0221 | 55123.377 | 63595.3991 | 0.0015775 | 544177.6241 | 294153.8043 | 2099.3013 | 13653.2808 | 15752.5821 | 47842.817 | -246310.9872 | 0
| 60546653 | RVL | 1998 | 33064586 | 33064584 | 180.57 | 49456.6662 | 17538.7641 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 0.00019328 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 3802.0438 | 53.9147 | 3855.9585 | 5.0842e-05 | 17538.7641 | 9480.5335 | 1000.1461 | 14.1825 | 1014.3286 | 2841.6299 | -6638.9036 | 0
| 60546710 | CHA | 1959 | 32038588 | 32038590 | 132.08 | 48008.7507 | 12828.9304 | 0.0012481 | 0.001352 | 0.0014649 | 0.0015876 | 0.0017211 | 0.0018662 | 0.0020241 | 0.0021959 | 0.0023827 | 0.0025861 | 0.0028074 | 0.0030482 | 0.0033104 | 0.0035958 | 0.0039066 | 0.004245 | 0.0043289 | 0.0043289 | 0.0043289 | 0.0043289 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 38555.1457 | 534.1858 | 39089.3315 | 3.7189e-05 | 12828.9304 | 6934.6451 | 545.7441 | 7.5882 | 553.3323 | 38535.9993 | 31601.3542 | 1
| 60548486 | RVL | 1973 | 33066545 | 33066572 | 1028.62 | 49456.6662 | 99909.8606 | 0.0011481 | 0.0012341 | 0.0013274 | 0.0014287 | 0.0015388 | 0.0016584 | 0.0017884 | 0.0019297 | 0.0020834 | 0.0022506 | 0.0024327 | 0.0026308 | 0.0028466 | 0.0030816 | 0.0033377 | 0.0036168 | 0.0039211 | 0.0042528 | 0.0046147 | 0.0050095 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 47684.1891 | 3795.3269 | 51479.5159 | 0.00028962 | 99909.8606 | 54006.0162 | 5697.3489 | 460.2273 | 6157.5762 | 45321.9397 | -8684.0765 | 0
| 60548544 | RVL | 1973 | 33066588 | 30275660 | 1780 | 49456.6662 | 172891.4 | 0.0019868 | 0.0021356 | 0.0022971 | 0.0024724 | 0.0026628 | 0.0028698 | 0.0030947 | 0.0033393 | 0.0036053 | 0.0038947 | 0.0042097 | 0.0045525 | 0.0049259 | 0.0053326 | 0.0057758 | 0.0062588 | 0.0067853 | 0.0073594 | 0.0079856 | 0.0086688 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 82516.2419 | 11365.257 | 93881.4989 | 0.00050119 | 172891.4 | 93455.9982 | 9859.1133 | 1378.1689 | 11237.2822 | 82644.2168 | -10811.7814 | 0
| 60548556 | CTN | 2014 | 30296743 | 30296744 | 39.79 | 45198.6405 | 3864.8027 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 4.259e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 550.1647 | 2.618 | 552.7827 | 1.1203e-05 | 3864.8027 | 2089.1091 | 144.7234 | 0.68867 | 145.4121 | 407.3706 | -1681.7385 | 0
| 60548617 | RVL | 2017 | 30352470 | 30352799 | 72.4 | 49456.6662 | 7032.212 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 1524.441 | 8.6675 | 1533.1085 | 2.0385e-05 | 7032.212 | 3801.244 | 401.0111 | 2.28 | 403.2911 | 1129.8174 | -2671.4266 | 0
| 60548624 | RVL | 1998 | 33063736 | 33063702 | 1008.51 | 49456.6662 | 97956.5763 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 0.0010795 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 21234.9957 | 1681.8102 | 22916.8058 | 0.00028396 | 97956.5763 | 52950.1734 | 5585.9631 | 442.4079 | 6028.371 | 16888.4348 | -36061.7386 | 0
| 60548631 | CHA | 1957 | 30223838 | 33021502 | 3626.48 | 48008.7507 | 352240.0024 | 0.03516 | 0.038009 | 0.0411 | 0.044453 | 0.048091 | 0.052039 | 0.056324 | 0.060975 | 0.066024 | 0.071507 | 0.07746 | 0.083926 | 0.090948 | 0.098577 | 0.10686 | 0.11587 | 0.11886 | 0.11886 | 0.11886 | 0.11886 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 1064956.2401 | 405154.6725 | 1470110.9126 | 0.0010211 | 352240.0024 | 190402.4203 | 14984.3279 | 5720.4871 | 20704.8151 | 1449406.0975 | 1259003.6772 | 1
| 60548707 | RVL | 1998 | 33063947 | 33063926 | 423.32 | 49456.6662 | 41117.0716 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 0.00045311 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 8913.3491 | 296.3154 | 9209.6645 | 0.00011919 | 41117.0716 | 22225.7265 | 2344.6965 | 77.9471 | 2422.6436 | 6787.0209 | -15438.7056 | 0
| 60548719 | CTN | 1955 | 30021528 | 30228886 | 932.43 | 45198.6405 | 90566.9259 | 0.0087259 | 0.0094079 | 0.010146 | 0.010944 | 0.011807 | 0.012742 | 0.013754 | 0.014849 | 0.016034 | 0.017318 | 0.018708 | 0.020213 | 0.021843 | 0.023609 | 0.025523 | 0.027596 | 0.029842 | 0.03056 | 0.03056 | 0.03056 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 229908.8522 | 25597.7094 | 255506.5616 | 0.00026254 | 90566.9259 | 48955.7171 | 3391.4156 | 378.1768 | 3769.5924 | 251736.9691 | 202781.2521 | 1
| 60548720 | RVL | 1973 | 33063699 | 33063702 | 34.57 | 49456.6662 | 3357.7841 | 3.8586e-05 | 4.1476e-05 | 4.4612e-05 | 4.8017e-05 | 5.1716e-05 | 5.5735e-05 | 6.0104e-05 | 6.4854e-05 | 7.002e-05 | 7.564e-05 | 8.1757e-05 | 8.8416e-05 | 9.5668e-05 | 0.00010357 | 0.00011217 | 0.00012155 | 0.00013178 | 0.00014293 | 0.00015509 | 0.00016836 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 1602.5773 | 4.2868 | 1606.8642 | 9.7337e-06 | 3357.7841 | 1815.0415 | 191.4773 | 0.51983 | 191.9971 | 1414.8671 | -400.1744 | 0
| 60548723 | RVL | 1999 | 33064383 | 33064373 | 728.98 | 49456.6662 | 70805.8274 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 0.00078028 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 15349.2597 | 878.7142 | 16227.9739 | 0.00020526 | 70805.8274 | 38273.9065 | 4037.6946 | 231.1499 | 4268.8445 | 11959.1294 | -26314.7771 | 0
| 60548727 | RVL | 1998 | 33063976 | 33063947 | 648.75 | 49456.6662 | 63013.0875 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 0.0006944 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 13659.963 | 695.9395 | 14355.9025 | 0.00018267 | 63013.0875 | 34061.5611 | 3593.3145 | 183.07 | 3776.3845 | 10579.518 | -23482.0431 | 0
| 60548758 | CTN | 2014 | 31037380 | 31037381 | 82.91 | 45198.6405 | 8053.0483 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 8.8744e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1146.3721 | 11.3666 | 1157.7387 | 2.3345e-05 | 8053.0483 | 4353.0544 | 301.5586 | 2.99 | 304.5486 | 853.19 | -3499.8643 | 0
| 60548775 | RVL | 2017 | 30352477 | 30352478 | 86.85 | 49456.6662 | 8435.7405 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 9.2961e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 1828.6974 | 12.4726 | 1841.17 | 2.4454e-05 | 8435.7405 | 4559.9177 | 481.0472 | 3.281 | 484.3282 | 1356.8418 | -3203.0759 | 0
| 60548808 | RVL | 2017 | 30352806 | 30352473 | 563.21 | 49456.6662 | 54704.5873 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 0.00060284 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 11858.8334 | 524.5138 | 12383.3472 | 0.00015858 | 54704.5873 | 29570.4229 | 3119.5231 | 137.9759 | 3257.499 | 9125.8482 | -20444.5747 | 0
| 60548824 | CTN | 2014 | 30296896 | 30296895 | 47.14 | 45198.6405 | 4578.7082 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 5.0457e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 651.7911 | 3.6745 | 655.4655 | 1.3273e-05 | 4578.7082 | 2475.0089 | 171.4567 | 0.96659 | 172.4232 | 483.0423 | -1991.9666 | 0
| 60548862 | RVL | 2017 | 30352799 | 30352466 | 1257.13 | 49456.6662 | 122105.0369 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 0.0013456 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 26469.8975 | 2613.2264 | 29083.1239 | 0.00035396 | 122105.0369 | 66003.5612 | 6963.0264 | 687.421 | 7650.4475 | 21432.6764 | -44570.8848 | 0
| 60548870 | CHA | 1959 | 30350615 | 32038422 | 3699.63 | 48008.7507 | 359345.0619 | 0.034961 | 0.03787 | 0.041032 | 0.04447 | 0.048209 | 0.052275 | 0.056697 | 0.061508 | 0.066742 | 0.072437 | 0.078636 | 0.085382 | 0.092726 | 0.10072 | 0.10943 | 0.1189 | 0.12125 | 0.12125 | 0.12125 | 0.12125 | 20.81 | 20.729 | 20.936 | 21.052 | 20.881 | 20.79 | 21.036 | 21.419 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 21.323 | 1079949.8205 | 419116.5215 | 1499066.342 | 0.0010417 | 359345.0619 | 194243.0418 | 15286.5779 | 5953.5914 | 21240.1693 | 1477826.1727 | 1283583.1309 | 1
| 60548874 | CTN | 2011 | 30296142 | 30296143 | 20.92 | 45198.6405 | 2031.9596 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 2.2392e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 289.255 | 0.72367 | 289.9787 | 5.8903e-06 | 2031.9596 | 1098.3705 | 76.0898 | 0.19036 | 76.2802 | 213.6985 | -884.672 | 0
| 60548909 | RVL | 1999 | 33064547 | 33064518 | 647.2 | 49456.6662 | 62862.536 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 0.00069274 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 13627.3279 | 692.618 | 14319.9459 | 0.00018223 | 62862.536 | 33980.1809 | 3584.7293 | 182.1963 | 3766.9255 | 10553.0204 | -23427.1605 | 0
| 60548927 | RVL | 1998 | 33063752 | 33063740 | 619.57 | 49456.6662 | 60178.8341 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 0.00066317 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 13045.541 | 634.7417 | 13680.2827 | 0.00017445 | 60178.8341 | 32529.5128 | 3431.6915 | 166.9718 | 3598.6633 | 10081.6194 | -22447.8934 | 0
| 60548949 | RVL | 1998 | 33064010 | 33063976 | 1100.89 | 49456.6662 | 106929.4457 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 0.0011784 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 23180.1212 | 2004.03 | 25184.1512 | 0.00030997 | 106929.4457 | 57800.4347 | 6097.64 | 527.1695 | 6624.8095 | 18559.3417 | -39241.093 | 0
| 60548965 | RVL | 2017 | 30352856 | 30352858 | 134.22 | 49456.6662 | 13036.7886 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 0.00014366 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 2826.1172 | 29.7887 | 2855.9059 | 3.7792e-05 | 13036.7886 | 7047.0023 | 743.4215 | 7.836 | 751.2575 | 2104.6484 | -4942.3539 | 0
| 60548476 | CTN | 2014 | 30296881 | 30296895 | 1400.91 | 45198.6405 | 136070.3883 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 0.0014995 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19369.9769 | 3245.1666 | 22615.1436 | 0.00039445 | 136070.3883 | 73552.4957 | 5095.3616 | 853.656 | 5949.0177 | 16666.1259 | -56886.3698 | 0
| 60547921 | CTN | 2010 | 30282337 | 30282338 | 65 | 45198.6405 | 6313.45 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 6.9574e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 898.7367 | 6.9862 | 905.7229 | 1.8302e-05 | 6313.45 | 3412.719 | 236.4167 | 1.8378 | 238.2545 | 667.4684 | -2745.2506 | 0
| 60547932 | RVL | 1998 | 33064093 | 33064096 | 176.2 | 49456.6662 | 17114.306 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 0.0001886 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 3710.0398 | 51.3368 | 3761.3767 | 4.9612e-05 | 17114.306 | 9251.0938 | 975.9414 | 13.5044 | 989.4458 | 2771.9308 | -6479.1629 | 0
| 60547940 | CTN | 2014 | 30296924 | 31037380 | 53.73 | 45198.6405 | 5218.7949 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 5.7511e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 742.9088 | 4.7736 | 747.6825 | 1.5128e-05 | 5218.7949 | 2821.0061 | 195.4257 | 1.2557 | 196.6814 | 551.0011 | -2270.005 | 0
| 60547941 | RVL | 1998 | 33063740 | 33063738 | 41.1 | 49456.6662 | 3992.043 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 4.3992e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 865.394 | 2.7932 | 868.1872 | 1.1572e-05 | 3992.043 | 2157.8885 | 227.6458 | 0.73476 | 228.3806 | 639.8066 | -1518.0819 | 0
| 60547946 | CTN | 1981 | 33011903 | 33012013 | 1017.32 | 45198.6405 | 98812.2916 | 0.0010889 | 0.0010889 | 0.0010889 | 0.0010889 | 0.0010889 | 0.0010889 | 0.0010889 | 0.0010889 | 0.0010889 | 0.0010889 | 0.0010889 | 0.0010889 | 0.0011417 | 0.0012365 | 0.0013404 | 0.0014542 | 0.0015789 | 0.0017156 | 0.0018655 | 0.00203 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 15865.9252 | 1929.5109 | 17795.4361 | 0.00028644 | 98812.2916 | 53412.7281 | 3700.1758 | 450.1711 | 4150.3469 | 13645.0892 | -39767.6389 | 0
| 60548007 | CTN | 2010 | 30228693 | 30228695 | 55.32 | 45198.6405 | 5373.2316 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 5.9213e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 764.8935 | 5.0604 | 769.9539 | 1.5576e-05 | 5373.2316 | 2904.4864 | 201.2088 | 1.3311 | 202.5399 | 567.4139 | -2337.0725 | 0
| 60548031 | RVL | 1973 | 33066572 | 33066588 | 271.64 | 49456.6662 | 26384.3932 | 0.0003032 | 0.0003259 | 0.00035055 | 0.0003773 | 0.00040637 | 0.00043795 | 0.00047227 | 0.0005096 | 0.00055019 | 0.00059436 | 0.00064242 | 0.00069475 | 0.00075173 | 0.0008138 | 0.00088143 | 0.00095513 | 0.0010355 | 0.0011231 | 0.0012187 | 0.0013229 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 12592.5344 | 264.6834 | 12857.2177 | 7.6484e-05 | 26384.3932 | 14262.0154 | 1504.5672 | 32.0959 | 1536.6631 | 11320.5547 | -2941.4607 | 0
| 60548050 | RVL | 1999 | 33064429 | 33064420 | 560.49 | 49456.6662 | 54440.3937 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 0.00059993 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 11801.5694 | 519.4601 | 12321.0295 | 0.00015781 | 54440.3937 | 29427.6137 | 3104.4575 | 136.6464 | 3241.1039 | 9079.9256 | -20347.6881 | 0
| 60548055 | CTN | 1955 | 30150101 | 30021365 | 1412.87 | 45198.6405 | 137232.0631 | 0.013222 | 0.014255 | 0.015373 | 0.016583 | 0.017891 | 0.019307 | 0.02084 | 0.022499 | 0.024296 | 0.026241 | 0.028347 | 0.030628 | 0.033098 | 0.035774 | 0.038674 | 0.041815 | 0.045218 | 0.046306 | 0.046306 | 0.046306 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 348370.7314 | 58772.3474 | 407143.0788 | 0.00039781 | 137232.0631 | 74180.436 | 5138.8623 | 868.2941 | 6007.1564 | 401135.9224 | 326955.4864 | 1
| 60548061 | OYN | 1998 | 33065571 | 33065757 | 6374.01 | 42821.2873 | 619107.5913 | 0.0068225 | 0.0068225 | 0.0068225 | 0.0068225 | 0.0068225 | 0.0068225 | 0.0068225 | 0.0068225 | 0.0068225 | 0.0068225 | 0.0068225 | 0.0068225 | 0.0068225 | 0.0068225 | 0.0068225 | 0.0071783 | 0.0080287 | 0.0089942 | 0.010091 | 0.011339 | 6.588 | 6.564 | 6.571 | 6.554 | 6.491 | 6.444 | 6.444 | 6.454 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 28938.7114 | 71348.8059 | 100287.5173 | 0.0017947 | 619107.5913 | 334657.0038 | 7171.6033 | 17672.0903 | 24843.6936 | 75443.8237 | -259213.1801 | 0
| 60548079 | RVL | 1998 | 33064551 | 33064547 | 40.58 | 49456.6662 | 3941.5354 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 4.3436e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 854.4448 | 2.723 | 857.1678 | 1.1426e-05 | 3941.5354 | 2130.5867 | 224.7656 | 0.71629 | 225.4819 | 631.6858 | -1498.9009 | 0
| 60548098 | CHM | 1975 | 30152639 | 30083715 | 1209.81 | 43924.3002 | 117508.8453 | 0.0036982 | 0.0040233 | 0.0043792 | 0.0047691 | 0.0051963 | 0.0056645 | 0.0061776 | 0.0067403 | 0.0073575 | 0.0080345 | 0.0087774 | 0.0095928 | 0.010488 | 0.011471 | 0.01255 | 0.013736 | 0.015038 | 0.01647 | 0.018043 | 0.019772 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 11534.9537 | 16256.2518 | 27791.2056 | 0.00034064 | 117508.8453 | 63519.1018 | 453.3198 | 636.6442 | 1089.9639 | 26701.2416 | -36817.8601 | 0
| 60548184 | RVL | 1998 | 33064659 | 33064647 | 177.2 | 49456.6662 | 17211.436 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 0.00018967 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 3731.0884 | 51.9211 | 3783.0095 | 4.9893e-05 | 17211.436 | 9303.5971 | 981.4803 | 13.6581 | 995.1384 | 2787.8712 | -6515.726 | 0
| 60548237 | RVL | 1999 | 33064196 | 33064146 | 4495.7 | 49456.6662 | 436667.341 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 0.0048121 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 94660.6139 | 33420.3679 | 128080.9818 | 0.0012658 | 436667.341 | 236039.3994 | 24900.9076 | 8791.3807 | 33692.2883 | 94388.6935 | -141650.7059 | 0
| 60548272 | RVL | 2017 | 30352799 | 30352470 | 72.4 | 49456.6662 | 7032.212 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 7.7495e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 1524.441 | 8.6675 | 1533.1085 | 2.0385e-05 | 7032.212 | 3801.244 | 401.0111 | 2.28 | 403.2911 | 1129.8174 | -2671.4266 | 0
| 60548344 | CTN | 2014 | 31037418 | 30323208 | 12.98 | 45198.6405 | 1260.7474 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 1.3893e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 179.4712 | 0.27859 | 179.7497 | 3.6547e-06 | 1260.7474 | 681.4937 | 47.2106 | 0.073284 | 47.2839 | 132.4659 | -549.0279 | 0
| 60548360 | CTN | 2014 | 30296880 | 30296881 | 105.51 | 45198.6405 | 10248.1863 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 0.00011293 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 1458.8506 | 18.4078 | 1477.2584 | 2.9708e-05 | 10248.1863 | 5539.6305 | 383.7588 | 4.8423 | 388.6011 | 1088.6573 | -4450.9733 | 0
| 60548363 | OYN | 1998 | 33065058 | 33065097 | 1916.67 | 42821.2873 | 186166.1571 | 0.0020515 | 0.0020515 | 0.0020515 | 0.0020515 | 0.0020515 | 0.0020515 | 0.0020515 | 0.0020515 | 0.0020515 | 0.0020515 | 0.0020515 | 0.0020515 | 0.0020515 | 0.0020515 | 0.0020515 | 0.0021585 | 0.0024142 | 0.0027046 | 0.0030345 | 0.0034097 | 6.588 | 6.564 | 6.571 | 6.554 | 6.491 | 6.444 | 6.444 | 6.454 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 8701.8954 | 6451.4299 | 15153.3253 | 0.00053967 | 186166.1571 | 100631.6337 | 2156.507 | 1597.9277 | 3754.4347 | 11398.8906 | -89232.7431 | 0
| 60548387 | RVL | 2017 | 30352470 | 30352471 | 40.09 | 49456.6662 | 3893.9417 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 4.2911e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 844.1271 | 2.6576 | 846.7846 | 1.1288e-05 | 3893.9417 | 2104.8601 | 222.0516 | 0.69909 | 222.7507 | 624.034 | -1480.8261 | 0
| 60548396 | CHM | 1982 | 33052667 | 33052660 | 52.22 | 43924.3002 | 5072.1286 | 5.5895e-05 | 5.5895e-05 | 5.9548e-05 | 6.4992e-05 | 7.1003e-05 | 7.7643e-05 | 8.4983e-05 | 9.3101e-05 | 0.00010208 | 0.00011202 | 0.00012303 | 0.00013523 | 0.00014875 | 0.00016374 | 0.00018037 | 0.00019882 | 0.00021931 | 0.00024206 | 0.00026733 | 0.00029541 | 2.136 | 2.12 | 2.12 | 2.12 | 2.11 | 2.09 | 2.09 | 2.1 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 164.5563 | 10.0109 | 174.5672 | 1.4703e-05 | 5072.1286 | 2741.726 | 19.567 | 1.1861 | 20.7531 | 153.814 | -2587.9119 | 0
| 60548400 | RVL | 1998 | 33064664 | 33064659 | 31.19 | 49456.6662 | 3029.4847 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 3.3385e-05 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 656.7317 | 1.6086 | 658.3403 | 8.782e-06 | 3029.4847 | 1637.5801 | 172.756 | 0.42315 | 173.1792 | 485.1611 | -1152.419 | 0
| 60548433 | OYN | 1998 | 30254687 | 32154848 | 14.67 | 42821.2873 | 1424.8971 | 1.5702e-05 | 1.5702e-05 | 1.5702e-05 | 1.5702e-05 | 1.5702e-05 | 1.5702e-05 | 1.5702e-05 | 1.5702e-05 | 1.5702e-05 | 1.5702e-05 | 1.5702e-05 | 1.5702e-05 | 1.5702e-05 | 1.5702e-05 | 1.5702e-05 | 1.6521e-05 | 1.8478e-05 | 2.07e-05 | 2.3226e-05 | 2.6097e-05 | 6.588 | 6.564 | 6.571 | 6.554 | 6.491 | 6.444 | 6.444 | 6.454 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 6.394 | 66.6035 | 0.37794 | 66.9814 | 4.1306e-06 | 1424.8971 | 770.2244 | 16.5057 | 0.09361 | 16.5993 | 50.3821 | -719.8423 | 0
| 60548436 | RVL | 1973 | 30275660 | 33063663 | 1774.97 | 49456.6662 | 172402.8361 | 0.0019812 | 0.0021295 | 0.0022906 | 0.0024654 | 0.0026553 | 0.0028617 | 0.003086 | 0.0033299 | 0.0035951 | 0.0038837 | 0.0041978 | 0.0045397 | 0.004912 | 0.0053176 | 0.0057595 | 0.0062411 | 0.0067661 | 0.0073386 | 0.007963 | 0.0086443 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 82283.0643 | 11301.115 | 93584.1792 | 0.00049977 | 172402.8361 | 93191.9062 | 9831.253 | 1370.3909 | 11201.6439 | 82382.5353 | -10809.3709 | 0
| 60548437 | RVL | 1998 | 33063770 | 33063753 | 1146.88 | 49456.6662 | 111396.4544 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 0.0012276 | 23.69 | 25.857 | 26.398 | 26.811 | 26.966 | 27.195 | 27.72 | 28.322 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 28.432 | 24148.494 | 2174.9667 | 26323.4607 | 0.00032292 | 111396.4544 | 60215.0647 | 6352.3707 | 572.1348 | 6924.5055 | 19398.9552 | -40816.1095 | 0
| 60470200 | CTN | 2014 | 30296762 | 30296761 | 43.71 | 45198.6405 | 4245.5523 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 4.6786e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 604.3649 | 3.1592 | 607.5241 | 1.2307e-05 | 4245.5523 | 2294.9223 | 158.9811 | 0.83104 | 159.8122 | 447.7119 | -1847.2104 | 0
| 60470201 | CTN | 2014 | 30296761 | 30296758 | 152.27 | 45198.6405 | 14789.9851 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 0.00016299 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 2105.3958 | 38.3394 | 2143.7352 | 4.2874e-05 | 14789.9851 | 7994.6881 | 553.8334 | 10.0854 | 563.9187 | 1579.8165 | -6414.8716 | 0
| 60470202 | CTN | 2014 | 30296758 | 30296754 | 167.4 | 45198.6405 | 16259.562 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 0.00017918 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 2314.5854 | 46.3368 | 2360.9223 | 4.7134e-05 | 16259.562 | 8789.0641 | 608.8639 | 12.1891 | 621.0531 | 1739.8692 | -7049.1949 | 0
| 60470203 | CTN | 2014 | 30296754 | 30296751 | 422.7 | 45198.6405 | 41056.851 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 0.00045244 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 5844.5482 | 295.4479 | 6139.996 | 0.00011902 | 41056.851 | 22193.1744 | 1537.4359 | 77.719 | 1615.1549 | 4524.8412 | -17668.3332 | 0
| 60470204 | CTN | 2014 | 30296751 | 30296750 | 51.5 | 45198.6405 | 5002.195 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 5.5124e-05 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 712.0755 | 4.3856 | 716.4611 | 1.4501e-05 | 5002.195 | 2703.9235 | 187.3148 | 1.1537 | 188.4684 | 527.9927 | -2175.9308 | 0
| 60470205 | CTN | 2014 | 30296750 | 30296744 | 640.4 | 45198.6405 | 62202.052 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 0.00068546 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 8854.6241 | 678.1396 | 9532.7637 | 0.00018031 | 62202.052 | 33623.158 | 2329.25 | 178.3878 | 2507.6378 | 7025.1259 | -26598.0321 | 0
| 60470307 | CME | 1999 | 33086444 | 33087524 | 8473.18 | 46875.2879 | 822999.9734 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 0.0090694 | 38.435 | 38.637 | 39.003 | 39.298 | 39.32 | 39.352 | 39.702 | 40.078 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 244240.795 | 118716.035 | 362956.83 | 0.0023858 | 822999.9734 | 444870.5025 | 64248.6678 | 31228.8006 | 95477.4684 | 267479.3616 | -177391.141 | 0
| 60470308 | CME | 1999 | 33087524 | 33086937 | 2137.78 | 46875.2879 | 207642.5714 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 0.0022882 | 38.435 | 38.637 | 39.003 | 39.298 | 39.32 | 39.352 | 39.702 | 40.078 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 61621.8476 | 7556.879 | 69178.7266 | 0.00060192 | 207642.5714 | 112240.6538 | 16209.9138 | 1987.8722 | 18197.786 | 50980.9406 | -61259.7132 | 0
| 60470309 | CME | 1999 | 33086937 | 33086929 | 94.54 | 46875.2879 | 9182.6702 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 0.00010119 | 38.435 | 38.637 | 39.003 | 39.298 | 39.32 | 39.352 | 39.702 | 40.078 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 2725.1443 | 14.7792 | 2739.9234 | 2.6619e-05 | 9182.6702 | 4963.6686 | 716.8583 | 3.8877 | 720.746 | 2019.1775 | -2944.4911 | 0
| 60470310 | CME | 1999 | 33086929 | 33085822 | 9285.08 | 46875.2879 | 901859.8204 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 0.0099384 | 38.435 | 38.637 | 39.003 | 39.298 | 39.32 | 39.352 | 39.702 | 40.078 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 267643.9708 | 142556.7744 | 410200.7452 | 0.0026144 | 901859.8204 | 487497.9884 | 70404.9743 | 37500.2135 | 107905.1878 | 302295.5574 | -185202.431 | 0
| 60470311 | CME | 1999 | 33085822 | 33085815 | 24.27 | 46875.2879 | 2357.3451 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 2.5978e-05 | 38.435 | 38.637 | 39.003 | 39.298 | 39.32 | 39.352 | 39.702 | 40.078 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 40.243 | 699.5865 | 0.97399 | 700.5605 | 6.8336e-06 | 2357.3451 | 1274.2568 | 184.0295 | 0.25621 | 184.2857 | 516.2747 | -757.9821 | 0
| 60470584 | CTN | 2014 | 30296163 | 30296143 | 2008.11 | 45198.6405 | 195047.7243 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 0.0021494 | 19.532 | 19.559 | 19.696 | 19.782 | 19.676 | 19.637 | 19.769 | 19.945 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 19.836 | 27765.5566 | 6667.9379 | 34433.4945 | 0.00056541 | 195047.7243 | 105432.5418 | 7303.8573 | 1754.0317 | 9057.889 | 25375.6056 | -80056.9363 | 0

## Sensitivities
Powercor
Risk-based replacement of deteriorated and aged 66kV radial lines
| Total | 57436009.7484 | 7750912.3412 | 49685097.4071 | 46 |  | 48910006.173 | 50460188.6413 | 55428698.382 | 43941496.4323 | 43166405.1982 | 411
|  | Option 2 | Option 2 | Option 2 | Option 2 | Capex sensitivity | 10% | -10% | 0% | 0% | 10% | Preferred
|  | Total benefits | Annualised capex |  | preferred | Benefits sensitivity | 0% | 0% | 10% | -10% | -10% | option
| Feeders | PV ($2023) | PV ($2023) | NPV ($2023) |  |  | Sensitivity 1 | Sensitivity 2 | Sensitivity 3 | Sensitivity 4 | Sensitivity 5 | unchanged
| 60555946 | 1142.0891 | 6116.6426 | -4974.5535 | 0 |  | -5586.2177 | -4362.8892 | -4860.3445 | -5088.7624 | -5700.4266 | 1
| 60555953 | 25384.0818 | 76984.116 | -51600.0342 | 0 |  | -59298.4458 | -43901.6226 | -49061.626 | -54138.4424 | -61836.854 | 1
| 60555962 | 1110901.9942 | 172456.7686 | 938445.2257 | 1 |  | 921199.5488 | 955690.9025 | 1049535.4251 | 827355.0263 | 810109.3494 | 1
| 60555980 | 3382.2735 | 11362.7793 | -7980.5057 | 0 |  | -9116.7837 | -6844.2278 | -7642.2784 | -8318.7331 | -9455.011 | 1
| 60555985 | 469.4323 | 2586.841 | -2117.4087 | 0 |  | -2376.0928 | -1858.7246 | -2070.4655 | -2164.3519 | -2423.036 | 1
| 60556023 | 2051.1506 | 6860.0903 | -4808.9397 | 0 |  | -5494.9487 | -4122.9307 | -4603.8247 | -5014.0548 | -5700.0638 | 1
| 60556219 | 36345.6617 | 82387.7628 | -46042.1011 | 0 |  | -54280.8774 | -37803.3248 | -42407.5349 | -49676.6673 | -57915.4436 | 1
| 60556221 | 203.8005 | 792.8009 | -589.0004 | 0 |  | -668.2805 | -509.7203 | -568.6203 | -609.3804 | -688.6605 | 1
| 60652205 | 13422.265 | 42622.2356 | -29199.9706 | 0 |  | -33462.1942 | -24937.747 | -27857.7441 | -30542.1971 | -34804.4206 | 1
| 60652302 | 9927.3176 | 12535.1795 | -2607.862 | 0 |  | -3861.3799 | -1354.344 | -1615.1302 | -3600.5937 | -4854.1117 | 1
| 60652318 | 1312.6957 | 4420.7837 | -3108.0881 | 0 |  | -3550.1664 | -2666.0097 | -2976.8185 | -3239.3576 | -3681.436 | 1
| 60652444 | 1312.6957 | 4420.7837 | -3108.0881 | 0 |  | -3550.1664 | -2666.0097 | -2976.8185 | -3239.3576 | -3681.436 | 1
| 60652627 | 111.0259 | 455.2042 | -344.1783 | 0 |  | -389.6988 | -298.6579 | -333.0758 | -355.2809 | -400.8014 | 1
| 60652630 | 1265.8392 | 3644.2589 | -2378.4197 | 0 |  | -2742.8456 | -2013.9938 | -2251.8358 | -2505.0036 | -2869.4295 | 1
| 60652643 | 34487.4112 | 41801.0829 | -7313.6717 | 0 |  | -11493.7799 | -3133.5634 | -3864.9305 | -10762.4128 | -14942.5211 | 1
| 60652659 | 160962.291 | 166318.0746 | -5355.7835 | 0 |  | -21987.591 | 11276.0239 | 10740.4456 | -21452.0126 | -38083.8201 | 1
| 60652797 | 12727705.8577 | 901694.9723 | 11826010.8854 | 1 |  | 11735841.3882 | 11916180.3826 | 13098781.4712 | 10553240.2996 | 10463070.8024 | 1
| 60652986 | 970.7573 | 2620.9682 | -1650.211 | 0 |  | -1912.3078 | -1388.1141 | -1553.1352 | -1747.2867 | -2009.3835 | 1
| 60669975 | 316.1762 | 1589.277 | -1273.1008 | 0 |  | -1432.0285 | -1114.1731 | -1241.4832 | -1304.7184 | -1463.6461 | 1
| 60669993 | 10576.6791 | 49170.9809 | -38594.3017 | 0 |  | -43511.3998 | -33677.2037 | -37536.6338 | -39651.9697 | -44569.0677 | 1
| 60670043 | 1572.9736 | 4418.1586 | -2845.185 | 0 |  | -3287.0008 | -2403.3691 | -2687.8876 | -3002.4823 | -3444.2982 | 1
| 60670055 | 378.3487 | 1165.0498 | -786.7011 | 0 |  | -903.2061 | -670.1961 | -748.8662 | -824.536 | -941.0409 | 1
| 60670067 | 1591.1888 | 4272.7242 | -2681.5354 | 0 |  | -3108.8079 | -2254.263 | -2522.4166 | -2840.6543 | -3267.9267 | 1
| 60670073 | 755.1212 | 3525.0762 | -2769.9551 | 0 |  | -3122.4627 | -2417.4474 | -2694.443 | -2845.4672 | -3197.9748 | 1
| 60555940 | 132.9624 | 5893.5033 | -5760.5408 | 0 |  | -6349.8912 | -5171.1905 | -5747.2446 | -5773.8371 | -6363.1874 | 1
| 60554187 | 6173.2801 | 7852.929 | -1679.649 | 0 |  | -2464.9419 | -894.3561 | -1062.3209 | -2296.977 | -3082.2699 | 1
| 60554191 | 1162.7797 | 3960.3292 | -2797.5494 | 0 |  | -3193.5824 | -2401.5165 | -2681.2715 | -2913.8274 | -3309.8603 | 1
| 60554210 | 184.4966 | 1072.6438 | -888.1472 | 0 |  | -995.4116 | -780.8828 | -869.6976 | -906.5969 | -1013.8613 | 1
| 60554215 | 572.9829 | 2043.9562 | -1470.9732 | 0 |  | -1675.3689 | -1266.5776 | -1413.675 | -1528.2715 | -1732.6672 | 1
| 60554221 | 17054.5189 | 75057.2423 | -58002.7234 | 0 |  | -65508.4477 | -50496.9992 | -56297.2716 | -59708.1753 | -67213.8996 | 1
| 60554226 | 2216.0423 | 7187.7113 | -4971.669 | 0 |  | -5690.4401 | -4252.8979 | -4750.0648 | -5193.2732 | -5912.0444 | 1
| 60554247 | 12242.3262 | 55775.9048 | -43533.5786 | 0 |  | -49111.1691 | -37955.9881 | -42309.346 | -44757.8112 | -50335.4017 | 1
| 60554256 | 10222.8538 | 47794.8676 | -37572.0137 | 0 |  | -42351.5005 | -32792.527 | -36549.7284 | -38594.2991 | -43373.7859 | 1
| 60554278 | 1600.7491 | 5460.8755 | -3860.1263 | 0 |  | -4406.2139 | -3314.0388 | -3700.0514 | -4020.2013 | -4566.2888 | 1
| 60554279 | 717949.663 | 121563.1521 | 596386.5109 | 1 |  | 584230.1957 | 608542.8261 | 668181.4772 | 524591.5446 | 512435.2294 | 1
| 60554285 | 586.0557 | 2781.6285 | -2195.5729 | 0 |  | -2473.7357 | -1917.41 | -2136.9673 | -2254.1784 | -2532.3413 | 1
| 60554344 | 892.6793 | 2761.1522 | -1868.4729 | 0 |  | -2144.5882 | -1592.3577 | -1779.205 | -1957.7409 | -2233.8561 | 1
| 60554356 | 811.2559 | 1852.8439 | -1041.588 | 0 |  | -1226.8724 | -856.3036 | -960.4624 | -1122.7136 | -1307.998 | 1
| 60554362 | 1174.0628 | 31643.2559 | -30469.1931 | 0 |  | -33633.5187 | -27304.8675 | -30351.7868 | -30586.5994 | -33750.925 | 1
| 60554459 | 13597.5948 | 42986.609 | -29389.0141 | 0 |  | -33687.675 | -25090.3532 | -28029.2547 | -30748.7736 | -35047.4345 | 1
| 60554471 | 15401.1927 | 68893.8717 | -53492.679 | 0 |  | -60382.0662 | -46603.2918 | -51952.5597 | -55032.7983 | -61922.1855 | 1
| 60554472 | 5981.9565 | 19490.3009 | -13508.3444 | 0 |  | -15457.3745 | -11559.3143 | -12910.1488 | -14106.5401 | -16055.5701 | 1
| 60554484 | 25821.7746 | 4664.9244 | 21156.8502 | 1 |  | 20690.3578 | 21623.3427 | 23739.0277 | 18574.6728 | 18108.1803 | 1
| 60554498 | 6012.5994 | 91591.0785 | -85578.4791 | 0 |  | -94737.5869 | -76419.3712 | -84977.2192 | -86179.739 | -95338.8469 | 1
| 60554500 | 580.0941 | 2868.7841 | -2288.69 | 0 |  | -2575.5684 | -2001.8116 | -2230.6806 | -2346.6994 | -2633.5778 | 1
| 60554517 | 3031.1643 | 7144.6586 | -4113.4943 | 0 |  | -4827.9601 | -3399.0284 | -3810.3778 | -4416.6107 | -5131.0766 | 1
| 60554539 | 960.449 | 4936.8919 | -3976.4429 | 0 |  | -4470.1321 | -3482.7537 | -3880.398 | -4072.4878 | -4566.177 | 1
| 60554558 | 2985657.7274 | 356398.1242 | 2629259.6031 | 1 |  | 2593619.7907 | 2664899.4156 | 2927825.3759 | 2330693.8304 | 2295054.018 | 1
| 60554568 | 8124.4712 | 26630.7592 | -18506.288 | 0 |  | -21169.3639 | -15843.2121 | -17693.8409 | -19318.7351 | -21981.811 | 1
| 60554582 | 656.8581 | 21890.755 | -21233.8968 | 0 |  | -23422.9723 | -19044.8213 | -21168.211 | -21299.5827 | -23488.6582 | 1
| 60554597 | 184.4966 | 1072.6438 | -888.1472 | 0 |  | -995.4116 | -780.8828 | -869.6976 | -906.5969 | -1013.8613 | 1
| 60554599 | 28248.1956 | 85040.233 | -56792.0374 | 0 |  | -65296.0607 | -48288.0141 | -53967.2178 | -59616.857 | -68120.8803 | 1
| 60554623 | 244.3784 | 9538.2872 | -9293.9087 | 0 |  | -10247.7375 | -8340.08 | -9269.4709 | -9318.3466 | -10272.1753 | 1
| 60554633 | 420326.167 | 871005.1775 | -450679.0105 | 0 |  | -537779.5283 | -363578.4928 | -408646.3938 | -492711.6272 | -579812.145 | 1
| 60554635 | 958.082 | 27598.9213 | -26640.8394 | 0 |  | -29400.7315 | -23880.9472 | -26545.0312 | -26736.6476 | -29496.5397 | 1
| 60554184 | 1330.5879 | 4249.0977 | -2918.5098 | 0 |  | -3343.4196 | -2493.6001 | -2785.4511 | -3051.5686 | -3476.4784 | 1
| 60548967 | 65.569 | 751.8483 | -686.2793 | 0 |  | -761.4641 | -611.0945 | -679.7224 | -692.8362 | -768.021 | 1
| 60548982 | 11305.0385 | 36351.7581 | -25046.7196 | 0 |  | -28681.8954 | -21411.5438 | -23916.2158 | -26177.2235 | -29812.3993 | 1
| 60553885 | 591.5497 | 1867.0198 | -1275.4701 | 0 |  | -1462.1721 | -1088.7681 | -1216.3151 | -1334.6251 | -1521.327 | 1
| 60553888 | 2157.3171 | 2761.1522 | -603.8351 | 0 |  | -879.9504 | -327.7199 | -388.1034 | -819.5668 | -1095.6821 | 1
| 60553897 | 82318.2582 | 351967.8899 | -269649.6317 | 0 |  | -304846.4207 | -234452.8427 | -261417.8059 | -277881.4575 | -313078.2465 | 1
| 60553934 | 3101.0192 | 10205.605 | -7104.5858 | 0 |  | -8125.1463 | -6084.0253 | -6794.4839 | -7414.6878 | -8435.2483 | 1
| 60553939 | 1579682.8682 | 203621.7188 | 1376061.1494 | 1 |  | 1355698.9776 | 1396423.3213 | 1534029.4363 | 1218092.8626 | 1197730.6907 | 1
| 60553973 | 252.8772 | 10295.9108 | -10043.0336 | 0 |  | -11072.6247 | -9013.4425 | -10017.7458 | -10068.3213 | -11097.9124 | 1
| 60554004 | 1449.2592 | 5011.4466 | -3562.1874 | 0 |  | -4063.3321 | -3061.0427 | -3417.2615 | -3707.1133 | -4208.258 | 1
| 60554030 | 164.8753 | 931.9348 | -767.0595 | 0 |  | -860.253 | -673.866 | -750.572 | -783.547 | -876.7405 | 1
| 60554032 | 40513.6117 | 116932.8799 | -76419.2682 | 0 |  | -88112.5562 | -64725.9802 | -72367.907 | -80470.6294 | -92163.9174 | 1
| 60554065 | 47502.2777 | 133929.7958 | -86427.5181 | 0 |  | -99820.4977 | -73034.5386 | -81677.2904 | -91177.7459 | -104570.7255 | 1
| 60554066 | 243.8169 | 9387.0775 | -9143.2606 | 0 |  | -10081.9683 | -8204.5528 | -9118.8789 | -9167.6423 | -10106.35 | 1
| 60554101 | 5070.4449 | 16493.4086 | -11422.9637 | 0 |  | -13072.3046 | -9773.6228 | -10915.9192 | -11930.0082 | -13579.349 | 1
| 60554107 | 15745.8035 | 49334.7914 | -33588.9879 | 0 |  | -38522.467 | -28655.5087 | -32014.4075 | -35163.5682 | -40097.0474 | 1
| 60555573 | 16115.5192 | 3452.6216 | 12662.8976 | 1 |  | 12317.6354 | 13008.1597 | 14274.4495 | 11051.3456 | 10706.0835 | 1
| 60555574 | 581.7993 | 1959.9508 | -1378.1515 | 0 |  | -1574.1466 | -1182.1564 | -1319.9716 | -1436.3315 | -1632.3265 | 1
| 60555640 | 31.4119 | 403.2259 | -371.814 | 0 |  | -412.1366 | -331.4914 | -368.6728 | -374.9552 | -415.2777 | 1
| 60555737 | 6582.1117 | 21607.2368 | -15025.1251 | 0 |  | -17185.8488 | -12864.4014 | -14366.9139 | -15683.3363 | -17844.0599 | 1
| 60555750 | 566.5897 | 2104.8601 | -1538.2704 | 0 |  | -1748.7564 | -1327.7844 | -1481.6114 | -1594.9294 | -1805.4154 | 1
| 60555752 | 15071.444 | 18862.3606 | -3790.9166 | 0 |  | -5677.1526 | -1904.6805 | -2283.7722 | -5298.061 | -7184.297 | 1
| 60555770 | 10993.3744 | 35272.8139 | -24279.4394 | 0 |  | -27806.7208 | -20752.158 | -23180.102 | -25378.7769 | -28906.0583 | 1
| 60555795 | 74.1199 | 3391.7177 | -3317.5978 | 0 |  | -3656.7696 | -2978.426 | -3310.1858 | -3325.0098 | -3664.1816 | 1
| 60555811 | 14401.005 | 45629.1036 | -31228.0986 | 0 |  | -35791.0089 | -26665.1882 | -29787.9981 | -32668.1991 | -37231.1094 | 1
| 60555814 | 975376.1704 | 139228.4359 | 836147.7345 | 1 |  | 822224.8909 | 850070.5781 | 933685.3516 | 738610.1175 | 724687.2739 | 1
| 60555815 | 107642.0723 | 215100.5305 | -107458.4582 | 0 |  | -128968.5113 | -85948.4052 | -96694.251 | -118222.6654 | -139732.7185 | 1
| 60555821 | 2281.6699 | 49948.5558 | -47666.8858 | 0 |  | -52661.7414 | -42672.0303 | -47438.7188 | -47895.0528 | -52889.9084 | 1
| 60555840 | 1553509.8453 | 222830.0766 | 1330679.7687 | 1 |  | 1308396.761 | 1352962.7763 | 1486030.7532 | 1175328.7841 | 1153045.7765 | 1
| 60555841 | 1030.6331 | 29090.5421 | -28059.909 | 0 |  | -30968.9632 | -25150.8548 | -27956.8457 | -28162.9723 | -31072.0265 | 1
| 60555843 | 2805.4861 | 9196.4902 | -6391.0041 | 0 |  | -7310.6531 | -5471.3551 | -6110.4555 | -6671.5527 | -7591.2017 | 1
| 60555867 | 213.5264 | 8351.711 | -8138.1846 | 0 |  | -8973.3557 | -7303.0135 | -8116.8319 | -8159.5372 | -8994.7083 | 1
| 60555871 | 1358.6751 | 6791.8359 | -5433.1608 | 0 |  | -6112.3444 | -4753.9773 | -5297.2933 | -5569.0284 | -6248.2119 | 1
| 60555888 | 63.0208 | 2887.6853 | -2824.6646 | 0 |  | -3113.4331 | -2535.896 | -2818.3625 | -2830.9666 | -3119.7352 | 1
| 60555891 | 11095.7995 | 13984.7976 | -2888.9981 | 0 |  | -4287.4779 | -1490.5183 | -1779.4181 | -3998.578 | -5397.0578 | 1
| 60555899 | 243.6204 | 9146.612 | -8902.9917 | 0 |  | -9817.6529 | -7988.3305 | -8878.6296 | -8927.3537 | -9842.0149 | 1
| 60555903 | 2241.1019 | 11352.8036 | -9111.7017 | 0 |  | -10246.9821 | -7976.4213 | -8887.5915 | -9335.8119 | -10471.0923 | 1
| 60555904 | 1701184.6563 | 221078.5642 | 1480106.0922 | 1 |  | 1457998.2357 | 1502213.9486 | 1650224.5578 | 1309987.6265 | 1287879.7701 | 1
| 60555905 | 68925.4886 | 79371.9692 | -10446.4806 | 0 |  | -18383.6776 | -2509.2837 | -3553.9318 | -17339.0295 | -25276.2264 | 1
| 60555915 | 148020.7223 | 29949.4972 | 118071.2251 | 1 |  | 115076.2754 | 121066.1748 | 132873.2973 | 103269.1529 | 100274.2032 | 1
| 60555938 | 1340064.6723 | 199290.7158 | 1140773.9565 | 1 |  | 1120844.885 | 1160703.0281 | 1274780.4238 | 1006767.4893 | 986838.4177 | 1
| 60554643 | 10148.6719 | 124761.1324 | -114612.4605 | 0 |  | -127088.5737 | -102136.3473 | -113597.5933 | -115627.3277 | -128103.4409 | 1
| 60554735 | 301.2457 | 1257.9807 | -956.735 | 0 |  | -1082.5331 | -830.937 | -926.6105 | -986.8596 | -1112.6577 | 1
| 60554744 | 196175.4998 | 411019.4799 | -214843.9801 | 0 |  | -255945.9281 | -173742.0322 | -195226.4302 | -234461.5301 | -275563.4781 | 1
| 60554745 | 18580.9205 | 57952.6945 | -39371.774 | 0 |  | -45167.0434 | -33576.5045 | -37513.6819 | -41229.866 | -47025.1355 | 1
| 60554800 | 1142.2752 | 4156.6918 | -3014.4165 | 0 |  | -3430.0857 | -2598.7474 | -2900.189 | -3128.6441 | -3544.3132 | 1
| 60554818 | 272.3606 | 1677.4827 | -1405.122 | 0 |  | -1572.8703 | -1237.3738 | -1377.886 | -1432.3581 | -1600.1064 | 1
| 60554830 | 10041.3158 | 32269.6211 | -22228.3053 | 0 |  | -25455.2674 | -19001.3432 | -21224.1737 | -23232.4369 | -26459.399 | 1
| 60554835 | 4303.5845 | 14126.0316 | -9822.4471 | 0 |  | -11235.0503 | -8409.844 | -9392.0887 | -10252.8056 | -11665.4087 | 1
| 60554842 | 15794.2201 | 70020.069 | -54225.8489 | 0 |  | -61227.8558 | -47223.842 | -52646.4269 | -55805.2709 | -62807.2778 | 1
| 60554844 | 6443.7508 | 20957.2451 | -14513.4943 | 0 |  | -16609.2188 | -12417.7698 | -13869.1192 | -15157.8694 | -17253.5939 | 1
| 60554851 | 1840625.1025 | 252640.9649 | 1587984.1376 | 1 |  | 1562720.0411 | 1613248.2341 | 1772046.6478 | 1403921.6273 | 1378657.5308 | 1
| 60554866 | 92598.8608 | 19174.7557 | 73424.1051 | 1 |  | 71506.6295 | 75341.5807 | 82683.9912 | 64164.219 | 62246.7435 | 1
| 60554921 | 601.1873 | 1775.1389 | -1173.9516 | 0 |  | -1351.4655 | -996.4377 | -1113.8328 | -1234.0703 | -1411.5842 | 1
| 60554944 | 372.6367 | 2105.3851 | -1732.7485 | 0 |  | -1943.287 | -1522.21 | -1695.4848 | -1770.0121 | -1980.5506 | 1
| 60554958 | 371.8424 | 2116.9359 | -1745.0935 | 0 |  | -1956.7871 | -1533.3999 | -1707.9093 | -1782.2777 | -1993.9713 | 1
| 60554965 | 11986.3009 | 55122.7629 | -43136.4619 | 0 |  | -48648.7382 | -37624.1857 | -41937.8318 | -44335.092 | -49847.3683 | 1
| 60554968 | 15393.0936 | 48575.0676 | -33181.974 | 0 |  | -38039.4808 | -28324.4672 | -31642.6646 | -34721.2834 | -39578.7901 | 1
| 60554977 | 39.7756 | 2136.8871 | -2097.1116 | 0 |  | -2310.8003 | -1883.4229 | -2093.134 | -2101.0891 | -2314.7779 | 1
| 60554994 | 58571.1222 | 159782.4551 | -101211.3329 | 0 |  | -117189.5784 | -85233.0873 | -95354.2206 | -107068.4451 | -123046.6906 | 1
| 60554999 | 243539.2757 | 47502.4238 | 196036.8519 | 1 |  | 191286.6095 | 200787.0943 | 220390.7795 | 171682.9243 | 166932.6819 | 1
| 60555007 | 1311.4369 | 4432.8595 | -3121.4227 | 0 |  | -3564.7086 | -2678.1367 | -2990.279 | -3252.5663 | -3695.8523 | 1
| 60555024 | 853.0346 | 4596.145 | -3743.1104 | 0 |  | -4202.7249 | -3283.4959 | -3657.8069 | -3828.4138 | -4288.0283 | 1
| 60555035 | 5042.3064 | 16772.7265 | -11730.4201 | 0 |  | -13407.6927 | -10053.1474 | -11226.1894 | -12234.6507 | -13911.9234 | 1
| 60555036 | 1141.3785 | 6127.1433 | -4985.7648 | 0 |  | -5598.4791 | -4373.0504 | -4871.6269 | -5099.9026 | -5712.6169 | 1
| 60555040 | 882090.3641 | 127489.2075 | 754601.1567 | 1 |  | 741852.2359 | 767350.0774 | 842810.1931 | 666392.1203 | 653643.1995 | 1
| 60555045 | 31.1328 | 416.3517 | -385.2189 | 0 |  | -426.8541 | -343.5838 | -382.1056 | -388.3322 | -429.9674 | 1
| 60555056 | 229.1983 | 525.0337 | -295.8354 | 0 |  | -348.3387 | -243.332 | -272.9155 | -318.7552 | -371.2586 | 1
| 60555102 | 21792.7724 | 92678.4233 | -70885.6509 | 0 |  | -80153.4932 | -61617.8085 | -68706.3736 | -73064.9281 | -82332.7704 | 1
| 60555569 | 436.12 | 6527.2189 | -6091.0989 | 0 |  | -6743.8208 | -5438.377 | -6047.4869 | -6134.7109 | -6787.4328 | 1
| 60845175 | 148253.0588 | 25575.9665 | 122677.0923 | 1 |  | 120119.4956 | 125234.6889 | 137502.3981 | 107851.7864 | 105294.1897 | 1
| 60846589 | 747110.8176 | 264765.0431 | 482345.7745 | 1 |  | 455869.2702 | 508822.2788 | 557056.8563 | 407634.6928 | 381158.1885 | 1
| 60846644 | 241580.9673 | 40524.2009 | 201056.7664 | 1 |  | 197004.3463 | 205109.1865 | 225214.8631 | 176898.6697 | 172846.2496 | 1
| 60859339 | 1161.7938 | 2889.2604 | -1727.4666 | 0 |  | -2016.3927 | -1438.5406 | -1611.2872 | -1843.646 | -2132.572 | 1
| 60859340 | 771.2563 | 1943.6747 | -1172.4185 | 0 |  | -1366.7859 | -978.051 | -1095.2928 | -1249.5441 | -1443.9116 | 1
| 60859342 | 1132.9528 | 3097.1738 | -1964.221 | 0 |  | -2273.9384 | -1654.5036 | -1850.9257 | -2077.5163 | -2387.2336 | 1
| 60823678 | 184.1705 | 1077.3691 | -893.1987 | 0 |  | -1000.9356 | -785.4618 | -874.7816 | -911.6157 | -1019.3526 | 1
| 60823677 | 176.0502 | 1194.9767 | -1018.9265 | 0 |  | -1138.4241 | -899.4288 | -1001.3215 | -1036.5315 | -1156.0292 | 1
| 60823590 | 295.8995 | 1335.6857 | -1039.7863 | 0 |  | -1173.3548 | -906.2177 | -1010.1963 | -1069.3762 | -1202.9448 | 1
| 60823555 | 300.1622 | 1273.7318 | -973.5696 | 0 |  | -1100.9428 | -846.1964 | -943.5534 | -1003.5858 | -1130.959 | 1
| 60823548 | 5919.5448 | 1273.7318 | 4645.8131 | 1 |  | 4518.4399 | 4773.1862 | 5237.7676 | 4053.8586 | 3926.4854 | 1
| 60823535 | 295.8995 | 1335.6857 | -1039.7863 | 0 |  | -1173.3548 | -906.2177 | -1010.1963 | -1069.3762 | -1202.9448 | 1
| 60859343 | 556.3918 | 1613.9536 | -1057.5617 | 0 |  | -1218.9571 | -896.1664 | -1001.9226 | -1113.2009 | -1274.5963 | 1
| 60859403 | 1933.8311 | 4863.9122 | -2930.0811 | 0 |  | -3416.4723 | -2443.6899 | -2736.698 | -3123.4642 | -3609.8554 | 1
| 60859404 | 1161.7938 | 2889.2604 | -1727.4666 | 0 |  | -2016.3927 | -1438.5406 | -1611.2872 | -1843.646 | -2132.572 | 1
| 60859408 | 1343.0795 | 3465.2224 | -2122.1429 | 0 |  | -2468.6651 | -1775.6206 | -1987.8349 | -2256.4508 | -2602.9731 | 1
| 60859588 | 1125.1576 | 3153.3524 | -2028.1948 | 0 |  | -2343.5301 | -1712.8596 | -1915.6791 | -2140.7106 | -2456.0458 | 1
| 60859590 | 1391.4023 | 5789.5466 | -4398.1443 | 0 |  | -4977.099 | -3819.1896 | -4259.0041 | -4537.2845 | -5116.2392 | 1
| 60859591 | 7838.7075 | 19631.535 | -11792.8275 | 0 |  | -13755.981 | -9829.674 | -11008.9567 | -12576.6982 | -14539.8517 | 1
| 60859634 | 16423.7194 | 40338.864 | -23915.1446 | 0 |  | -27949.031 | -19881.2582 | -22272.7726 | -25557.5165 | -29591.4029 | 1
| 60859637 | 2901.9697 | 7344.6964 | -4442.7267 | 0 |  | -5177.1963 | -3708.257 | -4152.5297 | -4732.9236 | -5467.3933 | 1
| 60859642 | 557.8531 | 1603.4529 | -1045.5998 | 0 |  | -1205.9451 | -885.2545 | -989.8145 | -1101.3851 | -1261.7304 | 1
| 60859660 | 56788.597 | 127134.8097 | -70346.2127 | 0 |  | -83059.6937 | -57632.7317 | -64667.353 | -76025.0724 | -88738.5534 | 1
| 60859664 | 6617.4356 | 16863.0323 | -10245.5967 | 0 |  | -11931.9 | -8559.2935 | -9583.8532 | -10907.3403 | -12593.6435 | 1
| 60859667 | 8615.1096 | 21790.9986 | -13175.889 | 0 |  | -15354.9888 | -10996.7891 | -12314.378 | -14037.3999 | -16216.4998 | 1
| 60859669 | 5078.9864 | 12594.5083 | -7515.522 | 0 |  | -8774.9728 | -6256.0711 | -7007.6233 | -8023.4206 | -9282.8714 | 1
| 60859672 | 3276.4641 | 8440.9668 | -5164.5026 | 0 |  | -6008.5993 | -4320.4059 | -4836.8562 | -5492.149 | -6336.2457 | 1
| 60859674 | 2899.1554 | 7365.1727 | -4466.0173 | 0 |  | -5202.5346 | -3729.5001 | -4176.1018 | -4755.9329 | -5492.4501 | 1
| 60740562 | 2333.9736 | 11954.4923 | -9620.5186 | 0 |  | -10815.9679 | -8425.0694 | -9387.1213 | -9853.916 | -11049.3652 | 1
| 60767383 | 1572.9736 | 4418.1586 | -2845.185 | 0 |  | -3287.0008 | -2403.3691 | -2687.8876 | -3002.4823 | -3444.2982 | 1
| 60767389 | 24963.0038 | 60178.8374 | -35215.8336 | 0 |  | -41233.7173 | -29197.9499 | -32719.5332 | -37712.134 | -43730.0177 | 1
| 60770694 | 8930.4402 | 22515.0201 | -13584.5799 | 0 |  | -15836.0819 | -11333.0778 | -12691.5358 | -14477.6239 | -16729.1259 | 1
| 60785776 | 680890.0935 | 103020.012 | 577870.0815 | 1 |  | 567568.0803 | 588172.0827 | 645959.0908 | 509781.0721 | 499479.0709 | 1
| 60785863 | 1651353.4682 | 211722.9887 | 1439630.4795 | 1 |  | 1418458.1806 | 1460802.7783 | 1604765.8263 | 1274495.1326 | 1253322.8338 | 1
| 60796872 | 238.2201 | 3568.654 | -3330.434 | 0 |  | -3687.2994 | -2973.5686 | -3306.612 | -3354.256 | -3711.1214 | 1
| 60797805 | 1973.9912 | 25541.8393 | -23567.8482 | 0 |  | -26122.0321 | -21013.6642 | -23370.449 | -23765.2473 | -26319.4312 | 1
| 60823120 | 341.7929 | 1754.1376 | -1412.3447 | 0 |  | -1587.7585 | -1236.931 | -1378.1654 | -1446.524 | -1621.9378 | 1
| 60823125 | 344.0515 | 1765.6883 | -1421.6368 | 0 |  | -1598.2057 | -1245.068 | -1387.2317 | -1456.042 | -1632.6108 | 1
| 60860110 | 5197.0762 | 13100.6408 | -7903.5646 | 0 |  | -9213.6287 | -6593.5005 | -7383.857 | -8423.2722 | -9733.3363 | 1
| 60860115 | 291.6048 | 1243.8048 | -952.2001 | 0 |  | -1076.5806 | -827.8196 | -923.0396 | -981.3606 | -1105.741 | 1
| 60860119 | 5477.2842 | 13796.3105 | -8319.0263 | 0 |  | -9698.6573 | -6939.3952 | -7771.2978 | -8866.7547 | -10246.3857 | 1
| 60860120 | 13879.6922 | 34184.419 | -20304.7268 | 0 |  | -23723.1687 | -16886.2849 | -18916.7576 | -21692.696 | -25111.1379 | 1
| 60860121 | 2207.7705 | 5612.0852 | -3404.3147 | 0 |  | -3965.5232 | -2843.1062 | -3183.5377 | -3625.0918 | -4186.3003 | 1
| 60860123 | 10088.997 | 25096.6107 | -15007.6137 | 0 |  | -17517.2748 | -12497.9527 | -13998.7141 | -16016.5134 | -18526.1745 | 1
| 60860134 | 1042.4725 | 2658.7706 | -1616.2981 | 0 |  | -1882.1752 | -1350.4211 | -1512.0509 | -1720.5454 | -1986.4224 | 1
| 60860135 | 14475.5941 | 35597.2847 | -21121.6906 | 0 |  | -24681.4191 | -17561.9621 | -19674.1312 | -22569.25 | -26128.9785 | 1
| 60860138 | 27841.8723 | 66258.2026 | -38416.3303 | 0 |  | -45042.1505 | -31790.51 | -35632.1431 | -41200.5175 | -47826.3378 | 1
| 60860244 | 606.5247 | 1548.8494 | -942.3247 | 0 |  | -1097.2097 | -787.4398 | -881.6723 | -1002.9772 | -1157.8621 | 1
| 60860280 | 1116.4064 | 2846.7327 | -1730.3263 | 0 |  | -2014.9996 | -1445.6531 | -1618.6857 | -1841.967 | -2126.6402 | 1
| 60863023 | 5021.5977 | 1082.6195 | 3938.9782 | 1 |  | 3830.7162 | 4047.2401 | 4441.138 | 3436.8184 | 3328.5565 | 1
| 60863185 | 9633.856 | 23993.5149 | -14359.6589 | 0 |  | -16759.0104 | -11960.3075 | -13396.2733 | -15323.0445 | -17722.396 | 1
| 60863224 | 11595.967 | 28730.369 | -17134.402 | 0 |  | -20007.4389 | -14261.3651 | -15974.8053 | -18293.9987 | -21167.0356 | 1
| 60863436 | 3341159.4275 | 385002.4851 | 2956156.9424 | 1 |  | 2917656.6939 | 2994657.191 | 3290272.8852 | 2622040.9997 | 2583540.7512 | 1
| 60863646 | 6511.752 | 16355.3247 | -9843.5727 | 0 |  | -11479.1052 | -8208.0402 | -9192.3975 | -10494.7479 | -12130.2804 | 1
| 60863651 | 3025.2348 | 7672.3174 | -4647.0826 | 0 |  | -5414.3144 | -3879.8509 | -4344.5592 | -4949.6061 | -5716.8379 | 1
| 60872966 | 81263.3798 | 389788.1672 | -308524.7874 | 0 |  | -347503.6042 | -269545.9707 | -300398.4495 | -316651.1254 | -355629.9421 | 1
| 60872973 | 2661.8579 | 55275.0226 | -52613.1648 | 0 |  | -58140.6671 | -47085.6625 | -52346.979 | -52879.3506 | -58406.8528 | 1
| 60876392 | 2143.5855 | 10780.5169 | -8636.9314 | 0 |  | -9714.9831 | -7558.8797 | -8422.5728 | -8851.2899 | -9929.3416 | 1
| 60876546 | 1311.0997 | 6654.8021 | -5343.7025 | 0 |  | -6009.1827 | -4678.2223 | -5212.5925 | -5474.8124 | -6140.2926 | 1
| 60860099 | 761.4775 | 1943.6747 | -1182.1972 | 0 |  | -1376.5647 | -987.8297 | -1106.0495 | -1258.345 | -1452.7124 | 1
| 60859677 | 10893.1765 | 27039.2354 | -16146.0589 | 0 |  | -18849.9824 | -13442.1354 | -15056.7412 | -17235.3765 | -19939.3001 | 1
| 60859679 | 1237.9091 | 3155.4525 | -1917.5434 | 0 |  | -2233.0887 | -1601.9982 | -1793.7525 | -2041.3343 | -2356.8796 | 1
| 60859680 | 13339.5901 | 32900.1866 | -19560.5965 | 0 |  | -22850.6151 | -16270.5778 | -18226.6374 | -20894.5555 | -24184.5741 | 1
| 60859734 | 337.5413 | 862.6304 | -525.089 | 0 |  | -611.3521 | -438.826 | -491.3349 | -558.8432 | -645.1062 | 1
| 60859738 | 20582.4966 | 49843.024 | -29260.5274 | 0 |  | -34244.8298 | -24276.225 | -27202.2777 | -31318.777 | -36303.0795 | 1
| 60859739 | 9003.5054 | 22461.4666 | -13457.9612 | 0 |  | -15704.1079 | -11211.8146 | -12557.6107 | -14358.3118 | -16604.4584 | 1
| 60859741 | 17078.1663 | 41719.7026 | -24641.5363 | 0 |  | -28813.5066 | -20469.5661 | -22933.7197 | -26349.353 | -30521.3232 | 1
| 60859771 | 10123.066 | 25179.041 | -15055.975 | 0 |  | -17573.8791 | -12538.0709 | -14043.6684 | -16068.2816 | -18586.1857 | 1
| 60859772 | 1231.5016 | 3139.1765 | -1907.6748 | 0 |  | -2221.5925 | -1593.7572 | -1784.5247 | -2030.825 | -2344.7426 | 1
| 60859773 | 3040.9017 | 7711.6949 | -4670.7933 | 0 |  | -5441.9628 | -3899.6238 | -4366.7031 | -4974.8835 | -5746.053 | 1
| 60859774 | 1342.5326 | 3421.1196 | -2078.587 | 0 |  | -2420.699 | -1736.475 | -1944.3337 | -2212.8403 | -2554.9522 | 1
| 60859776 | 6339.215 | 15929.5224 | -9590.3074 | 0 |  | -11183.2597 | -7997.3552 | -8956.3859 | -10224.2289 | -11817.1812 | 1
| 60859777 | 3466.985 | 8781.7136 | -5314.7286 | 0 |  | -6192.9 | -4436.5573 | -4968.0301 | -5661.4271 | -6539.5985 | 1
| 60859779 | 5572.3394 | 14032.0506 | -8459.7112 | 0 |  | -9862.9163 | -7056.5061 | -7902.4773 | -9016.9451 | -10420.1502 | 1
| 60859795 | 291.6048 | 1243.8048 | -952.2001 | 0 |  | -1076.5806 | -827.8196 | -923.0396 | -981.3606 | -1105.741 | 1
| 60859797 | 50410.2469 | 114205.8549 | -63795.608 | 0 |  | -75216.1935 | -52375.0225 | -58754.5833 | -68836.6327 | -80257.2182 | 1
| 60859798 | 1237.0826 | 3153.3524 | -1916.2697 | 0 |  | -2231.605 | -1600.9345 | -1792.5615 | -2039.978 | -2355.3132 | 1
| 60859799 | 1235.8404 | 3150.2022 | -1914.3618 | 0 |  | -2229.382 | -1599.3416 | -1790.7778 | -2037.9458 | -2352.9661 | 1
| 60859803 | 23996.3843 | 57629.7988 | -33633.4145 | 0 |  | -39396.3943 | -27870.4346 | -31233.776 | -36033.0529 | -41796.0328 | 1
| 60859804 | 6713.8473 | 16853.5817 | -10139.7344 | 0 |  | -11825.0926 | -8454.3763 | -9468.3497 | -10811.1192 | -12496.4773 | 1
| 60859807 | 21032.1862 | 50875.7653 | -29843.5791 | 0 |  | -34931.1557 | -24756.0026 | -27740.3605 | -31946.7978 | -37034.3743 | 1
| 60859911 | 2732.5033 | 6935.6951 | -4203.1918 | 0 |  | -4896.7614 | -3509.6223 | -3929.9415 | -4476.4422 | -5170.0117 | 1
| 60860042 | 4384.2257 | 11076.6359 | -6692.4102 | 0 |  | -7800.0738 | -5584.7466 | -6253.9876 | -7130.8328 | -8238.4963 | 1
| 60860044 | 8621.9436 | 21531.6319 | -12909.6883 | 0 |  | -15062.8515 | -10756.5251 | -12047.4939 | -13771.8827 | -15925.0459 | 1
| 60860045 | 892.4277 | 2277.0711 | -1384.6435 | 0 |  | -1612.3506 | -1156.9364 | -1295.4007 | -1473.8862 | -1701.5934 | 1
| 60860047 | 1691.181 | 4305.2763 | -2614.0953 | 0 |  | -3044.6229 | -2183.5677 | -2444.9772 | -2783.2134 | -3213.741 | 1
| 60860052 | 5023.4616 | 12669.0631 | -7645.6015 | 0 |  | -8912.5078 | -6378.6952 | -7143.2553 | -8147.9477 | -9414.854 | 1
| 60860055 | 761.0654 | 1942.6247 | -1181.5593 | 0 |  | -1375.8217 | -987.2968 | -1105.4527 | -1257.6658 | -1451.9283 | 1
| 60860058 | 7359.9131 | 18442.8587 | -11082.9456 | 0 |  | -12927.2315 | -9238.6597 | -10346.9543 | -11818.9369 | -13663.2228 | 1
| 60860060 | 5084.2579 | 12820.2728 | -7736.015 | 0 |  | -9018.0422 | -6453.9877 | -7227.5892 | -8244.4407 | -9526.468 | 1
| 60860065 | 5892.1608 | 14824.3264 | -8932.1657 | 0 |  | -10414.5983 | -7449.7331 | -8342.9496 | -9521.3818 | -11003.8144 | 1
| 60860078 | 17723.5748 | 43226.0243 | -25502.4496 | 0 |  | -29825.052 | -21179.8471 | -23730.0921 | -27274.807 | -31597.4095 | 1
| 60860083 | 8232.7542 | 20581.3209 | -12348.5667 | 0 |  | -14406.6988 | -10290.4346 | -11525.2913 | -13171.8421 | -15229.9742 | 1
| 60860086 | 5842.328 | 14700.9435 | -8858.6155 | 0 |  | -10328.7099 | -7388.5212 | -8274.3827 | -9442.8483 | -10912.9427 | 1
| 60740548 | 719.4453 | 3676.286 | -2956.8407 | 0 |  | -3324.4693 | -2589.2121 | -2884.8961 | -3028.7852 | -3396.4138 | 1
| 60674418 | 28948.8209 | 69227.2681 | -40278.4473 | 0 |  | -47201.1741 | -33355.7205 | -37383.5652 | -43173.3294 | -50096.0562 | 1
| 60674424 | 53010.372 | 119819.5152 | -66809.1432 | 0 |  | -78791.0947 | -54827.1917 | -61508.106 | -72110.1804 | -84092.1319 | 1
| 60674442 | 3387.909 | 8705.5837 | -5317.6747 | 0 |  | -6188.2331 | -4447.1164 | -4978.8838 | -5656.4656 | -6527.024 | 1
| 60674477 | 1374.4243 | 3858.9977 | -2484.5733 | 0 |  | -2870.4731 | -2098.6736 | -2347.1309 | -2622.0158 | -3007.9155 | 1
| 60674500 | 42791.595 | 98958.3513 | -56166.7564 | 0 |  | -66062.5915 | -46270.9212 | -51887.5969 | -60445.9159 | -70341.751 | 1
| 60674370 | 413.5566 | 1165.0498 | -751.4932 | 0 |  | -867.9981 | -634.9882 | -710.1375 | -792.8488 | -909.3538 | 1
| 60674374 | 41203.3751 | 95637.5132 | -54434.1381 | 0 |  | -63997.8894 | -44870.3868 | -50313.8006 | -58554.4756 | -68118.2269 | 1
| 60674397 | 39060.1343 | 91120.6483 | -52060.514 | 0 |  | -61172.5788 | -42948.4492 | -48154.5006 | -55966.5274 | -65078.5923 | 1
| 60674404 | 27098.138 | 65108.9038 | -38010.7658 | 0 |  | -44521.6561 | -31499.8754 | -35300.952 | -40720.5796 | -47231.4699 | 1
| 60698175 | 2313995.168 | 298063.2052 | 2015931.9628 | 1 |  | 1986125.6423 | 2045738.2834 | 2247331.4797 | 1784532.446 | 1754726.1255 | 1
| 60708224 | 1598.5042 | 6744.0578 | -5145.5536 | 0 |  | -5819.9594 | -4471.1478 | -4985.7032 | -5305.404 | -5979.8098 | 1
| 60708284 | 299128.896 | 49649.8116 | 249479.0843 | 1 |  | 244514.1032 | 254444.0655 | 279391.9739 | 219566.1947 | 214601.2136 | 1
| 60722942 | 373.0325 | 13303.3038 | -12930.2714 | 0 |  | -14260.6017 | -11599.941 | -12892.9681 | -12967.5746 | -14297.905 | 1
| 60722951 | 20767.8037 | 186784.4131 | -166016.6094 | 0 |  | -184695.0507 | -147338.1681 | -163939.829 | -168093.3898 | -186771.8311 | 1
| 60740522 | 719.4453 | 3676.286 | -2956.8407 | 0 |  | -3324.4693 | -2589.2121 | -2884.8961 | -3028.7852 | -3396.4138 | 1
| 60674631 | 6755.6887 | 17180.1527 | -10424.464 | 0 |  | -12142.4792 | -8706.4487 | -9748.8951 | -11100.0328 | -12818.0481 | 1
| 60674699 | 81504.2726 | 174009.2932 | -92505.0206 | 0 |  | -109905.9499 | -75104.0913 | -84354.5933 | -100655.4478 | -118056.3772 | 1
| 60674701 | 17686.1287 | 43575.1717 | -25889.043 | 0 |  | -30246.5602 | -21531.5258 | -24120.4301 | -27657.6559 | -32015.173 | 1
| 60468509 | 6380.2272 | 30724.972 | -24344.7448 | 0 |  | -27417.242 | -21272.2476 | -23706.7221 | -24982.7675 | -28055.2647 | 1
| 60468506 | 543.2624 | 2781.6285 | -2238.3662 | 0 |  | -2516.529 | -1960.2033 | -2184.0399 | -2292.6924 | -2570.8552 | 1
| 60468510 | 306.7825 | 1575.1011 | -1268.3186 | 0 |  | -1425.8287 | -1110.8085 | -1237.6404 | -1298.9969 | -1456.507 | 1
| 60468511 | 2067.1189 | 10404.5928 | -8337.4739 | 0 |  | -9377.9331 | -7297.0146 | -8130.762 | -8544.1858 | -9584.645 | 1
| 60468462 | 12946.803 | 58827.9257 | -45881.1226 | 0 |  | -51763.9152 | -39998.3301 | -44586.4423 | -47175.8029 | -53058.5955 | 1
| 60468461 | 361.3121 | 1853.894 | -1492.5819 | 0 |  | -1677.9713 | -1307.1925 | -1456.4507 | -1528.7131 | -1714.1025 | 1
| 60468460 | 26148.3403 | 108111.2638 | -81962.9235 | 0 |  | -92774.0498 | -71151.7971 | -79348.0894 | -84577.7575 | -95388.8839 | 1
| 60467905 | 1116.4648 | 5679.2895 | -4562.8247 | 0 |  | -5130.7536 | -3994.8957 | -4451.1782 | -4674.4712 | -5242.4001 | 1
| 60468607 | 1175.5566 | 5975.9335 | -4800.377 | 0 |  | -5397.9703 | -4202.7836 | -4682.8213 | -4917.9326 | -5515.526 | 1
| 60468608 | 7272.8979 | 34727.8289 | -27454.931 | 0 |  | -30927.7139 | -23982.1481 | -26727.6412 | -28182.2208 | -31655.0037 | 1
| 60468609 | 993.9142 | 5062.8999 | -4068.9858 | 0 |  | -4575.2758 | -3562.6958 | -3969.5944 | -4168.3772 | -4674.6672 | 1
| 60467904 | 4035.7566 | 19893.5268 | -15857.7702 | 0 |  | -17847.1229 | -13868.4175 | -15454.1946 | -16261.3459 | -18250.6986 | 1
| 60467584 | 3518.1267 | 17435.319 | -13917.1923 | 0 |  | -15660.7242 | -12173.6604 | -13565.3797 | -14269.005 | -16012.5369 | 1
| 60467585 | 708.8788 | 3622.7325 | -2913.8537 | 0 |  | -3276.1269 | -2551.5804 | -2842.9658 | -2984.7416 | -3347.0148 | 1
| 60467668 | 35.6291 | 1716.8602 | -1681.2311 | 0 |  | -1852.9171 | -1509.5451 | -1677.6682 | -1684.794 | -1856.48 | 1
| 60467669 | 779.5524 | 25081.3848 | -24301.8324 | 0 |  | -26809.9708 | -21793.6939 | -24223.8771 | -24379.7876 | -26887.9261 | 1
| 60467670 | 156.2398 | 6793.936 | -6637.6962 | 0 |  | -7317.0898 | -5958.3026 | -6622.0722 | -6653.3202 | -7332.7138 | 1
| 60467671 | 2684.503 | 58528.6565 | -55844.1535 | 0 |  | -61697.0191 | -49991.2878 | -55575.7032 | -56112.6038 | -61965.4694 | 1
| 60467672 | 948.1698 | 28925.1565 | -27976.9866 | 0 |  | -30869.5023 | -25084.471 | -27882.1696 | -28071.8036 | -30964.3193 | 1
| 60467781 | 3524.8183 | 14965.5605 | -11440.7422 | 0 |  | -12937.2983 | -9944.1862 | -11088.2604 | -11793.2241 | -13289.7801 | 1
| 60467782 | 244.6711 | 1071.5938 | -826.9227 | 0 |  | -934.0821 | -719.7633 | -802.4556 | -851.3898 | -958.5492 | 1
| 60467783 | 14576.5412 | 56682.638 | -42106.0968 | 0 |  | -47774.3606 | -36437.833 | -40648.4426 | -43563.7509 | -49232.0147 | 1
| 60467785 | 6384.8777 | 26440.697 | -20055.8193 | 0 |  | -22699.8891 | -17411.7496 | -19417.3316 | -20694.3071 | -23338.3768 | 1
| 60467786 | 1607.0231 | 6945.6708 | -5338.6477 | 0 |  | -6033.2148 | -4644.0806 | -5177.9454 | -5499.35 | -6193.9171 | 1
| 60467787 | 1879.3685 | 8101.795 | -6222.4265 | 0 |  | -7032.606 | -5412.247 | -6034.4897 | -6410.3634 | -7220.5429 | 1
| 60467788 | 1655.1541 | 7150.4339 | -5495.2798 | 0 |  | -6210.3232 | -4780.2364 | -5329.7644 | -5660.7952 | -6375.8386 | 1
| 60467837 | 2499.9442 | 12524.1538 | -10024.2097 | 0 |  | -11276.6251 | -8771.7943 | -9774.2153 | -10274.2041 | -11526.6195 | 1
| 60467838 | 667.4684 | 3412.719 | -2745.2506 | 0 |  | -3086.5225 | -2403.9787 | -2678.5037 | -2811.9974 | -3153.2693 | 1
| 60467841 | 1205.7159 | 6127.1433 | -4921.4273 | 0 |  | -5534.1417 | -4308.713 | -4800.8558 | -5041.9989 | -5654.7133 | 1
| 60467903 | 244.8408 | 1257.9807 | -1013.14 | 0 |  | -1138.938 | -887.3419 | -988.6559 | -1037.6241 | -1163.4221 | 1
| 60469531 | 618.6289 | 19843.6486 | -19225.0197 | 0 |  | -21209.3846 | -17240.6548 | -19163.1568 | -19286.8826 | -21271.2474 | 1
| 60469532 | 486.4831 | 16460.8565 | -15974.3734 | 0 |  | -17620.4591 | -14328.2878 | -15925.7251 | -16023.0217 | -17669.1074 | 1
| 60469533 | 397.2252 | 13999.4985 | -13602.2733 | 0 |  | -15002.2231 | -12202.3234 | -13562.5508 | -13641.9958 | -15041.9457 | 1
| 60469535 | 16866.7106 | 166350.6267 | -149483.916 | 0 |  | -166118.9787 | -132848.8534 | -147797.245 | -151170.5871 | -167805.6498 | 1
| 60469539 | 1661.7428 | 40470.1224 | -38808.3797 | 0 |  | -42855.3919 | -34761.3674 | -38642.2054 | -38974.5539 | -43021.5662 | 1
| 60469540 | 13439.2267 | 146370.4693 | -132931.2426 | 0 |  | -147568.2895 | -118294.1956 | -131587.3199 | -134275.1652 | -148912.2122 | 1
| 60469541 | 183.2123 | 7283.2675 | -7100.0552 | 0 |  | -7828.3819 | -6371.7284 | -7081.734 | -7118.3764 | -7846.7032 | 1
| 60469542 | 407109.3872 | 190085.825 | 217023.5622 | 1 |  | 198014.9797 | 236032.1447 | 257734.5009 | 176312.6235 | 157304.041 | 1
| 60469543 | 302172.4221 | 160999.4832 | 141172.9389 | 1 |  | 125072.9905 | 157272.8872 | 171390.1811 | 110955.6966 | 94855.7483 | 1
| 60469544 | 99286.1857 | 84271.5837 | 15014.602 | 1 |  | 6587.4436 | 23441.7604 | 24943.2206 | 5085.9834 | -3341.1749 | 0
| 60469545 | 46093.4787 | 52080.7176 | -5987.2389 | 0 |  | -11195.3107 | -779.1671 | -1377.891 | -10596.5868 | -15804.6585 | 1
| 60469546 | 62623.2014 | 63385.2182 | -762.0167 | 0 |  | -7100.5385 | 5576.5051 | 5500.3034 | -7024.3369 | -13362.8587 | 1
| 60469547 | 153696.7835 | 109305.1904 | 44391.5931 | 1 |  | 33461.074 | 55322.1121 | 59761.2714 | 29021.9147 | 18091.3957 | 1
| 60469548 | 107772.6454 | 88547.9832 | 19224.6623 | 1 |  | 10369.8639 | 28079.4606 | 30001.9268 | 8447.3977 | -407.4006 | 0
| 60469549 | 114124.7184 | 91644.1069 | 22480.6116 | 1 |  | 13316.2009 | 31645.0222 | 33893.0834 | 11068.1397 | 1903.729 | 1
| 60469550 | 58144.4958 | 60474.4313 | -2329.9355 | 0 |  | -8377.3786 | 3717.5076 | 3484.5141 | -8144.3851 | -14191.8282 | 1
| 60469551 | 2133659.2313 | 462028.6038 | 1671630.6275 | 1 |  | 1625427.7672 | 1717833.4879 | 1884996.5507 | 1458264.7044 | 1412061.844 | 1
| 60469554 | 4992.5791 | 9956.214 | -4963.6349 | 0 |  | -5959.2563 | -3968.0135 | -4464.377 | -5462.8928 | -6458.5142 | 1
| 60469555 | 101846.2619 | 85579.4426 | 16266.8193 | 1 |  | 7708.875 | 24824.7635 | 26451.4455 | 6082.1931 | -2475.7512 | 0
| 60469559 | 560.3946 | 2868.7841 | -2308.3896 | 0 |  | -2595.268 | -2021.5111 | -2252.3501 | -2364.429 | -2651.3074 | 1
| 60469899 | 412.8229 | 2116.9359 | -1704.113 | 0 |  | -1915.8066 | -1492.4194 | -1662.8307 | -1745.3953 | -1957.0889 | 1
| 60470115 | 141.0524 | 725.5966 | -584.5442 | 0 |  | -657.1038 | -511.9845 | -570.4389 | -598.6494 | -671.2091 | 1
| 60470150 | 6512.1588 | 26938.954 | -20426.7952 | 0 |  | -23120.6906 | -17732.8998 | -19775.5793 | -21078.0111 | -23771.9065 | 1
| 60470187 | 206.7349 | 1062.6682 | -855.9333 | 0 |  | -962.2001 | -749.6665 | -835.2598 | -876.6068 | -982.8736 | 1
| 60470188 | 10789.8208 | 49920.204 | -39130.3832 | 0 |  | -44122.4036 | -34138.3628 | -38051.4011 | -40209.3653 | -45201.3857 | 1
| 60470198 | 20325.7858 | 87351.9564 | -67026.1706 | 0 |  | -75761.3662 | -58290.9749 | -64993.592 | -69058.7492 | -77793.9448 | 1
| 60469530 | 7662.3997 | 105844.1683 | -98181.7685 | 0 |  | -108766.1853 | -87597.3517 | -97415.5285 | -98948.0085 | -109532.4253 | 1
| 60468611 | 341.9982 | 1755.1877 | -1413.1895 | 0 |  | -1588.7082 | -1237.6707 | -1378.9896 | -1447.3893 | -1622.908 | 1
| 60468612 | 9960.2957 | 46415.079 | -36454.7833 | 0 |  | -41096.2912 | -31813.2754 | -35458.7538 | -37450.8129 | -42092.3208 | 1
| 60469186 | 213.6985 | 1098.3705 | -884.672 | 0 |  | -994.509 | -774.8349 | -863.3021 | -906.0418 | -1015.8789 | 1
| 60469205 | 504.9965 | 2586.841 | -2081.8446 | 0 |  | -2340.5287 | -1823.1605 | -2031.3449 | -2132.3442 | -2391.0283 | 1
| 60469256 | 483.0423 | 2475.0089 | -1991.9666 | 0 |  | -2239.4675 | -1744.4657 | -1943.6623 | -2040.2708 | -2287.7717 | 1
| 60469257 | 2812.6819 | 14043.6013 | -11230.9195 | 0 |  | -12635.2796 | -9826.5593 | -10949.6513 | -11512.1876 | -12916.5478 | 1
| 60469527 | 4777.9363 | 79769.9448 | -74992.0085 | 0 |  | -82969.003 | -67015.014 | -74514.2149 | -75469.8021 | -83446.7966 | 1
| 60469528 | 119575.9529 | 477402.1154 | -357826.1626 | 0 |  | -405566.3741 | -310085.951 | -345868.5673 | -369783.7579 | -417523.9694 | 1
| 60469529 | 197.3603 | 7773.1239 | -7575.7636 | 0 |  | -8353.076 | -6798.4512 | -7556.0276 | -7595.4996 | -8372.812 | 1
| 60466995 | 268.1112 | 10820.9445 | -10552.8333 | 0 |  | -11634.9278 | -9470.7389 | -10526.0222 | -10579.6445 | -11661.7389 | 1
| 60467004 | 10346.1251 | 48051.084 | -37704.9589 | 0 |  | -42510.0673 | -32899.8505 | -36670.3464 | -38739.5714 | -43544.6798 | 1
| 60467035 | 2838.0487 | 14166.4592 | -11328.4105 | 0 |  | -12745.0565 | -9911.7646 | -11044.6057 | -11612.2154 | -13028.8613 | 1
| 60467036 | 5431.8121 | 26400.7944 | -20968.9824 | 0 |  | -23609.0618 | -18328.9029 | -20425.8011 | -21512.1636 | -24152.243 | 1
| 60467037 | 18444.0657 | 80335.9311 | -61891.8654 | 0 |  | -69925.4585 | -53858.2723 | -60047.4588 | -63736.272 | -71769.8651 | 1
| 60467038 | 49680.0829 | 181199.1047 | -131519.0217 | 0 |  | -149638.9322 | -113399.1113 | -126551.0135 | -136487.03 | -154606.9405 | 1
| 60467039 | 1438.7269 | 7292.193 | -5853.4661 | 0 |  | -6582.6854 | -5124.2468 | -5709.5934 | -5997.3388 | -6726.5581 | 1
| 60467040 | 1118.8667 | 5691.3653 | -4572.4986 | 0 |  | -5141.6351 | -4003.362 | -4460.6119 | -4684.3852 | -5253.5218 | 1
| 60467041 | 1338.5134 | 6791.8359 | -5453.3225 | 0 |  | -6132.5061 | -4774.139 | -5319.4712 | -5587.1739 | -6266.3575 | 1
| 60467042 | 11396.7444 | 52456.1167 | -41059.3723 | 0 |  | -46304.9839 | -35813.7606 | -39919.6978 | -42199.0467 | -47444.6584 | 1
| 60467043 | 3843.6423 | 18984.1684 | -15140.5261 | 0 |  | -17038.943 | -13242.1093 | -14756.1619 | -15524.8904 | -17423.3072 | 1
| 60467044 | 244994.628 | 47761.2654 | 197233.3626 | 1 |  | 192457.2361 | 202009.4892 | 221732.8254 | 172733.8998 | 167957.7733 | 1
| 60467045 | 215490.8128 | 42470.5008 | 173020.3119 | 1 |  | 168773.2619 | 177267.362 | 194569.3932 | 151471.2307 | 147224.1806 | 1
| 60467046 | 2596831.7319 | 323392.4059 | 2273439.3261 | 1 |  | 2241100.0855 | 2305778.5667 | 2533122.4993 | 2013756.1529 | 1981416.9123 | 1
| 60467047 | 2525181.5894 | 317088.8513 | 2208092.7381 | 1 |  | 2176383.853 | 2239801.6232 | 2460610.897 | 1955574.5791 | 1923865.694 | 1
| 60467048 | 17221.5031 | 3690.9869 | 13530.5162 | 1 |  | 13161.4176 | 13899.6149 | 15252.6666 | 11808.3659 | 11439.2672 | 1
| 60467050 | 3341159.4275 | 385002.4851 | 2956156.9424 | 1 |  | 2917656.6939 | 2994657.191 | 3290272.8852 | 2622040.9997 | 2583540.7512 | 1
| 60467145 | 3837.2326 | 18953.7165 | -15116.4838 | 0 |  | -17011.8555 | -13221.1122 | -14732.7606 | -15500.2071 | -17395.5788 | 1
| 60467146 | 410.5594 | 2105.3851 | -1694.8257 | 0 |  | -1905.3643 | -1484.2872 | -1653.7698 | -1735.8817 | -1946.4202 | 1
| 60467147 | 3331.7152 | 16543.8118 | -13212.0966 | 0 |  | -14866.4778 | -11557.7155 | -12878.9251 | -13545.2682 | -15199.6493 | 1
| 60467148 | 360.181 | 1848.1186 | -1487.9376 | 0 |  | -1672.7494 | -1303.1257 | -1451.9195 | -1523.9557 | -1708.7675 | 1
| 60467229 | 449.5657 | 2304.3729 | -1854.8072 | 0 |  | -2085.2445 | -1624.3699 | -1809.8506 | -1899.7638 | -2130.2011 | 1
| 60470199 | 1853.3061 | 9350.3251 | -7497.019 | 0 |  | -8432.0516 | -6561.9865 | -7311.6884 | -7682.3497 | -8617.3822 | 1
| 60547067 | 1084.3175 | 1391.8643 | -307.5468 | 0 |  | -446.7332 | -168.3604 | -199.115 | -415.9785 | -555.165 | 1
| 60547070 | 3548.1613 | 17578.6532 | -14030.4919 | 0 |  | -15788.3573 | -12272.6266 | -13675.6758 | -14385.3081 | -16143.1734 | 1
| 60547090 | 22448.7554 | 68864.4698 | -46415.7145 | 0 |  | -53302.1614 | -39529.2675 | -44170.8389 | -48660.59 | -55547.037 | 1
| 60547094 | 215831.9791 | 377637.8374 | -161805.8584 | 0 |  | -199569.6421 | -124042.0746 | -140222.6604 | -183389.0563 | -221152.84 | 1
| 60546911 | 461.1984 | 2015.6044 | -1554.406 | 0 |  | -1755.9664 | -1352.8456 | -1508.2862 | -1600.5258 | -1802.0863 | 1
| 60546908 | 9635.6798 | 31151.8244 | -21516.1446 | 0 |  | -24631.327 | -18400.9621 | -20552.5766 | -22479.7126 | -25594.895 | 1
| 60546906 | 4081563.1457 | 440610.3791 | 3640952.7666 | 1 |  | 3596891.7287 | 3685013.8045 | 4049109.0812 | 3232796.452 | 3188735.4141 | 1
| 60546832 | 6488.67 | 26847.0731 | -20358.4031 | 0 |  | -23043.1104 | -17673.6958 | -19709.5361 | -21007.2701 | -23691.9774 | 1
| 60546808 | 341.9982 | 1755.1877 | -1413.1895 | 0 |  | -1588.7082 | -1237.6707 | -1378.9896 | -1447.3893 | -1622.908 | 1
| 60546785 | 567.4139 | 2904.4864 | -2337.0725 | 0 |  | -2627.5211 | -2046.6239 | -2280.3311 | -2393.8139 | -2684.2625 | 1
| 60546778 | 862.5371 | 2126.9115 | -1264.3744 | 0 |  | -1477.0656 | -1051.6833 | -1178.1207 | -1350.6281 | -1563.3193 | 1
| 60547145 | 6594.7473 | 67658.9925 | -61064.2452 | 0 |  | -67830.1444 | -54298.3459 | -60404.7705 | -61723.7199 | -68489.6192 | 1
| 60547771 | 206.7349 | 1062.6682 | -855.9333 | 0 |  | -962.2001 | -749.6665 | -835.2598 | -876.6068 | -982.8736 | 1
| 60547811 | 28408.1533 | 85251.2966 | -56843.1432 | 0 |  | -65368.2729 | -48318.0136 | -54002.3279 | -59683.9586 | -68209.0882 | 1
| 60547819 | 19097.1385 | 59348.7591 | -40251.6206 | 0 |  | -46186.4965 | -34316.7447 | -38341.9067 | -42161.3344 | -48096.2103 | 1
| 60547831 | 1118.8667 | 5691.3653 | -4572.4986 | 0 |  | -5141.6351 | -4003.362 | -4460.6119 | -4684.3852 | -5253.5218 | 1
| 60547845 | 28420.6166 | 85284.8987 | -56864.2821 | 0 |  | -65392.772 | -48335.7923 | -54022.2205 | -59706.3438 | -68234.8337 | 1
| 60547856 | 18682.6248 | 58155.8825 | -39473.2578 | 0 |  | -45288.846 | -33657.6695 | -37604.9953 | -41341.5202 | -47157.1085 | 1
| 60547865 | 11482.7567 | 36824.8135 | -25342.0568 | 0 |  | -29024.5381 | -21659.5754 | -24193.7811 | -26490.3325 | -30172.8138 | 1
| 60547903 | 1177.3794 | 3960.3292 | -2782.9498 | 0 |  | -3178.9827 | -2386.9169 | -2665.2118 | -2900.6877 | -3296.7206 | 1
| 60546771 | 804.9787 | 11415.8077 | -10610.829 | 0 |  | -11752.4097 | -9469.2482 | -10530.3311 | -10691.3268 | -11832.9076 | 1
| 60546568 | 4347.0135 | 14398.5241 | -10051.5106 | 0 |  | -11491.363 | -8611.6582 | -9616.8093 | -10486.212 | -11926.0644 | 1
| 60546625 | 75168.6155 | 196554.7652 | -121386.1497 | 0 |  | -141041.6262 | -101730.6732 | -113869.2881 | -128903.0112 | -148558.4878 | 1
| 60546634 | 2550.2307 | 53765.0257 | -51214.795 | 0 |  | -56591.2976 | -45838.2924 | -50959.7719 | -51469.8181 | -56846.3206 | 1
| 60546637 | 4469.9488 | 14797.0247 | -10327.0759 | 0 |  | -11806.7783 | -8847.3734 | -9880.081 | -10774.0708 | -12253.7732 | 1
| 60546638 | 47842.817 | 294153.8043 | -246310.9872 | 0 |  | -275726.3677 | -216895.6068 | -241526.7055 | -251095.2689 | -280510.6494 | 1
| 60546653 | 2841.6299 | 9480.5335 | -6638.9036 | 0 |  | -7586.957 | -5690.8503 | -6354.7406 | -6923.0666 | -7871.1199 | 1
| 60546710 | 38535.9993 | 6934.6451 | 31601.3542 | 1 |  | 30907.8897 | 32294.8187 | 35454.9541 | 27747.7543 | 27054.2897 | 1
| 60548486 | 45321.9397 | 54006.0162 | -8684.0765 | 0 |  | -14084.6781 | -3283.4749 | -4151.8825 | -13216.2704 | -18616.8721 | 1
| 60548544 | 82644.2168 | 93455.9982 | -10811.7814 | 0 |  | -20157.3812 | -1466.1816 | -2547.3597 | -19076.2031 | -28421.8029 | 1
| 60548556 | 407.3706 | 2089.1091 | -1681.7385 | 0 |  | -1890.6494 | -1472.8276 | -1641.0014 | -1722.4755 | -1931.3864 | 1
| 60548617 | 1129.8174 | 3801.244 | -2671.4266 | 0 |  | -3051.551 | -2291.3022 | -2558.4449 | -2784.4083 | -3164.5327 | 1
| 60548624 | 16888.4348 | 52950.1734 | -36061.7386 | 0 |  | -41356.7559 | -30766.7213 | -34372.8951 | -37750.5821 | -43045.5994 | 1
| 60548631 | 1449406.0975 | 190402.4203 | 1259003.6772 | 1 |  | 1239963.4352 | 1278043.9192 | 1403944.287 | 1114063.0674 | 1095022.8254 | 1
| 60548707 | 6787.0209 | 22225.7265 | -15438.7056 | 0 |  | -17661.2782 | -13216.133 | -14760.0035 | -16117.4077 | -18339.9803 | 1
| 60548719 | 251736.9691 | 48955.7171 | 202781.2521 | 1 |  | 197885.6804 | 207676.8238 | 227954.949 | 177607.5552 | 172711.9835 | 1
| 60548720 | 1414.8671 | 1815.0415 | -400.1744 | 0 |  | -581.6786 | -218.6703 | -258.6877 | -541.6611 | -723.1653 | 1
| 60548723 | 11959.1294 | 38273.9065 | -26314.7771 | 0 |  | -30142.1677 | -22487.3864 | -25118.8641 | -27510.69 | -31338.0807 | 1
| 60548727 | 10579.518 | 34061.5611 | -23482.0431 | 0 |  | -26888.1992 | -20075.887 | -22424.0913 | -24539.9949 | -27946.151 | 1
| 60548758 | 853.19 | 4353.0544 | -3499.8643 | 0 |  | -3935.1698 | -3064.5589 | -3414.5453 | -3585.1833 | -4020.4888 | 1
| 60548775 | 1356.8418 | 4559.9177 | -3203.0759 | 0 |  | -3659.0676 | -2747.0841 | -3067.3917 | -3338.76 | -3794.7518 | 1
| 60548808 | 9125.8482 | 29570.4229 | -20444.5747 | 0 |  | -23401.617 | -17487.5324 | -19531.9899 | -21357.1595 | -24314.2018 | 1
| 60548824 | 483.0423 | 2475.0089 | -1991.9666 | 0 |  | -2239.4675 | -1744.4657 | -1943.6623 | -2040.2708 | -2287.7717 | 1
| 60548862 | 21432.6764 | 66003.5612 | -44570.8848 | 0 |  | -51171.241 | -37970.5287 | -42427.6172 | -46714.1525 | -53314.5086 | 1
| 60548870 | 1477826.1727 | 194243.0418 | 1283583.1309 | 1 |  | 1264158.8267 | 1303007.4351 | 1431365.7482 | 1135800.5136 | 1116376.2094 | 1
| 60548874 | 213.6985 | 1098.3705 | -884.672 | 0 |  | -994.509 | -774.8349 | -863.3021 | -906.0418 | -1015.8789 | 1
| 60548909 | 10553.0204 | 33980.1809 | -23427.1605 | 0 |  | -26825.1786 | -20029.1425 | -22371.8585 | -24482.4626 | -27880.4807 | 1
| 60548927 | 10081.6194 | 32529.5128 | -22447.8934 | 0 |  | -25700.8447 | -19194.9421 | -21439.7315 | -23456.0553 | -26709.0066 | 1
| 60548949 | 18559.3417 | 57800.4347 | -39241.093 | 0 |  | -45021.1365 | -33461.0496 | -37385.1589 | -41097.0272 | -46877.0707 | 1
| 60548965 | 2104.6484 | 7047.0023 | -4942.3539 | 0 |  | -5647.0541 | -4237.6537 | -4731.8891 | -5152.8187 | -5857.519 | 1
| 60548476 | 16666.1259 | 73552.4957 | -56886.3698 | 0 |  | -64241.6194 | -49531.1202 | -55219.7572 | -58552.9824 | -65908.232 | 1
| 60547921 | 667.4684 | 3412.719 | -2745.2506 | 0 |  | -3086.5225 | -2403.9787 | -2678.5037 | -2811.9974 | -3153.2693 | 1
| 60547932 | 2771.9308 | 9251.0938 | -6479.1629 | 0 |  | -7404.2723 | -5554.0535 | -6201.9698 | -6756.356 | -7681.4654 | 1
| 60547940 | 551.0011 | 2821.0061 | -2270.005 | 0 |  | -2552.1056 | -1987.9044 | -2214.9049 | -2325.1051 | -2607.2057 | 1
| 60547941 | 639.8066 | 2157.8885 | -1518.0819 | 0 |  | -1733.8707 | -1302.293 | -1454.1012 | -1582.0625 | -1797.8514 | 1
| 60547946 | 13645.0892 | 53412.7281 | -39767.6389 | 0 |  | -45108.9117 | -34426.3661 | -38403.13 | -41132.1478 | -46473.4206 | 1
| 60548007 | 567.4139 | 2904.4864 | -2337.0725 | 0 |  | -2627.5211 | -2046.6239 | -2280.3311 | -2393.8139 | -2684.2625 | 1
| 60548031 | 11320.5547 | 14262.0154 | -2941.4607 | 0 |  | -4367.6622 | -1515.2592 | -1809.4052 | -4073.5162 | -5499.7177 | 1
| 60548050 | 9079.9256 | 29427.6137 | -20347.6881 | 0 |  | -23290.4495 | -17404.9267 | -19439.6955 | -21255.6807 | -24198.442 | 1
| 60548055 | 401135.9224 | 74180.436 | 326955.4864 | 1 |  | 319537.4428 | 334373.53 | 367069.0787 | 286841.8942 | 279423.8506 | 1
| 60548061 | 75443.8237 | 334657.0038 | -259213.1801 | 0 |  | -292678.8805 | -225747.4797 | -251668.7978 | -266757.5625 | -300223.2629 | 1
| 60548079 | 631.6858 | 2130.5867 | -1498.9009 | 0 |  | -1711.9596 | -1285.8422 | -1435.7323 | -1562.0695 | -1775.1282 | 1
| 60548098 | 26701.2416 | 63519.1018 | -36817.8601 | 0 |  | -43169.7703 | -30465.95 | -34147.736 | -39487.9843 | -45839.8945 | 1
| 60548184 | 2787.8712 | 9303.5971 | -6515.726 | 0 |  | -7446.0857 | -5585.3663 | -6236.9389 | -6794.5131 | -7724.8728 | 1
| 60548237 | 94388.6935 | 236039.3994 | -141650.7059 | 0 |  | -165254.6459 | -118046.766 | -132211.8366 | -151089.5753 | -174693.5152 | 1
| 60548272 | 1129.8174 | 3801.244 | -2671.4266 | 0 |  | -3051.551 | -2291.3022 | -2558.4449 | -2784.4083 | -3164.5327 | 1
| 60548344 | 132.4659 | 681.4937 | -549.0279 | 0 |  | -617.1773 | -480.8785 | -535.7813 | -562.2745 | -630.4238 | 1
| 60548360 | 1088.6573 | 5539.6305 | -4450.9733 | 0 |  | -5004.9363 | -3897.0102 | -4342.1075 | -4559.839 | -5113.802 | 1
| 60548363 | 11398.8906 | 100631.6337 | -89232.7431 | 0 |  | -99295.9064 | -79169.5797 | -88092.854 | -90372.6321 | -100435.7955 | 1
| 60548387 | 624.034 | 2104.8601 | -1480.8261 | 0 |  | -1691.3121 | -1270.3401 | -1418.4227 | -1543.2295 | -1753.7155 | 1
| 60548396 | 153.814 | 2741.726 | -2587.9119 | 0 |  | -2862.0845 | -2313.7393 | -2572.5305 | -2603.2933 | -2877.4659 | 1
| 60548400 | 485.1611 | 1637.5801 | -1152.419 | 0 |  | -1316.177 | -988.661 | -1103.9029 | -1200.9351 | -1364.6931 | 1
| 60548433 | 50.3821 | 770.2244 | -719.8423 | 0 |  | -796.8648 | -642.8199 | -714.8041 | -724.8805 | -801.903 | 1
| 60548436 | 82382.5353 | 93191.9062 | -10809.3709 | 0 |  | -20128.5615 | -1490.1803 | -2571.1174 | -19047.6244 | -28366.815 | 1
| 60548437 | 19398.9552 | 60215.0647 | -40816.1095 | 0 |  | -46837.616 | -34794.6031 | -38876.214 | -42756.0051 | -48777.5115 | 1
| 60470200 | 447.7119 | 2294.9223 | -1847.2104 | 0 |  | -2076.7026 | -1617.7181 | -1802.4392 | -1891.9815 | -2121.4738 | 1
| 60470201 | 1579.8165 | 7994.6881 | -6414.8716 | 0 |  | -7214.3404 | -5615.4028 | -6256.89 | -6572.8533 | -7372.3221 | 1
| 60470202 | 1739.8692 | 8789.0641 | -7049.1949 | 0 |  | -7928.1013 | -6170.2885 | -6875.208 | -7223.1818 | -8102.0882 | 1
| 60470203 | 4524.8412 | 22193.1744 | -17668.3332 | 0 |  | -19887.6507 | -15449.0158 | -17215.8491 | -18120.8174 | -20340.1348 | 1
| 60470204 | 527.9927 | 2703.9235 | -2175.9308 | 0 |  | -2446.3232 | -1905.5385 | -2123.1316 | -2228.7301 | -2499.1225 | 1
| 60470205 | 7025.1259 | 33623.158 | -26598.0321 | 0 |  | -29960.3479 | -23235.7163 | -25895.5195 | -27300.5447 | -30662.8605 | 1
| 60470307 | 267479.3616 | 444870.5025 | -177391.141 | 0 |  | -221878.1912 | -132904.0907 | -150643.2048 | -204139.0771 | -248626.1274 | 1
| 60470308 | 50980.9406 | 112240.6538 | -61259.7132 | 0 |  | -72483.7785 | -50035.6478 | -56161.6191 | -66357.8072 | -77581.8726 | 1
| 60470309 | 2019.1775 | 4963.6686 | -2944.4911 | 0 |  | -3440.858 | -2448.1243 | -2742.5734 | -3146.4089 | -3642.7757 | 1
| 60470310 | 302295.5574 | 487497.9884 | -185202.431 | 0 |  | -233952.2299 | -136452.6322 | -154972.8753 | -215431.9868 | -264181.7856 | 1
| 60470311 | 516.2747 | 1274.2568 | -757.9821 | 0 |  | -885.4077 | -630.5564 | -706.3546 | -809.6095 | -937.0352 | 1
| 60470584 | 25375.6056 | 105432.5418 | -80056.9363 | 0 |  | -90600.1904 | -69513.6821 | -77519.3757 | -82594.4968 | -93137.751 | 1

## Misc_calcs
Powercor
Risk-based replacement of deteriorated and aged 66kV radial lines
ESCALATION & OTHER
| Year end |  |  |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
DISCOUNT FACTOR |  |  |  | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
| Discount factor |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129
0

## Data
Powercor
Risk-based replacement of deteriorated and aged 66kV radial lines
DATA
No change to existing practices
Not applicable (compliance)
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
DROPDOWN LISTS
| Business |  |  | Type |  | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year
| CitiPower | CP |  | - Select - |  | 0 | June | 6 | CY | Not used |  | 2023
| Powercor | PA |  | Capex |  | 1899-12-31 | December | 12 | FY |  |  | 2022
| United Energy | UE |  | Opex | [7 empty] | 2021
2020