## Cover
Powercor
Regulatory proposal 2026-31
RMUs
| Model number: | 4.13
2025-01-31
14

## Summary
Powercor
Recplacement of CRO inoperable RMUs
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Replace all CRO inoperatble RMUs over 1 year |  | -21.5424 | 89.0857 | 67.5433
| Option 3 | Replace all CRO inoperatble RMUs over 5 years |  | -18.5849 | 73.9956 | 55.4106
| Option 4 | Replace all CRO inoperatble RMUs over 10 years |  | -15.3371 | 65.787 | 50.45
| Option 5 | Replace all CRO inoperatble RMUs over 15 years |  | -12.2785 | 54.7497 | 42.4712
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | Replace all CRO inoperatble RMUs over 1 year |  | 67.5433
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 38.7878 | 0 | 0 | 0 | 0 |  | 38.7878
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 67.5433 | 55.4106 | 50.45 | 42.4712 |  | Option 2
| Capex 10% higher |  | 0 | 65.3891 | 53.5521 | 48.9163 | 41.2433 |  | Option 2
| Capex 10% lower |  | 0 | 69.6976 | 57.2691 | 51.9837 | 43.699 |  | Option 2
| Total benefits 10% higher |  | 0 | 76.4519 | 62.8102 | 57.0287 | 47.9461 |  | Option 2
| Total benefits 10% lower |  | 0 | 58.6348 | 48.0111 | 43.8713 | 36.9962 |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  | 0 | 56.4805 | 46.1526 | 42.3376 | 35.7684 |  | Option 2
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
Powercor
Recplacement of CRO inoperable RMUs
Project
|  | Business: |  | Powercor
|  | Descripton: |  | Recplacement of CRO inoperable RMUs
|  | Date of cost inputs: |  | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Replace all CRO inoperatble RMUs over 1 year
|  | Option 3 |  | Replace all CRO inoperatble RMUs over 5 years
|  | Option 4 |  | Replace all CRO inoperatble RMUs over 10 years
|  | Option 5 |  | Replace all CRO inoperatble RMUs over 15 years
|  | Compliance project |  | No
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | Network average |  | Network average | 43815.4862 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0.0011364 | 3 | 0
|  | Safety (moderate) |  |  |  | 1344753.7771 | 0.011364 | 3
|  | Safety (minor) |  |  |  | 127274.0425 | 0.11364 | 3 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 0 | 2023-12-31 | per MWh
|  | Network resilience |  |  |  | 0 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 4220.9954 | 2023-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.54769 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
Powercor
Recplacement of CRO inoperable RMUs
OPTION 1 (base case)
Count | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
[5 empty] | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Replacement of CRO inoperable RMUs |  | 55 | Capex | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | Safety | 2023-12-31 |  | 758444.0073 | 758444.0073 | 758444.0073 | 866793.1512 | 866793.1512 | 866793.1512 | 975142.2951 | 975142.2951 | 1083491.439 | 1083491.439 | 1191840.5829 | 1191840.5829 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 0
| Outages |  |  | Outages | 2023-12-31 |  | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 0
| Asset failure | (after DF) |  | Failures | 2023-12-31 |  | 86291.8378 | 86291.8378 | 86291.8378 | 98619.2432 | 98619.2432 | 98619.2432 | 110946.6486 | 110946.6486 | 123274.054 | 123274.054 | 135601.4594 | 135601.4594 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 0
| Outage for planned program |  |  | Planned | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost | [5 empty] | 5673114.6492 | 5673114.6492 | 5673114.6492 | 5793791.1985 | 5793791.1985 | 5793791.1985 | 5914467.7478 | 5914467.7478 | 6035144.2971 | 6035144.2971 | 6155820.8464 | 6155820.8464 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 |  | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 |  | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 |  | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 |  | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 |  | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  |  | 2023-12-31
Capital expenditure
| Replacement of CRO inoperable RMUs |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Replacement of CRO inoperable RMUs |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Replacement of CRO inoperable RMUs |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% |  | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% |  | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% |  | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% |  | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% |  | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% |  | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% |  | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% |  | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
Powercor
Recplacement of CRO inoperable RMUs
OPTION 2 | Replace all CRO inoperatble RMUs over 1 year
Count | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
[5 empty] | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Replacement of CRO inoperable RMUs |  | 55 | Capex | 2023-12-31 | 34852519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  |  | 2023-12-31 | 34852519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | Safety | 2023-12-31 | 0 | 85948.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Outages |  |  | Outages | 2023-12-31 | 4828378.8041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Asset failure | (after DF) |  | Failures | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Outage for planned program |  |  | Planned | 2023-12-31 | 1858972.7344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 6687351.5385 | 85948.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - residential | $/customer min | 0.54769 |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - business | $/customer min | 0.54769 |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  |  | 2023-12-31 | -1014236.8893 | 5587165.8164 | 5673114.6492 | 5793791.1985 | 5793791.1985 | 5793791.1985 | 5914467.7478 | 5914467.7478 | 6035144.2971 | 6035144.2971 | 6155820.8464 | 6155820.8464 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 0
Capital expenditure
| Replacement of CRO inoperable RMUs |  |  |  | 2023-12-31 | -34852519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Replacement of CRO inoperable RMUs |  |  |  | 2023-12-31 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Replacement of CRO inoperable RMUs |  |  |  | 2023-12-31 | 0 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Annualised capex - |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 2023-12-31 | 0 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Annualised capex |  |  |  | 2023-12-31 | 0 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Operating expenditure |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  |  | 2023-12-31 | -1014236.8893 | 5587165.8164 | 5673114.6492 | 5793791.1985 | 5793791.1985 | 5793791.1985 | 5914467.7478 | 5914467.7478 | 6035144.2971 | 6035144.2971 | 6155820.8464 | 6155820.8464 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 0
| Other benefits value |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  |  | 2023-12-31 | -1014236.8893 | 4150780.9444 | 4236729.7771 | 4357406.3264 | 4357406.3264 | 4357406.3264 | 4478082.8757 | 4478082.8757 | 4598759.425 | 4598759.425 | 4719435.9743 | 4719435.9743 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
| First capex year |  |  |  | 1
| First year |  |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  |  | Option 2NPV | -1014236.8893 | 4150780.9444 | 4236729.7771 | 4357406.3264 | 4357406.3264 | 4357406.3264 | 4478082.8757 | 4478082.8757 | 4598759.425 | 4598759.425 | 4719435.9743 | 4719435.9743 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
| Total annualised capex |  |  |  |  | 0 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Total benefits |  |  |  |  | -1014236.8893 | 5587165.8164 | 5673114.6492 | 5793791.1985 | 5793791.1985 | 5793791.1985 | 5914467.7478 | 5914467.7478 | 6035144.2971 | 6035144.2971 | 6155820.8464 | 6155820.8464 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% |  | Option 2sens1 | -1014236.8893 | 4007142.4572 | 4093091.2899 | 4213767.8392 | 4213767.8392 | 4213767.8392 | 4334444.3885 | 4334444.3885 | 4455120.9378 | 4455120.9378 | 4575797.4871 | 4575797.4871 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | -1580023.3592
sens2 | Capex 10% lower | -10% | 0% |  | Option 2sens2 | -1014236.8893 | 4294419.4316 | 4380368.2644 | 4501044.8136 | 4501044.8136 | 4501044.8136 | 4621721.3629 | 4621721.3629 | 4742397.9122 | 4742397.9122 | 4863074.4615 | 4863074.4615 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | -1292746.3848
sens3 | Total benefits 10% higher | 0% | 10% |  | Option 2sens3 | -1115660.5783 | 4709497.526 | 4804041.2421 | 4936785.4463 | 4936785.4463 | 4936785.4463 | 5069529.6505 | 5069529.6505 | 5202273.8547 | 5202273.8547 | 5335018.059 | 5335018.059 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | -1436384.872
sens4 | Total benefits 10% lower | 0% | -10% |  | Option 2sens4 | -912813.2004 | 3592064.3627 | 3669418.3122 | 3778027.2066 | 3778027.2066 | 3778027.2066 | 3886636.101 | 3886636.101 | 3995244.9953 | 3995244.9953 | 4103853.8897 | 4103853.8897 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | -1436384.872
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% |  | Option 2sens5 | -912813.2004 | 3448425.8755 | 3525779.825 | 3634388.7194 | 3634388.7194 | 3634388.7194 | 3742997.6138 | 3742997.6138 | 3851606.5081 | 3851606.5081 | 3960215.4025 | 3960215.4025 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | -1580023.3592
sens | 0 | 0% | 0% |  | Option 2sens | -1014236.8893 | 4150780.9444 | 4236729.7771 | 4357406.3264 | 4357406.3264 | 4357406.3264 | 4478082.8757 | 4478082.8757 | 4598759.425 | 4598759.425 | 4719435.9743 | 4719435.9743 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
sens | 0 | 0% | 0% |  | Option 2sens | -1014236.8893 | 4150780.9444 | 4236729.7771 | 4357406.3264 | 4357406.3264 | 4357406.3264 | 4478082.8757 | 4478082.8757 | 4598759.425 | 4598759.425 | 4719435.9743 | 4719435.9743 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
sens | 0 | 0% | 0% |  | Option 2sens | -1014236.8893 | 4150780.9444 | 4236729.7771 | 4357406.3264 | 4357406.3264 | 4357406.3264 | 4478082.8757 | 4478082.8757 | 4598759.425 | 4598759.425 | 4719435.9743 | 4719435.9743 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872

## Option3
Powercor
Recplacement of CRO inoperable RMUs
OPTION 3 | Replace all CRO inoperatble RMUs over 5 years
Count | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
[5 empty] | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Replacement of CRO inoperable RMUs |  | 55 | Capex | 2023-12-31 | 6933525 | 6933525 | 6933525 | 6933525 | 6933525 | 184894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  |  | 2023-12-31 | 6933525 | 6933525 | 6933525 | 6933525 | 6933525 | 184894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | Safety | 2023-12-31 | 2067184.2251 | 1240310.535 | 826873.69 | 413436.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Outages |  |  | Outages | 2023-12-31 | 4828378.8041 | 3867825.9916 | 2907273.1791 | 1946720.3666 | 986167.5542 | 25614.7417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Asset failure | (after DF) |  | Failures | 2023-12-31 | 235193.5333 | 141116.12 | 94077.4133 | 47038.7067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Outage for planned program |  |  | Planned | 2023-12-31 | 369822.162 | 369822.162 | 369822.162 | 369822.162 | 369822.162 | 9861.9243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 7500578.7244 | 5619074.8086 | 4198046.4445 | 2777018.0803 | 1355989.7162 | 35476.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  |  | 2023-12-31 | -1827464.0753 | 54039.8405 | 1475068.2047 | 3016773.1181 | 4437801.4823 | 5758314.5325 | 5914467.7478 | 5914467.7478 | 6035144.2971 | 6035144.2971 | 6155820.8464 | 6155820.8464 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 0
Capital expenditure
| Replacement of CRO inoperable RMUs |  |  |  | 2023-12-31 | -6933525 | -6933525 | -6933525 | -6933525 | -6933525 | -184894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Replacement of CRO inoperable RMUs |  |  |  | 2023-12-31 | -6933525 | -13867050 | -20800575 | -27734100 | -34667625 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Replacement of CRO inoperable RMUs |  |  |  | 2023-12-31 | 0 | -285752.9586 | -571505.9172 | -857258.8759 | -1143011.8345 | -1428764.7931 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Annualised capex - |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 2023-12-31 | 0 | -285752.9586 | -571505.9172 | -857258.8759 | -1143011.8345 | -1428764.7931 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Annualised capex |  |  |  | 2023-12-31 | 0 | -285752.9586 | -571505.9172 | -857258.8759 | -1143011.8345 | -1428764.7931 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Operating expenditure |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  |  | 2023-12-31 | -1827464.0753 | 54039.8405 | 1475068.2047 | 3016773.1181 | 4437801.4823 | 5758314.5325 | 5914467.7478 | 5914467.7478 | 6035144.2971 | 6035144.2971 | 6155820.8464 | 6155820.8464 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 0
| Other benefits value |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  |  | 2023-12-31 | -1827464.0753 | -231713.1181 | 903562.2874 | 2159514.2423 | 3294789.6478 | 4329549.7394 | 4478082.8757 | 4478082.8757 | 4598759.425 | 4598759.425 | 4719435.9743 | 4719435.9743 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
| First capex year |  |  |  | 1
| First year |  |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  |  | Option 3NPV | -1827464.0753 | -231713.1181 | 903562.2874 | 2159514.2423 | 3294789.6478 | 4329549.7394 | 4478082.8757 | 4478082.8757 | 4598759.425 | 4598759.425 | 4719435.9743 | 4719435.9743 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
| Total annualised capex |  |  |  |  | 0 | -285752.9586 | -571505.9172 | -857258.8759 | -1143011.8345 | -1428764.7931 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Total benefits |  |  |  |  | -1827464.0753 | 54039.8405 | 1475068.2047 | 3016773.1181 | 4437801.4823 | 5758314.5325 | 5914467.7478 | 5914467.7478 | 6035144.2971 | 6035144.2971 | 6155820.8464 | 6155820.8464 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% |  | Option 3sens1 | -1827464.0753 | -260288.4139 | 846411.6957 | 2073788.3547 | 3180488.4643 | 4186673.26 | 4334444.3885 | 4334444.3885 | 4455120.9378 | 4455120.9378 | 4575797.4871 | 4575797.4871 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | -1580023.3592
sens2 | Capex 10% lower | -10% | 0% |  | Option 3sens2 | -1827464.0753 | -203137.8222 | 960712.8792 | 2245240.1299 | 3409090.8312 | 4472426.2187 | 4621721.3629 | 4621721.3629 | 4742397.9122 | 4742397.9122 | 4863074.4615 | 4863074.4615 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | -1292746.3848
sens3 | Total benefits 10% higher | 0% | 10% |  | Option 3sens3 | -2010210.4828 | -226309.134 | 1051069.1079 | 2461191.5541 | 3738569.796 | 4905381.1926 | 5069529.6505 | 5069529.6505 | 5202273.8547 | 5202273.8547 | 5335018.059 | 5335018.059 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | -1436384.872
sens4 | Total benefits 10% lower | 0% | -10% |  | Option 3sens4 | -1644717.6677 | -237117.1021 | 756055.467 | 1857836.9305 | 2851009.4996 | 3753718.2861 | 3886636.101 | 3886636.101 | 3995244.9953 | 3995244.9953 | 4103853.8897 | 4103853.8897 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | -1436384.872
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% |  | Option 3sens5 | -1644717.6677 | -265692.398 | 698904.8753 | 1772111.0429 | 2736708.3161 | 3610841.8068 | 3742997.6138 | 3742997.6138 | 3851606.5081 | 3851606.5081 | 3960215.4025 | 3960215.4025 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | -1580023.3592
sens | 0 | 0% | 0% |  | Option 3sens | -1827464.0753 | -231713.1181 | 903562.2874 | 2159514.2423 | 3294789.6478 | 4329549.7394 | 4478082.8757 | 4478082.8757 | 4598759.425 | 4598759.425 | 4719435.9743 | 4719435.9743 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
sens | 0 | 0% | 0% |  | Option 3sens | -1827464.0753 | -231713.1181 | 903562.2874 | 2159514.2423 | 3294789.6478 | 4329549.7394 | 4478082.8757 | 4478082.8757 | 4598759.425 | 4598759.425 | 4719435.9743 | 4719435.9743 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
sens | 0 | 0% | 0% |  | Option 3sens | -1827464.0753 | -231713.1181 | 903562.2874 | 2159514.2423 | 3294789.6478 | 4329549.7394 | 4478082.8757 | 4478082.8757 | 4598759.425 | 4598759.425 | 4719435.9743 | 4719435.9743 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872

## Option4
Powercor
Recplacement of CRO inoperable RMUs
OPTION 4 | Replace all CRO inoperatble RMUs over 10 years
Count | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
[5 empty] | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Replacement of CRO inoperable RMUs |  | 55 | Capex | 2023-12-31 | 3512986 | 3512986 | 3512986 | 3512986 | 3512986 | 3512986 | 3512986 | 3512986 | 3512986 | 3235645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  |  | 2023-12-31 | 3512986 | 3512986 | 3512986 | 3512986 | 3512986 | 3512986 | 3512986 | 3512986 | 3512986 | 3235645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | Safety | 2023-12-31 | 541745.7195 | 541745.7195 | 433396.5756 | 325047.4317 | 216698.2878 | 216698.2878 | 108349.1439 | 108349.1439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Outages |  |  | Outages | 2023-12-31 | 4828378.8041 | 4341698.7124 | 3855018.6208 | 3368338.5291 | 2881658.4375 | 2394978.3458 | 1908298.2541 | 1421618.1625 | 934938.0708 | 448257.9792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Asset failure | (after DF) |  | Failures | 2023-12-31 | 61637.027 | 61637.027 | 49309.6216 | 36982.2162 | 24654.8108 | 24654.8108 | 12327.4054 | 12327.4054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Outage for planned program |  |  | Planned | 2023-12-31 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 172583.6756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 5619138.1127 | 5132458.021 | 4525101.38 | 3917744.7391 | 3310388.0981 | 2823708.0065 | 2216351.3655 | 1729671.2739 | 1122314.6329 | 620841.6548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  |  | 2023-12-31 | 53976.5365 | 540656.6282 | 1148013.2691 | 1876046.4594 | 2483403.1003 | 2970083.192 | 3698116.3822 | 4184796.4739 | 4912829.6641 | 5414302.6423 | 6155820.8464 | 6155820.8464 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 0
Capital expenditure
| Replacement of CRO inoperable RMUs |  |  |  | 2023-12-31 | -3512986 | -3512986 | -3512986 | -3512986 | -3512986 | -3512986 | -3512986 | -3512986 | -3512986 | -3235645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Replacement of CRO inoperable RMUs |  |  |  | 2023-12-31 | -3512986 | -7025972 | -10538958 | -14051944 | -17564930 | -21077916 | -24590902 | -28103888 | -31616874 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Replacement of CRO inoperable RMUs |  |  |  | 2023-12-31 | 0 | -144781.499 | -289562.9981 | -434344.4971 | -579125.9961 | -723907.4952 | -868688.9942 | -1013470.4933 | -1158251.9923 | -1303033.4913 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Annualised capex - |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 2023-12-31 | 0 | -144781.499 | -289562.9981 | -434344.4971 | -579125.9961 | -723907.4952 | -868688.9942 | -1013470.4933 | -1158251.9923 | -1303033.4913 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Annualised capex |  |  |  | 2023-12-31 | 0 | -144781.499 | -289562.9981 | -434344.4971 | -579125.9961 | -723907.4952 | -868688.9942 | -1013470.4933 | -1158251.9923 | -1303033.4913 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Operating expenditure |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  |  | 2023-12-31 | 53976.5365 | 540656.6282 | 1148013.2691 | 1876046.4594 | 2483403.1003 | 2970083.192 | 3698116.3822 | 4184796.4739 | 4912829.6641 | 5414302.6423 | 6155820.8464 | 6155820.8464 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 0
| Other benefits value |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  |  | 2023-12-31 | 53976.5365 | 395875.1291 | 858450.271 | 1441701.9623 | 1904277.1042 | 2246175.6968 | 2829427.388 | 3171325.9806 | 3754577.6719 | 4111269.151 | 4719435.9743 | 4719435.9743 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
| First capex year |  |  |  | 1
| First year |  |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  |  | Option 4NPV | 53976.5365 | 395875.1291 | 858450.271 | 1441701.9623 | 1904277.1042 | 2246175.6968 | 2829427.388 | 3171325.9806 | 3754577.6719 | 4111269.151 | 4719435.9743 | 4719435.9743 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
| Total annualised capex |  |  |  |  | 0 | -144781.499 | -289562.9981 | -434344.4971 | -579125.9961 | -723907.4952 | -868688.9942 | -1013470.4933 | -1158251.9923 | -1303033.4913 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Total benefits |  |  |  |  | 53976.5365 | 540656.6282 | 1148013.2691 | 1876046.4594 | 2483403.1003 | 2970083.192 | 3698116.3822 | 4184796.4739 | 4912829.6641 | 5414302.6423 | 6155820.8464 | 6155820.8464 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% |  | Option 4sens1 | 53976.5365 | 381396.9792 | 829493.9712 | 1398267.5126 | 1846364.5046 | 2173784.9473 | 2742558.4886 | 3069978.9313 | 3638752.4726 | 3980965.8018 | 4575797.4871 | 4575797.4871 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | -1580023.3592
sens2 | Capex 10% lower | -10% | 0% |  | Option 4sens2 | 53976.5365 | 410353.279 | 887406.5709 | 1485136.412 | 1962189.7038 | 2318566.4463 | 2916296.2874 | 3272673.03 | 3870402.8711 | 4241572.5001 | 4863074.4615 | 4863074.4615 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | -1292746.3848
sens3 | Total benefits 10% higher | 0% | 10% |  | Option 4sens3 | 59374.1902 | 449940.7919 | 973251.598 | 1629306.6082 | 2152617.4142 | 2543184.016 | 3199239.0262 | 3589805.628 | 4245860.6383 | 4652699.4152 | 5335018.059 | 5335018.059 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | -1436384.872
sens4 | Total benefits 10% lower | 0% | -10% |  | Option 4sens4 | 48578.8829 | 341809.4663 | 743648.9441 | 1254097.3163 | 1655936.7941 | 1949167.3776 | 2459615.7498 | 2752846.3333 | 3263294.7054 | 3569838.8867 | 4103853.8897 | 4103853.8897 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | -1436384.872
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% |  | Option 4sens5 | 48578.8829 | 327331.3164 | 714692.6443 | 1210662.8666 | 1598024.1945 | 1876776.6281 | 2372746.8504 | 2651499.2839 | 3147469.5062 | 3439535.5376 | 3960215.4025 | 3960215.4025 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | -1580023.3592
sens | 0 | 0% | 0% |  | Option 4sens | 53976.5365 | 395875.1291 | 858450.271 | 1441701.9623 | 1904277.1042 | 2246175.6968 | 2829427.388 | 3171325.9806 | 3754577.6719 | 4111269.151 | 4719435.9743 | 4719435.9743 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
sens | 0 | 0% | 0% |  | Option 4sens | 53976.5365 | 395875.1291 | 858450.271 | 1441701.9623 | 1904277.1042 | 2246175.6968 | 2829427.388 | 3171325.9806 | 3754577.6719 | 4111269.151 | 4719435.9743 | 4719435.9743 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
sens | 0 | 0% | 0% |  | Option 4sens | 53976.5365 | 395875.1291 | 858450.271 | 1441701.9623 | 1904277.1042 | 2246175.6968 | 2829427.388 | 3171325.9806 | 3754577.6719 | 4111269.151 | 4719435.9743 | 4719435.9743 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872

## Option5
Powercor
Recplacement of CRO inoperable RMUs
OPTION 5 | Replace all CRO inoperatble RMUs over 15 years
Count | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
[5 empty] | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Replacement of CRO inoperable RMUs |  | 55 | Capex | 2023-12-31 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 184894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  |  | 2023-12-31 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 184894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | Safety | 2023-12-31 | 541745.7195 | 541745.7195 | 541745.7195 | 433396.5756 | 325047.4317 | 325047.4317 | 216698.2878 | 216698.2878 | 216698.2878 | 108349.1439 | 108349.1439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Outages |  |  | Outages | 2023-12-31 | 4828378.8041 | 4508194.5333 | 4188010.2624 | 3867825.9916 | 3547641.7208 | 3227457.4499 | 2907273.1791 | 2587088.9083 | 2266904.6375 | 1946720.3666 | 1626536.0958 | 1306351.825 | 986167.5542 | 665983.2833 | 345799.0125 | 25614.7417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Asset failure | (after DF) |  | Failures | 2023-12-31 | 61637.027 | 61637.027 | 61637.027 | 49309.6216 | 36982.2162 | 36982.2162 | 24654.8108 | 24654.8108 | 24654.8108 | 12327.4054 | 12327.4054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Outage for planned program |  |  | Planned | 2023-12-31 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 5555035.6046 | 5234851.3337 | 4914667.0629 | 4473806.2428 | 4032945.4227 | 3712761.1518 | 3271900.3317 | 2951716.0609 | 2631531.7901 | 2190670.9699 | 1870486.6991 | 1429625.879 | 1109441.6082 | 665983.2833 | 345799.0125 | 25614.7417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 0 |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 4220.9954 |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.54769 |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.54769 |  | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 |  | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  |  | 2023-12-31 | 118079.0446 | 438263.3154 | 758447.5862 | 1319984.9557 | 1760845.7758 | 2081030.0466 | 2642567.416 | 2962751.6869 | 3403612.507 | 3844473.3271 | 4285334.1472 | 4726194.9674 | 5167055.7875 | 5610514.1123 | 5930698.3832 | 6250882.654 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 0
Capital expenditure
| Replacement of CRO inoperable RMUs |  |  |  | 2023-12-31 | -2311175 | -2311175 | -2311175 | -2311175 | -2311175 | -2311175 | -2311175 | -2311175 | -2311175 | -2311175 | -2311175 | -2311175 | -2311175 | -2311175 | -2311175 | -184894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Replacement of CRO inoperable RMUs |  |  |  | 2023-12-31 | -2311175 | -4622350 | -6933525 | -9244700 | -11555875 | -13867050 | -16178225 | -18489400 | -20800575 | -23111750 | -25422925 | -27734100 | -30045275 | -32356450 | -34667625 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519 | -34852519
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Replacement of CRO inoperable RMUs |  |  |  | 2023-12-31 | 0 | -95250.9862 | -190501.9724 | -285752.9586 | -381003.9448 | -476254.931 | -571505.9172 | -666756.9035 | -762007.8897 | -857258.8759 | -952509.8621 | -1047760.8483 | -1143011.8345 | -1238262.8207 | -1333513.8069 | -1428764.7931 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Annualised capex - |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 2023-12-31 | 0 | -95250.9862 | -190501.9724 | -285752.9586 | -381003.9448 | -476254.931 | -571505.9172 | -666756.9035 | -762007.8897 | -857258.8759 | -952509.8621 | -1047760.8483 | -1143011.8345 | -1238262.8207 | -1333513.8069 | -1428764.7931 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Annualised capex |  |  |  | 2023-12-31 | 0 | -95250.9862 | -190501.9724 | -285752.9586 | -381003.9448 | -476254.931 | -571505.9172 | -666756.9035 | -762007.8897 | -857258.8759 | -952509.8621 | -1047760.8483 | -1143011.8345 | -1238262.8207 | -1333513.8069 | -1428764.7931 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Operating expenditure |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  |  | 2023-12-31 | 118079.0446 | 438263.3154 | 758447.5862 | 1319984.9557 | 1760845.7758 | 2081030.0466 | 2642567.416 | 2962751.6869 | 3403612.507 | 3844473.3271 | 4285334.1472 | 4726194.9674 | 5167055.7875 | 5610514.1123 | 5930698.3832 | 6250882.654 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 0
| Other benefits value |  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  |  | 2023-12-31 | 118079.0446 | 343012.3292 | 567945.6138 | 1034231.997 | 1379841.831 | 1604775.1156 | 2071061.4988 | 2295994.7834 | 2641604.6173 | 2987214.4512 | 3332824.2852 | 3678434.1191 | 4024043.953 | 4372251.2916 | 4597184.5762 | 4822117.8609 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
| First capex year |  |  |  | 1
| First year |  |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  |  | Option 5NPV | 118079.0446 | 343012.3292 | 567945.6138 | 1034231.997 | 1379841.831 | 1604775.1156 | 2071061.4988 | 2295994.7834 | 2641604.6173 | 2987214.4512 | 3332824.2852 | 3678434.1191 | 4024043.953 | 4372251.2916 | 4597184.5762 | 4822117.8609 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
| Total annualised capex |  |  |  |  | 0 | -95250.9862 | -190501.9724 | -285752.9586 | -381003.9448 | -476254.931 | -571505.9172 | -666756.9035 | -762007.8897 | -857258.8759 | -952509.8621 | -1047760.8483 | -1143011.8345 | -1238262.8207 | -1333513.8069 | -1428764.7931 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872 | -1436384.872
| Total benefits |  |  |  |  | 118079.0446 | 438263.3154 | 758447.5862 | 1319984.9557 | 1760845.7758 | 2081030.0466 | 2642567.416 | 2962751.6869 | 3403612.507 | 3844473.3271 | 4285334.1472 | 4726194.9674 | 5167055.7875 | 5610514.1123 | 5930698.3832 | 6250882.654 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% |  | Option 5sens1 | 118079.0446 | 333487.2306 | 548895.4166 | 1005656.7012 | 1341741.4365 | 1557149.6225 | 2013910.9071 | 2229319.0931 | 2565403.8284 | 2901488.5637 | 3237573.299 | 3573658.0342 | 3909742.7695 | 4248425.0096 | 4463833.1955 | 4679241.3815 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | 4696474.0364 | -1580023.3592
sens2 | Capex 10% lower | -10% | 0% |  | Option 5sens2 | 118079.0446 | 352537.4278 | 586995.8111 | 1062807.2929 | 1417942.2254 | 1652400.6087 | 2128212.0905 | 2362670.4738 | 2717805.4063 | 3072940.3388 | 3428075.2714 | 3783210.2039 | 4138345.1364 | 4496077.5737 | 4730535.9569 | 4964994.3402 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | 4983751.0108 | -1292746.3848
sens3 | Total benefits 10% higher | 0% | 10% |  | Option 5sens3 | 129886.949 | 386838.6607 | 643790.3725 | 1166230.4926 | 1555926.4085 | 1812878.1202 | 2335318.2404 | 2592269.9521 | 2981965.868 | 3371661.784 | 3761357.6999 | 4151053.6158 | 4540749.5317 | 4933302.7029 | 5190254.4146 | 5447206.1263 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | 5467762.2632 | -1436384.872
sens4 | Total benefits 10% lower | 0% | -10% |  | Option 5sens4 | 106271.1401 | 299185.9977 | 492100.8552 | 902233.5015 | 1203757.2534 | 1396672.1109 | 1806804.7572 | 1999719.6147 | 2301243.3666 | 2602767.1185 | 2904290.8704 | 3205814.6223 | 3507338.3742 | 3811199.8804 | 4004114.7379 | 4197029.5955 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | 4212462.7841 | -1436384.872
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% |  | Option 5sens5 | 106271.1401 | 289660.899 | 473050.658 | 873658.2056 | 1165656.8589 | 1349046.6178 | 1749654.1655 | 1933043.9244 | 2225042.5777 | 2517041.2309 | 2809039.8842 | 3101038.5375 | 3393037.1908 | 3687373.5983 | 3870763.3572 | 4054153.1162 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | 4068824.2969 | -1580023.3592
sens | 0 | 0% | 0% |  | Option 5sens | 118079.0446 | 343012.3292 | 567945.6138 | 1034231.997 | 1379841.831 | 1604775.1156 | 2071061.4988 | 2295994.7834 | 2641604.6173 | 2987214.4512 | 3332824.2852 | 3678434.1191 | 4024043.953 | 4372251.2916 | 4597184.5762 | 4822117.8609 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
sens | 0 | 0% | 0% |  | Option 5sens | 118079.0446 | 343012.3292 | 567945.6138 | 1034231.997 | 1379841.831 | 1604775.1156 | 2071061.4988 | 2295994.7834 | 2641604.6173 | 2987214.4512 | 3332824.2852 | 3678434.1191 | 4024043.953 | 4372251.2916 | 4597184.5762 | 4822117.8609 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872
sens | 0 | 0% | 0% |  | Option 5sens | 118079.0446 | 343012.3292 | 567945.6138 | 1034231.997 | 1379841.831 | 1604775.1156 | 2071061.4988 | 2295994.7834 | 2641604.6173 | 2987214.4512 | 3332824.2852 | 3678434.1191 | 4024043.953 | 4372251.2916 | 4597184.5762 | 4822117.8609 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | 4840112.5236 | -1436384.872

## Consol
Powercor
Recplacement of CRO inoperable RMUs
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 96492080.8145 | 2026-06-30 |  | 6313681.0376 | 6313681.0376 | 6313681.0376 | 6447983.4955 | 6447983.4955 | 6447983.4955 | 6582285.9533 | 6582285.9533 | 6716588.4111 | 6716588.4111 | 6850890.869 | 6850890.869 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 0
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Capital expenditure | Option 2Capital expenditure | -38126336.3781 | 2026-06-30 |  | -38787809.1546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 7406360.3502 | 2026-06-30 |  | 7442438.0982 | 95653.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -21542397.225 | 2026-06-30 |  | 0 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | 0 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 89085720.4643 | 2026-06-30 |  | -1128757.0606 | 6218027.4947 | 6313681.0376 | 6447983.4955 | 6447983.4955 | 6447983.4955 | 6582285.9533 | 6582285.9533 | 6716588.4111 | 6716588.4111 | 6850890.869 | 6850890.869 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 0 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | -1128757.0606 | 4619456.6055 | 4715110.1484 | 4849412.6063 | 4849412.6063 | 4849412.6063 | 4983715.0641 | 4983715.0641 | 5118017.522 | 5118017.522 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 67543323.2393 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -21542397.225 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 89085720.4643 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Capital expenditure | Option 3Capital expenditure | -35614739.898 | 2026-06-30 |  | -7716407.6567 | -7716407.6567 | -7716407.6567 | -7716407.6567 | -7716407.6567 | -205770.8708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 22496529.2884 | 2026-06-30 |  | 8347488.9179 | 6253539.4157 | 4672058.9783 | 3090578.5409 | 1509098.1035 | 39482.4302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -18584940.0048 | 2026-06-30 |  | 0 | -318018.0814 | -636036.1628 | -954054.2442 | -1272072.3256 | -1590090.407 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 73995551.5261 | 2026-06-30 |  | -2033807.8802 | 60141.622 | 1641622.0593 | 3357404.9545 | 4938885.3919 | 6408501.0652 | 6582285.9533 | 6582285.9533 | 6716588.4111 | 6716588.4111 | 6850890.869 | 6850890.869 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 0 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | -2033807.8802 | -257876.4595 | 1005585.8965 | 2403350.7103 | 3666813.0663 | 4818410.6582 | 4983715.0641 | 4983715.0641 | 5118017.522 | 5118017.522 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | 55410611.5213 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -18584940.0048 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 73995551.5261 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | -32856497.4187 | 2026-06-30 |  | -3909646.5461 | -3909646.5461 | -3909646.5461 | -3909646.5461 | -3909646.5461 | -3909646.5461 | -3909646.5461 | -3909646.5461 | -3909646.5461 | -3600990.2398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 30705053.182 | 2026-06-30 |  | 6253609.8675 | 5711977.4388 | 5036042.5522 | 4360107.6656 | 3684172.779 | 3142540.3502 | 2466605.4636 | 1924973.0348 | 1249038.1482 | 690942.529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | -15337051.9781 | 2026-06-30 |  | 0 | -161129.1612 | -322258.3225 | -483387.4837 | -644516.645 | -805645.8062 | -966774.9675 | -1127904.1287 | -1289033.29 | -1450162.4512 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 65787027.6325 | 2026-06-30 |  | 60071.1701 | 601703.5989 | 1277638.4855 | 2087875.8299 | 2763810.7165 | 3305443.1453 | 4115680.4897 | 4657312.9185 | 5467550.2629 | 6025645.8821 | 6850890.869 | 6850890.869 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 60071.1701 | 440574.4376 | 955380.163 | 1604488.3462 | 2119294.0715 | 2499797.339 | 3148905.5222 | 3529408.7898 | 4178516.973 | 4575483.4309 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 50449975.6544 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | -15337051.9781 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 65787027.6325 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | -30259041.5195 | 2026-06-30 |  | -2572135.8856 | -2572135.8856 | -2572135.8856 | -2572135.8856 | -2572135.8856 | -2572135.8856 | -2572135.8856 | -2572135.8856 | -2572135.8856 | -2572135.8856 | -2572135.8856 | -2572135.8856 | -2572135.8856 | -2572135.8856 | -2572135.8856 | -205770.8708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 41742412.8367 | 2026-06-30 |  | 6182269.3756 | 5825932.2514 | 5469595.1273 | 4978955.5452 | 4488315.9632 | 4131978.839 | 3641339.257 | 3285002.1328 | 2928665.0086 | 2438025.4266 | 2081688.3024 | 1591048.7204 | 1234711.5962 | 741181.2183 | 384844.0941 | 28506.9699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | -12278493.5017 | 2026-06-30 |  | 0 | -106006.0271 | -212012.0543 | -318018.0814 | -424024.1085 | -530030.1357 | -636036.1628 | -742042.1899 | -848048.2171 | -954054.2442 | -1060060.2713 | -1166066.2985 | -1272072.3256 | -1378078.3527 | -1484084.3799 | -1590090.407 | -1598570.8892 | -1598570.8892 | -1598570.8892 | -1598570.8892 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 54749667.9778 | 2026-06-30 |  | 131411.662 | 487748.7862 | 844085.9104 | 1469027.9502 | 1959667.5323 | 2316004.6565 | 2940946.6963 | 3297283.8205 | 3787923.4025 | 4278562.9846 | 4769202.5666 | 5259842.1486 | 5750481.7306 | 6244012.1085 | 6600349.2327 | 6956686.3569 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 6985193.3268 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 131411.662 | 381742.7591 | 632073.8561 | 1151009.8688 | 1535643.4237 | 1785974.5208 | 2304910.5335 | 2555241.6306 | 2939875.1855 | 3324508.7403 | 3709142.2952 | 4093775.8501 | 4478409.405 | 4865933.7558 | 5116264.8528 | 5366595.9499 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 42471174.476 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | -12278493.5017 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 54749667.9778 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 1.5986 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 6.3137 | 6.3137 | 6.3137 | 6.448 | 6.448 | 6.448 | 6.5823 | 6.5823 | 6.7166 | 6.7166 | 6.8509 | 6.8509 | 6.9852 | 6.9852 | 6.9852 | 6.9852 | 6.9852 | 6.9852 | 6.9852 | 6.9852 | 6.9852 | 6.9852 | 6.9852 | 6.9852 | 0
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 0 |  |  | Energy at risk energy at risk (weighted) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Energy at risk value | 0 |  |  | Option 1 (base case) risk cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Sensitivity_calcs
Powercor
Recplacement of CRO inoperable RMUs
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
[7 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 67543323.2393 |  | 0 | -1128757.0606 | 4619456.6055 | 4715110.1484 | 4849412.6063 | 4849412.6063 | 4849412.6063 | 4983715.0641 | 4983715.0641 | 5118017.522 | 5118017.522 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 65389083.5168 |  | 0 | -1128757.0606 | 4459599.5166 | 4555253.0595 | 4689555.5174 | 4689555.5174 | 4689555.5174 | 4823857.9752 | 4823857.9752 | 4958160.433 | 4958160.433 | 5092462.8909 | 5092462.8909 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 0 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 69697562.9618 |  | 0 | -1128757.0606 | 4779313.6944 | 4874967.2374 | 5009269.6952 | 5009269.6952 | 5009269.6952 | 5143572.153 | 5143572.153 | 5277874.6109 | 5277874.6109 | 5412177.0687 | 5412177.0687 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 0 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 76451895.2858 |  | 0 | -1241632.7667 | 5241259.355 | 5346478.2522 | 5494210.9558 | 5494210.9558 | 5494210.9558 | 5641943.6594 | 5641943.6594 | 5789676.3631 | 5789676.3631 | 5937409.0667 | 5937409.0667 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 0 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 58634751.1929 |  | 0 | -1015881.3545 | 3997653.856 | 4083742.0447 | 4204614.2567 | 4204614.2567 | 4204614.2567 | 4325486.4688 | 4325486.4688 | 4446358.6808 | 4446358.6808 | 4567230.8929 | 4567230.8929 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 0 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 56480511.4704 |  | 0 | -1015881.3545 | 3837796.7671 | 3923884.9558 | 4044757.1678 | 4044757.1678 | 4044757.1678 | 4165629.3799 | 4165629.3799 | 4286501.5919 | 4286501.5919 | 4407373.804 | 4407373.804 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 67543323.2393 |  | 0 | -1128757.0606 | 4619456.6055 | 4715110.1484 | 4849412.6063 | 4849412.6063 | 4849412.6063 | 4983715.0641 | 4983715.0641 | 5118017.522 | 5118017.522 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 67543323.2393 |  | 0 | -1128757.0606 | 4619456.6055 | 4715110.1484 | 4849412.6063 | 4849412.6063 | 4849412.6063 | 4983715.0641 | 4983715.0641 | 5118017.522 | 5118017.522 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 67543323.2393 |  | 0 | -1128757.0606 | 4619456.6055 | 4715110.1484 | 4849412.6063 | 4849412.6063 | 4849412.6063 | 4983715.0641 | 4983715.0641 | 5118017.522 | 5118017.522 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | -2033807.8802 | -257876.4595 | 1005585.8965 | 2403350.7103 | 3666813.0663 | 4818410.6582 | 4983715.0641 | 4983715.0641 | 5118017.522 | 5118017.522 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 55410611.5213 |  | 0 | -2033807.8802 | -257876.4595 | 1005585.8965 | 2403350.7103 | 3666813.0663 | 4818410.6582 | 4983715.0641 | 4983715.0641 | 5118017.522 | 5118017.522 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 53552117.5208 |  | 0 | -2033807.8802 | -289678.2676 | 941982.2802 | 2307945.2859 | 3539605.8338 | 4659401.6175 | 4823857.9752 | 4823857.9752 | 4958160.433 | 4958160.433 | 5092462.8909 | 5092462.8909 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 0 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 57269105.5218 |  | 0 | -2033807.8802 | -226074.6513 | 1069189.5128 | 2498756.1348 | 3794020.2989 | 4977419.6989 | 5143572.153 | 5143572.153 | 5277874.6109 | 5277874.6109 | 5412177.0687 | 5412177.0687 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 0 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 62810166.6739 |  | 0 | -2237188.6683 | -251862.2973 | 1169748.1025 | 2739091.2058 | 4160701.6055 | 5459260.7647 | 5641943.6594 | 5641943.6594 | 5789676.3631 | 5789676.3631 | 5937409.0667 | 5937409.0667 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 0 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | 48011056.3687 |  | 0 | -1830427.0922 | -263890.6216 | 841423.6906 | 2067610.2149 | 3172924.5271 | 4177560.5517 | 4325486.4688 | 4325486.4688 | 4446358.6808 | 4446358.6808 | 4567230.8929 | 4567230.8929 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 0 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | 46152562.3682 |  | 0 | -1830427.0922 | -295692.4298 | 777820.0743 | 1972204.7905 | 3045717.2946 | 4018551.511 | 4165629.3799 | 4165629.3799 | 4286501.5919 | 4286501.5919 | 4407373.804 | 4407373.804 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 55410611.5213 |  | 0 | -2033807.8802 | -257876.4595 | 1005585.8965 | 2403350.7103 | 3666813.0663 | 4818410.6582 | 4983715.0641 | 4983715.0641 | 5118017.522 | 5118017.522 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 55410611.5213 |  | 0 | -2033807.8802 | -257876.4595 | 1005585.8965 | 2403350.7103 | 3666813.0663 | 4818410.6582 | 4983715.0641 | 4983715.0641 | 5118017.522 | 5118017.522 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 55410611.5213 |  | 0 | -2033807.8802 | -257876.4595 | 1005585.8965 | 2403350.7103 | 3666813.0663 | 4818410.6582 | 4983715.0641 | 4983715.0641 | 5118017.522 | 5118017.522 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 50449975.6544 |  | 0 | 60071.1701 | 440574.4376 | 955380.163 | 1604488.3462 | 2119294.0715 | 2499797.339 | 3148905.5222 | 3529408.7898 | 4178516.973 | 4575483.4309 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 48916270.4566 |  | 0 | 60071.1701 | 424461.5215 | 923154.3307 | 1556149.5978 | 2054842.407 | 2419232.7584 | 3052228.0255 | 3416618.3769 | 4049613.644 | 4430467.1858 | 5092462.8909 | 5092462.8909 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 51983680.8523 |  | 0 | 60071.1701 | 456687.3537 | 987605.9952 | 1652827.0945 | 2183745.736 | 2580361.9197 | 3245583.019 | 3642199.2026 | 4307420.302 | 4720499.676 | 5412177.0687 | 5412177.0687 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 57028678.4177 |  | 0 | 66078.2871 | 500744.7975 | 1083144.0115 | 1813275.9292 | 2395675.1432 | 2830341.6536 | 3560473.5712 | 3995140.0816 | 4725271.9993 | 5178048.0191 | 5937409.0667 | 5937409.0667 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 43871272.8912 |  | 0 | 54064.0531 | 380404.0777 | 827616.3144 | 1395700.7632 | 1842912.9999 | 2169253.0245 | 2737337.4733 | 3063677.4979 | 3631761.9467 | 3972918.8427 | 4567230.8929 | 4567230.8929 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 42337567.6934 |  | 0 | 54064.0531 | 364291.1616 | 795390.4822 | 1347362.0148 | 1778461.3354 | 2088688.4439 | 2640659.9765 | 2950887.085 | 3502858.6177 | 3827902.5976 | 4407373.804 | 4407373.804 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 50449975.6544 |  | 0 | 60071.1701 | 440574.4376 | 955380.163 | 1604488.3462 | 2119294.0715 | 2499797.339 | 3148905.5222 | 3529408.7898 | 4178516.973 | 4575483.4309 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 50449975.6544 |  | 0 | 60071.1701 | 440574.4376 | 955380.163 | 1604488.3462 | 2119294.0715 | 2499797.339 | 3148905.5222 | 3529408.7898 | 4178516.973 | 4575483.4309 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 50449975.6544 |  | 0 | 60071.1701 | 440574.4376 | 955380.163 | 1604488.3462 | 2119294.0715 | 2499797.339 | 3148905.5222 | 3529408.7898 | 4178516.973 | 4575483.4309 | 5252319.9798 | 5252319.9798 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 42471174.476 |  | 0 | 131411.662 | 381742.7591 | 632073.8561 | 1151009.8688 | 1535643.4237 | 1785974.5208 | 2304910.5335 | 2555241.6306 | 2939875.1855 | 3324508.7403 | 3709142.2952 | 4093775.8501 | 4478409.405 | 4865933.7558 | 5116264.8528 | 5366595.9499 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 41243325.1259 |  | 0 | 131411.662 | 371142.1563 | 610872.6507 | 1119208.0607 | 1493241.0129 | 1732971.5072 | 2241306.9172 | 2481037.4116 | 2855070.3637 | 3229103.3159 | 3603136.2681 | 3977169.2203 | 4351202.1725 | 4728125.9205 | 4967856.4148 | 5207586.9092 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 5226765.3487 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 43699023.8262 |  | 0 | 131411.662 | 392343.3618 | 653275.0615 | 1182811.677 | 1578045.8346 | 1838977.5343 | 2368514.1498 | 2629445.8496 | 3024680.0072 | 3419914.1648 | 3815148.3224 | 4210382.48 | 4605616.6376 | 5003741.591 | 5264673.2908 | 5525604.9906 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 5546479.5265 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 47946141.2738 |  | 0 | 144552.8282 | 430517.6377 | 716482.4471 | 1297912.6639 | 1731610.177 | 2017574.9864 | 2599005.2031 | 2884970.0126 | 3318667.5257 | 3752365.0388 | 4186062.5519 | 4619760.065 | 5053457.5781 | 5490334.9666 | 5776299.7761 | 6062264.5856 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 6085141.7703 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 36996207.6783 |  | 0 | 118270.4958 | 332967.8804 | 547665.2651 | 1004107.0738 | 1339676.6705 | 1554374.0551 | 2010815.8639 | 2225513.2485 | 2561082.8452 | 2896652.4419 | 3232222.0386 | 3567791.6353 | 3903361.232 | 4241532.5449 | 4456229.9295 | 4670927.3142 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 4688103.1049 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 35768358.3281 |  | 0 | 118270.4958 | 322367.2777 | 526464.0596 | 972305.2657 | 1297274.2596 | 1501371.0416 | 1947212.2476 | 2151309.0295 | 2476278.0235 | 2801247.0175 | 3126216.0114 | 3451185.0054 | 3776153.9994 | 4103724.7096 | 4307821.4916 | 4511918.2735 | 4528246.016 | 4528246.016 | 4528246.016 | 4528246.016 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 42471174.476 |  | 0 | 131411.662 | 381742.7591 | 632073.8561 | 1151009.8688 | 1535643.4237 | 1785974.5208 | 2304910.5335 | 2555241.6306 | 2939875.1855 | 3324508.7403 | 3709142.2952 | 4093775.8501 | 4478409.405 | 4865933.7558 | 5116264.8528 | 5366595.9499 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 42471174.476 |  | 0 | 131411.662 | 381742.7591 | 632073.8561 | 1151009.8688 | 1535643.4237 | 1785974.5208 | 2304910.5335 | 2555241.6306 | 2939875.1855 | 3324508.7403 | 3709142.2952 | 4093775.8501 | 4478409.405 | 4865933.7558 | 5116264.8528 | 5366595.9499 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 42471174.476 |  | 0 | 131411.662 | 381742.7591 | 632073.8561 | 1151009.8688 | 1535643.4237 | 1785974.5208 | 2304910.5335 | 2555241.6306 | 2939875.1855 | 3324508.7403 | 3709142.2952 | 4093775.8501 | 4478409.405 | 4865933.7558 | 5116264.8528 | 5366595.9499 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 5386622.4376 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 0 | 0 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 67.5433 | 55.4106 | 50.45 | 42.4712 |  | 2026-27: #NAME?; 2028-29: Option 2
sens1 | Capex 10% higher | 0 | 65.3891 | 53.5521 | 48.9163 | 41.2433 |  | 2026-27: #NAME?; 2028-29: Option 2
sens2 | Capex 10% lower | 0 | 69.6976 | 57.2691 | 51.9837 | 43.699 |  | 2026-27: #NAME?; 2028-29: Option 2
sens3 | Total benefits 10% higher | 0 | 76.4519 | 62.8102 | 57.0287 | 47.9461 |  | 2026-27: #NAME?; 2028-29: Option 2
sens4 | Total benefits 10% lower | 0 | 58.6348 | 48.0111 | 43.8713 | 36.9962 |  | 2026-27: #NAME?; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 56.4805 | 46.1526 | 42.3376 | 35.7684 |  | 2026-27: #NAME?; 2028-29: Option 2
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Workings_costs
Powercor
Recplacement of CRO inoperable RMUs
WORKINGS - COSTS
|  | Weighted average unit rate |  |  | 92447
Energy at risk
|  | Numvber of switch zones |  |  | 16053
|  | Number of switches |  |  | 377
2.348%
|  | VCR discount for planned outage |  |  | 60%
Program duration (years)
|  | Option 1 (base case) |  |  | 0
|  | Option 2 |  |  | 1
|  | Option 3 |  |  | 5
|  | Option 4 |  |  | 10
|  | Option 5 |  |  | 15
Option 1 (base case) | [6 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Option 1 (base case)
| Option 1 (base case) |  | Program duration |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case)
| Option 1 (base case) |  | Number of switches replaced pa | Option 1 (base case)Number of switches replaced pa | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option 1 (base case) |  | Remaining switches |  |  | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377
Option 1 (base case)
| Option 1 (base case) |  | Total CROd switches replaced |  |  |  | 2026-27: 0; 2027-28: 0; 2028-29: 0; 2029-30: 0; 2030-31: 0; 2031-32: 0; 2032-33: 0; 2033-34: 0; 2034-35: 0; 2035-36: 0; 2036-37: 0; 2037-38: 0; 2038-39: 0; 2039-40: 0
| Option 1 (base case) |  | Capex | Option 1 (base case)Capex |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | [6 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Option 2
| Option 2 |  | Program duration flag |  | 1 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2
| Option 2 |  | Number of switches replaced pa | Option 2Number of switches replaced pa | 377 |  | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option 2 |  | Remaining switches |  |  | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2
| Option 2 |  | Total CROd switches replaced |  |  |  | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377
| Option 2 |  | Capex | Option 2Capex |  |  | 34852519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | [6 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Option 3
| Option 3 |  | Program duration flag |  | 5 |  | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3
| Option 3 |  | Number of switches replaced pa | Option 3Number of switches replaced pa | 75 |  | 75 | 75 | 75 | 75 | 75 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option 3 |  | Remaining switches |  |  | 377 | 302 | 227 | 152 | 77 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3
| Option 3 |  | Total CROd switches replaced |  |  |  | 75 | 150 | 225 | 300 | 375 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377
| Option 3 |  | Capex | Option 3Capex |  |  | 6933525 | 6933525 | 6933525 | 6933525 | 6933525 | 184894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | [6 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Option 4
| Option 4 |  | Program duration |  | 10 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4
| Option 4 |  | Number of switches replaced pa | Option 4Number of switches replaced pa | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option 4 |  | Remaining switches |  |  | 377 | 339 | 301 | 263 | 225 | 187 | 149 | 111 | 73 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4
| Option 4 |  | Total CROd switches replaced |  |  |  | 38 | 76 | 114 | 152 | 190 | 228 | 266 | 304 | 342 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377
| Option 4 |  | Capex | Option 4Capex |  |  | 3512986 | 3512986 | 3512986 | 3512986 | 3512986 | 3512986 | 3512986 | 3512986 | 3512986 | 3235645 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | [6 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Option 5
| Option 5 |  | Program duration |  | 15 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Option 5
| Option 5 |  | Number of switches replaced pa | Option 5Number of switches replaced pa | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 2 | 0 | 0 | 0 | 0
| Option 5 |  | Remaining switches |  |  | 377 | 352 | 327 | 302 | 277 | 252 | 227 | 202 | 177 | 152 | 127 | 102 | 77 | 52 | 27 | 2 | 0 | 0 | 0 | 0 | 0
Option 5
| Option 5 |  | Total CROd switches replaced |  |  |  | 25 | 50 | 75 | 100 | 125 | 150 | 175 | 200 | 225 | 250 | 275 | 300 | 325 | 350 | 375 | 377 | 377 | 377 | 377 | 377
| Option 5 |  | Capex | Option 5Capex |  |  | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 2311175 | 184894

## Workings_risks
Powercor
Recplacement of CRO inoperable RMUs
WORKINGS - RISKS
| Number of CRO switches at 30 June 2026 |  |  | 377
| Average historical energy not served | Planned | MWh/year | 1756.6588 |  |  |  | 4
|  | Unplanned | MWh/year | 3638.3348
Energy at risk
| Numvber of switch zones |  |  | 16053 | [17 empty] | 3513000
| Number of switches |  |  | 377 | [17 empty] | 92447.3684
| VCR |  |  | 43815.4862
| VCR discount for planned outage |  |  | 60%
| VCR for planned outage |  |  | 26289.2917
Option 1 (base case) | [5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2045-46 | 2045-46 | 2045-46 | 2045-46 | 2050-51
| Number of switches replaced pa | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Remaining switches |  |  |  |  | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377
| CROd switches in service | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Value of lost load - unable to switch
| Unplanned outages |  | MWh
| % of total switch zones |  |  |  |  | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348% | 2.348%
| Unserved energy |  | MWh |  |  |  | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452 | 85.4452
| Value of lost load |  | 2023 |  |  |  | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409 | 3743824.1409
| Planned outages |  | MWh
| Unserved energy |  | MWh |  |  |  | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546 | 41.2546
| Value of unserved energy (discounted VCR) |  | 2023 |  |  |  | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632 | 1084554.6632
| Total value of unserved energy | [5 empty] | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041
Value of lost load - asset failure
Assumes failures are returned to service, not replaced
| Energy per hour per switching zone |  | MWh | 0.070337
| Weighted average PoF | [5 empty] | 0.04361% | 0.04361% | 0.04361% | 0.04983% | 0.04983% | 0.04983% | 0.05606% | 0.05606% | 0.06229% | 0.06229% | 0.06852% | 0.06852% | 0.07475% | 0.07475% | 0.07475% | 0.07475% | 0.07475% | 0.07475% | 0.07475% | 0.07475% | 0.07475% | 0.07475% | 0.07475% | 0.07475%
| Forecast asset failures | [5 empty] | 7 | 7 | 7 | 8 | 8 | 8 | 9 | 9 | 10 | 10 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
| Replacement duration |  |  | 4
| Unserved energy |  | MWh |  |  |  | 1.9694 | 1.9694 | 1.9694 | 2.2508 | 2.2508 | 2.2508 | 2.5321 | 2.5321 | 2.8135 | 2.8135 | 3.0948 | 3.0948 | 3.3762 | 3.3762 | 3.3762 | 3.3762 | 3.3762 | 3.3762 | 3.3762 | 3.3762 | 3.3762 | 3.3762 | 3.3762 | 3.3762
| Value of lost load |  |  | 43815.4862 |  |  | 86291.8378 | 86291.8378 | 86291.8378 | 98619.2432 | 98619.2432 | 98619.2432 | 110946.6486 | 110946.6486 | 123274.054 | 123274.054 | 135601.4594 | 135601.4594 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648
Value of lost load - replacing CROed switches
| Number | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bunding |  |  | 40%
| Unserved energy | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of unserved energy | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Safety risk | Weighted average per failure |  |  | 108349.1439 |  |  | 758444.0073 | 758444.0073 | 758444.0073 | 866793.1512 | 866793.1512 | 866793.1512 | 975142.2951 | 975142.2951 | 1083491.439 | 1083491.439 | 1191840.5829 | 1191840.5829 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267
Risk summary
Option 1 | Safety consequence |  |  | Safety | Option 1Safety |  | 758444.0073 | 758444.0073 | 758444.0073 | 866793.1512 | 866793.1512 | 866793.1512 | 975142.2951 | 975142.2951 | 1083491.439 | 1083491.439 | 1191840.5829 | 1191840.5829 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267 | 1300189.7267
Option 1 | Outages |  |  | Outages | Option 1Outages |  | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041 | 4828378.8041
Option 1 | Asset failure |  |  | Failures | Option 1Failures |  | 86291.8378 | 86291.8378 | 86291.8378 | 98619.2432 | 98619.2432 | 98619.2432 | 110946.6486 | 110946.6486 | 123274.054 | 123274.054 | 135601.4594 | 135601.4594 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648 | 147928.8648
Option 1 | Outage for planned program |  |  | Planned | Option 1Planned |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | [5 empty] | 5673114.6492 | 5673114.6492 | 5673114.6492 | 5793791.1985 | 5793791.1985 | 5793791.1985 | 5914467.7478 | 5914467.7478 | 6035144.2971 | 6035144.2971 | 6155820.8464 | 6155820.8464 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956 | 6276497.3956
Option 2 | [5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40
| Number of switches replaced pa | [5 empty] | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Remaining switches |  |  |  |  | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CROd switches in service | [5 empty] | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377
Value of lost load - unable to switch
| Unplanned outages |  | MWh | 3638
| % of total switch zones |  |  |  |  | 2.348% | bar: 2026-27 to 2045-46
| Unserved energy | [5 empty] | 85.4452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of lost load | [5 empty] | 3743824.1409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Planned outages |  | MWh | 1756.6588
| Planned outages | [5 empty] | 41.2546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of unserved energy (discounted VCR) |  |  | 0 |  |  | 1084554.6632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total value of unserved energy | [5 empty] | 4828378.8041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Value of lost load - asset failure
Assumes failures are returned to service, not replaced
| Energy per hour per switching zone |  | MWh | 0.070337
| Weighted average PoF | [5 empty] | 0.0218% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Forecast asset failures | [5 empty] | 0 | 0.79326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Replacement duration |  |  | 4 |  |  | 0 | 34756.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unserved energy |  |  | MWh
Value of lost load
[7 empty] | 0 | 0.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Value of lost load - replacing CROed switches
| Number | [5 empty] | 2026-27: 377; 2027-28: 0; 2028-29: 0; 2029-30: 0; 2030-31: 0; 2031-32: 0; 2032-33: 0; 2033-34: 0; 2034-35: 0; 2035-36: 0; 2036-37: 0; 2037-38: 0; 2038-39: 0
| Bunding |  |  | 40%
| Unserved energy | [5 empty] | 42.4273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of unserved energy | [5 empty] | 1858972.7344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Safety risk | Weighted average per failure |  |  | 108349.1439 |  |  | 2026-27: 0; 2027-28: 85948.8328; 2028-29: 0; 2029-30: 0; 2030-31: 0; 2031-32: 0; 2032-33: 0; 2033-34: 0; 2034-35: 0; 2035-36: 0; 2036-37: 0; 2037-38: 0
Risk summary
Option 2 | Safety consequence |  |  | Safety | Option 2Safety |  | 0 | 85948.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Outages |  |  | Outages | Option 2Outages |  | 4828378.8041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Asset failure |  |  | Failures | Option 2Failures |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Outage for planned program |  |  | Planned | Option 2Planned |  | 1858972.7344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | [5 empty] | 6687351.5385 | 85948.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | [5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40
| Number of switches replaced pa | [5 empty] | 75 | 75 | 75 | 75 | 75 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Remaining switches |  |  |  |  | 377 | 302 | 227 | 152 | 77 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CROd switches in service | [5 empty] | 75 | 150 | 225 | 300 | 375 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377
Value of lost load - unable to switch
| Unplanned outages |  | MWh | 3638
| % of total switch zones |  |  |  |  | 2.348% | 1.881% | 1.414% | 0.9469% | 0.4797% | 0.01246% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Unserved energy | [5 empty] | 85.4452 | 68.4468 | 51.4485 | 34.4501 | 17.4517 | 0.45329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of lost load | [5 empty] | 3743824.1409 | 2999031.5399 | 2254238.9389 | 1509446.338 | 764653.737 | 19861.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Planned outages |  | MWh | 1756.6588
| Planned outages | [5 empty] | 41.2546 | 33.0475 | 24.8403 | 16.6332 | 8.426 | 0.21886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of unserved energy (discounted VCR) |  |  | 0 |  |  | 1084554.6632 | 868794.4517 | 653034.2402 | 437274.0287 | 221513.8172 | 5753.6056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total value of unserved energy | [5 empty] | 4828378.8041 | 3867825.9916 | 2907273.1791 | 1946720.3666 | 986167.5542 | 25614.7417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Value of lost load - asset failure
Assumes failures are returned to service, not replaced
| Energy per hour per switching zone |  | MWh | 0.070337
| Weighted average PoF | [5 empty] | 0.1188% | 0.07131% | 0.04754% | 0.02377% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0
| Forecast asset failures | [5 empty] | 19.0789 | 11.4473 | 7.6316 | 3.8158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Replacement duration |  |  | 4
| Unserved energy |  |  | MWh |  |  | 5.3678 | 3.2207 | 2.1471 | 1.0736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of lost load | [5 empty] | 235193.5333 | 141116.12 | 94077.4133 | 47038.7067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Value of lost load - replacing CROed switches
| Number | [5 empty] | 2026-27: 75; 2027-28: 75; 2028-29: 75; 2029-30: 75; 2030-31: 75; 2031-32: 2; 2032-33: 0; 2033-34: 0; 2034-35: 0; 2035-36: 0; 2036-37: 0; 2037-38: 0; 2038-39: 0
| Bunding |  |  | 40%
| Unserved energy | [5 empty] | 8.4404 | 8.4404 | 8.4404 | 8.4404 | 8.4404 | 0.22508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of unserved energy | [5 empty] | 369822.162 | 369822.162 | 369822.162 | 369822.162 | 369822.162 | 9861.9243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Safety risk | Weighted average per failure |  |  | 108349.1439 |  |  | 2026-27: 2067184.2251; 2027-28: 1240310.535; 2028-29: 826873.69; 2029-30: 413436.845; 2030-31: 0; 2031-32: 0; 2032-33: 0; 2033-34: 0; 2034-35: 0; 2035-36: 0; 2036-37: 0; 2037-38: 0
Option 3 | Risk summary
Option 3 | Safety consequence |  |  | Safety | Option 3Safety |  | 2067184.2251 | 1240310.535 | 826873.69 | 413436.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Value of unserved energy (discounted VCR) |  |  | Outages | Option 3Outages |  | 4828378.8041 | 3867825.9916 | 2907273.1791 | 1946720.3666 | 986167.5542 | 25614.7417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Asset failure |  |  | Failures | Option 3Failures |  | 235193.5333 | 141116.12 | 94077.4133 | 47038.7067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Outage for planned program |  |  | Planned | Option 3Planned |  | 369822.162 | 369822.162 | 369822.162 | 369822.162 | 369822.162 | 9861.9243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | [5 empty] | 7500578.7244 | 5619074.8086 | 4198046.4445 | 2777018.0803 | 1355989.7162 | 35476.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | [5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40
| Number of switches replaced pa | [5 empty] | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Remaining switches |  |  |  |  | 377 | 339 | 301 | 263 | 225 | 187 | 149 | 111 | 73 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CROd switches in service | [5 empty] | 38 | 76 | 114 | 152 | 190 | 228 | 266 | 304 | 342 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377
Value of lost load - unable to switch
| Unplanned outages |  | MWh | 3638
| % of total switch zones |  |  |  |  | 2.348% | 2.112% | 1.875% | 1.638% | 1.402% | 1.165% | 0.9282% | 0.6915% | 0.4547% | 0.218% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Unserved energy | [5 empty] | 85.4452 | 76.8327 | 68.2202 | 59.6077 | 50.9952 | 42.3826 | 33.7701 | 25.1576 | 16.5451 | 7.9326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of lost load | [5 empty] | 3743824.1409 | 3366462.5564 | 2989100.9719 | 2611739.3874 | 2234377.8029 | 1857016.2184 | 1479654.6339 | 1102293.0494 | 724931.4649 | 347569.8805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Planned outages |  | MWh | 1756.6588
| Planned outages | [5 empty] | 41.2546 | 37.0963 | 32.938 | 28.7797 | 24.6215 | 20.4632 | 16.3049 | 12.1466 | 7.9883 | 3.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of unserved energy (discounted VCR) |  |  | 0 |  |  | 1084554.6632 | 975236.156 | 865917.6489 | 756599.1417 | 647280.6345 | 537962.1274 | 428643.6202 | 319325.113 | 210006.6059 | 100688.0987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total value of unserved energy | [5 empty] | 4828378.8041 | 4341698.7124 | 3855018.6208 | 3368338.5291 | 2881658.4375 | 2394978.3458 | 1908298.2541 | 1421618.1625 | 934938.0708 | 448257.9792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Value of lost load - asset failure
Assumes failures are returned to service, not replaced
| Energy per hour per switching zone |  | MWh | 0.070337
| Weighted average PoF | [5 empty] | 0.03115% | 0.03115% | 0.02492% | 0.01869% | 0.01246% | 0.01246% | 0.006229% | 0.006229% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Forecast asset failures | [5 empty] | 5 | 5 | 4 | 3 | 2 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Replacement duration |  |  | 4
| Unserved energy |  |  | MWh |  |  | 1.4067 | 1.4067 | 1.1254 | 0.84404 | 0.5627 | 0.5627 | 0.28135 | 0.28135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of lost load | [5 empty] | 61637.027 | 61637.027 | 49309.6216 | 36982.2162 | 24654.8108 | 24654.8108 | 12327.4054 | 12327.4054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Value of lost load - replacing CROed switches
| Number | [5 empty] | 2026-27: 38; 2027-28: 38; 2028-29: 38; 2029-30: 38; 2030-31: 38; 2031-32: 38; 2032-33: 38; 2033-34: 38; 2034-35: 38; 2035-36: 35; 2036-37: 0; 2037-38: 0; 2038-39: 0
| Bunding |  |  | 40%
| Unserved energy | [5 empty] | 4.2765 | 4.2765 | 4.2765 | 4.2765 | 4.2765 | 4.2765 | 4.2765 | 4.2765 | 4.2765 | 3.9389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of unserved energy | [5 empty] | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 172583.6756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Safety risk | Weighted average per failure |  |  | 108349.1439 |  |  | 2026-27: 541745.7195; 2027-28: 541745.7195; 2028-29: 433396.5756; 2029-30: 325047.4317; 2030-31: 216698.2878; 2031-32: 216698.2878; 2032-33: 108349.1439; 2033-34: 108349.1439; 2034-35: 0; 2035-36: 0; 2036-37: 0; 2037-38: 0
Option 4 | Risk summary
Option 4 | Safety consequence |  |  | Safety | Option 4Safety |  | 541745.7195 | 541745.7195 | 433396.5756 | 325047.4317 | 216698.2878 | 216698.2878 | 108349.1439 | 108349.1439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Value of unserved energy (discounted VCR) |  |  | Outages | Option 4Outages |  | 4828378.8041 | 4341698.7124 | 3855018.6208 | 3368338.5291 | 2881658.4375 | 2394978.3458 | 1908298.2541 | 1421618.1625 | 934938.0708 | 448257.9792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Asset failure |  |  | Failures | Option 4Failures |  | 61637.027 | 61637.027 | 49309.6216 | 36982.2162 | 24654.8108 | 24654.8108 | 12327.4054 | 12327.4054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Outage for planned program |  |  | Planned | Option 4Planned |  | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 187376.5621 | 172583.6756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | [5 empty] | 5619138.1127 | 5132458.021 | 4525101.38 | 3917744.7391 | 3310388.0981 | 2823708.0065 | 2216351.3655 | 1729671.2739 | 1122314.6329 | 620841.6548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | [5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40 | 2039-40
| Number of switches replaced pa | [5 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Remaining switches |  |  |  |  | 377 | 352 | 327 | 302 | 277 | 252 | 227 | 202 | 177 | 152 | 127 | 102 | 77 | 52 | 27 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CROd switches in service | [5 empty] | 25 | 50 | 75 | 100 | 125 | 150 | 175 | 200 | 225 | 250 | 275 | 300 | 325 | 350 | 375 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377 | 377
Value of lost load - unable to switch
| Unplanned outages |  | MWh | 3638
| % of total switch zones |  |  |  |  | 2.348% | 2.193% | 2.037% | 1.881% | 1.726% | 1.57% | 1.414% | 1.258% | 1.103% | 0.9469% | 0.7911% | 0.6354% | 0.4797% | 0.3239% | 0.1682% | 0.01246% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Unserved energy | [5 empty] | 85.4452 | 79.7791 | 74.113 | 68.4468 | 62.7807 | 57.1146 | 51.4485 | 45.7823 | 40.1162 | 34.4501 | 28.7839 | 23.1178 | 17.4517 | 11.7855 | 6.1194 | 0.45329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of lost load | [5 empty] | 3743824.1409 | 3495559.9406 | 3247295.7402 | 2999031.5399 | 2750767.3396 | 2502503.1393 | 2254238.9389 | 2005974.7386 | 1757710.5383 | 1509446.338 | 1261182.1376 | 1012917.9373 | 764653.737 | 516389.5367 | 268125.3363 | 19861.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Planned outages |  | MWh | 1756.6588
| Planned outages | [5 empty] | 41.2546 | 38.5189 | 35.7832 | 33.0475 | 30.3117 | 27.576 | 24.8403 | 22.1046 | 19.3689 | 16.6332 | 13.8974 | 11.1617 | 8.426 | 5.6903 | 2.9546 | 0.21886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of unserved energy (discounted VCR) |  |  | 0 |  |  | 1084554.6632 | 1012634.5927 | 940714.5222 | 868794.4517 | 796874.3812 | 724954.3107 | 653034.2402 | 581114.1697 | 509194.0992 | 437274.0287 | 365353.9582 | 293433.8877 | 221513.8172 | 149593.7466 | 77673.6761 | 5753.6056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total value of unserved energy | [5 empty] | 4828378.8041 | 4508194.5333 | 4188010.2624 | 3867825.9916 | 3547641.7208 | 3227457.4499 | 2907273.1791 | 2587088.9083 | 2266904.6375 | 1946720.3666 | 1626536.0958 | 1306351.825 | 986167.5542 | 665983.2833 | 345799.0125 | 25614.7417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Value of lost load - asset failure
Assumes failures are returned to service, not replaced
| Energy per hour per switching zone |  | MWh | 0.070337
| Weighted average PoF | [5 empty] | 0.03115% | 0.03115% | 0.03115% | 0.02492% | 0.01869% | 0.01869% | 0.01246% | 0.01246% | 0.01246% | 0.006229% | 0.006229% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Forecast asset failures | [5 empty] | 5 | 5 | 5 | 4 | 3 | 3 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Replacement duration |  |  | 4
| Unserved energy |  |  | MWh |  |  | 1.4067 | 1.4067 | 1.4067 | 1.1254 | 0.84404 | 0.84404 | 0.5627 | 0.5627 | 0.5627 | 0.28135 | 0.28135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of lost load | [5 empty] | 61637.027 | 61637.027 | 61637.027 | 49309.6216 | 36982.2162 | 36982.2162 | 24654.8108 | 24654.8108 | 24654.8108 | 12327.4054 | 12327.4054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Value of lost load - replacing CROed switches
| Number | [5 empty] | 2026-27: 25; 2027-28: 25; 2028-29: 25; 2029-30: 25; 2030-31: 25; 2031-32: 25; 2032-33: 25; 2033-34: 25; 2034-35: 25; 2035-36: 25; 2036-37: 25; 2037-38: 25; 2038-39: 25
| Bunding |  |  | 40%
| Unserved energy | [5 empty] | 2.8135 | 2.8135 | 2.8135 | 2.8135 | 2.8135 | 2.8135 | 2.8135 | 2.8135 | 2.8135 | 2.8135 | 2.8135 | 2.8135 | 2.8135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of unserved energy | [5 empty] | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Safety risk | Weighted average per failure |  |  | 108349.1439 |  |  | 2026-27: 541745.7195; 2027-28: 541745.7195; 2028-29: 541745.7195; 2029-30: 433396.5756; 2030-31: 325047.4317; 2031-32: 325047.4317; 2032-33: 216698.2878; 2033-34: 216698.2878; 2034-35: 216698.2878; 2035-36: 108349.1439; 2036-37: 108349.1439; 2037-38: 0
Option 5 | Risk summary
Option 5 | Safety consequence |  |  | Safety | Option 5Safety |  | 541745.7195 | 541745.7195 | 541745.7195 | 433396.5756 | 325047.4317 | 325047.4317 | 216698.2878 | 216698.2878 | 216698.2878 | 108349.1439 | 108349.1439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Value of unserved energy (discounted VCR) |  |  | Outages | Option 5Outages |  | 4828378.8041 | 4508194.5333 | 4188010.2624 | 3867825.9916 | 3547641.7208 | 3227457.4499 | 2907273.1791 | 2587088.9083 | 2266904.6375 | 1946720.3666 | 1626536.0958 | 1306351.825 | 986167.5542 | 665983.2833 | 345799.0125 | 25614.7417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Asset failure |  |  | Failures | Option 5Failures |  | 61637.027 | 61637.027 | 61637.027 | 49309.6216 | 36982.2162 | 36982.2162 | 24654.8108 | 24654.8108 | 24654.8108 | 12327.4054 | 12327.4054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Outage for planned program |  |  | Planned | Option 5Planned |  | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 123274.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | [5 empty] | 5555035.6046 | 5234851.3337 | 4914667.0629 | 4473806.2428 | 4032945.4227 | 3712761.1518 | 3271900.3317 | 2951716.0609 | 2631531.7901 | 2190670.9699 | 1870486.6991 | 1429625.879 | 1109441.6082 | 665983.2833 | 345799.0125 | 25614.7417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Misc_calcs
Powercor
Recplacement of CRO inoperable RMUs
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 1 | TRUE
| Option 3 | 1 | TRUE
| Option 4 | 1 | TRUE
| Option 5 | 1 | TRUE
| First year | 1
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
Powercor
Recplacement of CRO inoperable RMUs
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | FALSE |  |  | FALSE
Option5 | Option 5 | FALSE |  |  | FALSE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
|  |  | CitiPower | Powercor | United Energy
| Reliability in worst-served areas | per MWh | 0 | 151432.8174 | 0
| Network resilience | per MWh | 0 | 24590 | 38560
| Enabling solar exports | per MWh | 4220.9954 | 88.3577 | 862.6028
| Aesthetics | per customer impacted | 0 | 0 | 0
| Customer value of time - residential | per minute customer time | 0.54769 | 0.35181 | 0.34751
| Customer value of time - business | per minute customer time | 0.54769 | 0.35181 | 0.34751
| Communication | per customer impacted | 0 | 0 | 0
| Information accessibility | per customer impacted | 0 | 0 | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020