## Cover
Powercor
Regulatory proposal 2026-31
HV underground cables
| Model number: | 4.14
2025-01-31
14

## Summary
Powercor
HV cable replacement
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Replace highest 5 delta risk cable sections |  | -3.7851 | 15.5522 | 11.7671
| Option 3 | Replace highest 10 delta risk cable sections |  | -7.7898 | 26.8249 | 19.0352
| Option 4 | Monitor highest delta risk cable sections and replace those with high partial discharge |  | -7.4897 | 18.0034 | 10.5137
| Option 5 | Replace highest 5 delta risk cable sections and monitor further 10 |  | -5.829 | 22.0644 | 16.2354
NPV
| Preferred option: |  |  | 2026-06-30
| Option 3 | Replace highest 10 delta risk cable sections |  | 19.0352
PREFERRED OPTION
Preferred Option
Option 3
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 3.3388 | 3.3388 | 3.3388 | 3.3388 | 3.3388 |  | 16.6939
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
Preferred option capex and risk mitigated ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 11.7671 | 19.0352 | 10.5137 | 16.2354 |  | Option 3
| Capex 10% higher |  | 0 | 11.3886 | 18.2562 | 9.7648 | 15.6525 |  | Option 3
| Capex 10% lower |  | 0 | 12.1456 | 19.8141 | 11.2627 | 16.8183 |  | Option 3
| Total benefits 10% higher |  | 0 | 13.3224 | 21.7177 | 12.3141 | 18.4418 |  | Option 3
| Total benefits 10% lower |  | 0 | 10.2119 | 16.3527 | 8.7134 | 14.0289 |  | Option 3
| Capex 10% higher & total benefits 10% lower |  | 0 | 9.8334 | 15.5737 | 7.9644 | 13.446 |  | Option 3
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
Powercor
HV cable replacement
Project
|  | Business: |  | Powercor
|  | Descripton: |  | HV cable replacement
|  | Date of cost inputs: |  | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Replace highest 5 delta risk cable sections
|  | Option 3 |  | Replace highest 10 delta risk cable sections
|  | Option 4 |  | Monitor highest delta risk cable sections and replace those with high partial discharge
|  | Option 5 |  | Replace highest 5 delta risk cable sections and monitor further 10
|  | Compliance project |  | No
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2024-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | Network average |  | Network average | 47819.7904 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 151432.8174 | 2024-12-31 | per MWh
|  | Network resilience |  |  |  | 24590 | 2024-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 88.3577 | 2024-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2024-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.35181 | 2024-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.35181 | 2024-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2024-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2024-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
Powercor
HV cable replacement
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 789.9323 | 944.9372 | 1137.1579 | 1375.5362 | 1671.8055 | 2040.6377 | 2494.6094 | 2953.5521 | 3416.3395 | 3882.7675 | 4456.3152 | 5039.2423 | 5582.7339 | 5971.4492 | 6271.735 | 6537.6451 | 6696.7095 | 6831.8415 | 6945.3462 | 7047.2115 | 7141.2138 | 7208.0122 | 7259.9261 | 7305.1747 | 7348.3085
| Energy at risk value | $/MWh | 47819.7904 | 2023-12-31 |  | 37774399.3068 | 45186699.8028 | 54378650.3849 | 65777854.5136 | 79945389.9387 | 97582865.666 | 119291699.6627 | 141238243.3788 | 163368638.9361 | 185673129.7659 | 213100060.4404 | 240975508.3934 | 266965162.6204 | 285553449.9191 | 299913050.9078 | 312628820.1443 | 320235242.5828 | 326697226.8074 | 332124999.5011 | 336996178.8594 | 341491347.9966 | 344685633.8186 | 347168145.3063 | 349331922.4088 | 351394574.0967
| Safety consequence | (after DF) |  | 2023-12-31 |  | 3423495.0151 | 4095272.0457 | 4928338.8204 | 5961449.0545 | 7245453.2424 | 8843938.2307 | 10811410.5488 | 12800426.5065 | 14806104.9624 | 16827561.6783 | 19313265.281 | 21839618.0189 | 24195061.2112 | 25879718.2825 | 27181129.3786 | 28333559.9504 | 29022930.2589 | 29608580.0954 | 30100499.308 | 30541974.4487 | 30949371.7711 | 31238869.9972 | 31463860.0925 | 31659963.2804 | 31846901.4687
| Unplanned replacements |  |  | 2023-12-31 |  | 1900959.3721 | 2273976.0807 | 2736551.9238 | 3310205.6237 | 4023172.8645 | 4910761.4271 | 6003237.0773 | 7107675.2346 | 8221365.5544 | 9343817.047 | 10724050.2704 | 12126854.6832 | 13434758.3875 | 14370195.6043 | 15092828.355 | 15732736.8949 | 16115522.5986 | 16440715.5785 | 16713862.8836 | 16959000.1783 | 17185215.1296 | 17345964.4118 | 17470894.3528 | 17579784.3004 | 17683585.2114
| Environmental consequence | (after DF) |  | 2023-12-31 |  | 165853.3837 | 198398.0474 | 238756.4947 | 288806.1742 | 351010.5701 | 428450.1875 | 523765.6297 | 620124.7672 | 717291.13 | 815221.8806 | 935643.3656 | 1058034.1236 | 1172145.0605 | 1253759.3391 | 1316807.0236 | 1372637.2524 | 1406034.2335 | 1434406.4107 | 1458237.7484 | 1479625.2911 | 1499361.9124 | 1513386.8372 | 1524286.6249 | 1533786.968 | 1542843.3069
| Response cost |  |  | 2023-12-31 |  | 1114904.0814 | 1333676.6953 | 1604975.3369 | 1941420.6396 | 2359572.7044 | 2880139.3854 | 3520871.4174 | 4168619.4057 | 4821793.7456 | 5480106.4736 | 6289607.0219 | 7112345.4708 | 7879425.083 | 8428054.7834 | 8851875.6262 | 9227179.093 | 9451681.1785 | 9642405.3917 | 9802605.0518 | 9946376.9673 | 10079051.014 | 10173329.7416 | 10246600.5874 | 10310464.0497 | 10371342.8148
|  |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 44379611.1592 | 53088022.6719 | 63887272.9608 | 77279736.0056 | 93924599.3201 | 114646154.8967 | 140150984.336 | 165935089.2929 | 191935194.3285 | 218139836.8455 | 250362626.3792 | 283112360.6898 | 313646552.3626 | 335485177.9284 | 352355691.2911 | 367294933.335 | 376231410.8523 | 383823334.2837 | 390200204.4928 | 395923155.745 | 401204347.8238 | 404957184.8064 | 407873786.9639 | 410415921.0073 | 412839246.8985
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
Powercor
HV cable replacement
OPTION 2 | Replace highest 5 delta risk cable sections
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Cable replacement |  | 60 | 2023-12-31 | 1457739.1194 | 1457739.1194 | 1457739.1194 | 1457739.1194 | 1457739.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 1457739.1194 | 1457739.1194 | 1457739.1194 | 1457739.1194 | 1457739.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 789.9323 | 943.4738 | 1133.5254 | 1368.7786 | 1660.6319 | 2023.3111 | 2473.3684 | 2930.0219 | 3392.5112 | 3858.9392 | 4432.4869 | 5015.4139 | 5558.9055 | 5947.6209 | 6247.9066 | 6513.8168 | 6672.8811 | 6808.0131 | 6921.5179 | 7023.3832 | 7117.3855 | 7184.1839 | 7236.0978 | 7281.3464 | 7324.4802
| Energy at risk value | $/MWh | 47819.7904 | 2023-12-31 | 37774399.3068 | 45116717.067 | 54204947.066 | 65454705.8675 | 79411068.8971 | 96754312.1159 | 118275957.125 | 140113035.1217 | 162229172.9887 | 184533663.8185 | 211960594.493 | 239836042.446 | 265825696.673 | 284413983.9717 | 298773584.9603 | 311489354.1969 | 319095776.6354 | 325557760.8599 | 330985533.5537 | 335856712.912 | 340351882.0492 | 343546167.8712 | 346028679.3588 | 348192456.4614 | 350255108.1493
| Safety consequence | (after DF) |  | 2023-12-31 | 3423495.0151 | 4091030.7744 | 4917811.6111 | 5941864.7803 | 7213070.9628 | 8793724.1259 | 10749851.9421 | 12732233.7804 | 14737048.1556 | 16758504.8716 | 19244208.4742 | 21770561.2121 | 24126004.4044 | 25810661.4758 | 27112072.5718 | 28264503.1437 | 28953873.4521 | 29539523.2887 | 30031442.5012 | 30472917.6419 | 30880314.9644 | 31169813.1904 | 31394803.2858 | 31590906.4736 | 31777844.662
| Unplanned replacements |  |  | 2023-12-31 | 1900959.3721 | 2266730.141 | 2718566.8627 | 3276747.1488 | 3967849.8193 | 4824973.8539 | 5898068.1509 | 6991172.3414 | 8103386.4348 | 9225837.9274 | 10606071.1507 | 12008875.5635 | 13316779.2679 | 14252216.4846 | 14974849.2354 | 15614757.7752 | 15997543.479 | 16322736.4589 | 16595883.764 | 16841021.0587 | 17067236.01 | 17227985.2921 | 17352915.2332 | 17461805.1808 | 17565606.0917
| Environmental consequence | (after DF) |  | 2023-12-31 | 165853.3837 | 198357.0741 | 238654.7954 | 288616.9781 | 350697.7374 | 427965.0884 | 523170.9358 | 619465.9836 | 716623.9988 | 814554.7494 | 934976.2344 | 1057366.9924 | 1171477.9293 | 1253092.2079 | 1316139.8924 | 1371970.1212 | 1405367.1023 | 1433739.2795 | 1457570.6172 | 1478958.1599 | 1498694.7812 | 1512719.706 | 1523619.4937 | 1533119.8368 | 1542176.1757
| Response cost |  |  | 2023-12-31 | 1114904.0814 | 1332619.212 | 1602350.5701 | 1936537.6596 | 2351498.7762 | 2867619.4183 | 3505522.9065 | 4151616.7987 | 4804575.6959 | 5462888.4239 | 6272388.9722 | 7095127.4211 | 7862207.0333 | 8410836.7337 | 8834657.5765 | 9209961.0434 | 9434463.1288 | 9625187.342 | 9785387.0021 | 9929158.9176 | 10061832.9643 | 10156111.6919 | 10229382.5378 | 10293246 | 10354124.7651
|  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 44379611.1592 | 53005454.2684 | 63682330.9054 | 76898472.4343 | 93294186.1928 | 113668594.6024 | 138952571.0603 | 164607524.0259 | 190590807.2738 | 216795449.7908 | 249018239.3244 | 281767973.6351 | 312302165.3079 | 334140790.8737 | 351011304.2364 | 365950546.2803 | 374887023.7976 | 382478947.229 | 388855817.4381 | 394578768.6902 | 399859960.7691 | 403612797.7516 | 406529399.9092 | 409071533.9526 | 411494859.8438
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 82568.4034 | 204942.0554 | 381263.5713 | 630413.1273 | 977560.2943 | 1198413.2757 | 1327565.2671 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547
Capital expenditure
| Cable replacement |  |  | 2023-12-31 | -1457739.1194 | -1457739.1194 | -1457739.1194 | -1457739.1194 | -1457739.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Cable replacement |  |  | 2023-12-31 | -1457739.1194 | -2915478.2389 | -4373217.3583 | -5830956.4778 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Cable replacement |  |  | 2023-12-31 | 0 | -58438.7515 | -116877.5031 | -175316.2546 | -233755.0062 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -58438.7515 | -116877.5031 | -175316.2546 | -233755.0062 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577
| Annualised capex |  |  | 2023-12-31 | 0 | -58438.7515 | -116877.5031 | -175316.2546 | -233755.0062 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 82568.4034 | 204942.0554 | 381263.5713 | 630413.1273 | 977560.2943 | 1198413.2757 | 1327565.2671 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 24129.6519 | 88064.5523 | 205947.3167 | 396658.1211 | 685366.5366 | 906219.518 | 1035371.5093 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | 24129.6519 | 88064.5523 | 205947.3167 | 396658.1211 | 685366.5366 | 906219.518 | 1035371.5093 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297
| Total annualised capex |  |  |  | 0 | -58438.7515 | -116877.5031 | -175316.2546 | -233755.0062 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577
| Total benefits |  |  |  | 0 | 82568.4034 | 204942.0554 | 381263.5713 | 630413.1273 | 977560.2943 | 1198413.2757 | 1327565.2671 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547 | 1344387.0547
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | 18285.7767 | 76376.802 | 188415.6912 | 373282.6205 | 656147.1608 | 877000.1422 | 1006152.1336 | 1022973.9212 | 1022973.9212 | 1022973.9212 | 1022973.9212 | 1022973.9212 | 1022973.9212 | 1022973.9212 | 1022973.9212 | 1022973.9212 | 1022973.9212 | 1022973.9212 | 1022973.9212 | 1022973.9212 | 1022973.9212 | 1022973.9212 | 1022973.9212 | 1022973.9212
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | 29973.527 | 99752.3026 | 223478.9422 | 420033.6217 | 714585.9123 | 935438.8937 | 1064590.8851 | 1081412.6728 | 1081412.6728 | 1081412.6728 | 1081412.6728 | 1081412.6728 | 1081412.6728 | 1081412.6728 | 1081412.6728 | 1081412.6728 | 1081412.6728 | 1081412.6728 | 1081412.6728 | 1081412.6728 | 1081412.6728 | 1081412.6728 | 1081412.6728 | 1081412.6728
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | 32386.4922 | 108558.7578 | 244073.6738 | 459699.4338 | 783122.566 | 1026060.8455 | 1168128.0361 | 1186632.0025 | 1186632.0025 | 1186632.0025 | 1186632.0025 | 1186632.0025 | 1186632.0025 | 1186632.0025 | 1186632.0025 | 1186632.0025 | 1186632.0025 | 1186632.0025 | 1186632.0025 | 1186632.0025 | 1186632.0025 | 1186632.0025 | 1186632.0025 | 1186632.0025
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | 15872.8115 | 67570.3467 | 167820.9596 | 333616.8084 | 587610.5071 | 786378.1904 | 902614.9826 | 917754.5915 | 917754.5915 | 917754.5915 | 917754.5915 | 917754.5915 | 917754.5915 | 917754.5915 | 917754.5915 | 917754.5915 | 917754.5915 | 917754.5915 | 917754.5915 | 917754.5915 | 917754.5915 | 917754.5915 | 917754.5915 | 917754.5915
sens5 | Capex 10% higher & total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | 10028.9364 | 55882.5964 | 150289.3341 | 310241.3078 | 558391.1314 | 757158.8146 | 873395.6069 | 888535.2158 | 888535.2158 | 888535.2158 | 888535.2158 | 888535.2158 | 888535.2158 | 888535.2158 | 888535.2158 | 888535.2158 | 888535.2158 | 888535.2158 | 888535.2158 | 888535.2158 | 888535.2158 | 888535.2158 | 888535.2158 | 888535.2158
sens | 0 | 0% | 0% | Option 2sens | 0 | 24129.6519 | 88064.5523 | 205947.3167 | 396658.1211 | 685366.5366 | 906219.518 | 1035371.5093 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297
sens | 0 | 0% | 0% | Option 2sens | 0 | 24129.6519 | 88064.5523 | 205947.3167 | 396658.1211 | 685366.5366 | 906219.518 | 1035371.5093 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297
sens | 0 | 0% | 0% | Option 2sens | 0 | 24129.6519 | 88064.5523 | 205947.3167 | 396658.1211 | 685366.5366 | 906219.518 | 1035371.5093 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297 | 1052193.297

## Option3
Powercor
HV cable replacement
OPTION 3 | Replace highest 10 delta risk cable sections
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Cable replacement |  | 60 | 2023-12-31 | 3000038.9077 | 3000038.9077 | 3000038.9077 | 3000038.9077 | 3000038.9077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 3000038.9077 | 3000038.9077 | 3000038.9077 | 3000038.9077 | 3000038.9077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 789.9323 | 942.4715 | 1130.9583 | 1363.8587 | 1652.2612 | 2009.9678 | 2457.3749 | 2912.8328 | 3373.9412 | 3840.36 | 4413.9077 | 4996.8347 | 5540.3263 | 5929.0417 | 6229.3274 | 6495.2376 | 6654.3019 | 6789.4339 | 6902.9386 | 7004.804 | 7098.8063 | 7165.6047 | 7217.5186 | 7262.7671 | 7305.901
| Energy at risk value | $/MWh | 47819.7904 | 2023-12-31 | 37774399.3068 | 45068787.4 | 54082191.0203 | 65219435.8834 | 79010786.0027 | 96116237.3484 | 117511153.2139 | 139291055.1811 | 161341159.0964 | 183645209.1063 | 211072139.7808 | 238947587.7338 | 264937241.9608 | 283525529.2595 | 297885130.2482 | 310600899.4847 | 318207321.9232 | 324669306.1478 | 330097078.8415 | 334968258.1999 | 339463427.337 | 342657713.159 | 345140224.6467 | 347304001.7492 | 349366653.4371
| Safety consequence | (after DF) |  | 2023-12-31 | 3423495.0151 | 4087118.9557 | 4907840.0449 | 5922837.0236 | 7180829.7607 | 8742527.7566 | 10688294.1073 | 12665787.5691 | 14665914.2342 | 16687340.4696 | 19173044.0722 | 21699396.8101 | 24054840.0024 | 25739497.0738 | 27040908.1698 | 28193338.7416 | 28882709.0501 | 29468358.8867 | 29960278.0992 | 30401753.2399 | 30809150.5624 | 31098648.7884 | 31323638.8838 | 31519742.0716 | 31706680.26
| Unplanned replacements |  |  | 2023-12-31 | 1900959.3721 | 2266556.5788 | 2717897.5602 | 3275067.7755 | 3964363.9898 | 4818475.5319 | 5891198.2458 | 6985150.6633 | 8093788.7241 | 9216212.4786 | 10596445.7019 | 11999250.1147 | 13307153.8191 | 14242591.0358 | 14965223.7866 | 15605132.3264 | 15987918.0302 | 16313111.0101 | 16586258.3152 | 16831395.6099 | 17057610.5612 | 17218359.8433 | 17343289.7844 | 17452179.732 | 17555980.6429
| Environmental consequence | (after DF) |  | 2023-12-31 | 165853.3837 | 198175.8975 | 238197.958 | 287754.0997 | 349249.7531 | 425687.0234 | 520411.0361 | 616456.2164 | 713471.3078 | 811401.2278 | 931822.7128 | 1054213.4709 | 1168324.4078 | 1249938.6863 | 1312986.3709 | 1368816.5996 | 1402213.5807 | 1430585.7579 | 1454417.0956 | 1475804.6384 | 1495541.2596 | 1509566.1845 | 1520465.9721 | 1529966.3152 | 1539022.6541
| Response cost |  |  | 2023-12-31 | 1114904.0814 | 1331796.3334 | 1600247.6673 | 1932515.4772 | 2344668.4742 | 2856750.9048 | 3492476.8503 | 4137567.3846 | 4789461.3049 | 5447767.0032 | 6257267.5515 | 7080006.0003 | 7847085.6125 | 8395715.313 | 8819536.1557 | 9194839.6226 | 9419341.7081 | 9610065.9213 | 9770265.5813 | 9914037.4969 | 10046711.5436 | 10140990.2711 | 10214261.117 | 10278124.5792 | 10339003.3444
|  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 44379611.1592 | 52952435.1653 | 63546374.2507 | 76637610.2593 | 92849897.9806 | 112959678.565 | 138103533.4534 | 163696017.0145 | 189603794.6674 | 215807930.2855 | 248030719.8192 | 280780454.1298 | 311314645.8026 | 333153271.3684 | 350023784.7312 | 364963026.7751 | 373899504.2923 | 381491427.7237 | 387868297.9328 | 393591249.185 | 398872441.2638 | 402625278.2464 | 405541880.4039 | 408084014.4473 | 410507340.3385
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 135587.5065 | 340898.7101 | 642125.7463 | 1074701.3396 | 1686476.3317 | 2047450.8826 | 2239072.2784 | 2331399.6611 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56
Capital expenditure
| Cable replacement |  |  | 2023-12-31 | -3000038.9077 | -3000038.9077 | -3000038.9077 | -3000038.9077 | -3000038.9077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Cable replacement |  |  | 2023-12-31 | -3000038.9077 | -6000077.8154 | -9000116.7231 | -12000155.6308 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385 | -15000194.5385
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Cable replacement |  |  | 2023-12-31 | 0 | -120267.4237 | -240534.8474 | -360802.2712 | -481069.6949 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -120267.4237 | -240534.8474 | -360802.2712 | -481069.6949 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186
| Annualised capex |  |  | 2023-12-31 | 0 | -120267.4237 | -240534.8474 | -360802.2712 | -481069.6949 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 135587.5065 | 340898.7101 | 642125.7463 | 1074701.3396 | 1686476.3317 | 2047450.8826 | 2239072.2784 | 2331399.6611 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 15320.0828 | 100363.8627 | 281323.4751 | 593631.6447 | 1085139.2131 | 1446113.764 | 1637735.1598 | 1730062.5425 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | 15320.0828 | 100363.8627 | 281323.4751 | 593631.6447 | 1085139.2131 | 1446113.764 | 1637735.1598 | 1730062.5425 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414
| Total annualised capex |  |  |  | 0 | -120267.4237 | -240534.8474 | -360802.2712 | -481069.6949 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186 | -601337.1186
| Total benefits |  |  |  | 0 | 135587.5065 | 340898.7101 | 642125.7463 | 1074701.3396 | 1686476.3317 | 2047450.8826 | 2239072.2784 | 2331399.6611 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56 | 2331906.56
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | 3293.3404 | 76310.3779 | 245243.248 | 545524.6752 | 1025005.5012 | 1385980.0522 | 1577601.448 | 1669928.8307 | 1670435.7295 | 1670435.7295 | 1670435.7295 | 1670435.7295 | 1670435.7295 | 1670435.7295 | 1670435.7295 | 1670435.7295 | 1670435.7295 | 1670435.7295 | 1670435.7295 | 1670435.7295 | 1670435.7295 | 1670435.7295 | 1670435.7295 | 1670435.7295
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | 27346.8252 | 124417.3474 | 317403.7022 | 641738.6142 | 1145272.9249 | 1506247.4759 | 1697868.8717 | 1790196.2544 | 1790703.1533 | 1790703.1533 | 1790703.1533 | 1790703.1533 | 1790703.1533 | 1790703.1533 | 1790703.1533 | 1790703.1533 | 1790703.1533 | 1790703.1533 | 1790703.1533 | 1790703.1533 | 1790703.1533 | 1790703.1533 | 1790703.1533 | 1790703.1533
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | 28878.8335 | 134453.7337 | 345536.0497 | 701101.7787 | 1253786.8463 | 1650858.8523 | 1861642.3877 | 1963202.5086 | 1963760.0974 | 1963760.0974 | 1963760.0974 | 1963760.0974 | 1963760.0974 | 1963760.0974 | 1963760.0974 | 1963760.0974 | 1963760.0974 | 1963760.0974 | 1963760.0974 | 1963760.0974 | 1963760.0974 | 1963760.0974 | 1963760.0974 | 1963760.0974
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | 1761.3322 | 66273.9917 | 217110.9005 | 486161.5107 | 916491.5799 | 1241368.6758 | 1413827.932 | 1496922.5764 | 1497378.7854 | 1497378.7854 | 1497378.7854 | 1497378.7854 | 1497378.7854 | 1497378.7854 | 1497378.7854 | 1497378.7854 | 1497378.7854 | 1497378.7854 | 1497378.7854 | 1497378.7854 | 1497378.7854 | 1497378.7854 | 1497378.7854 | 1497378.7854
sens5 | Capex 10% higher & total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | -10265.4102 | 42220.5069 | 181030.6734 | 438054.5413 | 856357.8681 | 1181234.9639 | 1353694.2201 | 1436788.8645 | 1437245.0735 | 1437245.0735 | 1437245.0735 | 1437245.0735 | 1437245.0735 | 1437245.0735 | 1437245.0735 | 1437245.0735 | 1437245.0735 | 1437245.0735 | 1437245.0735 | 1437245.0735 | 1437245.0735 | 1437245.0735 | 1437245.0735 | 1437245.0735
sens | 0 | 0% | 0% | Option 3sens | 0 | 15320.0828 | 100363.8627 | 281323.4751 | 593631.6447 | 1085139.2131 | 1446113.764 | 1637735.1598 | 1730062.5425 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414
sens | 0 | 0% | 0% | Option 3sens | 0 | 15320.0828 | 100363.8627 | 281323.4751 | 593631.6447 | 1085139.2131 | 1446113.764 | 1637735.1598 | 1730062.5425 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414
sens | 0 | 0% | 0% | Option 3sens | 0 | 15320.0828 | 100363.8627 | 281323.4751 | 593631.6447 | 1085139.2131 | 1446113.764 | 1637735.1598 | 1730062.5425 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414 | 1730569.4414

## Option4
Powercor
HV cable replacement
OPTION 4 | Monitor highest delta risk cable sections and replace those with high partial discharge
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Condition assessment of top 30 delta risk cable sections |  | 1 | 2023-12-31 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Replacement of poor condition cable sections |  | 60 | 2023-12-31 | 0 | 1191610.2136 | 1191610.2136 | 1191610.2136 | 1191610.2136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 1000000 | 2191610.2136 | 2191610.2136 | 2191610.2136 | 2191610.2136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 761.7229 | 910.6816 | 1095.3823 | 1324.3832 | 1608.9294 | 2033.3256 | 2485.6765 | 2943.6465 | 3405.8346 | 3872.186 | 4445.6848 | 5028.559 | 5571.9932 | 5960.6465 | 6260.865 | 6526.7022 | 6685.6875 | 6820.7338 | 6934.1456 | 7035.9101 | 7129.8031 | 7196.4829 | 7248.2681 | 7293.377 | 7336.3594
| Energy at risk value | $/MWh | 47819.7904 | 2023-12-31 | 36425429.6824 | 43548602.3606 | 52380953.0678 | 63331727.7228 | 76938666.1294 | 97233203.8847 | 118864528.5818 | 140764558.9462 | 162866296.9388 | 185167120.599 | 212591716.2822 | 240464634.9968 | 266451549.1251 | 285036867.4065 | 299393250.8287 | 312105532.6085 | 319708174.4979 | 326166059.8537 | 331589387.9282 | 336455747.0883 | 340945688.0102 | 344134302.3225 | 346610660.6381 | 348767761.175 | 350823167.5118
| Safety consequence | (after DF) |  | 2023-12-31 | 3329625.8864 | 3981283.7269 | 4789327.4571 | 5791233.3681 | 7036227.9647 | 8819606.7363 | 10781685.508 | 12767464.7969 | 14771149.0933 | 16792350.6263 | 19277891.7467 | 21804068.4856 | 24159321.0059 | 25843771.4758 | 27144958.6749 | 28297146.5693 | 28986253.8052 | 29571618.4187 | 30063228.3489 | 30504368.0723 | 30911401.5852 | 31200505.1547 | 31425067.0766 | 31620705.6704 | 31807139.6852
| Unplanned replacements |  |  | 2023-12-31 | 1846704.2063 | 2208092.2781 | 2656205.1189 | 3211823.1158 | 3902243.3076 | 4896698.132 | 5986056.3807 | 7088623.7846 | 8201161.5054 | 9323465.5055 | 10703604.8162 | 12106307.5038 | 13414101.0021 | 14349418.8059 | 15071922.1471 | 15711690.4224 | 16094324.0736 | 16419352.1982 | 16692320.742 | 16937264.1697 | 17163268.8437 | 17323790.0194 | 17448472.4816 | 17557093.8997 | 17660603.4047
| Environmental consequence | (after DF) |  | 2023-12-31 | 162977.3237 | 194905.5547 | 234497.32 | 283590.9289 | 344600.1084 | 427704.6939 | 522854.883 | 619114.8521 | 716220.1157 | 814143.0478 | 934559.5544 | 1056944.92 | 1171050.0149 | 1252657.9634 | 1315698.788 | 1371521.5814 | 1404910.5022 | 1433273.9404 | 1457095.802 | 1478473.0679 | 1498198.5423 | 1512211.3753 | 1523098.0441 | 1532584.1525 | 1541625.044
| Response cost |  |  | 2023-12-31 | 1091499.5338 | 1305255.7962 | 1570315.4001 | 1898980.4764 | 2307406.2143 | 2874072.773 | 3513460.023 | 4160401.0073 | 4813078.14 | 5471327.2429 | 6280787.2791 | 7103481.8459 | 7870513.9175 | 8419092.1056 | 8842857.1238 | 9218100.0835 | 9442536.5767 | 9633189.6747 | 9793312.2209 | 9937000.5063 | 10069583.8437 | 10163764.1709 | 10236928.2596 | 10300675.8838 | 10361428.9425
|  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 42856236.6326 | 51238139.7165 | 61631298.3638 | 74517355.612 | 90529143.7243 | 114251286.22 | 139668585.3766 | 165400163.3871 | 191367905.7933 | 217568407.0214 | 249788559.6786 | 282535437.752 | 313066535.0656 | 334901807.7572 | 351768687.5624 | 366703991.2651 | 375636199.4556 | 383223494.0857 | 389595345.0419 | 395312852.9044 | 400588140.8252 | 404334573.0428 | 407244226.5001 | 409778820.7814 | 412193964.5882
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 1523374.5267 | 1849882.9554 | 2255974.597 | 2762380.3936 | 3395455.5958 | 394868.6767 | 482398.9594 | 534925.9058 | 567288.5352 | 571429.8241 | 574066.7005 | 576922.9378 | 580017.297 | 583370.1711 | 587003.7287 | 590942.0699 | 595211.3968 | 599840.198 | 604859.4509 | 610302.8406 | 616206.9986 | 622611.7636 | 629560.4638 | 637100.2259 | 645282.3104
Capital expenditure
| Condition assessment of top 30 delta risk cable sections |  |  | 2023-12-31 | -1000000 | -1000000 | -1000000 | -1000000 | -1000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Replacement of poor condition cable sections |  |  | 2023-12-31 | 0 | -1191610.2136 | -1191610.2136 | -1191610.2136 | -1191610.2136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Condition assessment of top 30 delta risk cable sections |  |  | 2023-12-31 | -1000000 | -1000000 | -1000000 | -1000000 | -1000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Replacement of poor condition cable sections |  |  | 2023-12-31 | 0 | -1191610.2136 | -2383220.4272 | -3574830.6407 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543 | -4766440.8543
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Condition assessment of top 30 delta risk cable sections |  |  | 2023-12-31 | 0 | -1035000 | -1035000 | -1035000 | -1035000 | -1035000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - Replacement of poor condition cable sections |  |  | 2023-12-31 | 0 | 0 | -47770.0106 | -95540.0212 | -143310.0318 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -1035000 | -1082770.0106 | -1130540.0212 | -1178310.0318 | -1226080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425
| Annualised capex |  |  | 2023-12-31 | 0 | -1035000 | -1082770.0106 | -1130540.0212 | -1178310.0318 | -1226080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 1523374.5267 | 1849882.9554 | 2255974.597 | 2762380.3936 | 3395455.5958 | 394868.6767 | 482398.9594 | 534925.9058 | 567288.5352 | 571429.8241 | 574066.7005 | 576922.9378 | 580017.297 | 583370.1711 | 587003.7287 | 590942.0699 | 595211.3968 | 599840.198 | 604859.4509 | 610302.8406 | 616206.9986 | 622611.7636 | 629560.4638 | 637100.2259 | 645282.3104
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 1523374.5267 | 814882.9554 | 1173204.5863 | 1631840.3723 | 2217145.5639 | -831211.3657 | 291318.9169 | 343845.8634 | 376208.4928 | 380349.7816 | 382986.6581 | 385842.8954 | 388937.2545 | 392290.1287 | 395923.6862 | 399862.0275 | 404131.3543 | 408760.1556 | 413779.4085 | 419222.7981 | 425126.9562 | 431531.7211 | 438480.4214 | 446020.1835 | 454202.2679
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 1523374.5267 | 814882.9554 | 1173204.5863 | 1631840.3723 | 2217145.5639 | -831211.3657 | 291318.9169 | 343845.8634 | 376208.4928 | 380349.7816 | 382986.6581 | 385842.8954 | 388937.2545 | 392290.1287 | 395923.6862 | 399862.0275 | 404131.3543 | 408760.1556 | 413779.4085 | 419222.7981 | 425126.9562 | 431531.7211 | 438480.4214 | 446020.1835 | 454202.2679
| Total annualised capex |  |  |  | 0 | -1035000 | -1082770.0106 | -1130540.0212 | -1178310.0318 | -1226080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425 | -191080.0425
| Total benefits |  |  |  | 1523374.5267 | 1849882.9554 | 2255974.597 | 2762380.3936 | 3395455.5958 | 394868.6767 | 482398.9594 | 534925.9058 | 567288.5352 | 571429.8241 | 574066.7005 | 576922.9378 | 580017.297 | 583370.1711 | 587003.7287 | 590942.0699 | 595211.3968 | 599840.198 | 604859.4509 | 610302.8406 | 616206.9986 | 622611.7636 | 629560.4638 | 637100.2259 | 645282.3104
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 1523374.5267 | 711382.9554 | 1064927.5853 | 1518786.3702 | 2099314.5607 | -953819.37 | 272210.9127 | 324737.8591 | 357100.4885 | 361241.7774 | 363878.6538 | 366734.8911 | 369829.2503 | 373182.1244 | 376815.682 | 380754.0232 | 385023.3501 | 389652.1513 | 394671.4042 | 400114.7939 | 406018.9519 | 412423.7169 | 419372.4171 | 426912.1792 | 435094.2637
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 1523374.5267 | 918382.9554 | 1281481.5874 | 1744894.3745 | 2334976.5671 | -708603.3615 | 310426.9212 | 362953.8676 | 395316.497 | 399457.7859 | 402094.6623 | 404950.8996 | 408045.2588 | 411398.1329 | 415031.6905 | 418970.0317 | 423239.3585 | 427868.1598 | 432887.4127 | 438330.8024 | 444234.9604 | 450639.7254 | 457588.4256 | 465128.1877 | 473310.2722
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 1675711.9793 | 999871.2509 | 1398802.046 | 1908078.4117 | 2556691.1235 | -791724.4981 | 339558.8129 | 397338.454 | 432937.3463 | 437492.764 | 440393.3281 | 443535.1891 | 446938.9842 | 450627.1458 | 454624.0591 | 458956.2345 | 463652.494 | 468744.1754 | 474265.3536 | 480253.0822 | 486747.656 | 493792.8975 | 501436.4677 | 509730.206 | 518730.4989
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 1371037.074 | 629894.6598 | 947607.1266 | 1355602.333 | 1877600.0044 | -870698.2334 | 243079.021 | 290353.2728 | 319479.6393 | 323206.7992 | 325579.988 | 328150.6016 | 330935.5248 | 333953.1116 | 337223.3134 | 340767.8205 | 344610.2146 | 348776.1358 | 353293.4634 | 358192.5141 | 363506.2563 | 369270.5448 | 375524.375 | 382310.1609 | 389674.0369
sens5 | Capex 10% higher & total benefits 10% lower | 10% | -10% | Option 4sens5 | 1371037.074 | 526394.6598 | 839330.1256 | 1242548.3309 | 1759769.0012 | -993306.2377 | 223971.0167 | 271245.2686 | 300371.635 | 304098.795 | 306471.9838 | 309042.5973 | 311827.5206 | 314845.1073 | 318115.3091 | 321659.8162 | 325502.2104 | 329668.1315 | 334185.4591 | 339084.5098 | 344398.2521 | 350162.5405 | 356416.3707 | 363202.1566 | 370566.0326
sens | 0 | 0% | 0% | Option 4sens | 1523374.5267 | 814882.9554 | 1173204.5863 | 1631840.3723 | 2217145.5639 | -831211.3657 | 291318.9169 | 343845.8634 | 376208.4928 | 380349.7816 | 382986.6581 | 385842.8954 | 388937.2545 | 392290.1287 | 395923.6862 | 399862.0275 | 404131.3543 | 408760.1556 | 413779.4085 | 419222.7981 | 425126.9562 | 431531.7211 | 438480.4214 | 446020.1835 | 454202.2679
sens | 0 | 0% | 0% | Option 4sens | 1523374.5267 | 814882.9554 | 1173204.5863 | 1631840.3723 | 2217145.5639 | -831211.3657 | 291318.9169 | 343845.8634 | 376208.4928 | 380349.7816 | 382986.6581 | 385842.8954 | 388937.2545 | 392290.1287 | 395923.6862 | 399862.0275 | 404131.3543 | 408760.1556 | 413779.4085 | 419222.7981 | 425126.9562 | 431531.7211 | 438480.4214 | 446020.1835 | 454202.2679
sens | 0 | 0% | 0% | Option 4sens | 1523374.5267 | 814882.9554 | 1173204.5863 | 1631840.3723 | 2217145.5639 | -831211.3657 | 291318.9169 | 343845.8634 | 376208.4928 | 380349.7816 | 382986.6581 | 385842.8954 | 388937.2545 | 392290.1287 | 395923.6862 | 399862.0275 | 404131.3543 | 408760.1556 | 413779.4085 | 419222.7981 | 425126.9562 | 431531.7211 | 438480.4214 | 446020.1835 | 454202.2679

## Option5
Powercor
HV cable replacement
OPTION 5 | Replace highest 5 delta risk cable sections and monitor further 10
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Cable replacement (top 5) |  | 60 | 2023-12-31 | 1457739.1194 | 1457739.1194 | 1457739.1194 | 1457739.1194 | 1457739.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Condition assessment of next 10 delta risk cable sections |  | 1 | 2023-12-31 | 333333.3333 | 333333.3333 | 333333.3333 | 333333.3333 | 333333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Replacement of poor condition cable sections |  | 60 | 2023-12-31 | 0 | 0 | 0 | 0 | 772268.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 1791072.4528 | 1791072.4528 | 1791072.4528 | 1791072.4528 | 2563340.6195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 779.4659 | 930.7189 | 1118.1324 | 1350.0837 | 1637.7901 | 2020.7542 | 2470.2847 | 2926.7132 | 3389.0322 | 3855.4147 | 4428.9139 | 5011.7885 | 5555.2232 | 5943.877 | 6244.096 | 6509.9338 | 6668.9197 | 6803.9666 | 6917.3791 | 7019.1445 | 7113.0383 | 7179.719 | 7231.5052 | 7276.6153 | 7319.5988
| Energy at risk value | $/MWh | 47819.7904 | 2023-12-31 | 37273895.1928 | 44506783.3603 | 53468855.6227 | 64560721.552 | 78318776.9134 | 96632040.1409 | 118128495.8273 | 139954809.519 | 162062811.5614 | 184365121.5918 | 211789735.5547 | 239662674.0697 | 265649609.6491 | 284234951.1738 | 298591359.785 | 311303668.8667 | 318906340.3525 | 325364257.7967 | 330787620.6663 | 335654017.5617 | 340143999.4133 | 343332658.1256 | 345809064.6119 | 347966217.4169 | 350021680.4746
| Safety consequence | (after DF) |  | 2023-12-31 | 3423495.0151 | 4042673.4729 | 4859452.1609 | 5870987.1282 | 7126470.9075 | 8782482.4507 | 10736263.5468 | 12717587.4962 | 14721730.2087 | 16743014.0246 | 19228533.9517 | 21754687.7342 | 24109915.3843 | 25794338.9061 | 27095496.9013 | 28247653.1421 | 28936726.0642 | 29522053.4747 | 30013623.0637 | 30454719.037 | 30861705.0965 | 31150757.189 | 31375263.2623 | 31570841.2568 | 31757209.5098
| Unplanned replacements |  |  | 2023-12-31 | 1900959.3721 | 2233343.727 | 2678274.855 | 3227812.4365 | 3908060.1865 | 4822324.3976 | 5894953.3916 | 6988002.5737 | 8099840.9093 | 9222173.0298 | 10602279.4415 | 12004946.4933 | 13312701.3849 | 14247977.3565 | 14970435.3636 | 15610154.5023 | 15992734.8873 | 16317705.2607 | 16590611.1818 | 16835486.6951 | 17061417.706 | 17221858.9726 | 17346454.7395 | 17454982.0878 | 17558389.5091
| Environmental consequence | (after DF) |  | 2023-12-31 | 165853.3837 | 197235.2337 | 237300.9153 | 286972.6884 | 348688.7039 | 427636.3112 | 522772.3584 | 619033.8828 | 716175.1463 | 814101.8858 | 934519.1097 | 1056905.2521 | 1171011.1887 | 1252620.0491 | 1315661.862 | 1371485.7266 | 1404875.8086 | 1433240.5058 | 1457063.7326 | 1478442.4791 | 1498169.5594 | 1512184.1345 | 1523072.6933 | 1532560.8524 | 1541603.9694
| Response cost |  |  | 2023-12-31 | 1114904.0814 | 1322231.6365 | 1589814.4447 | 1921312.5139 | 2332896.3194 | 2865377.9606 | 3502816.517 | 4148706.0682 | 4801523.6693 | 5459799.257 | 6269260.3501 | 7091956.0616 | 7858989.3734 | 8407568.9053 | 8831335.3798 | 9206579.918 | 9431018.1222 | 9621673.0754 | 9781797.6333 | 9925488.1003 | 10058073.8041 | 10152256.6982 | 10225423.5719 | 10289174.2179 | 10349930.556
|  |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 43879107.0452 | 52302267.4304 | 62833697.9986 | 75867806.319 | 92034893.0307 | 113529861.261 | 138785301.6412 | 164428139.5399 | 190402081.4951 | 216604209.789 | 248824328.4076 | 281571169.6108 | 312102226.9804 | 333937456.3909 | 350804289.2917 | 365739542.1557 | 374671695.2348 | 382258930.1133 | 388630716.2776 | 394348153.8733 | 399623365.5792 | 403369715.1199 | 406279278.8788 | 408813775.8319 | 411228814.0189
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 500504.114 | 785755.2414 | 1053574.9622 | 1411929.6865 | 1889706.2894 | 1116293.6357 | 1365682.6948 | 1506949.7531 | 1533112.8334 | 1535627.0565 | 1538297.9715 | 1541191.079 | 1544325.3823 | 1547721.5375 | 1551401.9994 | 1555391.1794 | 1559715.6175 | 1564404.1704 | 1569488.2152 | 1575001.8717 | 1580982.2445 | 1587469.6864 | 1594508.0851 | 1602145.1754 | 1610432.8797
Capital expenditure
| Cable replacement (top 5) |  |  | 2023-12-31 | -1457739.1194 | -1457739.1194 | -1457739.1194 | -1457739.1194 | -1457739.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Condition assessment of next 10 delta risk cable sections |  |  | 2023-12-31 | -333333.3333 | -333333.3333 | -333333.3333 | -333333.3333 | -333333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Replacement of poor condition cable sections |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -772268.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Cable replacement (top 5) |  |  | 2023-12-31 | -1457739.1194 | -2915478.2389 | -4373217.3583 | -5830956.4778 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972 | -7288695.5972
| Condition assessment of next 10 delta risk cable sections |  |  | 2023-12-31 | -333333.3333 | -333333.3333 | -333333.3333 | -333333.3333 | -333333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Replacement of poor condition cable sections |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667 | -772268.1667
Annualised capex
| Annualised capex - Cable replacement (top 5) |  |  | 2023-12-31 | 0 | -58438.7515 | -116877.5031 | -175316.2546 | -233755.0062 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577 | -292193.7577
| Annualised capex - Condition assessment of next 10 delta risk cable sections |  |  | 2023-12-31 | 0 | -345000 | -345000 | -345000 | -345000 | -345000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - Replacement of poor condition cable sections |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661 | -30959.1661
| Total annualised capex |  |  | 2023-12-31 | 0 | -403438.7515 | -461877.5031 | -520316.2546 | -578755.0062 | -668152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238
| Annualised capex |  |  | 2023-12-31 | 0 | -403438.7515 | -461877.5031 | -520316.2546 | -578755.0062 | -668152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 500504.114 | 785755.2414 | 1053574.9622 | 1411929.6865 | 1889706.2894 | 1116293.6357 | 1365682.6948 | 1506949.7531 | 1533112.8334 | 1535627.0565 | 1538297.9715 | 1541191.079 | 1544325.3823 | 1547721.5375 | 1551401.9994 | 1555391.1794 | 1559715.6175 | 1564404.1704 | 1569488.2152 | 1575001.8717 | 1580982.2445 | 1587469.6864 | 1594508.0851 | 1602145.1754 | 1610432.8797
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 500504.114 | 382316.4899 | 591697.4591 | 891613.4319 | 1310951.2833 | 448140.7119 | 1042529.771 | 1183796.8293 | 1209959.9096 | 1212474.1327 | 1215145.0477 | 1218038.1552 | 1221172.4584 | 1224568.6137 | 1228249.0756 | 1232238.2556 | 1236562.6937 | 1241251.2466 | 1246335.2914 | 1251848.9479 | 1257829.3207 | 1264316.7626 | 1271355.1613 | 1278992.2516 | 1287279.9559
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 500504.114 | 382316.4899 | 591697.4591 | 891613.4319 | 1310951.2833 | 448140.7119 | 1042529.771 | 1183796.8293 | 1209959.9096 | 1212474.1327 | 1215145.0477 | 1218038.1552 | 1221172.4584 | 1224568.6137 | 1228249.0756 | 1232238.2556 | 1236562.6937 | 1241251.2466 | 1246335.2914 | 1251848.9479 | 1257829.3207 | 1264316.7626 | 1271355.1613 | 1278992.2516 | 1287279.9559
| Total annualised capex |  |  |  | 0 | -403438.7515 | -461877.5031 | -520316.2546 | -578755.0062 | -668152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238 | -323152.9238
| Total benefits |  |  |  | 500504.114 | 785755.2414 | 1053574.9622 | 1411929.6865 | 1889706.2894 | 1116293.6357 | 1365682.6948 | 1506949.7531 | 1533112.8334 | 1535627.0565 | 1538297.9715 | 1541191.079 | 1544325.3823 | 1547721.5375 | 1551401.9994 | 1555391.1794 | 1559715.6175 | 1564404.1704 | 1569488.2152 | 1575001.8717 | 1580982.2445 | 1587469.6864 | 1594508.0851 | 1602145.1754 | 1610432.8797
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 500504.114 | 341972.6147 | 545509.7088 | 839581.8064 | 1253075.7826 | 381325.4195 | 1010214.4786 | 1151481.5369 | 1177644.6172 | 1180158.8404 | 1182829.7553 | 1185722.8628 | 1188857.1661 | 1192253.3213 | 1195933.7833 | 1199922.9632 | 1204247.4013 | 1208935.9542 | 1214019.999 | 1219533.6555 | 1225514.0284 | 1232001.4703 | 1239039.8689 | 1246676.9593 | 1254964.6635
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 500504.114 | 422660.3651 | 637885.2094 | 943645.0574 | 1368826.7839 | 514956.0043 | 1074845.0634 | 1216112.1217 | 1242275.202 | 1244789.4251 | 1247460.3401 | 1250353.4476 | 1253487.7508 | 1256883.9061 | 1260564.368 | 1264553.548 | 1268877.9861 | 1273566.539 | 1278650.5838 | 1284164.2403 | 1290144.6131 | 1296632.055 | 1303670.4537 | 1311307.544 | 1319595.2482
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 550554.5254 | 460892.014 | 697054.9553 | 1032806.4006 | 1499921.9122 | 559770.0755 | 1179098.0405 | 1334491.8046 | 1363271.1929 | 1366036.8384 | 1368974.8449 | 1372157.2631 | 1375604.9967 | 1379340.7674 | 1383389.2756 | 1387777.3735 | 1392534.2555 | 1397691.6637 | 1403284.1129 | 1409349.1351 | 1415927.5452 | 1423063.7313 | 1430805.9698 | 1439206.7692 | 1448323.2438
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 450453.7026 | 303740.9658 | 486339.9629 | 750420.4633 | 1121980.6543 | 336511.3483 | 905961.5015 | 1033101.854 | 1056648.6262 | 1058911.4271 | 1061315.2506 | 1063919.0473 | 1066739.9202 | 1069796.4599 | 1073108.8757 | 1076699.1376 | 1080591.132 | 1084810.8296 | 1089386.4699 | 1094348.7607 | 1099731.0963 | 1105569.794 | 1111904.3528 | 1118777.7341 | 1126236.6679
sens5 | Capex 10% higher & total benefits 10% lower | 10% | -10% | Option 5sens5 | 450453.7026 | 263397.0906 | 440152.2126 | 698388.8378 | 1064105.1537 | 269696.0559 | 873646.2091 | 1000786.5616 | 1024333.3339 | 1026596.1347 | 1028999.9582 | 1031603.7549 | 1034424.6278 | 1037481.1676 | 1040793.5833 | 1044383.8453 | 1048275.8396 | 1052495.5372 | 1057071.1775 | 1062033.4683 | 1067415.8039 | 1073254.5016 | 1079589.0604 | 1086462.4417 | 1093921.3755
sens | 0 | 0% | 0% | Option 5sens | 500504.114 | 382316.4899 | 591697.4591 | 891613.4319 | 1310951.2833 | 448140.7119 | 1042529.771 | 1183796.8293 | 1209959.9096 | 1212474.1327 | 1215145.0477 | 1218038.1552 | 1221172.4584 | 1224568.6137 | 1228249.0756 | 1232238.2556 | 1236562.6937 | 1241251.2466 | 1246335.2914 | 1251848.9479 | 1257829.3207 | 1264316.7626 | 1271355.1613 | 1278992.2516 | 1287279.9559
sens | 0 | 0% | 0% | Option 5sens | 500504.114 | 382316.4899 | 591697.4591 | 891613.4319 | 1310951.2833 | 448140.7119 | 1042529.771 | 1183796.8293 | 1209959.9096 | 1212474.1327 | 1215145.0477 | 1218038.1552 | 1221172.4584 | 1224568.6137 | 1228249.0756 | 1232238.2556 | 1236562.6937 | 1241251.2466 | 1246335.2914 | 1251848.9479 | 1257829.3207 | 1264316.7626 | 1271355.1613 | 1278992.2516 | 1287279.9559
sens | 0 | 0% | 0% | Option 5sens | 500504.114 | 382316.4899 | 591697.4591 | 891613.4319 | 1310951.2833 | 448140.7119 | 1042529.771 | 1183796.8293 | 1209959.9096 | 1212474.1327 | 1215145.0477 | 1218038.1552 | 1221172.4584 | 1224568.6137 | 1228249.0756 | 1232238.2556 | 1236562.6937 | 1241251.2466 | 1246335.2914 | 1251848.9479 | 1257829.3207 | 1264316.7626 | 1271355.1613 | 1278992.2516 | 1287279.9559

## Consol
Powercor
HV cable replacement
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 3712697794.2857 | 2026-06-30 |  | 42039606.6993 | 50288849.6604 | 60518687.7084 | 73205006.1423 | 88972235.4855 | 108601205.2733 | 132761241.1671 | 157185827.214 | 181815024.2999 | 206637974.2162 | 237161752.2162 | 268184690.7677 | 297108905.6329 | 317796045.6429 | 333777027.1806 | 347928567.5729 | 356393851.2987 | 363585475.2631 | 369626112.1359 | 375047309.2467 | 380050039.8273 | 383605000.9149 | 386367819.3443 | 388775914.2458 | 391071465.3944
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 3315591527.4499 | 2026-06-30 |  | 49390630.5021 | 59082331.8048 | 71100954.0231 | 86005595.5123 | 104529874.393 | 127591155.6476 | 155975802.8753 | 184671259.3584 | 213607105.0606 | 242770583.1126 | 278631733.0874 | 315079326.5686 | 349061214.6293 | 373365697.2018 | 392141104.8748 | 408767176.2733 | 418712695.1167 | 427161842.7141 | 434258742.2144 | 440627887.0377 | 446505392.4904 | 450681972.2283 | 453927895.654 | 456757068.7798 | 459454018.8105
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 3696588704.7184 | 2026-06-30 |  | 42039606.6993 | 50210964.9887 | 60325371.0881 | 72845369.9274 | 88377582.8411 | 107679097.5491 | 131630808.4514 | 155933568.7147 | 180546898.2368 | 205369848.1532 | 235893626.1532 | 266916564.7046 | 295840779.5699 | 316527919.5799 | 332508901.1176 | 346660441.5098 | 355125725.2356 | 362317349.2001 | 368357986.0728 | 373779183.1837 | 378781913.7642 | 382336874.8518 | 385099693.2813 | 387507788.1828 | 389803339.3313
Option 2 | Capital expenditure | Option 2Capital expenditure | -7452017.2835 | 2026-06-30 |  | -1622336.3012 | -1622336.3012 | -1622336.3012 | -1622336.3012 | -1622336.3012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 3300039298.3752 | 2026-06-30 |  | 49390630.5021 | 58990440.3844 | 70872871.4179 | 85581282.4622 | 103828279.6512 | 126503216.4334 | 154642073.5851 | 183193795.1837 | 212110919.7057 | 241274397.7578 | 277135547.7326 | 313583141.2137 | 347565029.2744 | 371869511.8469 | 390644919.5199 | 407270990.9184 | 417216509.7618 | 425665657.3592 | 432762556.8595 | 439131701.6829 | 0 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -3785093.1612 | 2026-06-30 |  | 0 | -65037.2256 | -130074.4513 | -195111.6769 | -260148.9025 | -325186.1282 | -325186.1282 | -325186.1282 | -325186.1282 | -325186.1282 | -325186.1282 | -325186.1282 | -325186.1282 | -325186.1282 | -325186.1282 | -325186.1282 | -325186.1282 | -325186.1282 | -325186.1282 | -325186.1282 | 0 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 15552229.0747 | 2026-06-30 |  | 0 | 91891.4204 | 228082.6052 | 424313.0501 | 701594.7418 | 1087939.2141 | 1333729.2901 | 1477464.1747 | 1496185.3549 | 1496185.3549 | 1496185.3549 | 1496185.3549 | 1496185.3549 | 1496185.3549 | 1496185.3549 | 1496185.3549 | 1496185.3549 | 1496185.3549 | 1496185.3549 | 1496185.3549 | 0 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | 26854.1947 | 98008.1539 | 229201.3732 | 441445.8393 | 762753.086 | 1008543.162 | 1152278.0465 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 11767135.9134 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -3785093.1612 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 15552229.0747 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 3684159752.6033 | 2026-06-30 |  | 42039606.6993 | 50157623.4561 | 60188754.3324 | 72583534.9868 | 87932102.9457 | 106968976.071 | 130779648.5067 | 155018776.8438 | 179558616.3459 | 204381075.6683 | 234904853.6682 | 265927792.2197 | 294852007.0849 | 315539147.0949 | 331520128.6326 | 345671669.0249 | 354136952.7507 | 361328576.7152 | 367369213.5879 | 372790410.6988 | 377793141.2793 | 381348102.3669 | 384110920.7963 | 386519015.6978 | 388814566.8464
Option 3 | Capital expenditure | Option 3Capital expenditure | -15336311.891 | 2026-06-30 |  | -3338781.2401 | -3338781.2401 | -3338781.2401 | -3338781.2401 | -3338781.2401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 3288766609.4294 | 2026-06-30 |  | 49390630.5021 | 58931434.7541 | 70721563.5375 | 85290965.6487 | 103333825.681 | 125714254.8102 | 153697168.8951 | 182179367.5035 | 211012460.8939 | 240175374.8118 | 276036524.7866 | 312484118.2677 | 346466006.3284 | 370770488.9009 | 389545896.5739 | 406171967.9724 | 416117486.8158 | 424566634.4132 | 431663533.9135 | 438032678.7369 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -7789752.3649 | 2026-06-30 |  | 0 | -133847.1368 | -267694.2736 | -401541.4104 | -535388.5472 | -669235.684 | -669235.684 | -669235.684 | -669235.684 | -669235.684 | -669235.684 | -669235.684 | -669235.684 | -669235.684 | -669235.684 | -669235.684 | -669235.684 | -669235.684 | -669235.684 | -669235.684 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 26824918.0205 | 2026-06-30 |  | 0 | 150897.0507 | 379390.4856 | 714629.8636 | 1196048.7119 | 1876900.8374 | 2278633.9802 | 2491891.8549 | 2594644.1667 | 2595208.3009 | 2595208.3009 | 2595208.3009 | 2595208.3009 | 2595208.3009 | 2595208.3009 | 2595208.3009 | 2595208.3009 | 2595208.3009 | 2595208.3009 | 2595208.3009 | 0 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | 17049.9139 | 111696.212 | 313088.4532 | 660660.1647 | 1207665.1534 | 1609398.2961 | 1822656.1709 | 1925408.4827 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | 19035165.6556 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -7789752.3649 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 26824918.0205 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 3695323066.0382 | 2026-06-30 |  | 40538321.3447 | 48465790.3009 | 58295425.1006 | 70482680.7021 | 85626014.5338 | 108212062.2549 | 132285837.0691 | 156658657.8185 | 181255961.5383 | 206074830.2151 | 236596009.5738 | 267616133.3039 | 296537298.6786 | 317221134.4317 | 333198535.099 | 347346194.2566 | 355807270.5615 | 362994332.843 | 369030023.2428 | 374445855.8941 | 379442767.9278 | 382991417.1205 | 385747387.607 | 388148052.0741 | 390435539.7798
Option 4 | Capital expenditure | Option 4Capital expenditure | -9900051.6847 | 2026-06-30 |  | -1112912.6464 | -2439070.7227 | -2439070.7227 | -2439070.7227 | -2439070.7227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 3297588128.9728 | 2026-06-30 |  | 47695247.7262 | 57023573.6693 | 68590251.3642 | 82931307.4381 | 100751028.9201 | 127151701.3036 | 155438934.9728 | 184075933.5529 | 212975762.4756 | 242134631.6349 | 277992846.9966 | 314437261.7351 | 348415706.0443 | 372716457.1608 | 391487821.0016 | 408109509.3704 | 418050276.826 | 426494272.9719 | 433585586.4822 | 439948673.2883 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | -7489675.8084 | 2026-06-30 |  | 0 | -1151864.589 | -1205028.438 | -1258192.2869 | -1311356.1358 | -1364519.9848 | -212655.3957 | -212655.3957 | -212655.3957 | -212655.3957 | -212655.3957 | -212655.3957 | -212655.3957 | -212655.3957 | -212655.3957 | -212655.3957 | -212655.3957 | -212655.3957 | -212655.3957 | -212655.3957 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 18003398.4771 | 2026-06-30 |  | 1695382.7759 | 2058758.1354 | 2510702.6589 | 3074288.0742 | 3778845.4729 | 439454.344 | 536867.9025 | 595325.8055 | 631342.585 | 635951.4778 | 638886.0909 | 642064.8335 | 645508.585 | 649240.041 | 653283.8732 | 657666.9029 | 662418.2907 | 667569.7422 | 673155.7323 | 679213.7494 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 1695382.7759 | 906893.5464 | 1305674.221 | 1816095.7873 | 2467489.337 | -925065.6408 | 324212.5068 | 382670.4098 | 418687.1893 | 423296.082 | 426230.6952 | 429409.4378 | 432853.1892 | 436584.6453 | 440628.4774 | 445011.5072 | 449762.895 | 454914.3465 | 460500.3365 | 466558.3537 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 10513722.6687 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | -7489675.8084 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 18003398.4771 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 3690274815.0005 | 2026-06-30 |  | 41482589.3413 | 49532162.053 | 59506165.6119 | 71850443.477 | 87161957.2788 | 107543019.5219 | 131466696.9084 | 155757477.4405 | 180361752.5005 | 205182275.3776 | 235703475.08 | 266723620.8461 | 295644810.0942 | 316328671.7149 | 332306100.4154 | 346453789.9576 | 354914899.2007 | 362101997.1939 | 368137726.3175 | 373553600.965 | 378550558.5498 | 382099257.1558 | 384855281.2521 | 387256003.8891 | 389543554.7202
Option 5 | Capital expenditure | Option 5Capital expenditure | -9892232.9298 | 2026-06-30 |  | -1993307.1833 | -1993307.1833 | -1993307.1833 | -1993307.1833 | -2852774.1925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 3293527124.2489 | 2026-06-30 |  | 48833613.1441 | 58207854.8596 | 69928417.1238 | 84434241.1084 | 102426796.3654 | 126348818.3433 | 154455917.3332 | 182994155.9207 | 211900884.3999 | 241061564.3412 | 276919741.821 | 313364115.5262 | 347342515.3812 | 371643218.3296 | 390414529.9699 | 407036161.7596 | 416976867.8811 | 425420797.5287 | 432512038.9313 | 438875047.5366 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | -5829023.2901 | 2026-06-30 |  | 0 | -448992.0886 | -514029.3143 | -579066.5399 | -644103.7655 | -743595.8386 | -359640.9756 | -359640.9756 | -359640.9756 | -359640.9756 | -359640.9756 | -359640.9756 | -359640.9756 | -359640.9756 | -359640.9756 | -359640.9756 | -359640.9756 | -359640.9756 | -359640.9756 | -359640.9756 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 22064403.201 | 2026-06-30 |  | 557017.358 | 874476.9452 | 1172536.8994 | 1571354.404 | 2103078.0275 | 1242337.3043 | 1519885.542 | 1677103.4377 | 1706220.6607 | 1709018.7714 | 1711991.2665 | 1715211.0424 | 1718699.2481 | 1722478.8722 | 1726574.9049 | 1731014.5137 | 1735827.2355 | 1741045.1854 | 1746703.2831 | 1752839.5011 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 557017.358 | 425484.8565 | 658507.5851 | 992287.8641 | 1458974.262 | 498741.4656 | 1160244.5664 | 1317462.4621 | 1346579.685 | 1349377.7958 | 1352350.2908 | 1355570.0668 | 1359058.2725 | 1362837.8966 | 1366933.9292 | 1371373.538 | 1376186.2599 | 1381404.2097 | 1387062.3075 | 1393198.5255 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 16235379.9109 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | -5829023.2901 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 22064403.201 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 3 | Annualised capex | -1 |  |  | Option 3 annualised capex | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0.66924 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | 1 |  |  | Option 3 risk mitigated | 0 | 0.1509 | 0.37939 | 0.71463 | 1.196 | 1.8769 | 2.2786 | 2.4919 | 2.5946 | 2.5952 | 2.5952 | 2.5952 | 2.5952 | 2.5952 | 2.5952 | 2.5952 | 2.5952 | 2.5952 | 2.5952 | 2.5952 | 0 | 0 | 0 | 0 | 0
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 7348.3085 |  |  | Energy at risk energy at risk (weighted) | 789.9323 | 944.9372 | 1137.1579 | 1375.5362 | 1671.8055 | 2040.6377 | 2494.6094 | 2953.5521 | 3416.3395 | 3882.7675 | 4456.3152 | 5039.2423 | 5582.7339 | 5971.4492 | 6271.735 | 6537.6451 | 6696.7095 | 6831.8415 | 6945.3462 | 7047.2115 | 7141.2138 | 7208.0122 | 7259.9261 | 7305.1747 | 7348.3085
Option 1 (base case) | Energy at risk value | 351.3946 |  |  | Option 1 (base case) risk cost | 37.7744 | 45.1867 | 54.3787 | 65.7779 | 79.9454 | 97.5829 | 119.2917 | 141.2382 | 163.3686 | 185.6731 | 213.1001 | 240.9755 | 266.9652 | 285.5534 | 299.9131 | 312.6288 | 320.2352 | 326.6972 | 332.125 | 336.9962 | 341.4913 | 344.6856 | 347.1681 | 349.3319 | 351.3946

## Sensitivity_calcs
Powercor
HV cable replacement
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
[7 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 1170999.2267 | 1170999.2267 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 11767135.9134 |  | 0 | 0 | 26854.1947 | 98008.1539 | 229201.3732 | 441445.8393 | 762753.086 | 1008543.162 | 1152278.0465 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 0 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 11388626.5973 |  | 0 | 0 | 20350.4722 | 85000.7088 | 209690.2056 | 415430.949 | 730234.4732 | 976024.5492 | 1119759.4337 | 1138480.6139 | 1138480.6139 | 1138480.6139 | 1138480.6139 | 1138480.6139 | 1138480.6139 | 1138480.6139 | 1138480.6139 | 1138480.6139 | 1138480.6139 | 1138480.6139 | 1138480.6139 | 0 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 12145645.2296 |  | 0 | 0 | 33357.9173 | 111015.5991 | 248712.5409 | 467460.7295 | 795271.6988 | 1041061.7748 | 1184796.6593 | 1203517.8395 | 1203517.8395 | 1203517.8395 | 1203517.8395 | 1203517.8395 | 1203517.8395 | 1203517.8395 | 1203517.8395 | 1203517.8395 | 1203517.8395 | 1203517.8395 | 1203517.8395 | 0 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 13322358.8209 |  | 0 | 0 | 36043.3368 | 120816.4145 | 271632.6783 | 511605.3135 | 871547.0074 | 1141916.091 | 1300024.464 | 1320617.7622 | 1320617.7622 | 1320617.7622 | 1320617.7622 | 1320617.7622 | 1320617.7622 | 1320617.7622 | 1320617.7622 | 1320617.7622 | 1320617.7622 | 1320617.7622 | 1320617.7622 | 0 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 10211913.006 |  | 0 | 0 | 17665.0527 | 75199.8934 | 186770.0682 | 371286.3651 | 653959.1646 | 875170.233 | 1004531.629 | 1021380.6912 | 1021380.6912 | 1021380.6912 | 1021380.6912 | 1021380.6912 | 1021380.6912 | 1021380.6912 | 1021380.6912 | 1021380.6912 | 1021380.6912 | 1021380.6912 | 1021380.6912 | 0 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & total benefits 10% lower | Option 2sens5 |  | 9833403.6898 |  | 0 | 0 | 11161.3301 | 62192.4483 | 167258.9005 | 345271.4748 | 621440.5517 | 842651.6201 | 972013.0162 | 988862.0784 | 988862.0784 | 988862.0784 | 988862.0784 | 988862.0784 | 988862.0784 | 988862.0784 | 988862.0784 | 988862.0784 | 988862.0784 | 988862.0784 | 988862.0784 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 11767135.9134 |  | 0 | 0 | 26854.1947 | 98008.1539 | 229201.3732 | 441445.8393 | 762753.086 | 1008543.162 | 1152278.0465 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 11767135.9134 |  | 0 | 0 | 26854.1947 | 98008.1539 | 229201.3732 | 441445.8393 | 762753.086 | 1008543.162 | 1152278.0465 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 11767135.9134 |  | 0 | 0 | 26854.1947 | 98008.1539 | 229201.3732 | 441445.8393 | 762753.086 | 1008543.162 | 1152278.0465 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 1170999.2267 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 17049.9139 | 111696.212 | 313088.4532 | 660660.1647 | 1207665.1534 | 1609398.2961 | 1822656.1709 | 1925408.4827 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 19035165.6556 |  | 0 | 0 | 17049.9139 | 111696.212 | 313088.4532 | 660660.1647 | 1207665.1534 | 1609398.2961 | 1822656.1709 | 1925408.4827 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 0 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 18256190.4191 |  | 0 | 0 | 3665.2002 | 84926.7847 | 272934.3121 | 607121.31 | 1140741.585 | 1542474.7277 | 1755732.6025 | 1858484.9143 | 1859049.0484 | 1859049.0484 | 1859049.0484 | 1859049.0484 | 1859049.0484 | 1859049.0484 | 1859049.0484 | 1859049.0484 | 1859049.0484 | 1859049.0484 | 1859049.0484 | 0 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 19814140.8921 |  | 0 | 0 | 30434.6276 | 138465.6394 | 353242.5942 | 714199.0194 | 1274588.7218 | 1676321.8645 | 1889579.7393 | 1992332.0511 | 1992896.1852 | 1992896.1852 | 1992896.1852 | 1992896.1852 | 1992896.1852 | 1992896.1852 | 1992896.1852 | 1992896.1852 | 1992896.1852 | 1992896.1852 | 1992896.1852 | 0 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 21717657.4577 |  | 0 | 0 | 32139.619 | 149635.2606 | 384551.4395 | 780265.0359 | 1395355.2371 | 1837261.6941 | 2071845.3564 | 2184872.8993 | 2185493.4469 | 2185493.4469 | 2185493.4469 | 2185493.4469 | 2185493.4469 | 2185493.4469 | 2185493.4469 | 2185493.4469 | 2185493.4469 | 2185493.4469 | 2185493.4469 | 0 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | 16352673.8536 |  | 0 | 0 | 1960.2088 | 73757.1634 | 241625.4668 | 541055.2935 | 1019975.0696 | 1381534.8981 | 1573466.9854 | 1665944.066 | 1666451.7867 | 1666451.7867 | 1666451.7867 | 1666451.7867 | 1666451.7867 | 1666451.7867 | 1666451.7867 | 1666451.7867 | 1666451.7867 | 1666451.7867 | 1666451.7867 | 0 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & total benefits 10% lower | Option 3sens5 |  | 15573698.6171 |  | 0 | 0 | -11424.5049 | 46987.7361 | 201471.3258 | 487516.4388 | 953051.5012 | 1314611.3297 | 1506543.417 | 1599020.4976 | 1599528.2183 | 1599528.2183 | 1599528.2183 | 1599528.2183 | 1599528.2183 | 1599528.2183 | 1599528.2183 | 1599528.2183 | 1599528.2183 | 1599528.2183 | 1599528.2183 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 19035165.6556 |  | 0 | 0 | 17049.9139 | 111696.212 | 313088.4532 | 660660.1647 | 1207665.1534 | 1609398.2961 | 1822656.1709 | 1925408.4827 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 19035165.6556 |  | 0 | 0 | 17049.9139 | 111696.212 | 313088.4532 | 660660.1647 | 1207665.1534 | 1609398.2961 | 1822656.1709 | 1925408.4827 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 19035165.6556 |  | 0 | 0 | 17049.9139 | 111696.212 | 313088.4532 | 660660.1647 | 1207665.1534 | 1609398.2961 | 1822656.1709 | 1925408.4827 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 1925972.6168 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 10513722.6687 |  | 0 | 1695382.7759 | 906893.5464 | 1305674.221 | 1816095.7873 | 2467489.337 | -925065.6408 | 324212.5068 | 382670.4098 | 418687.1893 | 423296.082 | 426230.6952 | 429409.4378 | 432853.1892 | 436584.6453 | 440628.4774 | 445011.5072 | 449762.895 | 454914.3465 | 460500.3365 | 466558.3537 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 9764755.0879 |  | 0 | 1695382.7759 | 791707.0875 | 1185171.3772 | 1690276.5586 | 2336353.7235 | -1061517.6393 | 302946.9672 | 361404.8702 | 397421.6497 | 402030.5425 | 404965.1556 | 408143.8982 | 411587.6497 | 415319.1057 | 419362.9379 | 423745.9676 | 428497.3554 | 433648.8069 | 439234.797 | 445292.8141 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 11262690.2495 |  | 0 | 1695382.7759 | 1022080.0053 | 1426177.0648 | 1941915.016 | 2598624.9506 | -788613.6423 | 345478.0464 | 403935.9494 | 439952.7289 | 444561.6216 | 447496.2347 | 450674.9773 | 454118.7288 | 457850.1848 | 461894.017 | 466277.0468 | 471028.4346 | 476179.886 | 481765.8761 | 487823.8933 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 12314062.5164 |  | 0 | 1864921.0535 | 1112769.3599 | 1556744.4869 | 2123524.5947 | 2845373.8843 | -881120.2064 | 377899.297 | 442202.9903 | 481821.4478 | 486891.2298 | 490119.3043 | 493615.9211 | 497404.0477 | 501508.6494 | 505956.8648 | 510778.1975 | 516004.7241 | 521671.3207 | 527815.9098 | 534479.7286 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 8713382.821 |  | 0 | 1525844.4983 | 701017.7328 | 1054603.9551 | 1508666.9799 | 2089604.7898 | -969011.0752 | 270525.7165 | 323137.8292 | 355552.9308 | 359700.9343 | 362342.0861 | 365202.9544 | 368302.3307 | 371660.6412 | 375300.0901 | 379244.8169 | 383521.0659 | 388157.3723 | 393184.7633 | 398636.9787 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & total benefits 10% lower | Option 4sens5 |  | 7964415.2401 |  | 0 | 1525844.4983 | 585831.2739 | 934101.1113 | 1382847.7512 | 1958469.1762 | -1105463.0737 | 249260.177 | 301872.2897 | 334287.3912 | 338435.3947 | 341076.5465 | 343937.4148 | 347036.7912 | 350395.1016 | 354034.5505 | 357979.2773 | 362255.5264 | 366891.8327 | 371919.2237 | 377371.4392 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 10513722.6687 |  | 0 | 1695382.7759 | 906893.5464 | 1305674.221 | 1816095.7873 | 2467489.337 | -925065.6408 | 324212.5068 | 382670.4098 | 418687.1893 | 423296.082 | 426230.6952 | 429409.4378 | 432853.1892 | 436584.6453 | 440628.4774 | 445011.5072 | 449762.895 | 454914.3465 | 460500.3365 | 466558.3537 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 10513722.6687 |  | 0 | 1695382.7759 | 906893.5464 | 1305674.221 | 1816095.7873 | 2467489.337 | -925065.6408 | 324212.5068 | 382670.4098 | 418687.1893 | 423296.082 | 426230.6952 | 429409.4378 | 432853.1892 | 436584.6453 | 440628.4774 | 445011.5072 | 449762.895 | 454914.3465 | 460500.3365 | 466558.3537 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 10513722.6687 |  | 0 | 1695382.7759 | 906893.5464 | 1305674.221 | 1816095.7873 | 2467489.337 | -925065.6408 | 324212.5068 | 382670.4098 | 418687.1893 | 423296.082 | 426230.6952 | 429409.4378 | 432853.1892 | 436584.6453 | 440628.4774 | 445011.5072 | 449762.895 | 454914.3465 | 460500.3365 | 466558.3537 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 16235379.9109 |  | 0 | 557017.358 | 425484.8565 | 658507.5851 | 992287.8641 | 1458974.262 | 498741.4656 | 1160244.5664 | 1317462.4621 | 1346579.685 | 1349377.7958 | 1352350.2908 | 1355570.0668 | 1359058.2725 | 1362837.8966 | 1366933.9292 | 1371373.538 | 1376186.2599 | 1381404.2097 | 1387062.3075 | 1393198.5255 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 15652477.5819 |  | 0 | 557017.358 | 380585.6477 | 607104.6537 | 934381.2101 | 1394563.8854 | 424381.8818 | 1124280.4688 | 1281498.3645 | 1310615.5875 | 1313413.6982 | 1316386.1933 | 1319605.9692 | 1323094.1749 | 1326873.799 | 1330969.8317 | 1335409.4405 | 1340222.1624 | 1345440.1122 | 1351098.2099 | 1357234.4279 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 16818282.2399 |  | 0 | 557017.358 | 470384.0654 | 709910.5165 | 1050194.5181 | 1523384.6385 | 573101.0495 | 1196208.664 | 1353426.5596 | 1382543.7826 | 1385341.8933 | 1388314.3884 | 1391534.1643 | 1395022.37 | 1398801.9941 | 1402898.0268 | 1407337.6356 | 1412150.3575 | 1417368.3073 | 1423026.405 | 1429162.6231 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 18441820.231 |  | 0 | 612719.0939 | 512932.5511 | 775761.275 | 1149423.3045 | 1669282.0647 | 622975.1961 | 1312233.1206 | 1485172.8059 | 1517201.7511 | 1520279.6729 | 1523549.4175 | 1527091.171 | 1530928.1973 | 1535085.7838 | 1539591.4197 | 1544474.9894 | 1549768.9835 | 1555508.7283 | 1561732.6358 | 1568482.4756 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 14028939.5908 |  | 0 | 501315.6222 | 338037.162 | 541253.8952 | 835152.4237 | 1248666.4592 | 374507.7352 | 1008256.0122 | 1149752.1183 | 1175957.619 | 1178475.9186 | 1181151.1642 | 1184048.9625 | 1187188.3477 | 1190590.0094 | 1194276.4387 | 1198272.0867 | 1202603.5364 | 1207299.6912 | 1212391.9791 | 1217914.5754 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & total benefits 10% lower | Option 5sens5 |  | 13446037.2618 |  | 0 | 501315.6222 | 293137.9532 | 489850.9637 | 777245.7697 | 1184256.0827 | 300148.1513 | 972291.9146 | 1113788.0207 | 1139993.5214 | 1142511.8211 | 1145187.0666 | 1148084.865 | 1151224.2501 | 1154625.9118 | 1158312.3412 | 1162307.9891 | 1166639.4388 | 1171335.5936 | 1176427.8816 | 1181950.4778 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 16235379.9109 |  | 0 | 557017.358 | 425484.8565 | 658507.5851 | 992287.8641 | 1458974.262 | 498741.4656 | 1160244.5664 | 1317462.4621 | 1346579.685 | 1349377.7958 | 1352350.2908 | 1355570.0668 | 1359058.2725 | 1362837.8966 | 1366933.9292 | 1371373.538 | 1376186.2599 | 1381404.2097 | 1387062.3075 | 1393198.5255 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 16235379.9109 |  | 0 | 557017.358 | 425484.8565 | 658507.5851 | 992287.8641 | 1458974.262 | 498741.4656 | 1160244.5664 | 1317462.4621 | 1346579.685 | 1349377.7958 | 1352350.2908 | 1355570.0668 | 1359058.2725 | 1362837.8966 | 1366933.9292 | 1371373.538 | 1376186.2599 | 1381404.2097 | 1387062.3075 | 1393198.5255 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 16235379.9109 |  | 0 | 557017.358 | 425484.8565 | 658507.5851 | 992287.8641 | 1458974.262 | 498741.4656 | 1160244.5664 | 1317462.4621 | 1346579.685 | 1349377.7958 | 1352350.2908 | 1355570.0668 | 1359058.2725 | 1362837.8966 | 1366933.9292 | 1371373.538 | 1376186.2599 | 1381404.2097 | 1387062.3075 | 1393198.5255 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 0 | 0 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 11.7671 | 19.0352 | 10.5137 | 16.2354 |  | 2026-27: #NAME?; 2028-29: Option 3
sens1 | Capex 10% higher | 0 | 11.3886 | 18.2562 | 9.7648 | 15.6525 |  | 2026-27: #NAME?; 2028-29: Option 3
sens2 | Capex 10% lower | 0 | 12.1456 | 19.8141 | 11.2627 | 16.8183 |  | 2026-27: #NAME?; 2028-29: Option 3
sens3 | Total benefits 10% higher | 0 | 13.3224 | 21.7177 | 12.3141 | 18.4418 |  | 2026-27: #NAME?; 2028-29: Option 3
sens4 | Total benefits 10% lower | 0 | 10.2119 | 16.3527 | 8.7134 | 14.0289 |  | 2026-27: #NAME?; 2028-29: Option 3
sens5 | Capex 10% higher & total benefits 10% lower | 0 | 9.8334 | 15.5737 | 7.9644 | 13.446 |  | 2026-27: #NAME?; 2028-29: Option 3
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Workings_costs
Powercor
HV cable replacement
WORKINGS - COSTS
Source: Cable CBRM (October 2024)
| Top 5 assets |  |  | Average Length (m) | Variable ($/m) | Section Count | Length (m) | Fixed Cost | Variable Cost | Total cost ($ 2023)
|  | Replacement Cost (Urban) |  | 87.5 | 3050 | 5 | 0 | 29650 | 0 | 29650
|  | Replacement Cost (Rural Short) |  | 194.3 | 1677.1 | 0 | 4328.332 | 0 | 7259045.5972 | 7259045.5972
|  | Replacement Cost (Rural Long) |  | 276.2 | 1677.1 | 0 | 0 | 0 | 0 | 0
|  | Replacement Cost (Blank) as Rural Short |  | 194.3 | 1677.1 | 0 | 0 | 0 | 0 | 0
|  | Total |  |  |  | 5 | 4328.332 |  |  | 7288695.5972
| Top 10 assets |  |  | Average Length (m) | Variable ($/m) | Section Count | Length (m) | Fixed Cost | Variable Cost | Total cost ($ 2023)
|  | Replacement Cost (Urban) |  | 87.5 | 3050 | 3 | 1757.014 | 59300 | 5358892.7 | 5418192.7
|  | Replacement Cost (Rural Short) |  | 194.3 | 1677.1 | 6 | 5006.034 | 0 | 8395619.6214 | 8395619.6214
|  | Replacement Cost (Rural Long) |  | 276.2 | 1677.1 | 1 | 707.401 | 0 | 1186382.2171 | 1186382.2171
|  | Replacement Cost (Blank) as Rural Short |  | 194.3 | 1677.1 | 0 | 0 | 0 | 0 | 0
|  | Total |  |  |  | 10 | 7470.449 |  |  | 15000194.5385
| Top 30 assets |  |  | Average Length (m) | Variable ($/m) | Section Count | Length (m) | Fixed Cost | Variable Cost | Total cost ($ 2023)
|  | Replacement Cost (Urban) |  | 87.5 | 3050 | 10 | 5039.336 | 118600 | 15369974.8 | 15488574.8
|  | Replacement Cost (Rural Short) |  | 194.3 | 1677.1 | 15 | 10728.325 | 9740 | 17992473.8575 | 18002213.8575
|  | Replacement Cost (Rural Long) |  | 276.2 | 1677.1 | 5 | 8451.267 | 0 | 14173619.8857 | 14173619.8857
|  | Replacement Cost (Blank) as Rural Short |  | 194.3 | 1677.1 | 0 | 0 | 0 | 0 | 0
|  | Total |  |  |  | 30 | 24218.928 |  |  | 47664408.5432
| Expenditure |  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31
| Option 2 | Replace highest 5 delta risk cable sections |  | 1457739.1194 | 1457739.1194 | 1457739.1194 | 1457739.1194 | 1457739.1194
| Option 3 | Replace highest 10 delta risk cable sections |  | 3000038.9077 | 3000038.9077 | 3000038.9077 | 3000038.9077 | 3000038.9077
| Option 4 | Monitor highest delta risk cable sections and replace those with high partial discharge
| Condition assessment failed cable detection rate |  | 10%
| Condition assessment of top 30 delta risk cable sections |  |  | 1000000 | 1000000 | 1000000 | 1000000 | 1000000
| Replacement of poor condition cable sections |  |  |  | 1191610.2136 | 1191610.2136 | 1191610.2136 | 1191610.2136
| Option 5 | Replace highest 5 delta risk cable sections and monitor further 10
| Cable replacement (top 5) |  |  | 1457739.1194 | 1457739.1194 | 1457739.1194 | 1457739.1194 | 1457739.1194
| Condition assessment of next 10 delta risk cable sections |  |  | 333333.3333 | 333333.3333 | 333333.3333 | 333333.3333 | 333333.3333 | 0
| Replacement of poor condition cable sections | [6 empty] | 772268.1667 | 0

## Workings_risks
Powercor
HV cable replacement
WORKINGS - RISKS
CBRM data
[6 empty] | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5
| Average Consequences per failure ($) |  |  |  |  | All assets | Replace top 5 | Replace top 10 | Replace top 30 | Replace top 15
|  | Response cost |  |  |  | 16091.4921 | 14195 | 15447.5 | 16004.1667 | 15586.6667
|  | Unplanned replacements |  |  |  | 27436.6855 | 97265 | 60952.5 | 37100 | 50096.6667
|  | Safety Consequence |  |  |  | 49411.5537 | 56932.1956 | 66979.0536 | 64188.2597 | 72560.6414
|  | Environmental Consequence |  |  |  | 2393.774 | 550 | 1825 | 1966.6667 | 1683.3333
| Total number of failures without replacement |  |  |  |  | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
|  | Option 1 (base case) | No change to existing practices |  |  | 69.2853 | 82.8809 | 99.7406 | 120.6489 | 146.6348 | 178.9852 | 218.8033 | 259.0574 | 299.6486 | 340.5593 | 390.8654 | 441.9942 | 489.664 | 523.7584 | 550.0966 | 573.4197 | 587.3713 | 599.2238 | 609.1794 | 618.114 | 626.359 | 632.2179 | 636.7713 | 640.7401 | 644.5234
|  | Option 2 | Replace highest 5 delta risk cable sections |  |  | 0.34068 | 0.41344 | 0.50322 | 0.61427 | 0.75193 | 0.92295 | 1.1222 | 1.2387 | 1.2539 | 1.2539 | 1.2539 | 1.2539 | 1.2539 | 1.2539 | 1.2539 | 1.2539 | 1.2539 | 1.2539 | 1.2539 | 1.2539 | 1.2539 | 1.2539 | 1.2539 | 1.2539 | 1.2539
|  | Option 3 | Replace highest 10 delta risk cable sections |  |  | 0.55387 | 0.67931 | 0.8358 | 1.0315 | 1.2767 | 1.5847 | 1.9088 | 2.0808 | 2.1637 | 2.1642 | 2.1642 | 2.1642 | 2.1642 | 2.1642 | 2.1642 | 2.1642 | 2.1642 | 2.1642 | 2.1642 | 2.1642 | 2.1642 | 2.1642 | 2.1642 | 2.1642 | 2.1642
|  | Option 4 | Monitor highest delta risk cable sections and replace those with high partial discharge |  |  | 1.4624 | 1.7758 | 2.1657 | 2.6518 | 3.2596 | 4.0198 | 4.8601 | 5.3643 | 5.675 | 5.7147 | 5.74 | 5.7675 | 5.7972 | 5.8294 | 5.8642 | 5.902 | 5.943 | 5.9875 | 6.0356 | 6.0879 | 6.1446 | 6.2061 | 6.2728 | 6.3451 | 6.4237
|  | Option 5 | Replace highest 5 delta risk cable sections and monitor further 10 |  |  | 0.89656 | 1.0799 | 1.3075 | 1.5911 | 1.9454 | 2.3895 | 2.8692 | 3.1064 | 3.2109 | 3.2347 | 3.2601 | 3.2875 | 3.3172 | 3.3494 | 3.3842 | 3.4221 | 3.463 | 3.5075 | 3.5557 | 3.6079 | 3.6646 | 3.7261 | 3.7928 | 3.8652 | 3.9437
| Number of failures after replacement |  |  |  |  | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
|  | Option 1 (base case) | All assets
|  | Option 2 | Top 5 delta |  |  | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951 | 0.040951
|  | Option 3 | Top 10 delta |  |  | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679 | 0.070679
|  | Option 4 | Top 30 delta |  |  | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914
|  | Option 5 | Top 15 delta |  |  | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815 | 0.14815
| Implementation profile |  |  |  |  | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 1 (base case)
|  | Option 2 | Top 5 delta |  |  | 0% | 20% | 40% | 60% | 80% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  | Option 3 | Top 10 delta |  |  | 0% | 20% | 40% | 60% | 80% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  | Option 4 | Top 30 delta |  | (no failures during monitoring, % thereafter) | 100% | 100% | 100% | 100% | 100% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
|  | Option 5 | Top 15 delta | Replacement |  | 0% | 20% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  |  |  | Monitoring | (no failures during monitoring, % thereafter) | 100% | 100% | 100% | 100% | 100% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
| Energy at risk (MWh) |  |  |  |  | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
|  | Option 1 (base case) | Energy at risk (weighted) |  |  | 789.9323 | 944.9372 | 1137.1579 | 1375.5362 | 1671.8055 | 2040.6377 | 2494.6094 | 2953.5521 | 3416.3395 | 3882.7675 | 4456.3152 | 5039.2423 | 5582.7339 | 5971.4492 | 6271.735 | 6537.6451 | 6696.7095 | 6831.8415 | 6945.3462 | 7047.2115 | 7141.2138 | 7208.0122 | 7259.9261 | 7305.1747 | 7348.3085
|  | Option 2 | Energy at risk (weighted) |  |  | 789.9323 | 943.4738 | 1133.5254 | 1368.7786 | 1660.6319 | 2023.3111 | 2473.3684 | 2930.0219 | 3392.5112 | 3858.9392 | 4432.4869 | 5015.4139 | 5558.9055 | 5947.6209 | 6247.9066 | 6513.8168 | 6672.8811 | 6808.0131 | 6921.5179 | 7023.3832 | 7117.3855 | 7184.1839 | 7236.0978 | 7281.3464 | 7324.4802
|  | Option 3 | Energy at risk (weighted) |  |  | 789.9323 | 942.4715 | 1130.9583 | 1363.8587 | 1652.2612 | 2009.9678 | 2457.3749 | 2912.8328 | 3373.9412 | 3840.36 | 4413.9077 | 4996.8347 | 5540.3263 | 5929.0417 | 6229.3274 | 6495.2376 | 6654.3019 | 6789.4339 | 6902.9386 | 7004.804 | 7098.8063 | 7165.6047 | 7217.5186 | 7262.7671 | 7305.901
|  | Option 4 | Energy at risk (weighted) |  |  | 761.7229 | 910.6816 | 1095.3823 | 1324.3832 | 1608.9294 | 2033.3256 | 2485.6765 | 2943.6465 | 3405.8346 | 3872.186 | 4445.6848 | 5028.559 | 5571.9932 | 5960.6465 | 6260.865 | 6526.7022 | 6685.6875 | 6820.7338 | 6934.1456 | 7035.9101 | 7129.8031 | 7196.4829 | 7248.2681 | 7293.377 | 7336.3594
|  | Option 5 | Energy at risk (weighted) |  |  | 779.4659 | 930.7189 | 1118.1324 | 1350.0837 | 1637.7901 | 2020.7542 | 2470.2847 | 2926.7132 | 3389.0322 | 3855.4147 | 4428.9139 | 5011.7885 | 5555.2232 | 5943.877 | 6244.096 | 6509.9338 | 6668.9197 | 6803.9666 | 6917.3791 | 7019.1445 | 7113.0383 | 7179.719 | 7231.5052 | 7276.6153 | 7319.5988
OPTION 1 (BASE CASE) RISK
| Option 1 (base case) |  |  |  | Consequence per failure ($) | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
|  | Option 1 (base case) | Response cost | Option 1 (base case)Response cost | 16091.4921 | 1114904.0814 | 1333676.6953 | 1604975.3369 | 1941420.6396 | 2359572.7044 | 2880139.3854 | 3520871.4174 | 4168619.4057 | 4821793.7456 | 5480106.4736 | 6289607.0219 | 7112345.4708 | 7879425.083 | 8428054.7834 | 8851875.6262 | 9227179.093 | 9451681.1785 | 9642405.3917 | 9802605.0518 | 9946376.9673 | 10079051.014 | 10173329.7416 | 10246600.5874 | 10310464.0497 | 10371342.8148
|  | Option 1 (base case) | Unplanned replacements | Option 1 (base case)Unplanned replacements | 27436.6855 | 1900959.3721 | 2273976.0807 | 2736551.9238 | 3310205.6237 | 4023172.8645 | 4910761.4271 | 6003237.0773 | 7107675.2346 | 8221365.5544 | 9343817.047 | 10724050.2704 | 12126854.6832 | 13434758.3875 | 14370195.6043 | 15092828.355 | 15732736.8949 | 16115522.5986 | 16440715.5785 | 16713862.8836 | 16959000.1783 | 17185215.1296 | 17345964.4118 | 17470894.3528 | 17579784.3004 | 17683585.2114
|  | Option 1 (base case) | Safety Consequence | Option 1 (base case)Safety Consequence | 49411.5537 | 3423495.0151 | 4095272.0457 | 4928338.8204 | 5961449.0545 | 7245453.2424 | 8843938.2307 | 10811410.5488 | 12800426.5065 | 14806104.9624 | 16827561.6783 | 19313265.281 | 21839618.0189 | 24195061.2112 | 25879718.2825 | 27181129.3786 | 28333559.9504 | 29022930.2589 | 29608580.0954 | 30100499.308 | 30541974.4487 | 30949371.7711 | 31238869.9972 | 31463860.0925 | 31659963.2804 | 31846901.4687
|  | Option 1 (base case) | Environmental Consequence | Option 1 (base case)Environmental Consequence | 2393.774 | 165853.3837 | 198398.0474 | 238756.4947 | 288806.1742 | 351010.5701 | 428450.1875 | 523765.6297 | 620124.7672 | 717291.13 | 815221.8806 | 935643.3656 | 1058034.1236 | 1172145.0605 | 1253759.3391 | 1316807.0236 | 1372637.2524 | 1406034.2335 | 1434406.4107 | 1458237.7484 | 1479625.2911 | 1499361.9124 | 1513386.8372 | 1524286.6249 | 1533786.968 | 1542843.3069
OPTION 2 RISK
| Option 2 |  |  |  | Consequence per failure ($) | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option risk before replacement
|  | Option 2 | Response cost | before | 14195 | 4835.9148 | 5868.7124 | 7143.2128 | 8719.5958 | 10673.7061 | 13101.2629 | 15929.8067 | 17583.9028 | 17799.3455 | 17799.3455 | 17799.3455 | 17799.3455 | 17799.3455 | 17799.3455 | 17799.3455 | 17799.3455 | 17799.3455 | 17799.3455 | 17799.3455 | 17799.3455 | 17799.3455 | 17799.3455 | 17799.3455 | 17799.3455 | 17799.3455
|  | Option 2 | Unplanned replacements |  | 97265 | 33135.9811 | 40212.7727 | 48945.7268 | 59747.1989 | 73136.8806 | 89770.6473 | 109152.0005 | 120485.9673 | 121962.1938 | 121962.1938 | 121962.1938 | 121962.1938 | 121962.1938 | 121962.1938 | 121962.1938 | 121962.1938 | 121962.1938 | 121962.1938 | 121962.1938 | 121962.1938 | 121962.1938 | 121962.1938 | 121962.1938 | 121962.1938 | 121962.1938
|  | Option 2 | Safety Consequence |  | 56932.1956 | 19395.5087 | 23537.7725 | 28649.439 | 34971.8728 | 42809.2653 | 52545.5205 | 63890.0225 | 70524.1418 | 71388.2225 | 71388.2225 | 71388.2225 | 71388.2225 | 71388.2225 | 71388.2225 | 71388.2225 | 71388.2225 | 71388.2225 | 71388.2225 | 71388.2225 | 71388.2225 | 71388.2225 | 71388.2225 | 71388.2225 | 71388.2225 | 71388.2225
|  | Option 2 | Environmental Consequence |  | 550 | 187.3725 | 227.3893 | 276.7712 | 337.8498 | 413.5638 | 507.622 | 617.2169 | 681.3066 | 689.6541 | 689.6541 | 689.6541 | 689.6541 | 689.6541 | 689.6541 | 689.6541 | 689.6541 | 689.6541 | 689.6541 | 689.6541 | 689.6541 | 689.6541 | 689.6541 | 689.6541 | 689.6541 | 689.6541
Option risk after replacement
|  | Option 2 | Response cost |  | 14195 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958 | 581.2958
|  | Option 2 | Unplanned replacements |  | 97265 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741 | 3983.0741
|  | Option 2 | Safety Consequence |  | 56932.1956 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158 | 2331.4158
|  | Option 2 | Environmental Consequence |  | 550 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229 | 22.5229
Change in risk
|  | Option 2 | Response cost |  |  | 0 | -1057.4833 | -2624.7668 | -4882.98 | -8073.9282 | -12519.9671 | -15348.5109 | -17002.607 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497
|  | Option 2 | Unplanned replacements |  |  | 0 | -7245.9397 | -17985.0611 | -33458.4749 | -55323.0452 | -85787.5732 | -105168.9264 | -116502.8932 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196
|  | Option 2 | Safety Consequence |  |  | 0 | -4241.2713 | -10527.2093 | -19584.2742 | -32382.2796 | -50214.1047 | -61558.6067 | -68192.7261 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068
|  | Option 2 | Environmental Consequence |  |  | 0 | -40.9733 | -101.6993 | -189.1961 | -312.8327 | -485.0991 | -594.694 | -658.7836 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312
Total risk after replacement of selected cable
|  | Option 2 | Response cost | Option 2Response cost |  | 1114904.0814 | 1332619.212 | 1602350.5701 | 1936537.6596 | 2351498.7762 | 2867619.4183 | 3505522.9065 | 4151616.7987 | 4804575.6959 | 5462888.4239 | 6272388.9722 | 7095127.4211 | 7862207.0333 | 8410836.7337 | 8834657.5765 | 9209961.0434 | 9434463.1288 | 9625187.342 | 9785387.0021 | 9929158.9176 | 10061832.9643 | 10156111.6919 | 10229382.5378 | 10293246 | 10354124.7651
|  | Option 2 | Unplanned replacements | Option 2Unplanned replacements |  | 1900959.3721 | 2266730.141 | 2718566.8627 | 3276747.1488 | 3967849.8193 | 4824973.8539 | 5898068.1509 | 6991172.3414 | 8103386.4348 | 9225837.9274 | 10606071.1507 | 12008875.5635 | 13316779.2679 | 14252216.4846 | 14974849.2354 | 15614757.7752 | 15997543.479 | 16322736.4589 | 16595883.764 | 16841021.0587 | 17067236.01 | 17227985.2921 | 17352915.2332 | 17461805.1808 | 17565606.0917
|  | Option 2 | Safety Consequence | Option 2Safety Consequence |  | 3423495.0151 | 4091030.7744 | 4917811.6111 | 5941864.7803 | 7213070.9628 | 8793724.1259 | 10749851.9421 | 12732233.7804 | 14737048.1556 | 16758504.8716 | 19244208.4742 | 21770561.2121 | 24126004.4044 | 25810661.4758 | 27112072.5718 | 28264503.1437 | 28953873.4521 | 29539523.2887 | 30031442.5012 | 30472917.6419 | 30880314.9644 | 31169813.1904 | 31394803.2858 | 31590906.4736 | 31777844.662
|  | Option 2 | Environmental Consequence | Option 2Environmental Consequence |  | 165853.3837 | 198357.0741 | 238654.7954 | 288616.9781 | 350697.7374 | 427965.0884 | 523170.9358 | 619465.9836 | 716623.9988 | 814554.7494 | 934976.2344 | 1057366.9924 | 1171477.9293 | 1253092.2079 | 1316139.8924 | 1371970.1212 | 1405367.1023 | 1433739.2795 | 1457570.6172 | 1478958.1599 | 1498694.7812 | 1512719.706 | 1523619.4937 | 1533119.8368 | 1542176.1757
OPTION 3 RISK
| Option 3 |  |  |  | Consequence per failure ($) | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option risk before replacement
|  | Option 3 | Response cost | before | 15447.5 | 8555.848 | 10493.617 | 12910.9817 | 15933.745 | 19722.0954 | 24480.2883 | 29486.3747 | 32143.8288 | 33424.2483 | 33431.2781 | 33431.2781 | 33431.2781 | 33431.2781 | 33431.2781 | 33431.2781 | 33431.2781 | 33431.2781 | 33431.2781 | 33431.2781 | 33431.2781 | 33431.2781 | 33431.2781 | 33431.2781 | 33431.2781 | 33431.2781
|  | Option 3 | Unplanned replacements |  | 60952.5 | 33759.529 | 41405.547 | 50943.9462 | 62871.1176 | 77819.1306 | 96593.9325 | 116346.8688 | 126832.6087 | 131884.8677 | 131912.6057 | 131912.6057 | 131912.6057 | 131912.6057 | 131912.6057 | 131912.6057 | 131912.6057 | 131912.6057 | 131912.6057 | 131912.6057 | 131912.6057 | 131912.6057 | 131912.6057 | 131912.6057 | 131912.6057 | 131912.6057
|  | Option 3 | Safety Consequence |  | 66979.0536 | 37097.4333 | 45499.4357 | 55980.9246 | 69087.3706 | 85513.3378 | 106144.4598 | 127850.4272 | 139372.9231 | 144924.7138 | 144955.1945 | 144955.1945 | 144955.1945 | 144955.1945 | 144955.1945 | 144955.1945 | 144955.1945 | 144955.1945 | 144955.1945 | 144955.1945 | 144955.1945 | 144955.1945 | 144955.1945 | 144955.1945 | 144955.1945 | 144955.1945
|  | Option 3 | Environmental Consequence |  | 1825 | 1010.8058 | 1239.7379 | 1525.3304 | 1882.446 | 2330.0097 | 2892.1525 | 3483.5821 | 3797.5392 | 3948.8107 | 3949.6412 | 3949.6412 | 3949.6412 | 3949.6412 | 3949.6412 | 3949.6412 | 3949.6412 | 3949.6412 | 3949.6412 | 3949.6412 | 3949.6412 | 3949.6412 | 3949.6412 | 3949.6412 | 3949.6412 | 3949.6412
Option risk after replacement
|  | Option 3 | Response cost |  | 15447.5 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077 | 1091.8077
|  | Option 3 | Unplanned replacements |  | 60952.5 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373 | 4308.0373
|  | Option 3 | Safety Consequence |  | 66979.0536 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857 | 4733.9857
|  | Option 3 | Environmental Consequence |  | 1825 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884 | 128.9884
Change in risk
|  | Option 3 | Response cost |  |  | 0 | -1880.3619 | -4727.6696 | -8905.1624 | -14904.2302 | -23388.4806 | -28394.5671 | -31052.0211 | -32332.4406 | -32339.4704 | -32339.4704 | -32339.4704 | -32339.4704 | -32339.4704 | -32339.4704 | -32339.4704 | -32339.4704 | -32339.4704 | -32339.4704 | -32339.4704 | -32339.4704 | -32339.4704 | -32339.4704 | -32339.4704 | -32339.4704
|  | Option 3 | Unplanned replacements |  |  | 0 | -7419.5019 | -18654.3636 | -35137.8482 | -58808.8747 | -92285.8952 | -112038.8315 | -122524.5714 | -127576.8303 | -127604.5684 | -127604.5684 | -127604.5684 | -127604.5684 | -127604.5684 | -127604.5684 | -127604.5684 | -127604.5684 | -127604.5684 | -127604.5684 | -127604.5684 | -127604.5684 | -127604.5684 | -127604.5684 | -127604.5684 | -127604.5684
|  | Option 3 | Safety Consequence |  |  | 0 | -8153.09 | -20498.7756 | -38612.031 | -64623.4817 | -101410.4741 | -123116.4415 | -134638.9374 | -140190.7282 | -140221.2088 | -140221.2088 | -140221.2088 | -140221.2088 | -140221.2088 | -140221.2088 | -140221.2088 | -140221.2088 | -140221.2088 | -140221.2088 | -140221.2088 | -140221.2088 | -140221.2088 | -140221.2088 | -140221.2088 | -140221.2088
|  | Option 3 | Environmental Consequence |  |  | 0 | -222.1499 | -558.5368 | -1052.0745 | -1760.817 | -2763.1641 | -3354.5936 | -3668.5508 | -3819.8222 | -3820.6528 | -3820.6528 | -3820.6528 | -3820.6528 | -3820.6528 | -3820.6528 | -3820.6528 | -3820.6528 | -3820.6528 | -3820.6528 | -3820.6528 | -3820.6528 | -3820.6528 | -3820.6528 | -3820.6528 | -3820.6528
Total risk after replacement of selected cable
|  | Option 3 | Response cost | Option 3Response cost |  | 1114904.0814 | 1331796.3334 | 1600247.6673 | 1932515.4772 | 2344668.4742 | 2856750.9048 | 3492476.8503 | 4137567.3846 | 4789461.3049 | 5447767.0032 | 6257267.5515 | 7080006.0003 | 7847085.6125 | 8395715.313 | 8819536.1557 | 9194839.6226 | 9419341.7081 | 9610065.9213 | 9770265.5813 | 9914037.4969 | 10046711.5436 | 10140990.2711 | 10214261.117 | 10278124.5792 | 10339003.3444
|  | Option 3 | Unplanned replacements | Option 3Unplanned replacements |  | 1900959.3721 | 2266556.5788 | 2717897.5602 | 3275067.7755 | 3964363.9898 | 4818475.5319 | 5891198.2458 | 6985150.6633 | 8093788.7241 | 9216212.4786 | 10596445.7019 | 11999250.1147 | 13307153.8191 | 14242591.0358 | 14965223.7866 | 15605132.3264 | 15987918.0302 | 16313111.0101 | 16586258.3152 | 16831395.6099 | 17057610.5612 | 17218359.8433 | 17343289.7844 | 17452179.732 | 17555980.6429
|  | Option 3 | Safety Consequence | Option 3Safety Consequence |  | 3423495.0151 | 4087118.9557 | 4907840.0449 | 5922837.0236 | 7180829.7607 | 8742527.7566 | 10688294.1073 | 12665787.5691 | 14665914.2342 | 16687340.4696 | 19173044.0722 | 21699396.8101 | 24054840.0024 | 25739497.0738 | 27040908.1698 | 28193338.7416 | 28882709.0501 | 29468358.8867 | 29960278.0992 | 30401753.2399 | 30809150.5624 | 31098648.7884 | 31323638.8838 | 31519742.0716 | 31706680.26
|  | Option 3 | Environmental Consequence | Option 3Environmental Consequence |  | 165853.3837 | 198175.8975 | 238197.958 | 287754.0997 | 349249.7531 | 425687.0234 | 520411.0361 | 616456.2164 | 713471.3078 | 811401.2278 | 931822.7128 | 1054213.4709 | 1168324.4078 | 1249938.6863 | 1312986.3709 | 1368816.5996 | 1402213.5807 | 1430585.7579 | 1454417.0956 | 1475804.6384 | 1495541.2596 | 1509566.1845 | 1520465.9721 | 1529966.3152 | 1539022.6541
OPTION 4 RISK
| Option 4 |  |  |  | Consequence per failure ($) | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
|  | Monitoring |  |  |  | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option risk before replacement |  |  |  |  | FY32: 6066.6124
|  | Option 4 | Response cost | before | 16004.1667 | 23404.5476 | 28420.8991 | 34659.9369 | 42440.1632 | 52166.4901 | 64333.2783 | 77781.0984 | 85851.139 | 90823.2105 | 91459.4623 | 91864.582 | 92303.4035 | 92778.8091 | 93293.9319 | 93852.1779 | 94457.2497 | 95113.1728 | 95824.3243 | 96595.4632 | 97431.765 | 98338.8574 | 99322.8611 | 100390.433 | 101548.8135 | 102805.8778
|  | Option 4 | Unplanned replacements |  | 37100 | 54255.1659 | 65883.8026 | 80346.8049 | 98382.5079 | 120929.5569 | 149133.952 | 180307.9668 | 199015.5016 | 210541.4907 | 212016.4157 | 212955.5424 | 213972.7947 | 215074.8544 | 216268.9846 | 217563.0804 | 218965.7254 | 220486.2512 | 222134.8043 | 223922.4173 | 225861.087 | 227963.8599 | 230244.9246 | 232719.7125 | 235405.0078 | 238319.067
|  | Option 4 | Safety Consequence |  | 64188.2597 | 93869.1287 | 113988.3189 | 139011.3634 | 170215.6865 | 209225.2777 | 258022.8798 | 311958.345 | 344325.0323 | 364266.6276 | 366818.4569 | 368443.2792 | 370203.27 | 372109.9895 | 374176.004 | 376414.9733 | 378841.7479 | 381472.4732 | 384324.7037 | 387417.5275 | 390771.701 | 394409.7963 | 398356.3616 | 402638.0955 | 407284.0371 | 412325.7726
|  | Option 4 | Environmental Consequence |  | 1966.6667 | 2876.06 | 3492.4927 | 4259.1747 | 5215.2453 | 6410.4617 | 7905.5734 | 9558.1043 | 10549.7885 | 11160.7798 | 11238.9654 | 11288.7484 | 11342.6729 | 11401.0929 | 11464.3936 | 11532.9935 | 11607.3475 | 11687.9504 | 11775.34 | 11870.1012 | 11972.8698 | 12084.3376 | 12205.2566 | 12336.4448 | 12478.792 | 12633.2659
Option risk after replacement
|  | Option 4 | Response cost |  | 16004.1667 | 0 | 0 | 0 | 0 | 0 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545 | 3667.1545
|  | Option 4 | Unplanned replacements |  | 37100 | 0 | 0 | 0 | 0 | 0 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008 | 8501.0008
|  | Option 4 | Safety Consequence |  | 64188.2597 | 0 | 0 | 0 | 0 | 0 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366 | 14707.9366
|  | Option 4 | Environmental Consequence |  | 1966.6667 | 0 | 0 | 0 | 0 | 0 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371 | 450.6371
Change in risk
|  | Option 4 | Response cost |  |  | -23404.5476 | -28420.8991 | -34659.9369 | -42440.1632 | -52166.4901 | -6066.6124 | -7411.3944 | -8218.3984 | -8715.6056 | -8779.2308 | -8819.7427 | -8863.6249 | -8911.1655 | -8962.6777 | -9018.5023 | -9079.0095 | -9144.6018 | -9215.717 | -9292.8309 | -9376.461 | -9467.1703 | -9565.5707 | -9672.3278 | -9788.1659 | -9913.8723
|  | Option 4 | Unplanned replacements |  |  | -54255.1659 | -65883.8026 | -80346.8049 | -98382.5079 | -120929.5569 | -14063.2951 | -17180.6966 | -19051.4501 | -20204.049 | -20351.5415 | -20445.4542 | -20547.1794 | -20657.3854 | -20776.7984 | -20906.208 | -21046.4725 | -21198.525 | -21363.3804 | -21542.1416 | -21736.0086 | -21946.2859 | -22174.3924 | -22421.8712 | -22690.4007 | -22981.8066
|  | Option 4 | Safety Consequence |  |  | -93869.1287 | -113988.3189 | -139011.3634 | -170215.6865 | -209225.2777 | -24331.4943 | -29725.0408 | -32961.7096 | -34955.8691 | -35211.052 | -35373.5343 | -35549.5333 | -35740.2053 | -35946.8067 | -36170.7037 | -36413.3811 | -36676.4537 | -36961.6767 | -37270.9591 | -37606.3764 | -37970.186 | -38364.8425 | -38793.0159 | -39257.61 | -39761.7836
|  | Option 4 | Environmental Consequence |  |  | -2876.06 | -3492.4927 | -4259.1747 | -5215.2453 | -6410.4617 | -745.4936 | -910.7467 | -1009.9151 | -1071.0143 | -1078.8328 | -1083.8111 | -1089.2036 | -1095.0456 | -1101.3757 | -1108.2356 | -1115.671 | -1123.7313 | -1132.4703 | -1141.9464 | -1152.2233 | -1163.3701 | -1175.462 | -1188.5808 | -1202.8155 | -1218.2629
Total risk after monitoring and replacement of failed cable
|  | Option 4 | Response cost | Option 4Response cost |  | 1091499.5338 | 1305255.7962 | 1570315.4001 | 1898980.4764 | 2307406.2143 | 2874072.773 | 3513460.023 | 4160401.0073 | 4813078.14 | 5471327.2429 | 6280787.2791 | 7103481.8459 | 7870513.9175 | 8419092.1056 | 8842857.1238 | 9218100.0835 | 9442536.5767 | 9633189.6747 | 9793312.2209 | 9937000.5063 | 10069583.8437 | 10163764.1709 | 10236928.2596 | 10300675.8838 | 10361428.9425
|  | Option 4 | Unplanned replacements | Option 4Unplanned replacements |  | 1846704.2063 | 2208092.2781 | 2656205.1189 | 3211823.1158 | 3902243.3076 | 4896698.132 | 5986056.3807 | 7088623.7846 | 8201161.5054 | 9323465.5055 | 10703604.8162 | 12106307.5038 | 13414101.0021 | 14349418.8059 | 15071922.1471 | 15711690.4224 | 16094324.0736 | 16419352.1982 | 16692320.742 | 16937264.1697 | 17163268.8437 | 17323790.0194 | 17448472.4816 | 17557093.8997 | 17660603.4047
|  | Option 4 | Safety Consequence | Option 4Safety Consequence |  | 3329625.8864 | 3981283.7269 | 4789327.4571 | 5791233.3681 | 7036227.9647 | 8819606.7363 | 10781685.508 | 12767464.7969 | 14771149.0933 | 16792350.6263 | 19277891.7467 | 21804068.4856 | 24159321.0059 | 25843771.4758 | 27144958.6749 | 28297146.5693 | 28986253.8052 | 29571618.4187 | 30063228.3489 | 30504368.0723 | 30911401.5852 | 31200505.1547 | 31425067.0766 | 31620705.6704 | 31807139.6852
|  | Option 4 | Environmental Consequence | Option 4Environmental Consequence |  | 162977.3237 | 194905.5547 | 234497.32 | 283590.9289 | 344600.1084 | 427704.6939 | 522854.883 | 619114.8521 | 716220.1157 | 814143.0478 | 934559.5544 | 1056944.92 | 1171050.0149 | 1252657.9634 | 1315698.788 | 1371521.5814 | 1404910.5022 | 1433273.9404 | 1457095.802 | 1478473.0679 | 1498198.5423 | 1512211.3753 | 1523098.0441 | 1532584.1525 | 1541625.044
OPTION 5 RISK
| Option 5 |  |  |  | Consequence per failure ($) | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY50
| Monitoring |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Option 5 risk before replacement
|  | Option 5 | Response cost | before | 15586.6667 | 13974.3071 | 16831.6518 | 20379.6531 | 24799.6039 | 30322.6046 | 37243.6369 | 44721.4981 | 48419.0044 | 50047.4072 | 50418.8118 | 50813.3632 | 51240.7371 | 51703.7408 | 52205.4257 | 52749.1087 | 53338.396 | 53977.2082 | 54669.8078 | 55420.8301 | 56235.3153 | 57118.7444 | 58077.0785 | 59116.8007 | 60244.9625 | 61469.2339
|  | Option 5 | Unplanned replacements |  | 50096.6667 | 44914.4272 | 54098.1383 | 65501.6696 | 79707.7088 | 97459.0301 | 119703.7251 | 143738.1085 | 155622.1595 | 160855.9631 | 162049.6842 | 163317.8005 | 164691.4111 | 166179.5383 | 167791.9894 | 169539.4258 | 171433.4376 | 173486.6256 | 175712.6907 | 178126.5303 | 180744.3441 | 183583.7488 | 186663.9035 | 190005.6454 | 193631.6384 | 197566.5347
|  | Option 5 | Safety Consequence |  | 72560.6414 | 65054.6206 | 78356.4232 | 94873.4412 | 115449.6469 | 141160.8836 | 173380.3793 | 208192.0823 | 225405.091 | 232985.7979 | 234714.7985 | 236551.5542 | 238541.1089 | 240696.5311 | 243032.0256 | 245563.0344 | 248306.3448 | 251280.2082 | 254504.4689 | 258000.7045 | 261792.3788 | 265905.0083 | 270366.343 | 275206.5639 | 280458.4978 | 286157.851
|  | Option 5 | Environmental Consequence |  | 1683.3333 | 1509.2013 | 1817.7896 | 2200.9677 | 2678.3148 | 3274.7894 | 4022.2491 | 4829.8453 | 5229.1696 | 5405.0344 | 5445.1454 | 5487.7563 | 5533.9119 | 5583.9156 | 5638.0967 | 5696.8135 | 5760.4555 | 5829.4461 | 5904.2457 | 5985.3548 | 6073.3178 | 6168.7267 | 6272.2251 | 6384.5133 | 6506.3529 | 6638.5721
Adjust for risk removed from replacing top 5 (option 2)
|  | option 2 |  |  | 15586.6667 | -5310.0241 | -6444.0763 | -7843.5278 | -9574.4582 | -11720.1478 | -14385.7005 | -17491.5524 | -19307.8148 | -19544.3794 | -19544.3794 | -19544.3794 | -19544.3794 | -19544.3794 | -19544.3794 | -19544.3794 | -19544.3794 | -19544.3794 | -19544.3794 | -19544.3794 | -19544.3794 | -19544.3794 | -19544.3794 | -19544.3794 | -19544.3794 | -19544.3794
|  | option 2 |  |  | 50096.6667 | -17066.799 | -20711.7243 | -25209.6618 | -30772.9965 | -37669.3973 | -46236.675 | -56219.1064 | -62056.7043 | -62817.0397 | -62817.0397 | -62817.0397 | -62817.0397 | -62817.0397 | -62817.0397 | -62817.0397 | -62817.0397 | -62817.0397 | -62817.0397 | -62817.0397 | -62817.0397 | -62817.0397 | -62817.0397 | -62817.0397 | -62817.0397 | -62817.0397
|  | option 2 |  |  | 72560.6414 | -24719.766 | -29999.1218 | -36513.9909 | -44571.9948 | -54560.8283 | -66969.781 | -81428.4601 | -89883.7102 | -90984.9895 | -90984.9895 | -90984.9895 | -90984.9895 | -90984.9895 | -90984.9895 | -90984.9895 | -90984.9895 | -90984.9895 | -90984.9895 | -90984.9895 | -90984.9895 | -90984.9895 | -90984.9895 | -90984.9895 | -90984.9895 | -90984.9895
|  | option 2 |  |  | 1683.3333 | -573.4735 | -695.9492 | -847.0876 | -1034.0251 | -1265.7559 | -1553.631 | -1889.0577 | -2085.211 | -2110.7595 | -2110.7595 | -2110.7595 | -2110.7595 | -2110.7595 | -2110.7595 | -2110.7595 | -2110.7595 | -2110.7595 | -2110.7595 | -2110.7595 | -2110.7595 | -2110.7595 | -2110.7595 | -2110.7595 | -2110.7595 | -2110.7595
|  | option 2 |  |  |  | 0 | -1057.4833 | -2624.7668 | -4882.98 | -8073.9282 | -12519.9671 | -15348.5109 | -17002.607 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497 | -17218.0497
|  | option 2 |  |  |  | 0 | -7245.9397 | -17985.0611 | -33458.4749 | -55323.0452 | -85787.5732 | -105168.9264 | -116502.8932 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196 | -117979.1196
|  | option 2 |  |  |  | 0 | -4241.2713 | -10527.2093 | -19584.2742 | -32382.2796 | -50214.1047 | -61558.6067 | -68192.7261 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068 | -69056.8068
|  | option 2 |  |  |  | 0 | -40.9733 | -101.6993 | -189.1961 | -312.8327 | -485.0991 | -594.694 | -658.7836 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312 | -667.1312
Adjust for risk removed from replacing failed cables
|  | Option 5 |  | 14195 | 15586.6667 | 0 | 0 | 0 | 0 | 0 | -2414.2374 | -2879.1691 | -3083.5102 | -3224.8062 | -3261.9466 | -3301.4018 | -3344.1392 | -3390.4395 | -3440.608 | -3494.9763 | -3553.9051 | -3617.7863 | -3687.0462 | -3762.1485 | -3843.597 | -3931.9399 | -4027.7733 | -4131.7455 | -4244.5617 | -4366.9888
|  | Option 5 |  | 97265 | 50096.6667 | 0 | 0 | 0 | 0 | 0 | -2993.3078 | -3458.6108 | -3513.6192 | -3889.3769 | -4008.749 | -4135.5607 | -4272.9217 | -4421.7345 | -4582.9796 | -4757.7232 | -4947.1244 | -5152.4432 | -5375.0497 | -5616.4337 | -5878.215 | -6162.1555 | -6470.171 | -6804.3452 | -7166.9445 | -7560.4341
|  | Option 5 |  | 56932.1956 | 72560.6414 | 0 | 0 | 0 | 0 | 0 | -12083.4859 | -14430.206 | -15488.0949 | -16159.7575 | -16332.6576 | -16516.3332 | -16715.2886 | -16930.8309 | -17164.3803 | -17417.4812 | -17691.8122 | -17989.1986 | -18311.6246 | -18661.2482 | -19040.4156 | -19451.6786 | -19897.812 | -20381.8341 | -20907.0275 | -21476.9628
|  | Option 5 |  | 550 | 1683.3333 | 0 | 0 | 0 | 0 | 0 | -351.4627 | -421.2628 | -454.7863 | -471.538 | -475.5491 | -479.8102 | -484.4258 | -489.4261 | -494.8443 | -500.7159 | -507.0801 | -513.9792 | -521.4592 | -529.5701 | -538.3664 | -547.9073 | -558.2571 | -569.4859 | -581.6699 | -594.8918
|  | Option 5 |  | 14195 | 15586.6667 | 0 | 0 | 0 | 0 | 0 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797 | 172.7797
|  | Option 5 |  | 97265 | 50096.6667 | 0 | 0 | 0 | 0 | 0 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515 | 343.8515
|  | Option 5 |  | 56932.1956 | 72560.6414 | 0 | 0 | 0 | 0 | 0 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107 | 841.8107
|  | Option 5 |  | 550 | 1683.3333 | 0 | 0 | 0 | 0 | 0 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855 | 22.6855
Change in risk
|  |  | Response cost |  |  | 0 | -11445.0588 | -15160.8922 | -20108.1257 | -26676.385 | -14761.4249 | -18054.9004 | -19913.3375 | -20270.0762 | -20307.2167 | -20346.6718 | -20389.4092 | -20435.7096 | -20485.8781 | -20540.2464 | -20599.1751 | -20663.0563 | -20732.3163 | -20807.4185 | -20888.867 | -20977.2099 | -21073.0433 | -21177.0156 | -21289.8317 | -21412.2589
|  |  | Unplanned replacements |  |  | 0 | -40632.3537 | -58277.0688 | -82393.1872 | -115112.678 | -88437.0295 | -108283.6857 | -119672.661 | -121524.6451 | -121644.0172 | -121770.8288 | -121908.1899 | -122057.0026 | -122218.2477 | -122392.9914 | -122582.3925 | -122787.7114 | -123010.3179 | -123251.7018 | -123513.4832 | -123797.4237 | -124105.4391 | -124439.6133 | -124802.2126 | -125195.7023
|  |  | Safety Consequence |  |  | 0 | -52598.5728 | -68886.6596 | -90461.9263 | -118982.3349 | -61455.7799 | -75147.0021 | -82839.0103 | -84374.7536 | -84547.6537 | -84731.3293 | -84930.2847 | -85145.827 | -85379.3764 | -85632.4773 | -85906.8083 | -86204.1947 | -86526.6207 | -86876.2443 | -87255.4117 | -87666.6747 | -88112.8081 | -88596.8302 | -89122.0236 | -89691.9589
|  |  | Environmental Consequence |  |  | 0 | -1162.8137 | -1455.5794 | -1833.4858 | -2321.8662 | -813.8763 | -993.2713 | -1090.8844 | -1115.9837 | -1119.9948 | -1124.2559 | -1128.8715 | -1133.8718 | -1139.2899 | -1145.1616 | -1151.5258 | -1158.4249 | -1165.9048 | -1174.0158 | -1182.8121 | -1192.3529 | -1202.7028 | -1213.9316 | -1226.1156 | -1239.3375
Total risk after monitoring and replacement of failed cable
|  | Option 5 | Response cost | Option 5Response cost |  | 1114904.0814 | 1322231.6365 | 1589814.4447 | 1921312.5139 | 2332896.3194 | 2865377.9606 | 3502816.517 | 4148706.0682 | 4801523.6693 | 5459799.257 | 6269260.3501 | 7091956.0616 | 7858989.3734 | 8407568.9053 | 8831335.3798 | 9206579.918 | 9431018.1222 | 9621673.0754 | 9781797.6333 | 9925488.1003 | 10058073.8041 | 10152256.6982 | 10225423.5719 | 10289174.2179 | 10349930.556
|  | Option 5 | Unplanned replacements | Option 5Unplanned replacements |  | 1900959.3721 | 2233343.727 | 2678274.855 | 3227812.4365 | 3908060.1865 | 4822324.3976 | 5894953.3916 | 6988002.5737 | 8099840.9093 | 9222173.0298 | 10602279.4415 | 12004946.4933 | 13312701.3849 | 14247977.3565 | 14970435.3636 | 15610154.5023 | 15992734.8873 | 16317705.2607 | 16590611.1818 | 16835486.6951 | 17061417.706 | 17221858.9726 | 17346454.7395 | 17454982.0878 | 17558389.5091
|  | Option 5 | Safety Consequence | Option 5Safety Consequence |  | 3423495.0151 | 4042673.4729 | 4859452.1609 | 5870987.1282 | 7126470.9075 | 8782482.4507 | 10736263.5468 | 12717587.4962 | 14721730.2087 | 16743014.0246 | 19228533.9517 | 21754687.7342 | 24109915.3843 | 25794338.9061 | 27095496.9013 | 28247653.1421 | 28936726.0642 | 29522053.4747 | 30013623.0637 | 30454719.037 | 30861705.0965 | 31150757.189 | 31375263.2623 | 31570841.2568 | 31757209.5098
|  | Option 5 | Environmental Consequence | Option 5Environmental Consequence |  | 165853.3837 | 197235.2337 | 237300.9153 | 286972.6884 | 348688.7039 | 427636.3112 | 522772.3584 | 619033.8828 | 716175.1463 | 814101.8858 | 934519.1097 | 1056905.2521 | 1171011.1887 | 1252620.0491 | 1315661.862 | 1371485.7266 | 1404875.8086 | 1433240.5058 | 1457063.7326 | 1478442.4791 | 1498169.5594 | 1512184.1345 | 1523072.6933 | 1532560.8524 | 1541603.9694

## Misc_calcs
Powercor
HV cable replacement
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR | bar: 2021-06-30 to 2025-06-30
| Option | First year | Option included
| Option 2 | 1 | TRUE
| Option 3 | 1 | TRUE
| Option 4 | 1 | TRUE
| Option 5 | 1 | TRUE
| First year | 1
FLAGS | bar: 2021-06-30 to 2025-06-30
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
Powercor
HV cable replacement
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | FALSE |  |  | FALSE
Option5 | Option 5 | FALSE |  |  | FALSE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
Powercor
| Reliability in worst-served areas | per MWh | 151432.8174
| Network resilience | per MWh | 0
| Enabling solar exports | per MWh | 88.3577
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.35181
| Customer value of time - business | per minute customer time | 0.35181
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020