## Cover
Powercor
Regulatory proposal 2026-31
Minimise risk from 22kV conductor (bushfire)
| Model number: | 4.17
2025-01-31
14

## Summary
Powercor
Minimise bushfire risk from bare 22kV non-REFCL lines in HBRA
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Targeted installation of covered conductor on bare 22kV non-REFCL lines lines in HBRA |  | -7.4139 | 13.5307 | 6.1167
| Option 3 | Install EFD on all bare 22kV non-REFCL lines lines in HBRA |  | -68.1183 | 50.8868 | -17.2315
| Option 4 | Targeted installation of EFD on bare 22kV non-REFCL lines lines in HBRA |  | -11.6988 | 10.346 | -1.3527
| Option 5 | Targeted installation of covered conductor and EFD on bare 22kV non-REFCL lines lines in HBRA |  | -19.1127 | 23.8767 | 4.764
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | Targeted installation of covered conductor on bare 22kV non-REFCL lines lines in HBRA |  | 6.1167
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 5.244 | 5.244 | 0 | 0 | 0 |  | 10.4881
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 6.1167 | -17.2315 | -1.3527 | 4.764 |  | Option 2
| Capex 10% higher |  | 0 | 5.3753 | -21.8379 | -2.1791 | 3.1962 |  | Option 2
| Capex 10% lower |  | 0 | 6.8581 | -12.6251 | -0.52637 | 6.3318 |  | Option 2
| Total benefits 10% higher |  | 0 | 7.4698 | -12.1428 | -0.31814 | 7.1517 |  | Option 2
| Total benefits 10% lower |  | 0 | 4.7637 | -22.3202 | -2.3873 | 2.3763 |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  | 0 | 4.0223 | -26.9266 | -3.2137 | 0.80854 |  | Option 2
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
Powercor
Minimise bushfire risk from bare 22kV non-REFCL lines in HBRA
Project
|  | Business: |  | Powercor
|  | Descripton: |  | Minimise bushfire risk from bare 22kV non-REFCL lines in HBRA
|  | Date of cost inputs: |  | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Targeted installation of covered conductor on bare 22kV non-REFCL lines lines in HBRA
|  | Option 3 |  | Install EFD on all bare 22kV non-REFCL lines lines in HBRA
|  | Option 4 |  | Targeted installation of EFD on bare 22kV non-REFCL lines lines in HBRA
|  | Option 5 |  | Targeted installation of covered conductor and EFD on bare 22kV non-REFCL lines lines in HBRA
|  | Compliance project |  | No
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | Network average |  | Network average | 43815.4862 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 151432.8174 | 2023-12-31 | per MWh
|  | Network resilience |  |  |  | 24590 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 88.3577 | 2023-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.35181 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
Powercor
Minimise bushfire risk from bare 22kV non-REFCL lines in HBRA
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 |  | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943
| Safety consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bushfire risk |  |  | 2023-12-31 |  | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
Powercor
Minimise bushfire risk from bare 22kV non-REFCL lines in HBRA
OPTION 2 | Targeted installation of covered conductor on bare 22kV non-REFCL lines lines in HBRA
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Covered conductor |  | 30 | 2023-12-31 | 4712000 | 4712000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 4712000 | 4712000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 42142234.2832 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bushfire risk |  |  | 2023-12-31 | 17039270.55 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 59181504.8332 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - residential | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - business | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 435220.5536 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
Capital expenditure
| Covered conductor |  |  | 2023-12-31 | -4712000 | -4712000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Covered conductor |  |  | 2023-12-31 | -4712000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Covered conductor |  |  | 2023-12-31 | 0 | -256197.7145 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -256197.7145 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291
| Annualised capex |  |  | 2023-12-31 | 0 | -256197.7145 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 435220.5536 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 435220.5536 | 614243.3927 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 435220.5536 | 614243.3927 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578
| Total annualised capex |  |  |  | 0 | -256197.7145 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291
| Total benefits |  |  |  | 435220.5536 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 435220.5536 | 588623.6213 | 306806.1353 | 306806.1353 | 306806.1353 | 306806.1353 | 306806.1353 | 306806.1353 | 306806.1353 | 306806.1353 | 306806.1353 | 306806.1353 | 306806.1353 | 306806.1353 | 306806.1353 | 306806.1353 | 306806.1353 | 306806.1353 | 306806.1353 | 306806.1353 | 59053090.4148 | 59053090.4148 | 59053090.4148 | 59053090.4148 | 59053090.4148
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 435220.5536 | 639863.1642 | 409285.2211 | 409285.2211 | 409285.2211 | 409285.2211 | 409285.2211 | 409285.2211 | 409285.2211 | 409285.2211 | 409285.2211 | 409285.2211 | 409285.2211 | 409285.2211 | 409285.2211 | 409285.2211 | 409285.2211 | 409285.2211 | 409285.2211 | 409285.2211 | 59155569.5007 | 59155569.5007 | 59155569.5007 | 59155569.5007 | 59155569.5007
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 478742.609 | 701287.5035 | 445089.7889 | 445089.7889 | 445089.7889 | 445089.7889 | 445089.7889 | 445089.7889 | 445089.7889 | 445089.7889 | 445089.7889 | 445089.7889 | 445089.7889 | 445089.7889 | 445089.7889 | 445089.7889 | 445089.7889 | 445089.7889 | 445089.7889 | 445089.7889 | 65066002.4964 | 65066002.4964 | 65066002.4964 | 65066002.4964 | 65066002.4964
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 391698.4983 | 527199.282 | 271001.5675 | 271001.5675 | 271001.5675 | 271001.5675 | 271001.5675 | 271001.5675 | 271001.5675 | 271001.5675 | 271001.5675 | 271001.5675 | 271001.5675 | 271001.5675 | 271001.5675 | 271001.5675 | 271001.5675 | 271001.5675 | 271001.5675 | 271001.5675 | 53142657.4191 | 53142657.4191 | 53142657.4191 | 53142657.4191 | 53142657.4191
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 391698.4983 | 501579.5106 | 219762.0246 | 219762.0246 | 219762.0246 | 219762.0246 | 219762.0246 | 219762.0246 | 219762.0246 | 219762.0246 | 219762.0246 | 219762.0246 | 219762.0246 | 219762.0246 | 219762.0246 | 219762.0246 | 219762.0246 | 219762.0246 | 219762.0246 | 219762.0246 | 53091417.8762 | 53091417.8762 | 53091417.8762 | 53091417.8762 | 53091417.8762
sens | 0 | 0% | 0% | Option 2sens | 435220.5536 | 614243.3927 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578
sens | 0 | 0% | 0% | Option 2sens | 435220.5536 | 614243.3927 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578
sens | 0 | 0% | 0% | Option 2sens | 435220.5536 | 614243.3927 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 358045.6782 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578

## Option3
Powercor
Minimise bushfire risk from bare 22kV non-REFCL lines in HBRA
OPTION 3 | Install EFD on all bare 22kV non-REFCL lines lines in HBRA
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| EFD |  | 15 | 2023-12-31 | 9010894.436 | 9010894.436 | 9010894.436 | 9010894.436 | 9010894.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 9010894.436 | 9010894.436 | 9010894.436 | 9010894.436 | 9010894.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 90841.6311 | 90841.6311 | 90841.6311 | 90841.6311 | 90841.6311 | 2147258.0117 | 2147258.0117 | 2147258.0117 | 2625095.667 | 2625095.667 | 2625095.667 | 2625095.667 | 2625095.667 | 2147258.0117 | 2147258.0117 | 1717806.4094 | 1288354.807 | 858903.2047 | 429451.6023 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 41699221.4986 | 41107143.3029 | 40515065.1072 | 39922986.9114 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39922986.9114 | 40515065.1072 | 41107143.3029 | 41699221.4986 | 42291299.6943 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bushfire risk |  |  | 2023-12-31 | 17082447.1615 | 16839468.6304 | 16596490.0993 | 16353511.5683 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16353511.5683 | 16596490.0993 | 16839468.6304 | 17082447.1615 | 17325425.6925 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 58781668.66 | 57946611.9333 | 57111555.2065 | 56276498.4797 | 55441441.753 | 55441441.753 | 55441441.753 | 55441441.753 | 55441441.753 | 55441441.753 | 55441441.753 | 55441441.753 | 55441441.753 | 55441441.753 | 55441441.753 | 56276498.4797 | 57111555.2065 | 57946611.9333 | 58781668.66 | 59616725.3868 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 835056.7268 | 1670113.4535 | 2505170.1803 | 3340226.9071 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 3340226.9071 | 2505170.1803 | 1670113.4535 | 835056.7268 | 0 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
Capital expenditure
| EFD |  |  | 2023-12-31 | -9010894.436 | -9010894.436 | -9010894.436 | -9010894.436 | -9010894.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| EFD |  |  | 2023-12-31 | -9010894.436 | -18021788.8719 | -27032683.3079 | -36043577.7438 | -45054472.1798 | -45054472.1798 | -45054472.1798 | -45054472.1798 | -45054472.1798 | -45054472.1798 | -45054472.1798 | -45054472.1798 | -45054472.1798 | -45054472.1798 | -45054472.1798 | -36043577.7438 | -27032683.3079 | -18021788.8719 | -9010894.436 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - EFD |  |  | 2023-12-31 | 0 | -782371.5345 | -1564743.0689 | -2347114.6034 | -3129486.1378 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3129486.1378 | -2347114.6034 | -1564743.0689 | -782371.5345 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -782371.5345 | -1564743.0689 | -2347114.6034 | -3129486.1378 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3129486.1378 | -2347114.6034 | -1564743.0689 | -782371.5345 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | -782371.5345 | -1564743.0689 | -2347114.6034 | -3129486.1378 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3129486.1378 | -2347114.6034 | -1564743.0689 | -782371.5345 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | -90841.6311 | -90841.6311 | -90841.6311 | -90841.6311 | -90841.6311 | -2147258.0117 | -2147258.0117 | -2147258.0117 | -2625095.667 | -2625095.667 | -2625095.667 | -2625095.667 | -2625095.667 | -2147258.0117 | -2147258.0117 | -1717806.4094 | -1288354.807 | -858903.2047 | -429451.6023 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 835056.7268 | 1670113.4535 | 2505170.1803 | 3340226.9071 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 3340226.9071 | 2505170.1803 | 1670113.4535 | 835056.7268 | 0 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 744215.0957 | 796900.288 | 849585.4803 | 902270.6727 | 954955.865 | -1883832.0501 | -1883832.0501 | -1883832.0501 | -2361669.7054 | -2361669.7054 | -2361669.7054 | -2361669.7054 | -2361669.7054 | -1883832.0501 | -1883832.0501 | -2289437.1746 | -1912670.7645 | -1535904.3545 | -1159137.9445 | -782371.5345 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 744215.0957 | 796900.288 | 849585.4803 | 902270.6727 | 954955.865 | -1883832.0501 | -1883832.0501 | -1883832.0501 | -2361669.7054 | -2361669.7054 | -2361669.7054 | -2361669.7054 | -2361669.7054 | -1883832.0501 | -1883832.0501 | -2289437.1746 | -1912670.7645 | -1535904.3545 | -1159137.9445 | -782371.5345 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
| Total annualised capex |  |  |  | 0 | -782371.5345 | -1564743.0689 | -2347114.6034 | -3129486.1378 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3911857.6723 | -3129486.1378 | -2347114.6034 | -1564743.0689 | -782371.5345 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 835056.7268 | 1670113.4535 | 2505170.1803 | 3340226.9071 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 4175283.6339 | 3340226.9071 | 2505170.1803 | 1670113.4535 | 835056.7268 | 0 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 744215.0957 | 718663.1346 | 693111.1734 | 667559.2123 | 642007.2512 | -2275017.8173 | -2275017.8173 | -2275017.8173 | -2752855.4726 | -2752855.4726 | -2752855.4726 | -2752855.4726 | -2752855.4726 | -2275017.8173 | -2275017.8173 | -2680622.9418 | -2225619.3783 | -1770615.8148 | -1315612.2514 | -860608.6879 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 744215.0957 | 875137.4415 | 1006059.7872 | 1136982.133 | 1267904.4788 | -1492646.2829 | -1492646.2829 | -1492646.2829 | -1970483.9382 | -1970483.9382 | -1970483.9382 | -1970483.9382 | -1970483.9382 | -1492646.2829 | -1492646.2829 | -1898251.4073 | -1599722.1507 | -1301192.8942 | -1002663.6376 | -704134.381 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 827720.7684 | 963911.6334 | 1100102.4984 | 1236293.3634 | 1372484.2284 | -1466303.6867 | -1466303.6867 | -1466303.6867 | -1944141.342 | -1944141.342 | -1944141.342 | -1944141.342 | -1944141.342 | -1466303.6867 | -1466303.6867 | -1955414.4838 | -1662153.7465 | -1368893.0091 | -1075632.2718 | -782371.5345 | 65578397.9255 | 65578397.9255 | 65578397.9255 | 65578397.9255 | 65578397.9255
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 660709.423 | 629888.9427 | 599068.4623 | 568247.9819 | 537427.5016 | -2301360.4135 | -2301360.4135 | -2301360.4135 | -2779198.0688 | -2779198.0688 | -2779198.0688 | -2779198.0688 | -2779198.0688 | -2301360.4135 | -2301360.4135 | -2623459.8653 | -2163187.7826 | -1702915.6999 | -1242643.6172 | -782371.5345 | 53655052.8481 | 53655052.8481 | 53655052.8481 | 53655052.8481 | 53655052.8481
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 660709.423 | 551651.7892 | 442594.1554 | 333536.5216 | 224478.8878 | -2692546.1807 | -2692546.1807 | -2692546.1807 | -3170383.836 | -3170383.836 | -3170383.836 | -3170383.836 | -3170383.836 | -2692546.1807 | -2692546.1807 | -3014645.6325 | -2476136.3963 | -1937627.1602 | -1399117.924 | -860608.6879 | 53655052.8481 | 53655052.8481 | 53655052.8481 | 53655052.8481 | 53655052.8481
sens | 0 | 0% | 0% | Option 3sens | 744215.0957 | 796900.288 | 849585.4803 | 902270.6727 | 954955.865 | -1883832.0501 | -1883832.0501 | -1883832.0501 | -2361669.7054 | -2361669.7054 | -2361669.7054 | -2361669.7054 | -2361669.7054 | -1883832.0501 | -1883832.0501 | -2289437.1746 | -1912670.7645 | -1535904.3545 | -1159137.9445 | -782371.5345 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
sens | 0 | 0% | 0% | Option 3sens | 744215.0957 | 796900.288 | 849585.4803 | 902270.6727 | 954955.865 | -1883832.0501 | -1883832.0501 | -1883832.0501 | -2361669.7054 | -2361669.7054 | -2361669.7054 | -2361669.7054 | -2361669.7054 | -1883832.0501 | -1883832.0501 | -2289437.1746 | -1912670.7645 | -1535904.3545 | -1159137.9445 | -782371.5345 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
sens | 0 | 0% | 0% | Option 3sens | 744215.0957 | 796900.288 | 849585.4803 | 902270.6727 | 954955.865 | -1883832.0501 | -1883832.0501 | -1883832.0501 | -2361669.7054 | -2361669.7054 | -2361669.7054 | -2361669.7054 | -2361669.7054 | -1883832.0501 | -1883832.0501 | -2289437.1746 | -1912670.7645 | -1535904.3545 | -1159137.9445 | -782371.5345 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868

## Option4
Powercor
Minimise bushfire risk from bare 22kV non-REFCL lines in HBRA
OPTION 4 | Targeted installation of EFD on bare 22kV non-REFCL lines lines in HBRA
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| EFD |  | 15 | 2023-12-31 | 3842052.7726 | 3842052.7726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 3842052.7726 | 3842052.7726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 15493.1719 | 15493.1719 | 15493.1719 | 15493.1719 | 15493.1719 | 366217.9668 | 366217.9668 | 366217.9668 | 569957.7288 | 569957.7288 | 366217.9668 | 366217.9668 | 366217.9668 | 366217.9668 | 366217.9668 | 183108.9834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 42038850.2078 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 42038850.2078 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bushfire risk |  |  | 2023-12-31 | 17174356.4319 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17174356.4319 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 59213206.6397 | 58809687.8926 | 58809687.8926 | 58809687.8926 | 58809687.8926 | 58809687.8926 | 58809687.8926 | 58809687.8926 | 58809687.8926 | 58809687.8926 | 58809687.8926 | 58809687.8926 | 58809687.8926 | 58809687.8926 | 58809687.8926 | 59213206.6397 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 403518.7471 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 403518.7471 | 0 | 0 | 0 | 0 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
Capital expenditure
| EFD |  |  | 2023-12-31 | -3842052.7726 | -3842052.7726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| EFD |  |  | 2023-12-31 | -3842052.7726 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -3842052.7726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - EFD |  |  | 2023-12-31 | 0 | -333586.4985 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -333586.4985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -333586.4985 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -333586.4985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | -333586.4985 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -333586.4985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | -15493.1719 | -15493.1719 | -15493.1719 | -15493.1719 | -15493.1719 | -366217.9668 | -366217.9668 | -366217.9668 | -569957.7288 | -569957.7288 | -366217.9668 | -366217.9668 | -366217.9668 | -366217.9668 | -366217.9668 | -183108.9834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 403518.7471 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 403518.7471 | 0 | 0 | 0 | 0 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 388025.5753 | 457957.8239 | 124371.3254 | 124371.3254 | 124371.3254 | -226353.4695 | -226353.4695 | -226353.4695 | -430093.2315 | -430093.2315 | -226353.4695 | -226353.4695 | -226353.4695 | -226353.4695 | -226353.4695 | -446763.2332 | -333586.4985 | 0 | 0 | 0 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 388025.5753 | 457957.8239 | 124371.3254 | 124371.3254 | 124371.3254 | -226353.4695 | -226353.4695 | -226353.4695 | -430093.2315 | -430093.2315 | -226353.4695 | -226353.4695 | -226353.4695 | -226353.4695 | -226353.4695 | -446763.2332 | -333586.4985 | 0 | 0 | 0 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
| Total annualised capex |  |  |  | 0 | -333586.4985 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -333586.4985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 403518.7471 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 807037.4943 | 403518.7471 | 0 | 0 | 0 | 0 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 388025.5753 | 424599.1741 | 57654.0257 | 57654.0257 | 57654.0257 | -293070.7692 | -293070.7692 | -293070.7692 | -496810.5312 | -496810.5312 | -293070.7692 | -293070.7692 | -293070.7692 | -293070.7692 | -293070.7692 | -513480.5329 | -366945.1483 | 0 | 0 | 0 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 388025.5753 | 491316.4738 | 191088.6251 | 191088.6251 | 191088.6251 | -159636.1698 | -159636.1698 | -159636.1698 | -363375.9318 | -363375.9318 | -159636.1698 | -159636.1698 | -159636.1698 | -159636.1698 | -159636.1698 | -380045.9335 | -300227.8486 | 0 | 0 | 0 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 428377.45 | 538661.5733 | 205075.0748 | 205075.0748 | 205075.0748 | -145649.72 | -145649.72 | -145649.72 | -349389.4821 | -349389.4821 | -145649.72 | -145649.72 | -145649.72 | -145649.72 | -145649.72 | -406411.3585 | -333586.4985 | 0 | 0 | 0 | 65578397.9255 | 65578397.9255 | 65578397.9255 | 65578397.9255 | 65578397.9255
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 347673.7005 | 377254.0745 | 43667.576 | 43667.576 | 43667.576 | -307057.2189 | -307057.2189 | -307057.2189 | -510796.981 | -510796.981 | -307057.2189 | -307057.2189 | -307057.2189 | -307057.2189 | -307057.2189 | -487115.1079 | -333586.4985 | 0 | 0 | 0 | 53655052.8481 | 53655052.8481 | 53655052.8481 | 53655052.8481 | 53655052.8481
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 347673.7005 | 343895.4246 | -23049.7237 | -23049.7237 | -23049.7237 | -373774.5186 | -373774.5186 | -373774.5186 | -577514.2807 | -577514.2807 | -373774.5186 | -373774.5186 | -373774.5186 | -373774.5186 | -373774.5186 | -553832.4076 | -366945.1483 | 0 | 0 | 0 | 53655052.8481 | 53655052.8481 | 53655052.8481 | 53655052.8481 | 53655052.8481
sens | 0 | 0% | 0% | Option 4sens | 388025.5753 | 457957.8239 | 124371.3254 | 124371.3254 | 124371.3254 | -226353.4695 | -226353.4695 | -226353.4695 | -430093.2315 | -430093.2315 | -226353.4695 | -226353.4695 | -226353.4695 | -226353.4695 | -226353.4695 | -446763.2332 | -333586.4985 | 0 | 0 | 0 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
sens | 0 | 0% | 0% | Option 4sens | 388025.5753 | 457957.8239 | 124371.3254 | 124371.3254 | 124371.3254 | -226353.4695 | -226353.4695 | -226353.4695 | -430093.2315 | -430093.2315 | -226353.4695 | -226353.4695 | -226353.4695 | -226353.4695 | -226353.4695 | -446763.2332 | -333586.4985 | 0 | 0 | 0 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
sens | 0 | 0% | 0% | Option 4sens | 388025.5753 | 457957.8239 | 124371.3254 | 124371.3254 | 124371.3254 | -226353.4695 | -226353.4695 | -226353.4695 | -430093.2315 | -430093.2315 | -226353.4695 | -226353.4695 | -226353.4695 | -226353.4695 | -226353.4695 | -446763.2332 | -333586.4985 | 0 | 0 | 0 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868

## Option5
Powercor
Minimise bushfire risk from bare 22kV non-REFCL lines in HBRA
OPTION 5 | Targeted installation of covered conductor and EFD on bare 22kV non-REFCL lines lines in HBRA
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Covered conductor |  | 30 | 2023-12-31 | 4712000 | 4712000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EFD |  | 15 | 2023-12-31 | 3842052.7726 | 3842052.7726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 8554052.7726 | 8554052.7726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 15493.1719 | 15493.1719 | 15493.1719 | 15493.1719 | 15493.1719 | 366217.9668 | 366217.9668 | 366217.9668 | 569957.7288 | 569957.7288 | 366217.9668 | 366217.9668 | 366217.9668 | 366217.9668 | 366217.9668 | 183108.9834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 43815.4862 | 2023-12-31 | 41889784.7967 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41740719.3856 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bushfire risk |  |  | 2023-12-31 | 16888201.2893 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16602046.1468 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 58777986.0861 | 57939246.7853 | 57939246.7853 | 57939246.7853 | 57939246.7853 | 57939246.7853 | 57939246.7853 | 57939246.7853 | 57939246.7853 | 57939246.7853 | 57939246.7853 | 57939246.7853 | 57939246.7853 | 57939246.7853 | 57939246.7853 | 58342765.5324 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 58746284.2795 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 151432.8174 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 24590 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 88.3577 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.35181 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 838739.3008 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1273959.8544 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
Capital expenditure
| Covered conductor |  |  | 2023-12-31 | -4712000 | -4712000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EFD |  |  | 2023-12-31 | -3842052.7726 | -3842052.7726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Covered conductor |  |  | 2023-12-31 | -4712000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000 | -9424000
| EFD |  |  | 2023-12-31 | -3842052.7726 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -7684105.5452 | -3842052.7726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Covered conductor |  |  | 2023-12-31 | 0 | -256197.7145 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291
| Annualised capex - EFD |  |  | 2023-12-31 | 0 | -333586.4985 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -667172.997 | -333586.4985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -589784.213 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -845981.9276 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291
| Annualised capex |  |  | 2023-12-31 | 0 | -589784.213 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -845981.9276 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291
| Operating expenditure |  |  | 2023-12-31 | -15493.1719 | -15493.1719 | -15493.1719 | -15493.1719 | -15493.1719 | -366217.9668 | -366217.9668 | -366217.9668 | -569957.7288 | -569957.7288 | -366217.9668 | -366217.9668 | -366217.9668 | -366217.9668 | -366217.9668 | -183108.9834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 838739.3008 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1273959.8544 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 823246.1289 | 1072201.2166 | 482417.0036 | 482417.0036 | 482417.0036 | 131692.2087 | 131692.2087 | 131692.2087 | -72047.5533 | -72047.5533 | 131692.2087 | 131692.2087 | 131692.2087 | 131692.2087 | 131692.2087 | -88717.555 | 24459.1797 | 358045.6782 | 358045.6782 | 358045.6782 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 823246.1289 | 1072201.2166 | 482417.0036 | 482417.0036 | 482417.0036 | 131692.2087 | 131692.2087 | 131692.2087 | -72047.5533 | -72047.5533 | 131692.2087 | 131692.2087 | 131692.2087 | 131692.2087 | 131692.2087 | -88717.555 | 24459.1797 | 358045.6782 | 358045.6782 | 358045.6782 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578
| Total annualised capex |  |  |  | 0 | -589784.213 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -1179568.426 | -845981.9276 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291 | -512395.4291
| Total benefits |  |  |  | 838739.3008 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1677478.6015 | 1273959.8544 | 870441.1073 | 870441.1073 | 870441.1073 | 870441.1073 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868 | 59616725.3868
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 823246.1289 | 1013222.7953 | 364460.161 | 364460.161 | 364460.161 | 13735.3661 | 13735.3661 | 13735.3661 | -190004.3959 | -190004.3959 | 13735.3661 | 13735.3661 | 13735.3661 | 13735.3661 | 13735.3661 | -206674.3976 | -60139.013 | 306806.1353 | 306806.1353 | 306806.1353 | 59053090.4148 | 59053090.4148 | 59053090.4148 | 59053090.4148 | 59053090.4148
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 823246.1289 | 1131179.6379 | 600373.8462 | 600373.8462 | 600373.8462 | 249649.0513 | 249649.0513 | 249649.0513 | 45909.2893 | 45909.2893 | 249649.0513 | 249649.0513 | 249649.0513 | 249649.0513 | 249649.0513 | 29239.2876 | 109057.3725 | 409285.2211 | 409285.2211 | 409285.2211 | 59155569.5007 | 59155569.5007 | 59155569.5007 | 59155569.5007 | 59155569.5007
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 907120.059 | 1239949.0768 | 650164.8638 | 650164.8638 | 650164.8638 | 299440.0689 | 299440.0689 | 299440.0689 | 95700.3068 | 95700.3068 | 299440.0689 | 299440.0689 | 299440.0689 | 299440.0689 | 299440.0689 | 38678.4304 | 111503.2904 | 445089.7889 | 445089.7889 | 445089.7889 | 65066002.4964 | 65066002.4964 | 65066002.4964 | 65066002.4964 | 65066002.4964
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 739372.1988 | 904453.3565 | 314669.1435 | 314669.1435 | 314669.1435 | -36055.6514 | -36055.6514 | -36055.6514 | -239795.4135 | -239795.4135 | -36055.6514 | -36055.6514 | -36055.6514 | -36055.6514 | -36055.6514 | -216113.5405 | -62584.931 | 271001.5675 | 271001.5675 | 271001.5675 | 53142657.4191 | 53142657.4191 | 53142657.4191 | 53142657.4191 | 53142657.4191
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 739372.1988 | 845474.9352 | 196712.3009 | 196712.3009 | 196712.3009 | -154012.494 | -154012.494 | -154012.494 | -357752.2561 | -357752.2561 | -154012.494 | -154012.494 | -154012.494 | -154012.494 | -154012.494 | -334070.3831 | -147183.1238 | 219762.0246 | 219762.0246 | 219762.0246 | 53091417.8762 | 53091417.8762 | 53091417.8762 | 53091417.8762 | 53091417.8762
sens | 0 | 0% | 0% | Option 5sens | 823246.1289 | 1072201.2166 | 482417.0036 | 482417.0036 | 482417.0036 | 131692.2087 | 131692.2087 | 131692.2087 | -72047.5533 | -72047.5533 | 131692.2087 | 131692.2087 | 131692.2087 | 131692.2087 | 131692.2087 | -88717.555 | 24459.1797 | 358045.6782 | 358045.6782 | 358045.6782 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578
sens | 0 | 0% | 0% | Option 5sens | 823246.1289 | 1072201.2166 | 482417.0036 | 482417.0036 | 482417.0036 | 131692.2087 | 131692.2087 | 131692.2087 | -72047.5533 | -72047.5533 | 131692.2087 | 131692.2087 | 131692.2087 | 131692.2087 | 131692.2087 | -88717.555 | 24459.1797 | 358045.6782 | 358045.6782 | 358045.6782 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578
sens | 0 | 0% | 0% | Option 5sens | 823246.1289 | 1072201.2166 | 482417.0036 | 482417.0036 | 482417.0036 | 131692.2087 | 131692.2087 | 131692.2087 | -72047.5533 | -72047.5533 | 131692.2087 | 131692.2087 | 131692.2087 | 131692.2087 | 131692.2087 | -88717.555 | 24459.1797 | 358045.6782 | 358045.6782 | 358045.6782 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578 | 59104329.9578

## Consol
Powercor
Minimise bushfire risk from bare 22kV non-REFCL lines in HBRA
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 789186057.0618 | 2026-06-30 |  | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 959327497.0659 | 2026-06-30 |  | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 675899638.6535 | 2026-06-30 |  | 46900625.4821 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 0 | 0 | 0 | 0 | 0
Option 2 | Capital expenditure | Option 2Capital expenditure | -10134918.2076 | 2026-06-30 |  | -5244044.3899 | -5244044.3899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 945796823.8838 | 2026-06-30 |  | 65863845.1628 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 0 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -7413941.4329 | 2026-06-30 |  | 0 | -285125.6765 | -570251.353 | -570251.353 | -570251.353 | -570251.353 | -570251.353 | -570251.353 | -570251.353 | -570251.353 | -570251.353 | -570251.353 | -570251.353 | -570251.353 | -570251.353 | -570251.353 | -570251.353 | -570251.353 | -570251.353 | -570251.353 | 0 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 13530673.182 | 2026-06-30 |  | 484362.4581 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 0 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 484362.4581 | 683599.2398 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 6116731.7491 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -7413941.4329 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 13530673.182 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 644453818.8481 | 2026-06-30 |  | 46407590.9515 | 45748659.6398 | 45089728.3281 | 44430797.0165 | 43771865.7048 | 43771865.7048 | 43771865.7048 | 43771865.7048 | 43771865.7048 | 43771865.7048 | 43771865.7048 | 43771865.7048 | 43771865.7048 | 43771865.7048 | 43771865.7048 | 44430797.0165 | 45089728.3281 | 45748659.6398 | 46407590.9515 | 47066522.2632 | 0 | 0 | 0 | 0 | 0
Option 3 | Capital expenditure | Option 3Capital expenditure | -46064031.747 | 2026-06-30 |  | -10028338.3733 | -10028338.3733 | -10028338.3733 | -10028338.3733 | -10028338.3733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 908440686.1269 | 2026-06-30 |  | 65418862.4292 | 64489517.2375 | 63560172.0458 | 62630826.8541 | 61701481.6624 | 61701481.6624 | 61701481.6624 | 61701481.6624 | 61701481.6624 | 61701481.6624 | 61701481.6624 | 61701481.6624 | 61701481.6624 | 61701481.6624 | 61701481.6624 | 62630826.8541 | 63560172.0458 | 64489517.2375 | 65418862.4292 | 66348207.6209 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -46064031.747 | 2026-06-30 |  | 0 | -870711.1749 | -1741422.3498 | -2612133.5247 | -3482844.6996 | -4353555.8744 | -4353555.8744 | -4353555.8744 | -4353555.8744 | -4353555.8744 | -4353555.8744 | -4353555.8744 | -4353555.8744 | -4353555.8744 | -4353555.8744 | -4353555.8744 | -3482844.6996 | -2612133.5247 | -1741422.3498 | -870711.1749 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | -22054256.525 | 2026-06-30 |  | -101098.8001 | -101098.8001 | -101098.8001 | -101098.8001 | -101098.8001 | -2389710.5964 | -2389710.5964 | -2389710.5964 | -2921502.1659 | -2921502.1659 | -2921502.1659 | -2921502.1659 | -2921502.1659 | -2389710.5964 | -2389710.5964 | -1911768.4771 | -1433826.3578 | -955884.2385 | -477942.1193 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 50886810.939 | 2026-06-30 |  | 929345.1917 | 1858690.3834 | 2788035.5751 | 3717380.7668 | 4646725.9585 | 4646725.9585 | 4646725.9585 | 4646725.9585 | 4646725.9585 | 4646725.9585 | 4646725.9585 | 4646725.9585 | 4646725.9585 | 4646725.9585 | 4646725.9585 | 3717380.7668 | 2788035.5751 | 1858690.3834 | 929345.1917 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 828246.3916 | 886880.4085 | 945514.4253 | 1004148.4421 | 1062782.4589 | -2096540.5123 | -2096540.5123 | -2096540.5123 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2096540.5123 | -2096540.5123 | -2547943.5847 | -2128635.4823 | -1709327.3798 | -1290019.2773 | -870711.1749 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | -17231477.3331 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -68118288.2721 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 50886810.939 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 674061280.0132 | 2026-06-30 |  | 46785568.0371 | 46504613.8109 | 46504613.8109 | 46504613.8109 | 46504613.8109 | 46504613.8109 | 46504613.8109 | 46504613.8109 | 46504613.8109 | 46504613.8109 | 46504613.8109 | 46504613.8109 | 46504613.8109 | 46504613.8109 | 46504613.8109 | 46785568.0371 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 47066522.2632 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | -8263771.3496 | 2026-06-30 |  | -4275869.1188 | -4275869.1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 948981463.2474 | 2026-06-30 |  | 65899126.5042 | 65450045.3874 | 65450045.3874 | 65450045.3874 | 65450045.3874 | 65450045.3874 | 65450045.3874 | 65450045.3874 | 65450045.3874 | 65450045.3874 | 65450045.3874 | 65450045.3874 | 65450045.3874 | 65450045.3874 | 65450045.3874 | 65899126.5042 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 66348207.6209 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | -8263771.3496 | 2026-06-30 |  | 0 | -371252.6328 | -742505.2657 | -742505.2657 | -742505.2657 | -742505.2657 | -742505.2657 | -742505.2657 | -742505.2657 | -742505.2657 | -742505.2657 | -742505.2657 | -742505.2657 | -742505.2657 | -742505.2657 | -742505.2657 | -371252.6328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | -3435008.4557 | 2026-06-30 |  | -17242.5469 | -17242.5469 | -17242.5469 | -17242.5469 | -17242.5469 | -407568.6065 | -407568.6065 | -407568.6065 | -634313.1643 | -634313.1643 | -407568.6065 | -407568.6065 | -407568.6065 | -407568.6065 | -407568.6065 | -203784.3033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 10346033.8185 | 2026-06-30 |  | 449081.1167 | 898162.2335 | 898162.2335 | 898162.2335 | 898162.2335 | 898162.2335 | 898162.2335 | 898162.2335 | 898162.2335 | 898162.2335 | 898162.2335 | 898162.2335 | 898162.2335 | 898162.2335 | 898162.2335 | 449081.1167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 431838.5698 | 509667.0537 | 138414.4209 | 138414.4209 | 138414.4209 | -251911.6387 | -251911.6387 | -251911.6387 | -478656.1965 | -478656.1965 | -251911.6387 | -251911.6387 | -251911.6387 | -251911.6387 | -251911.6387 | -497208.4522 | -371252.6328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | -1352745.9868 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | -11698779.8053 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 10346033.8185 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 669426950.7212 | 2026-06-30 |  | 46619671.2559 | 46172820.2486 | 46172820.2486 | 46172820.2486 | 46172820.2486 | 46172820.2486 | 46172820.2486 | 46172820.2486 | 46172820.2486 | 46172820.2486 | 46172820.2486 | 46172820.2486 | 46172820.2486 | 46172820.2486 | 46172820.2486 | 46453774.4748 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 46734728.7009 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | -18398689.5572 | 2026-06-30 |  | -9519913.5087 | -9519913.5087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 935450790.0653 | 2026-06-30 |  | 65414764.0461 | 64481320.4712 | 64481320.4712 | 64481320.4712 | 64481320.4712 | 64481320.4712 | 64481320.4712 | 64481320.4712 | 64481320.4712 | 64481320.4712 | 64481320.4712 | 64481320.4712 | 64481320.4712 | 64481320.4712 | 64481320.4712 | 64930401.5879 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 65379482.7047 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | -15677712.7825 | 2026-06-30 |  | 0 | -656378.3093 | -1312756.6187 | -1312756.6187 | -1312756.6187 | -1312756.6187 | -1312756.6187 | -1312756.6187 | -1312756.6187 | -1312756.6187 | -1312756.6187 | -1312756.6187 | -1312756.6187 | -1312756.6187 | -1312756.6187 | -1312756.6187 | -941503.9858 | -570251.353 | -570251.353 | -570251.353 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | -3435008.4557 | 2026-06-30 |  | -17242.5469 | -17242.5469 | -17242.5469 | -17242.5469 | -17242.5469 | -407568.6065 | -407568.6065 | -407568.6065 | -634313.1643 | -634313.1643 | -407568.6065 | -407568.6065 | -407568.6065 | -407568.6065 | -407568.6065 | -203784.3033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 23876707.0005 | 2026-06-30 |  | 933443.5749 | 1866887.1497 | 1866887.1497 | 1866887.1497 | 1866887.1497 | 1866887.1497 | 1866887.1497 | 1866887.1497 | 1866887.1497 | 1866887.1497 | 1866887.1497 | 1866887.1497 | 1866887.1497 | 1866887.1497 | 1866887.1497 | 1417806.033 | 968724.9162 | 968724.9162 | 968724.9162 | 968724.9162 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 916201.028 | 1193266.2935 | 536887.9842 | 536887.9842 | 536887.9842 | 146561.9245 | 146561.9245 | 146561.9245 | -80182.6332 | -80182.6332 | 146561.9245 | 146561.9245 | 146561.9245 | 146561.9245 | 146561.9245 | -98734.8889 | 27220.9304 | 398473.5633 | 398473.5633 | 398473.5633 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 4763985.7623 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | -19112721.2382 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 23876707.0005 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0.57025 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482 | 66.3482
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 0 |  |  | Energy at risk energy at risk (weighted) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Energy at risk value | 42.2913 |  |  | Option 1 (base case) risk cost | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913 | 42.2913

## Sensitivity_calcs
Powercor
Minimise bushfire risk from bare 22kV non-REFCL lines in HBRA
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
[7 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 398473.5633 | 398473.5633 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 6116731.7491 |  | 0 | 484362.4581 | 683599.2398 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 0 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 5375337.6058 |  | 0 | 484362.4581 | 655086.6721 | 341448.428 | 341448.428 | 341448.428 | 341448.428 | 341448.428 | 341448.428 | 341448.428 | 341448.428 | 341448.428 | 341448.428 | 341448.428 | 341448.428 | 341448.428 | 341448.428 | 341448.428 | 341448.428 | 341448.428 | 341448.428 | 0 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 6858125.8924 |  | 0 | 484362.4581 | 712111.8074 | 455498.6986 | 455498.6986 | 455498.6986 | 455498.6986 | 455498.6986 | 455498.6986 | 455498.6986 | 455498.6986 | 455498.6986 | 455498.6986 | 455498.6986 | 455498.6986 | 455498.6986 | 455498.6986 | 455498.6986 | 455498.6986 | 455498.6986 | 455498.6986 | 0 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 7469799.0673 |  | 0 | 532798.7039 | 780471.7314 | 495346.0549 | 495346.0549 | 495346.0549 | 495346.0549 | 495346.0549 | 495346.0549 | 495346.0549 | 495346.0549 | 495346.0549 | 495346.0549 | 495346.0549 | 495346.0549 | 495346.0549 | 495346.0549 | 495346.0549 | 495346.0549 | 495346.0549 | 495346.0549 | 0 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 4763664.4309 |  | 0 | 435926.2123 | 586726.7481 | 301601.0716 | 301601.0716 | 301601.0716 | 301601.0716 | 301601.0716 | 301601.0716 | 301601.0716 | 301601.0716 | 301601.0716 | 301601.0716 | 301601.0716 | 301601.0716 | 301601.0716 | 301601.0716 | 301601.0716 | 301601.0716 | 301601.0716 | 301601.0716 | 0 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 4022270.2876 |  | 0 | 435926.2123 | 558214.1805 | 244575.9363 | 244575.9363 | 244575.9363 | 244575.9363 | 244575.9363 | 244575.9363 | 244575.9363 | 244575.9363 | 244575.9363 | 244575.9363 | 244575.9363 | 244575.9363 | 244575.9363 | 244575.9363 | 244575.9363 | 244575.9363 | 244575.9363 | 244575.9363 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 6116731.7491 |  | 0 | 484362.4581 | 683599.2398 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 6116731.7491 |  | 0 | 484362.4581 | 683599.2398 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 6116731.7491 |  | 0 | 484362.4581 | 683599.2398 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 398473.5633 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 828246.3916 | 886880.4085 | 945514.4253 | 1004148.4421 | 1062782.4589 | -2096540.5123 | -2096540.5123 | -2096540.5123 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2096540.5123 | -2096540.5123 | -2547943.5847 | -2128635.4823 | -1709327.3798 | -1290019.2773 | -870711.1749 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | -17231477.3331 |  | 0 | 828246.3916 | 886880.4085 | 945514.4253 | 1004148.4421 | 1062782.4589 | -2096540.5123 | -2096540.5123 | -2096540.5123 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2096540.5123 | -2096540.5123 | -2547943.5847 | -2128635.4823 | -1709327.3798 | -1290019.2773 | -870711.1749 | 0 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | -21837880.5078 |  | 0 | 828246.3916 | 799809.291 | 771372.1903 | 742935.0896 | 714497.9889 | -2531896.0998 | -2531896.0998 | -2531896.0998 | -3063687.6693 | -3063687.6693 | -3063687.6693 | -3063687.6693 | -3063687.6693 | -2531896.0998 | -2531896.0998 | -2983299.1722 | -2476919.9522 | -1970540.7323 | -1464161.5123 | -957782.2924 | 0 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | -12625074.1584 |  | 0 | 828246.3916 | 973951.5259 | 1119656.6602 | 1265361.7946 | 1411066.9289 | -1661184.9249 | -1661184.9249 | -1661184.9249 | -2192976.4944 | -2192976.4944 | -2192976.4944 | -2192976.4944 | -2192976.4944 | -1661184.9249 | -1661184.9249 | -2112587.9973 | -1780351.0123 | -1448114.0273 | -1115877.0424 | -783640.0574 | 0 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | -12142796.2392 |  | 0 | 921180.9108 | 1072749.4468 | 1224317.9828 | 1375886.5188 | 1527455.0547 | -1631867.9165 | -1631867.9165 | -1631867.9165 | -2163659.486 | -2163659.486 | -2163659.486 | -2163659.486 | -2163659.486 | -1631867.9165 | -1631867.9165 | -2176205.5081 | -1849831.9248 | -1523458.3415 | -1197084.7582 | -870711.1749 | 0 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | -22320158.427 |  | 0 | 735311.8725 | 701011.3701 | 666710.8678 | 632410.3654 | 598109.863 | -2561213.1082 | -2561213.1082 | -2561213.1082 | -3093004.6777 | -3093004.6777 | -3093004.6777 | -3093004.6777 | -3093004.6777 | -2561213.1082 | -2561213.1082 | -2919681.6614 | -2407439.0398 | -1895196.4182 | -1382953.7965 | -870711.1749 | 0 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | -26926561.6017 |  | 0 | 735311.8725 | 613940.2526 | 492568.6328 | 371197.0129 | 249825.3931 | -2996568.6956 | -2996568.6956 | -2996568.6956 | -3528360.2651 | -3528360.2651 | -3528360.2651 | -3528360.2651 | -3528360.2651 | -2996568.6956 | -2996568.6956 | -3355037.2489 | -2755723.5097 | -2156409.7706 | -1557096.0315 | -957782.2924 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -17231477.3331 |  | 0 | 828246.3916 | 886880.4085 | 945514.4253 | 1004148.4421 | 1062782.4589 | -2096540.5123 | -2096540.5123 | -2096540.5123 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2096540.5123 | -2096540.5123 | -2547943.5847 | -2128635.4823 | -1709327.3798 | -1290019.2773 | -870711.1749 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -17231477.3331 |  | 0 | 828246.3916 | 886880.4085 | 945514.4253 | 1004148.4421 | 1062782.4589 | -2096540.5123 | -2096540.5123 | -2096540.5123 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2096540.5123 | -2096540.5123 | -2547943.5847 | -2128635.4823 | -1709327.3798 | -1290019.2773 | -870711.1749 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -17231477.3331 |  | 0 | 828246.3916 | 886880.4085 | 945514.4253 | 1004148.4421 | 1062782.4589 | -2096540.5123 | -2096540.5123 | -2096540.5123 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2628332.0818 | -2096540.5123 | -2096540.5123 | -2547943.5847 | -2128635.4823 | -1709327.3798 | -1290019.2773 | -870711.1749 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | -1352745.9868 |  | 0 | 431838.5698 | 509667.0537 | 138414.4209 | 138414.4209 | 138414.4209 | -251911.6387 | -251911.6387 | -251911.6387 | -478656.1965 | -478656.1965 | -251911.6387 | -251911.6387 | -251911.6387 | -251911.6387 | -251911.6387 | -497208.4522 | -371252.6328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | -2179123.1218 |  | 0 | 431838.5698 | 472541.7905 | 64163.8943 | 64163.8943 | 64163.8943 | -326162.1653 | -326162.1653 | -326162.1653 | -552906.7231 | -552906.7231 | -326162.1653 | -326162.1653 | -326162.1653 | -326162.1653 | -326162.1653 | -571458.9788 | -408377.8961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | -526368.8519 |  | 0 | 431838.5698 | 546792.317 | 212664.9475 | 212664.9475 | 212664.9475 | -177661.1122 | -177661.1122 | -177661.1122 | -404405.6699 | -404405.6699 | -177661.1122 | -177661.1122 | -177661.1122 | -177661.1122 | -177661.1122 | -422957.9256 | -334127.3696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | -318142.605 |  | 0 | 476746.6815 | 599483.2771 | 228230.6443 | 228230.6443 | 228230.6443 | -162095.4154 | -162095.4154 | -162095.4154 | -388839.9732 | -388839.9732 | -162095.4154 | -162095.4154 | -162095.4154 | -162095.4154 | -162095.4154 | -452300.3405 | -371252.6328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | -2387349.3687 |  | 0 | 386930.4582 | 419850.8304 | 48598.1976 | 48598.1976 | 48598.1976 | -341727.8621 | -341727.8621 | -341727.8621 | -568472.4199 | -568472.4199 | -341727.8621 | -341727.8621 | -341727.8621 | -341727.8621 | -341727.8621 | -542116.5639 | -371252.6328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | -3213726.5036 |  | 0 | 386930.4582 | 382725.5671 | -25652.329 | -25652.329 | -25652.329 | -415978.3886 | -415978.3886 | -415978.3886 | -642722.9464 | -642722.9464 | -415978.3886 | -415978.3886 | -415978.3886 | -415978.3886 | -415978.3886 | -616367.0904 | -408377.8961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | -1352745.9868 |  | 0 | 431838.5698 | 509667.0537 | 138414.4209 | 138414.4209 | 138414.4209 | -251911.6387 | -251911.6387 | -251911.6387 | -478656.1965 | -478656.1965 | -251911.6387 | -251911.6387 | -251911.6387 | -251911.6387 | -251911.6387 | -497208.4522 | -371252.6328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | -1352745.9868 |  | 0 | 431838.5698 | 509667.0537 | 138414.4209 | 138414.4209 | 138414.4209 | -251911.6387 | -251911.6387 | -251911.6387 | -478656.1965 | -478656.1965 | -251911.6387 | -251911.6387 | -251911.6387 | -251911.6387 | -251911.6387 | -497208.4522 | -371252.6328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | -1352745.9868 |  | 0 | 431838.5698 | 509667.0537 | 138414.4209 | 138414.4209 | 138414.4209 | -251911.6387 | -251911.6387 | -251911.6387 | -478656.1965 | -478656.1965 | -251911.6387 | -251911.6387 | -251911.6387 | -251911.6387 | -251911.6387 | -497208.4522 | -371252.6328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 4763985.7623 |  | 0 | 916201.028 | 1193266.2935 | 536887.9842 | 536887.9842 | 536887.9842 | 146561.9245 | 146561.9245 | 146561.9245 | -80182.6332 | -80182.6332 | 146561.9245 | 146561.9245 | 146561.9245 | 146561.9245 | 146561.9245 | -98734.8889 | 27220.9304 | 398473.5633 | 398473.5633 | 398473.5633 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 3196214.4841 |  | 0 | 916201.028 | 1127628.4626 | 405612.3223 | 405612.3223 | 405612.3223 | 15286.2627 | 15286.2627 | 15286.2627 | -211458.2951 | -211458.2951 | 15286.2627 | 15286.2627 | 15286.2627 | 15286.2627 | 15286.2627 | -230010.5508 | -66929.4682 | 341448.428 | 341448.428 | 341448.428 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 6331757.0406 |  | 0 | 916201.028 | 1258904.1244 | 668163.646 | 668163.646 | 668163.646 | 277837.5864 | 277837.5864 | 277837.5864 | 51093.0286 | 51093.0286 | 277837.5864 | 277837.5864 | 277837.5864 | 277837.5864 | 277837.5864 | 32540.7729 | 121371.329 | 455498.6986 | 455498.6986 | 455498.6986 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 7151656.4624 |  | 0 | 1009545.3854 | 1379955.0085 | 723576.6992 | 723576.6992 | 723576.6992 | 333250.6395 | 333250.6395 | 333250.6395 | 106506.0817 | 106506.0817 | 333250.6395 | 333250.6395 | 333250.6395 | 333250.6395 | 333250.6395 | 43045.7144 | 124093.4221 | 495346.0549 | 495346.0549 | 495346.0549 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 2376315.0623 |  | 0 | 822856.6705 | 1006577.5785 | 350199.2692 | 350199.2692 | 350199.2692 | -40126.7904 | -40126.7904 | -40126.7904 | -266871.3482 | -266871.3482 | -40126.7904 | -40126.7904 | -40126.7904 | -40126.7904 | -40126.7904 | -240515.4922 | -69651.5612 | 301601.0716 | 301601.0716 | 301601.0716 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 808543.784 |  | 0 | 822856.6705 | 940939.7476 | 218923.6073 | 218923.6073 | 218923.6073 | -171402.4523 | -171402.4523 | -171402.4523 | -398147.0101 | -398147.0101 | -171402.4523 | -171402.4523 | -171402.4523 | -171402.4523 | -171402.4523 | -371791.1541 | -163801.9598 | 244575.9363 | 244575.9363 | 244575.9363 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 4763985.7623 |  | 0 | 916201.028 | 1193266.2935 | 536887.9842 | 536887.9842 | 536887.9842 | 146561.9245 | 146561.9245 | 146561.9245 | -80182.6332 | -80182.6332 | 146561.9245 | 146561.9245 | 146561.9245 | 146561.9245 | 146561.9245 | -98734.8889 | 27220.9304 | 398473.5633 | 398473.5633 | 398473.5633 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 4763985.7623 |  | 0 | 916201.028 | 1193266.2935 | 536887.9842 | 536887.9842 | 536887.9842 | 146561.9245 | 146561.9245 | 146561.9245 | -80182.6332 | -80182.6332 | 146561.9245 | 146561.9245 | 146561.9245 | 146561.9245 | 146561.9245 | -98734.8889 | 27220.9304 | 398473.5633 | 398473.5633 | 398473.5633 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 4763985.7623 |  | 0 | 916201.028 | 1193266.2935 | 536887.9842 | 536887.9842 | 536887.9842 | 146561.9245 | 146561.9245 | 146561.9245 | -80182.6332 | -80182.6332 | 146561.9245 | 146561.9245 | 146561.9245 | 146561.9245 | 146561.9245 | -98734.8889 | 27220.9304 | 398473.5633 | 398473.5633 | 398473.5633 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 0 | 0 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 6.1167 | -17.2315 | -1.3527 | 4.764 |  | 2026-27: #NAME?; 2028-29: Option 2
sens1 | Capex 10% higher | 0 | 5.3753 | -21.8379 | -2.1791 | 3.1962 |  | 2026-27: #NAME?; 2028-29: Option 2
sens2 | Capex 10% lower | 0 | 6.8581 | -12.6251 | -0.52637 | 6.3318 |  | 2026-27: #NAME?; 2028-29: Option 2
sens3 | Total benefits 10% higher | 0 | 7.4698 | -12.1428 | -0.31814 | 7.1517 |  | 2026-27: #NAME?; 2028-29: Option 2
sens4 | Total benefits 10% lower | 0 | 4.7637 | -22.3202 | -2.3873 | 2.3763 |  | 2026-27: #NAME?; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 4.0223 | -26.9266 | -3.2137 | 0.80854 |  | 2026-27: #NAME?; 2028-29: Option 2
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Workings_costs
Powercor
Minimise bushfire risk from bare 22kV non-REFCL lines in HBRA
WORKINGS - COSTS
Option 1 (base case) - no change to existing practices
|  | Total capital costs |  | 0
|  | Total operating costs |  | 0
Option 2 - Targeted installation of covered conductor on bare 22kV non-REFCL lines lines in HBRA
|  | Length of bare 22kV non-REFCL lines to be replaced with covered conductor |  | 62 | km
|  | 22kV covered conductor unit cost |  | 152000 | 2023 $/km
|  | Total covered conductor capex costs |  | 9424000 | 2023 $
|  | Progam duration |  | 2 | years of the 2026-31 reg period
|  |  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46
|  | Option 2 capex costs |  | 2 2026-27: 4712000; years of the 2026-31 reg period 2027-28: 4712000
Option 2 opex costs
Option 3 - Install early fault detection (EFDs) on all bare 22kV non-REFCL lines lines in HBRA
|  |  | Distance per unit | 2 2026-27: 3.5; years of the 2026-31 reg period 2027-28: km
|  | Unitised EFD hardware and installation capex cost |  | 2 2026-27: 5122.737; years of the 2026-31 reg period 2027-28: 2023 $/km
|  | Unitised EFD 7.5 yearly site visit for battery change and inspection opex cost |  | 2 2026-27: 271.653; years of the 2026-31 reg period 2027-28: 2023 $/km
|  | Unitised EFD annual SaaS licencing opex cost after the first 5 years |  | 2 2026-27: 233.8165; years of the 2026-31 reg period 2027-28: 2023 $/km
|  | Unitised annual alert validation opex cost |  | 2 2026-27: 10.3288; years of the 2026-31 reg period 2027-28: 2023 $/km
|  | Total length of bare 22kV non-REFCL lines lines in HBRA |  | 2 2026-27: 8795; years of the 2026-31 reg period 2027-28: km
|  | Total EFD hardware and installation capex cost |  | 2 2026-27: 45054472.1798; years of the 2026-31 reg period 2027-28: 2023 $
|  | Total EFD 7.5 yearly site visit for battery change and inspection opex cost |  | 2 2026-27: 2389188.2765; years of the 2026-31 reg period 2027-28: 2023 $
|  | Total EFD annual SaaS licencing opex cost after the first 5 years |  | 2 2026-27: 2056416.3806; years of the 2026-31 reg period 2027-28: 2023 $
|  | Total annual alert validation opex cost |  | 2 2026-27: 90841.6311; years of the 2026-31 reg period 2027-28: 2023 $
|  | Progam duration |  | 2 2026-27: 5; years of the 2026-31 reg period 2027-28: years
|  |  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46
|  | Option 3 capex costs |  | 5 2026-27: 9010894.436; years 2027-28: 9010894.436; years 2028-29: 9010894.436; years 2029-30: 9010894.436; years 2030-31: 9010894.436
|  | Option 3 opex costs |  | 90841.6311 | 90841.6311 | 90841.6311 | 90841.6311 | 90841.6311 | 2147258.0117 | 2147258.0117 | 2147258.0117 | 2625095.667 | 2625095.667 | 2625095.667 | 2625095.667 | 2625095.667 | 2147258.0117 | 2147258.0117 | 1717806.4094 | 1288354.807 | 858903.2047 | 429451.6023
Option 4 - Targeted installation of EFDs on bare 22kV non-REFCL lines lines in HBRA
This option deploys EFD on 1,500km of highest risk bare 22kV non-REFCL lines in HBRA
|  | EFD applied to |  | 5 2026-27: 1500; years 2027-28: km of bare 22kV non-REFCL lines in HBRA
|  | Total EFD hardware and installation capex cost |  | 5 2026-27: 7684105.5452; years 2027-28: 2023 $
|  | Total EFD 7.5 yearly site visit for battery change and inspection opex cost |  | 5 2026-27: 407479.5241; years 2027-28: 2023 $
|  | Total EFD annual SaaS licencing opex cost after the first 5 years |  | 5 2026-27: 350724.7949; years 2027-28: 2023 $
|  | Total annual alert validation opex cost |  | 5 2026-27: 15493.1719; years 2027-28: 2023 $
|  | Progam duration |  | 5 2026-27: 2; years 2027-28: years of the 2026-31 reg period
|  |  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46
|  | Option 4 EFD capex costs |  | 2 2026-27: 3842052.7726; years of the 2026-31 reg period 2027-28: 3842052.7726
|  | Option 4 opex costs |  | 15493.1719 | 15493.1719 | 15493.1719 | 15493.1719 | 15493.1719 | 366217.9668 | 366217.9668 | 366217.9668 | 569957.7288 | 569957.7288 | 366217.9668 | 366217.9668 | 366217.9668 | 366217.9668 | 366217.9668 | 183108.9834
Option 5 - Targeted installation of covered conductor and EFDs on bare 22kV non-REFCL lines lines in HBRA
EFD on 1,500km of highest risk bare 22kV non-REFCL lines in HBRA
Install covered conductor on 62km of bare 22kV non-REFCL lines that do not have EFD monitoring
|  | EFD applied to |  | 2 2026-27: 1500; years of the 2026-31 reg period 2027-28: km of bare 22kV non-REFCL lines in HBRA
|  | Total EFD hardware and installation capex cost |  | 2 2026-27: 7684105.5452; years of the 2026-31 reg period 2027-28: 2023 $
|  | Total EFD 7.5 yearly site visit for battery change and inspection opex cost |  | 2 2026-27: 407479.5241; years of the 2026-31 reg period 2027-28: 2023 $
|  | Total EFD annual SaaS licencing opex cost after the first 5 years |  | 2 2026-27: 350724.7949; years of the 2026-31 reg period 2027-28: 2023 $
|  | Total annual alert validation opex cost |  | 2 2026-27: 15493.1719; years of the 2026-31 reg period 2027-28: 2023 $
|  | Length of SWER lines to be replaced with covered conductor, which are not monitored by EFD |  | 2 2026-27: 62; years of the 2026-31 reg period 2027-28: km
|  | SWER covered conductor unit cost |  | 2 2026-27: 152000; years of the 2026-31 reg period 2027-28: 2023 $/km
|  | Covered conductor capex costs |  | 2 2026-27: 9424000; years of the 2026-31 reg period 2027-28: 2023 $
|  | Total program upfront capex cost |  | 2 2026-27: 17108105.5452; years of the 2026-31 reg period 2027-28: 2023 $
|  | Progam duration |  | 2 2026-27: 2; years of the 2026-31 reg period 2027-28: years of the 2026-31 reg period
|  |  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46
|  | Option 5 EFD capex costs |  | 2 2026-27: 3842052.7726; years of the 2026-31 reg period 2027-28: 3842052.7726
|  | Option 5 covered conductor capex costs |  | 2 2026-27: 4712000; years of the 2026-31 reg period 2027-28: 4712000
|  | Option 5 opex costs |  | 15493.1719 | 15493.1719 | 15493.1719 | 15493.1719 | 15493.1719 | 366217.9668 | 366217.9668 | 366217.9668 | 569957.7288 | 569957.7288 | 366217.9668 | 366217.9668 | 366217.9668 | 366217.9668 | 366217.9668 | 183108.9834

## Workings_risks
Powercor
Minimise bushfire risk from bare 22kV non-REFCL lines in HBRA
WORKINGS - RISKS
|  |  | Escalation factor from December 2022 to December 2023 | 1.0564
|  |  | Descalation factor from June 2024 to December 2023 | 0.963
Option 1 (base case) - no change to existing practices
Bushfire risk
|  | Annual bushfire risk |  | 17325425.6925 | 2023 $
|  | Total energy at risk over 5 years for non-REFCL 22kV lines and downstream SWER |  | 175499842 | 5 years
|  | Average annual energy at risk for non-REFCL 22kV lines and downstream SWER |  | 35099968.4 | pa
|  | Non-REFCL 22kV lines |  | 7239 | km
|  | Average annual energy at risk per km for non-REFCL 22kV lines and downstream SWER |  | 4848.7316 | 2023 $/km
|  | Average annual energy at risk per km for SWER |  | 40.17 | 2023 $/km
|  | Annual energy at risk per km of non-REFCL 22kV lines |  | 4808.5616 | 2023 $/km
|  | Total length of bare 22kV non-REFCL lines in HBRA |  | 8795 | km
|  | Annual energy at risk for bare 22kV non-REFCL lines in HBRA |  | 42291299.6943 | 2023 $
Option 2 - Targeted installation of covered conductor on bare 22kV non-REFCL lines lines in HBRA
Bushfire risk
|  |  | Annual bushfire risk for 62km conductor | 853135 | 2023 $
|  |  | Bushfire risk reduction proportion | 63.5%
|  |  | Annual bushfire risk reduction after installation of 62km of covered conductor | 572310.2851 | 2023 $
|  |  | Residual annual bushfire risk after program completion | 16753115.4074 | 2023 $
|  |  | Length of bare 22kV non-REFCL lines protected by covered condutor | 62 | km
|  |  | Total annual energy at risk from covered conductor | 298130.8222 | 2023 $
|  |  | Progam duration | 2 | years
|  |  | Annual bushfire risk reduction for each of the program year | 286155.1425
|  |  | Annual energy at risk reduction for each of program year | 149065.4111
|  |  |  | Program implementation |  |  |  |  | Risks post implementation with 30 years lifespan of covered conductor
|  |  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46
|  | Residual annual bushfire risk cost |  | 17039270.55 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074
|  | Residual energy at risk |  | 42142234.2832 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721
Option 3 - Install early fault detection (EFDs) on all bare 22kV non-REFCL lines lines in HBRA
Bushfire risk
|  | Annual bushfire risk reduction after program completion |  | Program implementation 2026-27: 1214892.6553; Program implementation 2027-28: 2023 $
|  | Residual annual bushfire risk after program completion |  | Program implementation 2026-27: 16110533.0372; Program implementation 2027-28: 2023 $
Energy at risk reduction by EFD | bar: Program implementation 2026-27
|  | Annual energy at risk reduction per km of bare 22kV non-REFCL lines in HBRA by EFD |  | Program implementation 2026-27: 336.5993; Program implementation 2027-28: 2023 $/km
|  | Total length of bare 22kV non-REFCL lines in HBRA |  | Program implementation 2026-27: 8795; Program implementation 2027-28: km
|  | Total annual energy at risk reduction from EFD |  | Program implementation 2026-27: 2960390.9786; Program implementation 2027-28: 2023 $
|  | Progam duration |  | Program implementation 2026-27: 5; Program implementation 2027-28: years
|  | Annual bushfire risk reduction for each of the program year |  | Program implementation 2026-27: 242978.5311
|  | Annual energy at risk reduction for each of program year |  | Program implementation 2026-27: 592078.1957
|  |  |  | Program implementation |  |  |  |  | Risks post implementation with 15 years lifespan of EFD
|  |  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46
|  | Residual annual bushfire risk cost |  | 17082447.1615 | 16839468.6304 | 16596490.0993 | 16353511.5683 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16110533.0372 | 16353511.5683 | 16596490.0993 | 16839468.6304 | 17082447.1615 | 17325425.6925
|  | Residual energy at risk |  | 41699221.4986 | 41107143.3029 | 40515065.1072 | 39922986.9114 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39330908.7157 | 39922986.9114 | 40515065.1072 | 41107143.3029 | 41699221.4986 | 42291299.6943
Option 4 - Targeted installation of EFDs on bare 22kV non-REFCL lines lines in HBRA
Bushfire risk
|  | Annual bushifre risk reduction from EFD after installation |  | Program implementation 2026-27: 302138.5212; Program implementation 2027-28: 2023 $
|  | Residual annual bushfire risk after program completion |  | Program implementation 2026-27: 17023287.1713; Program implementation 2027-28: 2023 $
Energy at risk
Energy at risk reduction by EFD | bar: Program implementation 2026-27
|  | Annual energy at risk reduction per km of bare 22kV non-REFCL lines in HBRA protected by EFD |  | Program implementation 2026-27: 336.5993; Program implementation 2027-28: 2023 $/km
|  | Length of bare 22kV non-REFCL lines protected by EFD |  | Program implementation 2026-27: 1500; Program implementation 2027-28: km
|  | Total annual energy at risk reduction from EFD |  | Program implementation 2026-27: 504898.973; Program implementation 2027-28: 2023 $
|  | Progam duration |  | Program implementation 2026-27: 2; Program implementation 2027-28: years of the 2026-31 reg period
|  | Annual bushfire risk reduction for each of the program year |  | Program implementation 2026-27: 151069.2606; Program implementation 2027-28: 2023 $
|  | Annual energy at risk reduction for each of program year |  | Program implementation 2026-27: 252449.4865; Program implementation 2027-28: 2023 $
|  |  |  | Program implementation |  | Risks post implementation with 15 years lifespan of EFD
|  |  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46
|  | Residual annual bushfire risk cost |  | 17174356.4319 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17023287.1713 | 17174356.4319 | 17325425.6925 | 17325425.6925 | 17325425.6925 | 17325425.6925
|  | Residual energy at risk |  | 42038850.2078 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 41786400.7213 | 42038850.2078 | 42291299.6943 | 42291299.6943 | 42291299.6943 | 42291299.6943
Option 5 - Targeted installation of covered conductor and EFDs on bare 22kV non-REFCL lines lines in HBRA
Bushfire risk
|  |  | Annual bushifre risk reduction from EFD after installation | Program implementation 2026-27: 302138.5212; Program implementation 2027-28: 2023 $
|  |  | Annual bushfire risk reduction after installation of 62km of covered conductor | Program implementation 2026-27: 572310.2851; Program implementation 2027-28: 2023 $
|  |  | Total annual bushfire risk reduction | Program implementation 2026-27: 874448.8063; Program implementation 2027-28: 2023 $
|  |  | Residual annual bushfire risk after program completion | Program implementation 2026-27: 16450976.8862; Program implementation 2027-28: 2023 $
Energy at risk
Energy at risk reduction by EFD | bar: Program implementation 2026-27
|  |  | Annual energy at risk reduction per km of bare 22kV non-REFCL lines in HBRA protected by EFD | Program implementation 2026-27: 336.5993; Program implementation 2027-28: in 2023 $/km
|  |  | Length of bare 22kV non-REFCL lines protected by EFD | Program implementation 2026-27: 1500; Program implementation 2027-28: km
|  |  | Total annual energy at risk reduction from EFD | Program implementation 2026-27: 504898.973; Program implementation 2027-28: 2023 $
|  |  | Length of bare 22kV non-REFCL lines protected by covered condutor | Program implementation 2026-27: 62; Program implementation 2027-28: km
|  |  | Total annual energy at risk reduction from covered conductor | Program implementation 2026-27: 298130.8222; Program implementation 2027-28: 2023 $
|  |  | Residual annual energy at risk after program completion | Program implementation 2026-27: 41488269.8991; Program implementation 2027-28: 2023 $
|  |  | Progam duration | Program implementation 2026-27: 2
|  |  | Annual bushfire risk reduction for each of the program year | Program implementation 2026-27: 437224.4032; Program implementation 2027-28: 2023 $
|  |  | Annual energy at risk reduction for each of program year | Program implementation 2026-27: 401514.8976; Program implementation 2027-28: 2023 $
|  |  |  | Program implementation |  | Risks post implementation with 15 years lifespan of EFD
|  |  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46
|  |  | Residual annual bushfire risk cost | 16888201.2893 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16450976.8862 | 16602046.1468 | 16753115.4074 | 16753115.4074 | 16753115.4074 | 16753115.4074
|  |  | Residual energy at risk | 41889784.7967 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41488269.8991 | 41740719.3856 | 41993168.8721 | 41993168.8721 | 41993168.8721 | 41993168.8721

## Misc_calcs
Powercor
Minimise bushfire risk from bare 22kV non-REFCL lines in HBRA
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 1 | TRUE
| Option 3 | 1 | TRUE
| Option 4 | 1 | TRUE
| Option 5 | 1 | TRUE
| First year | 1
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
Powercor
Minimise bushfire risk from bare 22kV non-REFCL lines in HBRA
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | FALSE |  |  | FALSE
Option5 | Option 5 | FALSE |  |  | FALSE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
Powercor
| Reliability in worst-served areas | per MWh | 151432.8174
| Network resilience | per MWh | 24590
| Enabling solar exports | per MWh | 88.3577
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.35181
| Customer value of time - business | per minute customer time | 0.35181
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020